## Notes
Sub-Transmission Feeders Forecasts (Energex Distribution Annual Planning Report 2021-22 to 2025-26)
This workbook provides 5 year forecast capacity and loading information for sub-transmission feeders in the Energex network.
This workbook forms part of the Energex Distribution Annual Planning Report 2021-22 to 2025-26 (DAPR) and should be read in conjunction with the report document.
Energex Distribution Annual Planning Report is prepared and made available solely for information purposes. While care was taken in the preparation of the information in this report, and it is provided in good faith, Energex accepts no responsibility or liability (including without limitation, liability to any person by reason of negligence or negligent mis-statement) for any loss or damage that may be incurred by any person acting in reliance on this information or assumptions drawn from it, except to the extent that liability under any applicable Queensland or Commonwealth of Australia statute cannot be excluded.
It contains assumptions regarding, among other things, economic growth and load forecasts which may or may not prove to be correct. The forecasts included in the document involve subjective judgements and analysis which are subject to significant uncertainties and contingencies, many of which are out of the control of Energex. Furthermore, forecasted data is subject to ongoing variation due to COVID 19 impacts. Energex makes no representation or warranty as to the accuracy, reliability, completeness or suitability for any particular purpose of the information in this document. All information should be independently investigated, reviewed, analysed and verified, and must not be relied upon in connection with any investment proposal or decision.
The following sections list the 33kV feeders, their forecast loads, power factor, customer category and available load transfers. The feeder loads are calculated from load flow results using forecast substation demands. For the transmission and sub-transmission feeders, load flow studies are conducted for system normal and single contingency situations.
The forecast and capacity cut-off date for the winter season is 1 June of each year, and for the summer season is 1 December of each year. For example, 2022 winter forecast includes all committed projects with a proposed commissioning date up to 1 June 2022, and the 2021/22 summer forecast includes all committed projects with a proposed commissioning date up to 1 December 2021.
Assessment of 33kV feeders is performed under four possible risk periods: winter day, winter night, summer day and summer night. For the winter table, the worst case (highest) load between winter day and winter night has been represented in the table.
Peak, reconciled, compensated load forecasts have been used in the 33kV feeder analyses, with 50 PoE forecast load used for single contingency studies, and 10 PoE forecast load used for system normal studies.
Feeder capacities are shown for ECC and NCC. These ratings have also been adjusted for known committed projects. All load transfers associated with contingent condition include acceptable feeder voltage profiles.
Although the conductor rating is generally the limiting factor for feeder capacity, there are other significant items of plant, such as the feeder circuit breaker, that can also restrict capacity. Furthermore, other factors such as voltage constraints and load sharing between parallel underground feeders can sometimes de‑rate the capacity of the feeders due to thermal characteristic constraints. Each of these factors has been taken into account in the production of the forecast tables.
Interconnected feeders that supply multiple customers are examined in the following tables. Feeders exclusively supplying a customer owned substation or dedicated to a customer are not included in these tables.
A definition of terms is shown in the table below.
Definition of Terms Feeder Capacity and Forecast Tables
Term | Definition
NCC Rating (A) | Normal Cyclic Capacity - the total capacity with all network components and equipment intact. This is the maximum permissible peak daily loading for a given load cycle that a feeder can supply each day of its life. For overhead feeders, the NCC is the conductor rating with an assumed 1m/s wind, orthogonal to the line. For underground cables, the NCC assumes that there are sufficient temperature and current operating margins from the thermal inertia of the cable and its surroundings.
10 PoE Load (A) | Peak load forecast with 10% probability of being exceeded (one in every 10 years will be exceeded). Based on normal expected growth rates and weather corrected starting loads.
Power Factor (System Normal) | Lowest power factor along the feeder at 10 PoE Peak Load. Where the Power Factor is either 0 the feeder is a normally open feeder that does not have load under System Normal conditions.
ECC Rating (A) | Emergency Cyclic Capacity – the long term firm delivery capacity under single contingency conditions. Some underground cables are installed in close proximity to other circuits and are normally de‑rated to allow for the heat generated by the adjacent cables. ECC is the higher capacity available when any adjacent circuits have been unloaded. For overhead conductors which do not benefit from this phenomenon, the ECC is synonymous with the NCC.
50 PoE Load (A) | Peak load forecast with 50% probability of being exceeded (one in every two years will be exceeded). Based on normal expected growth rates & weather corrected starting loads. This is the worst case (highest) load forecast beween winter day and winter night.
Security Standard | For security standard application, the general type of customer a sub-transmission, or transmission feeder is supplying.
Transfers | This is the total amount of load transfers that are available following the worst case network contingency. This includes automatic transfers that are controlled automatically through SCADA and are generally implemented within a minute, load transfers that can be implemented through screen switching by a network controller, manual transfers that are deployed via manually controlled switchgear locally by field staff, and mobile generation which can be deployed by field staff by moving generation to specific sites. It should be noted under the Safety Net in the Distribution Authority, it is generally assumed that 4MVA (70A) of generation is available for Urban feeders to meet this criteria and 10MVA (170A) is available for Rural feeders. These values have been used as a default in the forecast tables where these are sufficient to reduce the 50PoE load below the ECC rating. Where the load is still above the ECC rating, specific load transfers have been calculated for the feeder to determine whether the Safety Net criteria is met.
Hours PA > 95% Peak Load | The forecast number of hours per annum where the load exceeded 95% of the peak 50 PoE demand. This information is not readily available for every feeder without significant analysis being undertaken. As such, this has only been provided where a feeder does not meet the Safety Net criteria or is otherwise in the Limitations and Proposed Solutions table.

## 33kV Feeders - Winter
Bulk Supply Name | Feeder | From Substation | To Substation | Attributes | 2022 | 2023 | 2024 | 2025 | 2026 | Security Standard | Transfers | Hours above 95%
Abermain Bulk | 357-1 | Abermain BS | 357 Tee1 | NCC Rating (A) | 554 | 554 | 554 | 554 | 554 | Urban | 70
Abermain Bulk | 357-1 | Abermain BS | 357 Tee1 | 10 POE Load (A) | 105.394 | 108.8231 | 106.3518 | 104.1353 | 103.5131
Abermain Bulk | 357-1 | Abermain BS | 357 Tee1 | Power Factor | 0.9989 | 0.99871 | 0.99884 | 0.99896 | 0.99899
Abermain Bulk | 357-1 | Abermain BS | 357 Tee1 | ECC Rating (A) | 554 | 554 | 554 | 554 | 554
Abermain Bulk | 357-1 | Abermain BS | 357 Tee1 | 50 POE Load (A) | 256.402 | 257.5789 | 254.9944 | 251.2161 | 250.6681
Abermain Bulk | 357-2 | 357 Tee1 | Redbank | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Abermain Bulk | 357-2 | 357 Tee1 | Redbank | 10 POE Load (A) | 0.19813 | 0.19807 | 0.19811 | 0.19814 | 0.19815
Abermain Bulk | 357-2 | 357 Tee1 | Redbank | Power Factor | 1.4767e-05 | 1.4765e-05 | 1.4766e-05 | 1.4766e-05 | 1.4766e-05
Abermain Bulk | 357-2 | 357 Tee1 | Redbank | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Abermain Bulk | 357-2 | 357 Tee1 | Redbank | 50 POE Load (A) | 238 | 237 | 236 | 236 | 236
Abermain Bulk | 357-3 | 357 Tee1 | Moggill | NCC Rating (A) | 840 | 840 | 840 | 840 | 840 | Urban | 70
Abermain Bulk | 357-3 | 357 Tee1 | Moggill | 10 POE Load (A) | 105.6415 | 109.0823 | 106.6027 | 104.3784 | 103.7541
Abermain Bulk | 357-3 | 357 Tee1 | Moggill | Power Factor | 0.9992 | 0.99907 | 0.99916 | 0.99925 | 0.99927
Abermain Bulk | 357-3 | 357 Tee1 | Moggill | ECC Rating (A) | 917 | 917 | 917 | 917 | 917
Abermain Bulk | 357-3 | 357 Tee1 | Moggill | 50 POE Load (A) | 266 | 264 | 261 | 259 | 259
Abermain Bulk | 358-1 | Abermain BS | Ebbw Vale | NCC Rating (A) | 525 | 525 | 525 | 525 | 525 | Rural | 170
Abermain Bulk | 358-1 | Abermain BS | Ebbw Vale | 10 POE Load (A) | 0.82619 | 0.82619 | 0.82619 | 0.82619 | 0.82619
Abermain Bulk | 358-1 | Abermain BS | Ebbw Vale | Power Factor | -6.9809e-06 | -6.981e-06 | -6.981e-06 | -6.981e-06 | -6.9806e-06
Abermain Bulk | 364-1 | Marburg | Rosewood | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
Abermain Bulk | 364-1 | Marburg | Rosewood | 10 POE Load (A) | 57.4455 | 63.2858 | 70.8476 | 94.4466 | 101.6197
Abermain Bulk | 364-1 | Marburg | Rosewood | Power Factor | 0.99994 | 0.99995 | 0.99999 | 0.99888 | 0.99867
Abermain Bulk | 364-1 | Marburg | Rosewood | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
Abermain Bulk | 364-1 | Marburg | Rosewood | 50 POE Load (A) | 202 | 226 | 242 | 260 | 260
Abermain Bulk | 365-1 | Abermain BS | 365 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Abermain Bulk | 365-1 | Abermain BS | 365 Tee1 | 10 POE Load (A) | 259.343 | 291.1059 | 319.6602 | 402.746 | 429.9367
Abermain Bulk | 365-1 | Abermain BS | 365 Tee1 | Power Factor | 0.97062 | 0.96928 | 0.96641 | 0.95762 | 0.95665
Abermain Bulk | 365-1 | Abermain BS | 365 Tee1 | ECC Rating (A) | 944 | 944 | 944 | 944 | 944
Abermain Bulk | 365-1 | Abermain BS | 365 Tee1 | 50 POE Load (A) | 646 | 732 | 779 | 827 | 827
Abermain Bulk | 365-2 | 365 Tee1 | 366 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Abermain Bulk | 365-2 | 365 Tee1 | 366 Tee1 | 10 POE Load (A) | 0.0095403 | 0.0095018 | 0.0094628 | 0.0093455 | 0.0093082
Abermain Bulk | 365-2 | 365 Tee1 | 366 Tee1 | Power Factor | 2.018e-05 | 2.018e-05 | 2.0181e-05 | 2.0181e-05 | 2.0182e-05
Abermain Bulk | 365-3 | 365 Tee1 | Karrabin | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Abermain Bulk | 365-3 | 365 Tee1 | Karrabin | 10 POE Load (A) | 259.5047 | 291.2696 | 319.8302 | 402.9341 | 430.1255
Abermain Bulk | 365-3 | 365 Tee1 | Karrabin | Power Factor | 0.97101 | 0.96975 | 0.96695 | 0.95839 | 0.95749
Abermain Bulk | 365-3 | 365 Tee1 | Karrabin | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Abermain Bulk | 365-3 | 365 Tee1 | Karrabin | 50 POE Load (A) | 511 | 579 | 616 | 654 | 654
Abermain Bulk | 366-1 | Abermain BS | 366 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Abermain Bulk | 366-1 | Abermain BS | 366 Tee1 | 10 POE Load (A) | 283.1174 | 317.7946 | 348.9682 | 439.6754 | 469.361
Abermain Bulk | 366-1 | Abermain BS | 366 Tee1 | Power Factor | 0.96129 | 0.95836 | 0.95376 | 0.93967 | 0.93708
Abermain Bulk | 366-1 | Abermain BS | 366 Tee1 | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Abermain Bulk | 366-1 | Abermain BS | 366 Tee1 | 50 POE Load (A) | 515 | 582 | 619 | 657 | 657
Abermain Bulk | 366-2 | 366 Tee1 | Karrabin | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Abermain Bulk | 366-2 | 366 Tee1 | Karrabin | 10 POE Load (A) | 283.1816 | 317.8597 | 349.0358 | 439.7503 | 469.4363
Abermain Bulk | 366-2 | 366 Tee1 | Karrabin | Power Factor | -0.97038 | -0.96934 | -0.96658 | -0.95766 | -0.95698
Abermain Bulk | 366-2 | 366 Tee1 | Karrabin | ECC Rating (A) | 845 | 845 | 845 | 845 | 845
Abermain Bulk | 366-2 | 366 Tee1 | Karrabin | 50 POE Load (A) | 574 | 649 | 690 | 732 | 740
Abermain Bulk | 366-3 | 366 Tee1 | 365 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Abermain Bulk | 366-3 | 366 Tee1 | 365 Tee1 | 10 POE Load (A) | 0.021395 | 0.021315 | 0.021233 | 0.020986 | 0.020908
Abermain Bulk | 366-3 | 366 Tee1 | 365 Tee1 | Power Factor | 9.0278e-06 | 9.0272e-06 | 9.0276e-06 | 9.0275e-06 | 9.0277e-06
Abermain Bulk | 367-1 | Abermain BS | Mt Crosby West | NCC Rating (A) | 581 | 581 | 581 | 581 | 581 | Rural | 170
Abermain Bulk | 367-1 | Abermain BS | Mt Crosby West | 10 POE Load (A) | 189.1103 | 187.7104 | 187.5227 | 186.7224 | 187.247
Abermain Bulk | 367-1 | Abermain BS | Mt Crosby West | Power Factor | 0.94995 | 0.95234 | 0.95234 | 0.95231 | 0.95233
Abermain Bulk | 367-1 | Abermain BS | Mt Crosby West | ECC Rating (A) | 581 | 581 | 581 | 581 | 581
Abermain Bulk | 367-1 | Abermain BS | Mt Crosby West | 50 POE Load (A) | 385 | 388 | 387 | 387 | 387
Abermain Bulk | 368-1 | Abermain BS | Mt Crosby | NCC Rating (A) | 552 | 552 | 552 | 552 | 552 | HighSec | 0
Abermain Bulk | 368-1 | Abermain BS | Mt Crosby | 10 POE Load (A) | 146.1288 | 144.2651 | 144.1406 | 143.6099 | 143.9578
Abermain Bulk | 368-1 | Abermain BS | Mt Crosby | Power Factor | 0.94088 | 0.94231 | 0.9423 | 0.94224 | 0.94228
Abermain Bulk | 368-1 | Abermain BS | Mt Crosby | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Abermain Bulk | 368-1 | Abermain BS | Mt Crosby | 50 POE Load (A) | 388 | 388 | 389 | 389 | 389
Abermain Bulk | 369-1 | Abermain BS | Nth Ipswich | NCC Rating (A) | 548 | 548 | 548 | 548 | 548 | Urban | 70
Abermain Bulk | 369-1 | Abermain BS | Nth Ipswich | 10 POE Load (A) | 136.1468 | 136.0213 | 137.9784 | 138.6091 | 140.0431
Abermain Bulk | 369-1 | Abermain BS | Nth Ipswich | Power Factor | 0.98793 | 0.98794 | 0.98783 | 0.98779 | 0.98771
Abermain Bulk | 369-1 | Abermain BS | Nth Ipswich | ECC Rating (A) | 548 | 548 | 548 | 548 | 548
Abermain Bulk | 369-1 | Abermain BS | Nth Ipswich | 50 POE Load (A) | 274 | 275 | 276 | 277 | 277
Abermain Bulk | 370-1 | Abermain BS | Nth Ipswich | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70
Abermain Bulk | 370-1 | Abermain BS | Nth Ipswich | 10 POE Load (A) | 138.5486 | 138.4209 | 140.4125 | 141.0544 | 142.5137
Abermain Bulk | 370-1 | Abermain BS | Nth Ipswich | Power Factor | 0.98864 | 0.98864 | 0.98854 | 0.9885 | 0.98843
Abermain Bulk | 370-1 | Abermain BS | Nth Ipswich | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Abermain Bulk | 370-1 | Abermain BS | Nth Ipswich | 50 POE Load (A) | 276 | 277 | 278 | 280 | 280
Abermain Bulk | 387-1 | Abermain BS | Marburg | NCC Rating (A) | 290 | 290 | 290 | 290 | 290 | Rural | 170
Abermain Bulk | 387-1 | Abermain BS | Marburg | 10 POE Load (A) | 124.5462 | 131.717 | 141.4592 | 167.3481 | 176.8574
Abermain Bulk | 387-1 | Abermain BS | Marburg | Power Factor | 0.99759 | 0.99753 | 0.99716 | 0.99577 | 0.99558
Abermain Bulk | 387-1 | Abermain BS | Marburg | ECC Rating (A) | 290 | 290 | 290 | 290 | 290
Abermain Bulk | 387-1 | Abermain BS | Marburg | 50 POE Load (A) | 163 | 177 | 187 | 198 | 205
Abermain Bulk | 3901-1 | Karrabin | Amberley | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Abermain Bulk | 3901-1 | Karrabin | Amberley | 10 POE Load (A) | 125.4902 | 124.6243 | 150.2137 | 233.3999 | 256.6063
Abermain Bulk | 3901-1 | Karrabin | Amberley | Power Factor | 0.95707 | 0.95522 | 0.952 | 0.94276 | 0.94389
Abermain Bulk | 3901-1 | Karrabin | Amberley | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Abermain Bulk | 3901-1 | Karrabin | Amberley | 50 POE Load (A) | 377 | 376 | 421 | 468 | 468
Abermain Bulk | 420-1 | Mt Crosby West | Mt Crosby | NCC Rating (A) | 490 | 490 | 490 | 490 | 490 | HighSec | 0
Abermain Bulk | 420-1 | Mt Crosby West | Mt Crosby | 10 POE Load (A) | 13.7983 | 14.7513 | 14.8068 | 15.0485 | 14.8892
Abermain Bulk | 420-1 | Mt Crosby West | Mt Crosby | Power Factor | 0.91432 | 0.88088 | 0.87675 | 0.85763 | 0.87045
Abermain Bulk | 420-1 | Mt Crosby West | Mt Crosby | ECC Rating (A) | 490 | 490 | 490 | 490 | 490
Abermain Bulk | 420-1 | Mt Crosby West | Mt Crosby | 50 POE Load (A) | 208 | 211 | 211 | 212 | 212
Abermain Bulk | 436-1 | Amberley | 436 Tee1 | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Rural | 170
Abermain Bulk | 436-1 | Amberley | 436 Tee1 | 10 POE Load (A) | 50.0446 | 47.1132 | 43.3578 | 29.6756 | 28.8594
Abermain Bulk | 436-1 | Amberley | 436 Tee1 | Power Factor | -0.76012 | -0.6981 | -0.59267 | 0.1716 | 0.36895
Abermain Bulk | 436-1 | Amberley | 436 Tee1 | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
Abermain Bulk | 436-1 | Amberley | 436 Tee1 | 50 POE Load (A) | 214 | 220 | 225 | 232 | 232
Abermain Bulk | 436-2 | 436 Tee1 | Ebeneezer | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170
Abermain Bulk | 436-2 | 436 Tee1 | Ebeneezer | 10 POE Load (A) | 0.17589 | 0.1752 | 0.1742 | 0.17119 | 0.17024
Abermain Bulk | 436-2 | 436 Tee1 | Ebeneezer | Power Factor | 5.5136e-06 | 5.5136e-06 | 5.5133e-06 | 5.5131e-06 | 5.5133e-06
Abermain Bulk | 436-4 | 436 Tee1 | Rosewood | NCC Rating (A) | 416 | 416 | 416 | 416 | 416 | Rural | 170
Abermain Bulk | 436-4 | 436 Tee1 | Rosewood | 10 POE Load (A) | 50.3531 | 47.4442 | 43.7158 | 30.1509 | 29.3566
Abermain Bulk | 436-4 | 436 Tee1 | Rosewood | Power Factor | -0.75285 | -0.68974 | -0.58322 | 0.16891 | 0.36235
Abermain Bulk | 436-4 | 436 Tee1 | Rosewood | ECC Rating (A) | 416 | 416 | 416 | 416 | 416
Abermain Bulk | 436-4 | 436 Tee1 | Rosewood | 50 POE Load (A) | 304 | 312 | 320 | 329 | 329
Abermain Bulk | 445-1 | Abermain BS | Moggill | NCC Rating (A) | 776 | 776 | 776 | 776 | 776 | Urban | 70
Abermain Bulk | 445-1 | Abermain BS | Moggill | 10 POE Load (A) | 142.9962 | 147.6511 | 144.2964 | 141.2874 | 140.4428
Abermain Bulk | 445-1 | Abermain BS | Moggill | Power Factor | 0.99803 | 0.99783 | 0.99797 | 0.9981 | 0.99813
Abermain Bulk | 445-1 | Abermain BS | Moggill | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Abermain Bulk | 445-1 | Abermain BS | Moggill | 50 POE Load (A) | 296 | 293 | 290 | 288 | 288
Abermain Bulk | 475-1 | Karrabin | Amberley | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Abermain Bulk | 475-1 | Karrabin | Amberley | 10 POE Load (A) | 123.6381 | 122.785 | 147.9967 | 229.9548 | 252.8184
Abermain Bulk | 475-1 | Karrabin | Amberley | Power Factor | 0.9578 | 0.95597 | 0.95278 | 0.94361 | 0.94473
Abermain Bulk | 475-1 | Karrabin | Amberley | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Abermain Bulk | 475-1 | Karrabin | Amberley | 50 POE Load (A) | 376 | 376 | 421 | 468 | 468
Abermain Bulk | 673-1 | Moggill | Kenmore | NCC Rating (A) | 636 | 636 | 636 | 636 | 636 | Urban | 70
Abermain Bulk | 673-1 | Moggill | Kenmore | 10 POE Load (A) | 3.4736 | 3.4715 | 3.4726 | 3.4737 | 3.4739
Abermain Bulk | 673-1 | Moggill | Kenmore | Power Factor | 2.3519e-06 | 2.3519e-06 | 2.3519e-06 | 2.3519e-06 | 2.3519e-06
Abermain Bulk | 673-1 | Moggill | Kenmore | ECC Rating (A) | 636 | 636 | 636 | 636 | 636
Abermain Bulk | 673-1 | Moggill | Kenmore | 50 POE Load (A) | 3.4779 | 3.4757 | 3.4767 | 3.4776 | 3.4778
Algester Bulk | 3400-1 | Algester BS | Calamvale | NCC Rating (A) | 735 | 735 | 735 | 735 | 735 | Urban | 70
Algester Bulk | 3400-1 | Algester BS | Calamvale | 10 POE Load (A) | 243.0435 | 240.666 | 241.6714 | 240.8112 | 242.9069
Algester Bulk | 3400-1 | Algester BS | Calamvale | Power Factor | 0.99439 | 0.99451 | 0.99446 | 0.9945 | 0.99439
Algester Bulk | 3400-1 | Algester BS | Calamvale | ECC Rating (A) | 810 | 810 | 810 | 810 | 810
Algester Bulk | 3400-1 | Algester BS | Calamvale | 50 POE Load (A) | 465 | 461 | 458 | 454 | 450
Algester Bulk | 3402-1 | Algester BS | Acacia Ridge | NCC Rating (A) | 728 | 728 | 728 | 728 | 728 | Urban | 70
Algester Bulk | 3402-1 | Algester BS | Acacia Ridge | 10 POE Load (A) | 139.5089 | 145.5848 | 150.4038 | 148.9675 | 148.8419
Algester Bulk | 3402-1 | Algester BS | Acacia Ridge | Power Factor | -0.93503 | -0.93414 | -0.99369 | -0.99405 | -0.99408
Algester Bulk | 3402-1 | Algester BS | Acacia Ridge | ECC Rating (A) | 782 | 782 | 782 | 782 | 782
Algester Bulk | 3402-1 | Algester BS | Acacia Ridge | 50 POE Load (A) | 287 | 283 | 281 | 279 | 279
Algester Bulk | 3403-1 | Algester BS | Acacia Ridge | NCC Rating (A) | 728 | 728 | 728 | 728 | 728 | Urban | 70
Algester Bulk | 3403-1 | Algester BS | Acacia Ridge | 10 POE Load (A) | 139.9053 | 145.9987 | 150.8353 | 149.3949 | 149.2689
Algester Bulk | 3403-1 | Algester BS | Acacia Ridge | Power Factor | -0.93506 | -0.93417 | -0.9937 | -0.99406 | -0.99409
Algester Bulk | 3403-1 | Algester BS | Acacia Ridge | ECC Rating (A) | 782 | 782 | 782 | 782 | 782
Algester Bulk | 3403-1 | Algester BS | Acacia Ridge | 50 POE Load (A) | 287 | 283 | 281 | 279 | 279
Algester Bulk | 3405-1 | Algester BS | Calamvale | NCC Rating (A) | 735 | 735 | 735 | 735 | 735 | Urban | 70
Algester Bulk | 3405-1 | Algester BS | Calamvale | 10 POE Load (A) | 243.3231 | 240.9429 | 241.9494 | 241.0882 | 243.1864
Algester Bulk | 3405-1 | Algester BS | Calamvale | Power Factor | 0.99438 | 0.99451 | 0.99445 | 0.9945 | 0.99439
Algester Bulk | 3405-1 | Algester BS | Calamvale | ECC Rating (A) | 810 | 810 | 810 | 810 | 810
Algester Bulk | 3405-1 | Algester BS | Calamvale | 50 POE Load (A) | 465 | 461 | 458 | 454 | 450
Archerfield Bulk | 597-1 | Rocklea | Salisbury | NCC Rating (A) | 710 | 710 | 710 | 710 | 710 | Urban | 70
Archerfield Bulk | 597-1 | Rocklea | Salisbury | 10 POE Load (A) | 143.703 | 136.7594 | 133.7782 | 132.4698 | 133.6162
Archerfield Bulk | 597-1 | Rocklea | Salisbury | Power Factor | 0.98506 | 0.98583 | 0.98616 | 0.98603 | 0.98618
Archerfield Bulk | 597-1 | Rocklea | Salisbury | ECC Rating (A) | 710 | 710 | 710 | 710 | 710
Archerfield Bulk | 597-1 | Rocklea | Salisbury | 50 POE Load (A) | 137.4382 | 130.8051 | 127.9566 | 126.7061 | 127.8016
Archerfield Bulk | 635-1 | Archerfield BS | Coopers Plains | NCC Rating (A) | 573 | 573 | 573 | 573 | 573 | Urban | 70
Archerfield Bulk | 635-1 | Archerfield BS | Coopers Plains | 10 POE Load (A) | 276.2149 | 247.9153 | 244.9642 | 239.5303 | 236.4932
Archerfield Bulk | 635-1 | Archerfield BS | Coopers Plains | Power Factor | 0.99792 | 0.93969 | 0.9399 | 0.9403 | 0.94052
Archerfield Bulk | 635-1 | Archerfield BS | Coopers Plains | ECC Rating (A) | 573 | 573 | 573 | 573 | 573
Archerfield Bulk | 635-1 | Archerfield BS | Coopers Plains | 50 POE Load (A) | 284.4059 | 233.1193 | 230.3501 | 224.9957 | 222.1528
Archerfield Bulk | 650-1 | Archerfield BS | Rocklea | NCC Rating (A) | 688 | 688 | 688 | 688 | 688 | Urban | 70
Archerfield Bulk | 650-1 | Archerfield BS | Rocklea | 10 POE Load (A) | 196.2641 | 189.0851 | 186.8889 | 184.4475 | 184.3869
Archerfield Bulk | 650-1 | Archerfield BS | Rocklea | Power Factor | 0.98199 | 0.98266 | 0.98285 | 0.98299 | 0.98313
Archerfield Bulk | 650-1 | Archerfield BS | Rocklea | ECC Rating (A) | 784 | 784 | 784 | 784 | 784
Archerfield Bulk | 650-1 | Archerfield BS | Rocklea | 50 POE Load (A) | 397 | 386 | 376 | 373 | 370
Archerfield Bulk | 651-1 | Archerfield BS | Rocklea | NCC Rating (A) | 688 | 688 | 688 | 688 | 688 | Urban | 70
Archerfield Bulk | 651-1 | Archerfield BS | Rocklea | 10 POE Load (A) | 194.0175 | 186.9211 | 184.7502 | 182.3369 | 182.277
Archerfield Bulk | 651-1 | Archerfield BS | Rocklea | Power Factor | 0.98205 | 0.98272 | 0.98291 | 0.98306 | 0.98319
Archerfield Bulk | 651-1 | Archerfield BS | Rocklea | ECC Rating (A) | 784 | 784 | 784 | 784 | 784
Archerfield Bulk | 651-1 | Archerfield BS | Rocklea | 50 POE Load (A) | 397 | 386 | 377 | 373 | 370
Ashgrove West Bulk | 432-1 | Ashgrove West BS | Toowong | NCC Rating (A) | 516 | 516 | 516 | 516 | 516 | Urban | 70
Ashgrove West Bulk | 432-1 | Ashgrove West BS | Toowong | 10 POE Load (A) | 13.5922 | 13.5922 | 13.5922 | 13.5922 | 13.5922
Ashgrove West Bulk | 432-1 | Ashgrove West BS | Toowong | Power Factor | 4.2657e-05 | 4.2657e-05 | 4.2657e-05 | 4.2657e-05 | 4.2657e-05
Ashgrove West Bulk | 432-1 | Ashgrove West BS | Toowong | ECC Rating (A) | 516 | 516 | 516 | 516 | 516
Ashgrove West Bulk | 432-1 | Ashgrove West BS | Toowong | 50 POE Load (A) | 13.5922 | 13.5922 | 13.5922 | 13.5922 | 13.5922
Ashgrove West Bulk | 552-1 | Ashgrove West BS | Ashgrove | NCC Rating (A) | 598 | 598 | 598 | 598 | 598 | Urban | 70
Ashgrove West Bulk | 552-1 | Ashgrove West BS | Ashgrove | 10 POE Load (A) | 129.8966 | 129.072 | 129.4919 | 129.0335 | 130.1296
Ashgrove West Bulk | 552-1 | Ashgrove West BS | Ashgrove | Power Factor | 0.99996 | 0.99995 | 0.99995 | 0.99994 | 0.99996
Ashgrove West Bulk | 552-1 | Ashgrove West BS | Ashgrove | ECC Rating (A) | 634 | 634 | 634 | 634 | 634
Ashgrove West Bulk | 552-1 | Ashgrove West BS | Ashgrove | 50 POE Load (A) | 120.3592 | 119.6 | 119.9866 | 119.5645 | 120.5737
Ashgrove West Bulk | 565-1 | Ashgrove West BS | Ashgrove | NCC Rating (A) | 851 | 851 | 851 | 851 | 851 | Urban | 70
Ashgrove West Bulk | 565-1 | Ashgrove West BS | Ashgrove | 10 POE Load (A) | 89.6248 | 89.05 | 89.3427 | 89.0231 | 89.7872
Ashgrove West Bulk | 565-1 | Ashgrove West BS | Ashgrove | Power Factor | 0.99997 | 0.99998 | 0.99998 | 0.99999 | 0.99997
Ashgrove West Bulk | 565-1 | Ashgrove West BS | Ashgrove | ECC Rating (A) | 882 | 882 | 882 | 882 | 882
Ashgrove West Bulk | 565-1 | Ashgrove West BS | Ashgrove | 50 POE Load (A) | 82.972 | 82.4419 | 82.7118 | 82.4171 | 83.1217
Ashgrove West Bulk | 570-1 | Ashgrove West BS | Ashgrove | NCC Rating (A) | 634 | 634 | 634 | 634 | 634 | Urban | 70
Ashgrove West Bulk | 570-1 | Ashgrove West BS | Ashgrove | 10 POE Load (A) | 126.8806 | 126.0755 | 126.4855 | 126.0378 | 127.1081
Ashgrove West Bulk | 570-1 | Ashgrove West BS | Ashgrove | Power Factor | 0.99866 | 0.99856 | 0.99861 | 0.99856 | 0.99868
Ashgrove West Bulk | 570-1 | Ashgrove West BS | Ashgrove | ECC Rating (A) | 712 | 712 | 712 | 712 | 712
Ashgrove West Bulk | 570-1 | Ashgrove West BS | Ashgrove | 50 POE Load (A) | 117.568 | 116.8267 | 117.2042 | 116.792 | 117.7775
Ashgrove West Bulk | 585-1 | Ashgrove West BS | The Gap | NCC Rating (A) | 659 | 659 | 659 | 659 | 659 | Urban | 70
Ashgrove West Bulk | 585-1 | Ashgrove West BS | The Gap | 10 POE Load (A) | 134.0408 | 132.1303 | 131.806 | 130.5287 | 130.5805
Ashgrove West Bulk | 585-1 | Ashgrove West BS | The Gap | Power Factor | 1 | 0.99999 | 0.99999 | 0.99998 | 0.99998
Ashgrove West Bulk | 585-1 | Ashgrove West BS | The Gap | ECC Rating (A) | 659 | 659 | 659 | 659 | 659
Ashgrove West Bulk | 585-1 | Ashgrove West BS | The Gap | 50 POE Load (A) | 114 | 113 | 112 | 111 | 110
Ashgrove West Bulk | 586-1 | Ashgrove West BS | The Gap | NCC Rating (A) | 659 | 659 | 659 | 659 | 659 | Urban | 70
Ashgrove West Bulk | 586-1 | Ashgrove West BS | The Gap | 10 POE Load (A) | 134.099 | 132.1857 | 131.8609 | 130.5819 | 130.6338
Ashgrove West Bulk | 586-1 | Ashgrove West BS | The Gap | Power Factor | 1 | 1 | 1 | 1 | 1
Ashgrove West Bulk | 586-1 | Ashgrove West BS | The Gap | ECC Rating (A) | 659 | 659 | 659 | 659 | 659
Ashgrove West Bulk | 586-1 | Ashgrove West BS | The Gap | 50 POE Load (A) | 129 | 128 | 127 | 126 | 126
Ashgrove West Bulk | 590-1 | Ashgrove BS | Toowong | NCC Rating (A) | 705 | 705 | 705 | 705 | 705 | Urban | 70
Ashgrove West Bulk | 590-1 | Ashgrove BS | Toowong | 10 POE Load (A) | 268.2868 | 265.574 | 266.0824 | 264.779 | 265.5413
Ashgrove West Bulk | 590-1 | Ashgrove BS | Toowong | Power Factor | 0.98652 | 0.98664 | 0.98662 | 0.98668 | 0.98665
Ashgrove West Bulk | 590-1 | Ashgrove BS | Toowong | ECC Rating (A) | 705 | 705 | 705 | 705 | 705
Ashgrove West Bulk | 590-1 | Ashgrove BS | Toowong | 50 POE Load (A) | 489 | 487 | 485 | 484 | 484
Ashgrove West Bulk | 591-1 | Ashgrove BS | Toowong | NCC Rating (A) | 705 | 705 | 705 | 705 | 705 | Urban | 70
Ashgrove West Bulk | 591-1 | Ashgrove BS | Toowong | 10 POE Load (A) | 268.2049 | 265.4928 | 266.0011 | 264.6981 | 265.4602
Ashgrove West Bulk | 591-1 | Ashgrove BS | Toowong | Power Factor | 0.98647 | 0.9866 | 0.98658 | 0.98664 | 0.9866
Ashgrove West Bulk | 591-1 | Ashgrove BS | Toowong | ECC Rating (A) | 705 | 705 | 705 | 705 | 705
Ashgrove West Bulk | 591-1 | Ashgrove BS | Toowong | 50 POE Load (A) | 489 | 487 | 485 | 484 | 484
Ashgrove West Bulk | 675-1 | Ashgrove | Newmarket | NCC Rating (A) | 527 | 527 | 527 | 527 | 527 | Urban | 70
Ashgrove West Bulk | 675-1 | Ashgrove | Newmarket | 10 POE Load (A) | 17.172 | 17.1721 | 17.172 | 17.1721 | 17.1719
Ashgrove West Bulk | 675-1 | Ashgrove | Newmarket | Power Factor | 3.5471e-05 | 3.5471e-05 | 3.5471e-05 | 3.5471e-05 | 3.5471e-05
Ashgrove West Bulk | 675-1 | Ashgrove | Newmarket | ECC Rating (A) | 527 | 527 | 527 | 527 | 527
Ashgrove West Bulk | 675-1 | Ashgrove | Newmarket | 50 POE Load (A) | 17.1731 | 17.1731 | 17.1731 | 17.1731 | 17.173
Ashgrove West Bulk | 676-1 | Ashgrove | Newmarket | NCC Rating (A) | 492 | 492 | 492 | 492 | 492 | Urban | 70
Ashgrove West Bulk | 676-1 | Ashgrove | Newmarket | 10 POE Load (A) | 17.0458 | 17.0459 | 17.0458 | 17.0459 | 17.0458
Ashgrove West Bulk | 676-1 | Ashgrove | Newmarket | Power Factor | 3.5079e-05 | 3.5079e-05 | 3.5079e-05 | 3.5079e-05 | 3.5079e-05
Ashgrove West Bulk | 676-1 | Ashgrove | Newmarket | ECC Rating (A) | 527 | 527 | 527 | 527 | 527
Ashgrove West Bulk | 676-1 | Ashgrove | Newmarket | 50 POE Load (A) | 17.0469 | 17.0469 | 17.0469 | 17.0469 | 17.0468
Beaudesert Bulk | 314-1 | Beaudesert BS | Jimboomba | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Rural | 170
Beaudesert Bulk | 314-1 | Beaudesert BS | Jimboomba | 10 POE Load (A) | 1.6333 | 1.6333 | 1.6333 | 1.6333 | 1.6333
Beaudesert Bulk | 314-1 | Beaudesert BS | Jimboomba | Power Factor | 0.00013446 | 0.00013446 | 0.00013446 | 0.00013446 | 0.00013446
Beaudesert Bulk | 314-1 | Beaudesert BS | Jimboomba | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
Beaudesert Bulk | 314-1 | Beaudesert BS | Jimboomba | 50 POE Load (A) | 1.6333 | 1.6333 | 1.6333 | 1.6333 | 1.6333
Beaudesert Bulk | 404-1 | Beaudesert | Innisplain | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
Beaudesert Bulk | 404-1 | Beaudesert | Innisplain | 10 POE Load (A) | 89.8733 | 91.0319 | 93.1043 | 94.1816 | 96.3563
Beaudesert Bulk | 404-1 | Beaudesert | Innisplain | Power Factor | 0.98942 | 0.98923 | 0.98888 | 0.9887 | 0.98858
Beaudesert Bulk | 404-1 | Beaudesert | Innisplain | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
Beaudesert Bulk | 404-1 | Beaudesert | Innisplain | 50 POE Load (A) | 191 | 194 | 196 | 199 | 199
Beaudesert Bulk | 466-1 | Beaudesert BS | Bromelton | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170
Beaudesert Bulk | 466-1 | Beaudesert BS | Bromelton | 10 POE Load (A) | 84.5577 | 90.4826 | 104.3764 | 117.7336 | 125.7749
Beaudesert Bulk | 466-1 | Beaudesert BS | Bromelton | Power Factor | 0.99637 | 0.99482 | 0.99184 | 0.98892 | 0.9874
Beaudesert Bulk | 466-1 | Beaudesert BS | Bromelton | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
Beaudesert Bulk | 466-1 | Beaudesert BS | Bromelton | 50 POE Load (A) | 215 | 247 | 279 | 312 | 320
Beaudesert Bulk | 467-1 | Beaudesert BS | Bromelton | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170
Beaudesert Bulk | 467-1 | Beaudesert BS | Bromelton | 10 POE Load (A) | 56.9502 | 60.9299 | 70.2677 | 79.2646 | 84.6805
Beaudesert Bulk | 467-1 | Beaudesert BS | Bromelton | Power Factor | 0.99919 | 0.99968 | 1 | 0.9997 | 0.99936
Beaudesert Bulk | 467-1 | Beaudesert BS | Bromelton | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Beaudesert Bulk | 467-1 | Beaudesert BS | Bromelton | 50 POE Load (A) | 222 | 256 | 289 | 324 | 324
Beaudesert Bulk | 468-1 | Beaudesert BS | Beaudesert | NCC Rating (A) | 579 | 579 | 579 | 579 | 579 | Rural | 170
Beaudesert Bulk | 468-1 | Beaudesert BS | Beaudesert | 10 POE Load (A) | 203.7214 | 203.966 | 207.8581 | 210.2388 | 214.8818
Beaudesert Bulk | 468-1 | Beaudesert BS | Beaudesert | Power Factor | 0.96245 | 0.9624 | 0.96173 | 0.96126 | 0.96055
Beaudesert Bulk | 468-1 | Beaudesert BS | Beaudesert | ECC Rating (A) | 579 | 579 | 579 | 579 | 579
Beaudesert Bulk | 468-1 | Beaudesert BS | Beaudesert | 50 POE Load (A) | 329.9487 | 329.0094 | 333.4891 | 335.6997 | 341.5621
Beaudesert Bulk | 469-1 | Beaudesert BS | 469 Tee1 | NCC Rating (A) | 537 | 537 | 537 | 537 | 537 | Rural | 170
Beaudesert Bulk | 469-1 | Beaudesert BS | 469 Tee1 | 10 POE Load (A) | 208.6442 | 208.8786 | 212.8434 | 215.2613 | 219.9965
Beaudesert Bulk | 469-1 | Beaudesert BS | 469 Tee1 | Power Factor | 0.98466 | 0.98463 | 0.98417 | 0.98386 | 0.98337
Beaudesert Bulk | 469-1 | Beaudesert BS | 469 Tee1 | ECC Rating (A) | 537 | 537 | 537 | 537 | 537
Beaudesert Bulk | 469-1 | Beaudesert BS | 469 Tee1 | 50 POE Load (A) | 488 | 491 | 495 | 499 | 505
Beaudesert Bulk | 469-2 | 469 Tee1 | Beaudesert | NCC Rating (A) | 579 | 579 | 579 | 579 | 579 | Rural | 170
Beaudesert Bulk | 469-2 | 469 Tee1 | Beaudesert | 10 POE Load (A) | 127.8185 | 128.8738 | 132.5296 | 135.1669 | 139.2255
Beaudesert Bulk | 469-2 | 469 Tee1 | Beaudesert | Power Factor | 0.98122 | 0.98113 | 0.98052 | 0.98006 | 0.97946
Beaudesert Bulk | 469-2 | 469 Tee1 | Beaudesert | ECC Rating (A) | 579 | 579 | 579 | 579 | 579
Beaudesert Bulk | 469-2 | 469 Tee1 | Beaudesert | 50 POE Load (A) | 331 | 335 | 339 | 345 | 347
Beaudesert Bulk | 469-3 | 469 Tee1 | Mt Tamborine Bus 2 | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Rural | 170
Beaudesert Bulk | 469-3 | 469 Tee1 | Mt Tamborine Bus 2 | 10 POE Load (A) | 81.1612 | 80.3433 | 80.6634 | 80.4535 | 81.1413
Beaudesert Bulk | 469-3 | 469 Tee1 | Mt Tamborine Bus 2 | Power Factor | 0.99613 | 0.99616 | 0.99615 | 0.99616 | 0.99613
Beaudesert Bulk | 469-3 | 469 Tee1 | Mt Tamborine Bus 2 | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
Beaudesert Bulk | 469-3 | 469 Tee1 | Mt Tamborine Bus 2 | 50 POE Load (A) | 314 | 312 | 311 | 310 | 310
Beenleigh Bulk | 3590-1 | Beenleigh BS | Loganholme | NCC Rating (A) | 810 | 810 | 810 | 810 | 810 | Urban | 70
Beenleigh Bulk | 3590-1 | Beenleigh BS | Loganholme | 10 POE Load (A) | 284.022 | 278.8854 | 278.0575 | 275.5326 | 275.6671
Beenleigh Bulk | 3590-1 | Beenleigh BS | Loganholme | Power Factor | 0.99103 | 0.99118 | 0.99121 | 0.99128 | 0.99129
Beenleigh Bulk | 3590-1 | Beenleigh BS | Loganholme | ECC Rating (A) | 810 | 810 | 810 | 810 | 810
Beenleigh Bulk | 3590-1 | Beenleigh BS | Loganholme | 50 POE Load (A) | 465 | 461 | 457 | 454 | 454
Beenleigh Bulk | 3591-1 | Cornubia | Loganholme | NCC Rating (A) | 859 | 859 | 859 | 859 | 859 | Urban | 70
Beenleigh Bulk | 3591-1 | Cornubia | Loganholme | 10 POE Load (A) | 29.8573 | 29.0798 | 28.9732 | 28.5164 | 28.0628
Beenleigh Bulk | 3591-1 | Cornubia | Loganholme | Power Factor | 0.90212 | 0.90047 | 0.90029 | 0.89906 | 0.89668
Beenleigh Bulk | 3591-1 | Cornubia | Loganholme | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Beenleigh Bulk | 3591-1 | Cornubia | Loganholme | 50 POE Load (A) | 286 | 283 | 280 | 279 | 276
Beenleigh Bulk | 3600-1 | Yatala | Stapylton | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Rural | 170
Beenleigh Bulk | 3600-1 | Yatala | Stapylton | 10 POE Load (A) | 78.866 | 77.817 | 77.5221 | 76.6092 | 76.8602
Beenleigh Bulk | 3600-1 | Yatala | Stapylton | Power Factor | 0.98179 | 0.98194 | 0.98198 | 0.9821 | 0.98207
Beenleigh Bulk | 3600-1 | Yatala | Stapylton | ECC Rating (A) | 921 | 921 | 921 | 921 | 921
Beenleigh Bulk | 3600-1 | Yatala | Stapylton | 50 POE Load (A) | 199 | 197 | 195 | 194 | 194
Beenleigh Bulk | 3601-1 | Yatala | Stapylton | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Rural | 170
Beenleigh Bulk | 3601-1 | Yatala | Stapylton | 10 POE Load (A) | 75.5512 | 74.5464 | 74.2639 | 73.3895 | 73.6299
Beenleigh Bulk | 3601-1 | Yatala | Stapylton | Power Factor | 0.98029 | 0.98045 | 0.9805 | 0.98064 | 0.9806
Beenleigh Bulk | 3601-1 | Yatala | Stapylton | ECC Rating (A) | 921 | 921 | 921 | 921 | 921
Beenleigh Bulk | 3601-1 | Yatala | Stapylton | 50 POE Load (A) | 200 | 197 | 195 | 194 | 194
Beenleigh Bulk | 3620-1 | Beenleigh BS | Logan Village | NCC Rating (A) | 490 | 490 | 490 | 490 | 490 | Rural | 170
Beenleigh Bulk | 3620-1 | Beenleigh BS | Logan Village | 10 POE Load (A) | 1.821 | 1.821 | 1.821 | 1.821 | 1.821
Beenleigh Bulk | 3620-1 | Beenleigh BS | Logan Village | Power Factor | 0.00010523 | 0.00010523 | 0.00010523 | 0.00010523 | 0.00010523
Beenleigh Bulk | 3620-1 | Beenleigh BS | Logan Village | ECC Rating (A) | 490 | 490 | 490 | 490 | 490
Beenleigh Bulk | 3620-1 | Beenleigh BS | Logan Village | 50 POE Load (A) | 179 | 182 | 185 | 189 | 189
Beenleigh Bulk | 402-1 | Beenleigh BS | 402 Tee1 | NCC Rating (A) | 579 | 579 | 579 | 579 | 579 | Urban | 70
Beenleigh Bulk | 402-1 | Beenleigh BS | 402 Tee1 | 10 POE Load (A) | 147.7926 | 146.5478 | 147.4442 | 147.4176 | 149.0346
Beenleigh Bulk | 402-1 | Beenleigh BS | 402 Tee1 | Power Factor | 0.99144 | 0.9915 | 0.99145 | 0.99146 | 0.99137
Beenleigh Bulk | 402-1 | Beenleigh BS | 402 Tee1 | ECC Rating (A) | 579 | 579 | 579 | 579 | 579
Beenleigh Bulk | 402-1 | Beenleigh BS | 402 Tee1 | 50 POE Load (A) | 398 | 396 | 395 | 394 | 390
Beenleigh Bulk | 402-2 | 402 Tee1 | Tamborine Village | NCC Rating (A) | 469 | 469 | 469 | 469 | 469 | Urban | 70
Beenleigh Bulk | 402-2 | 402 Tee1 | Tamborine Village | 10 POE Load (A) | 65.3762 | 64.9843 | 65.5537 | 65.7486 | 66.6546
Beenleigh Bulk | 402-2 | 402 Tee1 | Tamborine Village | Power Factor | 0.9902 | 0.99024 | 0.99018 | 0.99017 | 0.99008
Beenleigh Bulk | 402-2 | 402 Tee1 | Tamborine Village | ECC Rating (A) | 469 | 469 | 469 | 469 | 469
Beenleigh Bulk | 402-2 | 402 Tee1 | Tamborine Village | 50 POE Load (A) | 61.6401 | 61.2729 | 61.8081 | 61.9919 | 62.8279
Beenleigh Bulk | 402-3 | 402 Tee1 | Mt Tamborine Bus 1 | NCC Rating (A) | 812 | 812 | 812 | 812 | 812 | Urban | 70
Beenleigh Bulk | 402-3 | 402 Tee1 | Mt Tamborine Bus 1 | 10 POE Load (A) | 82.5419 | 81.6889 | 82.0162 | 81.7948 | 82.5063
Beenleigh Bulk | 402-3 | 402 Tee1 | Mt Tamborine Bus 1 | Power Factor | 0.99609 | 0.99612 | 0.99611 | 0.99611 | 0.99609
Beenleigh Bulk | 402-3 | 402 Tee1 | Mt Tamborine Bus 1 | ECC Rating (A) | 812 | 812 | 812 | 812 | 812
Beenleigh Bulk | 402-3 | 402 Tee1 | Mt Tamborine Bus 1 | 50 POE Load (A) | 335 | 333 | 332 | 330 | 329
Beenleigh Bulk | 405-1 | Beenleigh BS | 405 Tee1 | NCC Rating (A) | 868 | 868 | 868 | 868 | 868 | Urban | 70
Beenleigh Bulk | 405-1 | Beenleigh BS | 405 Tee1 | 10 POE Load (A) | 207.5043 | 203.8645 | 203.2698 | 201.5137 | 201.8207
Beenleigh Bulk | 405-1 | Beenleigh BS | 405 Tee1 | Power Factor | 0.98853 | 0.98875 | 0.98879 | 0.9889 | 0.9889
Beenleigh Bulk | 405-1 | Beenleigh BS | 405 Tee1 | ECC Rating (A) | 988 | 988 | 988 | 988 | 988
Beenleigh Bulk | 405-1 | Beenleigh BS | 405 Tee1 | 50 POE Load (A) | 545 | 540 | 535 | 532 | 531
Beenleigh Bulk | 405-3 | 405 Tee1 | Cornubia | NCC Rating (A) | 820 | 820 | 820 | 820 | 820 | Urban | 70
Beenleigh Bulk | 405-3 | 405 Tee1 | Cornubia | 10 POE Load (A) | 207.6599 | 204.0189 | 203.4239 | 201.6672 | 201.9743
Beenleigh Bulk | 405-3 | 405 Tee1 | Cornubia | Power Factor | 0.98997 | 0.99016 | 0.99019 | 0.99028 | 0.99028
Beenleigh Bulk | 405-3 | 405 Tee1 | Cornubia | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Beenleigh Bulk | 405-3 | 405 Tee1 | Cornubia | 50 POE Load (A) | 460 | 456 | 452 | 449 | 447
Beenleigh Bulk | 419-1 | Loganholme | Tanah Merah | NCC Rating (A) | 892 | 892 | 892 | 892 | 892 | Urban | 70
Beenleigh Bulk | 419-1 | Loganholme | Tanah Merah | 10 POE Load (A) | 0.91736 | 0.91767 | 0.91772 | 0.91787 | 0.91787
Beenleigh Bulk | 419-1 | Loganholme | Tanah Merah | Power Factor | -2.6738e-06 | -2.6755e-06 | -2.6742e-06 | -2.6747e-06 | -2.6755e-06
Beenleigh Bulk | 419-1 | Loganholme | Tanah Merah | ECC Rating (A) | 896 | 896 | 896 | 896 | 896
Beenleigh Bulk | 419-1 | Loganholme | Tanah Merah | 50 POE Load (A) | 231.6063 | 228.6482 | 228.9771 | 227.9793 | 229.8388
Beenleigh Bulk | 426-1 | Beenleigh BS | Yatala | NCC Rating (A) | 785 | 785 | 785 | 785 | 785 | Rural | 170
Beenleigh Bulk | 426-1 | Beenleigh BS | Yatala | 10 POE Load (A) | 78.7469 | 77.6991 | 77.4045 | 76.4926 | 76.7434
Beenleigh Bulk | 426-1 | Beenleigh BS | Yatala | Power Factor | 0.99898 | 0.99898 | 0.99898 | 0.99898 | 0.99898
Beenleigh Bulk | 426-1 | Beenleigh BS | Yatala | ECC Rating (A) | 785 | 785 | 785 | 785 | 785
Beenleigh Bulk | 426-1 | Beenleigh BS | Yatala | 50 POE Load (A) | 163 | 161 | 160 | 159 | 159
Beenleigh Bulk | 427-1 | Beenleigh BS | Yatala | NCC Rating (A) | 785 | 785 | 785 | 785 | 785 | Rural | 170
Beenleigh Bulk | 427-1 | Beenleigh BS | Yatala | 10 POE Load (A) | 75.5011 | 74.4972 | 74.2149 | 73.3413 | 73.5815
Beenleigh Bulk | 427-1 | Beenleigh BS | Yatala | Power Factor | 0.98101 | 0.98121 | 0.98126 | 0.98144 | 0.98139
Beenleigh Bulk | 427-1 | Beenleigh BS | Yatala | ECC Rating (A) | 785 | 785 | 785 | 785 | 785
Beenleigh Bulk | 427-1 | Beenleigh BS | Yatala | 50 POE Load (A) | 164 | 161 | 160 | 159 | 159
Beenleigh Bulk | 453-1 | Beenleigh BS | Beenleigh Nth | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Beenleigh Bulk | 453-1 | Beenleigh BS | Beenleigh Nth | 10 POE Load (A) | 539.4357 | 538.0312 | 546.0189 | 549.6478 | 560.2664
Beenleigh Bulk | 453-1 | Beenleigh BS | Beenleigh Nth | Power Factor | 0.99333 | 0.99331 | 0.99317 | 0.99311 | 0.99293
Beenleigh Bulk | 453-1 | Beenleigh BS | Beenleigh Nth | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Beenleigh Bulk | 453-1 | Beenleigh BS | Beenleigh Nth | 50 POE Load (A) | 476 | 477 | 479 | 480 | 480
Beenleigh Bulk | 496-1 | Beenleigh Nth | Bethania | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Beenleigh Bulk | 496-1 | Beenleigh Nth | Bethania | 10 POE Load (A) | 277.0222 | 264.7477 | 267.6263 | 268.9235 | 273.883
Beenleigh Bulk | 496-1 | Beenleigh Nth | Bethania | Power Factor | -0.99477 | -0.99514 | -0.99505 | -0.99501 | -0.99486
Beenleigh Bulk | 496-1 | Beenleigh Nth | Bethania | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Beenleigh Bulk | 496-1 | Beenleigh Nth | Bethania | 50 POE Load (A) | 399.6902 | 386.3588 | 389.8964 | 391.0908 | 397.2359
Beerwah Bulk | 324-1 | Woodford | Kilcoy | NCC Rating (A) | 348 | 348 | 348 | 348 | 348 | Rural | 170
Beerwah Bulk | 324-1 | Woodford | Kilcoy | 10 POE Load (A) | 203.0619 | 203.6101 | 207.0876 | 207.1832 | 210.1181
Beerwah Bulk | 324-1 | Woodford | Kilcoy | Power Factor | 0.99111 | 0.98874 | 0.98821 | 0.98819 | 0.98774
Beerwah Bulk | 324-1 | Woodford | Kilcoy | ECC Rating (A) | 348 | 348 | 348 | 348 | 348
Beerwah Bulk | 324-1 | Woodford | Kilcoy | 50 POE Load (A) | 196.7917 | 197.4925 | 200.7825 | 200.873 | 203.647
Beerwah Bulk | 428-1 | Beerwah BS | Woodford | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Rural | 170
Beerwah Bulk | 428-1 | Beerwah BS | Woodford | 10 POE Load (A) | 223.6863 | 224.3817 | 228.7587 | 228.8794 | 232.5947
Beerwah Bulk | 428-1 | Beerwah BS | Woodford | Power Factor | 0.9639 | 0.95959 | 0.95799 | 0.95794 | 0.95658
Beerwah Bulk | 428-1 | Beerwah BS | Woodford | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
Beerwah Bulk | 428-1 | Beerwah BS | Woodford | 50 POE Load (A) | 215.6037 | 216.3766 | 220.4648 | 220.5776 | 224.0427
Beerwah Bulk | 447-1 | Somerset Dam | Kilcoy | NCC Rating (A) | 290 | 290 | 290 | 290 | 290 | Rural | 170
Beerwah Bulk | 447-1 | Somerset Dam | Kilcoy | 10 POE Load (A) | 1.2288 | 1.5186 | 1.5144 | 1.5143 | 1.5107
Beerwah Bulk | 447-1 | Somerset Dam | Kilcoy | Power Factor | 0.00025447 | 0.00025447 | 0.00025447 | 0.00025447 | 0.00025447
Beerwah Bulk | 447-1 | Somerset Dam | Kilcoy | ECC Rating (A) | 290 | 290 | 290 | 290 | 290
Beerwah Bulk | 447-1 | Somerset Dam | Kilcoy | 50 POE Load (A) | 196.7917 | 197.4925 | 200.7825 | 200.873 | 203.647
Beerwah Bulk | 477-1 | 477 Tee1 | Maleny | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
Beerwah Bulk | 477-1 | 477 Tee1 | Maleny | 10 POE Load (A) | 1.5861 | 1.5868 | 1.5867 | 1.587 | 1.5866
Beerwah Bulk | 477-1 | 477 Tee1 | Maleny | Power Factor | 0.00031257 | 0.00031257 | 0.00031257 | 0.00031257 | 0.00031257
Beerwah Bulk | 477-1 | 477 Tee1 | Maleny | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
Beerwah Bulk | 477-1 | 477 Tee1 | Maleny | 50 POE Load (A) | 1.5885 | 1.5891 | 1.5891 | 1.5893 | 1.589
Beerwah Bulk | 477-2 | 477 Tee1 | Woodford | NCC Rating (A) | 381 | 381 | 381 | 381 | 381 | Rural | 170
Beerwah Bulk | 477-2 | 477 Tee1 | Woodford | 10 POE Load (A) | 148.6141 | 146.2001 | 146.4443 | 145.6032 | 146.7692
Beerwah Bulk | 477-2 | 477 Tee1 | Woodford | Power Factor | 0.99262 | 0.99277 | 0.99275 | 0.9928 | 0.99273
Beerwah Bulk | 477-2 | 477 Tee1 | Woodford | ECC Rating (A) | 381 | 381 | 381 | 381 | 381
Beerwah Bulk | 477-2 | 477 Tee1 | Woodford | 50 POE Load (A) | 140.423 | 138.1561 | 138.3854 | 137.5954 | 138.6905
Beerwah Bulk | 477-3 | Beerwah | 477 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Beerwah Bulk | 477-3 | Beerwah | 477 Tee1 | 10 POE Load (A) | 148.2982 | 145.8877 | 146.1315 | 145.2916 | 146.4559
Beerwah Bulk | 477-3 | Beerwah | 477 Tee1 | Power Factor | 0.98689 | 0.9873 | 0.98726 | 0.98741 | 0.98721
Beerwah Bulk | 477-3 | Beerwah | 477 Tee1 | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Beerwah Bulk | 477-3 | Beerwah | 477 Tee1 | 50 POE Load (A) | 140.119 | 137.8554 | 138.0844 | 137.2956 | 138.389
Beerwah Bulk | 608-1 | Beerwah BS | Landsborough | NCC Rating (A) | 412 | 412 | 412 | 412 | 412 | Rural | 170
Beerwah Bulk | 608-1 | Beerwah BS | Landsborough | 10 POE Load (A) | 220.5678 | 227.0167 | 253.4205 | 261.7584 | 273.5833
Beerwah Bulk | 608-1 | Beerwah BS | Landsborough | Power Factor | 0.99179 | 0.99172 | 0.98992 | 0.98932 | 0.98843
Beerwah Bulk | 608-1 | Beerwah BS | Landsborough | ECC Rating (A) | 412 | 412 | 412 | 412 | 412
Beerwah Bulk | 608-1 | Beerwah BS | Landsborough | 50 POE Load (A) | 202 | 219 | 226 | 232 | 232
Belmont Bulk | 527-1 | Mt Gravatt | Upper Mt Gravatt | NCC Rating (A) | 631 | 631 | 631 | 631 | 631 | Urban | 70
Belmont Bulk | 527-1 | Mt Gravatt | Upper Mt Gravatt | 10 POE Load (A) | 34.2877 | 33.7474 | 33.7849 | 33.5575 | 33.7196
Belmont Bulk | 527-1 | Mt Gravatt | Upper Mt Gravatt | Power Factor | 0.82259 | 0.81072 | 0.80261 | 0.79426 | 0.78154
Belmont Bulk | 527-1 | Mt Gravatt | Upper Mt Gravatt | ECC Rating (A) | 818 | 818 | 631 | 631 | 631
Belmont Bulk | 527-1 | Mt Gravatt | Upper Mt Gravatt | 50 POE Load (A) | 158 | 157 | 3 | 3 | 3
Belmont Bulk | 631-1 | Belmont BS | Mt Gravatt | NCC Rating (A) | #N/A | #N/A | #N/A | #N/A | #N/A | Urban | 70
Belmont Bulk | 631-1 | Belmont BS | Mt Gravatt | 10 POE Load (A) | #N/A | #N/A | #N/A | #N/A | #N/A
Belmont Bulk | 631-1 | Belmont BS | Mt Gravatt | Power Factor | #N/A | #N/A | #N/A | #N/A | #N/A
Belmont Bulk | 631-1 | Belmont BS | Mt Gravatt | ECC Rating (A) | 494 | 494 | 494 | 494 | 494
Belmont Bulk | 631-1 | Belmont BS | Mt Gravatt | 50 POE Load (A) | 366 | 365 | 365 | 365 | 365
Belmont Bulk | 632-1 | Belmont BS | Mt Gravatt | NCC Rating (A) | #N/A | #N/A | #N/A | #N/A | #N/A | Urban | 70
Belmont Bulk | 632-1 | Belmont BS | Mt Gravatt | 10 POE Load (A) | #N/A | #N/A | #N/A | #N/A | #N/A
Belmont Bulk | 632-1 | Belmont BS | Mt Gravatt | Power Factor | #N/A | #N/A | #N/A | #N/A | #N/A
Belmont Bulk | 632-1 | Belmont BS | Mt Gravatt | ECC Rating (A) | 481 | 481 | 481 | 481 | 481
Belmont Bulk | 632-1 | Belmont BS | Mt Gravatt | 50 POE Load (A) | 366 | 364 | 364 | 364 | 364
Belmont Bulk | 647-1 | Belmont BS | Eight Mile Plains Bus 2 | NCC Rating (A) | 566 | 566 | 566 | 566 | 566 | Urban | 70
Belmont Bulk | 647-1 | Belmont BS | Eight Mile Plains Bus 2 | 10 POE Load (A) | 192.362 | 169.6114 | 251.3677 | 250.7854 | 253.5284
Belmont Bulk | 647-1 | Belmont BS | Eight Mile Plains Bus 2 | Power Factor | 0.99905 | 0.99944 | 0.99742 | 0.99744 | 0.99734
Belmont Bulk | 647-1 | Belmont BS | Eight Mile Plains Bus 2 | ECC Rating (A) | 602 | 602 | 602 | 602 | 602
Belmont Bulk | 647-1 | Belmont BS | Eight Mile Plains Bus 2 | 50 POE Load (A) | 464 | 459 | 454 | 451 | 449
Belmont Bulk | 660-1 | Belmont BS | Scrub Road | NCC Rating (A) | 716 | 716 | 716 | 716 | 716 | Urban | 70
Belmont Bulk | 660-1 | Belmont BS | Scrub Road | 10 POE Load (A) | 177.5535 | 171.4602 | 169.0533 | 166.1683 | 164.6038
Belmont Bulk | 660-1 | Belmont BS | Scrub Road | Power Factor | 0.98896 | 0.98925 | 0.98937 | 0.9895 | 0.98958
Belmont Bulk | 660-1 | Belmont BS | Scrub Road | ECC Rating (A) | 795 | 795 | 795 | 795 | 795
Belmont Bulk | 660-1 | Belmont BS | Scrub Road | 50 POE Load (A) | 361 | 358 | 355 | 354 | 354
Belmont Bulk | 661-1 | Belmont BS | Scrub Road | NCC Rating (A) | 716 | 716 | 716 | 716 | 716 | Urban | 70
Belmont Bulk | 661-1 | Belmont BS | Scrub Road | 10 POE Load (A) | 179.4511 | 173.2926 | 170.8601 | 167.9442 | 166.363
Belmont Bulk | 661-1 | Belmont BS | Scrub Road | Power Factor | 0.98896 | 0.98925 | 0.98937 | 0.9895 | 0.98958
Belmont Bulk | 661-1 | Belmont BS | Scrub Road | ECC Rating (A) | 795 | 795 | 795 | 795 | 795
Belmont Bulk | 661-1 | Belmont BS | Scrub Road | 50 POE Load (A) | 361 | 358 | 355 | 354 | 354
Belmont Bulk | 662-1 | Belmont BS | Upper Mt Gravatt | NCC Rating (A) | 695 | 695 | 695 | 695 | 695 | Urban | 70
Belmont Bulk | 662-1 | Belmont BS | Upper Mt Gravatt | 10 POE Load (A) | 129.6215 | 128.0998 | 128.2332 | 127.4374 | 127.8708
Belmont Bulk | 662-1 | Belmont BS | Upper Mt Gravatt | Power Factor | 0.98929 | 0.98955 | 0.98947 | 0.98958 | 0.98942
Belmont Bulk | 662-1 | Belmont BS | Upper Mt Gravatt | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Belmont Bulk | 662-1 | Belmont BS | Upper Mt Gravatt | 50 POE Load (A) | 219 | 218 | 324 | 323 | 323
Belmont Bulk | 663-1 | Belmont BS | Upper Mt Gravatt | NCC Rating (A) | 695 | 695 | 695 | 695 | 695 | Urban | 70
Belmont Bulk | 663-1 | Belmont BS | Upper Mt Gravatt | 10 POE Load (A) | 131.1353 | 129.5955 | 129.7303 | 128.925 | 129.3635
Belmont Bulk | 663-1 | Belmont BS | Upper Mt Gravatt | Power Factor | 0.9891 | 0.98937 | 0.98929 | 0.9894 | 0.98924
Belmont Bulk | 663-1 | Belmont BS | Upper Mt Gravatt | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Belmont Bulk | 663-1 | Belmont BS | Upper Mt Gravatt | 50 POE Load (A) | 220 | 219 | 324 | 323 | 323
Belmont Bulk | 692-1 | Belmont BS | Holland Pk East | NCC Rating (A) | 447 | 447 | 447 | 447 | 447 | Urban | 70
Belmont Bulk | 692-1 | Belmont BS | Holland Pk East | 10 POE Load (A) | 148.394 | 141.5684 | 141.8677 | 141.3831 | 142.7247
Belmont Bulk | 692-1 | Belmont BS | Holland Pk East | Power Factor | -0.97997 | -0.98026 | -0.98023 | -0.98027 | -0.98015
Belmont Bulk | 692-1 | Belmont BS | Holland Pk East | ECC Rating (A) | 494 | 494 | 494 | 494 | 494
Belmont Bulk | 692-1 | Belmont BS | Holland Pk East | 50 POE Load (A) | 271 | 270 | 268 | 267 | 267
Belmont Bulk | 693-1 | Belmont BS | Holland Pk East | NCC Rating (A) | 447 | 447 | 447 | 447 | 447 | Urban | 70
Belmont Bulk | 693-1 | Belmont BS | Holland Pk East | 10 POE Load (A) | 149.6147 | 142.7314 | 143.0331 | 142.5445 | 143.8973
Belmont Bulk | 693-1 | Belmont BS | Holland Pk East | Power Factor | -0.98024 | -0.98055 | -0.98052 | -0.98056 | -0.98044
Belmont Bulk | 693-1 | Belmont BS | Holland Pk East | ECC Rating (A) | 494 | 494 | 494 | 494 | 494
Belmont Bulk | 693-1 | Belmont BS | Holland Pk East | 50 POE Load (A) | 271 | 270 | 268 | 267 | 267
Brendale Bulk | 303-1 | Brendale BS | Albany Ck | NCC Rating (A) | 788 | 788 | 788 | 788 | 788 | Urban | 70
Brendale Bulk | 303-1 | Brendale BS | Albany Ck | 10 POE Load (A) | 164.867 | 161.8561 | 161.8144 | 160.9281 | 161.7518
Brendale Bulk | 303-1 | Brendale BS | Albany Ck | Power Factor | 0.9974 | 0.99755 | 0.99755 | 0.9976 | 0.99755
Brendale Bulk | 303-1 | Brendale BS | Albany Ck | ECC Rating (A) | 902 | 902 | 902 | 902 | 902
Brendale Bulk | 303-1 | Brendale BS | Albany Ck | 50 POE Load (A) | 328 | 326 | 323 | 320 | 317.5
Brendale Bulk | 309-1 | Brendale BS | 309 Tee1 | NCC Rating (A) | 810 | 810 | 810 | 810 | 810 | Rural | 170
Brendale Bulk | 309-1 | Brendale BS | 309 Tee1 | 10 POE Load (A) | 219.8263 | 216.1231 | 216.2401 | 214.8725 | 216.4122
Brendale Bulk | 309-1 | Brendale BS | 309 Tee1 | Power Factor | 0.99361 | 0.99374 | 0.99371 | 0.99376 | 0.99368
Brendale Bulk | 309-1 | Brendale BS | 309 Tee1 | ECC Rating (A) | 894 | 894 | 894 | 894 | 894
Brendale Bulk | 309-1 | Brendale BS | 309 Tee1 | 50 POE Load (A) | 555 | 551 | 547 | 543 | 541
Brendale Bulk | 309-2 | 309 Tee1 | Samford | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Brendale Bulk | 309-2 | 309 Tee1 | Samford | 10 POE Load (A) | 64.2736 | 61.792 | 60.9661 | 60.3067 | 60.3518
Brendale Bulk | 309-2 | 309 Tee1 | Samford | Power Factor | -0.99978 | -0.99985 | -0.99988 | -0.99989 | -0.99991
Brendale Bulk | 309-2 | 309 Tee1 | Samford | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Brendale Bulk | 309-2 | 309 Tee1 | Samford | 50 POE Load (A) | 221 | 219 | 217 | 215 | 210
Brendale Bulk | 309-3 | 309 Tee1 | Arana Hills | NCC Rating (A) | 838 | 838 | 838 | 838 | 838 | Rural | 170
Brendale Bulk | 309-3 | 309 Tee1 | Arana Hills | 10 POE Load (A) | 156.2771 | 155.0498 | 156.0075 | 155.293 | 156.8063
Brendale Bulk | 309-3 | 309 Tee1 | Arana Hills | Power Factor | 0.98914 | 0.98933 | 0.9893 | 0.98937 | 0.98927
Brendale Bulk | 309-3 | 309 Tee1 | Arana Hills | ECC Rating (A) | 912 | 912 | 912 | 912 | 912
Brendale Bulk | 309-3 | 309 Tee1 | Arana Hills | 50 POE Load (A) | 538 | 534 | 531 | 527 | 523
Brendale Bulk | 310-1 | Brendale BS | 310 Tee1 | NCC Rating (A) | 715 | 715 | 715 | 715 | 715 | Urban | 70
Brendale Bulk | 310-1 | Brendale BS | 310 Tee1 | 10 POE Load (A) | 323.7799 | 319.121 | 319.7872 | 317.9192 | 320.4228
Brendale Bulk | 310-1 | Brendale BS | 310 Tee1 | Power Factor | 0.99338 | 0.99351 | 0.99348 | 0.99353 | 0.99345
Brendale Bulk | 310-1 | Brendale BS | 310 Tee1 | ECC Rating (A) | 894 | 894 | 894 | 894 | 894
Brendale Bulk | 310-1 | Brendale BS | 310 Tee1 | 50 POE Load (A) | 576 | 573 | 569 | 565 | 560
Brendale Bulk | 310-2 | 310 Tee1 | Arana Hills | NCC Rating (A) | 838 | 838 | 838 | 838 | 838 | Urban | 70
Brendale Bulk | 310-2 | 310 Tee1 | Arana Hills | 10 POE Load (A) | 323.8149 | 319.1556 | 319.822 | 317.9537 | 320.4576
Brendale Bulk | 310-2 | 310 Tee1 | Arana Hills | Power Factor | 0.9943 | 0.9944 | 0.99437 | 0.99442 | 0.99435
Brendale Bulk | 310-2 | 310 Tee1 | Arana Hills | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Brendale Bulk | 310-2 | 310 Tee1 | Arana Hills | 50 POE Load (A) | 408 | 406 | 403 | 400 | 398
Brendale Bulk | 310-3 | 310 Tee1 | 569 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Brendale Bulk | 310-3 | 310 Tee1 | 569 Tee1 | 10 POE Load (A) | 0.11255 | 0.11258 | 0.11258 | 0.11259 | 0.11257
Brendale Bulk | 310-3 | 310 Tee1 | 569 Tee1 | Power Factor | 2.0842e-06 | 2.0842e-06 | 2.0842e-06 | 2.0842e-06 | 2.0842e-06
Brendale Bulk | 333-1 | Brendale BS | Lawnton | NCC Rating (A) | 826 | 826 | 826 | 826 | 826 | Urban | 70
Brendale Bulk | 333-1 | Brendale BS | Lawnton | 10 POE Load (A) | 243.4548 | 241.3796 | 256.0765 | 255.5982 | 257.619
Brendale Bulk | 333-1 | Brendale BS | Lawnton | Power Factor | 0.98412 | 0.98441 | 0.98423 | 0.98433 | 0.98432
Brendale Bulk | 333-1 | Brendale BS | Lawnton | ECC Rating (A) | 846 | 846 | 846 | 846 | 846
Brendale Bulk | 333-1 | Brendale BS | Lawnton | 50 POE Load (A) | 385 | 411 | 410 | 410 | 410
Brendale Bulk | 3340-1 | Brendale Bs | Strathpine | NCC Rating (A) | 561 | 561 | 561 | 561 | 561 | Urban | 70
Brendale Bulk | 3340-1 | Brendale Bs | Strathpine | 10 POE Load (A) | 95.6733 | 94.4435 | 94.066 | 92.3446 | 91.6071
Brendale Bulk | 3340-1 | Brendale Bs | Strathpine | Power Factor | 0.99367 | 0.99427 | 0.99445 | 0.99524 | 0.99557
Brendale Bulk | 3340-1 | Brendale Bs | Strathpine | ECC Rating (A) | 561 | 561 | 561 | 561 | 561
Brendale Bulk | 3340-1 | Brendale Bs | Strathpine | 50 POE Load (A) | 168 | 161 | 156 | 153 | 151
Brendale Bulk | 334-1 | Lawnton | 334 Tee1 | NCC Rating (A) | 645 | 645 | 645 | 645 | 645 | Rural | 170
Brendale Bulk | 334-1 | Lawnton | 334 Tee1 | 10 POE Load (A) | 22.2586 | 20.1794 | 21.7356 | 22.4741 | 23.6935
Brendale Bulk | 334-1 | Lawnton | 334 Tee1 | Power Factor | 0.70385 | 0.79359 | 0.93476 | 0.94535 | 0.95377
Brendale Bulk | 334-1 | Lawnton | 334 Tee1 | ECC Rating (A) | 865 | 865 | 865 | 865 | 865
Brendale Bulk | 334-1 | Lawnton | 334 Tee1 | 50 POE Load (A) | 272 | 270 | 268 | 267 | 268
Brendale Bulk | 334-2 | 334 Tee1 | Whiteside | NCC Rating (A) | 860 | 860 | 860 | 860 | 860 | Rural | 170
Brendale Bulk | 334-2 | 334 Tee1 | Whiteside | 10 POE Load (A) | 68.2413 | 65.771 | 64.5436 | 63.6304 | 63.1904
Brendale Bulk | 334-2 | 334 Tee1 | Whiteside | Power Factor | 0.9475 | 0.94838 | 0.94859 | 0.94891 | 0.94894
Brendale Bulk | 334-2 | 334 Tee1 | Whiteside | ECC Rating (A) | 949 | 949 | 949 | 949 | 949
Brendale Bulk | 334-2 | 334 Tee1 | Whiteside | 50 POE Load (A) | 155 | 154 | 153 | 152 | 150
Brendale Bulk | 334-3 | 334 Tee1 | Nth Pine Dam | NCC Rating (A) | 645 | 645 | 645 | 645 | 645 | Rural | 170
Brendale Bulk | 334-3 | 334 Tee1 | Nth Pine Dam | 10 POE Load (A) | 74.2426 | 74.1269 | 80.3057 | 80.3973 | 81.3234
Brendale Bulk | 334-3 | 334 Tee1 | Nth Pine Dam | Power Factor | 0.99765 | 0.99758 | 0.99668 | 0.99663 | 0.99649
Brendale Bulk | 334-3 | 334 Tee1 | Nth Pine Dam | ECC Rating (A) | 865 | 865 | 865 | 865 | 865
Brendale Bulk | 334-3 | 334 Tee1 | Nth Pine Dam | 50 POE Load (A) | 133 | 147 | 147 | 147 | 146
Brendale Bulk | 335-1 | Brendale BS | 335 Tee1 | NCC Rating (A) | 531 | 531 | 531 | 531 | 531 | Rural | 170
Brendale Bulk | 335-1 | Brendale BS | 335 Tee1 | 10 POE Load (A) | 158.8015 | 156.1954 | 162.1483 | 161.3072 | 161.9404
Brendale Bulk | 335-1 | Brendale BS | 335 Tee1 | Power Factor | -0.96772 | -0.96838 | -0.96761 | -0.96784 | -0.96815
Brendale Bulk | 335-1 | Brendale BS | 335 Tee1 | ECC Rating (A) | 531 | 531 | 531 | 531 | 531
Brendale Bulk | 335-1 | Brendale BS | 335 Tee1 | 50 POE Load (A) | 223 | 233 | 233 | 232 | 232
Brendale Bulk | 335-2 | 335 Tee | Whiteside | NCC Rating (A) | 860 | 860 | 860 | 860 | 860 | Rural | 170
Brendale Bulk | 335-2 | 335 Tee | Whiteside | 10 POE Load (A) | 77.554 | 75.1172 | 74.8261 | 73.9416 | 73.6406
Brendale Bulk | 335-2 | 335 Tee | Whiteside | Power Factor | 0.95649 | 0.95726 | 0.95751 | 0.9578 | 0.95799
Brendale Bulk | 335-2 | 335 Tee | Whiteside | ECC Rating (A) | 949 | 949 | 949 | 949 | 949
Brendale Bulk | 335-2 | 335 Tee | Whiteside | 50 POE Load (A) | 154 | 153 | 152 | 151 | 151
Brendale Bulk | 335-3 | 335 Tee | Nth Pine Dam | NCC Rating (A) | 531 | 531 | 531 | 531 | 531 | Rural | 170
Brendale Bulk | 335-3 | 335 Tee | Nth Pine Dam | 10 POE Load (A) | 81.9132 | 81.7197 | 87.9269 | 87.9618 | 88.8979
Brendale Bulk | 335-3 | 335 Tee | Nth Pine Dam | Power Factor | -0.9845 | -0.98444 | -0.98286 | -0.98283 | -0.98306
Brendale Bulk | 335-3 | 335 Tee | Nth Pine Dam | ECC Rating (A) | 531 | 531 | 531 | 531 | 531
Brendale Bulk | 335-3 | 335 Tee | Nth Pine Dam | 50 POE Load (A) | 150 | 160 | 160 | 160 | 160
Brendale Bulk | 336-1 | Brendale BS | Strathpine | NCC Rating (A) | 515 | 515 | 515 | 515 | 515 | Urban | 70
Brendale Bulk | 336-1 | Brendale BS | Strathpine | 10 POE Load (A) | 109.2598 | 107.8547 | 107.4235 | 105.457 | 104.6144
Brendale Bulk | 336-1 | Brendale BS | Strathpine | Power Factor | 0.99953 | 0.99968 | 0.99972 | 0.99987 | 0.99992
Brendale Bulk | 336-1 | Brendale BS | Strathpine | ECC Rating (A) | 515 | 515 | 515 | 515 | 515
Brendale Bulk | 336-1 | Brendale BS | Strathpine | 50 POE Load (A) | 185 | 177 | 171 | 168 | 166
Brendale Bulk | 3364-1 | Brendale BS | Albany Ck | NCC Rating (A) | 788 | 788 | 788 | 788 | 788 | Urban | 70
Brendale Bulk | 3364-1 | Brendale BS | Albany Ck | 10 POE Load (A) | 168.9827 | 165.8967 | 165.8539 | 164.9455 | 165.7898
Brendale Bulk | 3364-1 | Brendale BS | Albany Ck | Power Factor | 0.99717 | 0.99733 | 0.99733 | 0.99737 | 0.99733
Brendale Bulk | 3364-1 | Brendale BS | Albany Ck | ECC Rating (A) | 902 | 902 | 902 | 902 | 902
Brendale Bulk | 3364-1 | Brendale BS | Albany Ck | 50 POE Load (A) | 327 | 325 | 323 | 320 | 318
Brendale Bulk | 337-1 | Brendale BS | Strathpine | NCC Rating (A) | 537 | 537 | 537 | 537 | 537 | Urban | 70
Brendale Bulk | 337-1 | Brendale BS | Strathpine | 10 POE Load (A) | 89.6657 | 88.513 | 88.1592 | 86.5459 | 85.8547
Brendale Bulk | 337-1 | Brendale BS | Strathpine | Power Factor | 0.99613 | 0.99655 | 0.99668 | 0.99723 | 0.99746
Brendale Bulk | 337-1 | Brendale BS | Strathpine | ECC Rating (A) | 537 | 537 | 537 | 537 | 537
Brendale Bulk | 337-1 | Brendale BS | Strathpine | 50 POE Load (A) | 159 | 153 | 147 | 145 | 145
Brendale Bulk | 342-1 | Brendale BS | Bald Hills Bus 2 | NCC Rating (A) | 654 | 654 | 654 | 654 | 654 | Urban | 70
Brendale Bulk | 342-1 | Brendale BS | Bald Hills Bus 2 | 10 POE Load (A) | 51.64 | 51.0712 | 51.1173 | 50.8896 | 51.259
Brendale Bulk | 342-1 | Brendale BS | Bald Hills Bus 2 | Power Factor | 0.99947 | 0.9995 | 0.9995 | 0.99951 | 0.99949
Brendale Bulk | 342-1 | Brendale BS | Bald Hills Bus 2 | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Brendale Bulk | 342-1 | Brendale BS | Bald Hills Bus 2 | 50 POE Load (A) | 276 | 274 | 272 | 270 | 270
Brendale Bulk | 349-1 | Brendale BS | Lawnton | NCC Rating (A) | 805 | 805 | 805 | 805 | 805 | Urban | 70
Brendale Bulk | 349-1 | Brendale BS | Lawnton | 10 POE Load (A) | 261.4921 | 259.2632 | 275.0477 | 274.5339 | 276.7039
Brendale Bulk | 349-1 | Brendale BS | Lawnton | Power Factor | 0.98372 | 0.98402 | 0.98379 | 0.98389 | 0.98387
Brendale Bulk | 349-1 | Brendale BS | Lawnton | ECC Rating (A) | 822 | 822 | 822 | 822 | 822
Brendale Bulk | 349-1 | Brendale BS | Lawnton | 50 POE Load (A) | 386 | 412 | 411 | 411 | 411
Brendale Bulk | 464-1 | Brendale BS | Samford | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Brendale Bulk | 464-1 | Brendale BS | Samford | 10 POE Load (A) | 159.9878 | 156.6129 | 156.2773 | 155.1566 | 156.0771
Brendale Bulk | 464-1 | Brendale BS | Samford | Power Factor | 0.99589 | 0.99597 | 0.99596 | 0.99599 | 0.99595
Brendale Bulk | 464-1 | Brendale BS | Samford | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Brendale Bulk | 464-1 | Brendale BS | Samford | 50 POE Load (A) | 317 | 315 | 313 | 310 | 308
Browns Plains Bulk | 406A-1 | Bethania | Kingston | NCC Rating (A) | 647 | 647 | 647 | 647 | 647 | Urban | 70
Browns Plains Bulk | 406A-1 | Bethania | Kingston | 10 POE Load (A) | 1.0631 | 1.0631 | 1.0631 | 1.0631 | 1.0631
Browns Plains Bulk | 406A-1 | Bethania | Kingston | Power Factor | 5.1151e-05 | 5.1146e-05 | 5.1149e-05 | 5.1161e-05 | 5.1154e-05
Browns Plains Bulk | 406A-1 | Bethania | Kingston | ECC Rating (A) | 775 | 775 | 775 | 775 | 775
Browns Plains Bulk | 406A-1 | Bethania | Kingston | 50 POE Load (A) | 351 | 352 | 351 | 352 | 258.6186
Browns Plains Bulk | 406B-1 | Crestmead | Kingston | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Browns Plains Bulk | 406B-1 | Crestmead | Kingston | 10 POE Load (A) | 1.6949 | 1.6949 | 1.6949 | 1.6949 | 1.6949
Browns Plains Bulk | 406B-1 | Crestmead | Kingston | Power Factor | 5.9384e-06 | 5.9381e-06 | 5.9377e-06 | 5.9382e-06 | 5.9381e-06
Browns Plains Bulk | 406B-1 | Crestmead | Kingston | ECC Rating (A) | 830 | 830 | 830 | 830 | 830
Browns Plains Bulk | 406B-1 | Crestmead | Kingston | 50 POE Load (A) | 255 | 255 | 255 | 255 | 259.2505
Browns Plains Bulk | 478-1 | Browns Plains BS | Nth Maclean | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Browns Plains Bulk | 478-1 | Browns Plains BS | Nth Maclean | 10 POE Load (A) | 2.172 | 2.172 | 2.172 | 2.172 | 2.172
Browns Plains Bulk | 478-1 | Browns Plains BS | Nth Maclean | Power Factor | 5.063e-05 | 5.063e-05 | 5.063e-05 | 5.063e-05 | 5.063e-05
Browns Plains Bulk | 478-1 | Browns Plains BS | Nth Maclean | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Browns Plains Bulk | 478-1 | Browns Plains BS | Nth Maclean | 50 POE Load (A) | 398.7854 | 395.3666 | 407.2912 | 417.1211 | 432.7035
Browns Plains Bulk | 481-1 | Browns Plains BS | Cresmead | NCC Rating (A) | 741 | 741 | 741 | 741 | 741 | Urban | 70
Browns Plains Bulk | 481-1 | Browns Plains BS | Cresmead | 10 POE Load (A) | 196.3384 | 193.5148 | 193.8631 | 193.6539 | 195.8005
Browns Plains Bulk | 481-1 | Browns Plains BS | Cresmead | Power Factor | 0.9898 | 0.99012 | 0.99008 | 0.99011 | 0.98986
Browns Plains Bulk | 481-1 | Browns Plains BS | Cresmead | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Browns Plains Bulk | 481-1 | Browns Plains BS | Cresmead | 50 POE Load (A) | 453 | 450 | 447 | 445 | 443
Browns Plains Bulk | 482-1 | Browns Plains BS | Cresmead | NCC Rating (A) | 741 | 741 | 741 | 741 | 741 | Urban | 70
Browns Plains Bulk | 482-1 | Browns Plains BS | Cresmead | 10 POE Load (A) | 197.4318 | 194.5924 | 194.9427 | 194.7323 | 196.8909
Browns Plains Bulk | 482-1 | Browns Plains BS | Cresmead | Power Factor | 0.98963 | 0.98995 | 0.98991 | 0.98993 | 0.98969
Browns Plains Bulk | 482-1 | Browns Plains BS | Cresmead | ECC Rating (A) | 775 | 775 | 775 | 775 | 775
Browns Plains Bulk | 482-1 | Browns Plains BS | Cresmead | 50 POE Load (A) | 475 | 471 | 468 | 466 | 466
Browns Plains Bulk | 542-1 | Browns Plains BS | Heathwood | NCC Rating (A) | 745 | 745 | 745 | 745 | 745 | Urban | 70
Browns Plains Bulk | 542-1 | Browns Plains BS | Heathwood | 10 POE Load (A) | 400.5641 | 391.8391 | 394.9402 | 393.59 | 396.8372
Browns Plains Bulk | 542-1 | Browns Plains BS | Heathwood | Power Factor | 0.99416 | 0.99413 | 0.99406 | 0.99409 | 0.99402
Browns Plains Bulk | 542-1 | Browns Plains BS | Heathwood | ECC Rating (A) | 745 | 745 | 745 | 745 | 745
Browns Plains Bulk | 542-1 | Browns Plains BS | Heathwood | 50 POE Load (A) | 388.0477 | 379.6142 | 382.6117 | 381.3067 | 384.4454
Burleigh Heads Bulk | 3751-1 | Burleigh Hds BS | Currumbin | NCC Rating (A) | 606 | 606 | 606 | 606 | 606 | Urban | 321
Burleigh Heads Bulk | 3751-1 | Burleigh Hds BS | Currumbin | 10 POE Load (A) | 543.5394 | 543.9244 | 548.8847 | 549.8374 | 555.374
Burleigh Heads Bulk | 3751-1 | Burleigh Hds BS | Currumbin | Power Factor | 0.9682 | 0.96822 | 0.96623 | 0.96619 | 0.96584
Burleigh Heads Bulk | 3751-1 | Burleigh Hds BS | Currumbin | ECC Rating (A) | 695 | 695 | 695 | 695 | 695
Burleigh Heads Bulk | 3751-1 | Burleigh Hds BS | Currumbin | 50 POE Load (A) | 858 | 857 | 857 | 857 | 857
Burleigh Heads Bulk | 3755-1 | Burleigh Hds BS | Currumbin | NCC Rating (A) | 606 | 606 | 606 | 606 | 606 | Urban | 321
Burleigh Heads Bulk | 3755-1 | Burleigh Hds BS | Currumbin | 10 POE Load (A) | 543.2492 | 543.634 | 548.5916 | 549.5438 | 555.0775
Burleigh Heads Bulk | 3755-1 | Burleigh Hds BS | Currumbin | Power Factor | 0.9682 | 0.96823 | 0.96623 | 0.9662 | 0.96584
Burleigh Heads Bulk | 3755-1 | Burleigh Hds BS | Currumbin | ECC Rating (A) | 695 | 695 | 695 | 695 | 695
Burleigh Heads Bulk | 3755-1 | Burleigh Hds BS | Currumbin | 50 POE Load (A) | 858 | 857 | 856 | 857 | 857
Burleigh Heads Bulk | 3756-1 | Burleigh Hds BS | 3756 Tee1 | NCC Rating (A) | 715 | 715 | 715 | 715 | 715 | Urban | 70
Burleigh Heads Bulk | 3756-1 | Burleigh Hds BS | 3756 Tee1 | 10 POE Load (A) | 171.6478 | 171.609 | 173.2405 | 173.5139 | 175.4396
Burleigh Heads Bulk | 3756-1 | Burleigh Hds BS | 3756 Tee1 | Power Factor | 0.98209 | 0.98215 | 0.97971 | 0.97968 | 0.97931
Burleigh Heads Bulk | 3756-1 | Burleigh Hds BS | 3756 Tee1 | ECC Rating (A) | 715 | 715 | 715 | 715 | 715
Burleigh Heads Bulk | 3756-1 | Burleigh Hds BS | 3756 Tee1 | 50 POE Load (A) | 251 | 251 | 251 | 251 | 251
Burleigh Heads Bulk | 3756-2 | 3756 Tee1 | Palm Beach | NCC Rating (A) | 614 | 614 | 614 | 614 | 614 | Urban | 70
Burleigh Heads Bulk | 3756-2 | 3756 Tee1 | Palm Beach | 10 POE Load (A) | 164.4744 | 162.9542 | 165.4519 | 165.4582 | 168.9786
Burleigh Heads Bulk | 3756-2 | 3756 Tee1 | Palm Beach | Power Factor | 0.99504 | 0.99542 | 0.98897 | 0.9889 | 0.98721
Burleigh Heads Bulk | 3756-2 | 3756 Tee1 | Palm Beach | ECC Rating (A) | 614 | 614 | 614 | 614 | 614
Burleigh Heads Bulk | 3756-2 | 3756 Tee1 | Palm Beach | 50 POE Load (A) | 366 | 366 | 365 | 365 | 365
Burleigh Heads Bulk | 3756-3 | 3756 Tee1 | 3756 Tee2 | NCC Rating (A) | 636 | 636 | 636 | 636 | 636 | Urban | 70
Burleigh Heads Bulk | 3756-3 | 3756 Tee1 | 3756 Tee2 | 10 POE Load (A) | 43.0517 | 44.384 | 42.9049 | 43.179 | 41.9934
Burleigh Heads Bulk | 3756-3 | 3756 Tee1 | 3756 Tee2 | Power Factor | -0.5063 | -0.56907 | -0.93796 | -0.93856 | -0.94429
Burleigh Heads Bulk | 3756-3 | 3756 Tee1 | 3756 Tee2 | ECC Rating (A) | 636 | 636 | 636 | 636 | 636
Burleigh Heads Bulk | 3756-3 | 3756 Tee1 | 3756 Tee2 | 50 POE Load (A) | 226 | 226 | 226 | 227 | 228
Burleigh Heads Bulk | 3756-4 | 3756 Tee2 | Currumbin | NCC Rating (A) | 790 | 790 | 790 | 790 | 790 | Urban | 70
Burleigh Heads Bulk | 3756-4 | 3756 Tee2 | Currumbin | 10 POE Load (A) | 43.2022 | 44.5339 | 43.0225 | 43.296 | 42.1051
Burleigh Heads Bulk | 3756-4 | 3756 Tee2 | Currumbin | Power Factor | -0.4935 | -0.55669 | -0.92697 | -0.93107 | -0.94179
Burleigh Heads Bulk | 3756-4 | 3756 Tee2 | Currumbin | ECC Rating (A) | 790 | 790 | 790 | 790 | 790
Burleigh Heads Bulk | 3756-4 | 3756 Tee2 | Currumbin | 50 POE Load (A) | 249 | 249 | 249 | 250 | 252
Burleigh Heads Bulk | 393-1 | Currumbin | Kirra | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Urban | 70
Burleigh Heads Bulk | 393-1 | Currumbin | Kirra | 10 POE Load (A) | 221.0086 | 222.681 | 226.5122 | 227.345 | 230.8049
Burleigh Heads Bulk | 393-1 | Currumbin | Kirra | Power Factor | 0.98205 | 0.98197 | 0.98204 | 0.982 | 0.98184
Burleigh Heads Bulk | 393-1 | Currumbin | Kirra | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
Burleigh Heads Bulk | 393-1 | Currumbin | Kirra | 50 POE Load (A) | 334 | 334 | 336 | 338 | 340
Burleigh Heads Bulk | 395-1 | Burleigh Hds BS | Miami | NCC Rating (A) | 747 | 747 | 747 | 747 | 747 | Urban | 70
Burleigh Heads Bulk | 395-1 | Burleigh Hds BS | Miami | 10 POE Load (A) | 420.4089 | 420.8336 | 426.6308 | 429.7551 | 438.612
Burleigh Heads Bulk | 395-1 | Burleigh Hds BS | Miami | Power Factor | 0.99368 | 0.99367 | 0.99359 | 0.99354 | 0.99358
Burleigh Heads Bulk | 396-1 | Burleigh Hds BS | Palm Beach | NCC Rating (A) | 806 | 806 | 806 | 806 | 806 | Urban | 70
Burleigh Heads Bulk | 396-1 | Burleigh Hds BS | Palm Beach | 10 POE Load (A) | 198.0375 | 197.9539 | 199.8332 | 200.1415 | 202.4031
Burleigh Heads Bulk | 396-1 | Burleigh Hds BS | Palm Beach | Power Factor | 0.98094 | 0.98103 | 0.97831 | 0.97828 | 0.97786
Burleigh Heads Bulk | 396-1 | Burleigh Hds BS | Palm Beach | ECC Rating (A) | 806 | 806 | 806 | 806 | 806
Burleigh Heads Bulk | 396-1 | Burleigh Hds BS | Palm Beach | 50 POE Load (A) | 319 | 318 | 318 | 318 | 318
Burleigh Heads Bulk | 397-1 | Burleigh Hds BS | 397 Tee1 | NCC Rating (A) | 659 | 659 | 659 | 659 | 659 | Urban | 70
Burleigh Heads Bulk | 397-1 | Burleigh Hds BS | 397 Tee1 | 10 POE Load (A) | 2.5543 | 2.5543 | 2.5543 | 2.5543 | 2.5543
Burleigh Heads Bulk | 397-1 | Burleigh Hds BS | 397 Tee1 | Power Factor | 1.828e-05 | 1.828e-05 | 1.828e-05 | 1.828e-05 | 1.828e-05
Burleigh Heads Bulk | 397-3 | 397 Tee1 | 397 Tee2 | NCC Rating (A) | 706 | 706 | 706 | 706 | 706 | Urban | 70
Burleigh Heads Bulk | 397-3 | 397 Tee1 | 397 Tee2 | 10 POE Load (A) | 1.5716 | 1.5716 | 1.5716 | 1.5716 | 1.5716
Burleigh Heads Bulk | 397-3 | 397 Tee1 | 397 Tee2 | Power Factor | 3.1331e-05 | 3.1331e-05 | 3.1331e-05 | 3.1331e-05 | 3.1331e-05
Burleigh Heads Bulk | 397-4 | 397 Tee2 | 3700 Tee1 | NCC Rating (A) | 362 | 362 | 362 | 362 | 362 | Urban | 70
Burleigh Heads Bulk | 397-4 | 397 Tee2 | 3700 Tee1 | 10 POE Load (A) | 0.47718 | 0.47718 | 0.47718 | 0.47718 | 0.47718
Burleigh Heads Bulk | 397-4 | 397 Tee2 | 3700 Tee1 | Power Factor | 2.8112e-05 | 2.8113e-05 | 2.8112e-05 | 2.8112e-05 | 2.8113e-05
Burleigh Heads Bulk | 397-5 | 397 Tee2 | Mudgeeraba BS | NCC Rating (A) | 863 | 863 | 863 | 863 | 863 | Urban | 70
Burleigh Heads Bulk | 397-5 | 397 Tee2 | Mudgeeraba BS | 10 POE Load (A) | 0.31956 | 0.31956 | 0.31956 | 0.31956 | 0.31956
Burleigh Heads Bulk | 397-5 | 397 Tee2 | Mudgeeraba BS | Power Factor | 4.0388e-06 | 4.0388e-06 | 4.0388e-06 | 4.0388e-06 | 4.0388e-06
Caboolture Bulk | 321-1 | Caboolture BS | Caboolture West | NCC Rating (A) | 688 | 688 | 688 | 688 | 688 | Rural | 170
Caboolture Bulk | 321-1 | Caboolture BS | Caboolture West | 10 POE Load (A) | 199.786 | 198.196 | 200.6852 | 201.9397 | 205.5659
Caboolture Bulk | 321-1 | Caboolture BS | Caboolture West | Power Factor | 0.99295 | 0.99304 | 0.99292 | 0.99285 | 0.99268
Caboolture Bulk | 321-1 | Caboolture BS | Caboolture West | ECC Rating (A) | 688 | 688 | 688 | 688 | 688
Caboolture Bulk | 321-1 | Caboolture BS | Caboolture West | 50 POE Load (A) | 382 | 383 | 383 | 384 | 384
Caboolture Bulk | 322-1 | Caboolture BS | Caboolture West | NCC Rating (A) | 688 | 688 | 688 | 688 | 688 | Rural | 170
Caboolture Bulk | 322-1 | Caboolture BS | Caboolture West | 10 POE Load (A) | 210.0651 | 208.3935 | 211.0106 | 212.3295 | 216.1419
Caboolture Bulk | 322-1 | Caboolture BS | Caboolture West | Power Factor | 0.98821 | 0.98832 | 0.98817 | 0.98809 | 0.98786
Caboolture Bulk | 322-1 | Caboolture BS | Caboolture West | ECC Rating (A) | 688 | 688 | 688 | 688 | 688
Caboolture Bulk | 322-1 | Caboolture BS | Caboolture West | 50 POE Load (A) | 388 | 390 | 390 | 390 | 390
Caboolture Bulk | 323-1 | Caboolture West | 323 Tee1 | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170
Caboolture Bulk | 323-1 | Caboolture West | 323 Tee1 | 10 POE Load (A) | 64.7812 | 63.5721 | 63.6459 | 63.445 | 64.1051
Caboolture Bulk | 323-1 | Caboolture West | 323 Tee1 | Power Factor | 0.99547 | 0.99558 | 0.99557 | 0.99559 | 0.99553
Caboolture Bulk | 323-1 | Caboolture West | 323 Tee1 | ECC Rating (A) | 584 | 584 | 584 | 584 | 584
Caboolture Bulk | 323-1 | Caboolture West | 323 Tee1 | 50 POE Load (A) | 228 | 227 | 225 | 224 | 223
Caboolture Bulk | 323-2 | 323 Tee1 | Wamuran | NCC Rating (A) | 489 | 489 | 489 | 489 | 489 | Rural | 170
Caboolture Bulk | 323-2 | 323 Tee1 | Wamuran | 10 POE Load (A) | 64.9271 | 63.7167 | 63.7906 | 63.5895 | 64.2502
Caboolture Bulk | 323-2 | 323 Tee1 | Wamuran | Power Factor | 0.99349 | 0.99358 | 0.99357 | 0.99359 | 0.99354
Caboolture Bulk | 323-2 | 323 Tee1 | Wamuran | ECC Rating (A) | 489 | 489 | 489 | 489 | 489
Caboolture Bulk | 323-2 | 323 Tee1 | Wamuran | 50 POE Load (A) | 63.4949 | 62.343 | 62.4124 | 62.2207 | 62.8487
Caboolture Bulk | 323-3 | 323 Tee1 | Woodford | NCC Rating (A) | 382 | 382 | 382 | 382 | 382 | Rural | 170
Caboolture Bulk | 323-3 | 323 Tee1 | Woodford | 10 POE Load (A) | 1.1572 | 1.1574 | 1.1573 | 1.1573 | 1.157
Caboolture Bulk | 323-3 | 323 Tee1 | Woodford | Power Factor | 0.00012196 | 0.00012191 | 0.00012186 | 0.0001219 | 0.00012199
Caboolture Bulk | 323-3 | 323 Tee1 | Woodford | ECC Rating (A) | 382 | 382 | 382 | 382 | 382
Caboolture Bulk | 323-3 | 323 Tee1 | Woodford | 50 POE Load (A) | 196 | 196 | 194 | 194 | 194
Caboolture Bulk | 350-1 | Caboolture BS | Ningi | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Caboolture Bulk | 350-1 | Caboolture BS | Ningi | 10 POE Load (A) | 339.4829 | 336.8923 | 339.2402 | 339.139 | 343.8967
Caboolture Bulk | 350-1 | Caboolture BS | Ningi | Power Factor | 0.99456 | 0.99464 | 0.99458 | 0.99458 | 0.99445
Caboolture Bulk | 350-1 | Caboolture BS | Ningi | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Caboolture Bulk | 350-1 | Caboolture BS | Ningi | 50 POE Load (A) | 584 | 582 | 582 | 580 | 580
Caboolture Bulk | 412-1 | Caboolture BS | Toorbul Pt | NCC Rating (A) | 823 | 823 | 823 | 823 | 823 | Rural | 170
Caboolture Bulk | 412-1 | Caboolture BS | Toorbul Pt | 10 POE Load (A) | 284.9777 | 282.6882 | 284.6084 | 284.5066 | 288.5457
Caboolture Bulk | 412-1 | Caboolture BS | Toorbul Pt | Power Factor | 0.98545 | 0.98563 | 0.98549 | 0.9855 | 0.98521
Caboolture Bulk | 412-1 | Caboolture BS | Toorbul Pt | ECC Rating (A) | 1018 | 1018 | 1018 | 1018 | 1018
Caboolture Bulk | 412-1 | Caboolture BS | Toorbul Pt | 50 POE Load (A) | 730 | 727 | 726 | 724 | 722
Caboolture Bulk | 417-1 | Ningi | Toorbul Pt | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Caboolture Bulk | 417-1 | Ningi | Toorbul Pt | 10 POE Load (A) | 197.444 | 195.6544 | 196.895 | 196.7944 | 199.6734
Caboolture Bulk | 417-1 | Ningi | Toorbul Pt | Power Factor | 0.99725 | 0.99731 | 0.99727 | 0.99728 | 0.99719
Caboolture Bulk | 417-1 | Ningi | Toorbul Pt | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Caboolture Bulk | 417-1 | Ningi | Toorbul Pt | 50 POE Load (A) | 460 | 459 | 459 | 457 | 455
Caboolture Bulk | 431-1 | Toorbul Point | Bribie Is | NCC Rating (A) | 419 | 419 | 419 | 419 | 419 | Urban | 70
Caboolture Bulk | 431-1 | Toorbul Point | Bribie Is | 10 POE Load (A) | 185.9893 | 184.2705 | 185.3598 | 185.1253 | 187.6904
Caboolture Bulk | 431-1 | Toorbul Point | Bribie Is | Power Factor | 0.99527 | 0.99536 | 0.99531 | 0.99532 | 0.99519
Caboolture Bulk | 431-1 | Toorbul Point | Bribie Is | ECC Rating (A) | 470 | 470 | 470 | 470 | 470
Caboolture Bulk | 431-1 | Toorbul Point | Bribie Is | 50 POE Load (A) | 325 | 324 | 324 | 323 | 323
Caboolture Bulk | 448-1 | Morayfield Nth | 448 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Caboolture Bulk | 448-1 | Morayfield Nth | 448 Tee1 | 10 POE Load (A) | 406.0285 | 411.5617 | 419.2799 | 424.5751 | 434.9498
Caboolture Bulk | 448-1 | Morayfield Nth | 448 Tee1 | Power Factor | -0.98421 | -0.98391 | -0.9835 | -0.98322 | -0.98266
Caboolture Bulk | 448-1 | Morayfield Nth | 448 Tee1 | ECC Rating (A) | 822 | 822 | 822 | 822 | 822
Caboolture Bulk | 448-1 | Morayfield Nth | 448 Tee1 | 50 POE Load (A) | 470 | 479 | 482 | 485 | 410.903
Caboolture Bulk | 448-2 | 448 Tee1 | Morayfield | NCC Rating (A) | 737 | 737 | 737 | 737 | 737 | Rural | 170
Caboolture Bulk | 448-2 | 448 Tee1 | Morayfield | 10 POE Load (A) | 388.0092 | 396.4377 | 404.6055 | 410.5257 | 421.2072
Caboolture Bulk | 448-2 | 448 Tee1 | Morayfield | Power Factor | 0.99482 | 0.99465 | 0.9945 | 0.99438 | 0.99417
Caboolture Bulk | 448-2 | 448 Tee1 | Morayfield | ECC Rating (A) | 737 | 737 | 737 | 737 | 737
Caboolture Bulk | 448-2 | 448 Tee1 | Morayfield | 50 POE Load (A) | 360 | 371 | 374 | 378 | 400.8752
Caboolture Bulk | 448-3 | 448 Tee1 | Caboolture West | NCC Rating (A) | 504 | 504 | 504 | 504 | 504 | Rural | 170
Caboolture Bulk | 448-3 | 448 Tee1 | Caboolture West | 10 POE Load (A) | 22.3589 | 20.0377 | 19.8047 | 19.3904 | 19.3294
Caboolture Bulk | 448-3 | 448 Tee1 | Caboolture West | Power Factor | 0.93001 | 0.92282 | 0.92139 | 0.91936 | 0.91886
Caboolture Bulk | 448-3 | 448 Tee1 | Caboolture West | ECC Rating (A) | 504 | 504 | 504 | 504 | 504
Caboolture Bulk | 448-3 | 448 Tee1 | Caboolture West | 50 POE Load (A) | 109 | 107 | 106 | 106 | 106
Caboolture Bulk | 457-1 | Toorbul Pt | Bribie Island | NCC Rating (A) | 425 | 425 | 425 | 425 | 425 | Urban | 70
Caboolture Bulk | 457-1 | Toorbul Pt | Bribie Island | 10 POE Load (A) | 184.7951 | 183.0866 | 184.1694 | 183.9363 | 186.4861
Caboolture Bulk | 457-1 | Toorbul Pt | Bribie Island | Power Factor | 0.99647 | 0.99654 | 0.99649 | 0.9965 | 0.99639
Caboolture Bulk | 457-1 | Toorbul Pt | Bribie Island | ECC Rating (A) | 618 | 618 | 618 | 618 | 618
Caboolture Bulk | 457-1 | Toorbul Pt | Bribie Island | 50 POE Load (A) | 325 | 324 | 323 | 323 | 321
Caboolture Bulk | 461-1 | Caboolture BS | Morayfield Nth | NCC Rating (A) | 762 | 762 | 762 | 762 | 762 | Urban | 238
Caboolture Bulk | 461-1 | Caboolture BS | Morayfield Nth | 10 POE Load (A) | 382.9471 | 383.8456 | 389.4266 | 392.7692 | 400.3285
Caboolture Bulk | 461-1 | Caboolture BS | Morayfield Nth | Power Factor | -0.98564 | -0.98554 | -0.98526 | -0.98508 | -0.98469
Caboolture Bulk | 461-1 | Caboolture BS | Morayfield Nth | ECC Rating (A) | 797 | 797 | 797 | 797 | 797
Caboolture Bulk | 461-1 | Caboolture BS | Morayfield Nth | 50 POE Load (A) | 695 | 703 | 705 | 709 | 709
Caboolture Bulk | 499-1 | Caboolture BS | Morayfield Nth | NCC Rating (A) | 762 | 762 | 762 | 762 | 762 | Urban | 239
Caboolture Bulk | 499-1 | Caboolture BS | Morayfield Nth | 10 POE Load (A) | 385.6985 | 386.6034 | 392.2246 | 395.5913 | 403.2049
Caboolture Bulk | 499-1 | Caboolture BS | Morayfield Nth | Power Factor | -0.98567 | -0.98557 | -0.98529 | -0.98511 | -0.98472
Caboolture Bulk | 499-1 | Caboolture BS | Morayfield Nth | ECC Rating (A) | 797 | 797 | 797 | 797 | 797
Caboolture Bulk | 499-1 | Caboolture BS | Morayfield Nth | 50 POE Load (A) | 696 | 704 | 706 | 710 | 710
Cleveland Bulk | 3550-1 | Cleveland BS | Victoria Pt | NCC Rating (A) | 775 | 775 | 775 | 775 | 775 | Urban | 70
Cleveland Bulk | 3550-1 | Cleveland BS | Victoria Pt | 10 POE Load (A) | 402.0136 | 397.0282 | 399.3789 | 399.5863 | 404.0601
Cleveland Bulk | 3550-1 | Cleveland BS | Victoria Pt | Power Factor | 0.99148 | 0.99371 | 0.99366 | 0.99367 | 0.99353
Cleveland Bulk | 3550-1 | Cleveland BS | Victoria Pt | ECC Rating (A) | 775 | 775 | 775 | 775 | 775
Cleveland Bulk | 3550-1 | Cleveland BS | Victoria Pt | 50 POE Load (A) | 522 | 521 | 521 | 521 | 521
Cleveland Bulk | 3570-1 | Capalaba South | Capalaba | NCC Rating (A) | 649 | 649 | 649 | 649 | 649 | Urban | 70
Cleveland Bulk | 3570-1 | Capalaba South | Capalaba | 10 POE Load (A) | 63.4749 | 64.5337 | 65.3329 | 64.6525 | 64.3141
Cleveland Bulk | 3570-1 | Capalaba South | Capalaba | Power Factor | 0.96993 | 0.97084 | 0.9711 | 0.97127 | 0.97112
Cleveland Bulk | 3570-1 | Capalaba South | Capalaba | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Cleveland Bulk | 3570-1 | Capalaba South | Capalaba | 50 POE Load (A) | 319 | 315 | 313 | 310 | 310
Cleveland Bulk | 3580-1 | Redland Bay | 3580 Tee1 | NCC Rating (A) | 848 | 848 | 848 | 848 | 848 | Urban | 70
Cleveland Bulk | 3580-1 | Redland Bay | 3580 Tee1 | 10 POE Load (A) | 31.5414 | 33.7154 | 35.6139 | 36.902 | 38.3218
Cleveland Bulk | 3580-1 | Redland Bay | 3580 Tee1 | Power Factor | 0.99998 | 0.99325 | 0.99487 | 0.9958 | 0.99652
Cleveland Bulk | 3580-1 | Redland Bay | 3580 Tee1 | ECC Rating (A) | 926 | 926 | 926 | 926 | 926
Cleveland Bulk | 3580-1 | Redland Bay | 3580 Tee1 | 50 POE Load (A) | 313 | 314 | 315 | 317 | 317
Cleveland Bulk | 3580-2 | 3580 Tee1 | Mt Cotton | NCC Rating (A) | 715 | 715 | 715 | 715 | 715 | Urban | 70
Cleveland Bulk | 3580-2 | 3580 Tee1 | Mt Cotton | 10 POE Load (A) | 31.563 | 33.8229 | 35.7085 | 36.9883 | 38.4008
Cleveland Bulk | 3580-2 | 3580 Tee1 | Mt Cotton | Power Factor | 0.99938 | 0.9898 | 0.99205 | 0.99334 | 0.99438
Cleveland Bulk | 3580-2 | 3580 Tee1 | Mt Cotton | ECC Rating (A) | 715 | 715 | 715 | 715 | 715
Cleveland Bulk | 3580-2 | 3580 Tee1 | Mt Cotton | 50 POE Load (A) | 328 | 330 | 331 | 333 | 333
Cleveland Bulk | 3580-3 | 3580 Tee1 | Cornubia | NCC Rating (A) | 926 | 926 | 926 | 926 | 926 | Urban | 70
Cleveland Bulk | 3580-3 | 3580 Tee1 | Cornubia | 10 POE Load (A) | 0.64967 | 0.65017 | 0.65021 | 0.65025 | 0.65019
Cleveland Bulk | 3580-3 | 3580 Tee1 | Cornubia | Power Factor | 1.4334e-05 | 1.4334e-05 | 1.4334e-05 | 1.4334e-05 | 1.4334e-05
Cleveland Bulk | 371-1 | Cleveland BS | Birkdale | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Cleveland Bulk | 371-1 | Cleveland BS | Birkdale | 10 POE Load (A) | 349.2105 | 343.7414 | 343.3328 | 341.2256 | 342.9097
Cleveland Bulk | 371-1 | Cleveland BS | Birkdale | Power Factor | 0.99179 | 0.99194 | 0.99196 | 0.99202 | 0.99198
Cleveland Bulk | 371-1 | Cleveland BS | Birkdale | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Cleveland Bulk | 371-1 | Cleveland BS | Birkdale | 50 POE Load (A) | 413 | 410 | 407 | 404 | 402
Cleveland Bulk | 372-1 | Cleveland BS | Raby Bay | NCC Rating (A) | 648 | 648 | 648 | 648 | 648 | Urban | 308
Cleveland Bulk | 372-1 | Cleveland BS | Raby Bay | 10 POE Load (A) | 318.8746 | 316.6944 | 318.825 | 319.0811 | 322.9059
Cleveland Bulk | 372-1 | Cleveland BS | Raby Bay | Power Factor | 0.9948 | 0.99489 | 0.99485 | 0.99486 | 0.99475
Cleveland Bulk | 372-1 | Cleveland BS | Raby Bay | ECC Rating (A) | 726 | 726 | 726 | 726 | 726
Cleveland Bulk | 372-1 | Cleveland BS | Raby Bay | 50 POE Load (A) | 576 | 575 | 575 | 575 | 575
Cleveland Bulk | 373-1 | Raby Bay | Capalaba | NCC Rating (A) | 715 | 715 | 715 | 715 | 715 | Urban | 70
Cleveland Bulk | 373-1 | Raby Bay | Capalaba | 10 POE Load (A) | 251.7986 | 247.16 | 246.5244 | 244.7431 | 245.6873
Cleveland Bulk | 373-1 | Raby Bay | Capalaba | Power Factor | -0.98835 | -0.98864 | -0.98866 | -0.98878 | -0.9887
Cleveland Bulk | 373-1 | Raby Bay | Capalaba | ECC Rating (A) | 715 | 715 | 715 | 715 | 715
Cleveland Bulk | 373-1 | Raby Bay | Capalaba | 50 POE Load (A) | 393 | 389 | 386 | 383 | 383
Cleveland Bulk | 374-1 | Cleveland BS | Capalaba South | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Cleveland Bulk | 374-1 | Cleveland BS | Capalaba South | 10 POE Load (A) | 295.8319 | 290.5479 | 290.056 | 288.3422 | 289.897
Cleveland Bulk | 374-1 | Cleveland BS | Capalaba South | Power Factor | 0.98896 | 0.98914 | 0.98915 | 0.98922 | 0.98919
Cleveland Bulk | 374-1 | Cleveland BS | Capalaba South | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Cleveland Bulk | 374-1 | Cleveland BS | Capalaba South | 50 POE Load (A) | 422 | 418 | 415 | 413 | 413
Cleveland Bulk | 375-1 | Cleveland BS | 375 Tee1 | NCC Rating (A) | 649 | 649 | 649 | 649 | 649 | Rural | 170
Cleveland Bulk | 375-1 | Cleveland BS | 375 Tee1 | 10 POE Load (A) | 160.1158 | 156.1392 | 155.9006 | 155.3277 | 156.6392
Cleveland Bulk | 375-1 | Cleveland BS | 375 Tee1 | Power Factor | 0.99227 | 0.99536 | 0.99539 | 0.99544 | 0.99538
Cleveland Bulk | 375-1 | Cleveland BS | 375 Tee1 | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Cleveland Bulk | 375-1 | Cleveland BS | 375 Tee1 | 50 POE Load (A) | 539 | 539 | 540 | 541 | 541
Cleveland Bulk | 375-2 | 375 Tee1 | Mt Cotton | NCC Rating (A) | 678 | 678 | 678 | 678 | 678 | Rural | 170
Cleveland Bulk | 375-2 | 375 Tee1 | Mt Cotton | 10 POE Load (A) | 160.1732 | 156.1826 | 155.9438 | 155.3707 | 156.6824
Cleveland Bulk | 375-2 | 375 Tee1 | Mt Cotton | Power Factor | 0.9945 | 0.99701 | 0.99704 | 0.99707 | 0.99704
Cleveland Bulk | 375-2 | 375 Tee1 | Mt Cotton | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Cleveland Bulk | 375-2 | 375 Tee1 | Mt Cotton | 50 POE Load (A) | 539 | 539 | 540 | 541 | 541
Cleveland Bulk | 375-3 | 375 Tee1 | 425 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Cleveland Bulk | 375-3 | 375 Tee1 | 425 Tee1 | 10 POE Load (A) | 0.00064839 | 0.00064853 | 0.00064854 | 0.00064855 | 0.00064853
Cleveland Bulk | 375-3 | 375 Tee1 | 425 Tee1 | Power Factor | 0.00030482 | 0.00030458 | 0.00030488 | 0.00030467 | 0.00030497
Cleveland Bulk | 413-1 | Cleveland BS | Raby Bay | NCC Rating (A) | 648 | 648 | 648 | 648 | 648 | Urban | 320
Cleveland Bulk | 413-1 | Cleveland BS | Raby Bay | 10 POE Load (A) | 322.7431 | 320.5364 | 322.6929 | 322.9521 | 326.8234
Cleveland Bulk | 413-1 | Cleveland BS | Raby Bay | Power Factor | 0.99477 | 0.99487 | 0.99482 | 0.99483 | 0.99473
Cleveland Bulk | 413-1 | Cleveland BS | Raby Bay | ECC Rating (A) | 726 | 726 | 726 | 726 | 726
Cleveland Bulk | 413-1 | Cleveland BS | Raby Bay | 50 POE Load (A) | 576 | 576 | 576 | 576 | 576
Cleveland Bulk | 425-1 | Cleveland BS | Victoria Pt | NCC Rating (A) | 705 | 705 | 705 | 705 | 705 | Urban | 70
Cleveland Bulk | 425-1 | Cleveland BS | Victoria Pt | 10 POE Load (A) | 177.8037 | 175.6284 | 176.6697 | 176.7611 | 178.7416
Cleveland Bulk | 425-1 | Cleveland BS | Victoria Pt | Power Factor | 0.99874 | 0.9995 | 0.99948 | 0.99949 | 0.99944
Cleveland Bulk | 425-1 | Cleveland BS | Victoria Pt | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Cleveland Bulk | 425-1 | Cleveland BS | Victoria Pt | 50 POE Load (A) | 662 | 662 | 662 | 662 | 662
Cleveland Bulk | 465-1 | Victoria Pt | Redland Bay | NCC Rating (A) | 562 | 562 | 562 | 562 | 562 | Urban | 70
Cleveland Bulk | 465-1 | Victoria Pt | Redland Bay | 10 POE Load (A) | 244.0846 | 238.6033 | 239.8236 | 240.4098 | 243.7223
Cleveland Bulk | 465-1 | Victoria Pt | Redland Bay | Power Factor | 0.98585 | 0.99358 | 0.99356 | 0.99356 | 0.99346
Cleveland Bulk | 465-1 | Victoria Pt | Redland Bay | ECC Rating (A) | 562 | 562 | 562 | 562 | 562
Cleveland Bulk | 465-1 | Victoria Pt | Redland Bay | 50 POE Load (A) | 394 | 394 | 395 | 395 | 395
Cleveland Bulk | 484-1 | Capalaba | Birkdale | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Cleveland Bulk | 484-1 | Capalaba | Birkdale | 10 POE Load (A) | 117.7081 | 116.4195 | 116.3023 | 115.551 | 116.0666
Cleveland Bulk | 484-1 | Capalaba | Birkdale | Power Factor | 0.9999 | 0.99991 | 0.99991 | 0.99992 | 0.99991
Cleveland Bulk | 484-1 | Capalaba | Birkdale | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Cleveland Bulk | 484-1 | Capalaba | Birkdale | 50 POE Load (A) | 600 | 596 | 592 | 588 | 586
Coomera Bulk | 3640-1 | Coomera BS | Hope Is | NCC Rating (A) | 759 | 759 | 759 | 759 | 759 | Urban | 70
Coomera Bulk | 3640-1 | Coomera BS | Hope Is | 10 POE Load (A) | 217.5765 | 217.2573 | 218.83 | 218.6934 | 221.4842
Coomera Bulk | 3640-1 | Coomera BS | Hope Is | Power Factor | 0.99989 | 0.99989 | 0.99987 | 0.99987 | 0.99982
Coomera Bulk | 3640-1 | Coomera BS | Hope Is | ECC Rating (A) | 921 | 921 | 921 | 921 | 921
Coomera Bulk | 3640-1 | Coomera BS | Hope Is | 50 POE Load (A) | 501 | 505 | 508 | 511 | 515
Coomera Bulk | 3641-1 | Coomera BS | Pimpama East | NCC Rating (A) | 848 | 848 | 848 | 848 | 848 | Urban | 70
Coomera Bulk | 3641-1 | Coomera BS | Pimpama East | 10 POE Load (A) | 240.1379 | 256.7353 | 266.3582 | 273.5985 | 284.4913
Coomera Bulk | 3641-1 | Coomera BS | Pimpama East | Power Factor | 0.98629 | 0.98545 | 0.98465 | 0.98404 | 0.98308
Coomera Bulk | 3641-1 | Coomera BS | Pimpama East | ECC Rating (A) | 921 | 921 | 921 | 921 | 921
Coomera Bulk | 3641-1 | Coomera BS | Pimpama East | 50 POE Load (A) | 537 | 557 | 578 | 598 | 592
Coomera Bulk | 3642-1 | Coomera BS | Pimpama East | NCC Rating (A) | 848 | 848 | 848 | 848 | 848 | Urban | 70
Coomera Bulk | 3642-1 | Coomera BS | Pimpama East | 10 POE Load (A) | 242.0324 | 258.7604 | 268.4592 | 275.7565 | 286.7351
Coomera Bulk | 3642-1 | Coomera BS | Pimpama East | Power Factor | 0.98624 | 0.98539 | 0.98459 | 0.98397 | 0.98302
Coomera Bulk | 3642-1 | Coomera BS | Pimpama East | ECC Rating (A) | 921 | 921 | 921 | 921 | 921
Coomera Bulk | 3642-1 | Coomera BS | Pimpama East | 50 POE Load (A) | 536 | 557 | 577 | 598 | 591
Coomera Bulk | 394-1 | Coomera BS | Hope Is | NCC Rating (A) | 759 | 759 | 759 | 759 | 759 | Urban | 70
Coomera Bulk | 394-1 | Coomera BS | Hope Is | 10 POE Load (A) | 222.8434 | 222.5162 | 224.1279 | 223.988 | 226.8479
Coomera Bulk | 394-1 | Coomera BS | Hope Is | Power Factor | 0.99999 | 0.99999 | 1 | 1 | 1
Coomera Bulk | 394-1 | Coomera BS | Hope Is | ECC Rating (A) | 759 | 759 | 759 | 759 | 759
Coomera Bulk | 394-1 | Coomera BS | Hope Is | 50 POE Load (A) | 413 | 416 | 418 | 421 | 421
Coorparoo Bulk | 3429-1 | Coorparoo BS | Holland Park | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
Coorparoo Bulk | 3429-1 | Coorparoo BS | Holland Park | 10 POE Load (A) | 169.4133 | 174.8792 | 176.3934 | 176.2929 | 178.2502
Coorparoo Bulk | 3429-1 | Coorparoo BS | Holland Park | Power Factor | 0.99589 | 0.99567 | 0.99561 | 0.99562 | 0.99555
Coorparoo Bulk | 3429-1 | Coorparoo BS | Holland Park | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Coorparoo Bulk | 3429-1 | Coorparoo BS | Holland Park | 50 POE Load (A) | 310 | 309 | 309 | 308 | 308
Coorparoo Bulk | 3430-1 | Coorparoo BS | Holland Park | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
Coorparoo Bulk | 3430-1 | Coorparoo BS | Holland Park | 10 POE Load (A) | 166.1577 | 171.5185 | 173.0036 | 172.905 | 174.8248
Coorparoo Bulk | 3430-1 | Coorparoo BS | Holland Park | Power Factor | 0.99587 | 0.99565 | 0.99559 | 0.9956 | 0.99553
Coorparoo Bulk | 3430-1 | Coorparoo BS | Holland Park | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Coorparoo Bulk | 3430-1 | Coorparoo BS | Holland Park | 50 POE Load (A) | 310 | 309 | 309 | 309 | 309
Coorparoo Bulk | 584-4 | 584 Tee2 | Coorparoo BS | NCC Rating (A) | 764 | 764 | 764 | 764 | 764 | Urban | 70
Coorparoo Bulk | 584-4 | 584 Tee2 | Coorparoo BS | 10 POE Load (A) | 2.2136 | 2.2136 | 2.2136 | 2.2136 | 2.2136
Coorparoo Bulk | 584-4 | 584 Tee2 | Coorparoo BS | Power Factor | -6.6105e-07 | -6.6104e-07 | -6.6105e-07 | -6.6105e-07 | -6.6104e-07
Coorparoo Bulk | 612-1 | Coorparoo BS | Camp Hill | NCC Rating (A) | 820 | 820 | 820 | 820 | 820 | Urban | 70
Coorparoo Bulk | 612-1 | Coorparoo BS | Camp Hill | 10 POE Load (A) | 250.5511 | 247.4847 | 247.7328 | 246.9006 | 249.1108
Coorparoo Bulk | 612-1 | Coorparoo BS | Camp Hill | Power Factor | -0.99182 | -0.992 | -0.99199 | -0.99204 | -0.99191
Coorparoo Bulk | 612-1 | Coorparoo BS | Camp Hill | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Coorparoo Bulk | 612-1 | Coorparoo BS | Camp Hill | 50 POE Load (A) | 429 | 427 | 425 | 423 | 423
Coorparoo Bulk | 613-1 | Coorparoo BS | Camp Hill | NCC Rating (A) | 820 | 820 | 820 | 820 | 820 | Urban | 70
Coorparoo Bulk | 613-1 | Coorparoo BS | Camp Hill | 10 POE Load (A) | 250.5511 | 247.4847 | 247.7328 | 246.9006 | 249.1108
Coorparoo Bulk | 613-1 | Coorparoo BS | Camp Hill | Power Factor | -0.99182 | -0.992 | -0.99199 | -0.99204 | -0.99191
Coorparoo Bulk | 613-1 | Coorparoo BS | Camp Hill | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Coorparoo Bulk | 613-1 | Coorparoo BS | Camp Hill | 50 POE Load (A) | 429 | 427 | 425 | 423 | 423
Coorparoo Bulk | 648-1 | Scrub Rd | 648 Tee1 | NCC Rating (A) | 654 | 654 | 654 | 654 | 654 | Urban | 70
Coorparoo Bulk | 648-1 | Scrub Rd | 648 Tee1 | 10 POE Load (A) | 0.60057 | 0.60058 | 0.60058 | 0.60058 | 0.60057
Coorparoo Bulk | 648-1 | Scrub Rd | 648 Tee1 | Power Factor | 1.126e-05 | 1.126e-05 | 1.126e-05 | 1.126e-05 | 1.126e-05
Coorparoo Bulk | 648-2 | 648 Tee1 | 584 Tee1 | NCC Rating (A) | 348 | 348 | 348 | 348 | 348 | Urban | 70
Coorparoo Bulk | 648-2 | 648 Tee1 | 584 Tee1 | 10 POE Load (A) | 0.059645 | 0.059646 | 0.059646 | 0.059646 | 0.059645
Coorparoo Bulk | 648-2 | 648 Tee1 | 584 Tee1 | Power Factor | 1.5495e-05 | 1.5496e-05 | 1.5497e-05 | 1.5498e-05 | 1.5499e-05
Coorparoo Bulk | 648-3 | 648 Tee1 | Camp Hill | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Coorparoo Bulk | 648-3 | 648 Tee1 | Camp Hill | 10 POE Load (A) | 0.88628 | 0.8863 | 0.8863 | 0.88631 | 0.88629
Coorparoo Bulk | 648-3 | 648 Tee1 | Camp Hill | Power Factor | 2.2115e-05 | 2.2116e-05 | 2.2116e-05 | 2.2116e-05 | 2.2116e-05
Doboy Bulk | 3426-1 | Queensport | Bulimba | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Doboy Bulk | 3426-1 | Queensport | Bulimba | 10 POE Load (A) | 221.4516 | 220.1942 | 220.9579 | 220.0046 | 221.6362
Doboy Bulk | 3426-1 | Queensport | Bulimba | Power Factor | 0.99371 | 0.99376 | 0.99373 | 0.99377 | 0.9937
Doboy Bulk | 3426-1 | Queensport | Bulimba | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Doboy Bulk | 3426-1 | Queensport | Bulimba | 50 POE Load (A) | 285 | 284 | 310 | 340 | 340
Doboy Bulk | 414-1 | Doboy BS | Tingalpa | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 70
Doboy Bulk | 414-1 | Doboy BS | Tingalpa | 10 POE Load (A) | 127.3521 | 126.8938 | 127.0372 | 126.3364 | 127.1243
Doboy Bulk | 414-1 | Doboy BS | Tingalpa | Power Factor | 0.99404 | 0.99387 | 0.99389 | 0.99395 | 0.99389
Doboy Bulk | 414-1 | Doboy BS | Tingalpa | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
Doboy Bulk | 414-1 | Doboy BS | Tingalpa | 50 POE Load (A) | 270 | 269 | 267 | 266 | 266
Doboy Bulk | 416-1 | Doboy BS | Murarrie | NCC Rating (A) | 397 | 397 | 397 | 397 | 397 | Urban | 70
Doboy Bulk | 416-1 | Doboy BS | Murarrie | 10 POE Load (A) | 169.522 | 168.2538 | 169.5502 | 168.822 | 169.9207
Doboy Bulk | 416-1 | Doboy BS | Murarrie | Power Factor | 0.96798 | 0.96817 | 0.96798 | 0.96809 | 0.96792
Doboy Bulk | 416-1 | Doboy BS | Murarrie | ECC Rating (A) | 528 | 528 | 528 | 528 | 528
Doboy Bulk | 416-1 | Doboy BS | Murarrie | 50 POE Load (A) | 359 | 354 | 351 | 350 | 350
Doboy Bulk | 443-1 | Queensport | Bulimba | NCC Rating (A) | 652 | 652 | 652 | 652 | 652 | Urban | 70
Doboy Bulk | 443-1 | Queensport | Bulimba | 10 POE Load (A) | 156.4344 | 155.5459 | 156.0856 | 155.4119 | 156.5649
Doboy Bulk | 443-1 | Queensport | Bulimba | Power Factor | 0.99632 | 0.99636 | 0.99634 | 0.99636 | 0.99631
Doboy Bulk | 443-1 | Queensport | Bulimba | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Doboy Bulk | 443-1 | Queensport | Bulimba | 50 POE Load (A) | 423 | 421 | 460 | 505 | 515
Doboy Bulk | 558-1 | Hemmant | Tingalpa | NCC Rating (A) | 680 | 680 | 680 | 680 | 680 | Urban | 70
Doboy Bulk | 558-1 | Hemmant | Tingalpa | 10 POE Load (A) | 169.278 | 166.4261 | 166.5457 | 165.6726 | 166.7776
Doboy Bulk | 558-1 | Hemmant | Tingalpa | Power Factor | 0.9916 | 0.99191 | 0.99188 | 0.99192 | 0.99186
Doboy Bulk | 558-1 | Hemmant | Tingalpa | ECC Rating (A) | 680 | 680 | 680 | 680 | 680
Doboy Bulk | 558-1 | Hemmant | Tingalpa | 50 POE Load (A) | 269 | 267 | 266 | 265 | 265
Doboy Bulk | 563-1 | Doboy BS | Hemmant | NCC Rating (A) | 389 | 389 | 389 | 389 | 389 | Urban | 70
Doboy Bulk | 563-1 | Doboy BS | Hemmant | 10 POE Load (A) | 142.7431 | 153.6894 | 154.1522 | 153.0674 | 153.6559
Doboy Bulk | 563-1 | Doboy BS | Hemmant | Power Factor | 0.99745 | 0.99643 | 0.99662 | 0.9967 | 0.99665
Doboy Bulk | 563-1 | Doboy BS | Hemmant | ECC Rating (A) | 452 | 452 | 452 | 452 | 452
Doboy Bulk | 563-1 | Doboy BS | Hemmant | 50 POE Load (A) | 272 | 293 | 290 | 289 | 289
Doboy Bulk | 564-1 | Doboy BS | Hemmant | NCC Rating (A) | 389 | 389 | 389 | 389 | 389 | Urban | 70
Doboy Bulk | 564-1 | Doboy BS | Hemmant | 10 POE Load (A) | 137.123 | 147.6364 | 148.0803 | 147.0384 | 147.6037
Doboy Bulk | 564-1 | Doboy BS | Hemmant | Power Factor | 0.99648 | 0.99523 | 0.99545 | 0.99555 | 0.99549
Doboy Bulk | 564-1 | Doboy BS | Hemmant | ECC Rating (A) | 452 | 452 | 452 | 452 | 452
Doboy Bulk | 564-1 | Doboy BS | Hemmant | 50 POE Load (A) | 271 | 292 | 289 | 288 | 288
Doboy Bulk | 575C-1 | Doboy BS | Murarrie | NCC Rating (A) | 397 | 397 | 397 | 397 | 397 | Urban | 70
Doboy Bulk | 575C-1 | Doboy BS | Murarrie | 10 POE Load (A) | 160.1534 | 158.9543 | 160.1801 | 159.4915 | 160.5304
Doboy Bulk | 575C-1 | Doboy BS | Murarrie | Power Factor | 0.96629 | 0.9665 | 0.96629 | 0.9664 | 0.96623
Doboy Bulk | 575C-1 | Doboy BS | Murarrie | ECC Rating (A) | 532 | 532 | 532 | 532 | 532
Doboy Bulk | 575C-1 | Doboy BS | Murarrie | 50 POE Load (A) | 360 | 355 | 351 | 350 | 350
Doboy Bulk | 581-1 | Doboy BS | Queensport | NCC Rating (A) | 699 | 699 | 699 | 699 | 699 | Urban | 166
Doboy Bulk | 581-1 | Doboy BS | Queensport | 10 POE Load (A) | 403.0472 | 400.746 | 402.538 | 400.7814 | 402.7912
Doboy Bulk | 581-1 | Doboy BS | Queensport | Power Factor | 0.9815 | 0.98159 | 0.98151 | 0.98157 | 0.98152
Doboy Bulk | 581-1 | Doboy BS | Queensport | ECC Rating (A) | 828 | 828 | 828 | 828 | 828
Doboy Bulk | 581-1 | Doboy BS | Queensport | 50 POE Load (A) | 703 | 698 | 751 | 805 | 808
Doboy Bulk | 645-1 | Doboy BS | Gibson Island | NCC Rating (A) | 468 | 468 | 468 | 468 | 468 | HighSec | 0
Doboy Bulk | 645-1 | Doboy BS | Gibson Island | 10 POE Load (A) | 6.747 | 6.747 | 6.747 | 6.747 | 6.747
Doboy Bulk | 645-1 | Doboy BS | Gibson Island | Power Factor | 2.1138e-05 | 2.1138e-05 | 2.1138e-05 | 2.1138e-05 | 2.1138e-05
Doboy Bulk | 645-1 | Doboy BS | Gibson Island | ECC Rating (A) | 468 | 468 | 468 | 468 | 468
Doboy Bulk | 645-1 | Doboy BS | Gibson Island | 50 POE Load (A) | 159 | 158 | 169 | 169 | 169
Doboy Bulk | 677-1 | Doboy BS | Queensport | NCC Rating (A) | 699 | 699 | 699 | 699 | 699 | Urban | 166
Doboy Bulk | 677-1 | Doboy BS | Queensport | 10 POE Load (A) | 401.9258 | 399.6311 | 401.4181 | 399.6664 | 401.6706
Doboy Bulk | 677-1 | Doboy BS | Queensport | Power Factor | 0.98151 | 0.9816 | 0.98152 | 0.98159 | 0.98153
Doboy Bulk | 677-1 | Doboy BS | Queensport | ECC Rating (A) | 828 | 828 | 828 | 828 | 828
Doboy Bulk | 677-1 | Doboy BS | Queensport | 50 POE Load (A) | 703 | 698 | 751 | 805 | 810
Gatton Bulk | 377-1 | Gatton BS | 377 Tee1 | NCC Rating (A) | 891 | 891 | 891 | 891 | 891 | Rural | 170
Gatton Bulk | 377-1 | Gatton BS | 377 Tee1 | 10 POE Load (A) | 180.5463 | 190.6918 | 190.3944 | 188.9323 | 189.209
Gatton Bulk | 377-1 | Gatton BS | 377 Tee1 | Power Factor | 0.975 | 0.97369 | 0.97376 | 0.97396 | 0.97397
Gatton Bulk | 377-1 | Gatton BS | 377 Tee1 | ECC Rating (A) | 1041 | 1041 | 1041 | 1041 | 1041
Gatton Bulk | 377-1 | Gatton BS | 377 Tee1 | 50 POE Load (A) | 381 | 393 | 390 | 389 | 389
Gatton Bulk | 377-2 | 377 Tee1 | 487 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Gatton Bulk | 377-2 | 377 Tee1 | 487 Tee1 | 10 POE Load (A) | 0.0043951 | 0.0043951 | 0.0043951 | 0.0043951 | 0.0043951
Gatton Bulk | 377-2 | 377 Tee1 | 487 Tee1 | Power Factor | 4.512e-05 | 4.5093e-05 | 4.5126e-05 | 4.5108e-05 | 4.5112e-05
Gatton Bulk | 377-3 | 377 Tee1 | 377 Tee2 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Gatton Bulk | 377-3 | 377 Tee1 | 377 Tee2 | 10 POE Load (A) | 180.6068 | 190.7537 | 190.4563 | 188.9939 | 189.2705
Gatton Bulk | 377-3 | 377 Tee1 | 377 Tee2 | Power Factor | 0.97456 | 0.97327 | 0.97334 | 0.97354 | 0.97355
Gatton Bulk | 377-3 | 377 Tee1 | 377 Tee2 | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Gatton Bulk | 377-3 | 377 Tee1 | 377 Tee2 | 50 POE Load (A) | 351 | 362 | 360 | 359 | 359
Gatton Bulk | 377-4 | 377 Tee2 | Gatton | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Gatton Bulk | 377-4 | 377 Tee2 | Gatton | 10 POE Load (A) | 180.8312 | 190.9811 | 190.6833 | 189.2203 | 189.4968
Gatton Bulk | 377-4 | 377 Tee2 | Gatton | Power Factor | 0.97849 | 0.97766 | 0.97772 | 0.97785 | 0.97787
Gatton Bulk | 377-4 | 377 Tee2 | Gatton | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Gatton Bulk | 377-4 | 377 Tee2 | Gatton | 50 POE Load (A) | 519 | 536 | 532 | 531 | 531
Gatton Bulk | 377-5 | 377 Tee2 | Glenmore Grove | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Rural | 170
Gatton Bulk | 377-5 | 377 Tee2 | Glenmore Grove | 10 POE Load (A) | 0.62683 | 0.61892 | 0.61893 | 0.61898 | 0.61897
Gatton Bulk | 377-5 | 377 Tee2 | Glenmore Grove | Power Factor | 3.1249e-05 | 3.0304e-05 | 3.0304e-05 | 3.0304e-05 | 3.0304e-05
Gatton Bulk | 3859-1 | Gatton BS | Springfield Central | NCC Rating (A) | 809 | 809 | 809 | 809 | 809 | Rural | 170
Gatton Bulk | 3859-1 | Gatton BS | Springfield Central | 10 POE Load (A) | 24.3241 | 23.7809 | 23.6887 | 23.4204 | 23.2996
Gatton Bulk | 3859-1 | Gatton BS | Springfield Central | Power Factor | 0.95695 | 0.9579 | 0.95806 | 0.95855 | 0.95877
Gatton Bulk | 3859-1 | Gatton BS | Springfield Central | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Gatton Bulk | 3859-1 | Gatton BS | Springfield Central | 50 POE Load (A) | 54 | 54 | 53 | 53 | 53
Gatton Bulk | 3860-1 | Gatton BS | Springfield Central | NCC Rating (A) | 809 | 809 | 809 | 809 | 809 | Rural | 170
Gatton Bulk | 3860-1 | Gatton BS | Springfield Central | 10 POE Load (A) | 24.3199 | 23.7769 | 23.6848 | 23.4166 | 23.2959
Gatton Bulk | 3860-1 | Gatton BS | Springfield Central | Power Factor | 0.9567 | 0.95765 | 0.95781 | 0.95829 | 0.95851
Gatton Bulk | 3860-1 | Gatton BS | Springfield Central | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Gatton Bulk | 3860-1 | Gatton BS | Springfield Central | 50 POE Load (A) | 54 | 54 | 53 | 53 | 53
Gatton Bulk | 487-1 | Gatton BS | 487 Tee1 | NCC Rating (A) | 891 | 891 | 891 | 891 | 891 | Rural | 170
Gatton Bulk | 487-1 | Gatton BS | 487 Tee1 | 10 POE Load (A) | 184.0471 | 201.8473 | 201.2599 | 199.4634 | 199.3955
Gatton Bulk | 487-1 | Gatton BS | 487 Tee1 | Power Factor | 0.97656 | 0.97409 | 0.97421 | 0.97446 | 0.97452
Gatton Bulk | 487-1 | Gatton BS | 487 Tee1 | ECC Rating (A) | 891 | 891 | 891 | 891 | 891
Gatton Bulk | 487-1 | Gatton BS | 487 Tee1 | 50 POE Load (A) | 457 | 468 | 465 | 463 | 463
Gatton Bulk | 487-2 | 487 Tee1 | 377 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Gatton Bulk | 487-2 | 487 Tee1 | 377 Tee1 | 10 POE Load (A) | 0.0045537 | 0.0045537 | 0.0045537 | 0.0045537 | 0.0045537
Gatton Bulk | 487-2 | 487 Tee1 | 377 Tee1 | Power Factor | 4.3514e-05 | 4.3531e-05 | 4.354e-05 | 4.3524e-05 | 4.3528e-05
Gatton Bulk | 487-3 | 487 Tee1 | 487 Tee2 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Gatton Bulk | 487-3 | 487 Tee1 | 487 Tee2 | 10 POE Load (A) | 184.8656 | 202.6987 | 202.1097 | 200.3099 | 200.2411
Gatton Bulk | 487-3 | 487 Tee1 | 487 Tee2 | Power Factor | 0.97799 | 0.97586 | 0.97596 | 0.97618 | 0.97623
Gatton Bulk | 487-3 | 487 Tee1 | 487 Tee2 | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Gatton Bulk | 487-3 | 487 Tee1 | 487 Tee2 | 50 POE Load (A) | 422 | 432 | 429 | 428 | 428
Gatton Bulk | 487-6 | 487 Tee3 | 3844 Tee1 | NCC Rating (A) | 348 | 348 | 348 | 348 | 348 | Rural | 170
Gatton Bulk | 487-6 | 487 Tee3 | 3844 Tee1 | 10 POE Load (A) | 0.015607 | 0.015519 | 0.015522 | 0.015528 | 0.01553
Gatton Bulk | 487-6 | 487 Tee3 | 3844 Tee1 | Power Factor | -6.7698e-05 | -6.77e-05 | -6.7699e-05 | -6.7696e-05 | -6.7696e-05
Gatton Bulk | 487-8 | 487 Tee4 | 3844 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Gatton Bulk | 487-8 | 487 Tee4 | 3844 Tee1 | 10 POE Load (A) | 0.00041482 | 0.00041231 | 0.0004124 | 0.00041258 | 0.00041265
Gatton Bulk | 487-8 | 487 Tee4 | 3844 Tee1 | Power Factor | -0.99997 | -0.99999 | -0.99992 | -1 | -0.99999
Gatton Bulk | 487-9 | 487 Tee2 | Gatton | NCC Rating (A) | 878 | 878 | 878 | 878 | 878 | Rural | 170
Gatton Bulk | 487-9 | 487 Tee2 | Gatton | 10 POE Load (A) | 114.1191 | 111.2351 | 111.401 | 110.8577 | 111.4684
Gatton Bulk | 487-9 | 487 Tee2 | Gatton | Power Factor | 0.98137 | 0.9827 | 0.98266 | 0.98269 | 0.98261
Gatton Bulk | 487-9 | 487 Tee2 | Gatton | ECC Rating (A) | 921 | 921 | 921 | 921 | 921
Gatton Bulk | 487-9 | 487 Tee2 | Gatton | 50 POE Load (A) | 460 | 474 | 471 | 470 | 470
Gatton Bulk | 531-1 | Gatton | Tenthill | NCC Rating (A) | 293 | 432 | 432 | 432 | 432 | Rural | 170
Gatton Bulk | 531-1 | Gatton | Tenthill | 10 POE Load (A) | 75.554 | 73.9966 | 73.8149 | 73.192 | 73.4655
Gatton Bulk | 531-1 | Gatton | Tenthill | Power Factor | -0.95006 | -0.95047 | -0.95063 | -0.95085 | -0.95093
Gatton Bulk | 531-1 | Gatton | Tenthill | ECC Rating (A) | 293 | 293 | 432 | 432 | 432
Gatton Bulk | 531-1 | Gatton | Tenthill | 50 POE Load (A) | 141 | 141 | 160 | 160 | 165
Gatton Bulk | 532-1 | Tenthill | 532 Tee1 | NCC Rating (A) | 416 | 416 | 416 | 416 | 416 | Rural | 170
Gatton Bulk | 532-1 | Tenthill | 532 Tee1 | 10 POE Load (A) | 0.0023191 | 0.0023377 | 0.0023379 | 0.0023385 | 0.0023384
Gatton Bulk | 532-1 | Tenthill | 532 Tee1 | Power Factor | 8.259e-05 | 8.2615e-05 | 8.2619e-05 | 8.2587e-05 | 8.2662e-05
Gatton Bulk | 533-1 | Tenthill | Mt Sylvia | NCC Rating (A) | 144 | 144 | 144 | 144 | 144 | Rural | 170
Gatton Bulk | 533-1 | Tenthill | Mt Sylvia | 10 POE Load (A) | 19.9374 | 19.4562 | 19.3035 | 19.0673 | 19.0174
Gatton Bulk | 533-1 | Tenthill | Mt Sylvia | Power Factor | 0.91461 | 0.91513 | 0.91524 | 0.91543 | 0.91547
Gatton Bulk | 533-1 | Tenthill | Mt Sylvia | ECC Rating (A) | 144 | 144 | 144 | 144 | 144
Gatton Bulk | 533-1 | Tenthill | Mt Sylvia | 50 POE Load (A) | 35 | 35 | 34 | 34 | 34
Goodna Bulk | 3800-1 | Goodna BS | Cooneana | NCC Rating (A) | 695 | 695 | 695 | 695 | 695 | Rural | 170
Goodna Bulk | 3800-1 | Goodna BS | Cooneana | 10 POE Load (A) | 63.3624 | 75.1536 | 65.6381 | 75.307 | 85.8449
Goodna Bulk | 3800-1 | Goodna BS | Cooneana | Power Factor | 0.99258 | 0.991 | 0.99289 | 0.99164 | 0.99036
Goodna Bulk | 3800-1 | Goodna BS | Cooneana | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Goodna Bulk | 3800-1 | Goodna BS | Cooneana | 50 POE Load (A) | 167 | 188 | 209 | 229 | 235
Goodna Bulk | 3801-1 | Goodna BS | Carol Pk Central | NCC Rating (A) | 793 | 793 | 793 | 793 | 793 | Urban | 70
Goodna Bulk | 3801-1 | Goodna BS | Carol Pk Central | 10 POE Load (A) | 249.2658 | 246.381 | 249.5589 | 249.3722 | 251.2959
Goodna Bulk | 3801-1 | Goodna BS | Carol Pk Central | Power Factor | 0.98968 | 0.99025 | 0.98981 | 0.98998 | 0.98978
Goodna Bulk | 3801-1 | Goodna BS | Carol Pk Central | ECC Rating (A) | 827 | 827 | 827 | 827 | 827
Goodna Bulk | 3801-1 | Goodna BS | Carol Pk Central | 50 POE Load (A) | 446 | 442 | 442 | 442 | 442
Goodna Bulk | 3802-1 | Goodna BS | Springfield | NCC Rating (A) | 627 | 627 | 627 | 627 | 627 | Urban | 70
Goodna Bulk | 3802-1 | Goodna BS | Springfield | 10 POE Load (A) | 240.5041 | 239.7229 | 246.4361 | 252.2113 | 260.7923
Goodna Bulk | 3802-1 | Goodna BS | Springfield | Power Factor | -0.98744 | -0.98742 | -0.98687 | -0.98638 | -0.98569
Goodna Bulk | 3802-1 | Goodna BS | Springfield | ECC Rating (A) | 714 | 714 | 714 | 714 | 714
Goodna Bulk | 3802-1 | Goodna BS | Springfield | 50 POE Load (A) | 466 | 473 | 480 | 488 | 488
Goodna Bulk | 3803-1 | Goodna BS | Carol Park | NCC Rating (A) | 550 | 550 | 550 | 550 | 550 | Urban | 70
Goodna Bulk | 3803-1 | Goodna BS | Carol Park | 10 POE Load (A) | 198.2227 | 197.645 | 202.0469 | 204.688 | 209.3229
Goodna Bulk | 3803-1 | Goodna BS | Carol Park | Power Factor | 0.97239 | 0.9727 | 0.97238 | 0.97236 | 0.97202
Goodna Bulk | 3803-1 | Goodna BS | Carol Park | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Goodna Bulk | 3803-1 | Goodna BS | Carol Park | 50 POE Load (A) | 409 | 411 | 414 | 418 | 418
Goodna Bulk | 3805-1 | Goodna BS | Carol Park | NCC Rating (A) | 550 | 550 | 550 | 550 | 550 | Urban | 70
Goodna Bulk | 3805-1 | Goodna BS | Carol Park | 10 POE Load (A) | 181.2644 | 180.7361 | 184.7612 | 187.1762 | 191.4145
Goodna Bulk | 3805-1 | Goodna BS | Carol Park | Power Factor | 0.96913 | 0.96946 | 0.96912 | 0.9691 | 0.96874
Goodna Bulk | 3805-1 | Goodna BS | Carol Park | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Goodna Bulk | 3805-1 | Goodna BS | Carol Park | 50 POE Load (A) | 393 | 395 | 398 | 402 | 402
Goodna Bulk | 3806-1 | Goodna BS | Springfield | NCC Rating (A) | 627 | 627 | 627 | 627 | 627 | Urban | 70
Goodna Bulk | 3806-1 | Goodna BS | Springfield | 10 POE Load (A) | 239.5999 | 238.8217 | 245.5096 | 251.263 | 259.8117
Goodna Bulk | 3806-1 | Goodna BS | Springfield | Power Factor | 0.99666 | 0.99667 | 0.99622 | 0.99583 | 0.99524
Goodna Bulk | 3806-1 | Goodna BS | Springfield | ECC Rating (A) | 714 | 714 | 714 | 714 | 714
Goodna Bulk | 3806-1 | Goodna BS | Springfield | 50 POE Load (A) | 466 | 473 | 480 | 487 | 487
Goodna Bulk | 3807-1 | Goodna BS | Redbank | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Goodna Bulk | 3807-1 | Goodna BS | Redbank | 10 POE Load (A) | 166.3208 | 163.542 | 163.1872 | 161.3609 | 161.377
Goodna Bulk | 3807-1 | Goodna BS | Redbank | Power Factor | 0.98495 | 0.98502 | 0.98503 | 0.98508 | 0.98508
Goodna Bulk | 3807-1 | Goodna BS | Redbank | ECC Rating (A) | 1250 | 1250 | 1250 | 1250 | 1250
Goodna Bulk | 3807-1 | Goodna BS | Redbank | 50 POE Load (A) | 388 | 386 | 384 | 384 | 384
Goodna Bulk | 3808-1 | Goodna BS | Carol Pk Central | NCC Rating (A) | 751 | 751 | 751 | 751 | 751 | Urban | 70
Goodna Bulk | 3808-1 | Goodna BS | Carol Pk Central | 10 POE Load (A) | 249.7069 | 246.8168 | 250.0005 | 249.8135 | 251.7407
Goodna Bulk | 3808-1 | Goodna BS | Carol Pk Central | Power Factor | 0.98978 | 0.99035 | 0.98991 | 0.99008 | 0.98989
Goodna Bulk | 3808-1 | Goodna BS | Carol Pk Central | ECC Rating (A) | 803 | 803 | 803 | 803 | 803
Goodna Bulk | 3808-1 | Goodna BS | Carol Pk Central | 50 POE Load (A) | 435 | 431 | 430 | 431 | 431
Goodna Bulk | 3809-1 | Goodna BS | Cooneana | NCC Rating (A) | 695 | 695 | 695 | 695 | 695 | Rural | 170
Goodna Bulk | 3809-1 | Goodna BS | Cooneana | 10 POE Load (A) | 71.6059 | 84.9333 | 74.178 | 85.1066 | 97.0177
Goodna Bulk | 3809-1 | Goodna BS | Cooneana | Power Factor | 0.99326 | 0.99173 | 0.99331 | 0.99223 | 0.99113
Goodna Bulk | 3809-1 | Goodna BS | Cooneana | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Goodna Bulk | 3809-1 | Goodna BS | Cooneana | 50 POE Load (A) | 167 | 188 | 209 | 229 | 229
Goodna Bulk | 3880-1 | Carol Park | Springfield Central | NCC Rating (A) | 794 | 794 | 794 | 794 | 794 | Urban | 70
Goodna Bulk | 3880-1 | Carol Park | Springfield Central | 10 POE Load (A) | 117.8557 | 120.6063 | 129.7646 | 138.3757 | 148.7179
Goodna Bulk | 3880-1 | Carol Park | Springfield Central | Power Factor | 0.99985 | 0.99995 | 0.99996 | 0.99967 | 1
Goodna Bulk | 3880-1 | Carol Park | Springfield Central | ECC Rating (A) | 794 | 794 | 794 | 794 | 794
Goodna Bulk | 3880-1 | Carol Park | Springfield Central | 50 POE Load (A) | 242 | 254 | 264 | 275 | 275
Goodna Bulk | 3881-1 | Springfield | Springfield Central | NCC Rating (A) | 794 | 794 | 794 | 794 | 794 | Urban | 70
Goodna Bulk | 3881-1 | Springfield | Springfield Central | 10 POE Load (A) | 141.4284 | 144.4068 | 154.5657 | 163.9121 | 175.2379
Goodna Bulk | 3881-1 | Springfield | Springfield Central | Power Factor | 0.98073 | 0.98038 | 0.97897 | 0.97776 | 0.97623
Goodna Bulk | 3881-1 | Springfield | Springfield Central | ECC Rating (A) | 794 | 794 | 794 | 794 | 794
Goodna Bulk | 3881-1 | Springfield | Springfield Central | 50 POE Load (A) | 240 | 251 | 261 | 272 | 272
Goodna Bulk | 456-1 | Wacol Sth | 456 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Goodna Bulk | 456-1 | Wacol Sth | 456 Tee1 | 10 POE Load (A) | 71.3122 | 71.883 | 74.3069 | 76.516 | 79.5827
Goodna Bulk | 456-1 | Wacol Sth | 456 Tee1 | Power Factor | 0.97113 | 0.97123 | 0.97091 | 0.97066 | 0.97005
Goodna Bulk | 456-2 | 456 Tee1 | Carol Pk Central | NCC Rating (A) | 493 | 493 | 493 | 493 | 493 | Urban | 70
Goodna Bulk | 456-2 | 456 Tee1 | Carol Pk Central | 10 POE Load (A) | 71.3122 | 71.883 | 74.3069 | 76.516 | 79.5827
Goodna Bulk | 456-2 | 456 Tee1 | Carol Pk Central | Power Factor | -0.91893 | -0.91943 | -0.92063 | -0.9217 | -0.92275
Goodna Bulk | 456-2 | 456 Tee1 | Carol Pk Central | ECC Rating (A) | 493 | 493 | 493 | 493 | 493
Goodna Bulk | 456-2 | 456 Tee1 | Carol Pk Central | 50 POE Load (A) | 156 | 158 | 160 | 162 | 162
Goodna Bulk | 456-3 | 456 Tee1 | Carol Pk | NCC Rating (A) | 493 | 493 | 493 | 493 | 493 | Urban | 70
Goodna Bulk | 456-3 | 456 Tee1 | Carol Pk | 10 POE Load (A) | 71.7304 | 72.3004 | 74.7257 | 76.9358 | 80.0058
Goodna Bulk | 456-3 | 456 Tee1 | Carol Pk | Power Factor | 0.97004 | 0.97015 | 0.96988 | 0.96967 | 0.9691
Goodna Bulk | 456-3 | 456 Tee1 | Carol Pk | ECC Rating (A) | 493 | 493 | 493 | 493 | 493
Goodna Bulk | 456-3 | 456 Tee1 | Carol Pk | 50 POE Load (A) | 156 | 158 | 160 | 162 | 162
Griffin Bulk | 312-1 | Kallangur | Narangba | NCC Rating (A) | 489 | 489 | 489 | 489 | 489 | Rural | 170
Griffin Bulk | 312-1 | Kallangur | Narangba | 10 POE Load (A) | 0.64837 | 0.64836 | 0.64831 | 0.64816 | 0.64787
Griffin Bulk | 312-1 | Kallangur | Narangba | Power Factor | -1.3717e-06 | -1.3713e-06 | -1.3714e-06 | -1.3711e-06 | -1.3717e-06
Griffin Bulk | 320-1 | Griffin BS | 320 Tee1 | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70
Griffin Bulk | 320-1 | Griffin BS | 320 Tee1 | 10 POE Load (A) | 228.0774 | 227.1962 | 229.4025 | 233.9553 | 244.4218
Griffin Bulk | 320-1 | Griffin BS | 320 Tee1 | Power Factor | 0.99987 | 0.99989 | 0.99987 | 0.99985 | 0.99977
Griffin Bulk | 320-1 | Griffin BS | 320 Tee1 | ECC Rating (A) | 912 | 912 | 912 | 912 | 912
Griffin Bulk | 320-1 | Griffin BS | 320 Tee1 | 50 POE Load (A) | 450 | 452 | 454 | 466 | 466
Griffin Bulk | 320-2 | 320 Tee1 | Mango Hill Bus 2 | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 70
Griffin Bulk | 320-2 | 320 Tee1 | Mango Hill Bus 2 | 10 POE Load (A) | 159.3324 | 156.7841 | 156.6033 | 153.9534 | 151.7571
Griffin Bulk | 320-2 | 320 Tee1 | Mango Hill Bus 2 | Power Factor | 1 | 1 | 1 | 1 | 1
Griffin Bulk | 320-2 | 320 Tee1 | Mango Hill Bus 2 | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
Griffin Bulk | 320-2 | 320 Tee1 | Mango Hill Bus 2 | 50 POE Load (A) | 315 | 315 | 316 | 317 | 317
Griffin Bulk | 320-3 | 320 Tee1 | Kalangur | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 70
Griffin Bulk | 320-3 | 320 Tee1 | Kalangur | 10 POE Load (A) | 69.2332 | 70.8976 | 73.258 | 80.4705 | 93.1683
Griffin Bulk | 320-3 | 320 Tee1 | Kalangur | Power Factor | 0.98967 | 0.99004 | 0.99073 | 0.99123 | 0.99152
Griffin Bulk | 320-3 | 320 Tee1 | Kalangur | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
Griffin Bulk | 320-3 | 320 Tee1 | Kalangur | 50 POE Load (A) | 241 | 243 | 244 | 255 | 255
Griffin Bulk | 3329-1 | Griffin BS | 3329 Tee1 | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70
Griffin Bulk | 3329-1 | Griffin BS | 3329 Tee1 | 10 POE Load (A) | 257.0757 | 257.5395 | 261.3564 | 270.8893 | 289.8671
Griffin Bulk | 3329-1 | Griffin BS | 3329 Tee1 | Power Factor | 0.99737 | 0.9973 | 0.99714 | 0.99668 | 0.99576
Griffin Bulk | 3329-1 | Griffin BS | 3329 Tee1 | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
Griffin Bulk | 3329-1 | Griffin BS | 3329 Tee1 | 50 POE Load (A) | 350 | 351 | 353 | 364 | 364
Griffin Bulk | 3329-2 | 3329 Tee1 | 3330 Tee1 | NCC Rating (A) | 865 | 865 | 865 | 865 | 865 | Urban | 70
Griffin Bulk | 3329-2 | 3329 Tee1 | 3330 Tee1 | 10 POE Load (A) | 0.029215 | 0.029214 | 0.029214 | 0.029212 | 0.029208
Griffin Bulk | 3329-2 | 3329 Tee1 | 3330 Tee1 | Power Factor | 6.7997e-06 | 6.7997e-06 | 6.7993e-06 | 6.7993e-06 | 6.7997e-06
Griffin Bulk | 3329-3 | 3329 Tee1 | Kallangur | NCC Rating (A) | 762 | 762 | 762 | 762 | 762 | Urban | 70
Griffin Bulk | 3329-3 | 3329 Tee1 | Kallangur | 10 POE Load (A) | 257.1219 | 257.586 | 261.403 | 270.938 | 289.9197
Griffin Bulk | 3329-3 | 3329 Tee1 | Kallangur | Power Factor | 0.99588 | 0.99581 | 0.99565 | 0.99519 | 0.99433
Griffin Bulk | 3329-3 | 3329 Tee1 | Kallangur | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Griffin Bulk | 3329-3 | 3329 Tee1 | Kallangur | 50 POE Load (A) | 403 | 405 | 406 | 420 | 420
Griffin Bulk | 3330-1 | Griffin BS | 3330 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Griffin Bulk | 3330-1 | Griffin BS | 3330 Tee1 | 10 POE Load (A) | 127.9488 | 128.1791 | 130.0784 | 134.819 | 144.2572
Griffin Bulk | 3330-1 | Griffin BS | 3330 Tee1 | Power Factor | 0.99968 | 0.99965 | 0.9996 | 0.99941 | 0.99899
Griffin Bulk | 3330-1 | Griffin BS | 3330 Tee1 | ECC Rating (A) | 926 | 926 | 926 | 926 | 926
Griffin Bulk | 3330-1 | Griffin BS | 3330 Tee1 | 50 POE Load (A) | 325 | 327 | 328 | 339 | 339
Griffin Bulk | 3330-2 | 3330 Tee1 | 3329 Tee1 | NCC Rating (A) | 793 | 793 | 793 | 793 | 793 | Urban | 70
Griffin Bulk | 3330-2 | 3330 Tee1 | 3329 Tee1 | 10 POE Load (A) | 0.014167 | 0.014167 | 0.014167 | 0.014166 | 0.014165
Griffin Bulk | 3330-2 | 3330 Tee1 | 3329 Tee1 | Power Factor | 1.9244e-05 | 1.9245e-05 | 1.9244e-05 | 1.9246e-05 | 1.9246e-05
Griffin Bulk | 3330-3 | 3330 Tee1 | APM | NCC Rating (A) | 865 | 865 | 865 | 865 | 865 | Urban | 70
Griffin Bulk | 3330-3 | 3330 Tee1 | APM | 10 POE Load (A) | 127.9972 | 128.2281 | 130.1277 | 134.8724 | 144.3179
Griffin Bulk | 3330-3 | 3330 Tee1 | APM | Power Factor | 0.99927 | 0.99923 | 0.99916 | 0.99894 | 0.99848
Griffin Bulk | 3330-3 | 3330 Tee1 | APM | ECC Rating (A) | 926 | 926 | 926 | 926 | 926
Griffin Bulk | 3330-3 | 3330 Tee1 | APM | 50 POE Load (A) | 325 | 327 | 328 | 339 | 339
Griffin Bulk | 3331-1 | 3331 Tee1 | Kallangur | NCC Rating (A) | 926 | 926 | 926 | 926 | 926 | Urban | 70
Griffin Bulk | 3331-1 | 3331 Tee1 | Kallangur | 10 POE Load (A) | 127.8182 | 128.0511 | 129.951 | 134.7073 | 144.1738
Griffin Bulk | 3331-1 | 3331 Tee1 | Kallangur | Power Factor | 0.99807 | 0.99802 | 0.99794 | 0.99768 | 0.99719
Griffin Bulk | 3331-1 | 3331 Tee1 | Kallangur | ECC Rating (A) | 926 | 926 | 926 | 926 | 926
Griffin Bulk | 3331-1 | 3331 Tee1 | Kallangur | 50 POE Load (A) | 291 | 293 | 295 | 306 | 306
Griffin Bulk | 3331-3 | Aust Paper Mills | 3331 Tee1 | NCC Rating (A) | 840 | 840 | 840 | 840 | 840 | Urban | 70
Griffin Bulk | 3331-3 | Aust Paper Mills | 3331 Tee1 | 10 POE Load (A) | 127.5777 | 127.8076 | 129.7068 | 134.4453 | 143.8795
Griffin Bulk | 3331-3 | Aust Paper Mills | 3331 Tee1 | Power Factor | 0.99968 | 0.99966 | 0.9996 | 0.99944 | 0.99908
Griffin Bulk | 3331-3 | Aust Paper Mills | 3331 Tee1 | ECC Rating (A) | 926 | 926 | 926 | 926 | 926
Griffin Bulk | 3331-3 | Aust Paper Mills | 3331 Tee1 | 50 POE Load (A) | 325 | 327 | 328 | 339 | 339
Griffin Bulk | 3359-1 | 3359 Tee1 | Hays Inlet | NCC Rating (A) | 880 | 880 | 880 | 880 | 880 | Urban | 70
Griffin Bulk | 3359-1 | 3359 Tee1 | Hays Inlet | 10 POE Load (A) | 0.39016 | 0.39018 | 0.39018 | 0.39018 | 0.39015
Griffin Bulk | 3359-1 | 3359 Tee1 | Hays Inlet | Power Factor | -1.0504e-06 | -1.05e-06 | -1.0509e-06 | -1.0506e-06 | -1.0503e-06
Griffin Bulk | 3359-2 | 3359 Tee1 | 3359 Tee2 | NCC Rating (A) | 912 | 912 | 912 | 912 | 912 | Urban | 70
Griffin Bulk | 3359-2 | 3359 Tee1 | 3359 Tee2 | 10 POE Load (A) | 176.7703 | 175.2422 | 176.1838 | 177.1649 | 181.13
Griffin Bulk | 3359-2 | 3359 Tee1 | 3359 Tee2 | Power Factor | 0.98173 | 0.98202 | 0.98207 | 0.98243 | 0.98275
Griffin Bulk | 3359-2 | 3359 Tee1 | 3359 Tee2 | ECC Rating (A) | 912 | 912 | 912 | 912 | 912
Griffin Bulk | 3359-2 | 3359 Tee1 | 3359 Tee2 | 50 POE Load (A) | 408 | 408 | 409 | 410 | 410
Griffin Bulk | 3359-3 | 3359 Tee2 | 3359 Tee3 | NCC Rating (A) | 912 | 912 | 912 | 912 | 912 | Urban | 70
Griffin Bulk | 3359-3 | 3359 Tee2 | 3359 Tee3 | 10 POE Load (A) | 176.8635 | 175.3347 | 176.2759 | 177.2562 | 181.2206
Griffin Bulk | 3359-3 | 3359 Tee2 | 3359 Tee3 | Power Factor | 0.98126 | 0.98155 | 0.9816 | 0.98196 | 0.98231
Griffin Bulk | 3359-3 | 3359 Tee2 | 3359 Tee3 | ECC Rating (A) | 912 | 912 | 912 | 912 | 912
Griffin Bulk | 3359-3 | 3359 Tee2 | 3359 Tee3 | 50 POE Load (A) | 408 | 408 | 409 | 410 | 410
Griffin Bulk | 3359-4 | 3359 Tee3 | Mango Hill Bus 2 | NCC Rating (A) | 806 | 806 | 806 | 806 | 806 | Urban | 70
Griffin Bulk | 3359-4 | 3359 Tee3 | Mango Hill Bus 2 | 10 POE Load (A) | 177.2607 | 175.7291 | 176.669 | 177.6456 | 181.6065
Griffin Bulk | 3359-4 | 3359 Tee3 | Mango Hill Bus 2 | Power Factor | 0.98149 | 0.98177 | 0.98182 | 0.98219 | 0.98255
Griffin Bulk | 3359-4 | 3359 Tee3 | Mango Hill Bus 2 | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Griffin Bulk | 3359-4 | 3359 Tee3 | Mango Hill Bus 2 | 50 POE Load (A) | 329 | 329 | 330 | 331 | 331
Griffin Bulk | 3359-5 | 3359 Tee2 | P51001-D | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Griffin Bulk | 3359-5 | 3359 Tee2 | P51001-D | 10 POE Load (A) | 0.46656 | 0.46659 | 0.46658 | 0.46658 | 0.46654
Griffin Bulk | 3359-5 | 3359 Tee2 | P51001-D | Power Factor | 8.5353e-06 | 8.5353e-06 | 8.5353e-06 | 8.5354e-06 | 8.5354e-06
Griffin Bulk | 3359-6 | 3359 Tee3 | X18574-E | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Urban | 70
Griffin Bulk | 3359-6 | 3359 Tee3 | X18574-E | 10 POE Load (A) | 0.19302 | 0.19303 | 0.19302 | 0.19302 | 0.19301
Griffin Bulk | 3359-6 | 3359 Tee3 | X18574-E | Power Factor | 3.3927e-06 | 3.3928e-06 | 3.3928e-06 | 3.3927e-06 | 3.3927e-06
Griffin Bulk | 3359-7 | Griffin BS | 3359 Tee1 | NCC Rating (A) | 917 | 917 | 917 | 917 | 917 | Urban | 70
Griffin Bulk | 3359-7 | Griffin BS | 3359 Tee1 | 10 POE Load (A) | 176.6901 | 175.1627 | 176.1045 | 177.0863 | 181.052
Griffin Bulk | 3359-7 | Griffin BS | 3359 Tee1 | Power Factor | 0.9804 | 0.98072 | 0.98076 | 0.98111 | 0.98139
Griffin Bulk | 3359-7 | Griffin BS | 3359 Tee1 | ECC Rating (A) | 917 | 917 | 917 | 917 | 917
Griffin Bulk | 3359-7 | Griffin BS | 3359 Tee1 | 50 POE Load (A) | 408 | 409 | 409 | 411 | 411
Griffin Bulk | 338-1 | Griffin BS | Strathpine | NCC Rating (A) | 348 | 348 | 348 | 348 | 348 | Urban | 70
Griffin Bulk | 338-1 | Griffin BS | Strathpine | 10 POE Load (A) | 4.0492 | 4.0492 | 4.0492 | 4.0492 | 4.0492
Griffin Bulk | 338-1 | Griffin BS | Strathpine | Power Factor | 0.00011973 | 0.00011973 | 0.00011973 | 0.00011973 | 0.00011973
Griffin Bulk | 338-1 | Griffin BS | Strathpine | ECC Rating (A) | 348 | 348 | 348 | 348 | 348
Griffin Bulk | 338-1 | Griffin BS | Strathpine | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Gympie Bulk | 3004-1 | Coondoo Ck Reg | Tin Can Bay | NCC Rating (A) | 246 | 246 | 246 | 246 | 246 | Rural | 170
Gympie Bulk | 3004-1 | Coondoo Ck Reg | Tin Can Bay | 10 POE Load (A) | 1.2217 | 1.2219 | 1.2217 | 1.2218 | 1.2215
Gympie Bulk | 3004-1 | Coondoo Ck Reg | Tin Can Bay | Power Factor | 0.00028204 | 0.00028204 | 0.00028204 | 0.00028204 | 0.00028204
Gympie Bulk | 3004-1 | Coondoo Ck Reg | Tin Can Bay | ECC Rating (A) | 246 | 246 | 246 | 246 | 246
Gympie Bulk | 3004-1 | Coondoo Ck Reg | Tin Can Bay | 50 POE Load (A) | 78 | 78 | 77 | 77 | 77
Gympie Bulk | 3005-1 | Coondoo Ck Reg | Tin Can Bay | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170
Gympie Bulk | 3005-1 | Coondoo Ck Reg | Tin Can Bay | 10 POE Load (A) | 65.3537 | 64.8865 | 65.3386 | 65.3155 | 66.1476
Gympie Bulk | 3005-1 | Coondoo Ck Reg | Tin Can Bay | Power Factor | 0.99895 | 0.99902 | 0.99895 | 0.99896 | 0.99884
Gympie Bulk | 3005-1 | Coondoo Ck Reg | Tin Can Bay | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
Gympie Bulk | 3005-1 | Coondoo Ck Reg | Tin Can Bay | 50 POE Load (A) | 94 | 93 | 92 | 92 | 92
Gympie Bulk | 3009-1 | Gympie BS | Gympie Nth | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Rural | 170
Gympie Bulk | 3009-1 | Gympie BS | Gympie Nth | 10 POE Load (A) | 107.7557 | 106.1953 | 106.0946 | 105.1693 | 105.1824
Gympie Bulk | 3009-1 | Gympie BS | Gympie Nth | Power Factor | 0.99999 | 1 | 1 | 1 | 1
Gympie Bulk | 3009-1 | Gympie BS | Gympie Nth | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
Gympie Bulk | 3009-1 | Gympie BS | Gympie Nth | 50 POE Load (A) | 195 | 194 | 193 | 192 | 192
Gympie Bulk | 3011-1 | Gympie BS | Gympie Nth | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Rural | 170
Gympie Bulk | 3011-1 | Gympie BS | Gympie Nth | 10 POE Load (A) | 107.7854 | 106.2245 | 106.1238 | 105.1983 | 105.2114
Gympie Bulk | 3011-1 | Gympie BS | Gympie Nth | Power Factor | 0.99999 | 1 | 1 | 1 | 1
Gympie Bulk | 3011-1 | Gympie BS | Gympie Nth | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
Gympie Bulk | 3011-1 | Gympie BS | Gympie Nth | 50 POE Load (A) | 195 | 194 | 193 | 192 | 192
Gympie Bulk | 339/2-1 | Amamoor | 339 Tee1 | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
Gympie Bulk | 339/2-1 | Amamoor | 339 Tee1 | 10 POE Load (A) | 64.3851 | 61.3804 | 59.4089 | 58.8381 | 58.8422
Gympie Bulk | 339/2-1 | Amamoor | 339 Tee1 | Power Factor | 0.87841 | 0.87995 | 0.88096 | 0.88126 | 0.88125
Gympie Bulk | 339/2-1 | Amamoor | 339 Tee1 | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
Gympie Bulk | 339/2-1 | Amamoor | 339 Tee1 | 50 POE Load (A) | 124 | 122 | 119 | 118 | 118
Gympie Bulk | 339/2-2 | 339 Tee1 | Imbil | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
Gympie Bulk | 339/2-2 | 339 Tee1 | Imbil | 10 POE Load (A) | 52.3471 | 49.3726 | 47.412 | 46.8477 | 46.8476
Gympie Bulk | 339/2-2 | 339 Tee1 | Imbil | Power Factor | 0.87193 | 0.8735 | 0.87454 | 0.87486 | 0.87485
Gympie Bulk | 339/2-2 | 339 Tee1 | Imbil | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
Gympie Bulk | 339/2-2 | 339 Tee1 | Imbil | 50 POE Load (A) | 115 | 113 | 110 | 109 | 109
Gympie Bulk | 339/2-5 | 339 Tee2 | 340 Tee2 | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
Gympie Bulk | 339/2-5 | 339 Tee2 | 340 Tee2 | 10 POE Load (A) | 0.13414 | 0.1345 | 0.13465 | 0.13473 | 0.13469
Gympie Bulk | 339/2-5 | 339 Tee2 | 340 Tee2 | Power Factor | 3.5781e-06 | 3.5781e-06 | 3.5781e-06 | 3.5781e-06 | 3.5781e-06
Gympie Bulk | 339-1 | Gympie BS | 339 Tee1 | NCC Rating (A) | 786 | 786 | 786 | 786 | 786 | Rural | 170
Gympie Bulk | 339-1 | Gympie BS | 339 Tee1 | 10 POE Load (A) | 160.8034 | 156.2736 | 154.5392 | 153.4155 | 154.0119
Gympie Bulk | 339-1 | Gympie BS | 339 Tee1 | Power Factor | 0.9085 | 0.9101 | 0.91101 | 0.91135 | 0.91128
Gympie Bulk | 339-1 | Gympie BS | 339 Tee1 | ECC Rating (A) | 786 | 786 | 786 | 786 | 786
Gympie Bulk | 339-1 | Gympie BS | 339 Tee1 | 50 POE Load (A) | 186 | 184 | 183 | 181 | 181
Gympie Bulk | 339-2 | 339 Tee1 | Amamoor | NCC Rating (A) | 322 | 322 | 322 | 322 | 322 | Rural | 170
Gympie Bulk | 339-2 | 339 Tee1 | Amamoor | 10 POE Load (A) | 161.2272 | 156.6947 | 154.9585 | 153.8342 | 154.4307
Gympie Bulk | 339-2 | 339 Tee1 | Amamoor | Power Factor | 0.91742 | 0.91863 | 0.9194 | 0.91964 | 0.91963
Gympie Bulk | 339-2 | 339 Tee1 | Amamoor | ECC Rating (A) | 322 | 322 | 322 | 322 | 322
Gympie Bulk | 339-2 | 339 Tee1 | Amamoor | 50 POE Load (A) | 271 | 268 | 265 | 263 | 263
Gympie Bulk | 339-3 | 339 Tee1 | 340 Tee1 | NCC Rating (A) | 322 | 322 | 322 | 322 | 322 | Rural | 170
Gympie Bulk | 339-3 | 339 Tee1 | 340 Tee1 | 10 POE Load (A) | 0.00034436 | 0.00034436 | 0.00034436 | 0.00034436 | 0.00034436
Gympie Bulk | 339-3 | 339 Tee1 | 340 Tee1 | Power Factor | 0.00059198 | 0.0005934 | 0.00059345 | 0.00059178 | 0.00059349
Gympie Bulk | 340-1 | Gympie BS | 340 Tee1 | NCC Rating (A) | 490 | 490 | 490 | 490 | 490 | Rural | 170
Gympie Bulk | 340-1 | Gympie BS | 340 Tee1 | 10 POE Load (A) | 57.1991 | 59.8476 | 60.0041 | 59.5423 | 59.6509
Gympie Bulk | 340-1 | Gympie BS | 340 Tee1 | Power Factor | 0.96876 | 0.96767 | 0.9676 | 0.96779 | 0.96775
Gympie Bulk | 340-1 | Gympie BS | 340 Tee1 | ECC Rating (A) | 490 | 490 | 490 | 490 | 490
Gympie Bulk | 340-1 | Gympie BS | 340 Tee1 | 50 POE Load (A) | 165 | 164 | 164 | 163 | 163
Gympie Bulk | 340-2 | 340 Tee1 | 339 Tee1 | NCC Rating (A) | 490 | 490 | 490 | 490 | 490 | Rural | 170
Gympie Bulk | 340-2 | 340 Tee1 | 339 Tee1 | 10 POE Load (A) | 0.001928 | 0.001928 | 0.001928 | 0.001928 | 0.001928
Gympie Bulk | 340-2 | 340 Tee1 | 339 Tee1 | Power Factor | 0.0001059 | 0.00010586 | 0.00010592 | 0.0001058 | 0.00010585
Gympie Bulk | 340-4 | 340 Tee1 | 340 Tee2 | NCC Rating (A) | 490 | 490 | 490 | 490 | 490 | Rural | 170
Gympie Bulk | 340-4 | 340 Tee1 | 340 Tee2 | 10 POE Load (A) | 57.2968 | 59.9466 | 60.1032 | 59.6411 | 59.7498
Gympie Bulk | 340-4 | 340 Tee1 | 340 Tee2 | Power Factor | 0.96816 | 0.96709 | 0.96702 | 0.96721 | 0.96717
Gympie Bulk | 340-4 | 340 Tee1 | 340 Tee2 | ECC Rating (A) | 490 | 490 | 490 | 490 | 490
Gympie Bulk | 340-4 | 340 Tee1 | 340 Tee2 | 50 POE Load (A) | 165 | 164 | 164 | 163 | 163
Gympie Bulk | 340-5 | 340 Tee2 | 340 Tee3 | NCC Rating (A) | 401 | 401 | 401 | 401 | 401 | Rural | 170
Gympie Bulk | 340-5 | 340 Tee2 | 340 Tee3 | 10 POE Load (A) | 3.4887 | 3.4881 | 3.4881 | 3.4882 | 3.4881
Gympie Bulk | 340-5 | 340 Tee2 | 340 Tee3 | Power Factor | 0.00076215 | 0.00076215 | 0.00076215 | 0.00076215 | 0.00076215
Gympie Bulk | 340-5 | 340 Tee2 | 340 Tee3 | ECC Rating (A) | 401 | 401 | 401 | 401 | 401
Gympie Bulk | 340-5 | 340 Tee2 | 340 Tee3 | 50 POE Load (A) | 4 | 4 | 4 | 4 | 4
Gympie Bulk | 340-6 | 340 Tee3 | 339 Tee2 | NCC Rating (A) | 912 | 912 | 912 | 912 | 912 | Rural | 170
Gympie Bulk | 340-6 | 340 Tee3 | 339 Tee2 | 10 POE Load (A) | 1.5752 | 1.575 | 1.575 | 1.575 | 1.575
Gympie Bulk | 340-6 | 340 Tee3 | 339 Tee2 | Power Factor | 0.00014067 | 0.00014067 | 0.00014067 | 0.00014067 | 0.00014067
Gympie Bulk | 340-6 | 340 Tee3 | 339 Tee2 | ECC Rating (A) | 912 | 912 | 912 | 912 | 912
Gympie Bulk | 340-6 | 340 Tee3 | 339 Tee2 | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Gympie Bulk | 340-7 | 339 Tee2 | Kenilworth | NCC Rating (A) | 416 | 416 | 416 | 416 | 416 | Rural | 170
Gympie Bulk | 340-7 | 339 Tee2 | Kenilworth | 10 POE Load (A) | 1.5715 | 1.5712 | 1.5712 | 1.5712 | 1.5712
Gympie Bulk | 340-7 | 339 Tee2 | Kenilworth | Power Factor | 0.0001403 | 0.0001403 | 0.0001403 | 0.0001403 | 0.0001403
Gympie Bulk | 340-7 | 339 Tee2 | Kenilworth | ECC Rating (A) | 416 | 416 | 416 | 416 | 416
Gympie Bulk | 340-7 | 339 Tee2 | Kenilworth | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Gympie Bulk | 340-8 | 340 Tee3 | Black Mountain | NCC Rating (A) | 401 | 401 | 401 | 401 | 401 | Rural | 170
Gympie Bulk | 340-8 | 340 Tee3 | Black Mountain | 10 POE Load (A) | 0.61368 | 0.61358 | 0.61357 | 0.61359 | 0.61359
Gympie Bulk | 340-8 | 340 Tee3 | Black Mountain | Power Factor | 4.3695e-05 | 4.3695e-05 | 4.3695e-05 | 4.3695e-05 | 4.3695e-05
Gympie Bulk | 340-9 | 340 Tee2 | Gympie South | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170
Gympie Bulk | 340-9 | 340 Tee2 | Gympie South | 10 POE Load (A) | 58.481 | 61.1392 | 61.2963 | 60.8327 | 60.9418
Gympie Bulk | 340-9 | 340 Tee2 | Gympie South | Power Factor | 0.9512 | 0.95079 | 0.95076 | 0.95084 | 0.95082
Gympie Bulk | 340-9 | 340 Tee2 | Gympie South | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
Gympie Bulk | 340-9 | 340 Tee2 | Gympie South | 50 POE Load (A) | 171 | 170 | 170 | 169 | 169
Gympie Bulk | 341-1 | Gympie BS | 341 Tee1 | NCC Rating (A) | 455 | 455 | 455 | 455 | 455 | Rural | 170
Gympie Bulk | 341-1 | Gympie BS | 341 Tee1 | 10 POE Load (A) | 136.0312 | 135.704 | 135.9317 | 135.8551 | 136.3026
Gympie Bulk | 341-1 | Gympie BS | 341 Tee1 | Power Factor | 0.99997 | 0.99996 | 0.99997 | 0.99997 | 0.99997
Gympie Bulk | 341-1 | Gympie BS | 341 Tee1 | ECC Rating (A) | 194 | 194 | 194 | 194 | 194
Gympie Bulk | 341-1 | Gympie BS | 341 Tee1 | 50 POE Load (A) | 416 | 415 | 414 | 412 | 412
Gympie Bulk | 341-2 | 341 Tee1 | Customer | NCC Rating (A) | 454 | 454 | 454 | 454 | 454 | Rural | 170
Gympie Bulk | 341-2 | 341 Tee1 | Customer | 10 POE Load (A) | 71.698 | 71.8205 | 71.6324 | 71.5912 | 71.268
Gympie Bulk | 341-2 | 341 Tee1 | Customer | Power Factor | 0.98851 | 0.98874 | 0.98851 | 0.98851 | 0.98807
Gympie Bulk | 341-2 | 341 Tee1 | Customer | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
Gympie Bulk | 341-2 | 341 Tee1 | Customer | 50 POE Load (A) | 300.2814 | 299.4495 | 298.4187 | 297.63 | 297.63
Gympie Bulk | 341-3 | 341 Tee1 | Coondoo Ck Reg | NCC Rating (A) | 292 | 292 | 292 | 292 | 292 | Rural | 170
Gympie Bulk | 341-3 | 341 Tee1 | Coondoo Ck Reg | 10 POE Load (A) | 67.6677 | 67.1866 | 67.6521 | 67.6283 | 68.4852
Gympie Bulk | 341-3 | 341 Tee1 | Coondoo Ck Reg | Power Factor | 0.9997 | 0.99974 | 0.9997 | 0.9997 | 0.99962
Gympie Bulk | 341-3 | 341 Tee1 | Coondoo Ck Reg | ECC Rating (A) | 292 | 292 | 292 | 292 | 292
Gympie Bulk | 341-3 | 341 Tee1 | Coondoo Ck Reg | 50 POE Load (A) | 219 | 218 | 216 | 215 | 215
Gympie Bulk | 341-4 | Coondoo Ck Reg | 341 Tee2 | NCC Rating (A) | 926 | 926 | 926 | 926 | 926 | Rural | 170
Gympie Bulk | 341-4 | Coondoo Ck Reg | 341 Tee2 | 10 POE Load (A) | 65.2223 | 64.7585 | 65.2072 | 65.1843 | 66.0103
Gympie Bulk | 341-4 | Coondoo Ck Reg | 341 Tee2 | Power Factor | 0.9997 | 0.99974 | 0.9997 | 0.9997 | 0.99963
Gympie Bulk | 341-4 | Coondoo Ck Reg | 341 Tee2 | ECC Rating (A) | 926 | 926 | 926 | 926 | 926
Gympie Bulk | 341-4 | Coondoo Ck Reg | 341 Tee2 | 50 POE Load (A) | 173 | 172 | 171 | 169 | 169
Gympie Bulk | 351-1 | Gympie BS | Gympie Sth | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Rural | 170
Gympie Bulk | 351-1 | Gympie BS | Gympie Sth | 10 POE Load (A) | 65.9807 | 69.028 | 69.208 | 68.6766 | 68.8016
Gympie Bulk | 351-1 | Gympie BS | Gympie Sth | Power Factor | 0.96453 | 0.9634 | 0.96333 | 0.96353 | 0.96348
Gympie Bulk | 351-1 | Gympie BS | Gympie Sth | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
Gympie Bulk | 351-1 | Gympie BS | Gympie Sth | 50 POE Load (A) | 171 | 170 | 169 | 169 | 169
Gympie Bulk | 429-1 | Gympie BS | 429 Tee1 | NCC Rating (A) | 786 | 786 | 786 | 786 | 786 | Rural | 170
Gympie Bulk | 429-1 | Gympie BS | 429 Tee1 | 10 POE Load (A) | 194.2101 | 193.6059 | 193.8948 | 193.6641 | 194.2909
Gympie Bulk | 429-1 | Gympie BS | 429 Tee1 | Power Factor | 0.97971 | 0.97978 | 0.97971 | 0.97971 | 0.97958
Gympie Bulk | 429-1 | Gympie BS | 429 Tee1 | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Gympie Bulk | 429-1 | Gympie BS | 429 Tee1 | 50 POE Load (A) | 516 | 514 | 512 | 510 | 510
Gympie Bulk | 429-2 | 429 Tee1 | Goomboorian | NCC Rating (A) | 492 | 492 | 492 | 492 | 492 | Rural | 170
Gympie Bulk | 429-2 | 429 Tee1 | Goomboorian | 10 POE Load (A) | 41.9446 | 41.5326 | 41.5558 | 41.2805 | 41.444
Gympie Bulk | 429-2 | 429 Tee1 | Goomboorian | Power Factor | 0.99729 | 0.99731 | 0.99731 | 0.99732 | 0.99731
Gympie Bulk | 429-2 | 429 Tee1 | Goomboorian | ECC Rating (A) | 492 | 492 | 492 | 492 | 492
Gympie Bulk | 429-2 | 429 Tee1 | Goomboorian | 50 POE Load (A) | 42 | 42 | 42 | 41 | 41
Gympie Bulk | 429-3 | 429 Tee1 | Toolara Forest | NCC Rating (A) | 454 | 454 | 454 | 454 | 454 | Rural | 170
Gympie Bulk | 429-3 | 429 Tee1 | Toolara Forest | 10 POE Load (A) | 152.6706 | 152.4757 | 152.7432 | 152.7872 | 153.2542
Gympie Bulk | 429-3 | 429 Tee1 | Toolara Forest | Power Factor | 0.98574 | 0.98581 | 0.98576 | 0.98578 | 0.98568
Gympie Bulk | 429-3 | 429 Tee1 | Toolara Forest | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
Gympie Bulk | 429-3 | 429 Tee1 | Toolara Forest | 50 POE Load (A) | 352 | 351 | 349 | 348 | 347
Hays Inlet Bulk | 305-1 | Hays Inlet BS | Deception Bay | NCC Rating (A) | 759 | 759 | 759 | 759 | 759 | Urban | 266
Hays Inlet Bulk | 305-1 | Hays Inlet BS | Deception Bay | 10 POE Load (A) | 489.9462 | 488.4033 | 493.8439 | 495.8384 | 503.6364
Hays Inlet Bulk | 305-1 | Hays Inlet BS | Deception Bay | Power Factor | 0.98955 | 0.98959 | 0.98937 | 0.98927 | 0.98895
Hays Inlet Bulk | 305-1 | Hays Inlet BS | Deception Bay | ECC Rating (A) | 759 | 759 | 759 | 759 | 759
Hays Inlet Bulk | 305-1 | Hays Inlet BS | Deception Bay | 50 POE Load (A) | 674 | 675 | 676 | 678 | 678
Hays Inlet Bulk | 311-1 | Hays Inlet BS | Deception Bay | NCC Rating (A) | 681 | 681 | 681 | 681 | 681 | Urban | 154 | 0.5
Hays Inlet Bulk | 311-1 | Hays Inlet BS | Deception Bay | 10 POE Load (A) | 161.7133 | 161.2037 | 163.0004 | 163.659 | 166.2342
Hays Inlet Bulk | 311-1 | Hays Inlet BS | Deception Bay | Power Factor | -0.99469 | -0.99472 | -0.99458 | -0.99451 | -0.9943
Hays Inlet Bulk | 311-1 | Hays Inlet BS | Deception Bay | ECC Rating (A) | 681 | 681 | 681 | 681 | 681
Hays Inlet Bulk | 311-1 | Hays Inlet BS | Deception Bay | 50 POE Load (A) | 529 | 530 | 530 | 530 | 530
Hays Inlet Bulk | 3250-1 | Deception Bay | Burpengary | NCC Rating (A) | 921 | 921 | 921 | 921 | 921 | Urban | 256
Hays Inlet Bulk | 3250-1 | Deception Bay | Burpengary | 10 POE Load (A) | 294.6063 | 293.2193 | 296.6261 | 298.4514 | 303.8814
Hays Inlet Bulk | 3250-1 | Deception Bay | Burpengary | Power Factor | 0.992 | 0.99203 | 0.99188 | 0.9918 | 0.99157
Hays Inlet Bulk | 3250-1 | Deception Bay | Burpengary | ECC Rating (A) | 921 | 921 | 921 | 921 | 921
Hays Inlet Bulk | 3250-1 | Deception Bay | Burpengary | 50 POE Load (A) | 746 | 748 | 750 | 754 | 754
Hays Inlet Bulk | 325-1 | Hays Inlet BS | Scarborough | NCC Rating (A) | 734 | 734 | 734 | 734 | 734 | Urban | 70
Hays Inlet Bulk | 325-1 | Hays Inlet BS | Scarborough | 10 POE Load (A) | 247.19 | 247.5317 | 250.8911 | 252.242 | 256.3233
Hays Inlet Bulk | 325-1 | Hays Inlet BS | Scarborough | Power Factor | 0.99658 | 0.99659 | 0.99656 | 0.99657 | 0.99653
Hays Inlet Bulk | 325-1 | Hays Inlet BS | Scarborough | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Hays Inlet Bulk | 325-1 | Hays Inlet BS | Scarborough | 50 POE Load (A) | 448 | 449 | 451 | 453 | 453
Hays Inlet Bulk | 3251-1 | Burpengary | Morayfield | NCC Rating (A) | 508 | 508 | 508 | 508 | 508 | Rural | 170
Hays Inlet Bulk | 3251-1 | Burpengary | Morayfield | 10 POE Load (A) | 1.2125 | 1.2126 | 1.2122 | 1.212 | 1.2115
Hays Inlet Bulk | 3251-1 | Burpengary | Morayfield | Power Factor | 4.3786e-07 | 4.3773e-07 | 4.3773e-07 | 4.3772e-07 | 4.3772e-07
Hays Inlet Bulk | 3251-1 | Burpengary | Morayfield | ECC Rating (A) | 508 | 508 | 508 | 508 | 508
Hays Inlet Bulk | 3251-1 | Burpengary | Morayfield | 50 POE Load (A) | 382 | 394 | 398 | 402 | 402
Hays Inlet Bulk | 326-1 | Redcliffe | Scarborough | NCC Rating (A) | 688 | 688 | 688 | 688 | 688 | Urban | 70
Hays Inlet Bulk | 326-1 | Redcliffe | Scarborough | 10 POE Load (A) | 32.606 | 34.2618 | 36.3436 | 38.5723 | 41.1308
Hays Inlet Bulk | 326-1 | Redcliffe | Scarborough | Power Factor | 0.99833 | 0.99798 | 0.99764 | 0.99721 | 0.99683
Hays Inlet Bulk | 326-1 | Redcliffe | Scarborough | ECC Rating (A) | 785 | 785 | 785 | 785 | 785
Hays Inlet Bulk | 326-1 | Redcliffe | Scarborough | 50 POE Load (A) | 577 | 583 | 588 | 593 | 593
Hays Inlet Bulk | 327-1 | Hays Inlet BS | Mango Hill Bus 1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Hays Inlet Bulk | 327-1 | Hays Inlet BS | Mango Hill Bus 1 | 10 POE Load (A) | 270.7735 | 274.2968 | 282.461 | 288.1571 | 297.3145
Hays Inlet Bulk | 327-1 | Hays Inlet BS | Mango Hill Bus 1 | Power Factor | -0.96993 | -0.96964 | -0.96896 | -0.96848 | -0.96828
Hays Inlet Bulk | 327-1 | Hays Inlet BS | Mango Hill Bus 1 | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Hays Inlet Bulk | 327-1 | Hays Inlet BS | Mango Hill Bus 1 | 50 POE Load (A) | 231 | 233 | 235 | 238 | 238
Hays Inlet Bulk | 329-1 | Redcliffe | Duffield Rd | NCC Rating (A) | 688 | 688 | 688 | 688 | 688 | Urban | 70
Hays Inlet Bulk | 329-1 | Redcliffe | Duffield Rd | 10 POE Load (A) | 67.9803 | 68.5154 | 70.0632 | 70.9527 | 72.1774
Hays Inlet Bulk | 329-1 | Redcliffe | Duffield Rd | Power Factor | 0.99666 | 0.99655 | 0.99644 | 0.99632 | 0.99632
Hays Inlet Bulk | 329-1 | Redcliffe | Duffield Rd | ECC Rating (A) | 864 | 864 | 864 | 864 | 864
Hays Inlet Bulk | 329-1 | Redcliffe | Duffield Rd | 50 POE Load (A) | 274 | 275 | 275 | 276 | 276
Hays Inlet Bulk | 330-1 | Hays Inlet BS | Duffield Rd | NCC Rating (A) | 595 | 595 | 595 | 595 | 595 | Urban | 70
Hays Inlet Bulk | 330-1 | Hays Inlet BS | Duffield Rd | 10 POE Load (A) | 226.5398 | 225.9389 | 227.9698 | 228.0761 | 230.987
Hays Inlet Bulk | 330-1 | Hays Inlet BS | Duffield Rd | Power Factor | -0.98962 | -0.98967 | -0.98955 | -0.98956 | -0.98939
Hays Inlet Bulk | 330-1 | Hays Inlet BS | Duffield Rd | ECC Rating (A) | 864 | 864 | 864 | 864 | 864
Hays Inlet Bulk | 330-1 | Hays Inlet BS | Duffield Rd | 50 POE Load (A) | 464 | 464 | 463 | 463 | 463
Hays Inlet Bulk | 331-1 | Hays Inlet BS | Duffield Rd | NCC Rating (A) | 293 | 293 | 430 | 430 | 430 | Urban | 70
Hays Inlet Bulk | 331-1 | Hays Inlet BS | Duffield Rd | 10 POE Load (A) | 227.7228 | 227.1188 | 229.1682 | 229.275 | 232.2012
Hays Inlet Bulk | 331-1 | Hays Inlet BS | Duffield Rd | Power Factor | -0.98705 | -0.98711 | -0.98698 | -0.98699 | -0.9868
Hays Inlet Bulk | 331-1 | Hays Inlet BS | Duffield Rd | ECC Rating (A) | 864 | 864 | 864 | 864 | 864
Hays Inlet Bulk | 331-1 | Hays Inlet BS | Duffield Rd | 50 POE Load (A) | 465 | 464 | 461 | 461 | 461
Hays Inlet Bulk | 332-1 | Hays Inlet BS | Redcliffe | NCC Rating (A) | 677 | 677 | 677 | 677 | 677 | Urban | 70
Hays Inlet Bulk | 332-1 | Hays Inlet BS | Redcliffe | 10 POE Load (A) | 229.8822 | 229.6883 | 232.2932 | 232.8991 | 236.0549
Hays Inlet Bulk | 332-1 | Hays Inlet BS | Redcliffe | Power Factor | 0.98517 | 0.9852 | 0.98509 | 0.98508 | 0.98493
Hays Inlet Bulk | 332-1 | Hays Inlet BS | Redcliffe | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Hays Inlet Bulk | 332-1 | Hays Inlet BS | Redcliffe | 50 POE Load (A) | 474 | 475 | 477 | 478 | 478
Hays Inlet Bulk | 451-1 | Narangba | Burpengary | NCC Rating (A) | 489 | 489 | 489 | 489 | 489 | Urban | 70
Hays Inlet Bulk | 451-1 | Narangba | Burpengary | 10 POE Load (A) | 26.6329 | 27.0744 | 28.1115 | 29.0302 | 30.5159
Hays Inlet Bulk | 451-1 | Narangba | Burpengary | Power Factor | 0.84971 | 0.83545 | 0.81637 | 0.81291 | 0.8183
Hays Inlet Bulk | 451-1 | Narangba | Burpengary | ECC Rating (A) | 489 | 489 | 489 | 489 | 489
Hays Inlet Bulk | 451-1 | Narangba | Burpengary | 50 POE Load (A) | 369 | 371 | 373 | 376 | 376
Hays Inlet Bulk | 497-1 | Hays Inlet BS | Narangba | NCC Rating (A) | 720 | 720 | 720 | 720 | 720 | Rural | 170
Hays Inlet Bulk | 497-1 | Hays Inlet BS | Narangba | 10 POE Load (A) | 340.3276 | 339.2427 | 343.5639 | 345.9029 | 352.4945
Hays Inlet Bulk | 497-1 | Hays Inlet BS | Narangba | Power Factor | -0.97815 | -0.97818 | -0.97786 | -0.97766 | -0.97717
Hays Inlet Bulk | 497-1 | Hays Inlet BS | Narangba | ECC Rating (A) | 921 | 921 | 921 | 921 | 921
Hays Inlet Bulk | 497-1 | Hays Inlet BS | Narangba | 50 POE Load (A) | 741 | 742 | 745 | 748 | 748
Jimboomba Bulk | 470-1 | Jimboomba BS | Logan Village | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Rural | 170
Jimboomba Bulk | 470-1 | Jimboomba BS | Logan Village | 10 POE Load (A) | 249.1883 | 252.7947 | 260.5828 | 266.4597 | 275.6339
Jimboomba Bulk | 470-1 | Jimboomba BS | Logan Village | Power Factor | 0.9887 | 0.98851 | 0.98808 | 0.98775 | 0.98681
Jimboomba Bulk | 479-1 | Jimboomba BS | Nth Maclean | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Jimboomba Bulk | 479-1 | Jimboomba BS | Nth Maclean | 10 POE Load (A) | 421.3525 | 418.2421 | 431.0264 | 441.2508 | 457.9415
Jimboomba Bulk | 479-1 | Jimboomba BS | Nth Maclean | Power Factor | 0.99349 | 0.99357 | 0.99332 | 0.99312 | 0.99279
Jimboomba Bulk | 479-1 | Jimboomba BS | Nth Maclean | ECC Rating (A) | 0 | 0 | 0 | 0 | 0
Jimboomba Bulk | 479-1 | Jimboomba BS | Nth Maclean | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lockrose Bulk | 378-1 | Lockrose BS | 378 Tee1 | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
Lockrose Bulk | 378-1 | Lockrose BS | 378 Tee1 | 10 POE Load (A) | 172.2026 | 140.4789 | 141.491 | 150.9739 | 184.8896
Lockrose Bulk | 378-1 | Lockrose BS | 378 Tee1 | Power Factor | -0.95672 | -0.95697 | -0.95676 | -0.95426 | -0.94656
Lockrose Bulk | 378-1 | Lockrose BS | 378 Tee1 | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
Lockrose Bulk | 378-1 | Lockrose BS | 378 Tee1 | 50 POE Load (A) | 271 | 232 | 233 | 234 | 234
Lockrose Bulk | 378-2 | 378 Tee1 | Glenmore Grove | NCC Rating (A) | 818 | 442 | 442 | 442 | 442 | Rural | 170
Lockrose Bulk | 378-2 | 378 Tee1 | Glenmore Grove | 10 POE Load (A) | 94.0379 | 61.2808 | 61.5877 | 61.4102 | 65.9708
Lockrose Bulk | 378-2 | 378 Tee1 | Glenmore Grove | Power Factor | -0.96628 | -0.95975 | -0.9597 | -0.95972 | -0.959
Lockrose Bulk | 378-2 | 378 Tee1 | Glenmore Grove | ECC Rating (A) | 800 | 473 | 473 | 473 | 473
Lockrose Bulk | 378-2 | 378 Tee1 | Glenmore Grove | 50 POE Load (A) | 119 | 85 | 85 | 85 | 85
Lockrose Bulk | 378-3 | 378 Tee1 | 378 Tee2 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Lockrose Bulk | 378-3 | 378 Tee1 | 378 Tee2 | 10 POE Load (A) | 79.9763 | 79.552 | 80.2588 | 89.944 | 119.3846
Lockrose Bulk | 378-3 | 378 Tee1 | 378 Tee2 | Power Factor | 0.94897 | 0.95925 | 0.95905 | 0.95627 | 0.94725
Lockrose Bulk | 378-3 | 378 Tee1 | 378 Tee2 | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Lockrose Bulk | 378-3 | 378 Tee1 | 378 Tee2 | 50 POE Load (A) | 152 | 152 | 154 | 154 | 154
Lockrose Bulk | 378-4 | 378 Tee2 | 532 Tee1 | NCC Rating (A) | 416 | 416 | 416 | 416 | 416 | Rural | 170
Lockrose Bulk | 378-4 | 378 Tee2 | 532 Tee1 | 10 POE Load (A) | 0.88685 | 0.90066 | 0.90047 | 0.89797 | 0.88961
Lockrose Bulk | 378-4 | 378 Tee2 | 532 Tee1 | Power Factor | -5.6276e-06 | -5.6276e-06 | -5.6276e-06 | -5.6276e-06 | -5.6276e-06
Lockrose Bulk | 378-5 | 378 Tee2 | Laidley | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Lockrose Bulk | 378-5 | 378 Tee2 | Laidley | 10 POE Load (A) | 80.288 | 79.8379 | 80.545 | 90.2357 | 119.6888
Lockrose Bulk | 378-5 | 378 Tee2 | Laidley | Power Factor | 0.9448 | 0.95496 | 0.95482 | 0.9529 | 0.94788
Lockrose Bulk | 378-5 | 378 Tee2 | Laidley | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Lockrose Bulk | 378-5 | 378 Tee2 | Laidley | 50 POE Load (A) | 153 | 153 | 154 | 155 | 155
Lockrose Bulk | 380-1 | Murrumba | 380 Tee1 | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
Lockrose Bulk | 380-1 | Murrumba | 380 Tee1 | 10 POE Load (A) | 45.4101 | 38.6499 | 38.8636 | 38.8409 | 39.3388
Lockrose Bulk | 380-1 | Murrumba | 380 Tee1 | Power Factor | 0.95038 | 0.97396 | 0.97382 | 0.97388 | 0.97347
Lockrose Bulk | 380-1 | Murrumba | 380 Tee1 | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
Lockrose Bulk | 380-1 | Murrumba | 380 Tee1 | 50 POE Load (A) | 244 | 244 | 244 | 244 | 244
Lockrose Bulk | 380-2 | 380 Tee1 | Somerset Dam | NCC Rating (A) | 324 | 324 | 324 | 324 | 324 | Rural | 170
Lockrose Bulk | 380-2 | 380 Tee1 | Somerset Dam | 10 POE Load (A) | 5.0549 | 4.9742 | 5.0325 | 5.0837 | 5.1483
Lockrose Bulk | 380-2 | 380 Tee1 | Somerset Dam | Power Factor | 0.99973 | 0.99979 | 0.99977 | 0.99976 | 0.99974
Lockrose Bulk | 380-2 | 380 Tee1 | Somerset Dam | ECC Rating (A) | 324 | 324 | 324 | 324 | 324
Lockrose Bulk | 380-2 | 380 Tee1 | Somerset Dam | 50 POE Load (A) | 15 | 15 | 15 | 15 | 15
Lockrose Bulk | 380-3 | 380 Tee1 | Toogoolahwah | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
Lockrose Bulk | 380-3 | 380 Tee1 | Toogoolahwah | 10 POE Load (A) | 40.9906 | 34.1324 | 34.2894 | 34.2169 | 34.6512
Lockrose Bulk | 380-3 | 380 Tee1 | Toogoolahwah | Power Factor | 0.93708 | 0.96328 | 0.96309 | 0.96299 | 0.96277
Lockrose Bulk | 380-3 | 380 Tee1 | Toogoolahwah | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
Lockrose Bulk | 380-3 | 380 Tee1 | Toogoolahwah | 50 POE Load (A) | 230 | 231 | 230 | 230 | 230
Lockrose Bulk | 381-1 | Lockrose BS | 381 Tee1 | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
Lockrose Bulk | 381-1 | Lockrose BS | 381 Tee1 | 10 POE Load (A) | 135.9112 | 141.8776 | 143.2338 | 142.9401 | 152.2999
Lockrose Bulk | 381-1 | Lockrose BS | 381 Tee1 | Power Factor | 0.9701 | 0.95079 | 0.95048 | 0.95059 | 0.94966
Lockrose Bulk | 381-1 | Lockrose BS | 381 Tee1 | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
Lockrose Bulk | 381-1 | Lockrose BS | 381 Tee1 | 50 POE Load (A) | 301 | 278 | 277 | 277 | 277
Lockrose Bulk | 381-2 | 381 Tee1 | 382 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Lockrose Bulk | 381-2 | 381 Tee1 | 382 Tee1 | 10 POE Load (A) | 0.0059127 | 0.0059691 | 0.0059689 | 0.005969 | 0.0059681
Lockrose Bulk | 381-2 | 381 Tee1 | 382 Tee1 | Power Factor | -1 | -1 | -1 | -1 | -1
Lockrose Bulk | 381-3 | 381 Tee1 | 381 Tee2 | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
Lockrose Bulk | 381-3 | 381 Tee1 | 381 Tee2 | 10 POE Load (A) | 136.0153 | 142.0127 | 143.3692 | 143.0754 | 152.4361
Lockrose Bulk | 381-3 | 381 Tee1 | 381 Tee2 | Power Factor | 0.97311 | 0.95445 | 0.9542 | 0.9543 | 0.95376
Lockrose Bulk | 381-3 | 381 Tee1 | 381 Tee2 | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
Lockrose Bulk | 381-3 | 381 Tee1 | 381 Tee2 | 50 POE Load (A) | 301 | 278 | 278 | 277 | 277
Lockrose Bulk | 381-4 | 381 Tee2 | 383 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Lockrose Bulk | 381-4 | 381 Tee2 | 383 Tee1 | 10 POE Load (A) | 0.0057512 | 0.0057972 | 0.005796 | 0.0057963 | 0.0057878
Lockrose Bulk | 381-4 | 381 Tee2 | 383 Tee1 | Power Factor | 3.3857e-05 | 3.3848e-05 | 3.3853e-05 | 3.3856e-05 | 3.3847e-05
Lockrose Bulk | 381-5 | 381 Tee2 | 381 Tee3 | NCC Rating (A) | 293 | 582 | 582 | 582 | 582 | Rural | 170
Lockrose Bulk | 381-5 | 381 Tee2 | 381 Tee3 | 10 POE Load (A) | 136.1504 | 142.2109 | 143.5679 | 143.2739 | 152.6347
Lockrose Bulk | 381-5 | 381 Tee2 | 381 Tee3 | Power Factor | 0.97319 | 0.95455 | 0.9543 | 0.9544 | 0.95387
Lockrose Bulk | 381-5 | 381 Tee2 | 381 Tee3 | ECC Rating (A) | 293 | 818 | 818 | 818 | 818
Lockrose Bulk | 381-5 | 381 Tee2 | 381 Tee3 | 50 POE Load (A) | 301 | 411 | 411 | 410 | 410
Lockrose Bulk | 381-6 | 381 Tee3 | Coominya TR2 | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170
Lockrose Bulk | 381-6 | 381 Tee3 | Coominya TR2 | 10 POE Load (A) | 47.1166 | 45.7833 | 46.4409 | 46.4419 | 52.5933
Lockrose Bulk | 381-6 | 381 Tee3 | Coominya TR2 | Power Factor | 0.97258 | 0.97257 | 0.97248 | 0.97248 | 0.97172
Lockrose Bulk | 381-6 | 381 Tee3 | Coominya TR2 | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
Lockrose Bulk | 381-6 | 381 Tee3 | Coominya TR2 | 50 POE Load (A) | 89 | 84 | 83 | 83 | 83
Lockrose Bulk | 381-7 | 381 Tee3 | 381 Tee4 | NCC Rating (A) | 293 | 582 | 582 | 582 | 582 | Rural | 170
Lockrose Bulk | 381-7 | 381 Tee3 | 381 Tee4 | 10 POE Load (A) | 89.0543 | 96.5041 | 97.2052 | 96.9095 | 100.1171
Lockrose Bulk | 381-7 | 381 Tee3 | 381 Tee4 | Power Factor | 0.98001 | 0.95363 | 0.95339 | 0.95349 | 0.95351
Lockrose Bulk | 381-7 | 381 Tee3 | 381 Tee4 | ECC Rating (A) | 293 | 582 | 582 | 582 | 582
Lockrose Bulk | 381-7 | 381 Tee3 | 381 Tee4 | 50 POE Load (A) | 240 | 220 | 220 | 220 | 220
Lockrose Bulk | 381-8 | 381 Tee4 | Coominya TR1 | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170
Lockrose Bulk | 381-8 | 381 Tee4 | Coominya TR1 | 10 POE Load (A) | 47.1616 | 45.8192 | 46.4757 | 46.4766 | 52.6161
Lockrose Bulk | 381-8 | 381 Tee4 | Coominya TR1 | Power Factor | 0.97193 | 0.97192 | 0.97186 | 0.97186 | 0.97129
Lockrose Bulk | 381-8 | 381 Tee4 | Coominya TR1 | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
Lockrose Bulk | 381-8 | 381 Tee4 | Coominya TR1 | 50 POE Load (A) | 62 | 58 | 58 | 58 | 58
Lockrose Bulk | 381-9 | 381 Tee4 | Paddys Gully | NCC Rating (A) | 293 | 432 | 432 | 432 | 432 | Rural | 170
Lockrose Bulk | 381-9 | 381 Tee4 | Paddys Gully | 10 POE Load (A) | 42.1329 | 51.2675 | 51.3211 | 51.0229 | 48.1271
Lockrose Bulk | 381-9 | 381 Tee4 | Paddys Gully | Power Factor | 0.98776 | 0.93372 | 0.93298 | 0.93308 | 0.92975
Lockrose Bulk | 381-9 | 381 Tee4 | Paddys Gully | ECC Rating (A) | 293 | 432 | 432 | 432 | 432
Lockrose Bulk | 381-9 | 381 Tee4 | Paddys Gully | 50 POE Load (A) | 374 | 390 | 390 | 390 | 390
Lockrose Bulk | 382-1 | Lockrose BS | 382 Tee1 | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
Lockrose Bulk | 382-1 | Lockrose BS | 382 Tee1 | 10 POE Load (A) | 138.3531 | 122.7817 | 123.7235 | 123.368 | 128.1557
Lockrose Bulk | 382-1 | Lockrose BS | 382 Tee1 | Power Factor | 0.93133 | 0.9572 | 0.95686 | 0.95698 | 0.95623
Lockrose Bulk | 382-1 | Lockrose BS | 382 Tee1 | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
Lockrose Bulk | 382-1 | Lockrose BS | 382 Tee1 | 50 POE Load (A) | 170 | 168 | 168 | 168 | 168
Lockrose Bulk | 382-2 | 382 Tee1 | 381 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Lockrose Bulk | 382-2 | 382 Tee1 | 381 Tee1 | 10 POE Load (A) | 0.010198 | 0.0103 | 0.010299 | 0.010299 | 0.010299
Lockrose Bulk | 382-2 | 382 Tee1 | 381 Tee1 | Power Factor | 1.9412e-05 | 1.9414e-05 | 1.9413e-05 | 1.9414e-05 | 1.9414e-05
Lockrose Bulk | 382-3 | 382 Tee1 | Paddys Gully | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
Lockrose Bulk | 382-3 | 382 Tee1 | Paddys Gully | 10 POE Load (A) | 138.9384 | 123.2503 | 124.1935 | 123.8374 | 128.6267
Lockrose Bulk | 382-3 | 382 Tee1 | Paddys Gully | Power Factor | 0.94497 | 0.96697 | 0.96678 | 0.96685 | 0.96682
Lockrose Bulk | 382-3 | 382 Tee1 | Paddys Gully | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
Lockrose Bulk | 382-3 | 382 Tee1 | Paddys Gully | 50 POE Load (A) | 170 | 169 | 169 | 169 | 169
Lockrose Bulk | 3828-1 | Paddy's Gully | Esk | NCC Rating (A) | 293 | 817 | 817 | 817 | 817 | Rural | 170
Lockrose Bulk | 3828-1 | Paddy's Gully | Esk | 10 POE Load (A) | 75.4005 | 76.9551 | 77.1661 | 76.8214 | 77.653
Lockrose Bulk | 3828-1 | Paddy's Gully | Esk | Power Factor | 0.98905 | 0.98097 | 0.98088 | 0.98093 | 0.9808
Lockrose Bulk | 3828-1 | Paddy's Gully | Esk | ECC Rating (A) | 293 | 912 | 912 | 912 | 912
Lockrose Bulk | 3828-1 | Paddy's Gully | Esk | 50 POE Load (A) | 321 | 215 | 215 | 215 | 215
Lockrose Bulk | 3829-1 | Paddy's Gully | Murrumba | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
Lockrose Bulk | 3829-1 | Paddy's Gully | Murrumba | 10 POE Load (A) | 97.8969 | 89.641 | 90.3771 | 90.0977 | 91.0326
Lockrose Bulk | 3829-1 | Paddy's Gully | Murrumba | Power Factor | 0.91846 | 0.9304 | 0.9301 | 0.93023 | 0.93004
Lockrose Bulk | 3829-1 | Paddy's Gully | Murrumba | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
Lockrose Bulk | 3829-1 | Paddy's Gully | Murrumba | 50 POE Load (A) | 303 | 303 | 303 | 302 | 302
Lockrose Bulk | 3831-1 | Lockrose BS | Tarampa | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Rural | 170
Lockrose Bulk | 3831-1 | Lockrose BS | Tarampa | 10 POE Load (A) | 112.2356 | 109.9583 | 110.7824 | 110.9742 | 112.33
Lockrose Bulk | 3831-1 | Lockrose BS | Tarampa | Power Factor | 0.96906 | 0.9691 | 0.96913 | 0.96912 | 0.96906
Lockrose Bulk | 3831-1 | Lockrose BS | Tarampa | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
Lockrose Bulk | 3831-1 | Lockrose BS | Tarampa | 50 POE Load (A) | 143 | 142 | 142 | 142 | 142
Lockrose Bulk | 3832-1 | Tarampa | 383 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Lockrose Bulk | 3832-1 | Tarampa | 383 Tee1 | 10 POE Load (A) | 0.0052203 | 0.0052752 | 0.0052747 | 0.005275 | 0.005274
Lockrose Bulk | 3832-1 | Tarampa | 383 Tee1 | Power Factor | -1 | -1 | -1 | -1 | -1
Lockrose Bulk | 3832-2 | 3832 Tee1 | 381 Tee1 | NCC Rating (A) | #N/A | #N/A | #N/A | #N/A | #N/A | Rural | 170
Lockrose Bulk | 3832-2 | 3832 Tee1 | 381 Tee1 | 10 POE Load (A) | #N/A | #N/A | #N/A | #N/A | #N/A
Lockrose Bulk | 3832-2 | 3832 Tee1 | 381 Tee1 | Power Factor | #N/A | #N/A | #N/A | #N/A | #N/A
Lockrose Bulk | 3832-3 | 3832 Tee1 | Lowood | NCC Rating (A) | 455 | 455 | 455 | 455 | 455 | Rural | 170
Lockrose Bulk | 3832-3 | 3832 Tee1 | Lowood | 10 POE Load (A) | 0.7379 | 0.74565 | 0.74559 | 0.74563 | 0.74549
Lockrose Bulk | 3832-3 | 3832 Tee1 | Lowood | Power Factor | -8.0548e-06 | -8.0547e-06 | -8.0548e-06 | -8.0548e-06 | -8.0548e-06
Lockrose Bulk | 3832-3 | 3832 Tee1 | Lowood | ECC Rating (A) | 434 | 434 | 434 | 434 | 434
Lockrose Bulk | 3832-3 | 3832 Tee1 | Lowood | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lockrose Bulk | 3840-1 | Esk | Toogoolawah | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
Lockrose Bulk | 3840-1 | Esk | Toogoolawah | 10 POE Load (A) | 32.6752 | 36.5467 | 36.8081 | 36.7785 | 37.2426
Lockrose Bulk | 3840-1 | Esk | Toogoolawah | Power Factor | 0.98339 | 0.96056 | 0.96047 | 0.96064 | 0.96057
Lockrose Bulk | 3840-1 | Esk | Toogoolawah | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
Lockrose Bulk | 3840-1 | Esk | Toogoolawah | 50 POE Load (A) | 255 | 248 | 248 | 248 | 248
Lockrose Bulk | 384-1 | Lockrose BS | 384 Tee1 | NCC Rating (A) | 451 | 451 | 451 | 451 | 451 | Rural | 170
Lockrose Bulk | 384-1 | Lockrose BS | 384 Tee1 | 10 POE Load (A) | 176.4968 | 145.9151 | 146.9668 | 156.8115 | 192.0387
Lockrose Bulk | 384-1 | Lockrose BS | 384 Tee1 | Power Factor | -0.95578 | -0.97844 | -0.97837 | -0.97831 | -0.97594
Lockrose Bulk | 384-1 | Lockrose BS | 384 Tee1 | ECC Rating (A) | 451 | 451 | 451 | 451 | 451
Lockrose Bulk | 384-1 | Lockrose BS | 384 Tee1 | 50 POE Load (A) | 272 | 190 | 191 | 192 | 192
Lockrose Bulk | 384-2 | 384 Tee1 | Glenmore Grove | NCC Rating (A) | 689 | 442 | 442 | 442 | 442 | Rural | 170
Lockrose Bulk | 384-2 | 384 Tee1 | Glenmore Grove | 10 POE Load (A) | 90.0858 | 61.174 | 61.4794 | 61.2851 | 65.7851
Lockrose Bulk | 384-2 | 384 Tee1 | Glenmore Grove | Power Factor | 0.90884 | 0.96456 | 0.9645 | 0.96452 | 0.9636
Lockrose Bulk | 384-2 | 384 Tee1 | Glenmore Grove | ECC Rating (A) | 689 | 689 | 689 | 689 | 689
Lockrose Bulk | 384-2 | 384 Tee1 | Glenmore Grove | 50 POE Load (A) | 279 | 89 | 89 | 89 | 89
Lockrose Bulk | 384-3 | 384 Tee1 | Laidley1 | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Rural | 170
Lockrose Bulk | 384-3 | 384 Tee1 | Laidley1 | 10 POE Load (A) | 88.8141 | 85.1444 | 85.8905 | 95.9044 | 126.5891
Lockrose Bulk | 384-3 | 384 Tee1 | Laidley1 | Power Factor | 0.9932 | 0.9899 | 0.98983 | 0.98895 | 0.98616
Lockrose Bulk | 384-3 | 384 Tee1 | Laidley1 | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
Lockrose Bulk | 384-3 | 384 Tee1 | Laidley1 | 50 POE Load (A) | 153 | 153 | 154 | 155 | 155
Lockrose Bulk | 3870-1 | Lockrose BS | Lowood | NCC Rating (A) | 898 | 898 | 898 | 898 | 898 | Rural | 170
Lockrose Bulk | 3870-1 | Lockrose BS | Lowood | 10 POE Load (A) | 116.1959 | 113.4561 | 113.8415 | 113.6106 | 114.4917
Lockrose Bulk | 3870-1 | Lockrose BS | Lowood | Power Factor | 0.97938 | 0.97966 | 0.97962 | 0.97964 | 0.97957
Lockrose Bulk | 3870-1 | Lockrose BS | Lowood | ECC Rating (A) | 917 | 917 | 917 | 917 | 917
Lockrose Bulk | 3870-1 | Lockrose BS | Lowood | 50 POE Load (A) | 139 | 139 | 139 | 139 | 139
Lockrose Bulk | 3871-1 | Lowood | Wivenhoe | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
Lockrose Bulk | 3871-1 | Lowood | Wivenhoe | 10 POE Load (A) | 81.128 | 78.9558 | 79.1416 | 79.0038 | 79.6208
Lockrose Bulk | 3871-1 | Lowood | Wivenhoe | Power Factor | 0.98206 | 0.98233 | 0.98232 | 0.98233 | 0.98227
Lockrose Bulk | 3871-1 | Lowood | Wivenhoe | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
Lockrose Bulk | 3871-1 | Lowood | Wivenhoe | 50 POE Load (A) | 75 | 75 | 75 | 75 | 75
Loganlea Bulk | 407-1 | Loganlea BS | Woodridge | NCC Rating (A) | 777 | 777 | 777 | 777 | 777 | Urban | 70
Loganlea Bulk | 407-1 | Loganlea BS | Woodridge | 10 POE Load (A) | 244.1782 | 236.8844 | 234.83 | 231.0847 | 229.6779
Loganlea Bulk | 407-1 | Loganlea BS | Woodridge | Power Factor | 0.98098 | 0.98146 | 0.98159 | 0.98183 | 0.98192
Loganlea Bulk | 407-1 | Loganlea BS | Woodridge | ECC Rating (A) | 832 | 832 | 832 | 832 | 832
Loganlea Bulk | 407-1 | Loganlea BS | Woodridge | 50 POE Load (A) | 466 | 460 | 454 | 451 | 451
Loganlea Bulk | 408-1 | Loganlea BS | Kingston | NCC Rating (A) | 647 | 647 | 647 | 647 | 647 | Urban | 280
Loganlea Bulk | 408-1 | Loganlea BS | Kingston | 10 POE Load (A) | 318.0503 | 314.5843 | 318.6612 | 320.2869 | 325.9523
Loganlea Bulk | 408-1 | Loganlea BS | Kingston | Power Factor | 0.9497 | 0.95008 | 0.94963 | 0.94945 | 0.94883
Loganlea Bulk | 408-1 | Loganlea BS | Kingston | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Loganlea Bulk | 408-1 | Loganlea BS | Kingston | 50 POE Load (A) | 707 | 706 | 703 | 702 | 702
Loganlea Bulk | 409-1 | Loganlea BS | Woodridge | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
Loganlea Bulk | 409-1 | Loganlea BS | Woodridge | 10 POE Load (A) | 218.0966 | 211.5814 | 209.7463 | 206.4008 | 205.1442
Loganlea Bulk | 409-1 | Loganlea BS | Woodridge | Power Factor | 0.98302 | 0.98346 | 0.98359 | 0.98381 | 0.9839
Loganlea Bulk | 409-1 | Loganlea BS | Woodridge | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Loganlea Bulk | 409-1 | Loganlea BS | Woodridge | 50 POE Load (A) | 436 | 430 | 425 | 422 | 422
Loganlea Bulk | 418-1 | Loganlea BS | Tanah Merah | NCC Rating (A) | 692 | 692 | 692 | 692 | 692 | Urban | 70
Loganlea Bulk | 418-1 | Loganlea BS | Tanah Merah | 10 POE Load (A) | 243.9153 | 240.783 | 241.1312 | 240.0748 | 242.0435
Loganlea Bulk | 418-1 | Loganlea BS | Tanah Merah | Power Factor | 0.00013335 | 0.00013341 | 0.0001335 | 0.00013342 | 0.00013353
Loganlea Bulk | 418-1 | Loganlea BS | Tanah Merah | ECC Rating (A) | 692 | 692 | 692 | 692 | 692
Loganlea Bulk | 418-1 | Loganlea BS | Tanah Merah | 50 POE Load (A) | 231 | 229 | 226 | 225 | 225
Loganlea Bulk | 452-1 | Loganlea BS | Kingston | NCC Rating (A) | 567 | 567 | 567 | 567 | 567 | Urban | 280
Loganlea Bulk | 452-1 | Loganlea BS | Kingston | 10 POE Load (A) | 258.1961 | 255.3821 | 258.6922 | 260.012 | 264.6117
Loganlea Bulk | 452-1 | Loganlea BS | Kingston | Power Factor | 0.98221 | 0.98244 | 0.98217 | 0.98206 | 0.98168
Loganlea Bulk | 452-1 | Loganlea BS | Kingston | ECC Rating (A) | 567 | 567 | 567 | 567 | 567
Loganlea Bulk | 452-1 | Loganlea BS | Kingston | 50 POE Load (A) | 536 | 534 | 533 | 532 | 532
Lytton Bulk | 3302-1 | Lytton BS | Fisherman Is B | NCC Rating (A) | 690 | 690 | 690 | 690 | 690 | Urban | 70
Lytton Bulk | 3302-1 | Lytton BS | Fisherman Is B | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lytton Bulk | 3302-1 | Lytton BS | Fisherman Is B | Power Factor | 1 | 1 | 1 | 1 | 1
Lytton Bulk | 3302-1 | Lytton BS | Fisherman Is B | ECC Rating (A) | 690 | 690 | 690 | 690 | 690
Lytton Bulk | 3302-1 | Lytton BS | Fisherman Is B | 50 POE Load (A) | 487 | 500 | 499 | 498 | 498
Lytton Bulk | 3303-1 | Lytton BS | Fisherman Is B | NCC Rating (A) | 650 | 650 | 650 | 650 | 650 | Urban | 70
Lytton Bulk | 3303-1 | Lytton BS | Fisherman Is B | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lytton Bulk | 3303-1 | Lytton BS | Fisherman Is B | Power Factor | 1 | 1 | 1 | 1 | 1
Lytton Bulk | 3303-1 | Lytton BS | Fisherman Is B | ECC Rating (A) | 650 | 650 | 650 | 650 | 650
Lytton Bulk | 3303-1 | Lytton BS | Fisherman Is B | 50 POE Load (A) | 497 | 511 | 509 | 508 | 508
Lytton Bulk | 490-1 | Lytton BS | Gibson Island | NCC Rating (A) | 664 | 664 | 664 | 664 | 664 | HighSec | 0
Lytton Bulk | 490-1 | Lytton BS | Gibson Island | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lytton Bulk | 490-1 | Lytton BS | Gibson Island | Power Factor | 1 | 1 | 1 | 1 | 1
Lytton Bulk | 490-1 | Lytton BS | Gibson Island | ECC Rating (A) | 664 | 664 | 664 | 664 | 664
Lytton Bulk | 490-1 | Lytton BS | Gibson Island | 50 POE Load (A) | 307 | 307 | 324 | 323 | 323
Lytton Bulk | 491-1 | Lytton BS | Lytton | NCC Rating (A) | 511 | 511 | 511 | 511 | 511 | HighSec | 314
Lytton Bulk | 491-1 | Lytton BS | Lytton | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lytton Bulk | 491-1 | Lytton BS | Lytton | Power Factor | 1 | 1 | 1 | 1 | 1
Lytton Bulk | 491-1 | Lytton BS | Lytton | ECC Rating (A) | 511 | 511 | 511 | 511 | 511
Lytton Bulk | 491-1 | Lytton BS | Lytton | 50 POE Load (A) | 464 | 497 | 492 | 491 | 491
Lytton Bulk | 492-1 | Lytton BS | Gibson Island | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | HighSec | 0
Lytton Bulk | 492-1 | Lytton BS | Gibson Island | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lytton Bulk | 492-1 | Lytton BS | Gibson Island | Power Factor | 1 | 1 | 1 | 1 | 1
Lytton Bulk | 492-1 | Lytton BS | Gibson Island | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
Lytton Bulk | 492-1 | Lytton BS | Gibson Island | 50 POE Load (A) | 321 | 321 | 339 | 338 | 338
Lytton Bulk | 493-1 | Lytton BS | Lytton | NCC Rating (A) | 573 | 573 | 573 | 573 | 573 | HighSec | 0
Lytton Bulk | 493-1 | Lytton BS | Lytton | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lytton Bulk | 493-1 | Lytton BS | Lytton | Power Factor | 1 | 1 | 1 | 1 | 1
Lytton Bulk | 493-1 | Lytton BS | Lytton | ECC Rating (A) | 573 | 573 | 573 | 573 | 573
Lytton Bulk | 493-1 | Lytton BS | Lytton | 50 POE Load (A) | 436 | 468 | 463 | 462 | 462
Lytton Bulk | 494-1 | Fisherman Is B | Fishermans Is | NCC Rating (A) | 546 | 546 | 546 | 546 | 546 | Urban | 70
Lytton Bulk | 494-1 | Fisherman Is B | Fishermans Is | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lytton Bulk | 494-1 | Fisherman Is B | Fishermans Is | Power Factor | 1 | 1 | 1 | 1 | 1
Lytton Bulk | 494-1 | Fisherman Is B | Fishermans Is | ECC Rating (A) | 546 | 546 | 546 | 546 | 546
Lytton Bulk | 494-1 | Fisherman Is B | Fishermans Is | 50 POE Load (A) | 250 | 264 | 263 | 263 | 263
Lytton Bulk | 495-1 | Fisherman Is B | Fisherman Is | NCC Rating (A) | 600 | 600 | 600 | 600 | 600 | Urban | 70
Lytton Bulk | 495-1 | Fisherman Is B | Fisherman Is | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lytton Bulk | 495-1 | Fisherman Is B | Fisherman Is | Power Factor | 1 | 1 | 1 | 1 | 1
Lytton Bulk | 495-1 | Fisherman Is B | Fisherman Is | ECC Rating (A) | 600 | 600 | 600 | 600 | 600
Lytton Bulk | 495-1 | Fisherman Is B | Fisherman Is | 50 POE Load (A) | 222 | 235 | 234 | 234 | 234
Lytton Bulk | 560-1 | Lytton BS | 560 Tee1 | NCC Rating (A) | 527 | 527 | 527 | 527 | 527 | Urban | 70
Lytton Bulk | 560-1 | Lytton BS | 560 Tee1 | 10 POE Load (A) | 132.1639 | 131.0227 | 131.2399 | 130.6468 | 131.6581
Lytton Bulk | 560-1 | Lytton BS | 560 Tee1 | Power Factor | 0.99985 | 0.99982 | 0.99983 | 0.99982 | 0.99984
Lytton Bulk | 560-1 | Lytton BS | 560 Tee1 | ECC Rating (A) | 527 | 527 | 527 | 527 | 527
Lytton Bulk | 560-1 | Lytton BS | 560 Tee1 | 50 POE Load (A) | 352 | 350 | 348 | 345 | 345
Lytton Bulk | 560-14 | 560 Tee1 | 560 Tee2 | NCC Rating (A) | 527 | 527 | 527 | 527 | 527 | Urban | 70
Lytton Bulk | 560-14 | 560 Tee1 | 560 Tee2 | 10 POE Load (A) | 54.4188 | 53.9479 | 54.0376 | 53.7928 | 54.2101
Lytton Bulk | 560-14 | 560 Tee1 | 560 Tee2 | Power Factor | -0.99792 | -0.99798 | -0.99797 | -0.998 | -0.99795
Lytton Bulk | 560-14 | 560 Tee1 | 560 Tee2 | ECC Rating (A) | 527 | 527 | 527 | 527 | 527
Lytton Bulk | 560-14 | 560 Tee1 | 560 Tee2 | 50 POE Load (A) | 208 | 207 | 206 | 205 | 205
Lytton Bulk | 560-15 | 560 Tee1 | 560 Tee2 | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 70
Lytton Bulk | 560-15 | 560 Tee1 | 560 Tee2 | 10 POE Load (A) | 78.8196 | 78.1425 | 78.2714 | 77.9195 | 78.5195
Lytton Bulk | 560-15 | 560 Tee1 | 560 Tee2 | Power Factor | 0.99992 | 0.9999 | 0.99991 | 0.9999 | 0.99991
Lytton Bulk | 560-15 | 560 Tee1 | 560 Tee2 | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
Lytton Bulk | 560-15 | 560 Tee1 | 560 Tee2 | 50 POE Load (A) | 292 | 290 | 288 | 287 | 287
Lytton Bulk | 560-16 | Lota | 560 Tee1 | NCC Rating (A) | 1053 | 1053 | 1053 | 1053 | 1053 | Urban | 70
Lytton Bulk | 560-16 | Lota | 560 Tee1 | 10 POE Load (A) | 133.0938 | 131.9443 | 132.1632 | 131.5657 | 132.5843
Lytton Bulk | 560-16 | Lota | 560 Tee1 | Power Factor | -0.99221 | -0.99226 | -0.99225 | -0.99228 | -0.99223
Lytton Bulk | 560-16 | Lota | 560 Tee1 | ECC Rating (A) | 1053 | 1053 | 1053 | 1053 | 1053
Lytton Bulk | 560-16 | Lota | 560 Tee1 | 50 POE Load (A) | 378 | 376 | 374 | 371 | 371
Lytton Bulk | 560-2 | 560 Tee1 | Tingalpa | NCC Rating (A) | 600 | 600 | 600 | 600 | 600 | Urban | 70
Lytton Bulk | 560-2 | 560 Tee1 | Tingalpa | 10 POE Load (A) | 0.10154 | 0.10154 | 0.10154 | 0.10155 | 0.10154
Lytton Bulk | 560-2 | 560 Tee1 | Tingalpa | Power Factor | 1.9408e-06 | 1.9406e-06 | 1.9409e-06 | 1.9409e-06 | 1.9395e-06
Lytton Bulk | 560-3 | 560 Tee1 | 560 Tee2 | NCC Rating (A) | 600 | 600 | 600 | 600 | 600 | Urban | 70
Lytton Bulk | 560-3 | 560 Tee1 | 560 Tee2 | 10 POE Load (A) | 132.1905 | 131.0486 | 131.266 | 130.6725 | 131.6844
Lytton Bulk | 560-3 | 560 Tee1 | 560 Tee2 | Power Factor | -0.99866 | -0.99872 | -0.9987 | -0.99873 | -0.99868
Lytton Bulk | 560-3 | 560 Tee1 | 560 Tee2 | ECC Rating (A) | 600 | 600 | 600 | 600 | 600
Lytton Bulk | 560-3 | 560 Tee1 | 560 Tee2 | 50 POE Load (A) | 352 | 350 | 348 | 346 | 342
Lytton Bulk | 560-5 | Lota | 560 Tee2 | NCC Rating (A) | 775 | 775 | 775 | 775 | 775 | Urban | 70
Lytton Bulk | 560-5 | Lota | 560 Tee2 | 10 POE Load (A) | 77.8215 | 77.1497 | 77.2776 | 76.9284 | 77.5238
Lytton Bulk | 560-5 | Lota | 560 Tee2 | Power Factor | -0.99877 | -0.99883 | -0.99882 | -0.99885 | -0.9988
Lytton Bulk | 560-5 | Lota | 560 Tee2 | ECC Rating (A) | 775 | 775 | 775 | 775 | 775
Lytton Bulk | 560-5 | Lota | 560 Tee2 | 50 POE Load (A) | 228 | 227 | 225 | 224 | 222
Lytton Bulk | 569-1 | Lytton BS | Lota | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Urban | 70
Lytton Bulk | 569-1 | Lytton BS | Lota | 10 POE Load (A) | 272.7914 | 270.436 | 270.8844 | 269.6603 | 271.7475
Lytton Bulk | 569-1 | Lytton BS | Lota | Power Factor | 0.99585 | 0.99593 | 0.99592 | 0.99596 | 0.99589
Lytton Bulk | 569-1 | Lytton BS | Lota | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
Lytton Bulk | 569-1 | Lytton BS | Lota | 50 POE Load (A) | 344 | 342 | 340 | 338 | 336
Lytton Bulk | 599-1 | Hemmant | Lindum | NCC Rating (A) | 630 | 630 | 630 | 630 | 630 | Urban | 70
Lytton Bulk | 599-1 | Hemmant | Lindum | 10 POE Load (A) | 1.7449 | 1.7449 | 1.7449 | 1.7449 | 1.7449
Lytton Bulk | 599-1 | Hemmant | Lindum | Power Factor | -1.164e-06 | -1.1625e-06 | -1.1632e-06 | -1.1633e-06 | -1.1636e-06
Lytton Bulk | 599-1 | Hemmant | Lindum | ECC Rating (A) | 630 | 630 | 630 | 630 | 630
Lytton Bulk | 599-1 | Hemmant | Lindum | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lytton Bulk | 681-1 | Lindum | Wynnum | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70
Lytton Bulk | 681-1 | Lindum | Wynnum | 10 POE Load (A) | 171.9947 | 171.4827 | 173.3851 | 174.1517 | 177.2085
Lytton Bulk | 681-1 | Lindum | Wynnum | Power Factor | 0.99218 | 0.99222 | 0.99208 | 0.99202 | 0.9918
Lytton Bulk | 681-1 | Lindum | Wynnum | ECC Rating (A) | 837 | 837 | 837 | 837 | 837
Lytton Bulk | 681-1 | Lindum | Wynnum | 50 POE Load (A) | 314 | 313 | 313 | 313 | 313
Lytton Bulk | 682-1 | Lindum | Wynnum | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70
Lytton Bulk | 682-1 | Lindum | Wynnum | 10 POE Load (A) | 164.8356 | 164.3449 | 166.168 | 166.9026 | 169.8321
Lytton Bulk | 682-1 | Lindum | Wynnum | Power Factor | -0.97996 | -0.98001 | -0.97984 | -0.97977 | -0.97949
Lytton Bulk | 682-1 | Lindum | Wynnum | ECC Rating (A) | 837 | 837 | 837 | 837 | 837
Lytton Bulk | 682-1 | Lindum | Wynnum | 50 POE Load (A) | 314 | 314 | 314 | 314 | 314
Lytton Bulk | 687-1 | Lytton BS | 687 Tee1 | NCC Rating (A) | 759 | 759 | 759 | 759 | 759 | Urban | 70
Lytton Bulk | 687-1 | Lytton BS | 687 Tee1 | 10 POE Load (A) | 122.0819 | 121.7178 | 123.071 | 123.6163 | 125.7909
Lytton Bulk | 687-1 | Lytton BS | 687 Tee1 | Power Factor | 0.99995 | 0.99995 | 0.99994 | 0.99993 | 0.9999
Lytton Bulk | 687-1 | Lytton BS | 687 Tee1 | ECC Rating (A) | 759 | 759 | 759 | 759 | 759
Lytton Bulk | 687-1 | Lytton BS | 687 Tee1 | 50 POE Load (A) | 288 | 288 | 288 | 288 | 288
Lytton Bulk | 687-2 | 687 Tee1 | Lytton | NCC Rating (A) | 517 | 517 | 517 | 517 | 517 | Urban | 70
Lytton Bulk | 687-2 | 687 Tee1 | Lytton | 10 POE Load (A) | 2.2895 | 2.2895 | 2.2895 | 2.2895 | 2.2895
Lytton Bulk | 687-2 | 687 Tee1 | Lytton | Power Factor | 1.8338e-05 | 1.8338e-05 | 1.8338e-05 | 1.8338e-05 | 1.8338e-05
Lytton Bulk | 687-2 | 687 Tee1 | Lytton | ECC Rating (A) | 517 | 517 | 517 | 517 | 517
Lytton Bulk | 687-2 | 687 Tee1 | Lytton | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lytton Bulk | 687-3 | 687 Tee1 | Lindum | NCC Rating (A) | 636 | 636 | 636 | 636 | 636 | Urban | 70
Lytton Bulk | 687-3 | 687 Tee1 | Lindum | 10 POE Load (A) | 122.2777 | 121.9127 | 123.2691 | 123.8157 | 125.9954
Lytton Bulk | 687-3 | 687 Tee1 | Lindum | Power Factor | 0.999 | 0.99902 | 0.99897 | 0.99894 | 0.99886
Lytton Bulk | 687-3 | 687 Tee1 | Lindum | ECC Rating (A) | 636 | 636 | 636 | 636 | 636
Lytton Bulk | 687-3 | 687 Tee1 | Lindum | 50 POE Load (A) | 288 | 288 | 288 | 288 | 288
Lytton Bulk | 688-1 | Lytton BS | Lindum | NCC Rating (A) | 636 | 636 | 636 | 636 | 636 | Urban | 70
Lytton Bulk | 688-1 | Lytton BS | Lindum | 10 POE Load (A) | 212.8629 | 212.2271 | 214.5896 | 215.5415 | 219.3377
Lytton Bulk | 688-1 | Lytton BS | Lindum | Power Factor | 0.98868 | 0.98873 | 0.98853 | 0.98845 | 0.98812
Lytton Bulk | 688-1 | Lytton BS | Lindum | ECC Rating (A) | 636 | 636 | 636 | 636 | 636
Lytton Bulk | 688-1 | Lytton BS | Lindum | 50 POE Load (A) | 288 | 288 | 288 | 287 | 287
Meeandah Bulk | 3374-1 | Whinstanes | Hamilton Lands | NCC Rating (A) | 775 | 775 | 775 | 775 | 775 | Urban | 70
Meeandah Bulk | 3374-1 | Whinstanes | Hamilton Lands | 10 POE Load (A) | 40.2197 | 79.5008 | 79.0818 | 77.6834 | 77.131
Meeandah Bulk | 3374-1 | Whinstanes | Hamilton Lands | Power Factor | 0.9568 | 0.94324 | 0.94342 | 0.94385 | 0.94409
Meeandah Bulk | 3374-1 | Whinstanes | Hamilton Lands | ECC Rating (A) | 0 | 0 | 0 | 0 | 0
Meeandah Bulk | 3374-1 | Whinstanes | Hamilton Lands | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Meeandah Bulk | 506-1 | Meeandah BS | Hamilton Lands | NCC Rating (A) | 771 | 771 | 771 | 771 | 771 | Urban | 70
Meeandah Bulk | 506-1 | Meeandah BS | Hamilton Lands | 10 POE Load (A) | 126.043 | 148.1916 | 151.444 | 153.0067 | 156.0408
Meeandah Bulk | 506-1 | Meeandah BS | Hamilton Lands | Power Factor | 0.95594 | 0.95211 | 0.9514 | 0.95104 | 0.95038
Meeandah Bulk | 506-1 | Meeandah BS | Hamilton Lands | ECC Rating (A) | 843 | 843 | 843 | 843 | 843
Meeandah Bulk | 506-1 | Meeandah BS | Hamilton Lands | 50 POE Load (A) | 269 | 268 | 266 | 266 | 266
Meeandah Bulk | 513-1 | Meeandah BS | Hamilton Lands | NCC Rating (A) | 771 | 771 | 771 | 771 | 771 | Urban | 70
Meeandah Bulk | 513-1 | Meeandah BS | Hamilton Lands | 10 POE Load (A) | 125.0515 | 147.0228 | 150.2492 | 151.7995 | 154.8092
Meeandah Bulk | 513-1 | Meeandah BS | Hamilton Lands | Power Factor | 0.95606 | 0.95222 | 0.95151 | 0.95114 | 0.95048
Meeandah Bulk | 513-1 | Meeandah BS | Hamilton Lands | ECC Rating (A) | 843 | 843 | 843 | 843 | 843
Meeandah Bulk | 513-1 | Meeandah BS | Hamilton Lands | 50 POE Load (A) | 268 | 267 | 266 | 266 | 266
Meeandah Bulk | 556-1 | Meeandah BS | Whinstanes | NCC Rating (A) | 775 | 775 | 775 | 775 | 775 | Urban | 70
Meeandah Bulk | 556-1 | Meeandah BS | Whinstanes | 10 POE Load (A) | 95.8042 | 131.8241 | 133.4304 | 133.4897 | 134.8917
Meeandah Bulk | 556-1 | Meeandah BS | Whinstanes | Power Factor | 0.95231 | 0.9467 | 0.9464 | 0.94635 | 0.94608
Meeandah Bulk | 556-1 | Meeandah BS | Whinstanes | ECC Rating (A) | 912 | 912 | 912 | 912 | 912
Meeandah Bulk | 556-1 | Meeandah BS | Whinstanes | 50 POE Load (A) | 274 | 274 | 273 | 272 | 272
Meeandah Bulk | 609-1 | Meeandah BS | Myrtletown | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Meeandah Bulk | 609-1 | Meeandah BS | Myrtletown | 10 POE Load (A) | 0.84162 | 0.84162 | 0.84162 | 0.84162 | 0.84162
Meeandah Bulk | 609-1 | Meeandah BS | Myrtletown | Power Factor | 5.6181e-06 | 5.6182e-06 | 5.6184e-06 | 5.6184e-06 | 5.6182e-06
Meeandah Bulk | 610-1 | Meeandah BS | Myrtletown | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Meeandah Bulk | 610-1 | Meeandah BS | Myrtletown | 10 POE Load (A) | 0.56892 | 0.56892 | 0.56892 | 0.56892 | 0.56892
Meeandah Bulk | 610-1 | Meeandah BS | Myrtletown | Power Factor | 9.097e-06 | 9.0972e-06 | 9.097e-06 | 9.097e-06 | 9.0972e-06
Molendinar Bulk | 3670-1 | Molendinar BS | Parkwood | NCC Rating (A) | 790 | 790 | 790 | 790 | 790 | Urban | 70
Molendinar Bulk | 3670-1 | Molendinar BS | Parkwood | 10 POE Load (A) | 255.1272 | 252.6931 | 263.3995 | 262.6419 | 275.0514
Molendinar Bulk | 3670-1 | Molendinar BS | Parkwood | Power Factor | 0.99311 | 0.99325 | 0.99277 | 0.99281 | 0.99222
Molendinar Bulk | 3670-1 | Molendinar BS | Parkwood | ECC Rating (A) | 790 | 790 | 790 | 790 | 790
Molendinar Bulk | 3670-1 | Molendinar BS | Parkwood | 50 POE Load (A) | 443 | 443 | 456 | 456 | 456
Molendinar Bulk | 3671-1 | Molendinar BS | Parkwood | NCC Rating (A) | 758 | 758 | 758 | 758 | 758 | Urban | 70
Molendinar Bulk | 3671-1 | Molendinar BS | Parkwood | 10 POE Load (A) | 202.8213 | 200.8854 | 209.3999 | 208.7974 | 218.6664
Molendinar Bulk | 3671-1 | Molendinar BS | Parkwood | Power Factor | 0.99672 | 0.9968 | 0.99655 | 0.99657 | 0.99625
Molendinar Bulk | 3671-1 | Molendinar BS | Parkwood | ECC Rating (A) | 758 | 758 | 758 | 758 | 758
Molendinar Bulk | 3671-1 | Molendinar BS | Parkwood | 50 POE Load (A) | 345 | 345 | 359 | 359 | 364
Molendinar Bulk | 389-1 | Parkwood | 389 Tee1 | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
Molendinar Bulk | 389-1 | Parkwood | 389 Tee1 | 10 POE Load (A) | 263.2321 | 261.8345 | 259.4199 | 260.1064 | 258.0357
Molendinar Bulk | 389-1 | Parkwood | 389 Tee1 | Power Factor | 0.99407 | 0.99418 | 0.99413 | 0.99413 | 0.99406
Molendinar Bulk | 389-1 | Parkwood | 389 Tee1 | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Molendinar Bulk | 389-1 | Parkwood | 389 Tee1 | 50 POE Load (A) | 532 | 533 | 532 | 533 | 533
Molendinar Bulk | 389-2 | F389 Tee1 | Labrador | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
Molendinar Bulk | 389-2 | F389 Tee1 | Labrador | 10 POE Load (A) | 191.9746 | 191.3616 | 193.5934 | 195.1386 | 197.1295
Molendinar Bulk | 389-2 | F389 Tee1 | Labrador | Power Factor | 0.98337 | 0.98342 | 0.98313 | 0.98309 | 0.9828
Molendinar Bulk | 389-2 | F389 Tee1 | Labrador | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Molendinar Bulk | 389-2 | F389 Tee1 | Labrador | 50 POE Load (A) | 312 | 314 | 316 | 318 | 318
Molendinar Bulk | 389-3 | F389 Tee1 | Hollywell | NCC Rating (A) | 659 | 659 | 659 | 659 | 659 | Urban | 70
Molendinar Bulk | 389-3 | F389 Tee1 | Hollywell | 10 POE Load (A) | 73.3339 | 72.5842 | 68.1073 | 67.3129 | 63.4141
Molendinar Bulk | 389-3 | F389 Tee1 | Hollywell | Power Factor | 0.99785 | 0.99758 | 0.99635 | 0.99591 | 0.99439
Molendinar Bulk | 389-3 | F389 Tee1 | Hollywell | ECC Rating (A) | 749 | 749 | 749 | 749 | 749
Molendinar Bulk | 389-3 | F389 Tee1 | Hollywell | 50 POE Load (A) | 467 | 467 | 467 | 467 | 467
Molendinar Bulk | 390-1 | Molendinar BS | F390 Tee1 | NCC Rating (A) | 637 | 637 | 637 | 637 | 637 | Urban | 70
Molendinar Bulk | 390-1 | Molendinar BS | F390 Tee1 | 10 POE Load (A) | 65.637 | 64.7467 | 80.0692 | 79.3628 | 79.4292
Molendinar Bulk | 390-1 | Molendinar BS | F390 Tee1 | Power Factor | 0.99793 | 0.99806 | 0.99578 | 0.99589 | 0.99588
Molendinar Bulk | 390-1 | Molendinar BS | F390 Tee1 | ECC Rating (A) | 637 | 637 | 637 | 637 | 637
Molendinar Bulk | 390-1 | Molendinar BS | F390 Tee1 | 50 POE Load (A) | 410 | 411 | 411 | 412 | 412
Molendinar Bulk | 390-2 | F390 Tee | Bundall | NCC Rating (A) | 701 | 701 | 701 | 701 | 701 | Urban | 70
Molendinar Bulk | 390-2 | F390 Tee | Bundall | 10 POE Load (A) | 66.1462 | 65.2542 | 80.6044 | 79.8968 | 79.9633
Molendinar Bulk | 390-2 | F390 Tee | Bundall | Power Factor | 0.99188 | 0.99199 | 0.99041 | 0.99049 | 0.99048
Molendinar Bulk | 390-2 | F390 Tee | Bundall | ECC Rating (A) | 721 | 721 | 721 | 721 | 721
Molendinar Bulk | 390-2 | F390 Tee | Bundall | 50 POE Load (A) | 209 | 207 | 205 | 205 | 205
Molendinar Bulk | 390-3 | F390 Tee | Miami | NCC Rating (A) | 688 | 688 | 688 | 688 | 688 | Urban | 70
Molendinar Bulk | 390-3 | F390 Tee | Miami | 10 POE Load (A) | 0.18357 | 0.18359 | 0.18328 | 0.1833 | 0.1833
Molendinar Bulk | 390-3 | F390 Tee | Miami | Power Factor | 1 | 1 | 1 | 1 | 1
Molendinar Bulk | 390-3 | F390 Tee | Miami | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Molendinar Bulk | 390-3 | F390 Tee | Miami | 50 POE Load (A) | 570 | 572 | 574 | 576 | 576
Molendinar Bulk | 391-1 | Molendinar BS | Bundall | NCC Rating (A) | 688 | 688 | 688 | 688 | 688 | Urban | 70
Molendinar Bulk | 391-1 | Molendinar BS | Bundall | 10 POE Load (A) | 82.4527 | 81.3421 | 100.4539 | 99.5729 | 99.6556
Molendinar Bulk | 391-1 | Molendinar BS | Bundall | Power Factor | 0.98493 | 0.98515 | 0.98167 | 0.98183 | 0.98181
Molendinar Bulk | 391-1 | Molendinar BS | Bundall | ECC Rating (A) | 688 | 688 | 688 | 688 | 688
Molendinar Bulk | 391-1 | Molendinar BS | Bundall | 50 POE Load (A) | 205 | 203 | 202 | 201 | 201
Molendinar Bulk | 392-1 | Molendinar BS | Gaven | NCC Rating (A) | 758 | 758 | 758 | 758 | 758 | Urban | 70
Molendinar Bulk | 392-1 | Molendinar BS | Gaven | 10 POE Load (A) | 174.7666 | 167.2758 | 164.5918 | 163.436 | 164.7789
Molendinar Bulk | 392-1 | Molendinar BS | Gaven | Power Factor | 0.99461 | 0.99498 | 0.99511 | 0.99517 | 0.9951
Molendinar Bulk | 392-1 | Molendinar BS | Gaven | ECC Rating (A) | 758 | 758 | 758 | 758 | 758
Molendinar Bulk | 392-1 | Molendinar BS | Gaven | 50 POE Load (A) | 348 | 346 | 343 | 342 | 342
Molendinar Bulk | 421-1 | Molendinar BS | Arundel | NCC Rating (A) | 713 | 713 | 713 | 713 | 713 | Urban | 553
Molendinar Bulk | 421-1 | Molendinar BS | Arundel | 10 POE Load (A) | 359.0839 | 354.0805 | 357.0589 | 355.2227 | 360.5219
Molendinar Bulk | 421-1 | Molendinar BS | Arundel | Power Factor | 0.99153 | 0.99183 | 0.99176 | 0.99187 | 0.99165
Molendinar Bulk | 421-1 | Molendinar BS | Arundel | ECC Rating (A) | 764 | 764 | 764 | 764 | 764
Molendinar Bulk | 421-1 | Molendinar BS | Arundel | 50 POE Load (A) | 623 | 621 | 625 | 625 | 627
Molendinar Bulk | 458-1 | Molendinar BS | Labrador | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
Molendinar Bulk | 458-1 | Molendinar BS | Labrador | 10 POE Load (A) | 147.1425 | 146.1131 | 148.8238 | 148.9418 | 152.1637
Molendinar Bulk | 458-1 | Molendinar BS | Labrador | Power Factor | 0.99597 | 0.99603 | 0.99596 | 0.99595 | 0.99584
Molendinar Bulk | 458-1 | Molendinar BS | Labrador | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Molendinar Bulk | 458-1 | Molendinar BS | Labrador | 50 POE Load (A) | 318 | 320 | 322 | 325 | 325
Molendinar Bulk | 473-1 | Molendinar BS | Gaven | NCC Rating (A) | 794 | 794 | 794 | 794 | 794 | Urban | 70
Molendinar Bulk | 473-1 | Molendinar BS | Gaven | 10 POE Load (A) | 175.1646 | 167.6567 | 164.9666 | 163.8082 | 165.1541
Molendinar Bulk | 473-1 | Molendinar BS | Gaven | Power Factor | 0.99459 | 0.99496 | 0.99509 | 0.99515 | 0.99509
Molendinar Bulk | 473-1 | Molendinar BS | Gaven | ECC Rating (A) | 926 | 926 | 926 | 926 | 926
Molendinar Bulk | 473-1 | Molendinar BS | Gaven | 50 POE Load (A) | 420 | 417 | 414 | 412 | 412
Molendinar Bulk | 474A-1 | Arundel | Hollywell | NCC Rating (A) | 659 | 659 | 659 | 659 | 659 | Urban | 517
Molendinar Bulk | 474A-1 | Arundel | Hollywell | 10 POE Load (A) | 427.2028 | 425.6349 | 433.7424 | 434.3749 | 443.8703
Molendinar Bulk | 474A-1 | Arundel | Hollywell | Power Factor | -0.98922 | -0.98927 | -0.9891 | -0.98906 | -0.98885
Molendinar Bulk | 474A-1 | Arundel | Hollywell | ECC Rating (A) | 2000 | 2000 | 2000 | 2000 | 2000
Molendinar Bulk | 474A-1 | Arundel | Hollywell | 50 POE Load (A) | 523 | 524 | 530 | 531 | 531
Molendinar Bulk | 474B-1 | Hope Is | Hollywell | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Urban | 70
Molendinar Bulk | 474B-1 | Hope Is | Hollywell | 10 POE Load (A) | 3.8066 | 3.807 | 3.8063 | 3.8063 | 3.8054
Molendinar Bulk | 474B-1 | Hope Is | Hollywell | Power Factor | 5.1781e-05 | 5.1781e-05 | 5.1781e-05 | 5.1781e-05 | 5.1781e-05
Molendinar Bulk | 474B-1 | Hope Is | Hollywell | ECC Rating (A) | 935 | 935 | 935 | 935 | 935
Molendinar Bulk | 474B-1 | Hope Is | Hollywell | 50 POE Load (A) | 237 | 239 | 240 | 242 | 244
Molendinar Bulk | 486-1 | Molendinar BS | Arundel | NCC Rating (A) | 713 | 713 | 713 | 713 | 713 | Urban | 70
Molendinar Bulk | 486-1 | Molendinar BS | Arundel | 10 POE Load (A) | 359.3439 | 354.3369 | 357.3175 | 355.48 | 360.783
Molendinar Bulk | 486-1 | Molendinar BS | Arundel | Power Factor | 0.99151 | 0.99182 | 0.99174 | 0.99186 | 0.99164
Molendinar Bulk | 486-1 | Molendinar BS | Arundel | ECC Rating (A) | 764 | 764 | 764 | 764 | 764
Molendinar Bulk | 486-1 | Molendinar BS | Arundel | 50 POE Load (A) | 624 | 621 | 625 | 625 | 630
Mudgeeraba Bulk | 3700-1 | Mudgeeraba BS | 3700 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Mudgeeraba Bulk | 3700-1 | Mudgeeraba BS | 3700 Tee1 | 10 POE Load (A) | 180.5606 | 179.5194 | 180.9318 | 181.5112 | 183.9122
Mudgeeraba Bulk | 3700-1 | Mudgeeraba BS | 3700 Tee1 | Power Factor | 0.99315 | 0.9932 | 0.99314 | 0.99311 | 0.993
Mudgeeraba Bulk | 3700-1 | Mudgeeraba BS | 3700 Tee1 | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Mudgeeraba Bulk | 3700-1 | Mudgeeraba BS | 3700 Tee1 | 50 POE Load (A) | 325 | 326 | 326 | 327 | 327
Mudgeeraba Bulk | 3700-2 | 3700 Tee1 | 3701 Tee1 | NCC Rating (A) | 1094 | 1094 | 1094 | 1094 | 1094 | Rural | 170
Mudgeeraba Bulk | 3700-2 | 3700 Tee1 | 3701 Tee1 | 10 POE Load (A) | 0.0029976 | 0.0029976 | 0.0029976 | 0.0029976 | 0.0029976
Mudgeeraba Bulk | 3700-2 | 3700 Tee1 | 3701 Tee1 | Power Factor | 6.6114e-05 | 6.6116e-05 | 6.6127e-05 | 6.6128e-05 | 6.6108e-05
Mudgeeraba Bulk | 3700-3 | 3700 Tee1 | 3700 Tee2 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Mudgeeraba Bulk | 3700-3 | 3700 Tee1 | 3700 Tee2 | 10 POE Load (A) | 180.5894 | 179.5481 | 180.9606 | 181.5401 | 183.9413
Mudgeeraba Bulk | 3700-3 | 3700 Tee1 | 3700 Tee2 | Power Factor | 0.99321 | 0.99325 | 0.9932 | 0.99317 | 0.99308
Mudgeeraba Bulk | 3700-3 | 3700 Tee1 | 3700 Tee2 | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Mudgeeraba Bulk | 3700-3 | 3700 Tee1 | 3700 Tee2 | 50 POE Load (A) | 325 | 326 | 326 | 327 | 327
Mudgeeraba Bulk | 3700-4 | 3700 Tee2 | 3702 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Mudgeeraba Bulk | 3700-4 | 3700 Tee2 | 3702 Tee1 | 10 POE Load (A) | 0.12338 | 0.12338 | 0.12338 | 0.12337 | 0.12337
Mudgeeraba Bulk | 3700-4 | 3700 Tee2 | 3702 Tee1 | Power Factor | 8.6877e-06 | 8.6871e-06 | 8.6866e-06 | 8.6877e-06 | 8.6869e-06
Mudgeeraba Bulk | 3700-5 | 3700 Tee2 | Mudgeeraba Pkg | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Mudgeeraba Bulk | 3700-5 | 3700 Tee2 | Mudgeeraba Pkg | 10 POE Load (A) | 180.6272 | 179.5858 | 180.9985 | 181.578 | 183.9795
Mudgeeraba Bulk | 3700-5 | 3700 Tee2 | Mudgeeraba Pkg | Power Factor | 0.99383 | 0.99386 | 0.99382 | 0.9938 | 0.99373
Mudgeeraba Bulk | 3700-5 | 3700 Tee2 | Mudgeeraba Pkg | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Mudgeeraba Bulk | 3700-5 | 3700 Tee2 | Mudgeeraba Pkg | 50 POE Load (A) | 325 | 326 | 326 | 327 | 327
Mudgeeraba Bulk | 3701-1 | Mudgeeraba | Mudgeeraba Pkg | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170
Mudgeeraba Bulk | 3701-1 | Mudgeeraba | Mudgeeraba Pkg | 10 POE Load (A) | 195.6101 | 194.4828 | 196.012 | 196.6394 | 199.239
Mudgeeraba Bulk | 3701-1 | Mudgeeraba | Mudgeeraba Pkg | Power Factor | 0.9908 | 0.99084 | 0.99079 | 0.99077 | 0.99068
Mudgeeraba Bulk | 3701-1 | Mudgeeraba | Mudgeeraba Pkg | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Mudgeeraba Bulk | 3701-1 | Mudgeeraba | Mudgeeraba Pkg | 50 POE Load (A) | 478 | 479 | 480 | 480 | 480
Nambour Bulk | 307-1 | Nambour BS | 307 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Nambour Bulk | 307-1 | Nambour BS | 307 Tee1 | 10 POE Load (A) | 80.722 | 80.6047 | 81.5013 | 81.7649 | 82.9059
Nambour Bulk | 307-1 | Nambour BS | 307 Tee1 | Power Factor | 0.96083 | 0.96087 | 0.96055 | 0.96046 | 0.96005
Nambour Bulk | 307-1 | Nambour BS | 307 Tee1 | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Nambour Bulk | 307-1 | Nambour BS | 307 Tee1 | 50 POE Load (A) | 377 | 377 | 377 | 376 | 376
Nambour Bulk | 307-2 | 307 Tee1 | Yandina | NCC Rating (A) | 799 | 799 | 799 | 799 | 799 | Rural | 170
Nambour Bulk | 307-2 | 307 Tee1 | Yandina | 10 POE Load (A) | 81.4261 | 81.3085 | 82.2073 | 82.4715 | 83.6153
Nambour Bulk | 307-2 | 307 Tee1 | Yandina | Power Factor | 0.95768 | 0.95772 | 0.95745 | 0.95737 | 0.95703
Nambour Bulk | 307-2 | 307 Tee1 | Yandina | ECC Rating (A) | 799 | 799 | 799 | 799 | 799
Nambour Bulk | 307-2 | 307 Tee1 | Yandina | 50 POE Load (A) | 141 | 141 | 142 | 142 | 142
Nambour Bulk | 344-1 | Nambour BS | Maleny | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
Nambour Bulk | 344-1 | Nambour BS | Maleny | 10 POE Load (A) | 216.0809 | 213.6292 | 214.234 | 213.2915 | 214.5596
Nambour Bulk | 344-1 | Nambour BS | Maleny | Power Factor | 0.97112 | 0.97088 | 0.97094 | 0.97085 | 0.97097
Nambour Bulk | 344-1 | Nambour BS | Maleny | ECC Rating (A) | 293 | 293 | 293 | 432 | 432
Nambour Bulk | 344-1 | Nambour BS | Maleny | 50 POE Load (A) | 310 | 309 | 307 | 332 | 350
Nambour Bulk | 345-1 | Nambour BS | Kenilworth | NCC Rating (A) | 416 | 416 | 416 | 416 | 416 | Rural | 170
Nambour Bulk | 345-1 | Nambour BS | Kenilworth | 10 POE Load (A) | 95.1688 | 94.14 | 94.4549 | 93.9975 | 94.5291
Nambour Bulk | 345-1 | Nambour BS | Kenilworth | Power Factor | 0.99171 | 0.99205 | 0.99202 | 0.99206 | 0.99201
Nambour Bulk | 345-1 | Nambour BS | Kenilworth | ECC Rating (A) | 416 | 416 | 416 | 416 | 416
Nambour Bulk | 345-1 | Nambour BS | Kenilworth | 50 POE Load (A) | 165 | 163 | 161 | 160 | 158
Nambour Bulk | 347-1 | Nambour BS | 347 Tee1 | NCC Rating (A) | 412 | 412 | 412 | 412 | 412 | Rural | 170
Nambour Bulk | 347-1 | Nambour BS | 347 Tee1 | 10 POE Load (A) | 174.0476 | 181.9528 | 184.2026 | 185.2654 | 188.8324
Nambour Bulk | 347-1 | Nambour BS | 347 Tee1 | Power Factor | 0.98254 | 0.98205 | 0.98181 | 0.9817 | 0.98131
Nambour Bulk | 347-1 | Nambour BS | 347 Tee1 | ECC Rating (A) | 412 | 412 | 412 | 412 | 412
Nambour Bulk | 347-1 | Nambour BS | 347 Tee1 | 50 POE Load (A) | 348 | 349 | 351 | 352 | 356
Nambour Bulk | 347-2 | 347 Tee1 | Palmwoods Central | NCC Rating (A) | 515 | 515 | 515 | 515 | 515 | Rural | 170
Nambour Bulk | 347-2 | 347 Tee1 | Palmwoods Central | 10 POE Load (A) | 174.4452 | 182.3584 | 184.6105 | 185.6744 | 189.245
Nambour Bulk | 347-2 | 347 Tee1 | Palmwoods Central | Power Factor | 0.98256 | 0.98232 | 0.98214 | 0.98206 | 0.98178
Nambour Bulk | 347-2 | 347 Tee1 | Palmwoods Central | ECC Rating (A) | 515 | 515 | 515 | 515 | 515
Nambour Bulk | 347-2 | 347 Tee1 | Palmwoods Central | 50 POE Load (A) | 502 | 504 | 506 | 508 | 508
Nambour Bulk | 347-3 | 347 Tee1 | Landsborough | NCC Rating (A) | 412 | 412 | 412 | 412 | 412 | Rural | 170
Nambour Bulk | 347-3 | 347 Tee1 | Landsborough | 10 POE Load (A) | 1.6684 | 1.6664 | 1.6659 | 1.6656 | 1.6647
Nambour Bulk | 347-3 | 347 Tee1 | Landsborough | Power Factor | 0.00019082 | 0.00019082 | 0.00019082 | 0.00019082 | 0.00019082
Nambour Bulk | 347-3 | 347 Tee1 | Landsborough | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
Nambour Bulk | 347-3 | 347 Tee1 | Landsborough | 50 POE Load (A) | 316 | 346 | 357 | 367 | 369
Nambour Bulk | 348-1 | Nambour BS | Palmwoods Central | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170
Nambour Bulk | 348-1 | Nambour BS | Palmwoods Central | 10 POE Load (A) | 222.7022 | 232.8148 | 235.6929 | 237.0525 | 241.6155
Nambour Bulk | 348-1 | Nambour BS | Palmwoods Central | Power Factor | 0.97853 | 0.97816 | 0.97794 | 0.97784 | 0.97749
Nambour Bulk | 348-1 | Nambour BS | Palmwoods Central | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
Nambour Bulk | 348-1 | Nambour BS | Palmwoods Central | 50 POE Load (A) | 491 | 493 | 495 | 497 | 499
Nambour Bulk | 489-1 | Nambour BS | Yandina | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
Nambour Bulk | 489-1 | Nambour BS | Yandina | 10 POE Load (A) | 73.401 | 73.2946 | 74.108 | 74.347 | 75.3821
Nambour Bulk | 489-1 | Nambour BS | Yandina | Power Factor | 0.99789 | 0.99788 | 0.99795 | 0.99797 | 0.99806
Nambour Bulk | 489-1 | Nambour BS | Yandina | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
Nambour Bulk | 489-1 | Nambour BS | Yandina | 50 POE Load (A) | 177 | 177 | 177 | 177 | 177
Nudgee Bulk | 3280-1 | Hendra | Clayfield | NCC Rating (A) | 725 | 725 | 725 | 725 | 725 | Urban | 70
Nudgee Bulk | 3280-1 | Hendra | Clayfield | 10 POE Load (A) | 119.1203 | 117.4576 | 118.835 | 119.1707 | 120.9945
Nudgee Bulk | 3280-1 | Hendra | Clayfield | Power Factor | 0.99934 | 0.9994 | 0.99935 | 0.99934 | 0.99928
Nudgee Bulk | 3280-1 | Hendra | Clayfield | ECC Rating (A) | 725 | 725 | 725 | 725 | 725
Nudgee Bulk | 3280-1 | Hendra | Clayfield | 50 POE Load (A) | 6 | 6 | 6 | 6 | 6
Nudgee Bulk | 535-1 | Hendra | Nundah | NCC Rating (A) | #N/A | #N/A | #N/A | #N/A | #N/A | Urban | 70
Nudgee Bulk | 535-1 | Hendra | Nundah | 10 POE Load (A) | #N/A | #N/A | #N/A | #N/A | #N/A
Nudgee Bulk | 535-1 | Hendra | Nundah | Power Factor | #N/A | #N/A | #N/A | #N/A | #N/A
Nudgee Bulk | 535-1 | Hendra | Nundah | ECC Rating (A) | 0 | 0 | 0 | 0 | 0
Nudgee Bulk | 535-1 | Hendra | Nundah | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Nudgee Bulk | 540-1 | Hendra | Nundah | NCC Rating (A) | 775 | 775 | 775 | 775 | 775 | Urban | 70
Nudgee Bulk | 540-1 | Hendra | Nundah | 10 POE Load (A) | 130.6283 | 133.0503 | 134.0818 | 134.1781 | 136.3159
Nudgee Bulk | 540-1 | Hendra | Nundah | Power Factor | -0.99797 | -0.99823 | -0.99828 | -0.99831 | -0.99843
Nudgee Bulk | 540-1 | Hendra | Nundah | ECC Rating (A) | 775 | 775 | 775 | 775 | 775
Nudgee Bulk | 540-1 | Hendra | Nundah | 50 POE Load (A) | 312 | 311 | 309 | 307 | 307
Nudgee Bulk | 593-1 | Nudgee BS | Nundah | NCC Rating (A) | 778 | 778 | 778 | 778 | 778 | Urban | 192
Nudgee Bulk | 593-1 | Nudgee BS | Nundah | 10 POE Load (A) | 466.3419 | 467.6408 | 470.4975 | 469.4373 | 474.6473
Nudgee Bulk | 593-1 | Nudgee BS | Nundah | Power Factor | -0.99431 | -0.99432 | -0.99425 | -0.99428 | -0.99417
Nudgee Bulk | 593-1 | Nudgee BS | Nundah | ECC Rating (A) | 778 | 778 | 778 | 778 | 778
Nudgee Bulk | 593-1 | Nudgee BS | Nundah | 50 POE Load (A) | 575 | 572 | 570 | 568 | 566
Nudgee Bulk | 604-1 | Nudgee BS | Geebung | NCC Rating (A) | 459 | 459 | 459 | 459 | 459 | Urban | 70
Nudgee Bulk | 604-1 | Nudgee BS | Geebung | 10 POE Load (A) | 156.8886 | 153.825 | 153.5523 | 151.3251 | 150.3063
Nudgee Bulk | 604-1 | Nudgee BS | Geebung | Power Factor | -0.96707 | -0.96743 | -0.96746 | -0.96772 | -0.96784
Nudgee Bulk | 604-1 | Nudgee BS | Geebung | ECC Rating (A) | 522 | 522 | 522 | 522 | 522
Nudgee Bulk | 604-1 | Nudgee BS | Geebung | 50 POE Load (A) | 246 | 241 | 236 | 234 | 234
Nudgee Bulk | 605-1 | Nudgee BS | Geebung | NCC Rating (A) | 459 | 459 | 459 | 459 | 459 | Urban | 70
Nudgee Bulk | 605-1 | Nudgee BS | Geebung | 10 POE Load (A) | 157.0652 | 153.9981 | 153.7251 | 151.4953 | 150.4754
Nudgee Bulk | 605-1 | Nudgee BS | Geebung | Power Factor | 0.99912 | 0.99875 | 0.99871 | 0.99839 | 0.99823
Nudgee Bulk | 605-1 | Nudgee BS | Geebung | ECC Rating (A) | 522 | 522 | 522 | 522 | 522
Nudgee Bulk | 605-1 | Nudgee BS | Geebung | 50 POE Load (A) | 246 | 241 | 236 | 235 | 235
Nudgee Bulk | 622-1 | Nudgee BS | Hendra | NCC Rating (A) | 758 | 758 | 758 | 758 | 758 | Urban | 70
Nudgee Bulk | 622-1 | Nudgee BS | Hendra | 10 POE Load (A) | 293.2399 | 295.7417 | 297.7372 | 297.3918 | 301.2378
Nudgee Bulk | 622-1 | Nudgee BS | Hendra | Power Factor | 0.99851 | 0.99845 | 0.99839 | 0.99841 | 0.9983
Nudgee Bulk | 622-1 | Nudgee BS | Hendra | ECC Rating (A) | 758 | 758 | 758 | 758 | 758
Nudgee Bulk | 622-1 | Nudgee BS | Hendra | 50 POE Load (A) | 469 | 466 | 464 | 463 | 463
Nudgee Bulk | 623-1 | Nudgee BS | Hendra | NCC Rating (A) | 758 | 758 | 758 | 758 | 758 | Urban | 70
Nudgee Bulk | 623-1 | Nudgee BS | Hendra | 10 POE Load (A) | 293.2399 | 295.7417 | 297.7372 | 297.3918 | 301.2378
Nudgee Bulk | 623-1 | Nudgee BS | Hendra | Power Factor | 0.99851 | 0.99845 | 0.99839 | 0.99841 | 0.9983
Nudgee Bulk | 623-1 | Nudgee BS | Hendra | ECC Rating (A) | 758 | 758 | 758 | 758 | 758
Nudgee Bulk | 623-1 | Nudgee BS | Hendra | 50 POE Load (A) | 469 | 466 | 464 | 463 | 463
Nudgee Bulk | 636-1 | Hendra | Clayfield | NCC Rating (A) | 725 | 725 | 725 | 725 | 725 | Urban | 70
Nudgee Bulk | 636-1 | Hendra | Clayfield | 10 POE Load (A) | 119.755 | 118.0835 | 119.4682 | 119.8057 | 121.639
Nudgee Bulk | 636-1 | Hendra | Clayfield | Power Factor | -0.99329 | -0.99338 | -0.9933 | -0.99328 | -0.99318
Nudgee Bulk | 636-1 | Hendra | Clayfield | ECC Rating (A) | 725 | 725 | 725 | 725 | 725
Nudgee Bulk | 636-1 | Hendra | Clayfield | 50 POE Load (A) | 205 | 204 | 204 | 203 | 203
Nudgee Bulk | 643-1 | Hendra | Hamilton | NCC Rating (A) | 753 | 753 | 753 | 753 | 753 | Urban | 70
Nudgee Bulk | 643-1 | Hendra | Hamilton | 10 POE Load (A) | 129.239 | 129.4651 | 131.2914 | 131.9966 | 134.2888
Nudgee Bulk | 643-1 | Hendra | Hamilton | Power Factor | 0.99766 | 0.99765 | 0.99756 | 0.99753 | 0.99742
Nudgee Bulk | 643-1 | Hendra | Hamilton | ECC Rating (A) | 805 | 805 | 805 | 805 | 805
Nudgee Bulk | 643-1 | Hendra | Hamilton | 50 POE Load (A) | 247 | 246 | 246 | 247 | 247
Nudgee Bulk | 674-1 | Hendra | Hamilton | NCC Rating (A) | 753 | 753 | 753 | 753 | 753 | Urban | 70
Nudgee Bulk | 674-1 | Hendra | Hamilton | 10 POE Load (A) | 128.9565 | 129.1821 | 131.0044 | 131.708 | 133.9952
Nudgee Bulk | 674-1 | Hendra | Hamilton | Power Factor | 0.99766 | 0.99765 | 0.99756 | 0.99753 | 0.99742
Nudgee Bulk | 674-1 | Hendra | Hamilton | ECC Rating (A) | 805 | 805 | 805 | 805 | 805
Nudgee Bulk | 674-1 | Hendra | Hamilton | 50 POE Load (A) | 247 | 246 | 246 | 247 | 247
Nudgee Bulk | 683-1 | Nudgee BS | Geebung | NCC Rating (A) | 488 | 488 | 488 | 488 | 488 | Urban | 70
Nudgee Bulk | 683-1 | Nudgee BS | Geebung | 10 POE Load (A) | 153.5705 | 150.5607 | 150.2928 | 148.1046 | 147.1037
Nudgee Bulk | 683-1 | Nudgee BS | Geebung | Power Factor | -0.95865 | -0.95917 | -0.95921 | -0.95959 | -0.95977
Nudgee Bulk | 683-1 | Nudgee BS | Geebung | ECC Rating (A) | 488 | 488 | 488 | 488 | 488
Nudgee Bulk | 683-1 | Nudgee BS | Geebung | 50 POE Load (A) | 231 | 226 | 222 | 220 | 220
Nudgee Bulk | 684-1 | Nudgee BS | Geebung | NCC Rating (A) | #N/A | #N/A | #N/A | #N/A | #N/A | Urban | 70
Nudgee Bulk | 684-1 | Nudgee BS | Geebung | 10 POE Load (A) | #N/A | #N/A | #N/A | #N/A | #N/A
Nudgee Bulk | 684-1 | Nudgee BS | Geebung | Power Factor | #N/A | #N/A | #N/A | #N/A | #N/A
Nudgee Bulk | 684-1 | Nudgee BS | Geebung | ECC Rating (A) | 578 | 578 | 578 | 578 | 578
Nudgee Bulk | 684-1 | Nudgee BS | Geebung | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Postmans Ridge Bulk | 376-1 | Postmans Ridge BS | Helidon | NCC Rating (A) | 290 | 290 | 290 | 290 | 290 | Rural | 170
Postmans Ridge Bulk | 376-1 | Postmans Ridge BS | Helidon | 10 POE Load (A) | 38.3844 | 37.913 | 37.8647 | 37.4898 | 37.5608
Postmans Ridge Bulk | 376-1 | Postmans Ridge BS | Helidon | Power Factor | 0.98154 | 0.98168 | 0.9817 | 0.98181 | 0.98179
Postmans Ridge Bulk | 376-1 | Postmans Ridge BS | Helidon | ECC Rating (A) | 290 | 290 | 290 | 290 | 290
Postmans Ridge Bulk | 376-1 | Postmans Ridge BS | Helidon | 50 POE Load (A) | 36 | 36 | 36 | 36 | 36
Postmans Ridge Bulk | 379-1 | Postmans Ridge BS | Carpendale | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
Postmans Ridge Bulk | 379-1 | Postmans Ridge BS | Carpendale | 10 POE Load (A) | 27.5201 | 27.5212 | 27.5376 | 27.4857 | 27.372
Postmans Ridge Bulk | 379-1 | Postmans Ridge BS | Carpendale | Power Factor | 0.99799 | 0.99799 | 0.99799 | 0.998 | 0.99802
Postmans Ridge Bulk | 379-1 | Postmans Ridge BS | Carpendale | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Postmans Ridge Bulk | 379-1 | Postmans Ridge BS | Carpendale | 50 POE Load (A) | 50 | 51 | 51 | 51 | 51
Postmans Ridge Bulk | 379-2 | Carpendale | Tenthill | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
Postmans Ridge Bulk | 379-2 | Carpendale | Tenthill | 10 POE Load (A) | 0.6669 | 0.6669 | 0.6669 | 0.6669 | 0.66691
Postmans Ridge Bulk | 379-2 | Carpendale | Tenthill | Power Factor | 0.00011888 | 0.00011884 | 0.00011884 | 0.00011878 | 0.00011882
Raceview Bulk | 354-1 | Raceview BS | Roderick St | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Urban | 70
Raceview Bulk | 354-1 | Raceview BS | Roderick St | 10 POE Load (A) | 199.5741 | 197.9847 | 198.7994 | 198.063 | 199.5136
Raceview Bulk | 354-1 | Raceview BS | Roderick St | Power Factor | 0.99571 | 0.99581 | 0.99575 | 0.99581 | 0.99571
Raceview Bulk | 354-1 | Raceview BS | Roderick St | ECC Rating (A) | 532 | 532 | 532 | 532 | 532
Raceview Bulk | 354-1 | Raceview BS | Roderick St | 50 POE Load (A) | 292 | 289 | 288 | 288 | 288
Raceview Bulk | 355-1 | Roderick St | Booval | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 70
Raceview Bulk | 355-1 | Roderick St | Booval | 10 POE Load (A) | 109.8666 | 109.2898 | 109.7299 | 109.1596 | 109.8976
Raceview Bulk | 355-1 | Roderick St | Booval | Power Factor | -0.98504 | -0.98512 | -0.98509 | -0.98511 | -0.98504
Raceview Bulk | 355-1 | Roderick St | Booval | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
Raceview Bulk | 355-1 | Roderick St | Booval | 50 POE Load (A) | 285 | 282 | 281 | 281 | 281
Raceview Bulk | 361-1 | Raceview BS | Booval | NCC Rating (A) | 870 | 870 | 870 | 870 | 870 | Urban | 70
Raceview Bulk | 361-1 | Raceview BS | Booval | 10 POE Load (A) | 236.734 | 233.9971 | 235.0007 | 234.5706 | 236.4834
Raceview Bulk | 361-1 | Raceview BS | Booval | Power Factor | 0.99309 | 0.99322 | 0.99317 | 0.9932 | 0.9931
Raceview Bulk | 361-1 | Raceview BS | Booval | ECC Rating (A) | 943 | 943 | 943 | 943 | 943
Raceview Bulk | 361-1 | Raceview BS | Booval | 50 POE Load (A) | 526 | 524 | 522 | 522 | 521
Raceview Bulk | 362-1 | Raceview BS | 362 Tee1 | NCC Rating (A) | 515 | 515 | 515 | 515 | 515 | Rural | 170
Raceview Bulk | 362-1 | Raceview BS | 362 Tee1 | 10 POE Load (A) | 101.1772 | 100.706 | 101.5977 | 101.5473 | 106.3066
Raceview Bulk | 362-1 | Raceview BS | 362 Tee1 | Power Factor | 0.99748 | 0.99763 | 0.99756 | 0.99761 | 0.99711
Raceview Bulk | 362-1 | Raceview BS | 362 Tee1 | ECC Rating (A) | 515 | 515 | 515 | 515 | 515
Raceview Bulk | 362-1 | Raceview BS | 362 Tee1 | 50 POE Load (A) | 309 | 312 | 315 | 318 | 318
Raceview Bulk | 362-2 | 362 Tee1 | Flinders | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Raceview Bulk | 362-2 | 362 Tee1 | Flinders | 10 POE Load (A) | 34.2062 | 33.2814 | 33.2582 | 32.8273 | 30.0727
Raceview Bulk | 362-2 | 362 Tee1 | Flinders | Power Factor | 0.72576 | 0.71697 | 0.71041 | 0.70614 | 0.64004
Raceview Bulk | 362-2 | 362 Tee1 | Flinders | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Raceview Bulk | 362-2 | 362 Tee1 | Flinders | 50 POE Load (A) | 129 | 129 | 128 | 127 | 127
Raceview Bulk | 362-3 | 362 Tee1 | Kalbar | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Raceview Bulk | 362-3 | 362 Tee1 | Kalbar | 10 POE Load (A) | 129.4317 | 127.9034 | 128.6189 | 128.0741 | 129.1583
Raceview Bulk | 362-3 | 362 Tee1 | Kalbar | Power Factor | 0.97962 | 0.97989 | 0.97962 | 0.97979 | 0.9794
Raceview Bulk | 362-3 | 362 Tee1 | Kalbar | ECC Rating (A) | 400 | 400 | 400 | 400 | 400
Raceview Bulk | 362-3 | 362 Tee1 | Kalbar | 50 POE Load (A) | 118 | 118 | 117 | 117 | 117
Raceview Bulk | 363-1 | Raceview BS | 363 Tee1 | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Rural | 170
Raceview Bulk | 363-1 | Raceview BS | 363 Tee1 | 10 POE Load (A) | 99.7364 | 99.2299 | 100.0897 | 100.0181 | 104.4792
Raceview Bulk | 363-1 | Raceview BS | 363 Tee1 | Power Factor | 0.99913 | 0.99922 | 0.99917 | 0.9992 | 0.9989
Raceview Bulk | 363-1 | Raceview BS | 363 Tee1 | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
Raceview Bulk | 363-1 | Raceview BS | 363 Tee1 | 50 POE Load (A) | 287 | 290 | 293 | 296 | 296
Raceview Bulk | 363-2 | 363 Tee1 | Flinders | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Rural | 170
Raceview Bulk | 363-2 | 363 Tee1 | Flinders | 10 POE Load (A) | 7.7592 | 7.1557 | 6.9479 | 6.6812 | 5.6381
Raceview Bulk | 363-2 | 363 Tee1 | Flinders | Power Factor | -0.66407 | -0.61473 | -0.59338 | -0.56003 | -0.040821
Raceview Bulk | 363-2 | 363 Tee1 | Flinders | ECC Rating (A) | 579 | 579 | 579 | 579 | 579
Raceview Bulk | 363-2 | 363 Tee1 | Flinders | 50 POE Load (A) | 150 | 153 | 157 | 160 | 160
Raceview Bulk | 363-3 | 363 Tee1 | Kalbar | NCC Rating (A) | 537 | 537 | 537 | 537 | 537 | Rural | 170
Raceview Bulk | 363-3 | 363 Tee1 | Kalbar | 10 POE Load (A) | 106.0715 | 104.86 | 105.4679 | 105.0422 | 106.1635
Raceview Bulk | 363-3 | 363 Tee1 | Kalbar | Power Factor | 1 | 1 | 1 | 1 | 1
Raceview Bulk | 363-3 | 363 Tee1 | Kalbar | ECC Rating (A) | 537 | 537 | 537 | 537 | 537
Raceview Bulk | 363-3 | 363 Tee1 | Kalbar | 50 POE Load (A) | 312 | 309 | 308 | 307 | 306
Raceview Bulk | 3960-1 | Ipswich Sth | Yamanto | NCC Rating (A) | 760 | 760 | 760 | 760 | 760 | Urban | 70
Raceview Bulk | 3960-1 | Ipswich Sth | Yamanto | 10 POE Load (A) | 236.8758 | 251.4351 | 257.6762 | 261.9082 | 273.1155
Raceview Bulk | 3960-1 | Ipswich Sth | Yamanto | Power Factor | 0.9855 | 0.98586 | 0.98562 | 0.98568 | 0.9844
Raceview Bulk | 3960-1 | Ipswich Sth | Yamanto | ECC Rating (A) | 760 | 760 | 760 | 760 | 760
Raceview Bulk | 3960-1 | Ipswich Sth | Yamanto | 50 POE Load (A) | 288 | 292 | 295 | 299 | 302
Raceview Bulk | 3972-1 | Yamanto | Flinders | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Raceview Bulk | 3972-1 | Yamanto | Flinders | 10 POE Load (A) | 106.9103 | 104.7794 | 105.1634 | 104.5106 | 109.5925
Raceview Bulk | 3972-1 | Yamanto | Flinders | Power Factor | 0.94027 | 0.93931 | 0.93838 | 0.93812 | 0.93567
Raceview Bulk | 3972-1 | Yamanto | Flinders | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Raceview Bulk | 3972-1 | Yamanto | Flinders | 50 POE Load (A) | 149 | 148 | 147 | 150 | 155
Raceview Bulk | 3980-1 | Kalbar | Boonah | NCC Rating (A) | 841 | 841 | 841 | 841 | 841 | Rural | 170
Raceview Bulk | 3980-1 | Kalbar | Boonah | 10 POE Load (A) | 56.5758 | 55.4302 | 55.6889 | 55.4479 | 55.9381
Raceview Bulk | 3980-1 | Kalbar | Boonah | Power Factor | 0.99943 | 0.99952 | 0.9995 | 0.99952 | 0.99948
Raceview Bulk | 3980-1 | Kalbar | Boonah | ECC Rating (A) | 921 | 921 | 921 | 921 | 921
Raceview Bulk | 3980-1 | Kalbar | Boonah | 50 POE Load (A) | 125 | 124 | 123 | 122 | 122
Raceview Bulk | 401-1 | Kalbar | Boonah | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Raceview Bulk | 401-1 | Kalbar | Boonah | 10 POE Load (A) | 54.2176 | 53.1209 | 53.3706 | 53.1386 | 53.6106
Raceview Bulk | 401-1 | Kalbar | Boonah | Power Factor | 0.99857 | 0.99867 | 0.99864 | 0.99866 | 0.99861
Raceview Bulk | 401-1 | Kalbar | Boonah | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Raceview Bulk | 401-1 | Kalbar | Boonah | 50 POE Load (A) | 144 | 142 | 141 | 141 | 141
Raceview Bulk | 411-1 | Raceview BS | Booval | NCC Rating (A) | 618 | 618 | 618 | 618 | 618 | Urban | 70
Raceview Bulk | 411-1 | Raceview BS | Booval | 10 POE Load (A) | 200.2915 | 197.9752 | 198.8246 | 198.4606 | 200.0794
Raceview Bulk | 411-1 | Raceview BS | Booval | Power Factor | 0.99699 | 0.99706 | 0.99703 | 0.99705 | 0.99699
Raceview Bulk | 411-1 | Raceview BS | Booval | ECC Rating (A) | 943 | 943 | 943 | 943 | 943
Raceview Bulk | 411-1 | Raceview BS | Booval | 50 POE Load (A) | 510 | 508 | 507 | 507 | 507
Raceview Bulk | 509A-1 | Raceview BS | Ipswich Sth | NCC Rating (A) | 763 | 763 | 763 | 763 | 763 | Urban | 70
Raceview Bulk | 509A-1 | Raceview BS | Ipswich Sth | 10 POE Load (A) | 255.3691 | 264.5885 | 272.3521 | 278.2485 | 289.2259
Raceview Bulk | 509A-1 | Raceview BS | Ipswich Sth | Power Factor | 0.99481 | 0.99468 | 0.99443 | 0.99432 | 0.99367
Raceview Bulk | 509A-1 | Raceview BS | Ipswich Sth | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Raceview Bulk | 509A-1 | Raceview BS | Ipswich Sth | 50 POE Load (A) | 462 | 470 | 479 | 489 | 489
Raceview Bulk | 509B-1 | Raceview BS | Cooneana | NCC Rating (A) | 509 | 509 | 509 | 509 | 509 | Rural | 170
Raceview Bulk | 509B-1 | Raceview BS | Cooneana | 10 POE Load (A) | 0.61752 | 0.61752 | 0.61752 | 0.61752 | 0.61752
Raceview Bulk | 509B-1 | Raceview BS | Cooneana | Power Factor | 8.7901e-06 | 8.7906e-06 | 8.7906e-06 | 8.7908e-06 | 8.7904e-06
Raceview Bulk | 510A-1 | Raceview BS | Ipswich Sth | NCC Rating (A) | 763 | 763 | 763 | 763 | 763 | Urban | 70
Raceview Bulk | 510A-1 | Raceview BS | Ipswich Sth | 10 POE Load (A) | 252.8035 | 261.93 | 269.6154 | 275.4525 | 286.3195
Raceview Bulk | 510A-1 | Raceview BS | Ipswich Sth | Power Factor | 0.99484 | 0.9947 | 0.99446 | 0.99435 | 0.99369
Raceview Bulk | 510A-1 | Raceview BS | Ipswich Sth | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Raceview Bulk | 510A-1 | Raceview BS | Ipswich Sth | 50 POE Load (A) | 462 | 470 | 479 | 489 | 489
Raceview Bulk | 510B-1 | Raceview BS | Cooneana | NCC Rating (A) | 476 | 476 | 476 | 476 | 476 | Rural | 170
Raceview Bulk | 510B-1 | Raceview BS | Cooneana | 10 POE Load (A) | 0.72281 | 0.72281 | 0.72281 | 0.72281 | 0.72281
Raceview Bulk | 510B-1 | Raceview BS | Cooneana | Power Factor | 1.6632e-05 | 1.6632e-05 | 1.6632e-05 | 1.6632e-05 | 1.6632e-05
Richlands Bulk | 3818-1 | Richlands BS | Wacol | NCC Rating (A) | 760 | 760 | 760 | 760 | 760 | Urban | 70
Richlands Bulk | 3818-1 | Richlands BS | Wacol | 10 POE Load (A) | 77.621 | 79.4937 | 79.4628 | 78.6994 | 78.737
Richlands Bulk | 3818-1 | Richlands BS | Wacol | Power Factor | 0.99241 | 0.99194 | 0.99195 | 0.99215 | 0.99214
Richlands Bulk | 3818-1 | Richlands BS | Wacol | ECC Rating (A) | 760 | 760 | 760 | 760 | 760
Richlands Bulk | 3818-1 | Richlands BS | Wacol | 50 POE Load (A) | 208 | 204 | 201 | 200 | 200
Richlands Bulk | 454-1 | Richlands BS | Wacol Sth | NCC Rating (A) | 475 | 475 | 475 | 475 | 475 | Urban | 70
Richlands Bulk | 454-1 | Richlands BS | Wacol Sth | 10 POE Load (A) | 178.1903 | 177.106 | 178.0007 | 176.9418 | 177.564
Richlands Bulk | 454-1 | Richlands BS | Wacol Sth | Power Factor | 0.97522 | 0.97533 | 0.97524 | 0.97534 | 0.97528
Richlands Bulk | 454-1 | Richlands BS | Wacol Sth | ECC Rating (A) | 520 | 520 | 520 | 520 | 520
Richlands Bulk | 454-1 | Richlands BS | Wacol Sth | 50 POE Load (A) | 358 | 353 | 350 | 349 | 349
Richlands Bulk | 455-1 | Richlands BS | Wacol Sth | NCC Rating (A) | 475 | 475 | 475 | 475 | 475 | Urban | 70
Richlands Bulk | 455-1 | Richlands BS | Wacol Sth | 10 POE Load (A) | 179.3309 | 178.2396 | 179.1401 | 178.0744 | 178.7006
Richlands Bulk | 455-1 | Richlands BS | Wacol Sth | Power Factor | 0.97526 | 0.97537 | 0.97528 | 0.97539 | 0.97532
Richlands Bulk | 455-1 | Richlands BS | Wacol Sth | ECC Rating (A) | 520 | 520 | 520 | 520 | 520
Richlands Bulk | 455-1 | Richlands BS | Wacol Sth | 50 POE Load (A) | 358 | 353 | 350 | 349 | 349
Richlands Bulk | 543-1 | Inala | 543 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Richlands Bulk | 543-1 | Inala | 543 Tee1 | 10 POE Load (A) | 2.969 | 2.9692 | 2.9689 | 2.9688 | 2.9685
Richlands Bulk | 543-1 | Inala | 543 Tee1 | Power Factor | -8.3786e-05 | -8.3786e-05 | -8.3786e-05 | -8.3786e-05 | -8.3786e-05
Richlands Bulk | 543-1 | Inala | 543 Tee1 | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Richlands Bulk | 543-1 | Inala | 543 Tee1 | 50 POE Load (A) | 353 | 351 | 349 | 348 | 348
Richlands Bulk | 543-2 | 543 Tee1 | Coopers Plains | NCC Rating (A) | 348 | 348 | 348 | 348 | 348 | Urban | 70
Richlands Bulk | 543-2 | 543 Tee1 | Coopers Plains | 10 POE Load (A) | 0.21259 | 0.21261 | 0.21259 | 0.21258 | 0.21255
Richlands Bulk | 543-2 | 543 Tee1 | Coopers Plains | Power Factor | -7.5155e-06 | -7.5153e-06 | -7.5152e-06 | -7.5153e-06 | -7.5143e-06
Richlands Bulk | 543-2 | 543 Tee1 | Coopers Plains | ECC Rating (A) | 348 | 348 | 348 | 348 | 348
Richlands Bulk | 543-2 | 543 Tee1 | Coopers Plains | 50 POE Load (A) | 305 | 257 | 244 | 238 | 238
Richlands Bulk | 543-3 | 543 Tee1 | Heathwood | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Richlands Bulk | 543-3 | 543 Tee1 | Heathwood | 10 POE Load (A) | 2.2192 | 2.2194 | 2.2191 | 2.2191 | 2.2188
Richlands Bulk | 543-3 | 543 Tee1 | Heathwood | Power Factor | 9.1011e-05 | 9.1011e-05 | 9.1011e-05 | 9.1011e-05 | 9.1011e-05
Richlands Bulk | 543-3 | 543 Tee1 | Heathwood | ECC Rating (A) | 855 | 855 | 855 | 855 | 855
Richlands Bulk | 543-3 | 543 Tee1 | Heathwood | 50 POE Load (A) | 374 | 372 | 370 | 369 | 369
Richlands Bulk | 616-1 | Richlands BS | Darra | NCC Rating (A) | 434 | 434 | 434 | 434 | 434 | Urban | 70
Richlands Bulk | 616-1 | Richlands BS | Darra | 10 POE Load (A) | 184.3351 | 182.4616 | 182.1429 | 181.0172 | 180.6125
Richlands Bulk | 616-1 | Richlands BS | Darra | Power Factor | 0.78432 | 0.77661 | 0.77563 | 0.77058 | 0.76972
Richlands Bulk | 616-1 | Richlands BS | Darra | ECC Rating (A) | 468 | 468 | 468 | 468 | 468
Richlands Bulk | 616-1 | Richlands BS | Darra | 50 POE Load (A) | 308 | 304 | 300 | 299 | 299
Richlands Bulk | 617-1 | Richlands BS | Darra | NCC Rating (A) | 434 | 434 | 434 | 434 | 434 | Urban | 70
Richlands Bulk | 617-1 | Richlands BS | Darra | 10 POE Load (A) | 190.4005 | 188.4621 | 188.1325 | 186.9676 | 186.5492
Richlands Bulk | 617-1 | Richlands BS | Darra | Power Factor | 0.78483 | 0.77714 | 0.77615 | 0.77111 | 0.77026
Richlands Bulk | 617-1 | Richlands BS | Darra | ECC Rating (A) | 468 | 468 | 468 | 468 | 468
Richlands Bulk | 617-1 | Richlands BS | Darra | 50 POE Load (A) | 312 | 308 | 305 | 303 | 300
Richlands Bulk | 618-1 | Richlands BS | Inala | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Richlands Bulk | 618-1 | Richlands BS | Inala | 10 POE Load (A) | 300.5599 | 296.9823 | 301.4462 | 302.8172 | 307.636
Richlands Bulk | 618-1 | Richlands BS | Inala | Power Factor | 0.98859 | 0.98878 | 0.98855 | 0.98847 | 0.9882
Richlands Bulk | 618-1 | Richlands BS | Inala | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Richlands Bulk | 618-1 | Richlands BS | Inala | 50 POE Load (A) | 498 | 497 | 495 | 495 | 493
Richlands Bulk | 619-1 | Richlands BS | Inala | NCC Rating (A) | 603 | 603 | 603 | 603 | 603 | Urban | 70
Richlands Bulk | 619-1 | Richlands BS | Inala | 10 POE Load (A) | 194.1182 | 191.808 | 194.6905 | 195.5758 | 198.6858
Richlands Bulk | 619-1 | Richlands BS | Inala | Power Factor | 0.98887 | 0.98906 | 0.98883 | 0.98876 | 0.98849
Richlands Bulk | 619-1 | Richlands BS | Inala | ECC Rating (A) | 603 | 603 | 603 | 603 | 603
Richlands Bulk | 619-1 | Richlands BS | Inala | 50 POE Load (A) | 513 | 512 | 511 | 512 | 512
Richlands Bulk | 620-1 | Richlands BS | Oxley | NCC Rating (A) | 342 | 342 | 342 | 342 | 342 | Urban | 70
Richlands Bulk | 620-1 | Richlands BS | Oxley | 10 POE Load (A) | 134.1824 | 130.8887 | 130.3311 | 128.5923 | 127.8999
Richlands Bulk | 620-1 | Richlands BS | Oxley | Power Factor | -0.97752 | -0.97782 | -0.97787 | -0.97802 | -0.97808
Richlands Bulk | 620-1 | Richlands BS | Oxley | ECC Rating (A) | 378 | 378 | 378 | 378 | 378
Richlands Bulk | 620-1 | Richlands BS | Oxley | 50 POE Load (A) | 250 | 247 | 244 | 243 | 243
Richlands Bulk | 621-1 | Richlands BS | Oxley | NCC Rating (A) | 342 | 342 | 342 | 342 | 342 | Urban | 70
Richlands Bulk | 621-1 | Richlands BS | Oxley | 10 POE Load (A) | 127.7036 | 124.5691 | 124.0385 | 122.3837 | 121.7248
Richlands Bulk | 621-1 | Richlands BS | Oxley | Power Factor | -0.97347 | -0.9738 | -0.97385 | -0.97402 | -0.97409
Richlands Bulk | 621-1 | Richlands BS | Oxley | ECC Rating (A) | 378 | 378 | 378 | 378 | 378
Richlands Bulk | 621-1 | Richlands BS | Oxley | 50 POE Load (A) | 250 | 247 | 244 | 243 | 243
Richlands Bulk | 641-1 | Darra | Jindalee | NCC Rating (A) | 744 | 744 | 744 | 744 | 744 | Urban | 70
Richlands Bulk | 641-1 | Darra | Jindalee | 10 POE Load (A) | 78.9737 | 76.7585 | 76.0204 | 74.9079 | 74.3922
Richlands Bulk | 641-1 | Darra | Jindalee | Power Factor | -0.99693 | -0.99701 | -0.99687 | -0.99665 | -0.99655
Richlands Bulk | 641-1 | Darra | Jindalee | ECC Rating (A) | 826 | 826 | 826 | 826 | 826
Richlands Bulk | 641-1 | Darra | Jindalee | 50 POE Load (A) | 147 | 145 | 144 | 143 | 143
Richlands Bulk | 642-1 | Darra | Jindalee | NCC Rating (A) | 744 | 744 | 744 | 744 | 744 | Urban | 70
Richlands Bulk | 642-1 | Darra | Jindalee | 10 POE Load (A) | 77.3926 | 75.22 | 74.4834 | 73.3726 | 72.8576
Richlands Bulk | 642-1 | Darra | Jindalee | Power Factor | -0.99645 | -0.99653 | -0.99656 | -0.9966 | -0.99662
Richlands Bulk | 642-1 | Darra | Jindalee | ECC Rating (A) | 826 | 826 | 826 | 826 | 826
Richlands Bulk | 642-1 | Darra | Jindalee | 50 POE Load (A) | 147 | 145 | 144 | 143 | 143
Richlands Bulk | 679-1 | Richlands BS | Wacol | NCC Rating (A) | 663 | 663 | 663 | 663 | 663 | Urban | 70
Richlands Bulk | 679-1 | Richlands BS | Wacol | 10 POE Load (A) | 78.6528 | 80.5507 | 80.5194 | 79.7457 | 79.7838
Richlands Bulk | 679-1 | Richlands BS | Wacol | Power Factor | -0.96537 | -0.96514 | -0.96514 | -0.96524 | -0.96523
Richlands Bulk | 679-1 | Richlands BS | Wacol | ECC Rating (A) | 663 | 663 | 663 | 663 | 663
Richlands Bulk | 679-1 | Richlands BS | Wacol | 50 POE Load (A) | 225 | 221 | 218 | 217 | 217
Richlands Bulk | 680-1 | Richlands BS | Wacol | NCC Rating (A) | 760 | 760 | 760 | 760 | 760 | Urban | 70
Richlands Bulk | 680-1 | Richlands BS | Wacol | 10 POE Load (A) | 158.112 | 161.993 | 161.9289 | 160.3465 | 160.4244
Richlands Bulk | 680-1 | Richlands BS | Wacol | Power Factor | 0.97454 | 0.97382 | 0.97384 | 0.97414 | 0.97413
Richlands Bulk | 680-1 | Richlands BS | Wacol | ECC Rating (A) | 760 | 760 | 760 | 760 | 760
Richlands Bulk | 680-1 | Richlands BS | Wacol | 50 POE Load (A) | 97 | 95 | 94 | 93 | 93
Richlands Bulk | 700-1 | Richlands BS | Darra | NCC Rating (A) | 551 | 551 | 551 | 551 | 551 | Urban | 70
Richlands Bulk | 700-1 | Richlands BS | Darra | 10 POE Load (A) | 145.8453 | 144.3665 | 144.1148 | 143.2264 | 142.9066
Richlands Bulk | 700-1 | Richlands BS | Darra | Power Factor | 0.83089 | 0.82396 | 0.82307 | 0.81852 | 0.81774
Richlands Bulk | 700-1 | Richlands BS | Darra | ECC Rating (A) | 551 | 551 | 551 | 551 | 551
Richlands Bulk | 700-1 | Richlands BS | Darra | 50 POE Load (A) | 243 | 240 | 238 | 236 | 234
Runcorn Bulk | 3440-1 | Runcorn BS | Sunnybank | NCC Rating (A) | 601 | 601 | 601 | 601 | 601 | Urban | 70
Runcorn Bulk | 3440-1 | Runcorn BS | Sunnybank | 10 POE Load (A) | 296.0359 | 314.7489 | 315.2138 | 312.3483 | 312.2248
Runcorn Bulk | 3440-1 | Runcorn BS | Sunnybank | Power Factor | 0.98176 | 0.98105 | 0.98103 | 0.98115 | 0.98116
Runcorn Bulk | 3440-1 | Runcorn BS | Sunnybank | ECC Rating (A) | 601 | 601 | 601 | 601 | 601
Runcorn Bulk | 3440-1 | Runcorn BS | Sunnybank | 50 POE Load (A) | 394 | 394 | 394 | 394 | 394
Runcorn Bulk | 433-1 | Runcorn BS | Calamvale | NCC Rating (A) | 450 | 450 | 450 | 450 | 450 | Urban | 70
Runcorn Bulk | 433-1 | Runcorn BS | Calamvale | 10 POE Load (A) | 2.3615 | 2.3615 | 2.3615 | 2.3615 | 2.3615
Runcorn Bulk | 433-1 | Runcorn BS | Calamvale | Power Factor | 4.0608e-05 | 4.0608e-05 | 4.0608e-05 | 4.0608e-05 | 4.0608e-05
Runcorn Bulk | 433-1 | Runcorn BS | Calamvale | ECC Rating (A) | 450 | 450 | 450 | 450 | 450
Runcorn Bulk | 433-1 | Runcorn BS | Calamvale | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Runcorn Bulk | 434-1 | Runcorn | Calamvale | NCC Rating (A) | 450 | 450 | 450 | 450 | 450 | Urban | 70
Runcorn Bulk | 434-1 | Runcorn | Calamvale | 10 POE Load (A) | 1.6855 | 1.6856 | 1.6855 | 1.6855 | 1.6854
Runcorn Bulk | 434-1 | Runcorn | Calamvale | Power Factor | 6.272e-05 | 6.272e-05 | 6.272e-05 | 6.272e-05 | 6.272e-05
Runcorn Bulk | 434-1 | Runcorn | Calamvale | ECC Rating (A) | 450 | 450 | 450 | 450 | 450
Runcorn Bulk | 434-1 | Runcorn | Calamvale | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Runcorn Bulk | 459A-1 | Upper Mt Gravatt | Sunnybank | NCC Rating (A) | #N/A | #N/A | #N/A | #N/A | #N/A | Urban | 70
Runcorn Bulk | 459A-1 | Upper Mt Gravatt | Sunnybank | 10 POE Load (A) | #N/A | #N/A | #N/A | #N/A | #N/A
Runcorn Bulk | 459A-1 | Upper Mt Gravatt | Sunnybank | Power Factor | #N/A | #N/A | #N/A | #N/A | #N/A
Runcorn Bulk | 459A-1 | Upper Mt Gravatt | Sunnybank | ECC Rating (A) | 818 | 818 | 0 | 0 | 0
Runcorn Bulk | 459A-1 | Upper Mt Gravatt | Sunnybank | 50 POE Load (A) | 537 | 575 | 0 | 0 | 0
Runcorn Bulk | 459B-1 | Runcorn BS | Upper Mt Gravatt | NCC Rating (A) | #N/A | #N/A | #N/A | #N/A | #N/A | Urban | 70
Runcorn Bulk | 459B-1 | Runcorn BS | Upper Mt Gravatt | 10 POE Load (A) | #N/A | #N/A | #N/A | #N/A | #N/A
Runcorn Bulk | 459B-1 | Runcorn BS | Upper Mt Gravatt | Power Factor | #N/A | #N/A | #N/A | #N/A | #N/A
Runcorn Bulk | 459B-1 | Runcorn BS | Upper Mt Gravatt | ECC Rating (A) | 848 | 848 | 0 | 0 | 0
Runcorn Bulk | 459B-1 | Runcorn BS | Upper Mt Gravatt | 50 POE Load (A) | 383 | 411 | 0 | 0 | 0
Runcorn Bulk | 667-1 | Runcorn BS | Acacia Ridge | NCC Rating (A) | 453 | 453 | 453 | 453 | 453 | Urban | 70
Runcorn Bulk | 667-1 | Runcorn BS | Acacia Ridge | 10 POE Load (A) | 27.7987 | 27.7987 | 27.7987 | 27.7987 | 27.7987
Runcorn Bulk | 667-1 | Runcorn BS | Acacia Ridge | Power Factor | 9.2863e-05 | 9.2863e-05 | 9.2863e-05 | 9.2863e-05 | 9.2863e-05
Runcorn Bulk | 667-1 | Runcorn BS | Acacia Ridge | ECC Rating (A) | 453 | 453 | 453 | 453 | 453
Runcorn Bulk | 667-1 | Runcorn BS | Acacia Ridge | 50 POE Load (A) | 30 | 30 | 30 | 30 | 30
Runcorn Bulk | 668-1 | Runcorn BS | Acacia Ridge | NCC Rating (A) | 453 | 453 | 453 | 453 | 453 | Urban | 70
Runcorn Bulk | 668-1 | Runcorn BS | Acacia Ridge | 10 POE Load (A) | 27.9347 | 27.9347 | 27.9347 | 27.9347 | 27.9347
Runcorn Bulk | 668-1 | Runcorn BS | Acacia Ridge | Power Factor | -1 | -1 | -1 | -1 | -1
Runcorn Bulk | 668-1 | Runcorn BS | Acacia Ridge | ECC Rating (A) | 453 | 453 | 453 | 453 | 453
Runcorn Bulk | 668-1 | Runcorn BS | Acacia Ridge | 50 POE Load (A) | 30 | 30 | 30 | 30 | 30
Runcorn Bulk | 690-1 | Runcorn BS | Runcorn | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Runcorn Bulk | 690-1 | Runcorn BS | Runcorn | 10 POE Load (A) | 193.7559 | 193.1432 | 194.3896 | 194.3333 | 197.0421
Runcorn Bulk | 690-1 | Runcorn BS | Runcorn | Power Factor | 0.99389 | 0.99392 | 0.99386 | 0.99386 | 0.99372
Runcorn Bulk | 690-1 | Runcorn BS | Runcorn | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Runcorn Bulk | 690-1 | Runcorn BS | Runcorn | 50 POE Load (A) | 462 | 459 | 455 | 452 | 451
Runcorn Bulk | 691-1 | Runcorn BS | Runcorn | NCC Rating (A) | 685 | 685 | 685 | 685 | 685 | Urban | 70
Runcorn Bulk | 691-1 | Runcorn BS | Runcorn | 10 POE Load (A) | 153.3382 | 152.8534 | 153.8398 | 153.7952 | 155.9389
Runcorn Bulk | 691-1 | Runcorn BS | Runcorn | Power Factor | 0.99416 | 0.99419 | 0.99412 | 0.99413 | 0.99399
Runcorn Bulk | 691-1 | Runcorn BS | Runcorn | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Runcorn Bulk | 691-1 | Runcorn BS | Runcorn | 50 POE Load (A) | 462 | 460 | 455 | 453 | 451
Runcorn Bulk | 694-1 | Runcorn BS | Eight Mile Plains Bus 1 | NCC Rating (A) | 581 | 581 | 581 | 581 | 581 | Urban | 70
Runcorn Bulk | 694-1 | Runcorn BS | Eight Mile Plains Bus 1 | 10 POE Load (A) | 199.1045 | 193.0852 | 192.6178 | 192.2971 | 194.4848
Runcorn Bulk | 694-1 | Runcorn BS | Eight Mile Plains Bus 1 | Power Factor | 0.99987 | 0.99996 | 0.99996 | 0.99996 | 0.99994
Runcorn Bulk | 694-1 | Runcorn BS | Eight Mile Plains Bus 1 | ECC Rating (A) | 581 | 581 | 581 | 581 | 581
Runcorn Bulk | 694-1 | Runcorn BS | Eight Mile Plains Bus 1 | 50 POE Load (A) | 391 | 387 | 382 | 380 | 380
Sandgate Bulk | 3290-1 | Sandgate BS | Bald Hills Bus 1 | NCC Rating (A) | 912 | 912 | 912 | 912 | 912 | Urban | 70
Sandgate Bulk | 3290-1 | Sandgate BS | Bald Hills Bus 1 | 10 POE Load (A) | 51.6685 | 51.0995 | 51.1457 | 50.9179 | 51.2874
Sandgate Bulk | 3290-1 | Sandgate BS | Bald Hills Bus 1 | Power Factor | 1 | 1 | 1 | 1 | 1
Sandgate Bulk | 3290-1 | Sandgate BS | Bald Hills Bus 1 | ECC Rating (A) | 912 | 912 | 912 | 912 | 912
Sandgate Bulk | 3290-1 | Sandgate BS | Bald Hills Bus 1 | 50 POE Load (A) | 201 | 200 | 198 | 197 | 197
Sandgate Bulk | 505-1 | Sandgate BS | Zilmere | NCC Rating (A) | 912 | 912 | 912 | 912 | 912 | Urban | 70
Sandgate Bulk | 505-1 | Sandgate BS | Zilmere | 10 POE Load (A) | 213.8865 | 211.9066 | 212.5772 | 211.5378 | 213.2895
Sandgate Bulk | 505-1 | Sandgate BS | Zilmere | Power Factor | -0.98023 | -0.98057 | -0.98043 | -0.98064 | -0.98028
Sandgate Bulk | 505-1 | Sandgate BS | Zilmere | ECC Rating (A) | 912 | 912 | 912 | 912 | 912
Sandgate Bulk | 505-1 | Sandgate BS | Zilmere | 50 POE Load (A) | 352 | 341 | 338 | 336 | 333
Sandgate Bulk | 524-1 | Sandgate BS | Geebung | NCC Rating (A) | 521 | 521 | 521 | 521 | 521 | Urban | 70
Sandgate Bulk | 524-1 | Sandgate BS | Geebung | 10 POE Load (A) | 144.0049 | 142.6765 | 143.1261 | 142.4292 | 143.6038
Sandgate Bulk | 524-1 | Sandgate BS | Geebung | Power Factor | -0.99131 | -0.99155 | -0.99145 | -0.9916 | -0.99135
Sandgate Bulk | 524-1 | Sandgate BS | Geebung | ECC Rating (A) | 521 | 521 | 521 | 521 | 521
Sandgate Bulk | 524-1 | Sandgate BS | Geebung | 50 POE Load (A) | 263 | 253 | 251 | 249 | 247
Sandgate Bulk | 524-2 | Geebung | Zillmere | NCC Rating (A) | 441 | 441 | 441 | 441 | 441 | Urban | 70
Sandgate Bulk | 524-2 | Geebung | Zillmere | 10 POE Load (A) | 149.0006 | 147.6517 | 148.1114 | 147.3988 | 148.5998
Sandgate Bulk | 524-2 | Geebung | Zillmere | Power Factor | 0.99808 | 0.99819 | 0.99814 | 0.99821 | 0.9981
Sandgate Bulk | 524-2 | Geebung | Zillmere | ECC Rating (A) | 441 | 441 | 441 | 441 | 441
Sandgate Bulk | 524-2 | Geebung | Zillmere | 50 POE Load (A) | 252 | 242 | 240 | 238 | 238
Sandgate Bulk | 561-1 | Sandgate BS | Brighton TR1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Sandgate Bulk | 561-1 | Sandgate BS | Brighton TR1 | 10 POE Load (A) | 82.6343 | 81.6292 | 81.6548 | 81.2169 | 81.6957
Sandgate Bulk | 561-1 | Sandgate BS | Brighton TR1 | Power Factor | 0.9963 | 0.99636 | 0.99636 | 0.99639 | 0.99636
Sandgate Bulk | 561-1 | Sandgate BS | Brighton TR1 | ECC Rating (A) | 841 | 841 | 841 | 841 | 841
Sandgate Bulk | 561-1 | Sandgate BS | Brighton TR1 | 50 POE Load (A) | 147 | 147 | 146 | 145 | 143
Sandgate Bulk | 656-1 | Sandgate BS | Brighton TR2 | NCC Rating (A) | 379 | 379 | 379 | 379 | 379 | Urban | 70
Sandgate Bulk | 656-1 | Sandgate BS | Brighton TR2 | 10 POE Load (A) | 79.2571 | 78.2929 | 78.3175 | 77.8974 | 78.3567
Sandgate Bulk | 656-1 | Sandgate BS | Brighton TR2 | Power Factor | 0.99999 | 0.99999 | 0.99999 | 1 | 0.99999
Sandgate Bulk | 656-1 | Sandgate BS | Brighton TR2 | ECC Rating (A) | 379 | 379 | 379 | 379 | 379
Sandgate Bulk | 656-1 | Sandgate BS | Brighton TR2 | 50 POE Load (A) | 195 | 194 | 192 | 191 | 191
Sandgate Bulk | 664-1 | Geebung | Zillmere | NCC Rating (A) | 441 | 441 | 441 | 441 | 441 | Urban | 70
Sandgate Bulk | 664-1 | Geebung | Zillmere | 10 POE Load (A) | 24.7883 | 24.7905 | 24.7897 | 24.7909 | 24.7889
Sandgate Bulk | 664-1 | Geebung | Zillmere | Power Factor | -1 | -1 | -1 | -1 | -1
Sandgate Bulk | 664-1 | Geebung | Zillmere | ECC Rating (A) | 441 | 441 | 441 | 441 | 441
Sandgate Bulk | 664-1 | Geebung | Zillmere | 50 POE Load (A) | 27 | 27 | 27 | 27 | 27
Sandgate Bulk | 671-1 | Sandagate BS | Zillmere | NCC Rating (A) | 527 | 527 | 527 | 527 | 527 | Urban | 70
Sandgate Bulk | 671-1 | Sandagate BS | Zillmere | 10 POE Load (A) | 125.6418 | 124.9981 | 125.3932 | 124.7807 | 125.8129
Sandgate Bulk | 671-1 | Sandagate BS | Zillmere | Power Factor | 1 | 1 | 1 | 0.99999 | 1
Sandgate Bulk | 671-1 | Sandagate BS | Zillmere | ECC Rating (A) | 495 | 599 | 599 | 599 | 599
Sandgate Bulk | 671-1 | Sandagate BS | Zillmere | 50 POE Load (A) | 189 | 228 | 226 | 225 | 225
Stafford Bulk | 502-1 | Kedron | Clayfield | NCC Rating (A) | #N/A | #N/A | #N/A | #N/A | #N/A | Urban | 70
Stafford Bulk | 502-1 | Kedron | Clayfield | 10 POE Load (A) | #N/A | #N/A | #N/A | #N/A | #N/A
Stafford Bulk | 502-1 | Kedron | Clayfield | Power Factor | #N/A | #N/A | #N/A | #N/A | #N/A
Stafford Bulk | 502-1 | Kedron | Clayfield | ECC Rating (A) | 0 | 0 | 0 | 0 | 0
Stafford Bulk | 502-1 | Kedron | Clayfield | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Stafford Bulk | 522-1 | Kedron | Chermside | NCC Rating (A) | #N/A | #N/A | #N/A | #N/A | #N/A | Urban | 70
Stafford Bulk | 522-1 | Kedron | Chermside | 10 POE Load (A) | #N/A | #N/A | #N/A | #N/A | #N/A
Stafford Bulk | 522-1 | Kedron | Chermside | Power Factor | #N/A | #N/A | #N/A | #N/A | #N/A
Stafford Bulk | 525-1 | Chermside | Zillmere | NCC Rating (A) | #N/A | #N/A | #N/A | #N/A | #N/A | Urban | 70
Stafford Bulk | 525-1 | Chermside | Zillmere | 10 POE Load (A) | #N/A | #N/A | #N/A | #N/A | #N/A
Stafford Bulk | 525-1 | Chermside | Zillmere | Power Factor | #N/A | #N/A | #N/A | #N/A | #N/A
Stafford Bulk | 534-1 | Kedron | Clayfield | NCC Rating (A) | #N/A | #N/A | #N/A | #N/A | #N/A | Urban | 70
Stafford Bulk | 534-1 | Kedron | Clayfield | 10 POE Load (A) | #N/A | #N/A | #N/A | #N/A | #N/A
Stafford Bulk | 534-1 | Kedron | Clayfield | Power Factor | #N/A | #N/A | #N/A | #N/A | #N/A
Stafford Bulk | 534-1 | Kedron | Clayfield | ECC Rating (A) | 0 | 0 | 0 | 0 | 0
Stafford Bulk | 534-1 | Kedron | Clayfield | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Stafford Bulk | 548-1 | Stafford BS | Enoggera | NCC Rating (A) | 886 | 886 | 886 | 886 | 886 | Urban | 70
Stafford Bulk | 548-1 | Stafford BS | Enoggera | 10 POE Load (A) | 426.7236 | 422.4585 | 423.7249 | 422.9272 | 425.5651
Stafford Bulk | 548-1 | Stafford BS | Enoggera | Power Factor | 0.99158 | 0.99166 | 0.99165 | 0.99167 | 0.99165
Stafford Bulk | 548-1 | Stafford BS | Enoggera | ECC Rating (A) | 1020 | 1020 | 1020 | 1020 | 1020
Stafford Bulk | 548-1 | Stafford BS | Enoggera | 50 POE Load (A) | 801 | 798 | 795 | 793 | 793
Stafford Bulk | 550-1 | Stafford BS | Chermside | NCC Rating (A) | 748 | 748 | 748 | 748 | 748 | Urban | 70
Stafford Bulk | 550-1 | Stafford BS | Chermside | 10 POE Load (A) | 236.7131 | 116.4708 | 116.8068 | 115.8764 | 116.143
Stafford Bulk | 550-1 | Stafford BS | Chermside | Power Factor | 0.99234 | 0.99826 | 0.9983 | 0.99836 | 0.99834
Stafford Bulk | 550-1 | Stafford BS | Chermside | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Stafford Bulk | 550-1 | Stafford BS | Chermside | 50 POE Load (A) | 541 | 538 | 536 | 535 | 535
Stafford Bulk | 551-1 | Stafford BS | Chermside | NCC Rating (A) | 748 | 748 | 748 | 748 | 748 | Urban | 70
Stafford Bulk | 551-1 | Stafford BS | Chermside | 10 POE Load (A) | 236.2624 | 116.25 | 116.5853 | 115.6567 | 115.9228
Stafford Bulk | 551-1 | Stafford BS | Chermside | Power Factor | 0.99235 | 0.99826 | 0.99831 | 0.99837 | 0.99835
Stafford Bulk | 551-1 | Stafford BS | Chermside | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Stafford Bulk | 551-1 | Stafford BS | Chermside | 50 POE Load (A) | 541 | 538 | 536 | 535 | 535
Stafford Bulk | 567-1 | Stafford BS | Kedron | NCC Rating (A) | 613 | 613 | 613 | 613 | 613 | Urban | 70
Stafford Bulk | 567-1 | Stafford BS | Kedron | 10 POE Load (A) | 197.502 | 196.599 | 208.8209 | 208.5945 | 210.8955
Stafford Bulk | 567-1 | Stafford BS | Kedron | Power Factor | 0.99996 | 0.99997 | 0.9998 | 0.99981 | 0.99977
Stafford Bulk | 567-1 | Stafford BS | Kedron | ECC Rating (A) | 685 | 685 | 685 | 685 | 685
Stafford Bulk | 567-1 | Stafford BS | Kedron | 50 POE Load (A) | 382 | 381 | 380 | 380 | 379
Stafford Bulk | 568-1 | Stafford BS | Kedron | NCC Rating (A) | 613 | 613 | 613 | 613 | 613 | Urban | 70
Stafford Bulk | 568-1 | Stafford BS | Kedron | 10 POE Load (A) | 199.0136 | 198.1037 | 210.4186 | 210.1904 | 212.509
Stafford Bulk | 568-1 | Stafford BS | Kedron | Power Factor | -0.99292 | -0.99297 | -0.99229 | -0.99231 | -0.99218
Stafford Bulk | 568-1 | Stafford BS | Kedron | ECC Rating (A) | 685 | 685 | 685 | 685 | 685
Stafford Bulk | 568-1 | Stafford BS | Kedron | 50 POE Load (A) | 382 | 381 | 380 | 380 | 379
Stafford Bulk | 594-1 | Stafford BS | Enoggera | NCC Rating (A) | 886 | 886 | 886 | 886 | 886 | Urban | 70
Stafford Bulk | 594-1 | Stafford BS | Enoggera | 10 POE Load (A) | 424.0329 | 419.7947 | 421.0531 | 420.2604 | 422.8817
Stafford Bulk | 594-1 | Stafford BS | Enoggera | Power Factor | 0.9916 | 0.99168 | 0.99167 | 0.99169 | 0.99167
Stafford Bulk | 594-1 | Stafford BS | Enoggera | ECC Rating (A) | 1020 | 1020 | 1020 | 1020 | 1020
Stafford Bulk | 594-1 | Stafford BS | Enoggera | 50 POE Load (A) | 801 | 798 | 795 | 793 | 790
Stafford Bulk | 595-1 | Enoggera | Grovely | NCC Rating (A) | 720 | 720 | 720 | 720 | 720 | Urban | 70
Stafford Bulk | 595-1 | Enoggera | Grovely | 10 POE Load (A) | 156.2423 | 151.9971 | 151.9361 | 150.8783 | 151.5507
Stafford Bulk | 595-1 | Enoggera | Grovely | Power Factor | 0.9987 | 0.99887 | 0.99888 | 0.99892 | 0.99889
Stafford Bulk | 595-1 | Enoggera | Grovely | ECC Rating (A) | 720 | 720 | 720 | 720 | 720
Stafford Bulk | 595-1 | Enoggera | Grovely | 50 POE Load (A) | 270 | 268 | 266 | 264 | 264
Stafford Bulk | 596-1 | Enoggera | Grovely | NCC Rating (A) | 720 | 720 | 720 | 720 | 720 | Urban | 70
Stafford Bulk | 596-1 | Enoggera | Grovely | 10 POE Load (A) | 157.2887 | 153.0149 | 152.9536 | 151.8887 | 152.5656
Stafford Bulk | 596-1 | Enoggera | Grovely | Power Factor | 0.99867 | 0.99885 | 0.99885 | 0.99889 | 0.99887
Stafford Bulk | 596-1 | Enoggera | Grovely | ECC Rating (A) | 720 | 720 | 720 | 720 | 720
Stafford Bulk | 596-1 | Enoggera | Grovely | 50 POE Load (A) | 270 | 268 | 266 | 264 | 264
Stafford Bulk | 607-1 | Chermside | Zillmere | NCC Rating (A) | 332 | 332 | 332 | 332 | 332 | Urban | 70
Stafford Bulk | 607-1 | Chermside | Zillmere | 10 POE Load (A) | 0.21083 | 0.21111 | 0.8338 | 0.83381 | 0.83381
Stafford Bulk | 607-1 | Chermside | Zillmere | Power Factor | 4.7374e-06 | 4.7372e-06 | 1.3215e-05 | 1.3215e-05 | 1.3215e-05
Sunrise Hills Bulk | 308-1 | Perigian | 308 Tee1 | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
Sunrise Hills Bulk | 308-1 | Perigian | 308 Tee1 | 10 POE Load (A) | 468.0207 | 465.3375 | 530.754 | 530.2742 | 538.1375
Sunrise Hills Bulk | 308-1 | Perigian | 308 Tee1 | Power Factor | 0.98906 | 0.98916 | 0.98705 | 0.98707 | 0.98676
Sunrise Hills Bulk | 308-1 | Perigian | 308 Tee1 | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Sunrise Hills Bulk | 308-1 | Perigian | 308 Tee1 | 50 POE Load (A) | 410 | 409 | 409 | 408 | 408
Sunrise Hills Bulk | 308-2 | 308 Tee1 | Coolum | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
Sunrise Hills Bulk | 308-2 | 308 Tee1 | Coolum | 10 POE Load (A) | 468.0372 | 465.3539 | 530.7713 | 530.2915 | 538.155
Sunrise Hills Bulk | 308-2 | 308 Tee1 | Coolum | Power Factor | 0.99192 | 0.99199 | 0.99059 | 0.99061 | 0.99039
Sunrise Hills Bulk | 308-2 | 308 Tee1 | Coolum | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Sunrise Hills Bulk | 308-2 | 308 Tee1 | Coolum | 50 POE Load (A) | 410 | 409 | 409 | 408 | 408
Sunrise Hills Bulk | 308-3 | 308 Tee1 | 307 Tee2 | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
Sunrise Hills Bulk | 308-3 | 308 Tee1 | 307 Tee2 | 10 POE Load (A) | 0.0070173 | 0.0070207 | 0.0069458 | 0.0069457 | 0.0069345
Sunrise Hills Bulk | 308-3 | 308 Tee1 | 307 Tee2 | Power Factor | -1 | -1 | -1 | -1 | -1
Sunrise Hills Bulk | 3100-1 | Sunrise Hills BS | 3100 Tee1 | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
Sunrise Hills Bulk | 3100-1 | Sunrise Hills BS | 3100 Tee1 | 10 POE Load (A) | 681.054 | 677.6659 | 747.0682 | 747.5993 | 759.0001
Sunrise Hills Bulk | 3100-1 | Sunrise Hills BS | 3100 Tee1 | Power Factor | -0.00040897 | -0.00040879 | -0.00040913 | -0.00040916 | -0.00040902
Sunrise Hills Bulk | 3100-1 | Sunrise Hills BS | 3100 Tee1 | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Sunrise Hills Bulk | 3100-1 | Sunrise Hills BS | 3100 Tee1 | 50 POE Load (A) | 599 | 599 | 599 | 598 | 598
Sunrise Hills Bulk | 3100-2 | 3100 Tee1 | Peregian | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
Sunrise Hills Bulk | 3100-2 | 3100 Tee1 | Peregian | 10 POE Load (A) | 681.1968 | 677.808 | 747.2213 | 747.7524 | 759.1552
Sunrise Hills Bulk | 3100-2 | 3100 Tee1 | Peregian | Power Factor | -0.98363 | -0.98379 | -0.98102 | -0.98103 | -0.9805
Sunrise Hills Bulk | 3100-2 | 3100 Tee1 | Peregian | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Sunrise Hills Bulk | 3100-2 | 3100 Tee1 | Peregian | 50 POE Load (A) | 594 | 594 | 594 | 593 | 593
Sunrise Hills Bulk | 343-1 | Sunrise Hills BS | 343 Tee1 | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Rural | 170
Sunrise Hills Bulk | 343-1 | Sunrise Hills BS | 343 Tee1 | 10 POE Load (A) | 375.6655 | 363.7725 | 331.4712 | 328.7752 | 329.5692
Sunrise Hills Bulk | 343-1 | Sunrise Hills BS | 343 Tee1 | Power Factor | 0.98558 | 0.9862 | 0.98945 | 0.9896 | 0.98959
Sunrise Hills Bulk | 343-1 | Sunrise Hills BS | 343 Tee1 | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Sunrise Hills Bulk | 343-1 | Sunrise Hills BS | 343 Tee1 | 50 POE Load (A) | 587 | 581 | 576 | 573 | 568
Sunrise Hills Bulk | 343-2 | 343 Tee1 | Tewantin | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Rural | 170
Sunrise Hills Bulk | 343-2 | 343 Tee1 | Tewantin | 10 POE Load (A) | 145.9039 | 137.4264 | 144.1934 | 141.5721 | 140.1388
Sunrise Hills Bulk | 343-2 | 343 Tee1 | Tewantin | Power Factor | -0.98248 | -0.98351 | -0.98184 | -0.98213 | -0.98226
Sunrise Hills Bulk | 343-2 | 343 Tee1 | Tewantin | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Sunrise Hills Bulk | 343-2 | 343 Tee1 | Tewantin | 50 POE Load (A) | 358 | 353 | 348 | 345 | 343
Sunrise Hills Bulk | 343-3 | 343 Tee1 | Cooroy | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Rural | 170
Sunrise Hills Bulk | 343-3 | 343 Tee1 | Cooroy | 10 POE Load (A) | 229.9922 | 226.5636 | 187.6579 | 187.5716 | 189.7874
Sunrise Hills Bulk | 343-3 | 343 Tee1 | Cooroy | Power Factor | 0.99405 | 0.99426 | 0.9972 | 0.9972 | 0.99715
Sunrise Hills Bulk | 343-3 | 343 Tee1 | Cooroy | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
Sunrise Hills Bulk | 343-3 | 343 Tee1 | Cooroy | 50 POE Load (A) | 230 | 229 | 229 | 228 | 228
Sunrise Hills Bulk | 346-1 | Sunrise Hills BS | 346 Tee1 | NCC Rating (A) | 1108 | 1108 | 1108 | 1108 | 1108 | Urban | 70
Sunrise Hills Bulk | 346-1 | Sunrise Hills BS | 346 Tee1 | 10 POE Load (A) | 264.7753 | 254.4721 | 241.2831 | 238.6004 | 238.2944
Sunrise Hills Bulk | 346-1 | Sunrise Hills BS | 346 Tee1 | Power Factor | -0.98291 | -0.9838 | -0.98537 | -0.9856 | -0.98564
Sunrise Hills Bulk | 346-1 | Sunrise Hills BS | 346 Tee1 | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Sunrise Hills Bulk | 346-1 | Sunrise Hills BS | 346 Tee1 | 50 POE Load (A) | 292 | 287 | 283 | 281 | 279
Sunrise Hills Bulk | 346-2 | 346 Tee1 | Tewantin | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
Sunrise Hills Bulk | 346-2 | 346 Tee1 | Tewantin | 10 POE Load (A) | 264.8097 | 254.5056 | 241.315 | 238.632 | 238.3259
Sunrise Hills Bulk | 346-2 | 346 Tee1 | Tewantin | Power Factor | 0.98548 | 0.98617 | 0.98783 | 0.98801 | 0.98805
Sunrise Hills Bulk | 346-2 | 346 Tee1 | Tewantin | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Sunrise Hills Bulk | 346-2 | 346 Tee1 | Tewantin | 50 POE Load (A) | 356 | 350 | 346 | 343 | 343
Sunrise Hills Bulk | 346-3 | 346 Tee1 | 3100 Tee1 | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
Sunrise Hills Bulk | 346-3 | 346 Tee1 | 3100 Tee1 | 10 POE Load (A) | 0.00064603 | 0.00064603 | 0.00064604 | 0.00064604 | 0.00064604
Sunrise Hills Bulk | 346-3 | 346 Tee1 | 3100 Tee1 | Power Factor | 0.0003073 | 0.00030692 | 0.00030662 | 0.00030718 | 0.00030691
Sunrise Hills Bulk | 488-1 | Cooroy | 488 Tee1 | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
Sunrise Hills Bulk | 488-1 | Cooroy | 488 Tee1 | 10 POE Load (A) | 109.7992 | 108.2849 | 70.2887 | 70.6155 | 71.7896
Sunrise Hills Bulk | 488-1 | Cooroy | 488 Tee1 | Power Factor | 0.99167 | 0.99204 | 0.99882 | 0.9988 | 0.99873
Sunrise Hills Bulk | 488-1 | Cooroy | 488 Tee1 | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
Sunrise Hills Bulk | 488-1 | Cooroy | 488 Tee1 | 50 POE Load (A) | 129 | 128 | 128 | 128 | 128
Sunrise Hills Bulk | 488-3 | 488 Tee1 | 488 Tee2 | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
Sunrise Hills Bulk | 488-3 | 488 Tee1 | 488 Tee2 | 10 POE Load (A) | 109.8138 | 108.2992 | 70.2953 | 70.6222 | 71.7964
Sunrise Hills Bulk | 488-3 | 488 Tee1 | 488 Tee2 | Power Factor | 0.99148 | 0.99183 | 0.99847 | 0.99845 | 0.99838
Sunrise Hills Bulk | 488-3 | 488 Tee1 | 488 Tee2 | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
Sunrise Hills Bulk | 488-3 | 488 Tee1 | 488 Tee2 | 50 POE Load (A) | 129 | 128 | 128 | 128 | 128
Sunrise Hills Bulk | 488-4 | 488 Tee2 | Black Mtn | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
Sunrise Hills Bulk | 488-4 | 488 Tee2 | Black Mtn | 10 POE Load (A) | 39.5942 | 38.5051 | 0.32318 | 0.3232 | 0.32306
Sunrise Hills Bulk | 488-4 | 488 Tee2 | Black Mtn | Power Factor | 0.97018 | 0.97006 | 1.5722e-05 | 1.5722e-05 | 1.5722e-05
Sunrise Hills Bulk | 488-4 | 488 Tee2 | Black Mtn | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
Sunrise Hills Bulk | 488-4 | 488 Tee2 | Black Mtn | 50 POE Load (A) | 69 | 69 | 69 | 69 | 69
Sunrise Hills Bulk | 488-5 | 488 Tee2 | 488 Tee3 | NCC Rating (A) | 293 | 582 | 582 | 582 | 582 | Rural | 170
Sunrise Hills Bulk | 488-5 | 488 Tee2 | 488 Tee3 | 10 POE Load (A) | 70.7258 | 70.3106 | 70.3378 | 70.6649 | 71.84
Sunrise Hills Bulk | 488-5 | 488 Tee2 | 488 Tee3 | Power Factor | 0.99791 | 0.99811 | 0.99815 | 0.99813 | 0.99805
Sunrise Hills Bulk | 488-5 | 488 Tee2 | 488 Tee3 | ECC Rating (A) | 293 | 490 | 490 | 490 | 490
Sunrise Hills Bulk | 488-5 | 488 Tee2 | 488 Tee3 | 50 POE Load (A) | 60 | 73 | 73 | 73 | 73
Sunrise Hills Bulk | 488-6 | 488 Tee3 | Eumundi | NCC Rating (A) | 468 | 468 | 468 | 468 | 468 | Rural | 170
Sunrise Hills Bulk | 488-6 | 488 Tee3 | Eumundi | 10 POE Load (A) | 70.7959 | 70.3848 | 70.4136 | 70.7409 | 71.917
Sunrise Hills Bulk | 488-6 | 488 Tee3 | Eumundi | Power Factor | 0.99721 | 0.99725 | 0.9972 | 0.99718 | 0.99712
Sunrise Hills Bulk | 488-6 | 488 Tee3 | Eumundi | ECC Rating (A) | 468 | 468 | 468 | 468 | 468
Sunrise Hills Bulk | 488-6 | 488 Tee3 | Eumundi | 50 POE Load (A) | 65 | 64 | 65 | 65 | 65
Sunrise Hills Bulk | 488-7 | 488 Tee3 | Yandina | NCC Rating (A) | 293 | 582 | 582 | 582 | 582 | Rural | 170
Sunrise Hills Bulk | 488-7 | 488 Tee3 | Yandina | 10 POE Load (A) | 0.96866 | 1.0457 | 1.0564 | 1.0564 | 1.0559
Sunrise Hills Bulk | 488-7 | 488 Tee3 | Yandina | Power Factor | 1.4325e-06 | 1.4325e-06 | 1.4325e-06 | 1.4325e-06 | 1.4326e-06
Sunrise Hills Bulk | 488-7 | 488 Tee3 | Yandina | ECC Rating (A) | 293 | 582 | 582 | 582 | 582
Sunrise Hills Bulk | 488-7 | 488 Tee3 | Yandina | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Tennyson Bulk | 3390-1 | Taringa | Indooroopilly | NCC Rating (A) | 779 | 779 | 779 | 779 | 779 | Urban | 70
Tennyson Bulk | 3390-1 | Taringa | Indooroopilly | 10 POE Load (A) | 90.1752 | 86.1789 | 83.4195 | 82.0828 | 82.1494
Tennyson Bulk | 3390-1 | Taringa | Indooroopilly | Power Factor | 0.9991 | 0.99949 | 0.9996 | 0.9997 | 0.99968
Tennyson Bulk | 3390-1 | Taringa | Indooroopilly | ECC Rating (A) | 779 | 779 | 779 | 779 | 779
Tennyson Bulk | 3390-1 | Taringa | Indooroopilly | 50 POE Load (A) | 118 | 116 | 116 | 115 | 115
Tennyson Bulk | 3393-1 | Tennyson BS | St Lucia TR1 | NCC Rating (A) | 640 | 640 | 640 | 640 | 640 | Urban | 70
Tennyson Bulk | 3393-1 | Tennyson BS | St Lucia TR1 | 10 POE Load (A) | 91.2159 | 93.9916 | 93.6033 | 92.6221 | 92.6114
Tennyson Bulk | 3393-1 | Tennyson BS | St Lucia TR1 | Power Factor | 0.99006 | 0.98957 | 0.98962 | 0.98985 | 0.98983
Tennyson Bulk | 3393-1 | Tennyson BS | St Lucia TR1 | ECC Rating (A) | 640 | 640 | 640 | 640 | 640
Tennyson Bulk | 3393-1 | Tennyson BS | St Lucia TR1 | 50 POE Load (A) | 267 | 265 | 263 | 262 | 262
Tennyson Bulk | 3394-1 | Tennyson BS | St Lucia TR2 | NCC Rating (A) | 640 | 640 | 640 | 640 | 640 | Urban | 70
Tennyson Bulk | 3394-1 | Tennyson BS | St Lucia TR2 | 10 POE Load (A) | 185.6879 | 192.1808 | 191.0812 | 188.8236 | 188.7268
Tennyson Bulk | 3394-1 | Tennyson BS | St Lucia TR2 | Power Factor | 0.97198 | 0.97147 | 0.97166 | 0.97203 | 0.97204
Tennyson Bulk | 3394-1 | Tennyson BS | St Lucia TR2 | ECC Rating (A) | 640 | 640 | 640 | 640 | 640
Tennyson Bulk | 3394-1 | Tennyson BS | St Lucia TR2 | 50 POE Load (A) | 122 | 121 | 121 | 120 | 120
Tennyson Bulk | 3460-1 | Annerley | Buranda | NCC Rating (A) | 859 | 859 | 859 | 859 | 859 | Urban | 70
Tennyson Bulk | 3460-1 | Annerley | Buranda | 10 POE Load (A) | 118.2171 | 100.4953 | 142.8721 | 142.3956 | 143.462
Tennyson Bulk | 3460-1 | Annerley | Buranda | Power Factor | 0.99505 | 0.99637 | 0.99304 | 0.99307 | 0.99299
Tennyson Bulk | 3460-1 | Annerley | Buranda | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Tennyson Bulk | 3460-1 | Annerley | Buranda | 50 POE Load (A) | 288 | 238 | 337 | 338 | 338
Tennyson Bulk | 3461-1 | Annerley | Buranda | NCC Rating (A) | 859 | 859 | 859 | 859 | 859 | Urban | 70
Tennyson Bulk | 3461-1 | Annerley | Buranda | 10 POE Load (A) | 118.3988 | 100.6497 | 143.0918 | 142.6145 | 143.6826
Tennyson Bulk | 3461-1 | Annerley | Buranda | Power Factor | 0.99506 | 0.99637 | 0.99304 | 0.99308 | 0.99299
Tennyson Bulk | 3461-1 | Annerley | Buranda | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Tennyson Bulk | 3461-1 | Annerley | Buranda | 50 POE Load (A) | 288 | 238 | 337 | 338 | 338
Tennyson Bulk | 410-1 | Sherwood | Indooroopilly | NCC Rating (A) | 425 | 425 | 425 | 425 | 425 | Urban | 70
Tennyson Bulk | 410-1 | Sherwood | Indooroopilly | 10 POE Load (A) | 167.9532 | 164.7035 | 165.4617 | 163.4818 | 163.9458
Tennyson Bulk | 410-1 | Sherwood | Indooroopilly | Power Factor | 0.99999 | 1 | 1 | 0.99999 | 0.99999
Tennyson Bulk | 410-1 | Sherwood | Indooroopilly | ECC Rating (A) | 480 | 480 | 480 | 480 | 480
Tennyson Bulk | 410-1 | Sherwood | Indooroopilly | 50 POE Load (A) | 282 | 280 | 279 | 278 | 278
Tennyson Bulk | 460-1 | Tennyson BS | Sherwood | NCC Rating (A) | 774 | 774 | 774 | 774 | 774 | Urban | 70
Tennyson Bulk | 460-1 | Tennyson BS | Sherwood | 10 POE Load (A) | 290.9032 | 283.9875 | 284.0103 | 281.2589 | 282.6289
Tennyson Bulk | 460-1 | Tennyson BS | Sherwood | Power Factor | 0.99792 | 0.99819 | 0.99823 | 0.99833 | 0.99828
Tennyson Bulk | 460-1 | Tennyson BS | Sherwood | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Tennyson Bulk | 460-1 | Tennyson BS | Sherwood | 50 POE Load (A) | 373 | 370 | 368 | 367 | 367
Tennyson Bulk | 480-1 | Taringa | St Lucia | NCC Rating (A) | 640 | 640 | 640 | 640 | 640 | Urban | 70
Tennyson Bulk | 480-1 | Taringa | St Lucia | 10 POE Load (A) | 91.6431 | 94.9354 | 94.2745 | 93.2503 | 93.1695
Tennyson Bulk | 480-1 | Taringa | St Lucia | Power Factor | -0.969 | -0.96855 | -0.96865 | -0.96875 | -0.96877
Tennyson Bulk | 480-1 | Taringa | St Lucia | ECC Rating (A) | 640 | 640 | 640 | 640 | 640
Tennyson Bulk | 480-1 | Taringa | St Lucia | 50 POE Load (A) | 266 | 263 | 262 | 261 | 261
Tennyson Bulk | 504-1 | Tennyson BS | Taringa | NCC Rating (A) | 637 | 637 | 637 | 637 | 637 | Urban | 70
Tennyson Bulk | 504-1 | Tennyson BS | Taringa | 10 POE Load (A) | 232.9311 | 230.1911 | 234.1889 | 232.3724 | 233.7263
Tennyson Bulk | 504-1 | Tennyson BS | Taringa | Power Factor | -0.99563 | -0.99582 | -0.99583 | -0.99597 | -0.99593
Tennyson Bulk | 504-1 | Tennyson BS | Taringa | ECC Rating (A) | 742 | 742 | 742 | 742 | 742
Tennyson Bulk | 504-1 | Tennyson BS | Taringa | 50 POE Load (A) | 358 | 356 | 354 | 353 | 353
Tennyson Bulk | 507A-1 | Toowong | Indooroopilly | NCC Rating (A) | 786 | 786 | 786 | 786 | 786 | Urban | 70
Tennyson Bulk | 507A-1 | Toowong | Indooroopilly | 10 POE Load (A) | 92.0581 | 87.968 | 85.1429 | 83.7749 | 83.843
Tennyson Bulk | 507A-1 | Toowong | Indooroopilly | Power Factor | 0.99412 | 0.9948 | 0.99487 | 0.99508 | 0.99503
Tennyson Bulk | 507A-1 | Toowong | Indooroopilly | ECC Rating (A) | 917 | 917 | 917 | 917 | 917
Tennyson Bulk | 507A-1 | Toowong | Indooroopilly | 50 POE Load (A) | 119 | 118 | 117 | 116 | 116
Tennyson Bulk | 507B-1 | Toowong | Taringa | NCC Rating (A) | 783 | 783 | 783 | 783 | 783 | Urban | 70
Tennyson Bulk | 507B-1 | Toowong | Taringa | 10 POE Load (A) | 90.9272 | 86.8664 | 84.0368 | 82.6797 | 82.7443
Tennyson Bulk | 507B-1 | Toowong | Taringa | Power Factor | 0.99966 | 0.99988 | 0.99993 | 0.99997 | 0.99996
Tennyson Bulk | 507B-1 | Toowong | Taringa | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Tennyson Bulk | 507B-1 | Toowong | Taringa | 50 POE Load (A) | 119 | 117 | 116 | 116 | 116
Tennyson Bulk | 511-1 | Tennyson BS | Moorooka | NCC Rating (A) | 801 | 801 | 801 | 801 | 801 | Urban | 70
Tennyson Bulk | 511-1 | Tennyson BS | Moorooka | 10 POE Load (A) | 132.1161 | 133.1034 | 135.2883 | 136.3444 | 139.0396
Tennyson Bulk | 511-1 | Tennyson BS | Moorooka | Power Factor | -0.97858 | -0.9785 | -0.97832 | -0.97823 | -0.97801
Tennyson Bulk | 511-1 | Tennyson BS | Moorooka | ECC Rating (A) | 816 | 816 | 816 | 816 | 816
Tennyson Bulk | 511-1 | Tennyson BS | Moorooka | 50 POE Load (A) | 251 | 251 | 251 | 253 | 253
Tennyson Bulk | 514-1 | Tennyson BS | Moorooka | NCC Rating (A) | 801 | 801 | 801 | 801 | 801 | Urban | 70
Tennyson Bulk | 514-1 | Tennyson BS | Moorooka | 10 POE Load (A) | 138.2833 | 139.3166 | 141.6033 | 142.7087 | 145.5294
Tennyson Bulk | 514-1 | Tennyson BS | Moorooka | Power Factor | 0.98083 | 0.98074 | 0.98053 | 0.98043 | 0.98017
Tennyson Bulk | 514-1 | Tennyson BS | Moorooka | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Tennyson Bulk | 514-1 | Tennyson BS | Moorooka | 50 POE Load (A) | 251 | 251 | 251 | 252 | 252
Tennyson Bulk | 515-1 | Tennyson BS | Sherwood | NCC Rating (A) | 768 | 768 | 768 | 768 | 768 | Urban | 70
Tennyson Bulk | 515-1 | Tennyson BS | Sherwood | 10 POE Load (A) | 308.3528 | 301.0196 | 301.044 | 298.1266 | 299.5793
Tennyson Bulk | 515-1 | Tennyson BS | Sherwood | Power Factor | 0.99894 | 0.99913 | 0.99916 | 0.99923 | 0.9992
Tennyson Bulk | 515-1 | Tennyson BS | Sherwood | ECC Rating (A) | 797 | 797 | 797 | 797 | 797
Tennyson Bulk | 515-1 | Tennyson BS | Sherwood | 50 POE Load (A) | 420 | 417 | 414 | 412 | 412
Tennyson Bulk | 523A&B-1 | Tennyson BS | Rocklea | NCC Rating (A) | #N/A | #N/A | #N/A | #N/A | #N/A | Urban | 70
Tennyson Bulk | 523A&B-1 | Tennyson BS | Rocklea | 10 POE Load (A) | #N/A | #N/A | #N/A | #N/A | #N/A
Tennyson Bulk | 523A&B-1 | Tennyson BS | Rocklea | Power Factor | #N/A | #N/A | #N/A | #N/A | #N/A
Tennyson Bulk | 523A-1 | Tennyson BS | Rocklea | NCC Rating (A) | 688 | 688 | 688 | 688 | 688 | Urban | 70
Tennyson Bulk | 523A-1 | Tennyson BS | Rocklea | 10 POE Load (A) | 7.7342 | 7.7342 | 7.7342 | 7.7342 | 7.7342
Tennyson Bulk | 523A-1 | Tennyson BS | Rocklea | Power Factor | 1.0729e-05 | 1.0729e-05 | 1.0729e-05 | 1.0729e-05 | 1.0729e-05
Tennyson Bulk | 523A-1 | Tennyson BS | Rocklea | ECC Rating (A) | 0 | 688 | 688 | 688 | 688
Tennyson Bulk | 523A-1 | Tennyson BS | Rocklea | 50 POE Load (A) | 0 | 8 | 8 | 8 | 8
Tennyson Bulk | 539-1 | Sherwood | Kenmore | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 340
Tennyson Bulk | 539-1 | Sherwood | Kenmore | 10 POE Load (A) | 214.4403 | 206.2052 | 203.4221 | 200.0013 | 200.4087
Tennyson Bulk | 539-1 | Sherwood | Kenmore | Power Factor | 0.99727 | 0.99757 | 0.99767 | 0.99779 | 0.99777
Tennyson Bulk | 539-1 | Sherwood | Kenmore | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
Tennyson Bulk | 539-1 | Sherwood | Kenmore | 50 POE Load (A) | 433 | 429 | 425 | 422 | 422
Tennyson Bulk | 554-1 | Tennyson BS | Sherwood | NCC Rating (A) | 768 | 768 | 768 | 768 | 768 | Urban | 70
Tennyson Bulk | 554-1 | Tennyson BS | Sherwood | 10 POE Load (A) | 326.8653 | 319.0946 | 319.1208 | 316.0292 | 317.5686
Tennyson Bulk | 554-1 | Tennyson BS | Sherwood | Power Factor | 0.99826 | 0.9985 | 0.99853 | 0.99862 | 0.99858
Tennyson Bulk | 554-1 | Tennyson BS | Sherwood | ECC Rating (A) | 768 | 768 | 768 | 768 | 768
Tennyson Bulk | 554-1 | Tennyson BS | Sherwood | 50 POE Load (A) | 433 | 430 | 428 | 426 | 426
Tennyson Bulk | 571-1 | Indooroopilly | Kenmore | NCC Rating (A) | 527 | 527 | 527 | 527 | 527 | Urban | 70
Tennyson Bulk | 571-1 | Indooroopilly | Kenmore | 10 POE Load (A) | 281.4931 | 269.9661 | 265.6503 | 261.0042 | 261.5058
Tennyson Bulk | 571-1 | Indooroopilly | Kenmore | Power Factor | 0.99043 | 0.99099 | 0.99119 | 0.99141 | 0.99138
Tennyson Bulk | 571-1 | Indooroopilly | Kenmore | ECC Rating (A) | 527 | 527 | 527 | 527 | 527
Tennyson Bulk | 571-1 | Indooroopilly | Kenmore | 50 POE Load (A) | 428 | 424 | 420 | 417 | 417
Tennyson Bulk | 606-1 | Tennyson BS | Taringa | NCC Rating (A) | 637 | 637 | 637 | 637 | 637 | Urban | 70
Tennyson Bulk | 606-1 | Tennyson BS | Taringa | 10 POE Load (A) | 234.0304 | 231.2776 | 235.2944 | 233.4693 | 234.8296
Tennyson Bulk | 606-1 | Tennyson BS | Taringa | Power Factor | 0.99932 | 0.99938 | 0.99935 | 0.99941 | 0.99939
Tennyson Bulk | 606-1 | Tennyson BS | Taringa | ECC Rating (A) | 742 | 742 | 742 | 742 | 742
Tennyson Bulk | 606-1 | Tennyson BS | Taringa | 50 POE Load (A) | 359 | 356 | 355 | 354 | 354
Tennyson Bulk | 637-1 | Tennyson BS | Annerley | NCC Rating (A) | 765 | 765 | 765 | 765 | 765 | Urban | 70
Tennyson Bulk | 637-1 | Tennyson BS | Annerley | 10 POE Load (A) | 250.0135 | 232.7057 | 276.4463 | 276.5526 | 279.8579
Tennyson Bulk | 637-1 | Tennyson BS | Annerley | Power Factor | 0.99757 | 0.99826 | 0.99634 | 0.99635 | 0.99625
Tennyson Bulk | 637-1 | Tennyson BS | Annerley | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Tennyson Bulk | 637-1 | Tennyson BS | Annerley | 50 POE Load (A) | 535 | 483 | 586 | 587 | 587
Tennyson Bulk | 638-1 | Tennyson BS | Annerley | NCC Rating (A) | 765 | 765 | 765 | 765 | 765 | Urban | 70
Tennyson Bulk | 638-1 | Tennyson BS | Annerley | 10 POE Load (A) | 250.8625 | 233.4958 | 277.3852 | 277.4918 | 280.8084
Tennyson Bulk | 638-1 | Tennyson BS | Annerley | Power Factor | 0.99756 | 0.99825 | 0.99633 | 0.99634 | 0.99624
Tennyson Bulk | 638-1 | Tennyson BS | Annerley | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Tennyson Bulk | 638-1 | Tennyson BS | Annerley | 50 POE Load (A) | 535 | 483 | 586 | 587 | 587
Tennyson Bulk | F703-1 | Sherwood | Indooroopilly | NCC Rating (A) | 425 | 425 | 425 | 425 | 425 | Urban | 70
Tennyson Bulk | F703-1 | Sherwood | Indooroopilly | 10 POE Load (A) | 169.7072 | 166.4238 | 167.1902 | 165.1897 | 165.6585
Tennyson Bulk | F703-1 | Sherwood | Indooroopilly | Power Factor | 0.99999 | 1 | 1 | 0.99999 | 0.99999
Tennyson Bulk | F703-1 | Sherwood | Indooroopilly | ECC Rating (A) | 480 | 480 | 480 | 480 | 480
Tennyson Bulk | F703-1 | Sherwood | Indooroopilly | 50 POE Load (A) | 283 | 281 | 280 | 279 | 279
Victoria Park Bulk | 627-1 | Victoria Pk BS | Astor Tce | NCC Rating (A) | 525 | 525 | 525 | 525 | 525 | Urban | 70
Victoria Park Bulk | 627-1 | Victoria Pk BS | Astor Tce | 10 POE Load (A) | 0.15298 | 0.15298 | 0.15298 | 0.15298 | 0.15298
Victoria Park Bulk | 627-1 | Victoria Pk BS | Astor Tce | Power Factor | 0.96802 | 0.96802 | 0.96802 | 0.96802 | 0.96802
Victoria Park Bulk | 627-1 | Victoria Pk BS | Astor Tce | ECC Rating (A) | 542 | 542 | 542 | 542 | 542
Victoria Park Bulk | 627-1 | Victoria Pk BS | Astor Tce | 50 POE Load (A) | 184 | 183 | 182 | 181 | 181
Victoria Park Bulk | 628-1 | Victoria Pk BS | Astor Tce | NCC Rating (A) | 502 | 502 | 502 | 502 | 502 | Urban | 70
Victoria Park Bulk | 628-1 | Victoria Pk BS | Astor Tce | 10 POE Load (A) | 128.0322 | 128.393 | 129.7261 | 129.3725 | 130.4352
Victoria Park Bulk | 628-1 | Victoria Pk BS | Astor Tce | Power Factor | 0.96907 | 0.96904 | 0.9689 | 0.96894 | 0.96883
Victoria Park Bulk | 628-1 | Victoria Pk BS | Astor Tce | ECC Rating (A) | 542 | 542 | 542 | 542 | 542
Victoria Park Bulk | 628-1 | Victoria Pk BS | Astor Tce | 50 POE Load (A) | 374 | 372 | 370 | 369 | 369
Victoria Park Bulk | 639-1 | Victoria Pk BS | Newmarket | NCC Rating (A) | 536 | 536 | 536 | 536 | 536 | Urban | 70
Victoria Park Bulk | 639-1 | Victoria Pk BS | Newmarket | 10 POE Load (A) | 153.4514 | 152.8521 | 153.7098 | 153.3739 | 154.8922
Victoria Park Bulk | 639-1 | Victoria Pk BS | Newmarket | Power Factor | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998
Victoria Park Bulk | 639-1 | Victoria Pk BS | Newmarket | ECC Rating (A) | 623 | 623 | 623 | 623 | 623
Victoria Park Bulk | 639-1 | Victoria Pk BS | Newmarket | 50 POE Load (A) | 280 | 278 | 276 | 275 | 275
Victoria Park Bulk | 649-1 | Victoria Pk BS | Astor Tce | NCC Rating (A) | 525 | 525 | 525 | 525 | 525 | Urban | 70
Victoria Park Bulk | 649-1 | Victoria Pk BS | Astor Tce | 10 POE Load (A) | 129.5684 | 129.9334 | 131.2822 | 130.9245 | 131.9997
Victoria Park Bulk | 649-1 | Victoria Pk BS | Astor Tce | Power Factor | 0.96942 | 0.96938 | 0.96924 | 0.96928 | 0.96917
Victoria Park Bulk | 649-1 | Victoria Pk BS | Astor Tce | ECC Rating (A) | 542 | 542 | 542 | 542 | 542
Victoria Park Bulk | 649-1 | Victoria Pk BS | Astor Tce | 50 POE Load (A) | 374 | 372 | 370 | 369 | 369
Victoria Park Bulk | 653-1 | Victoria Pk BS | Newmarket | NCC Rating (A) | 536 | 536 | 536 | 536 | 536 | Urban | 70
Victoria Park Bulk | 653-1 | Victoria Pk BS | Newmarket | 10 POE Load (A) | 153.4515 | 152.8521 | 153.7099 | 153.3739 | 154.8922
Victoria Park Bulk | 653-1 | Victoria Pk BS | Newmarket | Power Factor | -0.99339 | -0.99343 | -0.99338 | -0.9934 | -0.99353
Victoria Park Bulk | 653-1 | Victoria Pk BS | Newmarket | ECC Rating (A) | 623 | 623 | 623 | 623 | 623
Victoria Park Bulk | 653-1 | Victoria Pk BS | Newmarket | 50 POE Load (A) | 280 | 278 | 276 | 275 | 275
Victoria Park Bulk | 659B-1 | Victoria Pk BS | Clayfield | NCC Rating (A) | #N/A | #N/A | #N/A | #N/A | #N/A | Urban | 70
Victoria Park Bulk | 659B-1 | Victoria Pk BS | Clayfield | 10 POE Load (A) | #N/A | #N/A | #N/A | #N/A | #N/A
Victoria Park Bulk | 659B-1 | Victoria Pk BS | Clayfield | Power Factor | #N/A | #N/A | #N/A | #N/A | #N/A
Victoria Park Bulk | 659B-1 | Victoria Pk BS | Clayfield | ECC Rating (A) | 0 | 0 | 0 | 0 | 0
Victoria Park Bulk | 659B-1 | Victoria Pk BS | Clayfield | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Victoria Park Bulk | 689-1 | Victoria Pk BS | Astor Tce | NCC Rating (A) | 588 | 588 | 588 | 588 | 588 | Urban | 70
Victoria Park Bulk | 689-1 | Victoria Pk BS | Astor Tce | 10 POE Load (A) | 9.2482 | 9.2482 | 9.2482 | 9.2482 | 9.2482
Victoria Park Bulk | 689-1 | Victoria Pk BS | Astor Tce | Power Factor | -1 | -1 | -1 | -1 | -1
Victoria Park Bulk | 689-1 | Victoria Pk BS | Astor Tce | ECC Rating (A) | 588 | 588 | 588 | 588 | 588
Victoria Park Bulk | 689-1 | Victoria Pk BS | Astor Tce | 50 POE Load (A) | 10 | 10 | 10 | 10 | 10
Note on L537: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: F3751-1: Open CB3932 @ CRB, Open CB37562 @ PBH; KRA can be transferred to Country Energy network
Note on L542: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: F3755-1: Open CB3932 @ CRB, Open CB37562 @ PBH; KRA can be transferred to Country Energy network
Note on J1364: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: F3828-1: Approved project WR7111761 to reconductor this feeder with Moon by April 2020. Rating for new Moon 400A for 75A (As per Plant Rating Manual)
Note on L1631: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: F421-1: Open CB4742 @ ARL and Open CB3892 @ LDR
Note on L1646: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: F474A-1: Open CB4742 @ HWL and Open CB3892 @ LDR