## Notes
Transmission Feeders Forecasts (Energex Distribution Annual Planning Report 2020-21 to 2024-25)
This workbook provides 5 year forecast capacity and loading information for sub-transmission feeders in the Energex network.
This workbook forms part of the Energex Distribution Annual Planning Report 2020-21 to 2024-25 (DAPR) and should be read in conjunction with the report document.
Energex Distribution Annual Planning Report is prepared and made available solely for information purposes. While care was taken in the preparation of the information in this report, and it is provided in good faith, Energex accepts no responsibility or liability (including without limitation, liability to any person by reason of negligence or negligent mis-statement) for any loss or damage that may be incurred by any person acting in reliance on this information or assumptions drawn from it, except to the extent that liability under any applicable Queensland or Commonwealth of Australia statute cannot be excluded.
It contains assumptions regarding, among other things, economic growth and load forecasts which may or may not prove to be correct. The forecasts included in the document involve subjective judgements and analysis which are subject to significant uncertainties and contingencies, many of which are out of the control of Energex. Furthermore, forecasted data is subject to ongoing variation due to COVID 19 impacts. Energex makes no representation or warranty as to the accuracy, reliability, completeness or suitability for any particular purpose of the information in this document. All information should be independently investigated, reviewed, analysed and verified, and must not be relied upon in connection with any investment proposal or decision.
The following sections list the 110kV and 132kV feeders, their forecast loads, power factor, customer category and available load transfers. The feeder loads are calculated from load flow results using forecast substation demands. For the transmission and sub-transmission feeders, load flow studies are conducted for system normal and single contingency situations.
The forecast and capacity cut-off date for the winter season is 1 June of each year, and for the summer season is 1 December of each year. For example, 2021 winter forecast includes all committed projects with a proposed commissioning date up to 1 June 2021, and the 2020/21 summer forecast includes all committed projects with a proposed commissioning date up to 1 December 2020.
Assessment of 110kV & 132kV feeders is performed under four possible risk periods: winter day, winter night, summer day and summer night. For the summer table, the worst case (highest) load between summer day and summer night has been represented in the table.
Peak, reconciled, compensated load forecasts have been used in the 110kV & 132kV feeder analyses, with 50 PoE forecast load used for single contingency studies, and 10 PoE forecast load used for system normal studies.
Feeder capacities are shown for ECC and NCC. These ratings have also been adjusted for known committed projects. All load transfers associated with contingent condition include acceptable feeder voltage profiles.
Although the conductor rating is generally the limiting factor for feeder capacity, there are other significant items of plant, such as the feeder circuit breaker, that can also restrict capacity. Furthermore, other factors such as voltage constraints and load sharing between parallel underground feeders can sometimes de‑rate the capacity of the feeders due to thermal characteristic constraints. Each of these factors has been taken into account in the production of the forecast tables.
Interconnected feeders that supply multiple customers are examined in the following tables. Feeders exclusively supplying a customer owned substation or dedicated to a customer are not included in these tables.
A definition of terms is shown in the table below.
Definition of Terms Feeder Capacity and Forecast Tables
Term | Definition
NCC Rating (A) | Normal Cyclic Capacity - the total capacity with all network components and equipment intact. This is the maximum permissible peak daily loading for a given load cycle that a feeder can supply each day of its life. For overhead feeders, the NCC is the conductor rating with an assumed 1m/s wind, orthogonal to the line. For underground cables, the NCC assumes that there are sufficient temperature and current operating margins from the thermal inertia of the cable and its surroundings.
10 PoE Load (A) | Peak load forecast with 10% probability of being exceeded (one in every 10 years will be exceeded). Based on normal expected growth rates and weather corrected starting loads.
Power Factor (System Normal) | Lowest power factor along the feeder at 10 PoE Peak Load. Where the Power Factor is 0 the feeder is a normally open feeder that does not have load under System Normal conditions.
ECC Rating (A) | Emergency Cyclic Capacity – the long term firm delivery capacity under single contingency conditions. Some underground cables are installed in close proximity to other circuits and are normally de‑rated to allow for the heat generated by the adjacent cables. ECC is the higher capacity available when any adjacent circuits have been unloaded. For overhead conductors which do not benefit from this phenomenon, the ECC is synonymous with the NCC.
50 PoE Load (A) | Peak load forecast with 50% probability of being exceeded (one in every two years will be exceeded). Based on normal expected growth rates & weather corrected starting loads. This is the worst case (highest) load forecast beween summer day and summer night.
Customer Category | For security standard application, the general type of customer a sub-transmission, or transmission feeder is supplying.
Transfers | This is the total amount of load transfers that are available following the worst case network contingency. This includes automatic transfers that are controlled automatically through SCADA and are generally implemented within a minute, load transfers that can be implemented through screen switching by a network controller, manual transfers that are deployed via manually controlled switchgear locally by field staff, and mobile generation which can be deployed by field staff by moving generation to specific sites. It should be noted under the Safety Net in the Distribution Authority, it is generally assumed that 4MVA (21A) of generation is available for Urban feeders to meet this criteria and 10MVA (52A) is available for Rural feeders. These values have been used as a default in the forecast tables where these are sufficient to reduce the 50PoE load below the ECC rating. Where the load is still above the ECC rating, specific load transfers have been calculated for the feeder to determine whether the Safety Net criteria is met.
Hours PA > 95% Peak Load | The forecast number of hours per annum where the load exceeded 95% of the peak 50 PoE demand. This information is not readily available for every feeder without significant analysis being undertaken. As such, this has only been provided where a feeder does not meet the Safety Net criteria or is otherwise in the Limitations and Proposed Solutions table.

## 110kV & 132kV Feeders - Winter
Connection Point | Feeder | From Substation | To Substation | Attributes | 2020 | 2021 | 2022 | 2023 | 2024 | Customer Category | Transfers (Amps) | Hours PA > 95% Peak Load
Abermain | F7259/1 | Abermain | Wulkuraka Tee | NCC Rating (A) | 613 | 613 | 613 | 613 | 613 | Rural | 52 | NA
|  |  |  | 10 POE Load (A) | 252 | 252 | 252 | 252 | 252
|  |  |  | Power Factor | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | ECC Rating (A) | 613 | 613 | 613 | 613 | 613
|  |  |  | 50 POE Load (A) | 367 | 369 | 372 | 371 | 370
Abermain | F7259/2 | Wulkuraka Tee | Lockrose | NCC Rating (A) | 613 | 613 | 613 | 613 | 613 | Rural | 52 | NA
|  |  |  | 10 POE Load (A) | 214 | 214 | 214 | 214 | 214
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | ECC Rating (A) | 613 | 613 | 613 | 613 | 613
|  |  |  | 50 POE Load (A) | 329 | 331 | 335 | 334 | 333
Abermain | F7289 | Lockrose | Gatton | NCC Rating (A) | 690 | 690 | 690 | 690 | 690 | Rural | 52 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 690 | 690 | 690 | 690 | 690
|  |  |  | 50 POE Load (A) | 212 | 212 | 215 | 213 | 211
Belmont | F750 | Belmont | Beenleigh | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Rural | 52 | NA
|  |  |  | 10 POE Load (A) | 203 | 216 | 238 | 196 | 188
|  |  |  | Power Factor | 0.97 | 0.89 | 0.83 | 0.87 | 0.93
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 285 | 297 | 304 | 271 | 272
Belmont | F766 | Belmont | Cleveland | NCC Rating (A) | 1600 | 1600 | 1600 | 1600 | 1600 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 328 | 328 | 327 | 324 | 324
|  |  |  | Power Factor | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | ECC Rating (A) | 1600 | 1600 | 1600 | 1600 | 1600
|  |  |  | 50 POE Load (A) | 651 | 646 | 644 | 640 | 642
Belmont | F767 | Belmont | Cleveland | NCC Rating (A) | 1600 | 1600 | 1600 | 1600 | 1600 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 328 | 328 | 327 | 324 | 324
|  |  |  | Power Factor | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | ECC Rating (A) | 1600 | 1600 | 1600 | 1600 | 1600
|  |  |  | 50 POE Load (A) | 651 | 646 | 644 | 640 | 642
Blackstone | F713 | Blackstone | Raceview | NCC Rating (A) | 1131 | 1131 | 1131 | 1131 | 1131 | Rural | 52 | NA
|  |  |  | 10 POE Load (A) | 177 | 181 | 180 | 182 | 182
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | ECC Rating (A) | 1131 | 1131 | 1131 | 1131 | 1131
|  |  |  | 50 POE Load (A) | 346 | 344 | 347 | 347 | 353
Blackstone | F714 | Blackstone | Raceview | NCC Rating (A) | 1131 | 1131 | 1131 | 1131 | 1131 | Rural | 52 | NA
|  |  |  | 10 POE Load (A) | 177 | 181 | 180 | 182 | 182
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | ECC Rating (A) | 1131 | 1131 | 1131 | 1131 | 1131
|  |  |  | 50 POE Load (A) | 346 | 344 | 347 | 347 | 353
CBD East | F7231 | Wellington Road | Charlotte St | NCC Rating (A) | 1283 | 1283 | 1283 | 1283 | 1283 | CBD | NA | NA
|  |  |  | 10 POE Load (A) | 304 | 295 | 318 | 304 | 313
|  |  |  | Power Factor | 0.97 | 1 | 1 | 0.98 | 0.98
|  |  |  | ECC Rating (A) | 1283 | 1283 | 1283 | 1283 | 1283
|  |  |  | 50 POE Load (A) | 567 | 554 | 598 | 571 | 581
CBD East | F7232 | Wellington Road | Charlotte St | NCC Rating (A) | 1283 | 1283 | 1283 | 1283 | 1283 | CBD | NA | NA
|  |  |  | 10 POE Load (A) | 304 | 295 | 318 | 304 | 313
|  |  |  | Power Factor | 0.97 | 1 | 1 | 0.98 | 0.98
|  |  |  | ECC Rating (A) | 1283 | 1283 | 1283 | 1283 | 1283
|  |  |  | 50 POE Load (A) | 567 | 554 | 598 | 571 | 581
CBD East | F7287/3 | Tingalpa Tee | Wellington Road | NCC Rating (A) | 1197 | 1197 | 1197 | 1197 | 1197 | CBD | NA | NA
|  |  |  | 10 POE Load (A) | 539 | 556 | 562 | 546 | 555
|  |  |  | Power Factor | 0.99 | 1 | 1 | 0.99 | 0.99
|  |  |  | ECC Rating (A) | 1197 | 1197 | 1197 | 1197 | 1197
|  |  |  | 50 POE Load (A) | 873 | 904 | 917 | 885 | 902
CBD East | F7288/3 | Tingalpa Tee | Wellington Road | NCC Rating (A) | 1197 | 1197 | 1197 | 1197 | 1197 | CBD | NA | NA
|  |  |  | 10 POE Load (A) | 547 | 558 | 565 | 554 | 563
|  |  |  | Power Factor | 0.99 | 1 | 1 | 0.99 | 0.99
|  |  |  | ECC Rating (A) | 1197 | 1197 | 1197 | 1197 | 1197
|  |  |  | 50 POE Load (A) | 876 | 906 | 919 | 890 | 904
CBD East | F7230 | Wellington Road | Coorparoo | NCC Rating (A) | 1300 | 1300 | 1300 | 1300 | 1300 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 151 | 150 | 150 | 149 | 149
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | ECC Rating (A) | 1300 | 1300 | 1300 | 1300 | 1300
|  |  |  | 50 POE Load (A) | 288 | 284 | 284 | 283 | 283
CBD East | F7362 | Wellington Road | Coorparoo | NCC Rating (A) | 1300 | 1300 | 1300 | 1300 | 1300 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 151 | 150 | 150 | 149 | 149
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | ECC Rating (A) | 1300 | 1300 | 1300 | 1300 | 1300
|  |  |  | 50 POE Load (A) | 288 | 284 | 284 | 283 | 283
CBD East | F752 | Murarrie | Newstead | NCC Rating (A) | 1456 | 1456 | 1456 | 1456 | 1456 | CBD | NA | NA
|  |  |  | 10 POE Load (A) | 250 | 245 | 248 | 268 | 270
|  |  |  | Power Factor | 0.98 | 1 | 1 | 0.99 | 0.99
|  |  |  | ECC Rating (A) | 1456 | 1456 | 1456 | 1456 | 1456
|  |  |  | 50 POE Load (A) | 338 | 336 | 334 | 353 | 354
CBD East | F753 | Murarrie | Newstead | NCC Rating (A) | 1456 | 1456 | 1456 | 1456 | 1456 | CBD | NA | NA
|  |  |  | 10 POE Load (A) | 250 | 245 | 248 | 268 | 270
|  |  |  | Power Factor | 0.98 | 1 | 1 | 0.99 | 0.99
|  |  |  | ECC Rating (A) | 1456 | 1456 | 1456 | 1456 | 1456
|  |  |  | 50 POE Load (A) | 338 | 336 | 334 | 353 | 354
CBD East | F809 | Newstead | Victoria Park | NCC Rating (A) | 704 | 704 | 704 | 704 | 704 | CBD | NA | NA
|  |  |  | 10 POE Load (A) | 85 | 83 | 84 | 90 | 93
|  |  |  | Power Factor | 0.93 | 0.97 | 0.97 | 0.94 | 0.94
|  |  |  | ECC Rating (A) | 704 | 704 | 704 | 704 | 704
|  |  |  | 50 POE Load (A) | 173 | 174 | 173 | 172 | 183
CBD East | F810 | Newstead | Victoria Park | NCC Rating (A) | 704 | 704 | 704 | 704 | 704 | CBD | NA | NA
|  |  |  | 10 POE Load (A) | 85 | 83 | 84 | 90 | 93
|  |  |  | Power Factor | 0.93 | 0.97 | 0.97 | 0.94 | 0.94
|  |  |  | ECC Rating (A) | 704 | 704 | 704 | 704 | 704
|  |  |  | 50 POE Load (A) | 173 | 174 | 173 | 172 | 183
CBD East | F829 | Charlotte St | Ann St | NCC Rating (A) | 963 | 963 | 963 | 963 | 963 | CBD | NA | NA
|  |  |  | 10 POE Load (A) | 171 | 164 | 158 | 145 | 154
|  |  |  | Power Factor | 0.95 | 1 | 1 | 0.96 | 0.96
|  |  |  | ECC Rating (A) | 963 | 963 | 963 | 963 | 963
|  |  |  | 50 POE Load (A) | 327 | 318 | 308 | 282 | 291
CBD East | F833 | Charlotte St | Ann St | NCC Rating (A) | 963 | 963 | 963 | 963 | 963 | CBD | NA | NA
|  |  |  | 10 POE Load (A) | 171 | 164 | 158 | 145 | 154
|  |  |  | Power Factor | 0.95 | 1 | 1 | 0.96 | 0.96
|  |  |  | ECC Rating (A) | 963 | 963 | 963 | 963 | 963
|  |  |  | 50 POE Load (A) | 327 | 318 | 308 | 282 | 291
CBD East | F834 | McLachlan St | Ann St | NCC Rating (A) | 967 | 967 | 967 | 967 | 967 | CBD | NA | NA
|  |  |  | 10 POE Load (A) | 223 | 201 | 191 | 173 | 190
|  |  |  | Power Factor | 0.91 | 1 | 1 | 0.89 | 0.9
|  |  |  | ECC Rating (A) | 967 | 967 | 967 | 967 | 967
|  |  |  | 50 POE Load (A) | 365 | 361 | 353 | 331 | 348
CBD East | F835 | McLachlan St | Victoria Park | NCC Rating (A) | 967 | 967 | 967 | 967 | 967 | CBD | NA | NA
|  |  |  | 10 POE Load (A) | 196 | 193 | 190 | 184 | 200
|  |  |  | Power Factor | 0.99 | 1 | 1 | 0.99 | 0.98
|  |  |  | ECC Rating (A) | 967 | 967 | 967 | 967 | 967
|  |  |  | 50 POE Load (A) | 244 | 243 | 241 | 237 | 252
CBD East | F914 | Newstead | McLachlan St | NCC Rating (A) | 1305 | 1305 | 1305 | 1305 | 1305 | CBD | NA | NA
|  |  |  | 10 POE Load (A) | 75 | 70 | 72 | 88 | 87
|  |  |  | Power Factor | 0.96 | 0.96 | 0.98 | 0.99 | 0.99
|  |  |  | ECC Rating (A) | 1305 | 1305 | 1305 | 1305 | 1305
|  |  |  | 50 POE Load (A) | 141 | 141 | 140 | 153 | 152
CBD East | F915 | Newstead | McLachlan St | NCC Rating (A) | 1305 | 1305 | 1305 | 1305 | 1305 | CBD | NA | NA
|  |  |  | 10 POE Load (A) | 75 | 70 | 72 | 88 | 87
|  |  |  | Power Factor | 0.96 | 0.96 | 0.98 | 0.99 | 0.99
|  |  |  | ECC Rating (A) | 1305 | 1305 | 1305 | 1305 | 1305
|  |  |  | 50 POE Load (A) | 141 | 141 | 140 | 153 | 152
CBD South | F830 | West End | Charlotte St | NCC Rating (A) | 690 | 690 | 690 | 690 | 690 | CBD | NA | NA
|  |  |  | 10 POE Load (A) | 296 | 331 | 164 | 324 | 340
|  |  |  | Power Factor | 0.14 | 0.13 | 0.37 | 0.16 | 0.15
|  |  |  | ECC Rating (A) | 690 | 690 | 690 | 690 | 690
|  |  |  | 50 POE Load (A) | 446 | 454 | 324 | 415 | 421
CBD South | F905 | Rocklea | West End | NCC Rating (A) | 693 | 693 | 693 | 693 | 693 | CBD | NA | NA
|  |  |  | 10 POE Load (A) | 358 | 385 | 292 | 385 | 397
|  |  |  | Power Factor | 0.69 | 0.65 | 0.91 | 0.67 | 0.65
|  |  |  | ECC Rating (A) | 693 | 693 | 693 | 693 | 693
|  |  |  | 50 POE Load (A) | 554 | 558 | 479 | 538 | 542
CBD West | F7266 | Milton | Customer | NCC Rating (A) | 966 | 966 | 966 | 966 | 966 | CBD | NA | NA
|  |  |  | 10 POE Load (A) | 194 | 204 | 139 | 207 | 216
|  |  |  | Power Factor | 0.55 | 0.53 | 0.75 | 0.55 | 0.54
|  |  |  | ECC Rating (A) | 966 | 966 | 966 | 966 | 966
|  |  |  | 50 POE Load (A) | 362 | 408 | 280 | 421 | 356
CBD West | F7267 | Milton | Makerston St | NCC Rating (A) | 966 | 966 | 966 | 966 | 966 | CBD | NA | NA
|  |  |  | 10 POE Load (A) | 209 | 220 | 148 | 228 | 244
|  |  |  | Power Factor | 0.57 | 0.56 | 0.79 | 0.59 | 0.59
|  |  |  | ECC Rating (A) | 966 | 966 | 966 | 966 | 966
|  |  |  | 50 POE Load (A) | 363 | 410 | 281 | 423 | 358
CBD West | F7321 | Customer | Makerston St | NCC Rating (A) | 966 | 966 | 966 | 966 | 966 | CBD | NA | NA
|  |  |  | 10 POE Load (A) | 136 | 147 | 72 | 149 | 162
|  |  |  | Power Factor | 0.31 | 0.3 | 0.56 | 0.34 | 0.36
|  |  |  | ECC Rating (A) | 966 | 966 | 966 | 966 | 966
|  |  |  | 50 POE Load (A) | 299 | 348 | 212 | 360 | 295
CBD West | F7365 | Kelvin Grove | Milton | NCC Rating (A) | 973 | 973 | 973 | 973 | 973 | CBD | NA | NA
|  |  |  | 10 POE Load (A) | 204 | 212 | 155 | 217 | 227
|  |  |  | Power Factor | 0.65 | 0.64 | 0.84 | 0.65 | 0.65
|  |  |  | ECC Rating (A) | 973 | 973 | 973 | 973 | 973
|  |  |  | 50 POE Load (A) | 428 | 470 | 366 | 482 | 431
CBD West | F781 | Ashgrove West | Kelvin Grove | NCC Rating (A) | 913 | 913 | 913 | 913 | 913 | CBD | NA | NA
|  |  |  | 10 POE Load (A) | 244 | 250 | 206 | 256 | 265
|  |  |  | Power Factor | 0.82 | 0.81 | 0.95 | 0.81 | 0.8
|  |  |  | ECC Rating (A) | 913 | 913 | 913 | 913 | 913
|  |  |  | 50 POE Load (A) | 470 | 509 | 415 | 521 | 476
CBD West | F782 | Ashgrove West | Milton | NCC Rating (A) | 913 | 913 | 913 | 913 | 913 | CBD | NA | NA
|  |  |  | 10 POE Load (A) | 295 | 304 | 243 | 311 | 323
|  |  |  | Power Factor | 0.79 | 0.77 | 0.93 | 0.78 | 0.77
|  |  |  | ECC Rating (A) | 913 | 913 | 913 | 913 | 913
|  |  |  | 50 POE Load (A) | 480 | 520 | 423 | 532 | 486
CBD West | F807 | Makerston St | Charlotte St | NCC Rating (A) | 629 | 629 | 629 | 629 | 629 | CBD | NA | NA
|  |  |  | 10 POE Load (A) | 130 | 146 | 70 | 143 | 151
|  |  |  | Power Factor | 0.19 | 0.17 | 0.45 | 0.19 | 0.17
|  |  |  | ECC Rating (A) | 629 | 629 | 629 | 629 | 629
|  |  |  | 50 POE Load (A) | 269 | 325 | 169 | 327 | 245
CBD West | F808 | Makerston St | Charlotte St | NCC Rating (A) | 629 | 629 | 629 | 629 | 629 | CBD | NA | NA
|  |  |  | 10 POE Load (A) | 159 | 179 | 89 | 175 | 183
|  |  |  | Power Factor | 0.1 | 0.1 | 0.31 | 0.13 | 0.14
|  |  |  | ECC Rating (A) | 629 | 629 | 629 | 629 | 629
|  |  |  | 50 POE Load (A) | 289 | 349 | 188 | 345 | 253
Loganlea | F704 | Beenleigh | Yatala | NCC Rating (A) | 1088 | 1088 | 1088 | 1088 | 1088 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 263 | 257 | 297 | 281 | 279
|  |  |  | Power Factor | 0.97 | 1 | 0.99 | 0.99 | 1
|  |  |  | ECC Rating (A) | 1088 | 1088 | 1088 | 1088 | 1088
|  |  |  | 50 POE Load (A) | 595 | 621 | 607 | 613 | 620
Loganlea | F7351 | Jimboomba | Beaudesert | NCC Rating (A) | 865 | 865 | 865 | 865 | 865 | Rural | 52 | NA
|  |  |  | 10 POE Load (A) | 173 | 177 | 183 | 190 | 199
|  |  |  | Power Factor | 0.97 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | ECC Rating (A) | 865 | 865 | 865 | 865 | 865
|  |  |  | 50 POE Load (A) | 171 | 172 | 180 | 187 | 197
Loganlea | F7354 | Loganlea | Jimboomba | NCC Rating (A) | 952 | 952 | 952 | 952 | 952 | Rural | 52 | NA
|  |  |  | 10 POE Load (A) | 267 | 267 | 272 | 278 | 287
|  |  |  | Power Factor | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | ECC Rating (A) | 952 | 952 | 952 | 952 | 952
|  |  |  | 50 POE Load (A) | 434 | 426 | 440 | 451 | 466
Loganlea | F7377 | Yatala | Coomera | NCC Rating (A) | 1088 | 1088 | 1088 | 1088 | 1088 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 41 | 36 | 75 | 63 | 64
|  |  |  | Power Factor | 0.66 | 0.9 | 0.99 | 1 | 0.98
|  |  |  | ECC Rating (A) | 1088 | 1088 | 1088 | 1088 | 1088
|  |  |  | 50 POE Load (A) | 372 | 390 | 393 | 403 | 411
Loganlea | F787 | Loganlea | Beenleigh | NCC Rating (A) | 1200 | 1200 | 1200 | 1200 | 1200 | Rural | 52 | NA
|  |  |  | 10 POE Load (A) | 359 | 362 | 384 | 380 | 372
|  |  |  | Power Factor | 0.93 | 0.94 | 0.91 | 0.94 | 0.95
|  |  |  | ECC Rating (A) | 1200 | 1200 | 1200 | 1200 | 1200
|  |  |  | 50 POE Load (A) | 538 | 563 | 582 | 586 | 577
Loganlea | F788/1 | Beenleigh | Russell Island Tee | NCC Rating (A) | 325 | 325 | 325 | 325 | 325 | Rural | 52 | NA
|  |  |  | 10 POE Load (A) | 48 | 49 | 49 | 49 | 50
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1
|  |  |  | ECC Rating (A) | 325 | 325 | 325 | 325 | 325
|  |  |  | 50 POE Load (A) | 102 | 100 | 101 | 101 | 102
Loganlea | F788/2 | Russell Island Tee | Stradbroke Island | NCC Rating (A) | 441 | 441 | 441 | 441 | 441 | Rural | 52 | NA
|  |  |  | 10 POE Load (A) | 18 | 18 | 18 | 18 | 18
|  |  |  | Power Factor | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | ECC Rating (A) | 441 | 441 | 441 | 441 | 441
|  |  |  | 50 POE Load (A) | 76 | 75 | 75 | 75 | 75
Loganlea | F788/3 | Russell Island Tee | Russell Island | NCC Rating (A) | 902 | 902 | 902 | 902 | 902 | Rural | 52 | NA
|  |  |  | 10 POE Load (A) | 31 | 31 | 31 | 32 | 32
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1
|  |  |  | ECC Rating (A) | 902 | 902 | 902 | 902 | 902
|  |  |  | 50 POE Load (A) | 28 | 28 | 29 | 29 | 30
Loganlea | F793 | Loganlea | North Springwood | NCC Rating (A) | 872 | 872 | 872 | 872 | 872 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 43 | 43 | 42 | 50 | 40
|  |  |  | Power Factor | 1 | 0.99 | 0.98 | 0.86 | 1
|  |  |  | ECC Rating (A) | 872 | 872 | 872 | 872 | 872
|  |  |  | 50 POE Load (A) | 153 | 148 | 147 | 144 | 144
Loganlea | F799 | Loganlea | North Springwood | NCC Rating (A) | 872 | 872 | 872 | 872 | 872 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 112 | 110 | 107 | 105 | 106
|  |  |  | Power Factor | 1 | 1 | 1 | 0.99 | 1
|  |  |  | ECC Rating (A) | 872 | 872 | 872 | 872 | 872
|  |  |  | 50 POE Load (A) | 149 | 145 | 143 | 141 | 141
Loganlea | F820 | Loganlea | Jimboomba | NCC Rating (A) | 962 | 962 | 962 | 962 | 962 | Rural | 52 | NA
|  |  |  | 10 POE Load (A) | 184 | 184 | 188 | 192 | 198
|  |  |  | Power Factor | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | ECC Rating (A) | 962 | 962 | 962 | 962 | 962
|  |  |  | 50 POE Load (A) | 442 | 434 | 449 | 460 | 476
Loganlea | F837 | Loganlea | Beenleigh | NCC Rating (A) | 1200 | 1200 | 1200 | 1200 | 1200 | Rural | 52 | NA
|  |  |  | 10 POE Load (A) | 359 | 362 | 384 | 380 | 372
|  |  |  | Power Factor | 0.93 | 0.94 | 0.91 | 0.94 | 0.95
|  |  |  | ECC Rating (A) | 1200 | 1200 | 1200 | 1200 | 1200
|  |  |  | 50 POE Load (A) | 538 | 563 | 582 | 586 | 577
Loganlea | F836 | Loganlea | Browns Plains | NCC Rating (A) | 894 | 894 | 894 | 894 | 894 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 169 | 171 | 182 | 173 | 174
|  |  |  | Power Factor | 0.98 | 0.99 | 0.95 | 0.98 | 0.98
|  |  |  | ECC Rating (A) | 894 | 894 | 894 | 894 | 894
|  |  |  | 50 POE Load (A) | 384 | 396 | 394 | 392 | 393
Loganlea | F843 | Loganlea | Browns Plains | NCC Rating (A) | 949 | 949 | 949 | 949 | 949 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 216 | 233 | 216 | 221 | 221
|  |  |  | Power Factor | 0.98 | 0.96 | 0.99 | 0.98 | 0.98
|  |  |  | ECC Rating (A) | 949 | 949 | 949 | 949 | 949
|  |  |  | 50 POE Load (A) | 379 | 391 | 389 | 387 | 388
Loganlea | F904/1 | Beenleigh | Rocky Point Tee | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Rural | 52 | NA
|  |  |  | 10 POE Load (A) | 56 | 56 | 55 | 55 | 55
|  |  |  | Power Factor | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 96 | 94 | 94 | 94 | 94
Loganlea | F904/2 | Rocky Point Tee | Rocky Point | NCC Rating (A) | 868 | 868 | 868 | 868 | 868 | Rural | 52 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0.1 | 0.97 | 0.59 | 0.68 | 0.59
|  |  |  | ECC Rating (A) | 868 | 868 | 868 | 868 | 868
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Loganlea | F904/3 | Rocky Point Tee | Ibis | NCC Rating (A) | 325 | 325 | 325 | 325 | 325 | Rural | 52 | NA
|  |  |  | 10 POE Load (A) | 58 | 57 | 57 | 56 | 57
|  |  |  | Power Factor | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | ECC Rating (A) | 325 | 325 | 325 | 325 | 325
|  |  |  | 50 POE Load (A) | 97 | 96 | 96 | 96 | 96
Middle Ridge | F726 | Postmans Ridge | Gatton | NCC Rating (A) | 690 | 690 | 690 | 690 | 690 | Rural | 52 | NA
|  |  |  | 10 POE Load (A) | 123 | 124 | 128 | 127 | 126
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | ECC Rating (A) | 690 | 690 | 690 | 690 | 690
|  |  |  | 50 POE Load (A) | 334 | 335 | 342 | 338 | 335
Middle Ridge | F727 | Middle Ridge | Postmans Ridge | NCC Rating (A) | 690 | 690 | 690 | 690 | 690 | Rural | 52 | NA
|  |  |  | 10 POE Load (A) | 130 | 130 | 133 | 132 | 131
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1
|  |  |  | ECC Rating (A) | 690 | 690 | 690 | 690 | 690
|  |  |  | 50 POE Load (A) | 269 | 268 | 273 | 271 | 272
Middle Ridge | F7348 | Middle Ridge | Postmans Ridge | NCC Rating (A) | 1280 | 1280 | 1280 | 1280 | 1280 | Rural | 52 | NA
|  |  |  | 10 POE Load (A) | 150 | 149 | 153 | 152 | 151
|  |  |  | Power Factor | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
|  |  |  | ECC Rating (A) | 1280 | 1280 | 1280 | 1280 | 1280
|  |  |  | 50 POE Load (A) | 266 | 265 | 270 | 267 | 269
Molendinar | F7193 | Molendinar | Cades County | NCC Rating (A) | 1108 | 1108 | 1108 | 1108 | 1108 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 290 | 285 | 265 | 273 | 279
|  |  |  | Power Factor | 0.98 | 0.98 | 0.99 | 0.99 | 0.98
|  |  |  | ECC Rating (A) | 1108 | 1108 | 1108 | 1108 | 1108
|  |  |  | 50 POE Load (A) | 495 | 486 | 453 | 472 | 487
Molendinar | F7229 | Molendinar | Robina | NCC Rating (A) | 1412 | 1412 | 1412 | 1412 | 1412 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 38 | 103 | 96 | 131 | 45
|  |  |  | Power Factor | 0.15 | 0.09 | 0.37 | 0.26 | 0.94
|  |  |  | ECC Rating (A) | 1412 | 1412 | 1412 | 1412 | 1412
|  |  |  | 50 POE Load (A) | 180 | 178 | 242 | 177 | 252
Molendinar | F7283 | Cades County | Coomera | NCC Rating (A) | 1088 | 1088 | 1088 | 1088 | 1088 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 355 | 365 | 325 | 342 | 354
|  |  |  | Power Factor | 0.98 | 0.98 | 0.99 | 0.99 | 0.98
|  |  |  | ECC Rating (A) | 1088 | 1088 | 1088 | 1088 | 1088
|  |  |  | 50 POE Load (A) | 582 | 594 | 598 | 600 | 607
Molendinar | F7297 | Molendinar | Cades County | NCC Rating (A) | 1108 | 1108 | 1108 | 1108 | 1108 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 290 | 285 | 265 | 273 | 279
|  |  |  | Power Factor | 0.98 | 0.98 | 0.99 | 0.99 | 0.98
|  |  |  | ECC Rating (A) | 1108 | 1108 | 1108 | 1108 | 1108
|  |  |  | 50 POE Load (A) | 495 | 486 | 453 | 472 | 487
Molendinar | F798 | Molendinar | Nerang | NCC Rating (A) | 1250 | 1250 | 1250 | 1250 | 1250 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 125 | 162 | 186 | 207 | 160
|  |  |  | Power Factor | 0.89 | 0.67 | 0.81 | 0.72 | 0.98
|  |  |  | ECC Rating (A) | 1250 | 1250 | 1250 | 1250 | 1250
|  |  |  | 50 POE Load (A) | 240 | 197 | 333 | 279 | 339
Molendinar | F907 | Molendinar | Southport | NCC Rating (A) | 834 | 834 | 834 | 834 | 834 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 125 | 124 | 123 | 122 | 123
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1
|  |  |  | ECC Rating (A) | 834 | 834 | 834 | 834 | 834
|  |  |  | 50 POE Load (A) | 264 | 261 | 259 | 259 | 259
Molendinar | F917 | Molendinar | Southport | NCC Rating (A) | 1035 | 1035 | 1035 | 1035 | 1035 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 145 | 144 | 143 | 142 | 143
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | ECC Rating (A) | 1035 | 1035 | 1035 | 1035 | 1035
|  |  |  | 50 POE Load (A) | 263 | 260 | 259 | 258 | 259
Molendinar | F916 | Molendinar | Surfers Paradise | NCC Rating (A) | 1100 | 1100 | 1100 | 1100 | 1100 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 237 | 318 | 379 | 429 | 340
|  |  |  | Power Factor | 0.94 | 0.69 | 0.85 | 0.75 | 1
|  |  |  | ECC Rating (A) | 1100 | 1100 | 1100 | 1100 | 1100
|  |  |  | 50 POE Load (A) | 435 | 360 | 556 | 532 | 571
Mudgeeraba | F706 | Mudgeeraba | Nerang | NCC Rating (A) | 1250 | 1250 | 1250 | 1250 | 1250 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 97 | 131 | 91 | 123 | 46
|  |  |  | Power Factor | 0.98 | 0.76 | 0.6 | 0.45 | 1
|  |  |  | ECC Rating (A) | 1250 | 1250 | 1250 | 1250 | 1250
|  |  |  | 50 POE Load (A) | 230 | 198 | 200 | 197 | 198
Mudgeeraba | F754 | Mudgeeraba | Burleigh Heads | NCC Rating (A) | 1267 | 1267 | 1267 | 1267 | 1267 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 382 | 383 | 382 | 382 | 379
|  |  |  | Power Factor | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | ECC Rating (A) | 1267 | 1267 | 1267 | 1267 | 1267
|  |  |  | 50 POE Load (A) | 764 | 751 | 757 | 754 | 757
Mudgeeraba | F755 | Mudgeeraba | Burleigh Heads | NCC Rating (A) | 1267 | 1267 | 1267 | 1267 | 1267 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 383 | 383 | 383 | 382 | 379
|  |  |  | Power Factor | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | ECC Rating (A) | 1267 | 1267 | 1267 | 1267 | 1267
|  |  |  | 50 POE Load (A) | 764 | 751 | 757 | 754 | 758
Mudgeeraba | F779 | Mudgeeraba | Merrimac | NCC Rating (A) | 1412 | 1412 | 1412 | 1412 | 1412 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 160 | 193 | 144 | 175 | 102
|  |  |  | Power Factor | 0.98 | 0.83 | 0.76 | 0.63 | 1
|  |  |  | ECC Rating (A) | 1412 | 1412 | 1412 | 1412 | 1412
|  |  |  | 50 POE Load (A) | 311 | 263 | 266 | 263 | 267
Mudgeeraba | F780 | Mudgeeraba | Merrimac | NCC Rating (A) | 1412 | 1412 | 1412 | 1412 | 1412 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 160 | 193 | 144 | 175 | 102
|  |  |  | Power Factor | 0.98 | 0.83 | 0.76 | 0.63 | 1
|  |  |  | ECC Rating (A) | 1412 | 1412 | 1412 | 1412 | 1412
|  |  |  | 50 POE Load (A) | 311 | 263 | 266 | 263 | 267
Mudgeeraba | F794 | Mudgeeraba | Robina | NCC Rating (A) | 1412 | 1412 | 1412 | 1412 | 1412 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 187 | 203 | 157 | 175 | 138
|  |  |  | Power Factor | 1 | 0.94 | 0.93 | 0.84 | 0.99
|  |  |  | ECC Rating (A) | 1412 | 1412 | 1412 | 1412 | 1412
|  |  |  | 50 POE Load (A) | 308 | 277 | 259 | 229 | 261
Mudgeeraba | F826 | Broadbeach | Surfers Paradise | NCC Rating (A) | 574 | 574 | 574 | 574 | 574 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 46 | 121 | 112 | 152 | 51
|  |  |  | Power Factor | 0.15 | 0.08 | 0.36 | 0.26 | 0.93
|  |  |  | ECC Rating (A) | 574 | 574 | 574 | 574 | 574
|  |  |  | 50 POE Load (A) | 287 | 122 | 273 | 163 | 257
Mudgeeraba | F827 | Broadbeach | Surfers Paradise | NCC Rating (A) | 574 | 574 | 574 | 574 | 574 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 46 | 121 | 112 | 152 | 51
|  |  |  | Power Factor | 0.16 | 0.08 | 0.36 | 0.26 | 0.93
|  |  |  | ECC Rating (A) | 574 | 574 | 574 | 574 | 574
|  |  |  | 50 POE Load (A) | 287 | 122 | 272 | 163 | 256
Mudgeeraba | F838 | Mudgeeraba | Varsity Lakes | NCC Rating (A) | 1347 | 1347 | 1347 | 1347 | 1347 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 64 | 64 | 64 | 64 | 63
|  |  |  | Power Factor | 0.99 | 1 | 1 | 1 | 1
|  |  |  | ECC Rating (A) | 1347 | 1347 | 1347 | 1347 | 1347
|  |  |  | 50 POE Load (A) | 125 | 123 | 125 | 123 | 124
Mudgeeraba | F839 | Mudgeeraba | Varsity Lakes | NCC Rating (A) | 1347 | 1347 | 1347 | 1347 | 1347 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 64 | 64 | 64 | 64 | 63
|  |  |  | Power Factor | 0.99 | 1 | 1 | 1 | 1
|  |  |  | ECC Rating (A) | 1347 | 1347 | 1347 | 1347 | 1347
|  |  |  | 50 POE Load (A) | 125 | 123 | 125 | 123 | 124
Mudgeeraba | F918 | Merrimac | Broadbeach | NCC Rating (A) | 1286 | 1286 | 1286 | 1286 | 1286 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 113 | 157 | 113 | 151 | 54
|  |  |  | Power Factor | 0.98 | 0.74 | 0.58 | 0.43 | 1
|  |  |  | ECC Rating (A) | 1286 | 1286 | 1286 | 1286 | 1286
|  |  |  | 50 POE Load (A) | 310 | 216 | 238 | 216 | 223
Mudgeeraba | F919 | Merrimac | Broadbeach | NCC Rating (A) | 1286 | 1286 | 1286 | 1286 | 1286 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 113 | 157 | 113 | 151 | 54
|  |  |  | Power Factor | 0.98 | 0.74 | 0.58 | 0.43 | 1
|  |  |  | ECC Rating (A) | 1286 | 1286 | 1286 | 1286 | 1286
|  |  |  | 50 POE Load (A) | 310 | 216 | 238 | 216 | 223
Murarrie | F7270 | Murarrie | Lytton Bulk | NCC Rating (A) | 1364 | 1364 | 1364 | 1364 | 1364 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 291 | 298 | 307 | 306 | 300
|  |  |  | Power Factor | 0.95 | 0.96 | 0.96 | 0.96 | 0.98
|  |  |  | ECC Rating (A) | 1364 | 1364 | 1364 | 1364 | 1364
|  |  |  | 50 POE Load (A) | 568 | 580 | 598 | 598 | 596
Murarrie | F7271 | Murarrie | Lytton Bulk | NCC Rating (A) | 1364 | 1364 | 1364 | 1364 | 1364 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 291 | 298 | 307 | 306 | 300
|  |  |  | Power Factor | 0.95 | 0.96 | 0.96 | 0.96 | 0.98
|  |  |  | ECC Rating (A) | 1364 | 1364 | 1364 | 1364 | 1364
|  |  |  | 50 POE Load (A) | 568 | 580 | 598 | 598 | 596
Murarrie | F7272 | Murarrie | Doboy | NCC Rating (A) | 1220 | 1220 | 1220 | 1220 | 1220 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 170 | 170 | 171 | 175 | 179
|  |  |  | Power Factor | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | ECC Rating (A) | 1220 | 1220 | 1220 | 1220 | 1220
|  |  |  | 50 POE Load (A) | 249 | 248 | 249 | 256 | 262
Murarrie | F7273 | Murarrie | Doboy | NCC Rating (A) | 1220 | 1220 | 1220 | 1220 | 1220 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 170 | 170 | 171 | 175 | 179
|  |  |  | Power Factor | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | ECC Rating (A) | 1220 | 1220 | 1220 | 1220 | 1220
|  |  |  | 50 POE Load (A) | 249 | 248 | 249 | 256 | 262
Murarrie | F7274 | Murarrie | Doboy | NCC Rating (A) | 1220 | 1220 | 1220 | 1220 | 1220 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 170 | 170 | 171 | 175 | 179
|  |  |  | Power Factor | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | ECC Rating (A) | 1220 | 1220 | 1220 | 1220 | 1220
|  |  |  | 50 POE Load (A) | 249 | 248 | 249 | 256 | 262
Palmwoods | F745/2 | Moodlu | Beerwah Tee | NCC Rating (A) | 1064 | 1064 | 1064 | 1064 | 1064 | Rural | 52 | NA
|  |  |  | 10 POE Load (A) | 143 | 146 | 143 | 138 | 137
|  |  |  | Power Factor | 0.98 | 0.98 | 1 | 0.99 | 1
|  |  |  | ECC Rating (A) | 1064 | 1064 | 1064 | 1064 | 1064
|  |  |  | 50 POE Load (A) | 222 | 227 | 222 | 221 | 219
Palmwoods | F745/3 | Moodlu | Caboolture | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Rural | 52 | NA
|  |  |  | 10 POE Load (A) | 304 | 308 | 309 | 309 | 309
|  |  |  | Power Factor | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 598 | 598 | 605 | 601 | 607
Palmwoods | F745/4 | Palmwoods | Beerwah Tee | NCC Rating (A) | 1064 | 1064 | 1064 | 1064 | 1064 | Rural | 52 | NA
|  |  |  | 10 POE Load (A) | 250 | 256 | 257 | 251 | 251
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1
|  |  |  | ECC Rating (A) | 1064 | 1064 | 1064 | 1064 | 1064
|  |  |  | 50 POE Load (A) | 426 | 432 | 434 | 433 | 431
Palmwoods | F745/5 | Beerwah Tee | Beerwah | NCC Rating (A) | 975 | 975 | 975 | 975 | 975 | Rural | 52 | NA
|  |  |  | 10 POE Load (A) | 111 | 114 | 115 | 116 | 117
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | ECC Rating (A) | 975 | 975 | 975 | 975 | 975
|  |  |  | 50 POE Load (A) | 217 | 219 | 225 | 225 | 228
Palmwoods | F746/2 | Moodlu | Beerwah Tee | NCC Rating (A) | 1064 | 1064 | 1064 | 1064 | 1064 | Rural | 52 | NA
|  |  |  | 10 POE Load (A) | 143 | 146 | 143 | 138 | 137
|  |  |  | Power Factor | 0.98 | 0.98 | 1 | 0.99 | 1
|  |  |  | ECC Rating (A) | 1064 | 1064 | 1064 | 1064 | 1064
|  |  |  | 50 POE Load (A) | 222 | 227 | 222 | 221 | 219
Palmwoods | F746/3 | Moodlu | Caboolture | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Rural | 52 | NA
|  |  |  | 10 POE Load (A) | 305 | 308 | 309 | 310 | 309
|  |  |  | Power Factor | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 598 | 598 | 605 | 601 | 607
Palmwoods | F746/4 | Palmwoods | Beerwah Tee | NCC Rating (A) | 1064 | 1064 | 1064 | 1064 | 1064 | Rural | 52 | NA
|  |  |  | 10 POE Load (A) | 250 | 256 | 257 | 251 | 251
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1
|  |  |  | ECC Rating (A) | 1064 | 1064 | 1064 | 1064 | 1064
|  |  |  | 50 POE Load (A) | 426 | 432 | 434 | 433 | 431
Palmwoods | F746/5 | Beerwah Tee | Beerwah | NCC Rating (A) | 1033 | 1033 | 1033 | 1033 | 1033 | Rural | 52 | NA
|  |  |  | 10 POE Load (A) | 111 | 114 | 115 | 116 | 117
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | ECC Rating (A) | 1033 | 1033 | 1033 | 1033 | 1033
|  |  |  | 50 POE Load (A) | 217 | 219 | 225 | 225 | 228
Palmwoods 132 kV | F7189/1 | Palmwoods | Image Flat | NCC Rating (A) | 1052 | 1052 | 1052 | 1052 | 1052 | Rural | 44 | NA
|  |  |  | 10 POE Load (A) | 78 | 107 | 109 | 113 | 112
|  |  |  | Power Factor | 0.88 | 0.57 | 0.51 | 0.53 | 0.49
|  |  |  | ECC Rating (A) | 1052 | 1052 | 1052 | 1052 | 1052
|  |  |  | 50 POE Load (A) | 235 | 233 | 242 | 241 | 247
Palmwoods 132 kV | F7189/2 | Image Flat | Cooroy | NCC Rating (A) | 942 | 942 | 942 | 942 | 942 | Rural | 44 | NA
|  |  |  | 10 POE Load (A) | 78 | 116 | 123 | 123 | 127
|  |  |  | Power Factor | 0.91 | 0.7 | 0.7 | 0.68 | 0.69
|  |  |  | ECC Rating (A) | 942 | 942 | 942 | 942 | 942
|  |  |  | 50 POE Load (A) | 344 | 346 | 352 | 352 | 360
Palmwoods 132 kV | F7189/3 | Image Flat | Nambour | NCC Rating (A) | 833 | 833 | 833 | 833 | 833 | Rural | 44 | NA
|  |  |  | 10 POE Load (A) | 139 | 140 | 140 | 141 | 140
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1
|  |  |  | ECC Rating (A) | 833 | 833 | 833 | 833 | 833
|  |  |  | 50 POE Load (A) | 263 | 266 | 266 | 266 | 266
Palmwoods 132 kV | F7298 | Sunrise Hills | Noosaville | NCC Rating (A) | 975 | 975 | 975 | 975 | 975 | Urban | 17 | NA
|  |  |  | 10 POE Load (A) | 72 | 73 | 72 | 73 | 73
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | ECC Rating (A) | 975 | 975 | 975 | 975 | 975
|  |  |  | 50 POE Load (A) | 139 | 137 | 137 | 137 | 136
Palmwoods 132 kV | F777 | Palmwoods | Mooloolaba | NCC Rating (A) | 1469 | 1469 | 1469 | 1469 | 1469 | Urban | 17 | NA
|  |  |  | 10 POE Load (A) | 453 | 262 | 272 | 279 | 282
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 1 | 1
|  |  |  | ECC Rating (A) | 1469 | 1469 | 1469 | 1469 | 1469
|  |  |  | 50 POE Load (A) | 873 | 366 | 381 | 389 | 392
Palmwoods 132 kV | F778 | Palmwoods | Mooloolaba | NCC Rating (A) | 1469 | 1469 | 1469 | 1469 | 1469 | Urban | 17 | NA
|  |  |  | 10 POE Load (A) | 453 | 262 | 272 | 279 | 282
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 1 | 1
|  |  |  | ECC Rating (A) | 1469 | 1469 | 1469 | 1469 | 1469
|  |  |  | 50 POE Load (A) | 872 | 417 | 434 | 444 | 448
Palmwoods 132 kV | F790 | Sunrise Hills | Noosaville | NCC Rating (A) | 975 | 975 | 975 | 975 | 975 | Urban | 17 | NA
|  |  |  | 10 POE Load (A) | 73 | 73 | 73 | 74 | 73
|  |  |  | Power Factor | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | ECC Rating (A) | 975 | 975 | 975 | 975 | 975
|  |  |  | 50 POE Load (A) | 143 | 141 | 141 | 141 | 140
Palmwoods 132 kV | F795/1 | Palmwoods | Image Flat | NCC Rating (A) | 1052 | 1052 | 1052 | 1052 | 1052 | Rural | 44 | NA
|  |  |  | 10 POE Load (A) | 78 | 107 | 109 | 113 | 112
|  |  |  | Power Factor | 0.88 | 0.56 | 0.51 | 0.53 | 0.49
|  |  |  | ECC Rating (A) | 1052 | 1052 | 1052 | 1052 | 1052
|  |  |  | 50 POE Load (A) | 236 | 233 | 243 | 241 | 248
Palmwoods 132 kV | F795/2 | Image Flat | Cooroy | NCC Rating (A) | 942 | 942 | 942 | 942 | 942 | Rural | 44 | NA
|  |  |  | 10 POE Load (A) | 79 | 116 | 123 | 123 | 127
|  |  |  | Power Factor | 0.91 | 0.7 | 0.7 | 0.68 | 0.69
|  |  |  | ECC Rating (A) | 942 | 942 | 942 | 942 | 942
|  |  |  | 50 POE Load (A) | 345 | 347 | 353 | 353 | 360
Palmwoods 132 kV | F795/3 | Image Flat | Nambour | NCC Rating (A) | 833 | 833 | 833 | 833 | 833 | Rural | 44 | NA
|  |  |  | 10 POE Load (A) | 139 | 140 | 140 | 141 | 140
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1
|  |  |  | ECC Rating (A) | 833 | 833 | 833 | 833 | 833
|  |  |  | 50 POE Load (A) | 263 | 266 | 266 | 266 | 266
Palmwoods 132 kV | F796 | Cooroy | Sunrise Hills | NCC Rating (A) | 949 | 949 | 949 | 949 | 949 | Rural | 44 | NA
|  |  |  | 10 POE Load (A) | 233 | 233 | 233 | 234 | 232
|  |  |  | Power Factor | 0.97 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | ECC Rating (A) | 949 | 949 | 949 | 949 | 949
|  |  |  | 50 POE Load (A) | 448 | 441 | 439 | 437 | 435
Palmwoods 132 kV | F797 | Cooroy | Sunrise Hills | NCC Rating (A) | 975 | 975 | 975 | 975 | 975 | Rural | 44 | NA
|  |  |  | 10 POE Load (A) | 233 | 234 | 233 | 234 | 232
|  |  |  | Power Factor | 0.97 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | ECC Rating (A) | 975 | 975 | 975 | 975 | 975
|  |  |  | 50 POE Load (A) | 448 | 441 | 439 | 437 | 435
Palmwoods 132 kV | F803 | Mooloolaba | Caloundra | NCC Rating (A) | 975 | 975 | 975 | 975 | 975 | Urban | 17 | NA
|  |  |  | 10 POE Load (A) | 169 | 171 | 178 | 187 | 189
|  |  |  | Power Factor | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | ECC Rating (A) | 975 | 975 | 975 | 975 | 975
|  |  |  | 50 POE Load (A) | 396 | 397 | 415 | 433 | 436
Palmwoods 132 kV | F804 | Caloundra | Currimundi | NCC Rating (A) | 975 | 975 | 975 | 975 | 975 | Urban | 17 | NA
|  |  |  | 10 POE Load (A) | 25 | 27 | 25 | 23 | 25
|  |  |  | Power Factor | 0.98 | 0.98 | 0.98 | 0.98 | 0.97
|  |  |  | ECC Rating (A) | 975 | 975 | 975 | 975 | 975
|  |  |  | 50 POE Load (A) | 209 | 208 | 220 | 234 | 234
Palmwoods 132 kV | F815 | Mooloolaba | Alexandra Headlands | NCC Rating (A) | 975 | 975 | 975 | 975 | 975 | Urban | 17 | NA
|  |  |  | 10 POE Load (A) | 210 | 69 | 70 | 67 | 70
|  |  |  | Power Factor | 0.99 | 0.75 | 0.75 | 0.74 | 0.75
|  |  |  | ECC Rating (A) | 975 | 975 | 975 | 975 | 975
|  |  |  | 50 POE Load (A) | 357 | 138 | 143 | 148 | 147
Palmwoods 132 kV | F816 | Mooloolaba | West Maroochydore | NCC Rating (A) | 975 | 975 | 975 | 975 | 975 | Urban | 17 | NA
|  |  |  | 10 POE Load (A) | 162 | 83 | 88 | 91 | 91
|  |  |  | Power Factor | 0.99 | 0.87 | 0.89 | 0.9 | 0.9
|  |  |  | ECC Rating (A) | 975 | 975 | 975 | 975 | 975
|  |  |  | 50 POE Load (A) | 155 | 157 | 164 | 169 | 170
Palmwoods 132 kV | F819 | Mooloolaba | Kawana | NCC Rating (A) | 894 | 894 | 894 | 894 | 894 | Urban | 17 | NA
|  |  |  | 10 POE Load (A) | 240 | 242 | 253 | 266 | 267
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | ECC Rating (A) | 894 | 894 | 894 | 894 | 894
|  |  |  | 50 POE Load (A) | 395 | 395 | 412 | 431 | 434
Palmwoods 132 kV | F821 | West Maroochydore | Alexandra Headlands | NCC Rating (A) | 975 | 975 | 975 | 975 | 975 | Urban | 17 | NA
|  |  |  | 10 POE Load (A) | 35 | 188 | 196 | 200 | 204
|  |  |  | Power Factor | 0.98 | 1 | 1 | 1 | 1
|  |  |  | ECC Rating (A) | 975 | 975 | 975 | 975 | 975
|  |  |  | 50 POE Load (A) | 123 | 331 | 346 | 353 | 359
Palmwoods 132 kV | F844 | Kawana | Birtinya | NCC Rating (A) | 975 | 975 | 975 | 975 | 975 | Urban | 17 | NA
|  |  |  | 10 POE Load (A) | 151 | 154 | 165 | 178 | 179
|  |  |  | Power Factor | 1 | 1 | 1 | 0.99 | 0.99
|  |  |  | ECC Rating (A) | 975 | 975 | 975 | 975 | 975
|  |  |  | 50 POE Load (A) | 311 | 312 | 330 | 348 | 352
Palmwoods 132 kV | F851 | Birtinya | Currimundi | NCC Rating (A) | 975 | 975 | 975 | 975 | 975 | Urban | 17 | NA
|  |  |  | 10 POE Load (A) | 86 | 88 | 87 | 86 | 88
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1
|  |  |  | ECC Rating (A) | 975 | 975 | 975 | 975 | 975
|  |  |  | 50 POE Load (A) | 248 | 249 | 254 | 260 | 263
Palmwoods 132 kV | F845 | Palmwoods | West Maroochydore | NCC Rating (A) |  | 1376 | 1376 | 1376 | 1376 | Urban | 17 | NA
|  |  |  | 10 POE Load (A) |  | 192 | 199 | 204 | 206
|  |  |  | Power Factor |  | 1 | 1 | 1 | 1
|  |  |  | ECC Rating (A) |  | 1376 | 1376 | 1376 | 1376
|  |  |  | 50 POE Load (A) |  | 258 | 267 | 272 | 275
Palmwoods 132 kV | F846 | Palmwoods | West Maroochydore | NCC Rating (A) |  | 1376 | 1376 | 1376 | 1376 | Urban | 17 | NA
|  |  |  | 10 POE Load (A) |  | 192 | 199 | 204 | 206
|  |  |  | Power Factor |  | 1 | 1 | 1 | 1
|  |  |  | ECC Rating (A) |  | 1376 | 1376 | 1376 | 1376
|  |  |  | 50 POE Load (A) |  | 258 | 267 | 272 | 275
Rocklea | F817 | Rocklea | Archerfield | NCC Rating (A) | 1220 | 1220 | 1220 | 1220 | 1220 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 142 | 137 | 128 | 125 | 123
|  |  |  | Power Factor | 0.94 | 0.95 | 0.95 | 0.95 | 0.95
|  |  |  | ECC Rating (A) | 1220 | 1220 | 1220 | 1220 | 1220
|  |  |  | 50 POE Load (A) | 280 | 271 | 251 | 244 | 241
Rocklea | F818 | Rocklea | Archerfield | NCC Rating (A) | 1220 | 1220 | 1220 | 1220 | 1220 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 142 | 137 | 128 | 125 | 123
|  |  |  | Power Factor | 0.94 | 0.95 | 0.95 | 0.95 | 0.95
|  |  |  | ECC Rating (A) | 1220 | 1220 | 1220 | 1220 | 1220
|  |  |  | 50 POE Load (A) | 280 | 271 | 251 | 244 | 241
South Pine | F7337 | Nudgee | Myrtletown | NCC Rating (A) | 1171 | 1171 | 1171 | 1171 | 1171 | High Sec | NA | NA
|  |  |  | 10 POE Load (A) | 94 | 95 | 95 | 95 | 94
|  |  |  | Power Factor | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | ECC Rating (A) | 1171 | 1171 | 1171 | 1171 | 1171
|  |  |  | 50 POE Load (A) | 187 | 189 | 189 | 187 | 188
South Pine | F7338 | Nudgee | Myrtletown | NCC Rating (A) | 1171 | 1171 | 1171 | 1171 | 1171 | High Sec | NA | NA
|  |  |  | 10 POE Load (A) | 94 | 95 | 95 | 95 | 94
|  |  |  | Power Factor | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | ECC Rating (A) | 1171 | 1171 | 1171 | 1171 | 1171
|  |  |  | 50 POE Load (A) | 187 | 189 | 189 | 187 | 188
South Pine | F7341 | South Pine | Nudgee | NCC Rating (A) | 1663 | 1663 | 1663 | 1663 | 1663 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 498 | 514 | 515 | 509 | 507
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1
|  |  |  | ECC Rating (A) | 1663 | 1663 | 1663 | 1663 | 1663
|  |  |  | 50 POE Load (A) | 985 | 1008 | 1015 | 999 | 1000
South Pine | F7342 | South Pine | Nudgee | NCC Rating (A) | 1663 | 1663 | 1663 | 1663 | 1663 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 498 | 515 | 516 | 510 | 507
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1
|  |  |  | ECC Rating (A) | 1663 | 1663 | 1663 | 1663 | 1663
|  |  |  | 50 POE Load (A) | 985 | 1008 | 1015 | 999 | 999
South Pine | F7344 | South Pine | Griffin | NCC Rating (A) | 1293 | 1293 | 1293 | 1293 | 1293 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 201 | 209 | 374 | 211 | 206
|  |  |  | Power Factor | 0.99 | 0.99 | 0.64 | 0.99 | 1
|  |  |  | ECC Rating (A) | 1293 | 1293 | 1293 | 1293 | 1293
|  |  |  | 50 POE Load (A) | 373 | 383 | 529 | 385 | 380
South Pine | F7345 | South Pine | Griffin | NCC Rating (A) | 1293 | 1293 | 1293 | 1293 | 1293 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 201 | 209 | 374 | 211 | 206
|  |  |  | Power Factor | 0.99 | 0.99 | 0.64 | 0.99 | 1
|  |  |  | ECC Rating (A) | 1293 | 1293 | 1293 | 1293 | 1293
|  |  |  | 50 POE Load (A) | 373 | 383 | 529 | 385 | 380
South Pine | F7358 | Griffin | Hays Inlet | NCC Rating (A) | 1600 | 1600 | 1600 | 1600 | 1600 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 189 | 189 | 602 | 189 | 179
|  |  |  | Power Factor | 0.89 | 0.98 | 0.42 | 0.98 | 0.98
|  |  |  | ECC Rating (A) | 1600 | 1600 | 1600 | 1600 | 1600
|  |  |  | 50 POE Load (A) | 264 | 278 | 409 | 279 | 262
South Pine | F737/1 | South Pine | Bunyaville | NCC Rating (A) | 1164 | 1164 | 1164 | 1164 | 1164 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 297 | 298 | 298 | 296 | 294
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | ECC Rating (A) | 1164 | 1164 | 1164 | 1164 | 1164
|  |  |  | 50 POE Load (A) | 586 | 583 | 576 | 577 | 573
South Pine | F737/2 | Bunyaville | Stafford | NCC Rating (A) | 1370 | 1370 | 1370 | 1370 | 1370 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 301 | 302 | 302 | 300 | 298
|  |  |  | Power Factor | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | ECC Rating (A) | 1370 | 1370 | 1370 | 1370 | 1370
|  |  |  | 50 POE Load (A) | 592 | 589 | 582 | 583 | 578
South Pine | F738/1 | South Pine | Bunyaville | NCC Rating (A) | 1164 | 1164 | 1164 | 1164 | 1164 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 297 | 298 | 298 | 296 | 294
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | ECC Rating (A) | 1164 | 1164 | 1164 | 1164 | 1164
|  |  |  | 50 POE Load (A) | 586 | 583 | 576 | 577 | 573
South Pine | F738/2 | Bunyaville B | Stafford | NCC Rating (A) | 1370 | 1370 | 1370 | 1370 | 1370 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 301 | 302 | 302 | 300 | 298
|  |  |  | Power Factor | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | ECC Rating (A) | 1370 | 1370 | 1370 | 1370 | 1370
|  |  |  | 50 POE Load (A) | 592 | 589 | 582 | 583 | 578
South Pine | F739 | South Pine | Bald Hills | NCC Rating (A) | 1600 | 1600 | 1600 | 1600 | 1600 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 186 | 184 | 184 | 182 | 181
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | ECC Rating (A) | 1600 | 1600 | 1600 | 1600 | 1600
|  |  |  | 50 POE Load (A) | 343 | 337 | 337 | 333 | 333
South Pine | F740 | South Pine | Sandgate | NCC Rating (A) | 1600 | 1600 | 1600 | 1600 | 1600 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 173 | 172 | 171 | 170 | 169
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | ECC Rating (A) | 1600 | 1600 | 1600 | 1600 | 1600
|  |  |  | 50 POE Load (A) | 343 | 337 | 337 | 333 | 333
South Pine | F741 | South Pine | Hays Inlet | NCC Rating (A) | 904 | 904 | 904 | 904 | 904 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 237 | 207 | 239 | 208 | 223
|  |  |  | Power Factor | 0.89 | 0.98 | 0.75 | 0.98 | 0.94
|  |  |  | ECC Rating (A) | 904 | 904 | 904 | 904 | 904
|  |  |  | 50 POE Load (A) | 326 | 297 | 290 | 298 | 335
South Pine | F742 | South Pine | Hays Inlet | NCC Rating (A) | 904 | 904 | 904 | 904 | 904 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 236 | 206 | 238 | 207 | 223
|  |  |  | Power Factor | 0.89 | 0.98 | 0.75 | 0.98 | 0.94
|  |  |  | ECC Rating (A) | 904 | 904 | 904 | 904 | 904
|  |  |  | 50 POE Load (A) | 325 | 296 | 289 | 297 | 334
South Pine | F7299 | South Pine | Brendale | NCC Rating (A) | 1336 | 1336 | 1336 | 1336 | 1336 | Rural | 52 | NA
|  |  |  | 10 POE Load (A) | 208 | 207 | 209 | 207 | 206
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1
|  |  |  | ECC Rating (A) | 1336 | 1336 | 1336 | 1336 | 1336
|  |  |  | 50 POE Load (A) | 297 | 293 | 297 | 293 | 293
South Pine | F743 | South Pine | Brendale | NCC Rating (A) | 785 | 785 | 785 | 785 | 785 | Rural | 52 | NA
|  |  |  | 10 POE Load (A) | 208 | 207 | 209 | 207 | 206
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1
|  |  |  | ECC Rating (A) | 785 | 785 | 785 | 785 | 785
|  |  |  | 50 POE Load (A) | 297 | 293 | 297 | 293 | 293
South Pine | F744 | South Pine | Brendale | NCC Rating (A) | 785 | 785 | 785 | 785 | 785 | Rural | 52 | NA
|  |  |  | 10 POE Load (A) | 208 | 207 | 209 | 207 | 206
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1
|  |  |  | ECC Rating (A) | 785 | 785 | 785 | 785 | 785
|  |  |  | 50 POE Load (A) | 297 | 293 | 297 | 293 | 293
South Pine | F745/1 | South Pine | Moodlu | NCC Rating (A) | 1064 | 1064 | 1064 | 1064 | 1064 | Rural | 52 | NA
|  |  |  | 10 POE Load (A) | 182 | 183 | 174 | 189 | 183
|  |  |  | Power Factor | 0.86 | 0.86 | 0.91 | 0.88 | 0.9
|  |  |  | ECC Rating (A) | 1064 | 1064 | 1064 | 1064 | 1064
|  |  |  | 50 POE Load (A) | 394 | 391 | 399 | 397 | 411
South Pine | F746/1 | South Pine | Moodlu | NCC Rating (A) | 1064 | 1064 | 1064 | 1064 | 1064 | Rural | 52 | NA
|  |  |  | 10 POE Load (A) | 183 | 183 | 175 | 189 | 184
|  |  |  | Power Factor | 0.86 | 0.86 | 0.91 | 0.88 | 0.9
|  |  |  | ECC Rating (A) | 1064 | 1064 | 1064 | 1064 | 1064
|  |  |  | 50 POE Load (A) | 394 | 391 | 399 | 396 | 411
South Pine | F831 | Bald Hills | Sandgate | NCC Rating (A) | 1600 | 1600 | 1600 | 1600 | 1600 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 153 | 152 | 151 | 149 | 148
|  |  |  | Power Factor | 0.99 | 0.99 | 1 | 0.99 | 0.99
|  |  |  | ECC Rating (A) | 1600 | 1600 | 1600 | 1600 | 1600
|  |  |  | 50 POE Load (A) | 311 | 305 | 305 | 301 | 301
South Pine | F912 | Nudgee | Meeandah | NCC Rating (A) | 491 | 491 | 491 | 491 | 491 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 92 | 100 | 104 | 102 | 101
|  |  |  | Power Factor | 0.93 | 0.93 | 0.93 | 0.93 | 0.93
|  |  |  | ECC Rating (A) | 491 | 491 | 491 | 491 | 491
|  |  |  | 50 POE Load (A) | 184 | 199 | 207 | 201 | 200
South Pine | F913 | Nudgee | Meeandah | NCC Rating (A) | 491 | 491 | 491 | 491 | 491 | Urban | 21 | NA
|  |  |  | 10 POE Load (A) | 92 | 100 | 104 | 102 | 101
|  |  |  | Power Factor | 0.93 | 0.93 | 0.93 | 0.93 | 0.93
|  |  |  | ECC Rating (A) | 491 | 491 | 491 | 491 | 491
|  |  |  | 50 POE Load (A) | 184 | 199 | 207 | 201 | 200
Woolooga 132 kV | F7186 | Cooran | Cooroy | NCC Rating (A) | 963 | 963 | 963 | 963 | 963 | Rural | 44 | NA
|  |  |  | 10 POE Load (A) | 285 | 286 | 305 | 288 | 293
|  |  |  | Power Factor | 0.92 | 0.89 | 0.82 | 0.9 | 0.88
|  |  |  | ECC Rating (A) | 963 | 963 | 963 | 963 | 963
|  |  |  | 50 POE Load (A) | 525 | 536 | 550 | 539 | 547
Woolooga 132 kV | F7343 | Traveston | Cooran | NCC Rating (A) | 963 | 963 | 963 | 963 | 963 | Rural | 44 | NA
|  |  |  | 10 POE Load (A) | 309 | 309 | 327 | 312 | 317
|  |  |  | Power Factor | 0.95 | 0.92 | 0.86 | 0.93 | 0.92
|  |  |  | ECC Rating (A) | 963 | 963 | 963 | 963 | 963
|  |  |  | 50 POE Load (A) | 547 | 558 | 571 | 560 | 568
Woolooga 132 kV | F747/1 | Gympie | Traveston | NCC Rating (A) | 963 | 963 | 963 | 963 | 963 | Rural | 44 | NA
|  |  |  | 10 POE Load (A) | 323 | 323 | 340 | 325 | 330
|  |  |  | Power Factor | 0.96 | 0.94 | 0.89 | 0.95 | 0.94
|  |  |  | ECC Rating (A) | 963 | 963 | 963 | 963 | 963
|  |  |  | 50 POE Load (A) | 561 | 571 | 584 | 574 | 581
Woolooga 132 kV | F747/2 | Woolooga | Gympie | NCC Rating (A) | 983 | 983 | 983 | 983 | 983 | Rural | 44 | NA
|  |  |  | 10 POE Load (A) | 519 | 483 | 489 | 488 | 488
|  |  |  | Power Factor | 0.89 | 0.99 | 1 | 0.98 | 0.98
|  |  |  | ECC Rating (A) | 983 | 983 | 983 | 983 | 983
|  |  |  | 50 POE Load (A) | 745 | 730 | 731 | 737 | 735
Woolooga 132 kV | F748/1 | Gympie | Cooroy | NCC Rating (A) | 963 | 963 | 963 | 963 | 963 | Rural | 44 | NA
|  |  |  | 10 POE Load (A) | 456 | 395 | 395 | 403 | 404
|  |  |  | Power Factor | 0.79 | 0.94 | 0.97 | 0.93 | 0.94
|  |  |  | ECC Rating (A) | 963 | 963 | 963 | 963 | 963
|  |  |  | 50 POE Load (A) | 715 | 695 | 698 | 706 | 707
Woolooga 132 kV | F748/2 | Woolooga | Gympie | NCC Rating (A) | 983 | 983 | 983 | 983 | 983 | Rural | 44 | NA
|  |  |  | 10 POE Load (A) | 504 | 501 | 516 | 505 | 508
|  |  |  | Power Factor | 1 | 0.98 | 0.95 | 0.98 | 0.97
|  |  |  | ECC Rating (A) | 983 | 983 | 983 | 983 | 983
|  |  |  | 50 POE Load (A) | 778 | 789 | 802 | 791 | 797