## Notes
Transmission Feeders Forecasts (Energex Distribution Annual Planning Report 2023-24 to 2027-28)
This workbook provides 5 year DER forecast for sub-transmission feeders in the Energex network.
https://www.energex.com.au/about-us/company-reports,-plans-and-charters
Energex Distribution Annual Planning Report is prepared and made available solely for information purposes. While care was taken in the preparation of the information in this report, and it is provided in good faith, Energex accepts no responsibility or liability (including without limitation, liability to any person by reason of negligence or negligent mis-statement) for any loss or damage that may be incurred by any person acting in reliance on this information or assumptions drawn from it, except to the extent that liability under any applicable Queensland or Commonwealth of Australia statute cannot be excluded.
It contains assumptions regarding, among other things, economic growth and load forecasts which may or may not prove to be correct. The forecasts included in the document involve subjective judgements and analysis which are subject to significant uncertainties and contingencies, many of which are out of the control of Energex. Furthermore, forecasted data is subject to ongoing variation as new information becomes available. Energex makes no representation or warranty as to the accuracy, reliability, completeness or suitability for any particular purpose of the information in this document. All information should be independently investigated, reviewed, analysed and verified, and must not be relied upon in connection with any investment proposal or decision.
The following sections list the 110kV and 132kV feeders and their DER forecasts. Assessment of feeders is performed at midday of the forecast minimum load day.
Feeder capacities are shown for ECC and NCC. These ratings have also been adjusted for known committed projects.
Although the conductor rating is generally the limiting factor for feeder capacity, there are other significant items of plant, such as the feeder circuit breaker, that can also restrict capacity. Furthermore, other factors such as voltage constraints and load sharing between parallel underground feeders can sometimes de‑rate the capacity of the feeders due to thermal characteristic constraints. Each of these factors has been taken into account in the production of the forecast tables.
Interconnected feeders that supply multiple customers are examined in the following tables. Feeders exclusively supplying a customer owned substation or dedicated to a customer are not included in these tables.
A definition of terms is shown in the table below.
Definition of Terms Feeder Capacity and Forecast Tables
Term | Definition
NCC Rating (A) | Normal Cyclic Capacity - the total capacity with all network components and equipment intact. This is the maximum permissible peak daily loading for a given load cycle that a feeder can supply each day of its life. For overhead feeders, the NCC is the conductor rating with an assumed 1m/s wind, orthogonal to the line. For underground cables, the NCC assumes that there are sufficient temperature and current operating margins from the thermal inertia of the cable and its surroundings.
DER Forecast under System Normal (A) | Forecast load at midday of the forecast minimum load day, including the impacts of distributed energy resources (DER), under System Normal conditions.
ECC Rating (A) | Emergency Cyclic Capacity – the long term firm delivery capacity under single contingency conditions. Some underground cables are installed in close proximity to other circuits and are normally de‑rated to allow for the heat generated by the adjacent cables. ECC is the higher capacity available when any adjacent circuits have been unloaded. For overhead conductors which do not benefit from this phenomenon, the ECC is synonymous with the NCC.
DER Forecast under N-1 Contingency (A) | Forecast load at midday of the forecast minimum load day, including the impacts of distributed energy resources (DER), under N-1 contingency conditions.

## 110kV & 132kV Feeders DER Min
Connection Point | Feeder | From Substation | To Substation | Attributes | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28
Abermain | F7259/1 | Abermain | Wulkuraka Tee | NCC Rating (A) | 407 | 407 | 407 | 407 | 407
|  |  |  | DER Forecast under System Normal (A) | 69 | 94 | 110 | 131 | 152
|  |  |  | ECC Rating (A) | 407 | 407 | 407 | 407 | 407
|  |  |  | DER Forecast under N-1 Contingency (A) | 71 | 101 | 123 | 150 | 174
Abermain | F7259/2 | Wulkuraka Tee | Lockrose | NCC Rating (A) | 407 | 407 | 407 | 407 | 407
|  |  |  | DER Forecast under System Normal (A) | 81 | 106 | 122 | 143 | 164
|  |  |  | ECC Rating (A) | 407 | 407 | 407 | 407 | 407
|  |  |  | DER Forecast under N-1 Contingency (A) | 82 | 113 | 135 | 162 | 186
Abermain | F7289 | Lockrose | Gatton | NCC Rating (A) | 441 | 441 | 441 | 441 | 441
|  |  |  | DER Forecast under System Normal (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 441 | 441 | 441 | 441 | 441
|  |  |  | DER Forecast under N-1 Contingency (A) | 0 | 0 | 0 | 0 | 0
Belmont | F750 | Belmont | Beenleigh | NCC Rating (A) | 524 | 524 | 524 | 524 | 524
|  |  |  | DER Forecast under System Normal (A) | 154 | 202 | 238 | 283 | 322
|  |  |  | ECC Rating (A) | 524 | 524 | 524 | 524 | 524
|  |  |  | DER Forecast under N-1 Contingency (A) | 210 | 277 | 342 | 414 | 478
Belmont | F766 | Belmont | Cleveland | NCC Rating (A) | 1394 | 1394 | 1394 | 1394 | 1394
|  |  |  | DER Forecast under System Normal (A) | 79 | 109 | 137 | 163 | 188
|  |  |  | ECC Rating (A) | 1394 | 1394 | 1394 | 1394 | 1394
|  |  |  | DER Forecast under N-1 Contingency (A) | 158 | 218 | 274 | 326 | 377
Belmont | F767 | Belmont | Cleveland | NCC Rating (A) | 1394 | 1394 | 1394 | 1394 | 1394
|  |  |  | DER Forecast under System Normal (A) | 79 | 109 | 137 | 163 | 188
|  |  |  | ECC Rating (A) | 1394 | 1394 | 1394 | 1394 | 1394
|  |  |  | DER Forecast under N-1 Contingency (A) | 158 | 218 | 274 | 326 | 377
Blackstone | F713 | Blackstone | Raceview | NCC Rating (A) | 756 | 756 | 756 | 756 | 756
|  |  |  | DER Forecast under System Normal (A) | 13 | 26 | 39 | 53 | 67
|  |  |  | ECC Rating (A) | 756 | 756 | 756 | 756 | 756
|  |  |  | DER Forecast under N-1 Contingency (A) | 25 | 52 | 78 | 106 | 133
Blackstone | F714 | Blackstone | Raceview | NCC Rating (A) | 756 | 756 | 756 | 756 | 756
|  |  |  | DER Forecast under System Normal (A) | 13 | 26 | 39 | 53 | 67
|  |  |  | ECC Rating (A) | 756 | 756 | 756 | 756 | 756
|  |  |  | DER Forecast under N-1 Contingency (A) | 25 | 52 | 78 | 106 | 133
CBD East | F7231 | Wellington Road | Charlotte St | NCC Rating (A) | 1184 | 1184 | 1184 | 1184 | 1184
|  |  |  | DER Forecast under System Normal (A) | 242 | 254 | 274 | 306 | 310
|  |  |  | ECC Rating (A) | 1184 | 1184 | 1184 | 1184 | 1184
|  |  |  | DER Forecast under N-1 Contingency (A) | 460 | 483 | 522 | 583 | 589
CBD East | F7232 | Wellington Road | Charlotte St | NCC Rating (A) | 1184 | 1184 | 1184 | 1184 | 1184
|  |  |  | DER Forecast under System Normal (A) | 242 | 254 | 274 | 306 | 310
|  |  |  | ECC Rating (A) | 1184 | 1184 | 1184 | 1184 | 1184
|  |  |  | DER Forecast under N-1 Contingency (A) | 460 | 483 | 522 | 583 | 589
CBD East | F7287/3 | Tingalpa Tee | Wellington Road | NCC Rating (A) | 1130 | 1130 | 1130 | 1130 | 1130
|  |  |  | DER Forecast under System Normal (A) | 307 | 309 | 313 | 323 | 314
|  |  |  | ECC Rating (A) | 1130 | 1130 | 1130 | 1130 | 1130
|  |  |  | DER Forecast under N-1 Contingency (A) | 530 | 541 | 551 | 577 | 562
CBD East | F7288/3 | Tingalpa Tee | Wellington Road | NCC Rating (A) | 1130 | 1130 | 1130 | 1130 | 1130
|  |  |  | DER Forecast under System Normal (A) | 308 | 309 | 312 | 324 | 313
|  |  |  | ECC Rating (A) | 1130 | 1130 | 1130 | 1130 | 1130
|  |  |  | DER Forecast under N-1 Contingency (A) | 530 | 540 | 550 | 576 | 560
CBD East | F7230 | Wellington Road | Coorparoo | NCC Rating (A) | 1155 | 1155 | 1155 | 1155 | 1155
|  |  |  | DER Forecast under System Normal (A) | 20 | 31 | 45 | 59 | 72
|  |  |  | ECC Rating (A) | 1155 | 1155 | 1155 | 1155 | 1155
|  |  |  | DER Forecast under N-1 Contingency (A) | 26 | 55 | 84 | 113 | 141
CBD East | F7362 | Wellington Road | Coorparoo | NCC Rating (A) | 1155 | 1155 | 1155 | 1155 | 1155
|  |  |  | DER Forecast under System Normal (A) | 20 | 31 | 45 | 59 | 72
|  |  |  | ECC Rating (A) | 1155 | 1155 | 1155 | 1155 | 1155
|  |  |  | DER Forecast under N-1 Contingency (A) | 26 | 55 | 84 | 113 | 141
CBD East | F752 | Murarrie | Newstead | NCC Rating (A) | 1352 | 1352 | 1352 | 1352 | 1352
|  |  |  | DER Forecast under System Normal (A) | 102 | 89 | 81 | 84 | 70
|  |  |  | ECC Rating (A) | 1352 | 1352 | 1352 | 1352 | 1352
|  |  |  | DER Forecast under N-1 Contingency (A) | 190 | 182 | 180 | 173 | 166
CBD East | F753 | Murarrie | Newstead | NCC Rating (A) | 1352 | 1352 | 1352 | 1352 | 1352
|  |  |  | DER Forecast under System Normal (A) | 102 | 89 | 81 | 84 | 70
|  |  |  | ECC Rating (A) | 1352 | 1352 | 1352 | 1352 | 1352
|  |  |  | DER Forecast under N-1 Contingency (A) | 190 | 182 | 180 | 173 | 166
CBD East | F809 | Newstead | Victoria Park | NCC Rating (A) | 655 | 655 | 655 | 655 | 655
|  |  |  | DER Forecast under System Normal (A) | 37 | 33 | 28 | 30 | 25
|  |  |  | ECC Rating (A) | 655 | 655 | 655 | 655 | 655
|  |  |  | DER Forecast under N-1 Contingency (A) | 77 | 72 | 67 | 62 | 58
CBD East | F810 | Newstead | Victoria Park | NCC Rating (A) | 655 | 655 | 655 | 655 | 655
|  |  |  | DER Forecast under System Normal (A) | 37 | 33 | 28 | 30 | 25
|  |  |  | ECC Rating (A) | 655 | 655 | 655 | 655 | 655
|  |  |  | DER Forecast under N-1 Contingency (A) | 77 | 72 | 67 | 62 | 58
CBD East | F829 | Charlotte St | Ann St | NCC Rating (A) | 909 | 909 | 909 | 909 | 909
|  |  |  | DER Forecast under System Normal (A) | 120 | 132 | 137 | 151 | 155
|  |  |  | ECC Rating (A) | 909 | 909 | 909 | 909 | 909
|  |  |  | DER Forecast under N-1 Contingency (A) | 237 | 261 | 271 | 298 | 306
CBD East | F833 | Charlotte St | Ann St | NCC Rating (A) | 909 | 909 | 909 | 909 | 909
|  |  |  | DER Forecast under System Normal (A) | 120 | 132 | 137 | 151 | 155
|  |  |  | ECC Rating (A) | 909 | 909 | 909 | 909 | 909
|  |  |  | DER Forecast under N-1 Contingency (A) | 237 | 261 | 271 | 298 | 306
CBD East | F834 | McLachlan St | Ann St | NCC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | DER Forecast under System Normal (A) | 179 | 189 | 200 | 183 | 193
|  |  |  | ECC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | DER Forecast under N-1 Contingency (A) | 248 | 250 | 255 | 239 | 241
CBD East | F835 | McLachlan St | Victoria Park | NCC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | DER Forecast under System Normal (A) | 88 | 86 | 84 | 76 | 75
|  |  |  | ECC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | DER Forecast under N-1 Contingency (A) | 106 | 101 | 98 | 90 | 87
CBD East | F914 | Newstead | McLachlan St | NCC Rating (A) | 1232 | 1232 | 1232 | 1232 | 1232
|  |  |  | DER Forecast under System Normal (A) | 17 | 11 | 14 | 6 | 15
|  |  |  | ECC Rating (A) | 1232 | 1232 | 1232 | 1232 | 1232
|  |  |  | DER Forecast under N-1 Contingency (A) | 82 | 77 | 73 | 69 | 65
CBD East | F915 | Newstead | McLachlan St | NCC Rating (A) | 1232 | 1232 | 1232 | 1232 | 1232
|  |  |  | DER Forecast under System Normal (A) | 17 | 11 | 14 | 6 | 15
|  |  |  | ECC Rating (A) | 1232 | 1232 | 1232 | 1232 | 1232
|  |  |  | DER Forecast under N-1 Contingency (A) | 82 | 77 | 73 | 69 | 65
CBD South | F830 | West End | Charlotte St | NCC Rating (A) | 651 | 651 | 651 | 651 | 651
|  |  |  | DER Forecast under System Normal (A) | 71 | 63 | 106 | 108 | 67
|  |  |  | ECC Rating (A) | 651 | 651 | 651 | 651 | 651
|  |  |  | DER Forecast under N-1 Contingency (A) | 175 | 171 | 167 | 163 | 161
CBD South | F905 | Rocklea | West End | NCC Rating (A) | 653 | 653 | 653 | 653 | 653
|  |  |  | DER Forecast under System Normal (A) | 207 | 184 | 195 | 188 | 162
|  |  |  | ECC Rating (A) | 653 | 653 | 653 | 653 | 653
|  |  |  | DER Forecast under N-1 Contingency (A) | 241 | 216 | 231 | 232 | 206
CBD West | F7266 | Milton | Customer | NCC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | DER Forecast under System Normal (A) | 82 | 90 | 101 | 108 | 102
|  |  |  | ECC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | DER Forecast under N-1 Contingency (A) | 192 | 209 | 232 | 249 | 237
CBD West | F7267 | Milton | Makerston St | NCC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | DER Forecast under System Normal (A) | 116 | 124 | 137 | 147 | 140
|  |  |  | ECC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | DER Forecast under N-1 Contingency (A) | 214 | 212 | 234 | 251 | 239
CBD West | F7321 | Customer | Makerston St | NCC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | DER Forecast under System Normal (A) | 65 | 73 | 84 | 91 | 85
|  |  |  | ECC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | DER Forecast under N-1 Contingency (A) | 175 | 192 | 215 | 231 | 219
CBD West | F7365 | Kelvin Grove | Milton | NCC Rating (A) | 905 | 905 | 905 | 905 | 905
|  |  |  | DER Forecast under System Normal (A) | 100 | 112 | 121 | 127 | 121
|  |  |  | ECC Rating (A) | 905 | 905 | 905 | 905 | 905
|  |  |  | DER Forecast under N-1 Contingency (A) | 220 | 240 | 253 | 263 | 249
CBD West | F781 | Ashgrove West | Kelvin Grove | NCC Rating (A) | 857 | 857 | 857 | 857 | 857
|  |  |  | DER Forecast under System Normal (A) | 110 | 116 | 118 | 120 | 110
|  |  |  | ECC Rating (A) | 857 | 857 | 857 | 857 | 857
|  |  |  | DER Forecast under N-1 Contingency (A) | 230 | 245 | 251 | 256 | 238
CBD West | F782 | Ashgrove West | Milton | NCC Rating (A) | 857 | 857 | 857 | 857 | 857
|  |  |  | DER Forecast under System Normal (A) | 136 | 146 | 152 | 155 | 144
|  |  |  | ECC Rating (A) | 857 | 857 | 857 | 857 | 857
|  |  |  | DER Forecast under N-1 Contingency (A) | 243 | 250 | 261 | 271 | 255
CBD West | F807 | Makerston St | Charlotte St | NCC Rating (A) | 588 | 588 | 588 | 588 | 588
|  |  |  | DER Forecast under System Normal (A) | 28 | 26 | 47 | 48 | 31
|  |  |  | ECC Rating (A) | 588 | 588 | 588 | 588 | 588
|  |  |  | DER Forecast under N-1 Contingency (A) | 118 | 132 | 162 | 174 | 156
CBD West | F808 | Makerston St | Charlotte St | NCC Rating (A) | 588 | 588 | 588 | 588 | 588
|  |  |  | DER Forecast under System Normal (A) | 38 | 31 | 54 | 54 | 32
|  |  |  | ECC Rating (A) | 588 | 588 | 588 | 588 | 588
|  |  |  | DER Forecast under N-1 Contingency (A) | 129 | 128 | 128 | 136 | 135
Loganlea | F704 | Beenleigh | Yatala | NCC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | DER Forecast under System Normal (A) | 28 | 52 | 101 | 138 | 162
|  |  |  | ECC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | DER Forecast under N-1 Contingency (A) | 236 | 377 | 530 | 676 | 797
Loganlea | F7351 | Jimboomba | Beaudesert | NCC Rating (A) | 578 | 578 | 578 | 578 | 578
|  |  |  | DER Forecast under System Normal (A) | 17 | 39 | 61 | 84 | 108
|  |  |  | ECC Rating (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | DER Forecast under N-1 Contingency (A) | 0 | 0 | 0 | 0 | 0
Loganlea | F7354 | Loganlea | Jimboomba | NCC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | DER Forecast under System Normal (A) | 126 | 189 | 250 | 311 | 375
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | DER Forecast under N-1 Contingency (A) | 211 | 319 | 422 | 526 | 635
Loganlea | F7377 | Yatala | Coomera | NCC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | DER Forecast under System Normal (A) | 52 | 20 | 24 | 26 | 23
|  |  |  | ECC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | DER Forecast under N-1 Contingency (A) | 188 | 307 | 436 | 559 | 657
Loganlea | F787 | Loganlea | Beenleigh | NCC Rating (A) | 1047 | 1047 | 1047 | 1047 | 1047
|  |  |  | DER Forecast under System Normal (A) | 79 | 107 | 146 | 180 | 209
|  |  |  | ECC Rating (A) | 1047 | 1047 | 1047 | 1047 | 1047
|  |  |  | DER Forecast under N-1 Contingency (A) | 153 | 227 | 308 | 383 | 447
Loganlea | F788/1 | Beenleigh | Russell Island Tee | NCC Rating (A) | 184 | 184 | 184 | 184 | 184
|  |  |  | DER Forecast under System Normal (A) | 23 | 31 | 39 | 46 | 54
|  |  |  | ECC Rating (A) | 184 | 184 | 184 | 184 | 184
|  |  |  | DER Forecast under N-1 Contingency (A) | 23 | 31 | 39 | 47 | 54
Loganlea | F788/2 | Russell Island Tee | Stradbroke Island | NCC Rating (A) | 184 | 184 | 184 | 184 | 184
|  |  |  | DER Forecast under System Normal (A) | 6 | 6 | 6 | 6 | 6
|  |  |  | ECC Rating (A) | 184 | 184 | 184 | 184 | 184
|  |  |  | DER Forecast under N-1 Contingency (A) | 6 | 6 | 6 | 6 | 6
Loganlea | F788/3 | Russell Island Tee | Russell Island | NCC Rating (A) | 681 | 681 | 681 | 681 | 681
|  |  |  | DER Forecast under System Normal (A) | 23 | 30 | 38 | 45 | 52
|  |  |  | ECC Rating (A) | 681 | 681 | 681 | 681 | 681
|  |  |  | DER Forecast under N-1 Contingency (A) | 23 | 31 | 38 | 46 | 53
Loganlea | F793 | Loganlea | North Springwood | NCC Rating (A) | 640 | 640 | 640 | 640 | 640
|  |  |  | DER Forecast under System Normal (A) | 8 | 11 | 13 | 15 | 17
|  |  |  | ECC Rating (A) | 640 | 640 | 640 | 640 | 640
|  |  |  | DER Forecast under N-1 Contingency (A) | 28 | 38 | 48 | 56 | 63
Loganlea | F799 | Loganlea | North Springwood | NCC Rating (A) | 640 | 640 | 640 | 640 | 640
|  |  |  | DER Forecast under System Normal (A) | 20 | 28 | 35 | 40 | 45
|  |  |  | ECC Rating (A) | 640 | 640 | 640 | 640 | 640
|  |  |  | DER Forecast under N-1 Contingency (A) | 28 | 38 | 48 | 56 | 63
Loganlea | F820 | Loganlea | Jimboomba | NCC Rating (A) | 743 | 743 | 743 | 743 | 743
|  |  |  | DER Forecast under System Normal (A) | 86 | 130 | 172 | 214 | 258
|  |  |  | ECC Rating (A) | 743 | 743 | 743 | 743 | 743
|  |  |  | DER Forecast under N-1 Contingency (A) | 210 | 317 | 420 | 523 | 631
Loganlea | F837 | Loganlea | Beenleigh | NCC Rating (A) | 1047 | 1047 | 1047 | 1047 | 1047
|  |  |  | DER Forecast under System Normal (A) | 79 | 107 | 146 | 180 | 209
|  |  |  | ECC Rating (A) | 1047 | 1047 | 1047 | 1047 | 1047
|  |  |  | DER Forecast under N-1 Contingency (A) | 153 | 227 | 308 | 383 | 447
Loganlea | F836 | Loganlea | Browns Plains | NCC Rating (A) | 627 | 627 | 627 | 627 | 627
|  |  |  | DER Forecast under System Normal (A) | 57 | 87 | 119 | 155 | 195
|  |  |  | ECC Rating (A) | 627 | 627 | 627 | 627 | 627
|  |  |  | DER Forecast under N-1 Contingency (A) | 130 | 197 | 272 | 353 | 445
Loganlea | F843 | Loganlea | Browns Plains | NCC Rating (A) | 684 | 684 | 684 | 684 | 684
|  |  |  | DER Forecast under System Normal (A) | 73 | 111 | 153 | 198 | 249
|  |  |  | ECC Rating (A) | 684 | 684 | 684 | 684 | 684
|  |  |  | DER Forecast under N-1 Contingency (A) | 131 | 197 | 272 | 352 | 444
Loganlea | F904/1 | Beenleigh | Rocky Point Tee | NCC Rating (A) | 625 | 625 | 625 | 625 | 625
|  |  |  | DER Forecast under System Normal (A) | 151 | 151 | 152 | 152 | 153
|  |  |  | ECC Rating (A) | 625 | 625 | 625 | 625 | 625
|  |  |  | DER Forecast under N-1 Contingency (A) | 151 | 151 | 153 | 154 | 155
Loganlea | F904/2 | Rocky Point Tee | Rocky Point | NCC Rating (A) | 640 | 640 | 640 | 640 | 640
|  |  |  | DER Forecast under System Normal (A) | 150 | 150 | 150 | 150 | 150
|  |  |  | ECC Rating (A) | 640 | 640 | 640 | 640 | 640
|  |  |  | DER Forecast under N-1 Contingency (A) | 151 | 151 | 151 | 152 | 152
Loganlea | F904/3 | Rocky Point Tee | Ibis | NCC Rating (A) | 309 | 309 | 309 | 309 | 309
|  |  |  | DER Forecast under System Normal (A) | 4 | 4 | 5 | 5 | 5
|  |  |  | ECC Rating (A) | 309 | 309 | 309 | 309 | 309
|  |  |  | DER Forecast under N-1 Contingency (A) | 5 | 5 | 5 | 5 | 5
Middle Ridge | F726 | Postmans Ridge | Gatton | NCC Rating (A) | 441 | 441 | 441 | 441 | 441
|  |  |  | DER Forecast under System Normal (A) | 7 | 11 | 16 | 20 | 24
|  |  |  | ECC Rating (A) | 441 | 441 | 441 | 441 | 441
|  |  |  | DER Forecast under N-1 Contingency (A) | 83 | 114 | 135 | 161 | 186
Middle Ridge | F727 | Middle Ridge | Postmans Ridge | NCC Rating (A) | 441 | 441 | 441 | 441 | 441
|  |  |  | DER Forecast under System Normal (A) | 12 | 16 | 19 | 23 | 26
|  |  |  | ECC Rating (A) | 441 | 441 | 441 | 441 | 441
|  |  |  | DER Forecast under N-1 Contingency (A) | 48 | 64 | 75 | 89 | 101
Middle Ridge | F7348 | Middle Ridge | Postmans Ridge | NCC Rating (A) | 1000 | 1000 | 1000 | 1000 | 1000
|  |  |  | DER Forecast under System Normal (A) | 15 | 19 | 23 | 27 | 30
|  |  |  | ECC Rating (A) | 1000 | 1000 | 1000 | 1000 | 1000
|  |  |  | DER Forecast under N-1 Contingency (A) | 56 | 74 | 87 | 102 | 117
Molendinar | F7193 | Molendinar | Cades County | NCC Rating (A) | 895 | 895 | 895 | 895 | 895
|  |  |  | DER Forecast under System Normal (A) | 133 | 191 | 255 | 319 | 378
|  |  |  | ECC Rating (A) | 895 | 895 | 895 | 895 | 895
|  |  |  | DER Forecast under N-1 Contingency (A) | 239 | 343 | 459 | 574 | 681
Molendinar | F7229 | Molendinar | Robina | NCC Rating (A) | 929 | 929 | 929 | 929 | 929
|  |  |  | DER Forecast under System Normal (A) | 31 | 51 | 60 | 75 | 56
|  |  |  | ECC Rating (A) | 929 | 929 | 929 | 929 | 929
|  |  |  | DER Forecast under N-1 Contingency (A) | 59 | 93 | 111 | 139 | 115
Molendinar | F7283 | Cades County | Coomera | NCC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | DER Forecast under System Normal (A) | 235 | 326 | 429 | 530 | 621
|  |  |  | ECC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | DER Forecast under N-1 Contingency (A) | 268 | 378 | 526 | 666 | 781
Molendinar | F7297 | Molendinar | Cades County | NCC Rating (A) | 895 | 895 | 895 | 895 | 895
|  |  |  | DER Forecast under System Normal (A) | 133 | 191 | 255 | 319 | 378
|  |  |  | ECC Rating (A) | 895 | 895 | 895 | 895 | 895
|  |  |  | DER Forecast under N-1 Contingency (A) | 239 | 343 | 459 | 574 | 681
Molendinar | F798 | Molendinar | Nerang | NCC Rating (A) | 929 | 929 | 929 | 929 | 929
|  |  |  | DER Forecast under System Normal (A) | 42 | 62 | 72 | 85 | 70
|  |  |  | ECC Rating (A) | 929 | 929 | 929 | 929 | 929
|  |  |  | DER Forecast under N-1 Contingency (A) | 57 | 83 | 100 | 118 | 115
Molendinar | F907 | Molendinar | Southport | NCC Rating (A) | 777 | 777 | 777 | 777 | 777
|  |  |  | DER Forecast under System Normal (A) | 73 | 68 | 63 | 59 | 55
|  |  |  | ECC Rating (A) | 777 | 777 | 777 | 777 | 777
|  |  |  | DER Forecast under N-1 Contingency (A) | 158 | 146 | 136 | 127 | 119
Molendinar | F917 | Molendinar | Southport | NCC Rating (A) | 777 | 777 | 777 | 777 | 777
|  |  |  | DER Forecast under System Normal (A) | 85 | 79 | 73 | 68 | 64
|  |  |  | ECC Rating (A) | 777 | 777 | 777 | 777 | 777
|  |  |  | DER Forecast under N-1 Contingency (A) | 158 | 146 | 136 | 127 | 119
Molendinar | F916 | Molendinar | Surfers Paradise | NCC Rating (A) | 1037 | 1037 | 1037 | 1037 | 1037
|  |  |  | DER Forecast under System Normal (A) | 128 | 170 | 188 | 218 | 196
|  |  |  | ECC Rating (A) | 1037 | 1037 | 1037 | 1037 | 1037
|  |  |  | DER Forecast under N-1 Contingency (A) | 147 | 190 | 218 | 260 | 266
Mudgeeraba | F706 | Mudgeeraba | Nerang | NCC Rating (A) | 929 | 929 | 929 | 929 | 929
|  |  |  | DER Forecast under System Normal (A) | 31 | 51 | 63 | 82 | 71
|  |  |  | ECC Rating (A) | 929 | 929 | 929 | 929 | 929
|  |  |  | DER Forecast under N-1 Contingency (A) | 58 | 97 | 119 | 151 | 136
Mudgeeraba | F754 | Mudgeeraba | Burleigh Heads | NCC Rating (A) | 982 | 982 | 982 | 982 | 982
|  |  |  | DER Forecast under System Normal (A) | 9 | 11 | 29 | 45 | 59
|  |  |  | ECC Rating (A) | 982 | 982 | 982 | 982 | 982
|  |  |  | DER Forecast under N-1 Contingency (A) | 18 | 22 | 57 | 90 | 119
Mudgeeraba | F755 | Mudgeeraba | Burleigh Heads | NCC Rating (A) | 982 | 982 | 982 | 982 | 982
|  |  |  | DER Forecast under System Normal (A) | 9 | 11 | 29 | 45 | 59
|  |  |  | ECC Rating (A) | 982 | 982 | 982 | 982 | 982
|  |  |  | DER Forecast under N-1 Contingency (A) | 18 | 22 | 57 | 90 | 119
Mudgeeraba | F779 | Mudgeeraba | Merrimac | NCC Rating (A) | 1333 | 1333 | 1333 | 1333 | 1333
|  |  |  | DER Forecast under System Normal (A) | 70 | 84 | 87 | 99 | 73
|  |  |  | ECC Rating (A) | 1333 | 1333 | 1333 | 1333 | 1333
|  |  |  | DER Forecast under N-1 Contingency (A) | 115 | 129 | 133 | 153 | 111
Mudgeeraba | F780 | Mudgeeraba | Merrimac | NCC Rating (A) | 1333 | 1333 | 1333 | 1333 | 1333
|  |  |  | DER Forecast under System Normal (A) | 70 | 84 | 87 | 99 | 73
|  |  |  | ECC Rating (A) | 1333 | 1333 | 1333 | 1333 | 1333
|  |  |  | DER Forecast under N-1 Contingency (A) | 115 | 129 | 133 | 153 | 111
Mudgeeraba | F794 | Mudgeeraba | Robina | NCC Rating (A) | 929 | 929 | 929 | 929 | 929
|  |  |  | DER Forecast under System Normal (A) | 46 | 52 | 57 | 74 | 62
|  |  |  | ECC Rating (A) | 929 | 929 | 929 | 929 | 929
|  |  |  | DER Forecast under N-1 Contingency (A) | 62 | 78 | 103 | 138 | 125
Mudgeeraba | F826 | Broadbeach | Surfers Paradise | NCC Rating (A) | 537 | 537 | 537 | 537 | 537
|  |  |  | DER Forecast under System Normal (A) | 42 | 63 | 74 | 92 | 71
|  |  |  | ECC Rating (A) | 537 | 537 | 537 | 537 | 537
|  |  |  | DER Forecast under N-1 Contingency (A) | 82 | 121 | 141 | 175 | 136
Mudgeeraba | F827 | Broadbeach | Surfers Paradise | NCC Rating (A) | 537 | 537 | 537 | 537 | 537
|  |  |  | DER Forecast under System Normal (A) | 42 | 63 | 74 | 92 | 71
|  |  |  | ECC Rating (A) | 537 | 537 | 537 | 537 | 537
|  |  |  | DER Forecast under N-1 Contingency (A) | 82 | 121 | 141 | 175 | 136
Mudgeeraba | F838 | Mudgeeraba | Varsity Lakes | NCC Rating (A) | 1272 | 1272 | 1272 | 1272 | 1272
|  |  |  | DER Forecast under System Normal (A) | 12 | 15 | 19 | 23 | 27
|  |  |  | ECC Rating (A) | 1272 | 1272 | 1272 | 1272 | 1272
|  |  |  | DER Forecast under N-1 Contingency (A) | 14 | 22 | 32 | 41 | 51
Mudgeeraba | F839 | Mudgeeraba | Varsity Lakes | NCC Rating (A) | 1272 | 1272 | 1272 | 1272 | 1272
|  |  |  | DER Forecast under System Normal (A) | 12 | 15 | 19 | 23 | 27
|  |  |  | ECC Rating (A) | 1272 | 1272 | 1272 | 1272 | 1272
|  |  |  | DER Forecast under N-1 Contingency (A) | 14 | 22 | 32 | 41 | 51
Mudgeeraba | F918 | Merrimac | Broadbeach | NCC Rating (A) | 1214 | 1214 | 1214 | 1214 | 1214
|  |  |  | DER Forecast under System Normal (A) | 74 | 89 | 91 | 102 | 74
|  |  |  | ECC Rating (A) | 1214 | 1214 | 1214 | 1214 | 1214
|  |  |  | DER Forecast under N-1 Contingency (A) | 129 | 152 | 154 | 171 | 120
Mudgeeraba | F919 | Merrimac | Broadbeach | NCC Rating (A) | 1214 | 1214 | 1214 | 1214 | 1214
|  |  |  | DER Forecast under System Normal (A) | 75 | 89 | 91 | 102 | 74
|  |  |  | ECC Rating (A) | 1214 | 1214 | 1214 | 1214 | 1214
|  |  |  | DER Forecast under N-1 Contingency (A) | 130 | 152 | 154 | 171 | 120
Murarrie | F7270 | Murarrie | Lytton Bulk | NCC Rating (A) | 1009 | 1009 | 1009 | 1009 | 1009
|  |  |  | DER Forecast under System Normal (A) | 51 | 75 | 78 | 67 | 53
|  |  |  | ECC Rating (A) | 1009 | 1009 | 1009 | 1009 | 1009
|  |  |  | DER Forecast under N-1 Contingency (A) | 102 | 150 | 157 | 136 | 107
Murarrie | F7271 | Murarrie | Lytton Bulk | NCC Rating (A) | 1009 | 1009 | 1009 | 1009 | 1009
|  |  |  | DER Forecast under System Normal (A) | 51 | 76 | 79 | 68 | 54
|  |  |  | ECC Rating (A) | 1009 | 1009 | 1009 | 1009 | 1009
|  |  |  | DER Forecast under N-1 Contingency (A) | 102 | 150 | 157 | 136 | 107
Murarrie | F7272 | Murarrie | Doboy | NCC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | DER Forecast under System Normal (A) | 30 | 23 | 6 | 11 | 29
|  |  |  | ECC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | DER Forecast under N-1 Contingency (A) | 45 | 34 | 10 | 16 | 43
Murarrie | F7273 | Murarrie | Doboy | NCC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | DER Forecast under System Normal (A) | 30 | 23 | 6 | 11 | 29
|  |  |  | ECC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | DER Forecast under N-1 Contingency (A) | 45 | 34 | 10 | 16 | 43
Murarrie | F7274 | Murarrie | Doboy | NCC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | DER Forecast under System Normal (A) | 30 | 23 | 6 | 11 | 29
|  |  |  | ECC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | DER Forecast under N-1 Contingency (A) | 45 | 34 | 10 | 16 | 43
Palmwoods | F745/2 | Moodlu | Beerwah Tee | NCC Rating (A) | 768 | 768 | 768 | 768 | 768
|  |  |  | DER Forecast under System Normal (A) | 53 | 56 | 62 | 74 | 80
|  |  |  | ECC Rating (A) | 768 | 768 | 768 | 768 | 768
|  |  |  | DER Forecast under N-1 Contingency (A) | 87 | 105 | 127 | 146 | 174
Palmwoods | F745/3 | Moodlu | Caboolture | NCC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | DER Forecast under System Normal (A) | 126 | 191 | 257 | 323 | 389
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | DER Forecast under N-1 Contingency (A) | 252 | 381 | 512 | 642 | 778
Palmwoods | F745/4 | Palmwoods | Beerwah Tee | NCC Rating (A) | 768 | 768 | 768 | 768 | 768
|  |  |  | DER Forecast under System Normal (A) | 84 | 101 | 120 | 143 | 159
|  |  |  | ECC Rating (A) | 768 | 768 | 768 | 768 | 768
|  |  |  | DER Forecast under N-1 Contingency (A) | 149 | 195 | 243 | 287 | 337
Palmwoods | F745/5 | Beerwah Tee | Beerwah | NCC Rating (A) | 684 | 684 | 684 | 684 | 684
|  |  |  | DER Forecast under System Normal (A) | 31 | 45 | 58 | 71 | 82
|  |  |  | ECC Rating (A) | 684 | 684 | 684 | 684 | 684
|  |  |  | DER Forecast under N-1 Contingency (A) | 62 | 91 | 117 | 141 | 165
Palmwoods | F746/2 | Moodlu | Beerwah Tee | NCC Rating (A) | 768 | 768 | 768 | 768 | 768
|  |  |  | DER Forecast under System Normal (A) | 53 | 56 | 62 | 74 | 80
|  |  |  | ECC Rating (A) | 768 | 768 | 768 | 768 | 768
|  |  |  | DER Forecast under N-1 Contingency (A) | 87 | 105 | 127 | 146 | 174
Palmwoods | F746/3 | Moodlu | Caboolture | NCC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | DER Forecast under System Normal (A) | 126 | 192 | 257 | 323 | 390
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | DER Forecast under N-1 Contingency (A) | 252 | 381 | 512 | 642 | 778
Palmwoods | F746/4 | Palmwoods | Beerwah Tee | NCC Rating (A) | 768 | 768 | 768 | 768 | 768
|  |  |  | DER Forecast under System Normal (A) | 84 | 101 | 120 | 143 | 159
|  |  |  | ECC Rating (A) | 768 | 768 | 768 | 768 | 768
|  |  |  | DER Forecast under N-1 Contingency (A) | 149 | 195 | 243 | 287 | 337
Palmwoods | F746/5 | Beerwah Tee | Beerwah | NCC Rating (A) | 976 | 976 | 976 | 976 | 976
|  |  |  | DER Forecast under System Normal (A) | 31 | 45 | 58 | 71 | 82
|  |  |  | ECC Rating (A) | 976 | 976 | 976 | 976 | 976
|  |  |  | DER Forecast under N-1 Contingency (A) | 62 | 91 | 117 | 141 | 165
Palmwoods 132 kV | F7189/1 | Palmwoods | Image Flat | NCC Rating (A) | 748 | 748 | 748 | 748 | 748
|  |  |  | DER Forecast under System Normal (A) | 43 | 69 | 95 | 127 | 145
|  |  |  | ECC Rating (A) | 748 | 748 | 748 | 748 | 748
|  |  |  | DER Forecast under N-1 Contingency (A) | 82 | 129 | 176 | 230 | 262
Palmwoods 132 kV | F7189/2 | Image Flat | Cooroy | NCC Rating (A) | 703 | 703 | 703 | 703 | 703
|  |  |  | DER Forecast under System Normal (A) | 43 | 36 | 33 | 51 | 43
|  |  |  | ECC Rating (A) | 703 | 703 | 703 | 703 | 703
|  |  |  | DER Forecast under N-1 Contingency (A) | 106 | 104 | 102 | 106 | 112
Palmwoods 132 kV | F7189/3 | Image Flat | Nambour | NCC Rating (A) | 524 | 524 | 524 | 524 | 524
|  |  |  | DER Forecast under System Normal (A) | 72 | 86 | 101 | 117 | 130
|  |  |  | ECC Rating (A) | 524 | 524 | 524 | 524 | 524
|  |  |  | DER Forecast under N-1 Contingency (A) | 143 | 173 | 203 | 234 | 261
Palmwoods 132 kV | F7298 | Sunrise Hills | Noosaville | NCC Rating (A) | 684 | 684 | 684 | 684 | 684
|  |  |  | DER Forecast under System Normal (A) | 2 | 9 | 18 | 28 | 38
|  |  |  | ECC Rating (A) | 684 | 684 | 684 | 684 | 684
|  |  |  | DER Forecast under N-1 Contingency (A) | 3 | 17 | 36 | 56 | 76
Palmwoods 132 kV | F777 | Palmwoods | Mooloolaba | NCC Rating (A) | 1078 | 1078 | 1078 | 1078 | 1078
|  |  |  | DER Forecast under System Normal (A) | 34 | 69 | 101 | 137 | 173
|  |  |  | ECC Rating (A) | 1078 | 1078 | 1078 | 1078 | 1078
|  |  |  | DER Forecast under N-1 Contingency (A) | 49 | 102 | 148 | 202 | 254
Palmwoods 132 kV | F778 | Palmwoods | Mooloolaba | NCC Rating (A) | 1078 | 1078 | 1078 | 1078 | 1078
|  |  |  | DER Forecast under System Normal (A) | 34 | 69 | 101 | 137 | 173
|  |  |  | ECC Rating (A) | 1078 | 1078 | 1078 | 1078 | 1078
|  |  |  | DER Forecast under N-1 Contingency (A) | 62 | 121 | 174 | 236 | 296
Palmwoods 132 kV | F790 | Sunrise Hills | Noosaville | NCC Rating (A) | 684 | 684 | 684 | 684 | 684
|  |  |  | DER Forecast under System Normal (A) | 2 | 9 | 18 | 28 | 38
|  |  |  | ECC Rating (A) | 684 | 684 | 684 | 684 | 684
|  |  |  | DER Forecast under N-1 Contingency (A) | 3 | 17 | 36 | 56 | 76
Palmwoods 132 kV | F795/1 | Palmwoods | Image Flat | NCC Rating (A) | 748 | 748 | 748 | 748 | 748
|  |  |  | DER Forecast under System Normal (A) | 43 | 69 | 95 | 127 | 145
|  |  |  | ECC Rating (A) | 748 | 748 | 748 | 748 | 748
|  |  |  | DER Forecast under N-1 Contingency (A) | 82 | 129 | 176 | 230 | 262
Palmwoods 132 kV | F795/2 | Image Flat | Cooroy | NCC Rating (A) | 703 | 703 | 703 | 703 | 703
|  |  |  | DER Forecast under System Normal (A) | 43 | 36 | 33 | 51 | 43
|  |  |  | ECC Rating (A) | 703 | 703 | 703 | 703 | 703
|  |  |  | DER Forecast under N-1 Contingency (A) | 106 | 104 | 102 | 107 | 113
Palmwoods 132 kV | F795/3 | Image Flat | Nambour | NCC Rating (A) | 524 | 524 | 524 | 524 | 524
|  |  |  | DER Forecast under System Normal (A) | 72 | 86 | 101 | 117 | 130
|  |  |  | ECC Rating (A) | 524 | 524 | 524 | 524 | 524
|  |  |  | DER Forecast under N-1 Contingency (A) | 143 | 173 | 203 | 234 | 261
Palmwoods 132 kV | F796 | Cooroy | Sunrise Hills | NCC Rating (A) | 684 | 684 | 684 | 684 | 684
|  |  |  | DER Forecast under System Normal (A) | 55 | 92 | 129 | 166 | 204
|  |  |  | ECC Rating (A) | 684 | 684 | 684 | 684 | 684
|  |  |  | DER Forecast under N-1 Contingency (A) | 111 | 184 | 257 | 332 | 407
Palmwoods 132 kV | F797 | Cooroy | Sunrise Hills | NCC Rating (A) | 684 | 684 | 684 | 684 | 684
|  |  |  | DER Forecast under System Normal (A) | 55 | 92 | 129 | 167 | 204
|  |  |  | ECC Rating (A) | 684 | 684 | 684 | 684 | 684
|  |  |  | DER Forecast under N-1 Contingency (A) | 111 | 184 | 257 | 332 | 407
Palmwoods 132 kV | F803 | Mooloolaba | Caloundra | NCC Rating (A) | 684 | 684 | 684 | 684 | 684
|  |  |  | DER Forecast under System Normal (A) | 39 | 63 | 79 | 104 | 124
|  |  |  | ECC Rating (A) | 684 | 684 | 684 | 684 | 684
|  |  |  | DER Forecast under N-1 Contingency (A) | 76 | 131 | 172 | 230 | 281
Palmwoods 132 kV | F804 | Caloundra | Currimundi | NCC Rating (A) | 664 | 664 | 664 | 664 | 664
|  |  |  | DER Forecast under System Normal (A) | 18 | 28 | 32 | 43 | 50
|  |  |  | ECC Rating (A) | 664 | 664 | 664 | 664 | 664
|  |  |  | DER Forecast under N-1 Contingency (A) | 56 | 90 | 110 | 145 | 172
Palmwoods 132 kV | F815 | Mooloolaba | Alexandra Headlands | NCC Rating (A) | 684 | 684 | 684 | 684 | 684
|  |  |  | DER Forecast under System Normal (A) | 41 | 42 | 41 | 46 | 47
|  |  |  | ECC Rating (A) | 684 | 684 | 684 | 684 | 684
|  |  |  | DER Forecast under N-1 Contingency (A) | 73 | 97 | 116 | 144 | 169
Palmwoods 132 kV | F816 | Mooloolaba | West Maroochydore | NCC Rating (A) | 684 | 684 | 684 | 684 | 684
|  |  |  | DER Forecast under System Normal (A) | 26 | 38 | 47 | 60 | 71
|  |  |  | ECC Rating (A) | 684 | 684 | 684 | 684 | 684
|  |  |  | DER Forecast under N-1 Contingency (A) | 37 | 60 | 79 | 103 | 126
Palmwoods 132 kV | F819 | Mooloolaba | Kawana | NCC Rating (A) | 627 | 627 | 627 | 627 | 627
|  |  |  | DER Forecast under System Normal (A) | 38 | 68 | 94 | 127 | 157
|  |  |  | ECC Rating (A) | 627 | 627 | 627 | 627 | 627
|  |  |  | DER Forecast under N-1 Contingency (A) | 76 | 131 | 172 | 230 | 280
Palmwoods 132 kV | F821 | West Maroochydore | Alexandra Headlands | NCC Rating (A) | 380 | 380 | 380 | 380 | 380
|  |  |  | DER Forecast under System Normal (A) | 15 | 2 | 17 | 31 | 47
|  |  |  | ECC Rating (A) | 380 | 380 | 380 | 380 | 380
|  |  |  | DER Forecast under N-1 Contingency (A) | 19 | 57 | 92 | 130 | 168
Palmwoods 132 kV | F844 | Kawana | Birtinya | NCC Rating (A) | 664 | 664 | 664 | 664 | 664
|  |  |  | DER Forecast under System Normal (A) | 34 | 52 | 64 | 80 | 92
|  |  |  | ECC Rating (A) | 664 | 664 | 664 | 664 | 664
|  |  |  | DER Forecast under N-1 Contingency (A) | 73 | 115 | 142 | 183 | 215
Palmwoods 132 kV | F851 | Birtinya | Currimundi | NCC Rating (A) | 664 | 664 | 664 | 664 | 664
|  |  |  | DER Forecast under System Normal (A) | 51 | 63 | 69 | 81 | 88
|  |  |  | ECC Rating (A) | 664 | 664 | 664 | 664 | 664
|  |  |  | DER Forecast under N-1 Contingency (A) | 89 | 125 | 148 | 184 | 211
Palmwoods 132 kV | F845 | Palmwoods | West Maroochydore | NCC Rating (A) | 1018 | 1018 | 1018 | 1018 | 1018
|  |  |  | DER Forecast under System Normal (A) | 18 | 44 | 67 | 93 | 120
|  |  |  | ECC Rating (A) | 1018 | 1018 | 1018 | 1018 | 1018
|  |  |  | DER Forecast under N-1 Contingency (A) | 27 | 62 | 95 | 132 | 169
Palmwoods 132 kV | F846 | Palmwoods | West Maroochydore | NCC Rating (A) | 1018 | 1018 | 1018 | 1018 | 1018
|  |  |  | DER Forecast under System Normal (A) | 18 | 44 | 67 | 93 | 120
|  |  |  | ECC Rating (A) | 1018 | 1018 | 1018 | 1018 | 1018
|  |  |  | DER Forecast under N-1 Contingency (A) | 27 | 62 | 95 | 132 | 169
Rocklea | F817 | Rocklea | Archerfield | NCC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | DER Forecast under System Normal (A) | 2 | 12 | 24 | 35 | 47
|  |  |  | ECC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | DER Forecast under N-1 Contingency (A) | 4 | 24 | 48 | 71 | 94
Rocklea | F818 | Rocklea | Archerfield | NCC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | DER Forecast under System Normal (A) | 2 | 12 | 24 | 35 | 47
|  |  |  | ECC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | DER Forecast under N-1 Contingency (A) | 4 | 24 | 48 | 71 | 94
South Pine | F7337 | Nudgee | Myrtletown | NCC Rating (A) | 1106 | 1106 | 1106 | 1106 | 1106
|  |  |  | DER Forecast under System Normal (A) | 32 | 32 | 31 | 31 | 30
|  |  |  | ECC Rating (A) | 1106 | 1106 | 1106 | 1106 | 1106
|  |  |  | DER Forecast under N-1 Contingency (A) | 40 | 39 | 37 | 34 | 32
South Pine | F7338 | Nudgee | Myrtletown | NCC Rating (A) | 1106 | 1106 | 1106 | 1106 | 1106
|  |  |  | DER Forecast under System Normal (A) | 32 | 32 | 31 | 31 | 30
|  |  |  | ECC Rating (A) | 1106 | 1106 | 1106 | 1106 | 1106
|  |  |  | DER Forecast under N-1 Contingency (A) | 40 | 39 | 37 | 34 | 32
South Pine | F7341 | South Pine | Nudgee | NCC Rating (A) | 1553 | 1553 | 1553 | 1553 | 1553
|  |  |  | DER Forecast under System Normal (A) | 131 | 126 | 112 | 104 | 95
|  |  |  | ECC Rating (A) | 1553 | 1553 | 1553 | 1553 | 1553
|  |  |  | DER Forecast under N-1 Contingency (A) | 252 | 243 | 214 | 195 | 178
South Pine | F7342 | South Pine | Nudgee | NCC Rating (A) | 1553 | 1553 | 1553 | 1553 | 1553
|  |  |  | DER Forecast under System Normal (A) | 131 | 127 | 112 | 104 | 95
|  |  |  | ECC Rating (A) | 1553 | 1553 | 1553 | 1553 | 1553
|  |  |  | DER Forecast under N-1 Contingency (A) | 252 | 243 | 214 | 195 | 178
South Pine | F7344 | South Pine | Griffin | NCC Rating (A) | 1220 | 1220 | 1220 | 1220 | 1220
|  |  |  | DER Forecast under System Normal (A) | 49 | 75 | 100 | 119 | 140
|  |  |  | ECC Rating (A) | 1220 | 1220 | 1220 | 1220 | 1220
|  |  |  | DER Forecast under N-1 Contingency (A) | 94 | 143 | 192 | 229 | 269
South Pine | F7345 | South Pine | Griffin | NCC Rating (A) | 1220 | 1220 | 1220 | 1220 | 1220
|  |  |  | DER Forecast under System Normal (A) | 49 | 75 | 100 | 119 | 140
|  |  |  | ECC Rating (A) | 1220 | 1220 | 1220 | 1220 | 1220
|  |  |  | DER Forecast under N-1 Contingency (A) | 94 | 143 | 192 | 229 | 269
South Pine | F7358 | Griffin | Hays Inlet | NCC Rating (A) | 1373 | 1373 | 1373 | 1373 | 1373
|  |  |  | DER Forecast under System Normal (A) | 66 | 86 | 113 | 118 | 132
|  |  |  | ECC Rating (A) | 1373 | 1373 | 1373 | 1373 | 1373
|  |  |  | DER Forecast under N-1 Contingency (A) | 93 | 126 | 161 | 180 | 202
South Pine | F737/1 | South Pine | Bunyaville | NCC Rating (A) | 918 | 918 | 918 | 918 | 918
|  |  |  | DER Forecast under System Normal (A) | 43 | 30 | 33 | 47 | 65
|  |  |  | ECC Rating (A) | 918 | 918 | 918 | 918 | 918
|  |  |  | DER Forecast under N-1 Contingency (A) | 69 | 33 | 42 | 79 | 120
South Pine | F737/2 | Bunyaville | Stafford | NCC Rating (A) | 1264 | 1264 | 1264 | 1264 | 1264
|  |  |  | DER Forecast under System Normal (A) | 42 | 29 | 32 | 46 | 64
|  |  |  | ECC Rating (A) | 1264 | 1264 | 1264 | 1264 | 1264
|  |  |  | DER Forecast under N-1 Contingency (A) | 68 | 31 | 41 | 78 | 119
South Pine | F738/1 | South Pine | Bunyaville | NCC Rating (A) | 918 | 918 | 918 | 918 | 918
|  |  |  | DER Forecast under System Normal (A) | 43 | 30 | 33 | 47 | 65
|  |  |  | ECC Rating (A) | 918 | 918 | 918 | 918 | 918
|  |  |  | DER Forecast under N-1 Contingency (A) | 69 | 33 | 42 | 79 | 120
South Pine | F738/2 | Bunyaville B | Stafford | NCC Rating (A) | 1264 | 1264 | 1264 | 1264 | 1264
|  |  |  | DER Forecast under System Normal (A) | 42 | 29 | 32 | 46 | 64
|  |  |  | ECC Rating (A) | 1264 | 1264 | 1264 | 1264 | 1264
|  |  |  | DER Forecast under N-1 Contingency (A) | 68 | 31 | 41 | 78 | 119
South Pine | F739 | South Pine | Bald Hills | NCC Rating (A) | 1600 | 1600 | 1600 | 1600 | 1600
|  |  |  | DER Forecast under System Normal (A) | 32 | 43 | 54 | 63 | 71
|  |  |  | ECC Rating (A) | 1600 | 1600 | 1600 | 1600 | 1600
|  |  |  | DER Forecast under N-1 Contingency (A) | 66 | 89 | 110 | 128 | 144
South Pine | F740 | South Pine | Sandgate | NCC Rating (A) | 1600 | 1600 | 1600 | 1600 | 1600
|  |  |  | DER Forecast under System Normal (A) | 34 | 46 | 56 | 65 | 73
|  |  |  | ECC Rating (A) | 1600 | 1600 | 1600 | 1600 | 1600
|  |  |  | DER Forecast under N-1 Contingency (A) | 72 | 95 | 116 | 134 | 151
South Pine | F741 | South Pine | Hays Inlet | NCC Rating (A) | 635 | 635 | 635 | 635 | 635
|  |  |  | DER Forecast under System Normal (A) | 63 | 87 | 112 | 126 | 142
|  |  |  | ECC Rating (A) | 635 | 635 | 635 | 635 | 635
|  |  |  | DER Forecast under N-1 Contingency (A) | 94 | 131 | 169 | 190 | 214
South Pine | F742 | South Pine | Hays Inlet | NCC Rating (A) | 635 | 635 | 635 | 635 | 635
|  |  |  | DER Forecast under System Normal (A) | 62 | 87 | 111 | 126 | 142
|  |  |  | ECC Rating (A) | 635 | 635 | 635 | 635 | 635
|  |  |  | DER Forecast under N-1 Contingency (A) | 94 | 131 | 169 | 189 | 214
South Pine | F7299 | South Pine | Brendale | NCC Rating (A) | 949 | 949 | 949 | 949 | 949
|  |  |  | DER Forecast under System Normal (A) | 53 | 67 | 80 | 96 | 107
|  |  |  | ECC Rating (A) | 949 | 949 | 949 | 949 | 949
|  |  |  | DER Forecast under N-1 Contingency (A) | 80 | 100 | 120 | 144 | 160
South Pine | F743 | South Pine | Brendale | NCC Rating (A) | 594 | 594 | 594 | 594 | 594
|  |  |  | DER Forecast under System Normal (A) | 53 | 67 | 80 | 96 | 107
|  |  |  | ECC Rating (A) | 594 | 594 | 594 | 594 | 594
|  |  |  | DER Forecast under N-1 Contingency (A) | 80 | 100 | 120 | 144 | 160
South Pine | F744 | South Pine | Brendale | NCC Rating (A) | 594 | 594 | 594 | 594 | 594
|  |  |  | DER Forecast under System Normal (A) | 53 | 67 | 80 | 96 | 107
|  |  |  | ECC Rating (A) | 594 | 594 | 594 | 594 | 594
|  |  |  | DER Forecast under N-1 Contingency (A) | 80 | 100 | 120 | 144 | 160
South Pine | F745/1 | South Pine | Moodlu | NCC Rating (A) | 768 | 768 | 768 | 768 | 768
|  |  |  | DER Forecast under System Normal (A) | 76 | 138 | 198 | 259 | 321
|  |  |  | ECC Rating (A) | 768 | 768 | 768 | 768 | 768
|  |  |  | DER Forecast under N-1 Contingency (A) | 168 | 279 | 388 | 499 | 612
South Pine | F746/1 | South Pine | Moodlu | NCC Rating (A) | 768 | 768 | 768 | 768 | 768
|  |  |  | DER Forecast under System Normal (A) | 76 | 138 | 198 | 260 | 321
|  |  |  | ECC Rating (A) | 768 | 768 | 768 | 768 | 768
|  |  |  | DER Forecast under N-1 Contingency (A) | 168 | 279 | 388 | 499 | 612
South Pine | F831 | Bald Hills | Sandgate | NCC Rating (A) | 1600 | 1600 | 1600 | 1600 | 1600
|  |  |  | DER Forecast under System Normal (A) | 38 | 50 | 60 | 69 | 77
|  |  |  | ECC Rating (A) | 1600 | 1600 | 1600 | 1600 | 1600
|  |  |  | DER Forecast under N-1 Contingency (A) | 72 | 95 | 116 | 134 | 151
South Pine | F912 | Nudgee | Meeandah | NCC Rating (A) | 455 | 455 | 455 | 455 | 455
|  |  |  | DER Forecast under System Normal (A) | 53 | 59 | 58 | 56 | 56
|  |  |  | ECC Rating (A) | 455 | 455 | 455 | 455 | 455
|  |  |  | DER Forecast under N-1 Contingency (A) | 70 | 88 | 84 | 81 | 78
South Pine | F913 | Nudgee | Meeandah | NCC Rating (A) | 455 | 455 | 455 | 455 | 455
|  |  |  | DER Forecast under System Normal (A) | 53 | 59 | 58 | 57 | 56
|  |  |  | ECC Rating (A) | 455 | 455 | 455 | 455 | 455
|  |  |  | DER Forecast under N-1 Contingency (A) | 71 | 88 | 84 | 81 | 78
Woolooga 132 kV | F7186 | Cooran | Cooroy | NCC Rating (A) | 734 | 734 | 734 | 734 | 734
|  |  |  | DER Forecast under System Normal (A) | 78 | 99 | 119 | 144 | 168
|  |  |  | ECC Rating (A) | 734 | 734 | 734 | 734 | 734
|  |  |  | DER Forecast under N-1 Contingency (A) | 139 | 168 | 197 | 229 | 264
Woolooga 132 kV | F7343 | Traveston | Cooran | NCC Rating (A) | 734 | 734 | 734 | 734 | 734
|  |  |  | DER Forecast under System Normal (A) | 91 | 115 | 139 | 166 | 192
|  |  |  | ECC Rating (A) | 734 | 734 | 734 | 734 | 734
|  |  |  | DER Forecast under N-1 Contingency (A) | 153 | 185 | 217 | 252 | 289
Woolooga 132 kV | F747/1 | Gympie | Traveston | NCC Rating (A) | 734 | 734 | 734 | 734 | 734
|  |  |  | DER Forecast under System Normal (A) | 85 | 109 | 133 | 160 | 187
|  |  |  | ECC Rating (A) | 734 | 734 | 734 | 734 | 734
|  |  |  | DER Forecast under N-1 Contingency (A) | 147 | 180 | 212 | 246 | 283
Woolooga 132 kV | F747/2 | Woolooga | Gympie | NCC Rating (A) | 763 | 763 | 763 | 763 | 763
|  |  |  | DER Forecast under System Normal (A) | 91 | 127 | 164 | 201 | 240
|  |  |  | ECC Rating (A) | 763 | 763 | 763 | 763 | 763
|  |  |  | DER Forecast under N-1 Contingency (A) | 155 | 199 | 244 | 290 | 345
Woolooga 132 kV | F748/1 | Gympie | Cooroy | NCC Rating (A) | 734 | 734 | 734 | 734 | 734
|  |  |  | DER Forecast under System Normal (A) | 103 | 132 | 162 | 194 | 227
|  |  |  | ECC Rating (A) | 734 | 734 | 734 | 734 | 734
|  |  |  | DER Forecast under N-1 Contingency (A) | 178 | 217 | 256 | 298 | 344
Woolooga 132 kV | F748/2 | Woolooga | Gympie | NCC Rating (A) | 763 | 763 | 763 | 763 | 763
|  |  |  | DER Forecast under System Normal (A) | 106 | 144 | 183 | 223 | 265
|  |  |  | ECC Rating (A) | 763 | 763 | 763 | 763 | 763
|  |  |  | DER Forecast under N-1 Contingency (A) | 180 | 227 | 276 | 325 | 379