## Limitations Not Addressed
Limitations Not Addressed
The following limitations currently do not have or require a planned solution.
Energex has contingency plans in place and is actively monitoring load developments in the supply area.
Location:
Maps of Energex’s network showing the location of all Energex’s bulk supply and zone substations are presented via the following link:
https://www.energex.com.au/daprmap2023
Supply Point | Class | Limitation | Comments
Beenleigh BS | Cornubia ZS | N-1 limitation for the loss of a 33/11 kV 25MVA transformer | Monitoring load development.
Palmwoods 132kV CP | Mooloolaba ZS | N-1 limitation for the loss of a 132/11 kV 30MVA transformer | Monitoring load development.
Brendale BS | Whiteside ZS | N-1 limitation for the loss of a 33/11 kV 15MVA transformer | Monitoring load development.
Caboolture BS | Morayfield ZS | N-1 limitation for the loss of a 33/11 kV 25MVA transformer | Planning studies currently in progress, mitigation works likely to be beyond 2028.
Goodna BS | Cooneana ZS | N-1 limitation for the loss of a 33/11 kV 25MVA transformer | Planning studies currently in progress, mitigation works likely to be beyond 2028.
Loganlea 110kV CP | Jimboomba BS | N-1 limitation for the loss of a 110/33 kV 80MVA transformer | Planning studies currently in progress, mitigation works likely to be beyond 2028.
Cleveland BS | 33kV Feeder | Feeder 413 overloads when 372 is out of service | Monitoring load development.
Victoria Park BS | 33kV Feeder | Feeder 628 overloads when 649 is out of service | Monitoring load development.
Victoria Park BS | 33 kV Feeder | Feeder 649 overloads when 628 is out of service | Monitoring load development.
Gympie BS | 33 kV Feeder | Feeder 341 exceeds NCC rating | Monitoring load development.
Gympie BS | 33kV Feeder | Voltage constraint at Tin Can Bay and Customer Substations when feeder 429 is out of service. | Operational strategy to deploy generators under contingency.
Burleigh BS | 33kV Feeder | Feeder 3751 and 3755 exceeds NCC rating | Monitoring load development.
Caboolture BS | 33 kV Feeder | Voltage constraint at Toorbul Point Substation when feeder 350 or 412 are out of service. | Operational strategy to remotely reconfigure network under contingency.
Sunrise Hills BS | 33 kV Feeder | Feeder 3100 exceeds NCC rating | Operational strategy to deploy generators.
Belmont BS | 33 kV Feeder | Feeder 647 overloads when 694 is out of service | Monitoring load development.
Hays Inlet BS | 33 kV Feeder | Feeder 3251 overloads when 448 is out of service | Planning studies currently in progress, mitigation works likely to be beyond 2028.
Browns Plains BS | 33 kV Feeder | Feeder 406A overloads when 453 is out of service | Planning studies currently in progress, mitigation works likely to be beyond 2028.
Caboolture BS | 33 kV Feeder | Feeder 412 overloads when 350 is out of service | Monitoring load development.
Beaudesert BS | 33 kV Feeder | Feeder 469 overloads when 468 is out of service | Monitoring load development.
Belmont ZS | 11kV Feeder | BBSRDL12 exceeds TMU by 0.40MW in summer 2023/24 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Archerfield | 11kV Feeder | AFD19A exceeds TMU by 0.1MW in summer 2024/25 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Alexandra Headland | 11kV Feeder | AHD17 exceeds TMU by 0.2MW in summer 2024/25 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Broadbeach | 11kV Feeder | BBH13B exceeds TMU by 0.4MW in summer 2024/25 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Broadbeach | 11kV Feeder | BBH16A exceeds TMU by 0.1MW in summer 2023/24 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Beaudesert | 11kV Feeder | BDT5A exceeds TMU by 0.3MW in summer 2024/25 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Burpengary | 11kV Feeder | BGY5A exceeds TMU by 0.1MW in summer 2023/24 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Burleigh Heads | 11kV Feeder | BHD20A exceeds TMU by 0.1MW in summer 2023/24 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Burleigh Heads | 11kV Feeder | BHD35A exceeds TMU by 0.5MW in Winter 2024 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Beenleigh | 11kV Feeder | BLH12A exceeds TMU by 0.9MW in Summer 2023/24 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Bethania | 11kV Feeder | BTA3A exceeds TMU by 0.3MW in Summer 2023/24 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Birtinya | 11kV Feeder | BTY7A exceeds TMU by 0.3MW in Summer 2024/25 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Booval | 11kV Feeder | BVL5A exceeds TMU by 0.3MW in Summer 2023/24 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Camp Hill | 11kV Feeder | CHL3 exceeds TMU by 0.2MW in Summer 2023/24 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Coomera | 11kV Feeder | CMA11A exceeds TMU by 0.2MW in Summer 2023/24 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Charlotte St | 11kV Feeder | CSTQEA29 exceeds TMU by 0.2MW in Summer 2024/25 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Charlotte St | 11kV Feeder | CSTTCD3 exceeds TMU by 0.6MW in Summer 2023/24 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Darra | 11kV Feeder | DRA12A exceeds TMU by 0.8MW in Summer 2023/24 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Darra | 11kV Feeder | DRA13A exceeds TMU by 2.8MW in Summer 2023/24 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Fisherman Is BS | 11kV Feeder | FBSFIS13 exceeds TMU by 0.2MW in Winter 2025 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Geebung | 11kV Feeder | GBG21A exceeds TMU by 0.1MW in Summer 2024/25 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Goodna | 11kV Feeder | GNA7A exceeds TMU by 0.1MW in Summer 2023/24 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Hemmant | 11kV Feeder | HMT7A exceeds TMU by 0.9MW in Summer 2024/25 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Ipswich South | 11kV Feeder | IPS2B exceeds TMU by 0.2MW in Summer 2024/25 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Kingston | 11kV Feeder | KSN7 exceeds TMU by 0.6MW in Summer 2023/24 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Kingston | 11kV Feeder | KSN8 exceeds TMU by 0.6MW in Summer 2023/24 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Lawnton | 11kV Feeder | LTN2 exceeds TMU by 0.2MW in Summer 2023/24 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Lawnton | 11kV Feeder | LTN3 exceeds TMU by 0.2MW in Summer 2023/24 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Lawnton | 11kV Feeder | LTN9 exceeds TMU by 0.1MW in Summer 2023/24 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
McLachlan St | 11kV Feeder | FPTMLS22 exceeds TMU by 0.6MW in Summer 2024/25 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
McLachlan St | 11kV Feeder | MLS11A exceeds TMU by 0.1MW in Summer 2023/24 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
McLachlan St | 11kV Feeder | MLS26B exceeds TMU by 0.2MW in Summer 2023/24 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
McLachlan St | 11kV Feeder | MLS2A exceeds TMU by 0.4MW in Summer 2023/24 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Milton | 11kV Feeder | MLT42A exceeds TMU by 0.4MW in Summer 2023/24 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Murarrie | 11kV Feeder | MRE4A exceeds TMU by 0.1MW in Summer 2023/24 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Makerston St | 11kV Feeder | MSTSCB28 exceeds TMU by 0.1MW in Winter 2025 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Nambour | 11kV Feeder | NBR7A exceeds TMU by 0.1MW in Summer 2023/24 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Nudgee | 11kV Feeder | GCNNGE15 exceeds TMU by 0.1MW in Summer 2023/24 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Narangba | 11kV Feeder | NRA15A exceeds TMU by 0.4MW in Summer 2023/24 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Newstead | 11kV Feeder | NSD2B exceeds TMU by 0.7MW in Summer 2023/24 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Oxley | 11kV Feeder | OXL11A exceeds TMU by 0.2MW in Summer 2024/25 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Pimpama East | 11kV Feeder | PPE17A exceeds TMU by 0.4MW in Summer 2024/25 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Pimpama East | 11kV Feeder | PPE5A exceeds TMU by 0.6MW in Summer 2023/24 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Redland Bay | 11kV Feeder | RLB15A exceeds TMU by 0.1MW in Summer 2024/25 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Redbank Plains | 11kV Feeder | RPN5A exceeds TMU by 0.8MW in Summer 2023/24 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Scarborough | 11kV Feeder | SBH9 exceeds TMU by 0.2MW in Summer 2023/24 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Sunnybank | 11kV Feeder | SBK21 exceeds TMU by 0.3MW in Summer 2024/25 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Springfield Central | 11kV Feeder | PDBSFC12 exceeds TMU by 0.1MW in Summer 2024/25 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Strathpine | 11kV Feeder | SPEWSP29 exceeds TMU by 1.3MW in Summer 2023/24 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Springfield | 11kV Feeder | SPF15A exceeds TMU by 0.5MW in Summer 2023/24 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Southport | 11kV Feeder | SPO69A exceeds TMU by 0.1MW in Summer 2023/24 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Toowong | 11kV Feeder | TWG19 exceeds TMU by 0.1MW in Summer 2023/24 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Victoria Park | 11kV Feeder | VPK35A exceeds TMU by 0.2MW in Summer 2023/24 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Victoria Park | 11kV Feeder | VPK9A exceeds TMU by 0.1MW in Summer 2024/25 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
West End | 11kV Feeder | WED16A exceeds TMU by 0.1MW in Summer 2023/24 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
West Maroochydore | 11kV Feeder | WMD11A exceeds TMU by 0.4MW in Summer 2024/25 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Wellington Rd | 11kV Feeder | WRD19A exceeds TMU by 0.2MW in Summer 2023/24 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Woodridge | 11kV Feeder | WRG5A exceeds TMU by 0.8MW in Winter 2024 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Yamanto | 11kV Feeder | YMT6A exceeds TMU by 0.6MW in Summer 2024/25 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Yatala | 11kV Feeder | YTA35A exceeds TMU by 0.7MW in Summer 2023/24 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.
Yatala | 11kV Feeder | YTA43A exceeds TMU by 0.6MW in Summer 2023/24 | Operational decision to deploy generators or load transfers. Load growth and block loads being monitored.