## Notes
Sub-Transmission Feeders Forecasts (Energex Distribution Annual Planning Report 2023-24 to 2027-28)
This workbook provides 5 year forecast capacity and loading information for sub-transmission feeders in the Energex network.
Energex Distribution Annual Planning Report is prepared and made available solely for information purposes. While care was taken in the preparation of the information in this report, and it is provided in good faith, Energex accepts no responsibility or liability (including without limitation, liability to any person by reason of negligence or negligent mis-statement) for any loss or damage that may be incurred by any person acting in reliance on this information or assumptions drawn from it, except to the extent that liability under any applicable Queensland or Commonwealth of Australia statute cannot be excluded.
It contains assumptions regarding, among other things, economic growth and load forecasts which may or may not prove to be correct. The forecasts included in the document involve subjective judgements and analysis which are subject to significant uncertainties and contingencies, many of which are out of the control of Energex. Furthermore, forecasted data is subject to ongoing variation as new information becomes available. Energex makes no representation or warranty as to the accuracy, reliability, completeness or suitability for any particular purpose of the information in this document. All information should be independently investigated, reviewed, analysed and verified, and must not be relied upon in connection with any investment proposal or decision.
The following sections list the 33kV feeders, their forecast loads, power factor, customer category and available load transfers. The feeder loads are calculated from load flow results using forecast substation demands. For the transmission and sub-transmission feeders, load flow studies are conducted for system normal and single contingency situations.
The forecast and capacity accounts for committed projects, the project cut-off date for the winter season is 1 June of each year, and for the summer season is 1 December of each year. For example, 2024 winter forecast includes all committed projects with a proposed commissioning date up to 1 June 2024, and the 2023/24 summer forecast includes all committed projects with a proposed commissioning date up to 1 December 2023. The committed status of projects used in the forecast are taken as of 1 May 2023.
Assessment of 33kV feeders is performed under four possible risk periods: winter day, winter night, summer day and summer night. The worst case (highest) load between day and night has been represented in the table.
Peak, reconciled, compensated load forecasts have been used in the 33kV feeder analyses, with 50 PoE forecast load used for single contingency studies, and 10 PoE forecast load used for system normal studies.
Feeder capacities are shown for ECC and NCC. These ratings have also been adjusted for known committed projects. All load transfers associated with contingent condition include acceptable feeder voltage profiles.
Although the conductor rating is generally the limiting factor for feeder capacity, there are other significant items of plant, such as the feeder circuit breaker, that can also restrict capacity. Furthermore, other factors such as voltage constraints and load sharing between parallel underground feeders can sometimes de‑rate the capacity of the feeders due to thermal characteristic constraints. Each of these factors has been taken into account in the production of the forecast tables.
Interconnected feeders that supply multiple customers are examined in the following tables. Feeders exclusively supplying a customer owned substation or dedicated to a customer are not included in these tables.
A definition of terms is shown in the table below.
Definition of Terms Feeder Capacity and Forecast Tables
Term | Definition
NCC Rating (A) | Normal Cyclic Capacity - the total capacity with all network components and equipment intact. This is the maximum permissible peak daily loading for a given load cycle that a feeder can supply each day of its life. For overhead feeders, the NCC is the conductor rating with an assumed 1m/s wind, orthogonal to the line. For underground cables, the NCC assumes that there are sufficient temperature and current operating margins from the thermal inertia of the cable and its surroundings.
10 PoE Load (A) | Peak load forecast with 10% probability of being exceeded (one in every 10 years will be exceeded). Based on normal expected growth rates and weather corrected starting loads.
Power Factor | Lowest power factor along the feeder at 10 PoE Peak Load. Where the Power Factor is either 0 the feeder is a normally open feeder that does not have load under System Normal conditions.
ECC Rating (A) | Emergency Cyclic Capacity – the long term firm delivery capacity under single contingency conditions. Some underground cables are installed in close proximity to other circuits and are normally de‑rated to allow for the heat generated by the adjacent cables. ECC is the higher capacity available when any adjacent circuits have been unloaded. For overhead conductors which do not benefit from this phenomenon, the ECC is synonymous with the NCC.
50 PoE Load (A) | Peak load forecast with 50% probability of being exceeded (one in every two years will be exceeded). Based on normal expected growth rates & weather corrected starting loads. This is the worst case (highest) load forecast beween summer day and summer night.
Security Standard | For security standard application, the general type of customer a sub-transmission, or transmission feeder is supplying.
Transfers | This is the total amount of load transfers that are available following the worst case network contingency. This includes automatic transfers that are controlled automatically through SCADA and are generally implemented within a minute, load transfers that can be implemented through screen switching by a network controller, manual transfers that are deployed via manually controlled switchgear locally by field staff, and mobile generation which can be deployed by field staff by moving generation to specific sites. It should be noted under the Safety Net in the Distribution Authority, it is generally assumed that 4MVA (70A) of generation is available for Urban feeders to meet this criteria and 10MVA (170A) is available for Rural feeders. These values have been used as a default in the forecast tables where these are sufficient to reduce the 50PoE load below the ECC rating. Where the load is still above the ECC rating, specific load transfers have been calculated for the feeder to determine whether the Safety Net criteria is met.
Hours PA > 95% Peak Load | The forecast number of hours per annum where the load exceeded 95% of the peak 50 PoE demand. This information is not readily available for every feeder without significant analysis being undertaken. As such, this has only been provided where a feeder does not meet the Safety Net criteria or is otherwise in the Limitations and Proposed Solutions table.

## 33kV Feeders - Summer
Bulk Supply Name | Feeder | From Substation | To Substation | Attributes | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | Security Standard | Transfers | Hours above 95%
Abermain Bulk | 357-1 | Abermain BS | 357 Tee1 | NCC Rating (A) | 505 | 505 | 505 | 505 | 505 | Urban | 70
|  |  |  | 10 POE Load (A) | 154 | 151 | 149 | 147 | 146
|  |  |  | Power Factor | 0.98621 | 0.98675 | 0.98714 | 0.98753 | 0.98766
|  |  |  | ECC Rating (A) | 505 | 505 | 505 | 505 | 505
|  |  |  | 50 POE Load (A) | 349 | 357 | 357 | 353 | 355
Abermain Bulk | 357-2 | 357 Tee1 | Redbank | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 3.128e-06 | 3.1282e-06 | 3.1282e-06 | 3.1281e-06 | 3.128e-06
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 310 | 327 | 329 | 327 | 331
Abermain Bulk | 357-3 | 357 Tee1 | Moggill | NCC Rating (A) | 710 | 710 | 710 | 710 | 710 | Urban | 70
|  |  |  | 10 POE Load (A) | 155 | 152 | 150 | 147 | 147
|  |  |  | Power Factor | 0.98805 | 0.98832 | 0.98852 | 0.98872 | 0.98879
|  |  |  | ECC Rating (A) | 710 | 710 | 710 | 710 | 710
|  |  |  | 50 POE Load (A) | 338 | 330 | 326 | 320 | 318
Abermain Bulk | 358-1 | Abermain BS | Ebbw Vale | NCC Rating (A) | 473 | 473 | 473 | 473 | 473 | Rural | 170
|  |  |  | 10 POE Load (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 7.0411e-06 | 7.0417e-06 | 7.0414e-06 | 7.041e-06 | 7.0412e-06
|  |  |  | ECC Rating (A) | 473 | 473 | 473 | 473 | 473
|  |  |  | 50 POE Load (A) | 1 | 1 | 1 | 1 | 1
Abermain Bulk | 364-1 | Marburg | Rosewood | NCC Rating (A) | 155 | 155 | 155 | 155 | 155 | Rural | 170
|  |  |  | 10 POE Load (A) | 74 | 75 | 75 | 76 | 75
|  |  |  | Power Factor | 0.99691 | 0.99679 | 0.99686 | 0.99679 | 0.99471
|  |  |  | ECC Rating (A) | 155 | 155 | 155 | 155 | 155
|  |  |  | 50 POE Load (A) | 141 | 148 | 153 | 160 | 168
Abermain Bulk | 365-1 | Abermain BS | 365 Tee1 | NCC Rating (A) | 746 | 746 | 746 | 746 | 746 | Rural | 170
|  |  |  | 10 POE Load (A) | 342 | 344 | 347 | 351 | 350
|  |  |  | Power Factor | 0.93595 | 0.9355 | 0.93508 | 0.93451 | 0.94523
|  |  |  | ECC Rating (A) | 746 | 746 | 746 | 746 | 746
|  |  |  | 50 POE Load (A) | 641 | 646 | 652 | 658 | 661
Abermain Bulk | 365-2 | 365 Tee1 | 366 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 2.0193e-05 | 2.0191e-05 | 2.0191e-05 | 2.019e-05 | 2.019e-05
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Abermain Bulk | 365-3 | 365 Tee1 | Karrabin | NCC Rating (A) | 804 | 804 | 804 | 804 | 804 | Rural | 170
|  |  |  | 10 POE Load (A) | 342 | 345 | 348 | 351 | 351
|  |  |  | Power Factor | 0.95311 | 0.95286 | 0.95265 | 0.95234 | 0.96182
|  |  |  | ECC Rating (A) | 804 | 804 | 804 | 804 | 804
|  |  |  | 50 POE Load (A) | 642 | 646 | 653 | 658 | 662
Abermain Bulk | 366-1 | Abermain BS | 366 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 373 | 376 | 379 | 383 | 383
|  |  |  | Power Factor | 0.93608 | 0.93563 | 0.93521 | 0.93464 | 0.94535
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 644 | 649 | 655 | 661 | 664
Abermain Bulk | 366-2 | 366 Tee1 | Karrabin | NCC Rating (A) | 758 | 758 | 758 | 758 | 758 | Rural | 170
|  |  |  | 10 POE Load (A) | 373 | 376 | 379 | 383 | 383
|  |  |  | Power Factor | 0.95374 | 0.95349 | 0.95327 | 0.95296 | 0.96238
|  |  |  | ECC Rating (A) | 758 | 758 | 758 | 758 | 758
|  |  |  | 50 POE Load (A) | 645 | 649 | 655 | 661 | 665
Abermain Bulk | 366-3 | 366 Tee1 | 365 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 9.0312e-06 | 9.0317e-06 | 9.032e-06 | 9.0321e-06 | 9.0316e-06
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Abermain Bulk | 367-1 | Abermain BS | Mt Crosby West | NCC Rating (A) | 530 | 530 | 530 | 530 | 530 | Rural | 170
|  |  |  | 10 POE Load (A) | 295 | 175 | 294 | 290 | 289
|  |  |  | Power Factor | 0.94394 | 0.95758 | 0.94401 | 0.94408 | 0.9441
|  |  |  | ECC Rating (A) | 530 | 530 | 530 | 530 | 530
|  |  |  | 50 POE Load (A) | 482 | 256 | 474 | 470 | 468
Abermain Bulk | 368-1 | Abermain BS | Mt Crosby | NCC Rating (A) | 529 | 529 | 529 | 529 | 529 | HighSec | 0
|  |  |  | 10 POE Load (A) | 230 | 230 | 228 | 225 | 225
|  |  |  | Power Factor | 0.93718 | 0.96017 | 0.9337 | 0.93371 | 0.93371
|  |  |  | ECC Rating (A) | 529 | 529 | 529 | 529 | 529
|  |  |  | 50 POE Load (A) | 487 | 479 | 479 | 475 | 473
Abermain Bulk | 369-1 | Abermain BS | Nth Ipswich | NCC Rating (A) | 499 | 499 | 499 | 499 | 499 | Urban | 70
|  |  |  | 10 POE Load (A) | 208 | 206 | 206 | 203 | 202
|  |  |  | Power Factor | 0.96806 | 0.96827 | 0.96837 | 0.96868 | 0.96879
|  |  |  | ECC Rating (A) | 499 | 499 | 499 | 499 | 499
|  |  |  | 50 POE Load (A) | 409 | 405 | 403 | 397 | 397
Abermain Bulk | 370-1 | Abermain BS | Nth Ipswich | NCC Rating (A) | 499 | 499 | 499 | 499 | 499 | Urban | 70
|  |  |  | 10 POE Load (A) | 212 | 210 | 209 | 206 | 205
|  |  |  | Power Factor | 0.96931 | 0.96952 | 0.96962 | 0.96992 | 0.97002
|  |  |  | ECC Rating (A) | 499 | 499 | 499 | 499 | 499
|  |  |  | 50 POE Load (A) | 408 | 404 | 402 | 396 | 396
Abermain Bulk | 387-1 | Abermain BS | Marburg | NCC Rating (A) | 290 | 290 | 290 | 290 | 290 | Rural | 170 | 4
|  |  |  | 10 POE Load (A) | 169 | 172 | 177 | 182 | 188
|  |  |  | Power Factor | 0.99408 | 0.99385 | 0.9936 | 0.99327 | 0.99293
|  |  |  | ECC Rating (A) | 290 | 290 | 290 | 290 | 290
|  |  |  | 50 POE Load (A) | 232 | 244 | 251 | 263 | 277
Abermain Bulk | 3901-1 | Karrabin | Amberley | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
|  |  |  | 10 POE Load (A) | 176 | 179 | 181 | 184 | 182
|  |  |  | Power Factor | 0.92438 | 0.92427 | 0.92411 | 0.92383 | 0.94691
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 320 | 324 | 328 | 333 | 333
Abermain Bulk | 420-1 | Mt Crosby West | Mt Crosby | NCC Rating (A) | 349 | 349 | 349 | 349 | 349 | HighSec | 0
|  |  |  | 10 POE Load (A) | 19 | 19 | 29 | 30 | 30
|  |  |  | Power Factor | 0.37943 | 0.96417 | 0.42408 | 0.46762 | 0.48878
|  |  |  | ECC Rating (A) | 349 | 349 | 349 | 349 | 349
|  |  |  | 50 POE Load (A) | 268 | 257 | 261 | 257 | 255
Abermain Bulk | 436-1 | Amberley | 436 Tee1 | NCC Rating (A) | 351 | 351 | 351 | 351 | 351 | Rural | 170 | 12
|  |  |  | 10 POE Load (A) | 74 | 78 | 83 | 88 | 94
|  |  |  | Power Factor | 0.86263 | 0.86679 | 0.87076 | 0.87439 | 0.87814
|  |  |  | ECC Rating (A) | 351 | 351 | 351 | 351 | 351
|  |  |  | 50 POE Load (A) | 236 | 247 | 254 | 266 | 280
Abermain Bulk | 436-4 | 436 Tee1 | Rosewood | NCC Rating (A) | 208 | 208 | 208 | 208 | 208 | Rural | 170
|  |  |  | 10 POE Load (A) | 74 | 78 | 83 | 89 | 95
|  |  |  | Power Factor | 0.86217 | 0.86674 | 0.87119 | 0.87529 | 0.87952
|  |  |  | ECC Rating (A) | 208 | 208 | 208 | 208 | 208
|  |  |  | 50 POE Load (A) | 236 | 247 | 254 | 266 | 280
Abermain Bulk | 445-1 | Abermain BS | Moggill | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70
|  |  |  | 10 POE Load (A) | 210 | 206 | 202 | 199 | 198
|  |  |  | Power Factor | 0.98721 | 0.98758 | 0.98785 | 0.98813 | 0.98822
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 331 | 324 | 320 | 314 | 312
Abermain Bulk | 475-1 | Karrabin | Amberley | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
|  |  |  | 10 POE Load (A) | 174 | 177 | 179 | 181 | 179
|  |  |  | Power Factor | 0.92824 | 0.92819 | 0.92808 | 0.92787 | 0.95041
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 319 | 323 | 327 | 333 | 333
Abermain Bulk | 673-1 | Moggill | Kenmore | NCC Rating (A) | 636 | 636 | 636 | 636 | 636 | Urban | 70
|  |  |  | 10 POE Load (A) | 3 | 3 | 3 | 3 | 3
|  |  |  | Power Factor | 4.7649e-05 | 4.7649e-05 | 4.7649e-05 | 4.7649e-05 | 4.7649e-05
|  |  |  | ECC Rating (A) | 636 | 636 | 636 | 636 | 636
|  |  |  | 50 POE Load (A) | 3 | 3 | 3 | 3 | 3
Algester Bulk | 3400-1 | Algester BS | Calamvale | NCC Rating (A) | 694 | 694 | 694 | 694 | 694 | Urban | 70
|  |  |  | 10 POE Load (A) | 341 | 336 | 334 | 330 | 330
|  |  |  | Power Factor | 0.96976 | 0.97028 | 0.97049 | 0.97101 | 0.97101
|  |  |  | ECC Rating (A) | 694 | 694 | 694 | 694 | 694
|  |  |  | 50 POE Load (A) | 658 | 649 | 645 | 638 | 636
Algester Bulk | 3402-1 | Algester BS | Acacia Ridge | NCC Rating (A) | 687 | 687 | 687 | 687 | 687 | Urban | 70
|  |  |  | 10 POE Load (A) | 155 | 153 | 152 | 149 | 149
|  |  |  | Power Factor | 0.99285 | 0.99295 | 0.99299 | 0.99724 | 0.99724
|  |  |  | ECC Rating (A) | 687 | 687 | 687 | 687 | 687
|  |  |  | 50 POE Load (A) | 297 | 302 | 301 | 297 | 295
Algester Bulk | 3403-1 | Algester BS | Acacia Ridge | NCC Rating (A) | 687 | 687 | 687 | 687 | 687 | Urban | 70
|  |  |  | 10 POE Load (A) | 155 | 154 | 153 | 150 | 150
|  |  |  | Power Factor | 0.99286 | 0.99296 | 0.993 | 0.99725 | 0.99725
|  |  |  | ECC Rating (A) | 687 | 687 | 687 | 687 | 687
|  |  |  | 50 POE Load (A) | 297 | 302 | 301 | 297 | 295
Algester Bulk | 3405-1 | Algester BS | Calamvale | NCC Rating (A) | 694 | 694 | 694 | 694 | 694 | Urban | 70
|  |  |  | 10 POE Load (A) | 341 | 336 | 335 | 330 | 330
|  |  |  | Power Factor | 0.96976 | 0.97029 | 0.9705 | 0.97101 | 0.97101
|  |  |  | ECC Rating (A) | 694 | 694 | 694 | 694 | 694
|  |  |  | 50 POE Load (A) | 658 | 649 | 645 | 638 | 636
Archerfield Bulk | 597-1 | Rocklea | Salisbury | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70
|  |  |  | 10 POE Load (A) | 185 | 184 | 182 | 182 | 182
|  |  |  | Power Factor | 0.95457 | 0.95481 | 0.95505 | 0.95505 | 0.95505
|  |  |  | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | 50 POE Load (A) | 173 | 172 | 172 | 170 | 170
Archerfield Bulk | 635-1 | Archerfield BS | Coopers Plains | NCC Rating (A) | 523 | 523 | 523 | 523 | 523 | Urban | 70
|  |  |  | 10 POE Load (A) | 371 | 374 | 365 | 358 | 356
|  |  |  | Power Factor | 0.98652 | 0.98676 | 0.98674 | 0.98702 | 0.98927
|  |  |  | ECC Rating (A) | 523 | 523 | 523 | 523 | 523
|  |  |  | 50 POE Load (A) | 349 | 353 | 346 | 338 | 336
Archerfield Bulk | 650-1 | Archerfield BS | Rocklea | NCC Rating (A) | 650 | 650 | 650 | 650 | 650 | Urban | 70
|  |  |  | 10 POE Load (A) | 243 | 239 | 237 | 235 | 234
|  |  |  | Power Factor | 0.95644 | 0.95686 | 0.95705 | 0.95721 | 0.95729
|  |  |  | ECC Rating (A) | 650 | 650 | 650 | 650 | 650
|  |  |  | 50 POE Load (A) | 458 | 449 | 447 | 442 | 442
Archerfield Bulk | 651-1 | Archerfield BS | Rocklea | NCC Rating (A) | 650 | 650 | 650 | 650 | 650 | Urban | 70
|  |  |  | 10 POE Load (A) | 240 | 236 | 234 | 232 | 232
|  |  |  | Power Factor | 0.95637 | 0.95679 | 0.95698 | 0.95713 | 0.95721
|  |  |  | ECC Rating (A) | 650 | 650 | 650 | 650 | 650
|  |  |  | 50 POE Load (A) | 458 | 449 | 447 | 442 | 442
Ashgrove West Bulk | 432-1 | Ashgrove West BS | Toowong | NCC Rating (A) | 476 | 476 | 476 | 476 | 476 | Urban | 70
|  |  |  | 10 POE Load (A) | 14 | 14 | 14 | 14 | 14
|  |  |  | Power Factor | 4.2657e-05 | 4.2657e-05 | 4.2657e-05 | 4.2657e-05 | 4.2657e-05
|  |  |  | ECC Rating (A) | 476 | 476 | 476 | 476 | 476
|  |  |  | 50 POE Load (A) | 14 | 14 | 14 | 14 | 14
Ashgrove West Bulk | 552-1 | Ashgrove West BS | Ashgrove | NCC Rating (A) | 598 | 598 | 598 | 598 | 598 | Urban | 70
|  |  |  | 10 POE Load (A) | 167 | 165 | 163 | 161 | 161
|  |  |  | Power Factor | 0.99941 | 0.99952 | 0.99957 | 0.99967 | 0.99964
|  |  |  | ECC Rating (A) | 598 | 598 | 598 | 598 | 598
|  |  |  | 50 POE Load (A) | 248 | 244 | 242 | 239 | 239
Ashgrove West Bulk | 565-1 | Ashgrove West BS | Ashgrove | NCC Rating (A) | 851 | 851 | 851 | 851 | 851 | Urban | 70
|  |  |  | 10 POE Load (A) | 115 | 114 | 113 | 111 | 111
|  |  |  | Power Factor | 0.9836 | 0.98418 | 0.98446 | 0.98504 | 0.98489
|  |  |  | ECC Rating (A) | 851 | 851 | 851 | 851 | 851
|  |  |  | 50 POE Load (A) | 173 | 170 | 169 | 167 | 167
Ashgrove West Bulk | 570-1 | Ashgrove West BS | Ashgrove | NCC Rating (A) | 598 | 598 | 598 | 598 | 598 | Urban | 70
|  |  |  | 10 POE Load (A) | 163 | 161 | 160 | 157 | 158
|  |  |  | Power Factor | 0.99938 | 0.99949 | 0.99954 | 0.99964 | 0.99962
|  |  |  | ECC Rating (A) | 598 | 598 | 598 | 598 | 598
|  |  |  | 50 POE Load (A) | 246 | 241 | 239 | 236 | 236
Ashgrove West Bulk | 585-1 | Ashgrove West BS | The Gap | NCC Rating (A) | 622 | 622 | 622 | 622 | 622 | Urban | 70
|  |  |  | 10 POE Load (A) | 161 | 157 | 156 | 154 | 153
|  |  |  | Power Factor | 0.99276 | 0.99295 | 0.993 | 0.99293 | 0.99298
|  |  |  | ECC Rating (A) | 622 | 622 | 622 | 622 | 622
|  |  |  | 50 POE Load (A) | 150 | 148 | 146 | 143 | 143
Ashgrove West Bulk | 586-1 | Ashgrove West BS | The Gap | NCC Rating (A) | 622 | 622 | 622 | 622 | 622 | Urban | 70
|  |  |  | 10 POE Load (A) | 161 | 157 | 156 | 154 | 153
|  |  |  | Power Factor | 0.99201 | 0.99224 | 0.99229 | 0.99245 | 0.99251
|  |  |  | ECC Rating (A) | 622 | 622 | 622 | 622 | 622
|  |  |  | 50 POE Load (A) | 150 | 148 | 146 | 143 | 143
Ashgrove West Bulk | 590-1 | Ashgrove BS | Toowong | NCC Rating (A) | 705 | 705 | 705 | 705 | 705 | Urban | 70
|  |  |  | 10 POE Load (A) | 340 | 333 | 362 | 359 | 359
|  |  |  | Power Factor | 0.98655 | 0.98644 | 0.97864 | 0.97883 | 0.97883
|  |  |  | ECC Rating (A) | 705 | 705 | 705 | 705 | 705
|  |  |  | 50 POE Load (A) | 637 | 624 | 682 | 677 | 677
Ashgrove West Bulk | 591-1 | Ashgrove BS | Toowong | NCC Rating (A) | 705 | 705 | 705 | 705 | 705 | Urban | 70
|  |  |  | 10 POE Load (A) | 340 | 333 | 362 | 359 | 359
|  |  |  | Power Factor | 0.98651 | 0.9864 | 0.97859 | 0.97878 | 0.97878
|  |  |  | ECC Rating (A) | 705 | 705 | 705 | 705 | 705
|  |  |  | 50 POE Load (A) | 637 | 624 | 682 | 677 | 677
Ashgrove West Bulk | 675-1 | Ashgrove | Newmarket | NCC Rating (A) | 492 | 492 | 492 | 492 | 492 | Urban | 70
|  |  |  | 10 POE Load (A) | 17 | 17 | 17 | 17 | 17
|  |  |  | Power Factor | 3.5471e-05 | 3.5471e-05 | 3.5471e-05 | 3.5471e-05 | 3.5471e-05
|  |  |  | ECC Rating (A) | 492 | 492 | 492 | 492 | 492
|  |  |  | 50 POE Load (A) | 17 | 17 | 17 | 17 | 17
Ashgrove West Bulk | 676-1 | Ashgrove | Newmarket | NCC Rating (A) | 492 | 492 | 492 | 492 | 492 | Urban | 70
|  |  |  | 10 POE Load (A) | 17 | 17 | 17 | 17 | 17
|  |  |  | Power Factor | 3.4731e-05 | 3.4731e-05 | 3.4731e-05 | 3.4731e-05 | 3.4731e-05
|  |  |  | ECC Rating (A) | 492 | 492 | 492 | 492 | 492
|  |  |  | 50 POE Load (A) | 17 | 17 | 17 | 17 | 17
Beaudesert Bulk | 314-1 | Beaudesert BS | Jimboomba | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Rural | 170 | 1
|  |  |  | 10 POE Load (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 1.6107e-05 | 1.6107e-05 | 1.6107e-05 | 1.6107e-05 | 1.6107e-05
|  |  |  | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
|  |  |  | 50 POE Load (A) | 1 | 1 | 1 | 1 | 1
Beaudesert Bulk | 404-1 | Beaudesert | Innisplain | NCC Rating (A) | 155 | 155 | 155 | 155 | 155 | Rural | 170 | 4
|  |  |  | 10 POE Load (A) | 83 | 83 | 83 | 83 | 83
|  |  |  | Power Factor | 0.97585 | 0.97585 | 0.97584 | 0.97584 | 0.97584
|  |  |  | ECC Rating (A) | 155 | 155 | 155 | 155 | 155
|  |  |  | 50 POE Load (A) | 80 | 80 | 80 | 80 | 80
Beaudesert Bulk | 466-1 | Beaudesert BS | Bromelton | NCC Rating (A) | 403 | 403 | 403 | 403 | 403 | Rural | 170
|  |  |  | 10 POE Load (A) | 88 | 88 | 89 | 89 | 90
|  |  |  | Power Factor | 0.96915 | 0.96915 | 0.96904 | 0.96904 | 0.96893
|  |  |  | ECC Rating (A) | 403 | 403 | 403 | 403 | 403
|  |  |  | 50 POE Load (A) | 141 | 141 | 143 | 143 | 143
Beaudesert Bulk | 467-1 | Beaudesert BS | Bromelton | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
|  |  |  | 10 POE Load (A) | 59 | 59 | 60 | 60 | 61
|  |  |  | Power Factor | 0.99274 | 0.99274 | 0.99267 | 0.99267 | 0.9926
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 142 | 142 | 144 | 144 | 144
Beaudesert Bulk | 468-1 | Beaudesert BS | Beaudesert | NCC Rating (A) | 579 | 579 | 579 | 579 | 579 | Rural | 170
|  |  |  | 10 POE Load (A) | 273 | 273 | 275 | 275 | 278
|  |  |  | Power Factor | 0.93104 | 0.93062 | 0.93027 | 0.93922 | 0.92922
|  |  |  | ECC Rating (A) | 579 | 579 | 579 | 579 | 579
|  |  |  | 50 POE Load (A) | 389 | 393 | 396 | 392 | 404
Beaudesert Bulk | 469-1 | Beaudesert BS | 469 Tee1 | NCC Rating (A) | 537 | 537 | 537 | 537 | 537 | Rural | 170 | 1
|  |  |  | 10 POE Load (A) | 281 | 281 | 283 | 283 | 285
|  |  |  | Power Factor | 0.96317 | 0.96287 | 0.96261 | 0.96912 | 0.96182
|  |  |  | ECC Rating (A) | 537 | 537 | 537 | 537 | 537
|  |  |  | 50 POE Load (A) | 530 | 532 | 534 | 535 | 540
Beaudesert Bulk | 469-2 | 469 Tee1 | Beaudesert | NCC Rating (A) | 579 | 579 | 579 | 579 | 579 | Rural | 170
|  |  |  | 10 POE Load (A) | 134 | 138 | 140 | 142 | 145
|  |  |  | Power Factor | 0.96475 | 0.96357 | 0.96265 | 0.9622 | 0.96115
|  |  |  | ECC Rating (A) | 579 | 579 | 579 | 579 | 579
|  |  |  | 50 POE Load (A) | 392 | 396 | 400 | 402 | 408
Beaudesert Bulk | 469-3 | 469 Tee1 | Mt Tamborine Bus 2 | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Rural | 170
|  |  |  | 10 POE Load (A) | 152 | 150 | 148 | 148 | 148
|  |  |  | Power Factor | 0.97521 | 0.9756 | 0.97597 | 0.97597 | 0.97596
|  |  |  | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
|  |  |  | 50 POE Load (A) | 307 | 302 | 302 | 298 | 298
Beenleigh Bulk | 3590-1 | Beenleigh BS | Loganholme | NCC Rating (A) | 766 | 766 | 766 | 766 | 766 | Urban | 70
|  |  |  | 10 POE Load (A) | 410 | 400 | 393 | 384 | 380
|  |  |  | Power Factor | 0.98311 | 0.98325 | 0.98353 | 0.98388 | 0.98406
|  |  |  | ECC Rating (A) | 766 | 766 | 766 | 766 | 766
|  |  |  | 50 POE Load (A) | 653 | 635 | 624 | 611 | 605
Beenleigh Bulk | 3591-1 | Cornubia | Loganholme | NCC Rating (A) | 807 | 807 | 807 | 807 | 807 | Urban | 70
|  |  |  | 10 POE Load (A) | 63 | 60 | 58 | 56 | 55
|  |  |  | Power Factor | 0.90431 | 0.90116 | 0.8996 | 0.89924 | 0.89871
|  |  |  | ECC Rating (A) | 807 | 807 | 807 | 807 | 807
|  |  |  | 50 POE Load (A) | 449 | 437 | 427 | 417 | 411
Beenleigh Bulk | 3601-1 | Yatala | Stapylton | NCC Rating (A) | 713 | 713 | 713 | 713 | 713 | Rural | 170
|  |  |  | 10 POE Load (A) | 100 | 99 | 98 | 96 | 96
|  |  |  | Power Factor | 0.95132 | 0.95146 | 0.95161 | 0.95189 | 0.95203
|  |  |  | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
|  |  |  | 50 POE Load (A) | 203 | 199 | 197 | 195 | 194
Beenleigh Bulk | 3620-1 | Beenleigh BS | Logan Village | NCC Rating (A) | 490 | 490 | 490 | 490 | 490 | Rural | 170
|  |  |  | 10 POE Load (A) | 2 | 2 | 2 | 2 | 2
|  |  |  | Power Factor | 0.00018079 | 0.00018079 | 0.00018079 | 0.00018079 | 0.00018079
|  |  |  | ECC Rating (A) | 490 | 490 | 490 | 490 | 490
|  |  |  | 50 POE Load (A) | 430 | 434 | 441 | 441 | 445
Beenleigh Bulk | 402-1 | Beenleigh BS | 402 Tee1 | NCC Rating (A) | 579 | 579 | 579 | 579 | 579 | Urban | 70
|  |  |  | 10 POE Load (A) | 255 | 253 | 248 | 246 | 246
|  |  |  | Power Factor | 0.97667 | 0.9769 | 0.97738 | 0.97772 | 0.97772
|  |  |  | ECC Rating (A) | 579 | 579 | 579 | 579 | 579
|  |  |  | 50 POE Load (A) | 411 | 403 | 403 | 398 | 395
Beenleigh Bulk | 402-2 | 402 Tee1 | Tamborine Village | NCC Rating (A) | 439 | 439 | 439 | 439 | 439 | Urban | 70
|  |  |  | 10 POE Load (A) | 92 | 91 | 89 | 89 | 89
|  |  |  | Power Factor | 0.99263 | 0.99245 | 0.99262 | 0.99263 | 0.99263
|  |  |  | ECC Rating (A) | 439 | 439 | 439 | 439 | 439
|  |  |  | 50 POE Load (A) | 81 | 80 | 80 | 79 | 78
Beenleigh Bulk | 402-3 | 402 Tee1 | Mt Tamborine Bus 1 | NCC Rating (A) | 812 | 812 | 812 | 812 | 812 | Urban | 70
|  |  |  | 10 POE Load (A) | 164 | 161 | 159 | 157 | 157
|  |  |  | Power Factor | 0.97995 | 0.98025 | 0.98058 | 0.98088 | 0.98088
|  |  |  | ECC Rating (A) | 812 | 812 | 812 | 812 | 812
|  |  |  | 50 POE Load (A) | 324 | 318 | 318 | 313 | 313
Beenleigh Bulk | 405-1 | Beenleigh BS | 405 Tee1 | NCC Rating (A) | 807 | 807 | 807 | 807 | 807 | Urban | 70
|  |  |  | 10 POE Load (A) | 290 | 283 | 279 | 273 | 270
|  |  |  | Power Factor | 0.97751 | 0.97785 | 0.97824 | 0.97875 | 0.97901
|  |  |  | ECC Rating (A) | 807 | 807 | 807 | 807 | 807
|  |  |  | 50 POE Load (A) | 668 | 650 | 638 | 624 | 618
Beenleigh Bulk | 405-3 | 405 Tee1 | Cornubia | NCC Rating (A) | 774 | 774 | 774 | 774 | 774 | Urban | 70
|  |  |  | 10 POE Load (A) | 290 | 283 | 279 | 273 | 270
|  |  |  | Power Factor | 0.9802 | 0.98044 | 0.98075 | 0.98115 | 0.98135
|  |  |  | ECC Rating (A) | 774 | 774 | 774 | 774 | 774
|  |  |  | 50 POE Load (A) | 668 | 650 | 638 | 624 | 618
Beenleigh Bulk | 419-1 | Loganholme | Tanah Merah | NCC Rating (A) | 713 | 713 | 713 | 713 | 713 | Urban | 70
|  |  |  | 10 POE Load (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 2.0559e-06 | 2.0558e-06 | 2.0559e-06 | 2.0558e-06 | 2.0557e-06
|  |  |  | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
|  |  |  | 50 POE Load (A) | 312 | 305 | 301 | 297 | 295
Beenleigh Bulk | 426-1 | Beenleigh BS | Stapylton | NCC Rating (A) | 740 | 740 | 740 | 740 | 740 | Rural | 170
|  |  |  | 10 POE Load (A) | 104 | 103 | 102 | 101 | 100
|  |  |  | Power Factor | 0.95465 | 0.95479 | 0.95493 | 0.9552 | 0.95534
|  |  |  | ECC Rating (A) | 740 | 740 | 740 | 740 | 740
|  |  |  | 50 POE Load (A) | 202 | 199 | 197 | 195 | 194
Beenleigh Bulk | 427-1 | Beenleigh BS | Yatala | NCC Rating (A) | 740 | 740 | 740 | 740 | 740 | Rural | 170
|  |  |  | 10 POE Load (A) | 99 | 99 | 98 | 96 | 95
|  |  |  | Power Factor | 0.95374 | 0.95395 | 0.95416 | 0.95459 | 0.9548
|  |  |  | ECC Rating (A) | 740 | 740 | 740 | 740 | 740
|  |  |  | 50 POE Load (A) | 202 | 199 | 197 | 195 | 193
Beenleigh Bulk | 453-1 | Beenleigh BS | Beenleigh Nth | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 713
|  |  |  | 10 POE Load (A) | 777 | 771 | 768 | 764 | 764
|  |  |  | Power Factor | 0.97713 | 0.97734 | 0.97748 | 0.97762 | 0.97762
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 718 | 713 | 709 | 706 | 706
Beenleigh Bulk | 496-1 | Beenleigh Nth | Bethania | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70
|  |  |  | 10 POE Load (A) | 429 | 427 | 425 | 424 | 424
|  |  |  | Power Factor | 0.98602 | 0.98612 | 0.98621 | 0.9863 | 0.9863
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 391 | 389 | 387 | 385 | 385
Beerwah Bulk | 3190-1 | Woodford | Kilcoy | NCC Rating (A) | 0 | 700 | 700 | 700 | 700 | Rural | 170
|  |  |  | 10 POE Load (A) | 0 | 157 | 156 | 155 | 153
|  |  |  | Power Factor | 0 | 0.92792 | 0.92845 | 0.92898 | 0.9295
|  |  |  | ECC Rating (A) | 0 | 700 | 700 | 700 | 700
|  |  |  | 50 POE Load (A) | 0 | 214 | 212 | 210 | 210
Beerwah Bulk | 324-1 | Woodford | Kilcoy | NCC Rating (A) | 348 | 348 | 348 | 348 | 348 | Rural | 170
|  |  |  | 10 POE Load (A) | 322 | 81 | 80 | 80 | 79
|  |  |  | Power Factor | 0.95879 | 0.99656 | 0.99644 | 0.99632 | 0.99619
|  |  |  | ECC Rating (A) | 348 | 348 | 348 | 348 | 348
|  |  |  | 50 POE Load (A) | 257 | 74 | 73 | 72 | 72
Beerwah Bulk | 428-1 | Beerwah BS | Woodford | NCC Rating (A) | 351 | 351 | 351 | 351 | 351 | Rural | 170
|  |  |  | 10 POE Load (A) | 369 | 259 | 256 | 254 | 252
|  |  |  | Power Factor | 0.8838 | 0.95542 | 0.95608 | 0.95673 | 0.95738
|  |  |  | ECC Rating (A) | 351 | 351 | 351 | 351 | 351
|  |  |  | 50 POE Load (A) | 293 | 237 | 234 | 232 | 232
Beerwah Bulk | 447-1 | Somerset Dam | Kilcoy | NCC Rating (A) | 155 | 704 | 704 | 704 | 704 | Rural | 170
|  |  |  | 10 POE Load (A) | 1 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0.00023397 | 1 | 1 | 1 | 1
|  |  |  | ECC Rating (A) | 155 | 0 | 0 | 0 | 0
|  |  |  | 50 POE Load (A) | 1 | 0 | 0 | 0 | 0
Beerwah Bulk | 477-1 | 477 Tee1 | Maleny | NCC Rating (A) | 155 | 155 | 155 | 155 | 155 | Rural | 170
|  |  |  | 10 POE Load (A) | 2 | 2 | 2 | 2 | 2
|  |  |  | Power Factor | 3.5253e-05 | 3.5253e-05 | 3.5253e-05 | 3.5253e-05 | 3.5253e-05
|  |  |  | ECC Rating (A) | 155 | 155 | 155 | 155 | 155
|  |  |  | 50 POE Load (A) | 2 | 2 | 2 | 2 | 2
Beerwah Bulk | 477-2 | 477 Tee1 | Woodford | NCC Rating (A) | 330 | 330 | 704 | 704 | 704 | Rural | 170
|  |  |  | 10 POE Load (A) | 206 | 201 | 193 | 189 | 189
|  |  |  | Power Factor | 0.98416 | 0.98462 | 0.98872 | 0.98899 | 0.98899
|  |  |  | ECC Rating (A) | 330 | 330 | 704 | 704 | 704
|  |  |  | 50 POE Load (A) | 195 | 191 | 185 | 182 | 182
Beerwah Bulk | 477-3 | Beerwah | 477 Tee1 | NCC Rating (A) | 711 | 711 | 711 | 711 | 711 | Rural | 170
|  |  |  | 10 POE Load (A) | 205 | 201 | 193 | 189 | 189
|  |  |  | Power Factor | 0.97585 | 0.9767 | 0.9775 | 0.97828 | 0.97828
|  |  |  | ECC Rating (A) | 711 | 711 | 711 | 711 | 711
|  |  |  | 50 POE Load (A) | 195 | 191 | 185 | 181 | 181
Beerwah Bulk | 608-1 | Beerwah BS | Landsborough | NCC Rating (A) | 412 | 412 | 412 | 412 | 412 | Rural | 170
|  |  |  | 10 POE Load (A) | 235 | 233 | 233 | 231 | 233
|  |  |  | Power Factor | 0.98738 | 0.98754 | 0.98754 | 0.9877 | 0.98754
|  |  |  | ECC Rating (A) | 412 | 412 | 412 | 412 | 412
|  |  |  | 50 POE Load (A) | 220 | 218 | 218 | 216 | 218
Belmont Bulk | 527-1 | Mt Gravatt | Upper Mt Gravatt | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70
|  |  |  | 10 POE Load (A) | 67 | 66 | 66 | 64 | 64
|  |  |  | Power Factor | 0.98276 | 0.98328 | 0.98371 | 0.98203 | 0.98136
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 157 | 155 | 153 | 151 | 150
Belmont Bulk | 631-1 | Belmont BS | Mt Gravatt | NCC Rating (A) | 420 | 420 | 420 | 420 | 420 | Urban | 70
|  |  |  | 10 POE Load (A) | 287 | 283 | 280 | 277 | 278
|  |  |  | Power Factor | 0.98088 | 0.98109 | 0.98131 | 0.98151 | 0.98145
|  |  |  | ECC Rating (A) | 465 | 465 | 465 | 465 | 465
|  |  |  | 50 POE Load (A) | 467 | 460 | 455 | 451 | 453
Belmont Bulk | 632-1 | Belmont BS | Mt Gravatt | NCC Rating (A) | 420 | 420 | 420 | 420 | 420 | Urban | 70
|  |  |  | 10 POE Load (A) | 285 | 281 | 278 | 276 | 276
|  |  |  | Power Factor | 0.98079 | 0.981 | 0.98122 | 0.98141 | 0.98135
|  |  |  | ECC Rating (A) | 452 | 452 | 452 | 452 | 452
|  |  |  | 50 POE Load (A) | 466 | 459 | 454 | 450 | 453
Belmont Bulk | 647-1 | Belmont BS | Eight Mile Plains Bus 2 | NCC Rating (A) | 479 | 479 | 479 | 479 | 479 | Urban | 270 | 2
|  |  |  | 10 POE Load (A) | 335 | 329 | 327 | 341 | 359
|  |  |  | Power Factor | 0.95306 | 0.95395 | 0.95424 | 0.95216 | 0.95082
|  |  |  | ECC Rating (A) | 479 | 479 | 479 | 479 | 479
|  |  |  | 50 POE Load (A) | 710 | 695 | 683 | 722 | 770
Belmont Bulk | 660-1 | Belmont BS | Scrub Road | NCC Rating (A) | 676 | 676 | 676 | 676 | 676 | Urban | 70
|  |  |  | 10 POE Load (A) | 279 | 272 | 268 | 262 | 259
|  |  |  | Power Factor | 0.97473 | 0.9757 | 0.97599 | 0.97648 | 0.97669
|  |  |  | ECC Rating (A) | 676 | 676 | 676 | 676 | 676
|  |  |  | 50 POE Load (A) | 510 | 497 | 490 | 479 | 474
Belmont Bulk | 661-1 | Belmont BS | Scrub Road | NCC Rating (A) | 676 | 676 | 676 | 676 | 676 | Urban | 70
|  |  |  | 10 POE Load (A) | 282 | 275 | 271 | 265 | 262
|  |  |  | Power Factor | 0.97473 | 0.9757 | 0.97599 | 0.97648 | 0.97669
|  |  |  | ECC Rating (A) | 676 | 676 | 676 | 676 | 676
|  |  |  | 50 POE Load (A) | 510 | 497 | 490 | 479 | 474
Belmont Bulk | 662-1 | Belmont BS | Upper Mt Gravatt | NCC Rating (A) | 656 | 656 | 656 | 656 | 656 | Urban | 70
|  |  |  | 10 POE Load (A) | 202 | 199 | 198 | 195 | 195
|  |  |  | Power Factor | 0.94251 | 0.94244 | 0.94274 | 0.94307 | 0.943
|  |  |  | ECC Rating (A) | 656 | 656 | 656 | 656 | 656
|  |  |  | 50 POE Load (A) | 295 | 291 | 287 | 284 | 285
Belmont Bulk | 663-1 | Belmont BS | Upper Mt Gravatt | NCC Rating (A) | 656 | 656 | 656 | 656 | 656 | Urban | 70
|  |  |  | 10 POE Load (A) | 205 | 202 | 200 | 197 | 197
|  |  |  | Power Factor | 0.94274 | 0.94267 | 0.94298 | 0.94331 | 0.94324
|  |  |  | ECC Rating (A) | 656 | 656 | 656 | 656 | 656
|  |  |  | 50 POE Load (A) | 297 | 292 | 289 | 286 | 286
Belmont Bulk | 692-1 | Belmont BS | Holland Pk East | NCC Rating (A) | 421 | 421 | 421 | 421 | 421 | Urban | 70
|  |  |  | 10 POE Load (A) | 179 | 177 | 176 | 173 | 173
|  |  |  | Power Factor | 0.97631 | 0.97657 | 0.97666 | 0.97692 | 0.97692
|  |  |  | ECC Rating (A) | 421 | 421 | 421 | 421 | 421
|  |  |  | 50 POE Load (A) | 344 | 338 | 336 | 331 | 331
Belmont Bulk | 693-1 | Belmont BS | Holland Pk East | NCC Rating (A) | 421 | 421 | 421 | 421 | 421 | Urban | 70
|  |  |  | 10 POE Load (A) | 181 | 178 | 177 | 175 | 175
|  |  |  | Power Factor | 0.97656 | 0.97682 | 0.97691 | 0.97718 | 0.97718
|  |  |  | ECC Rating (A) | 421 | 421 | 421 | 421 | 421
|  |  |  | 50 POE Load (A) | 343 | 338 | 336 | 331 | 331
Brendale Bulk | 303-1 | Brendale BS | Albany Ck | NCC Rating (A) | 725 | 725 | 725 | 725 | 725 | Urban | 70
|  |  |  | 10 POE Load (A) | 246 | 240 | 239 | 235 | 234
|  |  |  | Power Factor | 0.98373 | 0.98419 | 0.98434 | 0.98463 | 0.98471
|  |  |  | ECC Rating (A) | 725 | 725 | 725 | 725 | 725
|  |  |  | 50 POE Load (A) | 485 | 473 | 469 | 462 | 460
Brendale Bulk | 309-1 | Brendale BS | 309 Tee1 | NCC Rating (A) | 627 | 627 | 627 | 627 | 627 | Rural | 170
|  |  |  | 10 POE Load (A) | 298 | 294 | 291 | 288 | 287
|  |  |  | Power Factor | 0.97159 | 0.97217 | 0.97237 | 0.97284 | 0.97294
|  |  |  | ECC Rating (A) | 627 | 627 | 627 | 627 | 627
|  |  |  | 50 POE Load (A) | 602 | 592 | 587 | 580 | 577
Brendale Bulk | 309-2 | 309 Tee1 | Samford | NCC Rating (A) | 711 | 711 | 711 | 711 | 711 | Rural | 170
|  |  |  | 10 POE Load (A) | 93 | 92 | 92 | 91 | 91
|  |  |  | Power Factor | 0.99286 | 0.9928 | 0.99229 | 0.99233 | 0.99224
|  |  |  | ECC Rating (A) | 711 | 711 | 711 | 711 | 711
|  |  |  | 50 POE Load (A) | 292 | 286 | 284 | 282 | 280
Brendale Bulk | 309-3 | 309 Tee1 | Arana Hills | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Rural | 170
|  |  |  | 10 POE Load (A) | 213 | 209 | 207 | 205 | 204
|  |  |  | Power Factor | 0.96638 | 0.96717 | 0.96764 | 0.96825 | 0.96841
|  |  |  | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | 50 POE Load (A) | 647 | 637 | 632 | 623 | 620
Brendale Bulk | 310-1 | Brendale BS | 310 Tee1 | NCC Rating (A) | 627 | 627 | 627 | 627 | 627 | Urban | 70
|  |  |  | 10 POE Load (A) | 436 | 430 | 426 | 421 | 419
|  |  |  | Power Factor | 0.97073 | 0.97137 | 0.97167 | 0.97218 | 0.9723
|  |  |  | ECC Rating (A) | 627 | 627 | 627 | 627 | 627
|  |  |  | 50 POE Load (A) | 618 | 608 | 604 | 596 | 594
Brendale Bulk | 310-2 | 310 Tee1 | Arana Hills | NCC Rating (A) | 792 | 792 | 792 | 792 | 792 | Urban | 70
|  |  |  | 10 POE Load (A) | 436 | 430 | 426 | 421 | 420
|  |  |  | Power Factor | 0.97779 | 0.97825 | 0.97846 | 0.97883 | 0.97891
|  |  |  | ECC Rating (A) | 792 | 792 | 792 | 792 | 792
|  |  |  | 50 POE Load (A) | 619 | 608 | 604 | 596 | 594
Brendale Bulk | 333-1 | Brendale BS | Lawnton | NCC Rating (A) | 732 | 732 | 732 | 732 | 732 | Urban | 70
|  |  |  | 10 POE Load (A) | 325 | 322 | 321 | 320 | 321
|  |  |  | Power Factor | 0.9699 | 0.9702 | 0.97027 | 0.97046 | 0.97037
|  |  |  | ECC Rating (A) | 732 | 732 | 732 | 732 | 732
|  |  |  | 50 POE Load (A) | 537 | 531 | 530 | 527 | 530
Brendale Bulk | 3340-1 | Brendale Bs | Strathpine | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Urban | 70
|  |  |  | 10 POE Load (A) | 171 | 175 | 172 | 168 | 168
|  |  |  | Power Factor | 0.95573 | 0.95386 | 0.95548 | 0.95622 | 0.95634
|  |  |  | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
|  |  |  | 50 POE Load (A) | 257 | 264 | 259 | 254 | 253
Brendale Bulk | 334-1 | Lawnton | 334 Tee1 | NCC Rating (A) | 578 | 578 | 578 | 578 | 578 | Rural | 170
|  |  |  | 10 POE Load (A) | 26 | 24 | 24 | 23 | 22
|  |  |  | Power Factor | 0.13966 | 0.058701 | 0.021359 | 0.099559 | 0.17069
|  |  |  | ECC Rating (A) | 578 | 578 | 578 | 578 | 578
|  |  |  | 50 POE Load (A) | 221 | 217 | 212 | 209 | 207
Brendale Bulk | 334-2 | 334 Tee1 | Whiteside | NCC Rating (A) | 750 | 750 | 750 | 750 | 750 | Rural | 170
|  |  |  | 10 POE Load (A) | 80 | 77 | 76 | 73 | 72
|  |  |  | Power Factor | 0.92785 | 0.92797 | 0.92826 | 0.92914 | 0.92941
|  |  |  | ECC Rating (A) | 750 | 750 | 750 | 750 | 750
|  |  |  | 50 POE Load (A) | 163 | 159 | 155 | 151 | 149
Brendale Bulk | 334-3 | 334 Tee1 | Nth Pine Dam | NCC Rating (A) | 578 | 578 | 578 | 578 | 578 | Rural | 170
|  |  |  | 10 POE Load (A) | 78 | 78 | 79 | 79 | 80
|  |  |  | Power Factor | 0.99631 | 0.99648 | 0.99624 | 0.99626 | 0.99599
|  |  |  | ECC Rating (A) | 578 | 578 | 578 | 578 | 578
|  |  |  | 50 POE Load (A) | 167 | 166 | 166 | 165 | 167
Brendale Bulk | 335-1 | Brendale BS | 335 Tee1 | NCC Rating (A) | 485 | 485 | 485 | 485 | 485 | Rural | 170
|  |  |  | 10 POE Load (A) | 219 | 216 | 215 | 212 | 212
|  |  |  | Power Factor | 0.94747 | 0.94798 | 0.9482 | 0.94886 | 0.94902
|  |  |  | ECC Rating (A) | 485 | 485 | 485 | 485 | 485
|  |  |  | 50 POE Load (A) | 305 | 302 | 300 | 298 | 298
Brendale Bulk | 335-2 | 335 Tee | Whiteside | NCC Rating (A) | 750 | 750 | 750 | 750 | 750 | Rural | 170
|  |  |  | 10 POE Load (A) | 93 | 91 | 90 | 87 | 86
|  |  |  | Power Factor | 0.94002 | 0.9404 | 0.94073 | 0.94172 | 0.94205
|  |  |  | ECC Rating (A) | 750 | 750 | 750 | 750 | 750
|  |  |  | 50 POE Load (A) | 160 | 156 | 152 | 148 | 146
Brendale Bulk | 335-3 | 335 Tee | Nth Pine Dam | NCC Rating (A) | 485 | 485 | 485 | 485 | 485 | Rural | 170
|  |  |  | 10 POE Load (A) | 127 | 126 | 126 | 126 | 127
|  |  |  | Power Factor | 0.96722 | 0.96727 | 0.967 | 0.96697 | 0.96681
|  |  |  | ECC Rating (A) | 485 | 485 | 485 | 485 | 485
|  |  |  | 50 POE Load (A) | 215 | 212 | 212 | 212 | 213
Brendale Bulk | 336-1 | Brendale BS | Strathpine | NCC Rating (A) | 455 | 455 | 455 | 455 | 455 | Urban | 70
|  |  |  | 10 POE Load (A) | 195 | 200 | 197 | 193 | 192
|  |  |  | Power Factor | 0.97742 | 0.97602 | 0.97723 | 0.9778 | 0.97789
|  |  |  | ECC Rating (A) | 455 | 455 | 455 | 455 | 455
|  |  |  | 50 POE Load (A) | 274 | 281 | 276 | 270 | 269
Brendale Bulk | 3364-1 | Brendale BS | Albany Ck | NCC Rating (A) | 725 | 725 | 725 | 725 | 725 | Urban | 70
|  |  |  | 10 POE Load (A) | 252 | 246 | 244 | 241 | 240
|  |  |  | Power Factor | 0.98362 | 0.98407 | 0.98422 | 0.98452 | 0.98459
|  |  |  | ECC Rating (A) | 725 | 725 | 725 | 725 | 725
|  |  |  | 50 POE Load (A) | 484 | 472 | 468 | 461 | 459
Brendale Bulk | 337-1 | Brendale BS | Strathpine | NCC Rating (A) | 490 | 490 | 490 | 490 | 490 | Urban | 70
|  |  |  | 10 POE Load (A) | 160 | 164 | 161 | 158 | 157
|  |  |  | Power Factor | 0.96985 | 0.96823 | 0.96962 | 0.97029 | 0.9704
|  |  |  | ECC Rating (A) | 490 | 490 | 490 | 490 | 490
|  |  |  | 50 POE Load (A) | 241 | 247 | 243 | 238 | 237
Brendale Bulk | 342-1 | Brendale BS | Bald Hills Bus 2 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70
|  |  |  | 10 POE Load (A) | 172 | 169 | 167 | 166 | 164
|  |  |  | Power Factor | 0.99954 | 0.99957 | 0.99959 | 0.9996 | 0.99962
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 323 | 316 | 313 | 306 | 306
Brendale Bulk | 349-1 | Brendale BS | Lawnton | NCC Rating (A) | 717 | 717 | 717 | 717 | 717 | Urban | 70
|  |  |  | 10 POE Load (A) | 351 | 348 | 347 | 345 | 347
|  |  |  | Power Factor | 0.97141 | 0.97169 | 0.97176 | 0.97194 | 0.97185
|  |  |  | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
|  |  |  | 50 POE Load (A) | 549 | 542 | 541 | 538 | 541
Brendale Bulk | 464-1 | Brendale BS | Samford | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
|  |  |  | 10 POE Load (A) | 220 | 217 | 215 | 213 | 212
|  |  |  | Power Factor | 0.96984 | 0.9704 | 0.97042 | 0.97091 | 0.97098
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 333 | 326 | 324 | 320 | 319
Browns Plains Bulk | 406A-1 | Bethania | Kingston | NCC Rating (A) | 529 | 529 | 529 | 529 | 529 | Urban | 260 | 1.5
|  |  |  | 10 POE Load (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 6.3211e-06 | 6.3215e-06 | 6.3211e-06 | 6.3209e-06 | 6.3211e-06
|  |  |  | ECC Rating (A) | 529 | 529 | 529 | 529 | 529
|  |  |  | 50 POE Load (A) | 790 | 783 | 779 | 774 | 774
Browns Plains Bulk | 406B-1 | Crestmead | Kingston | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
|  |  |  | 10 POE Load (A) | 2 | 2 | 2 | 2 | 2
|  |  |  | Power Factor | 4.3755e-05 | 4.3754e-05 | 4.3755e-05 | 4.3754e-05 | 4.3755e-05
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 790 | 783 | 778 | 774 | 774
Browns Plains Bulk | 478-1 | Browns Plains BS | Nth Maclean | NCC Rating (A) | 813 | 813 | 813 | 813 | 813 | Rural | 170
|  |  |  | 10 POE Load (A) | 2 | 2 | 2 | 2 | 2
|  |  |  | Power Factor | 3.0986e-05 | 3.0986e-05 | 3.0986e-05 | 3.0986e-05 | 3.0986e-05
|  |  |  | ECC Rating (A) | 813 | 813 | 813 | 813 | 813
|  |  |  | 50 POE Load (A) | 659 | 653 | 651 | 659 | 673
Browns Plains Bulk | 481-1 | Browns Plains BS | Cresmead | NCC Rating (A) | 705 | 705 | 705 | 705 | 705 | Urban | 70
|  |  |  | 10 POE Load (A) | 272 | 272 | 267 | 261 | 260
|  |  |  | Power Factor | 0.9632 | 0.9632 | 0.96467 | 0.96813 | 0.96835
|  |  |  | ECC Rating (A) | 705 | 705 | 705 | 705 | 705
|  |  |  | 50 POE Load (A) | 647 | 645 | 638 | 630 | 629
Browns Plains Bulk | 482-1 | Browns Plains BS | Cresmead | NCC Rating (A) | 704 | 704 | 704 | 704 | 704 | Urban | 70
|  |  |  | 10 POE Load (A) | 274 | 274 | 269 | 263 | 261
|  |  |  | Power Factor | 0.96302 | 0.96302 | 0.9645 | 0.96797 | 0.96819
|  |  |  | ECC Rating (A) | 704 | 704 | 704 | 704 | 704
|  |  |  | 50 POE Load (A) | 651 | 648 | 642 | 634 | 633
Browns Plains Bulk | 542-1 | Browns Plains BS | Heathwood | NCC Rating (A) | 704 | 704 | 704 | 704 | 704 | Urban | 70
|  |  |  | 10 POE Load (A) | 572 | 560 | 555 | 543 | 537
|  |  |  | Power Factor | 0.97381 | 0.97469 | 0.97512 | 0.97597 | 0.97639
|  |  |  | ECC Rating (A) | 704 | 704 | 704 | 704 | 704
|  |  |  | 50 POE Load (A) | 533 | 524 | 517 | 507 | 503
Burleigh Heads Bulk | 3751-1 | Burleigh Hds BS | Currumbin | NCC Rating (A) | 606 | 606 | 606 | 606 | 606 | Urban | 321 | 3
|  |  |  | 10 POE Load (A) | 608 | 604 | 603 | 601 | 601
|  |  |  | Power Factor | 0.96678 | 0.96563 | 0.96558 | 0.96565 | 0.9656
|  |  |  | ECC Rating (A) | 695 | 695 | 695 | 695 | 695
|  |  |  | 50 POE Load (A) | 974 | 968 | 967 | 961 | 963
Burleigh Heads Bulk | 3755-1 | Burleigh Hds BS | Currumbin | NCC Rating (A) | 606 | 606 | 606 | 606 | 606 | Urban | 321 | 3
|  |  |  | 10 POE Load (A) | 607 | 604 | 603 | 600 | 601
|  |  |  | Power Factor | 0.96678 | 0.96563 | 0.96558 | 0.96565 | 0.9656
|  |  |  | ECC Rating (A) | 695 | 695 | 695 | 695 | 695
|  |  |  | 50 POE Load (A) | 974 | 968 | 967 | 961 | 962
Burleigh Heads Bulk | 3756-1 | Burleigh Hds BS | 3756 Tee1 | NCC Rating (A) | 715 | 715 | 715 | 715 | 715 | Urban | 70
|  |  |  | 10 POE Load (A) | 190 | 189 | 189 | 188 | 188
|  |  |  | Power Factor | 0.98326 | 0.98205 | 0.98204 | 0.98209 | 0.98206
|  |  |  | ECC Rating (A) | 715 | 715 | 715 | 715 | 715
|  |  |  | 50 POE Load (A) | 284 | 282 | 282 | 280 | 281
Burleigh Heads Bulk | 3756-2 | 3756 Tee1 | Palm Beach | NCC Rating (A) | 532 | 532 | 532 | 532 | 532 | Urban | 70
|  |  |  | 10 POE Load (A) | 154 | 152 | 151 | 150 | 150
|  |  |  | Power Factor | 0.99868 | 0.9967 | 0.99683 | 0.99688 | 0.99691
|  |  |  | ECC Rating (A) | 532 | 532 | 532 | 532 | 532
|  |  |  | 50 POE Load (A) | 351 | 347 | 347 | 344 | 344
Burleigh Heads Bulk | 3756-3 | 3756 Tee1 | 3756 Tee2 | NCC Rating (A) | 636 | 636 | 636 | 636 | 636 | Urban | 70
|  |  |  | 10 POE Load (A) | 48 | 46 | 47 | 48 | 47
|  |  |  | Power Factor | 0.81853 | 0.85782 | 0.85728 | 0.86103 | 0.85833
|  |  |  | ECC Rating (A) | 636 | 636 | 636 | 636 | 636
|  |  |  | 50 POE Load (A) | 257 | 256 | 256 | 255 | 255
Burleigh Heads Bulk | 3756-4 | 3756 Tee2 | Currumbin | NCC Rating (A) | 717 | 717 | 717 | 717 | 717 | Urban | 70
|  |  |  | 10 POE Load (A) | 48 | 46 | 47 | 48 | 47
|  |  |  | Power Factor | 0.81523 | 0.8546 | 0.85412 | 0.85796 | 0.8552
|  |  |  | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
|  |  |  | 50 POE Load (A) | 257 | 256 | 256 | 255 | 255
Burleigh Heads Bulk | 393-1 | Currumbin | Kirra | NCC Rating (A) | 403 | 403 | 445 | 445 | 445 | Urban | 70
|  |  |  | 10 POE Load (A) | 355 | 355 | 355 | 353 | 355
|  |  |  | Power Factor | 0.96057 | 0.96057 | 0.96812 | 0.96826 | 0.96812
|  |  |  | ECC Rating (A) | 403 | 403 | 445 | 445 | 445
|  |  |  | 50 POE Load (A) | 341 | 339 | 341 | 339 | 341
Burleigh Heads Bulk | 395-1 | Burleigh Hds BS | Miami | NCC Rating (A) | 654 | 654 | 654 | 654 | 654 | Urban | 70
|  |  |  | 10 POE Load (A) | 489 | 491 | 497 | 503 | 514
|  |  |  | Power Factor | 0.97928 | 0.97919 | 0.9789 | 0.9786 | 0.97848
|  |  |  | ECC Rating (A) | 654 | 654 | 654 | 654 | 654
|  |  |  | 50 POE Load (A) | 448 | 450 | 456 | 461 | 470
Burleigh Heads Bulk | 396-1 | Burleigh Hds BS | Palm Beach | NCC Rating (A) | 806 | 806 | 806 | 806 | 806 | Urban | 70
|  |  |  | 10 POE Load (A) | 217 | 216 | 216 | 215 | 215
|  |  |  | Power Factor | 0.98116 | 0.9798 | 0.97979 | 0.97986 | 0.97982
|  |  |  | ECC Rating (A) | 806 | 806 | 806 | 806 | 806
|  |  |  | 50 POE Load (A) | 352 | 349 | 349 | 345 | 345
Burleigh Heads Bulk | 397-1 | Burleigh Hds BS | 397 Tee1 | NCC Rating (A) | 602 | 602 | 602 | 602 | 602 | Urban | 70
|  |  |  | 10 POE Load (A) | 3 | 3 | 3 | 3 | 3
|  |  |  | Power Factor | 1.8279e-05 | 1.8279e-05 | 1.8279e-05 | 1.8279e-05 | 1.8279e-05
|  |  |  | ECC Rating (A) | 602 | 602 | 602 | 602 | 602
|  |  |  | 50 POE Load (A) | 3 | 3 | 3 | 3 | 3
Burleigh Heads Bulk | 397-2 | 397 Tee1 | 396 Tee | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 4.7615e-05 | 4.7615e-05 | 4.7615e-05 | 4.7615e-05 | 4.7615e-05
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Burleigh Heads Bulk | 397-3 | 397 Tee1 | 397 Tee2 | NCC Rating (A) | 529 | 529 | 529 | 529 | 529 | Urban | 70
|  |  |  | 10 POE Load (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 8.5552e-06 | 8.555e-06 | 8.555e-06 | 8.5549e-06 | 8.5549e-06
|  |  |  | ECC Rating (A) | 529 | 529 | 529 | 529 | 529
|  |  |  | 50 POE Load (A) | 1 | 1 | 1 | 1 | 1
Burleigh Heads Bulk | 397-4 | 397 Tee2 | 3700 Tee1 | NCC Rating (A) | 362 | 362 | 362 | 362 | 362 | Urban | 70
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 8.644e-07 | 8.6457e-07 | 8.6457e-07 | 8.6457e-07 | 8.6457e-07
|  |  |  | ECC Rating (A) | 362 | 362 | 362 | 362 | 362
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Burleigh Heads Bulk | 397-5 | 397 Tee2 | Mudgeeraba BS | NCC Rating (A) | 703 | 703 | 703 | 703 | 703 | Urban | 70
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 2.5251e-06 | 2.5243e-06 | 2.5243e-06 | 2.5241e-06 | 2.5241e-06
|  |  |  | ECC Rating (A) | 703 | 703 | 703 | 703 | 703
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Caboolture Bulk | 321-1 | Caboolture BS | Caboolture West | NCC Rating (A) | 509 | 509 | 509 | 509 | 509 | Urban | 70
|  |  |  | 10 POE Load (A) | 295 | 290 | 287 | 285 | 284
|  |  |  | Power Factor | 0.9765 | 0.97684 | 0.97714 | 0.97749 | 0.97759
|  |  |  | ECC Rating (A) | 509 | 509 | 509 | 509 | 509
|  |  |  | 50 POE Load (A) | 440 | 431 | 428 | 423 | 422
Caboolture Bulk | 322-1 | Caboolture BS | Caboolture West | NCC Rating (A) | 509 | 509 | 509 | 509 | 509 | Urban | 70
|  |  |  | 10 POE Load (A) | 310 | 305 | 302 | 299 | 298
|  |  |  | Power Factor | 0.96859 | 0.96898 | 0.96933 | 0.96973 | 0.96984
|  |  |  | ECC Rating (A) | 509 | 509 | 509 | 509 | 509
|  |  |  | 50 POE Load (A) | 449 | 440 | 437 | 433 | 431
Caboolture Bulk | 323-1 | Caboolture West | 323 Tee1 | NCC Rating (A) | 250 | 250 | 250 | 250 | 250 | Rural | 170
|  |  |  | 10 POE Load (A) | 80 | 79 | 78 | 78 | 78
|  |  |  | Power Factor | 0.99422 | 0.9943 | 0.9943 | 0.99431 | 0.99431
|  |  |  | ECC Rating (A) | 250 | 250 | 250 | 250 | 250
|  |  |  | 50 POE Load (A) | 76 | 74 | 74 | 74 | 74
Caboolture Bulk | 323-2 | 323 Tee1 | Wamuran | NCC Rating (A) | 457 | 457 | 457 | 457 | 457 | Rural | 170
|  |  |  | 10 POE Load (A) | 80 | 79 | 79 | 79 | 79
|  |  |  | Power Factor | 0.99317 | 0.99315 | 0.99315 | 0.99315 | 0.99315
|  |  |  | ECC Rating (A) | 457 | 457 | 457 | 457 | 457
|  |  |  | 50 POE Load (A) | 76 | 74 | 74 | 74 | 74
Caboolture Bulk | 323-3 | 323 Tee1 | Woodford | NCC Rating (A) | 251 | 251 | 251 | 251 | 251 | Rural | 170
|  |  |  | 10 POE Load (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 1.5118e-05 | 1.5118e-05 | 1.5119e-05 | 1.5119e-05 | 1.5118e-05
|  |  |  | ECC Rating (A) | 251 | 251 | 251 | 251 | 251
|  |  |  | 50 POE Load (A) | 1 | 1 | 1 | 1 | 1
Caboolture Bulk | 350-1 | Caboolture BS | Ningi | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 424 | 418 | 417 | 410 | 409
|  |  |  | Power Factor | 0.97392 | 0.97446 | 0.97458 | 0.97721 | 0.97732
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 786 | 773 | 770 | 755 | 753
Caboolture Bulk | 412-1 | Caboolture BS | Toorbul Pt | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Rural | 170 | 4.5
|  |  |  | 10 POE Load (A) | 343 | 338 | 337 | 332 | 331
|  |  |  | Power Factor | 0.97195 | 0.97249 | 0.97263 | 0.97583 | 0.97595
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 837 | 820 | 817 | 797 | 794
Caboolture Bulk | 417-1 | Ningi | Toorbul Pt | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 216 | 213 | 212 | 209 | 208
|  |  |  | Power Factor | 0.99197 | 0.99226 | 0.99237 | 0.99464 | 0.99473
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 577 | 568 | 566 | 553 | 553
Caboolture Bulk | 431-1 | Toorbul Point | Bribie Is | NCC Rating (A) | 396 | 396 | 396 | 396 | 396 | Urban | 70
|  |  |  | 10 POE Load (A) | 216 | 213 | 212 | 208 | 207
|  |  |  | Power Factor | 0.98667 | 0.98692 | 0.987 | 0.99007 | 0.99014
|  |  |  | ECC Rating (A) | 443 | 443 | 443 | 443 | 443
|  |  |  | 50 POE Load (A) | 401 | 395 | 393 | 386 | 386
Caboolture Bulk | 448-1 | Morayfield Nth | 448 Tee1 | NCC Rating (A) | 776 | 776 | 776 | 776 | 776 | Urban | 70
|  |  |  | 10 POE Load (A) | 660 | 653 | 647 | 643 | 641
|  |  |  | Power Factor | 0.96082 | 0.96101 | 0.96151 | 0.96179 | 0.96195
|  |  |  | ECC Rating (A) | 776 | 776 | 776 | 776 | 776
|  |  |  | 50 POE Load (A) | 762 | 752 | 747 | 740 | 739
Caboolture Bulk | 448-2 | 448 Tee1 | Morayfield | NCC Rating (A) | 698 | 698 | 698 | 698 | 698 | Urban | 70
|  |  |  | 10 POE Load (A) | 653 | 646 | 639 | 635 | 633
|  |  |  | Power Factor | 0.9727 | 0.97273 | 0.97307 | 0.9733 | 0.97341
|  |  |  | ECC Rating (A) | 698 | 698 | 698 | 698 | 698
|  |  |  | 50 POE Load (A) | 620 | 612 | 608 | 602 | 602
Caboolture Bulk | 448-3 | 448 Tee1 | Caboolture West | NCC Rating (A) | 485 | 485 | 485 | 485 | 485 | Urban | 70
|  |  |  | 10 POE Load (A) | 7 | 8 | 8 | 8 | 8
|  |  |  | Power Factor | 0.96856 | 0.96737 | 0.96553 | 0.95951 | 0.9589
|  |  |  | ECC Rating (A) | 485 | 485 | 485 | 485 | 485
|  |  |  | 50 POE Load (A) | 146 | 144 | 143 | 142 | 141
Caboolture Bulk | 457-1 | Toorbul Pt | Bribie Island | NCC Rating (A) | 402 | 402 | 402 | 402 | 402 | Urban | 70
|  |  |  | 10 POE Load (A) | 215 | 212 | 211 | 207 | 206
|  |  |  | Power Factor | 0.98882 | 0.98905 | 0.98912 | 0.99191 | 0.99197
|  |  |  | ECC Rating (A) | 402 | 402 | 402 | 402 | 402
|  |  |  | 50 POE Load (A) | 402 | 396 | 394 | 386 | 386
Caboolture Bulk | 461-1 | Caboolture BS | Morayfield Nth | NCC Rating (A) | 676 | 676 | 676 | 676 | 676 | Urban | 280
|  |  |  | 10 POE Load (A) | 604 | 590 | 585 | 579 | 577
|  |  |  | Power Factor | 0.96627 | 0.96683 | 0.96722 | 0.96788 | 0.96801
|  |  |  | ECC Rating (A) | 758 | 758 | 758 | 758 | 758
|  |  |  | 50 POE Load (A) | 1036 | 1011 | 1002 | 991 | 989
Caboolture Bulk | 499-1 | Caboolture BS | Morayfield Nth | NCC Rating (A) | 676 | 676 | 676 | 676 | 676 | Urban | 280 | 6.5
|  |  |  | 10 POE Load (A) | 608 | 595 | 589 | 583 | 581
|  |  |  | Power Factor | 0.9663 | 0.96686 | 0.96725 | 0.96791 | 0.96804
|  |  |  | ECC Rating (A) | 758 | 758 | 758 | 758 | 758
|  |  |  | 50 POE Load (A) | 1038 | 1012 | 1004 | 992 | 990
Cleveland Bulk | 3550-1 | Cleveland BS | Victoria Pt | NCC Rating (A) | 746 | 746 | 746 | 746 | 746 | Urban | 70
|  |  |  | 10 POE Load (A) | 520 | 513 | 509 | 502 | 502
|  |  |  | Power Factor | 0.98497 | 0.98517 | 0.98539 | 0.98552 | 0.98555
|  |  |  | ECC Rating (A) | 746 | 746 | 746 | 746 | 746
|  |  |  | 50 POE Load (A) | 686 | 676 | 672 | 664 | 662
Cleveland Bulk | 3570-1 | Capalaba South | Capalaba | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70
|  |  |  | 10 POE Load (A) | 102 | 102 | 102 | 99 | 99
|  |  |  | Power Factor | 0.90986 | 0.91264 | 0.91371 | 0.91443 | 0.91554
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 321 | 318 | 315 | 310 | 309
Cleveland Bulk | 3580-1 | Redland Bay | 3580 Tee1 | NCC Rating (A) | 717 | 717 | 717 | 717 | 717 | Urban | 70
|  |  |  | 10 POE Load (A) | 40 | 41 | 41 | 41 | 43
|  |  |  | Power Factor | 1 | 0.99999 | 0.99999 | 0.99996 | 0.99991
|  |  |  | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
|  |  |  | 50 POE Load (A) | 347 | 343 | 343 | 341 | 341
Cleveland Bulk | 3580-2 | 3580 Tee1 | Mt Cotton | NCC Rating (A) | 527 | 527 | 527 | 527 | 527 | Urban | 70
|  |  |  | 10 POE Load (A) | 40 | 41 | 41 | 41 | 43
|  |  |  | Power Factor | 0.99975 | 0.99978 | 0.99979 | 0.99988 | 0.99995
|  |  |  | ECC Rating (A) | 527 | 527 | 527 | 527 | 527
|  |  |  | 50 POE Load (A) | 347 | 343 | 343 | 341 | 341
Cleveland Bulk | 3580-3 | 3580 Tee1 | Cornubia | NCC Rating (A) | 717 | 717 | 717 | 717 | 717 | Urban | 70
|  |  |  | 10 POE Load (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 2.2671e-06 | 2.2669e-06 | 2.2666e-06 | 2.2667e-06 | 2.2669e-06
|  |  |  | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
|  |  |  | 50 POE Load (A) | 1 | 1 | 1 | 1 | 1
Cleveland Bulk | 371-1 | Cleveland BS | Birkdale | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
|  |  |  | 10 POE Load (A) | 472 | 464 | 460 | 453 | 451
|  |  |  | Power Factor | 0.96001 | 0.96081 | 0.9612 | 0.96193 | 0.9622
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 598 | 589 | 583 | 572 | 570
Cleveland Bulk | 372-1 | Cleveland BS | Raby Bay | NCC Rating (A) | 611 | 611 | 611 | 611 | 611 | Urban | 361
|  |  |  | 10 POE Load (A) | 442 | 436 | 434 | 428 | 428
|  |  |  | Power Factor | 0.98013 | 0.98049 | 0.98063 | 0.98119 | 0.98127
|  |  |  | ECC Rating (A) | 611 | 611 | 611 | 611 | 611
|  |  |  | 50 POE Load (A) | 802 | 792 | 788 | 777 | 777
Cleveland Bulk | 373-1 | Raby Bay | Capalaba | NCC Rating (A) | 715 | 715 | 715 | 715 | 715 | Urban | 70
|  |  |  | 10 POE Load (A) | 354 | 346 | 342 | 336 | 333
|  |  |  | Power Factor | 0.97797 | 0.97839 | 0.97859 | 0.97896 | 0.97911
|  |  |  | ECC Rating (A) | 715 | 715 | 715 | 715 | 715
|  |  |  | 50 POE Load (A) | 573 | 563 | 557 | 546 | 543
Cleveland Bulk | 374-1 | Cleveland BS | Capalaba South | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
|  |  |  | 10 POE Load (A) | 408 | 399 | 395 | 389 | 386
|  |  |  | Power Factor | 0.96194 | 0.96272 | 0.96309 | 0.96376 | 0.96406
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 613 | 602 | 596 | 585 | 582
Cleveland Bulk | 375-1 | Cleveland BS | 375 Tee1 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
|  |  |  | 10 POE Load (A) | 205 | 201 | 200 | 197 | 196
|  |  |  | Power Factor | 0.99133 | 0.99152 | 0.99165 | 0.99183 | 0.99186
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 507 | 499 | 497 | 491 | 491
Cleveland Bulk | 375-2 | 375 Tee1 | Mt Cotton | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
|  |  |  | 10 POE Load (A) | 205 | 201 | 200 | 197 | 196
|  |  |  | Power Factor | 0.99305 | 0.99318 | 0.99329 | 0.99342 | 0.99345
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 507 | 499 | 497 | 491 | 491
Cleveland Bulk | 375-3 | 375 Tee1 | 425 Tee1 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0.00030502 | 0.00030508 | 0.0003049 | 0.00030494 | 0.00030455
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Cleveland Bulk | 413-1 | Cleveland BS | Raby Bay | NCC Rating (A) | 611 | 611 | 611 | 611 | 611 | Urban | 370 | 9.5
|  |  |  | 10 POE Load (A) | 447 | 441 | 439 | 434 | 433
|  |  |  | Power Factor | 0.98016 | 0.98052 | 0.98066 | 0.98122 | 0.9813
|  |  |  | ECC Rating (A) | 611 | 611 | 611 | 611 | 611
|  |  |  | 50 POE Load (A) | 803 | 792 | 789 | 778 | 778
Cleveland Bulk | 425-1 | Cleveland BS | Victoria Pt | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70
|  |  |  | 10 POE Load (A) | 230 | 227 | 225 | 222 | 222
|  |  |  | Power Factor | 0.99474 | 0.99488 | 0.995 | 0.9951 | 0.99512
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 614 | 604 | 600 | 593 | 592
Cleveland Bulk | 465-1 | Victoria Pt | Redland Bay | NCC Rating (A) | 508 | 508 | 508 | 508 | 508 | Urban | 70
|  |  |  | 10 POE Load (A) | 309 | 305 | 303 | 300 | 301
|  |  |  | Power Factor | 0.99018 | 0.99029 | 0.99034 | 0.99044 | 0.99042
|  |  |  | ECC Rating (A) | 508 | 508 | 508 | 508 | 508
|  |  |  | 50 POE Load (A) | 489 | 481 | 479 | 474 | 474
Cleveland Bulk | 484-1 | Capalaba | Birkdale | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70
|  |  |  | 10 POE Load (A) | 142 | 142 | 142 | 141 | 141
|  |  |  | Power Factor | 0.9753 | 0.97567 | 0.97587 | 0.97631 | 0.97627
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 594 | 588 | 583 | 574 | 572
Coomera Bulk | 3640-1 | Coomera BS | Hope Is | NCC Rating (A) | 716 | 716 | 716 | 716 | 716 | Urban | 70
|  |  |  | 10 POE Load (A) | 339 | 336 | 335 | 334 | 337
|  |  |  | Power Factor | 0.9731 | 0.97303 | 0.97313 | 0.97323 | 0.97292
|  |  |  | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
|  |  |  | 50 POE Load (A) | 642 | 636 | 634 | 632 | 636
Coomera Bulk | 3641-1 | Coomera BS | Pimpama East | NCC Rating (A) | 713 | 713 | 713 | 713 | 713 | Urban | 200 | 4.5
|  |  |  | 10 POE Load (A) | 394 | 435 | 440 | 448 | 459
|  |  |  | Power Factor | 0.97641 | 0.97104 | 0.97035 | 0.96923 | 0.969
|  |  |  | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
|  |  |  | 50 POE Load (A) | 750 | 838 | 847 | 863 | 887
Coomera Bulk | 3642-1 | Coomera BS | Pimpama East | NCC Rating (A) | 713 | 713 | 713 | 713 | 713 | Urban | 200 | 4.5
|  |  |  | 10 POE Load (A) | 397 | 439 | 444 | 452 | 463
|  |  |  | Power Factor | 0.97634 | 0.97097 | 0.97028 | 0.96915 | 0.96892
|  |  |  | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
|  |  |  | 50 POE Load (A) | 750 | 838 | 847 | 862 | 886
Coomera Bulk | 394-1 | Coomera BS | Hope Is | NCC Rating (A) | 716 | 716 | 716 | 716 | 716 | Urban | 70
|  |  |  | 10 POE Load (A) | 347 | 344 | 343 | 342 | 345
|  |  |  | Power Factor | 0.9786 | 0.97854 | 0.97863 | 0.97873 | 0.97845
|  |  |  | ECC Rating (A) | 716 | 716 | 716 | 716 | 716
|  |  |  | 50 POE Load (A) | 644 | 639 | 637 | 635 | 639
Coorparoo Bulk | 3429-1 | Coorparoo BS | Holland Park | NCC Rating (A) | 735 | 735 | 735 | 735 | 735 | Urban | 70
|  |  |  | 10 POE Load (A) | 230 | 243 | 241 | 238 | 238
|  |  |  | Power Factor | 0.97606 | 0.92988 | 0.92973 | 0.92948 | 0.92948
|  |  |  | ECC Rating (A) | 735 | 735 | 735 | 735 | 735
|  |  |  | 50 POE Load (A) | 449 | 437 | 433 | 427 | 427
Coorparoo Bulk | 3430-1 | Coorparoo BS | Holland Park | NCC Rating (A) | 735 | 735 | 735 | 735 | 735 | Urban | 70
|  |  |  | 10 POE Load (A) | 226 | 209 | 208 | 205 | 205
|  |  |  | Power Factor | 0.97602 | 0.99917 | 0.99926 | 0.99939 | 0.99939
|  |  |  | ECC Rating (A) | 735 | 735 | 735 | 735 | 735
|  |  |  | 50 POE Load (A) | 450 | 442 | 438 | 432 | 432
Coorparoo Bulk | 584-4 | 584 Tee2 | Coorparoo BS | NCC Rating (A) | 721 | 721 | 721 | 721 | 721 | Urban | 70
|  |  |  | 10 POE Load (A) | 2 | 2 | 2 | 2 | 2
|  |  |  | Power Factor | 7.9103e-07 | 7.9103e-07 | 7.9103e-07 | 7.9103e-07 | 7.9103e-07
|  |  |  | ECC Rating (A) | 721 | 721 | 721 | 721 | 721
|  |  |  | 50 POE Load (A) | 2 | 2 | 2 | 2 | 2
Coorparoo Bulk | 612-1 | Coorparoo BS | Camp Hill | NCC Rating (A) | 766 | 766 | 766 | 766 | 766 | Urban | 70
|  |  |  | 10 POE Load (A) | 332 | 328 | 328 | 324 | 325
|  |  |  | Power Factor | 0.97618 | 0.97706 | 0.97706 | 0.9779 | 0.97781
|  |  |  | ECC Rating (A) | 766 | 766 | 766 | 766 | 766
|  |  |  | 50 POE Load (A) | 635 | 630 | 628 | 623 | 623
Coorparoo Bulk | 613-1 | Coorparoo BS | Camp Hill | NCC Rating (A) | 766 | 766 | 766 | 766 | 766 | Urban | 70
|  |  |  | 10 POE Load (A) | 332 | 328 | 328 | 324 | 325
|  |  |  | Power Factor | 0.97618 | 0.97706 | 0.97706 | 0.9779 | 0.97781
|  |  |  | ECC Rating (A) | 766 | 766 | 766 | 766 | 766
|  |  |  | 50 POE Load (A) | 635 | 630 | 628 | 623 | 623
Coorparoo Bulk | 648-1 | Scrub Rd | 648 Tee1 | NCC Rating (A) | 597 | 597 | 597 | 597 | 597 | Urban | 70
|  |  |  | 10 POE Load (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 1.2328e-06 | 1.232e-06 | 1.2332e-06 | 1.2336e-06 | 1.2324e-06
|  |  |  | ECC Rating (A) | 597 | 597 | 597 | 597 | 597
|  |  |  | 50 POE Load (A) | 1 | 1 | 1 | 1 | 1
Coorparoo Bulk | 648-2 | 648 Tee1 | 584 Tee1 | NCC Rating (A) | 348 | 348 | 348 | 348 | 348 | Urban | 70
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 1.5487e-05 | 1.5488e-05 | 1.5488e-05 | 1.5491e-05 | 1.5488e-05
|  |  |  | ECC Rating (A) | 348 | 348 | 348 | 348 | 348
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Coorparoo Bulk | 648-3 | 648 Tee1 | Camp Hill | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
|  |  |  | 10 POE Load (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 2.1171e-05 | 2.1171e-05 | 2.1171e-05 | 2.1171e-05 | 2.1171e-05
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 1 | 1 | 1 | 1 | 1
Doboy Bulk | 3426-1 | Queensport | Bulimba | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
|  |  |  | 10 POE Load (A) | 278 | 273 | 270 | 267 | 267
|  |  |  | Power Factor | 0.97171 | 0.97228 | 0.97262 | 0.97296 | 0.97296
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 444 | 437 | 432 | 426 | 426
Doboy Bulk | 414-1 | Doboy BS | Tingalpa | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 70
|  |  |  | 10 POE Load (A) | 183 | 179 | 177 | 175 | 174
|  |  |  | Power Factor | 0.98019 | 0.98065 | 0.98082 | 0.98109 | 0.98118
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | 50 POE Load (A) | 407 | 398 | 396 | 389 | 389
Doboy Bulk | 416-1 | Doboy BS | Murarrie | NCC Rating (A) | 355 | 355 | 355 | 355 | 355 | Urban | 70
|  |  |  | 10 POE Load (A) | 199 | 197 | 196 | 191 | 191
|  |  |  | Power Factor | 0.99082 | 0.99098 | 0.99104 | 0.99616 | 0.9962
|  |  |  | ECC Rating (A) | 355 | 355 | 355 | 355 | 355
|  |  |  | 50 POE Load (A) | 374 | 371 | 367 | 359 | 357
Doboy Bulk | 443-1 | Queensport | Bulimba | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70
|  |  |  | 10 POE Load (A) | 197 | 193 | 191 | 189 | 189
|  |  |  | Power Factor | 0.97699 | 0.97749 | 0.9778 | 0.9781 | 0.9781
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 447 | 440 | 434 | 429 | 429
Doboy Bulk | 446-11 | Doboy BS | Wellington Rd | NCC Rating (A) | 468 | 468 | 468 | 468 | 468 | Urban | 70
|  |  |  | 10 POE Load (A) | 119 | 118 | 118 | 117 | 117
|  |  |  | Power Factor | 0.95939 | 0.95948 | 0.95934 | 0.95942 | 0.95943
|  |  |  | ECC Rating (A) | 468 | 468 | 468 | 468 | 468
|  |  |  | 50 POE Load (A) | 182 | 182 | 182 | 182 | 182
Doboy Bulk | 446-12 | Wellington Rd | Queensport | NCC Rating (A) | 731 | 731 | 731 | 731 | 731 | Urban | 70
|  |  |  | 10 POE Load (A) | 66 | 67 | 67 | 68 | 68
|  |  |  | Power Factor | 0.88648 | 0.88756 | 0.88812 | 0.88892 | 0.88901
|  |  |  | ECC Rating (A) | 731 | 731 | 731 | 731 | 731
|  |  |  | 50 POE Load (A) | 182 | 182 | 182 | 182 | 182
Doboy Bulk | 558-1 | Hemmant | Tingalpa | NCC Rating (A) | 680 | 680 | 680 | 680 | 680 | Urban | 70
|  |  |  | 10 POE Load (A) | 242 | 236 | 234 | 231 | 230
|  |  |  | Power Factor | 0.9781 | 0.97858 | 0.97878 | 0.97906 | 0.97916
|  |  |  | ECC Rating (A) | 680 | 680 | 680 | 680 | 680
|  |  |  | 50 POE Load (A) | 404 | 395 | 393 | 386 | 386
Doboy Bulk | 563-1 | Doboy BS | Hemmant | NCC Rating (A) | 371 | 371 | 371 | 371 | 371 | Urban | 70
|  |  |  | 10 POE Load (A) | 215 | 212 | 211 | 208 | 207
|  |  |  | Power Factor | 0.97257 | 0.97296 | 0.9731 | 0.9734 | 0.97342
|  |  |  | ECC Rating (A) | 429 | 429 | 429 | 429 | 429
|  |  |  | 50 POE Load (A) | 388 | 381 | 379 | 375 | 372
Doboy Bulk | 564-1 | Doboy BS | Hemmant | NCC Rating (A) | 371 | 371 | 371 | 371 | 371 | Urban | 70
|  |  |  | 10 POE Load (A) | 207 | 203 | 202 | 199 | 199
|  |  |  | Power Factor | 0.96869 | 0.9691 | 0.96925 | 0.96958 | 0.9696
|  |  |  | ECC Rating (A) | 429 | 429 | 429 | 429 | 429
|  |  |  | 50 POE Load (A) | 387 | 380 | 378 | 373 | 371
Doboy Bulk | 575C-1 | Doboy BS | Murarrie | NCC Rating (A) | 355 | 355 | 355 | 355 | 355 | Urban | 70
|  |  |  | 10 POE Load (A) | 189 | 186 | 185 | 181 | 180
|  |  |  | Power Factor | 0.98961 | 0.98979 | 0.98985 | 0.99538 | 0.99542
|  |  |  | ECC Rating (A) | 475 | 475 | 475 | 475 | 475
|  |  |  | 50 POE Load (A) | 375 | 371 | 367 | 359 | 357
Doboy Bulk | 581-1 | Doboy BS | Queensport | NCC Rating (A) | 661 | 661 | 661 | 661 | 661 | Urban | 135 | 10
|  |  |  | 10 POE Load (A) | 528 | 520 | 516 | 509 | 508
|  |  |  | Power Factor | 0.96288 | 0.96337 | 0.96321 | 0.96363 | 0.96369
|  |  |  | ECC Rating (A) | 785 | 785 | 785 | 785 | 785
|  |  |  | 50 POE Load (A) | 962 | 949 | 939 | 925 | 924
Doboy Bulk | 645-1 | Doboy BS | Gibson Island | NCC Rating (A) | 433 | 433 | 433 | 433 | 433 | HighSec | 0
|  |  |  | 10 POE Load (A) | 5 | 5 | 5 | 5 | 5
|  |  |  | Power Factor | 1.3174e-06 | 1.3174e-06 | 1.3174e-06 | 1.3174e-06 | 1.3174e-06
|  |  |  | ECC Rating (A) | 433 | 433 | 433 | 433 | 433
|  |  |  | 50 POE Load (A) | 5 | 5 | 5 | 5 | 5
Doboy Bulk | 677-1 | Doboy BS | Queensport | NCC Rating (A) | 661 | 661 | 661 | 661 | 661 | Urban | 135 | 7
|  |  |  | 10 POE Load (A) | 527 | 518 | 514 | 507 | 506
|  |  |  | Power Factor | 0.96287 | 0.96336 | 0.9632 | 0.96362 | 0.96368
|  |  |  | ECC Rating (A) | 785 | 785 | 785 | 785 | 785
|  |  |  | 50 POE Load (A) | 962 | 949 | 939 | 925 | 923
Gatton Bulk | 377-1 | Gatton BS | 377 Tee1 | NCC Rating (A) | 821 | 821 | 821 | 821 | 821 | Rural | 170
|  |  |  | 10 POE Load (A) | 257 | 253 | 251 | 248 | 246
|  |  |  | Power Factor | 0.95317 | 0.9536 | 0.95387 | 0.95453 | 0.95471
|  |  |  | ECC Rating (A) | 821 | 821 | 821 | 821 | 821
|  |  |  | 50 POE Load (A) | 383 | 379 | 375 | 371 | 369
Gatton Bulk | 377-2 | 377 Tee1 | 487 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 4.5148e-05 | 4.5128e-05 | 4.5119e-05 | 4.5115e-05 | 4.5115e-05
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Gatton Bulk | 377-3 | 377 Tee1 | 377 Tee2 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 257 | 253 | 251 | 248 | 246
|  |  |  | Power Factor | 0.95316 | 0.9536 | 0.95387 | 0.95452 | 0.95471
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 383 | 379 | 375 | 371 | 370
Gatton Bulk | 377-4 | 377 Tee2 | Gatton | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
|  |  |  | 10 POE Load (A) | 257 | 254 | 252 | 248 | 246
|  |  |  | Power Factor | 0.96092 | 0.96119 | 0.96136 | 0.96183 | 0.96193
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 383 | 380 | 376 | 372 | 370
Gatton Bulk | 377-5 | 377 Tee2 | Glenmore Grove | NCC Rating (A) | 355 | 355 | 355 | 355 | 355 | Rural | 170
|  |  |  | 10 POE Load (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 2.1626e-05 | 2.1626e-05 | 2.1626e-05 | 2.1626e-05 | 2.1626e-05
|  |  |  | ECC Rating (A) | 355 | 355 | 355 | 355 | 355
|  |  |  | 50 POE Load (A) | 1 | 1 | 1 | 1 | 1
Gatton Bulk | 3859-1 | Gatton BS | Springfield Central | NCC Rating (A) | 764 | 764 | 764 | 764 | 764 | Rural | 170
|  |  |  | 10 POE Load (A) | 36 | 34 | 34 | 33 | 33
|  |  |  | Power Factor | 0.89172 | 0.89236 | 0.89236 | 0.89268 | 0.89268
|  |  |  | ECC Rating (A) | 764 | 764 | 764 | 764 | 764
|  |  |  | 50 POE Load (A) | 66 | 64 | 63 | 61 | 61
Gatton Bulk | 3860-1 | Gatton BS | Springfield Central | NCC Rating (A) | 764 | 764 | 764 | 764 | 764 | Rural | 170
|  |  |  | 10 POE Load (A) | 36 | 34 | 34 | 33 | 33
|  |  |  | Power Factor | 0.89145 | 0.89208 | 0.89208 | 0.89239 | 0.89239
|  |  |  | ECC Rating (A) | 764 | 764 | 764 | 764 | 764
|  |  |  | 50 POE Load (A) | 66 | 64 | 63 | 61 | 61
Gatton Bulk | 487-1 | Gatton BS | 487 Tee1 | NCC Rating (A) | 821 | 821 | 821 | 821 | 821 | Rural | 170
|  |  |  | 10 POE Load (A) | 269 | 266 | 263 | 260 | 257
|  |  |  | Power Factor | 0.94725 | 0.94773 | 0.94825 | 0.94838 | 0.94855
|  |  |  | ECC Rating (A) | 821 | 821 | 821 | 821 | 821
|  |  |  | 50 POE Load (A) | 505 | 495 | 493 | 487 | 481
Gatton Bulk | 487-2 | 487 Tee1 | 377 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 4.3541e-05 | 4.3561e-05 | 4.3551e-05 | 4.3561e-05 | 4.3557e-05
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Gatton Bulk | 487-3 | 487 Tee1 | 487 Tee2 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 270 | 267 | 264 | 261 | 259
|  |  |  | Power Factor | 0.94809 | 0.94847 | 0.94887 | 0.9489 | 0.94899
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 507 | 496 | 494 | 488 | 482
Gatton Bulk | 487-6 | 487 Tee3 | 3844 Tee1 | NCC Rating (A) | 251 | 251 | 251 | 251 | 251 | Rural | 170
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 3.383e-05 | 3.3844e-05 | 3.3834e-05 | 3.384e-05 | 3.3841e-05
|  |  |  | ECC Rating (A) | 251 | 251 | 251 | 251 | 251
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Gatton Bulk | 487-8 | 487 Tee4 | 3844 Tee2 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0.00046557 | 0.00046351 | 0.0004661 | 0.00046292 | 0.00046586
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Gatton Bulk | 487-9 | 487 Tee2 | Gatton | NCC Rating (A) | 713 | 713 | 713 | 713 | 713 | Rural | 170
|  |  |  | 10 POE Load (A) | 156 | 154 | 152 | 150 | 148
|  |  |  | Power Factor | 0.96222 | 0.96242 | 0.96271 | 0.96319 | 0.96338
|  |  |  | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
|  |  |  | 50 POE Load (A) | 390 | 386 | 382 | 378 | 376
Gatton Bulk | 531-1 | Gatton | Tenthill | NCC Rating (A) | 154 | 154 | 154 | 154 | 154 | Rural | 170
|  |  |  | 10 POE Load (A) | 80 | 78 | 78 | 76 | 74
|  |  |  | Power Factor | 0.96161 | 0.96162 | 0.96162 | 0.96285 | 0.96285
|  |  |  | ECC Rating (A) | 154 | 154 | 154 | 154 | 154
|  |  |  | 50 POE Load (A) | 77 | 77 | 75 | 75 | 75
Gatton Bulk | 532-1 | Tenthill | 532 Tee1 | NCC Rating (A) | 208 | 208 | 208 | 208 | 208 | Rural | 170
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 8.2582e-05 | 8.2583e-05 | 8.2574e-05 | 8.2594e-05 | 8.2587e-05
|  |  |  | ECC Rating (A) | 208 | 208 | 208 | 208 | 208
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Gatton Bulk | 533-1 | Tenthill | Mt Sylvia | NCC Rating (A) | 78 | 78 | 78 | 78 | 78 | Rural | 170
|  |  |  | 10 POE Load (A) | 23 | 23 | 23 | 22 | 22
|  |  |  | Power Factor | 0.8797 | 0.8797 | 0.90733 | 0.87997 | 0.88004
|  |  |  | ECC Rating (A) | 78 | 78 | 78 | 78 | 78
|  |  |  | 50 POE Load (A) | 22 | 22 | 22 | 22 | 20
Goodna Bulk | 3800-1 | Goodna BS | Cooneana | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
|  |  |  | 10 POE Load (A) | 70 | 117 | 121 | 124 | 127
|  |  |  | Power Factor | 0.99717 | 0.99134 | 0.9908 | 0.9908 | 0.99026
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 134 | 235 | 242 | 249 | 255
Goodna Bulk | 3801-1 | Goodna BS | Carol Pk Central | NCC Rating (A) | 720 | 720 | 720 | 720 | 720 | Urban | 70
|  |  |  | 10 POE Load (A) | 299 | 329 | 326 | 323 | 323
|  |  |  | Power Factor | 0.96719 | 0.97826 | 0.97854 | 0.97931 | 0.97937
|  |  |  | ECC Rating (A) | 720 | 720 | 720 | 720 | 720
|  |  |  | 50 POE Load (A) | 487 | 541 | 538 | 533 | 531
Goodna Bulk | 3802-1 | Goodna BS | Springfield | NCC Rating (A) | 592 | 592 | 592 | 592 | 592 | Urban | 70
|  |  |  | 10 POE Load (A) | 379 | 385 | 384 | 383 | 385
|  |  |  | Power Factor | 0.97489 | 0.97483 | 0.97505 | 0.97535 | 0.97541
|  |  |  | ECC Rating (A) | 675 | 675 | 675 | 675 | 675
|  |  |  | 50 POE Load (A) | 687 | 700 | 696 | 696 | 700
Goodna Bulk | 3803-1 | Goodna BS | Carol Park | NCC Rating (A) | 502 | 502 | 502 | 502 | 502 | Urban | 70
|  |  |  | 10 POE Load (A) | 258 | 266 | 266 | 265 | 266
|  |  |  | Power Factor | 0.99134 | 0.9933 | 0.99334 | 0.99428 | 0.99416
|  |  |  | ECC Rating (A) | 502 | 502 | 502 | 502 | 502
|  |  |  | 50 POE Load (A) | 373 | 386 | 383 | 382 | 385
Goodna Bulk | 3805-1 | Goodna BS | Carol Park | NCC Rating (A) | 502 | 502 | 502 | 502 | 502 | Urban | 70
|  |  |  | 10 POE Load (A) | 236 | 243 | 243 | 242 | 244
|  |  |  | Power Factor | 0.98948 | 0.99164 | 0.99169 | 0.99275 | 0.99261
|  |  |  | ECC Rating (A) | 502 | 502 | 502 | 502 | 502
|  |  |  | 50 POE Load (A) | 358 | 371 | 368 | 367 | 370
Goodna Bulk | 3806-1 | Goodna BS | Springfield | NCC Rating (A) | 592 | 592 | 592 | 592 | 592 | Urban | 70
|  |  |  | 10 POE Load (A) | 378 | 383 | 382 | 382 | 384
|  |  |  | Power Factor | 0.97483 | 0.97476 | 0.97499 | 0.97529 | 0.97535
|  |  |  | ECC Rating (A) | 675 | 675 | 675 | 675 | 675
|  |  |  | 50 POE Load (A) | 687 | 700 | 696 | 696 | 700
Goodna Bulk | 3807-1 | Goodna BS | Redbank | NCC Rating (A) | 748 | 748 | 748 | 748 | 748 | Urban | 70
|  |  |  | 10 POE Load (A) | 315 | 331 | 331 | 331 | 333
|  |  |  | Power Factor | 0.97042 | 0.96973 | 0.96973 | 0.96973 | 0.96964
|  |  |  | ECC Rating (A) | 748 | 748 | 748 | 748 | 748
|  |  |  | 50 POE Load (A) | 298 | 314 | 315 | 314 | 317
Goodna Bulk | 3808-1 | Goodna BS | Carol Pk Central | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70
|  |  |  | 10 POE Load (A) | 299 | 330 | 327 | 323 | 323
|  |  |  | Power Factor | 0.96741 | 0.97844 | 0.97871 | 0.97949 | 0.97954
|  |  |  | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | 50 POE Load (A) | 487 | 541 | 538 | 533 | 531
Goodna Bulk | 3809-1 | Goodna BS | Cooneana | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
|  |  |  | 10 POE Load (A) | 79 | 133 | 136 | 140 | 144
|  |  |  | Power Factor | 0.99755 | 0.99233 | 0.99184 | 0.99185 | 0.99137
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 134 | 234 | 242 | 249 | 254
Goodna Bulk | 3880-1 | Carol Park | Springfield Central | NCC Rating (A) | 742 | 742 | 742 | 742 | 742 | Urban | 70
|  |  |  | 10 POE Load (A) | 180 | 202 | 204 | 210 | 219
|  |  |  | Power Factor | 0.9935 | 0.99199 | 0.99183 | 0.99133 | 0.99079
|  |  |  | ECC Rating (A) | 742 | 742 | 742 | 742 | 742
|  |  |  | 50 POE Load (A) | 367 | 419 | 423 | 437 | 454
Goodna Bulk | 3881-1 | Springfield | Springfield Central | NCC Rating (A) | 742 | 742 | 742 | 742 | 742 | Urban | 70
|  |  |  | 10 POE Load (A) | 208 | 234 | 237 | 243 | 253
|  |  |  | Power Factor | 0.98884 | 0.98721 | 0.987 | 0.98665 | 0.98591
|  |  |  | ECC Rating (A) | 742 | 742 | 742 | 742 | 742
|  |  |  | 50 POE Load (A) | 363 | 413 | 416 | 430 | 447
Goodna Bulk | 456-1 | Wacol Sth | 456 Tee1 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70
|  |  |  | 10 POE Load (A) | 102 | 100 | 100 | 100 | 102
|  |  |  | Power Factor | 0.99811 | 0.9882 | 0.98822 | 0.9903 | 0.99003
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 202 | 203 | 201 | 201 | 204
Goodna Bulk | 456-2 | 456 Tee1 | Carol Pk Central | NCC Rating (A) | 441 | 441 | 441 | 441 | 441 | Urban | 70
|  |  |  | 10 POE Load (A) | 102 | 100 | 100 | 100 | 102
|  |  |  | Power Factor | 0.99805 | 0.98809 | 0.98811 | 0.9902 | 0.98992
|  |  |  | ECC Rating (A) | 441 | 441 | 441 | 441 | 441
|  |  |  | 50 POE Load (A) | 202 | 203 | 201 | 201 | 204
Goodna Bulk | 456-3 | 456 Tee1 | Carol Pk | NCC Rating (A) | 441 | 441 | 441 | 441 | 441 | Urban | 70
|  |  |  | 10 POE Load (A) | 102 | 100 | 100 | 101 | 102
|  |  |  | Power Factor | 0.99751 | 0.98675 | 0.98678 | 0.98899 | 0.98873
|  |  |  | ECC Rating (A) | 441 | 441 | 441 | 441 | 441
|  |  |  | 50 POE Load (A) | 203 | 203 | 202 | 201 | 204
Griffin Bulk | 312-1 | Kallangur | Narangba | NCC Rating (A) | 422 | 422 | 422 | 422 | 422 | Urban | 70 | 2.5
|  |  |  | 10 POE Load (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 1.4388e-05 | 1.4388e-05 | 1.4388e-05 | 1.4388e-05 | 1.4388e-05
|  |  |  | ECC Rating (A) | 422 | 422 | 422 | 422 | 422
|  |  |  | 50 POE Load (A) | 1 | 1 | 1 | 1 | 1
Griffin Bulk | 320-1 | Griffin BS | 320 Tee1 | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70 | 3.5
|  |  |  | 10 POE Load (A) | 412 | 401 | 399 | 439 | 437
|  |  |  | Power Factor | 0.98062 | 0.98143 | 0.9819 | 0.98283 | 0.98318
|  |  |  | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | 50 POE Load (A) | 579 | 564 | 558 | 648 | 649
Griffin Bulk | 320-2 | 320 Tee1 | Mango Hill Bus 2 | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 220
|  |  |  | 10 POE Load (A) | 325 | 315 | 306 | 291 | 279
|  |  |  | Power Factor | 0.99878 | 0.99903 | 0.99906 | 0.97631 | 0.9774
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | 50 POE Load (A) | 629 | 619 | 604 | 599 | 581
Griffin Bulk | 320-3 | 320 Tee1 | Kalangur | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 70
|  |  |  | 10 POE Load (A) | 89 | 89 | 96 | 165 | 174
|  |  |  | Power Factor | 0.9856 | 0.98559 | 0.98479 | 0.98577 | 0.9852
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | 50 POE Load (A) | 319 | 314 | 324 | 466 | 477
Griffin Bulk | 3329-1 | Griffin BS | 3329 Tee1 | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70
|  |  |  | 10 POE Load (A) | 439 | 429 | 433 | 520 | 526
|  |  |  | Power Factor | 0.97421 | 0.97493 | 0.97445 | 0.97008 | 0.96944
|  |  |  | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | 50 POE Load (A) | 508 | 497 | 501 | 597 | 607
Griffin Bulk | 3329-2 | 3329 Tee1 | 3330 Tee1 | NCC Rating (A) | 748 | 748 | 748 | 748 | 748 | Urban | 70
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 6.7996e-06 | 6.799e-06 | 6.7991e-06 | 6.7991e-06 | 6.7991e-06
|  |  |  | ECC Rating (A) | 748 | 748 | 748 | 748 | 748
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Griffin Bulk | 3329-3 | 3329 Tee1 | Kallangur | NCC Rating (A) | 711 | 711 | 711 | 711 | 711 | Urban | 70
|  |  |  | 10 POE Load (A) | 440 | 430 | 434 | 521 | 527
|  |  |  | Power Factor | 0.97528 | 0.97589 | 0.97545 | 0.97212 | 0.97154
|  |  |  | ECC Rating (A) | 711 | 711 | 711 | 711 | 711
|  |  |  | 50 POE Load (A) | 509 | 498 | 502 | 598 | 608
Griffin Bulk | 3330-1 | Griffin BS | 3330 Tee1 | NCC Rating (A) | 717 | 717 | 717 | 717 | 717 | Urban | 70
|  |  |  | 10 POE Load (A) | 224 | 219 | 221 | 292 | 294
|  |  |  | Power Factor | 0.98266 | 0.98322 | 0.98285 | 0.97657 | 0.97615
|  |  |  | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
|  |  |  | 50 POE Load (A) | 379 | 372 | 375 | 467 | 471
Griffin Bulk | 3330-2 | 3330 Tee1 | 3329 Tee1 | NCC Rating (A) | 523 | 523 | 523 | 523 | 523 | Urban | 70
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 2.797e-05 | 2.7978e-05 | 2.7962e-05 | 2.7965e-05 | 2.7962e-05
|  |  |  | ECC Rating (A) | 523 | 523 | 523 | 523 | 523
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Griffin Bulk | 3330-3 | 3330 Tee1 | APM | NCC Rating (A) | 717 | 717 | 717 | 717 | 717 | Urban | 70
|  |  |  | 10 POE Load (A) | 224 | 219 | 221 | 292 | 294
|  |  |  | Power Factor | 0.98387 | 0.98437 | 0.98402 | 0.97873 | 0.97836
|  |  |  | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
|  |  |  | 50 POE Load (A) | 380 | 372 | 375 | 468 | 471
Griffin Bulk | 3331-1 | 3331 Tee1 | Kallangur | NCC Rating (A) | 717 | 717 | 717 | 717 | 717 | Urban | 70
|  |  |  | 10 POE Load (A) | 187 | 182 | 184 | 186 | 188
|  |  |  | Power Factor | 0.9868 | 0.98734 | 0.98696 | 0.99941 | 0.99881
|  |  |  | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
|  |  |  | 50 POE Load (A) | 344 | 336 | 339 | 330 | 334
Griffin Bulk | 3331-3 | APM | 3331 Tee1 | NCC Rating (A) | 717 | 717 | 717 | 717 | 717 | Urban | 70
|  |  |  | 10 POE Load (A) | 224 | 219 | 221 | 223 | 225
|  |  |  | Power Factor | 0.98451 | 0.98498 | 0.98464 | 0.99396 | 0.99313
|  |  |  | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
|  |  |  | 50 POE Load (A) | 380 | 372 | 375 | 376 | 370
Griffin Bulk | 3359-1 | 3359 Tee1 | Hays Inlet | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 1.0501e-06 | 1.0507e-06 | 1.0518e-06 | 1.0507e-06 | 1.051e-06
|  |  |  | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Griffin Bulk | 3359-2 | 3359 Tee1 | 3359 Tee2 | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70
|  |  |  | 10 POE Load (A) | 333 | 324 | 318 | 332 | 325
|  |  |  | Power Factor | 0.93105 | 0.93286 | 0.93465 | 0.93111 | 0.93336
|  |  |  | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | 50 POE Load (A) | 624 | 607 | 591 | 595 | 578
Griffin Bulk | 3359-3 | 3359 Tee2 | 3359 Tee3 | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70
|  |  |  | 10 POE Load (A) | 333 | 324 | 318 | 332 | 325
|  |  |  | Power Factor | 0.93139 | 0.93319 | 0.93496 | 0.93145 | 0.93369
|  |  |  | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | 50 POE Load (A) | 624 | 607 | 591 | 595 | 578
Griffin Bulk | 3359-4 | 3359 Tee3 | Mango Hill Bus 2 | NCC Rating (A) | 762 | 762 | 762 | 762 | 762 | Urban | 70
|  |  |  | 10 POE Load (A) | 334 | 325 | 319 | 332 | 326
|  |  |  | Power Factor | 0.93254 | 0.93419 | 0.93587 | 0.93258 | 0.93471
|  |  |  | ECC Rating (A) | 762 | 762 | 762 | 762 | 762
|  |  |  | 50 POE Load (A) | 625 | 608 | 592 | 595 | 578
Griffin Bulk | 3359-5 | 3359 Tee2 | P51001-D | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 70
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 6.7088e-06 | 6.7087e-06 | 6.7088e-06 | 6.7086e-06 | 6.7088e-06
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Griffin Bulk | 3359-6 | 3359 Tee3 | X18574-E | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 70
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 3.3931e-06 | 3.3931e-06 | 3.3931e-06 | 3.3931e-06 | 3.3931e-06
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Griffin Bulk | 3359-7 | Griffin BS | 3359 Tee1 | NCC Rating (A) | 703 | 703 | 703 | 703 | 703 | Urban | 70
|  |  |  | 10 POE Load (A) | 333 | 324 | 318 | 332 | 325
|  |  |  | Power Factor | 0.92399 | 0.9261 | 0.92807 | 0.92409 | 0.92659
|  |  |  | ECC Rating (A) | 703 | 703 | 703 | 703 | 703
|  |  |  | 50 POE Load (A) | 624 | 607 | 591 | 595 | 578
Griffin Bulk | 338-1 | Griffin BS | Strathpine | NCC Rating (A) | 348 | 348 | 348 | 348 | 348 | Urban | 70
|  |  |  | 10 POE Load (A) | 2 | 2 | 2 | 2 | 2
|  |  |  | Power Factor | 0.00011716 | 0.00011716 | 0.00011716 | 0.00011716 | 0.00011716
|  |  |  | ECC Rating (A) | 348 | 348 | 348 | 348 | 348
|  |  |  | 50 POE Load (A) | 2 | 2 | 2 | 2 | 2
Gympie Bulk | 3004-1 | Coondoo Ck Reg | Tin Can Bay | NCC Rating (A) | 127 | 127 | 127 | 127 | 127 | Rural | 170
|  |  |  | 10 POE Load (A) | 87 | 86 | 85 | 83 | 82
|  |  |  | Power Factor | 0.98634 | 0.98652 | 0.9867 | 0.98688 | 0.98706
|  |  |  | ECC Rating (A) | 127 | 127 | 127 | 127 | 127
|  |  |  | 50 POE Load (A) | 156 | 121 | 121 | 116 | 112
Gympie Bulk | 3005-1 | Coondoo Ck Reg | Tin Can Bay | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170
|  |  |  | 10 POE Load (A) | 83 | 82 | 81 | 80 | 79
|  |  |  | Power Factor | 0.98781 | 0.98792 | 0.98802 | 0.98813 | 0.98823
|  |  |  | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
|  |  |  | 50 POE Load (A) | 130 | 109 | 109 | 105 | 102
Gympie Bulk | 3009-1 | Gympie BS | Gympie Nth | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70
|  |  |  | 10 POE Load (A) | 160 | 158 | 156 | 154 | 153
|  |  |  | Power Factor | 0.98633 | 0.98618 | 0.98633 | 0.98649 | 0.98657
|  |  |  | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | 50 POE Load (A) | 271 | 266 | 264 | 260 | 259
Gympie Bulk | 3011-1 | Gympie BS | Gympie Nth | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70
|  |  |  | 10 POE Load (A) | 160 | 158 | 156 | 154 | 153
|  |  |  | Power Factor | 0.98632 | 0.98616 | 0.98632 | 0.98647 | 0.98655
|  |  |  | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | 50 POE Load (A) | 271 | 266 | 264 | 260 | 259
Gympie Bulk | 339/2-1 | Amamoor | 339 Tee1 | NCC Rating (A) | 155 | 155 | 403 | 403 | 403 | Rural | 170
|  |  |  | 10 POE Load (A) | 58 | 56 | 56 | 54 | 54
|  |  |  | Power Factor | 0.98409 | 0.98594 | 0.98605 | 0.98814 | 0.98814
|  |  |  | ECC Rating (A) | 155 | 155 | 403 | 403 | 403
|  |  |  | 50 POE Load (A) | 54 | 54 | 54 | 52 | 52
Gympie Bulk | 339/2-2 | 339 Tee1 | Imbil | NCC Rating (A) | 200 | 200 | 200 | 200 | 200 | Rural | 170
|  |  |  | 10 POE Load (A) | 46 | 44 | 44 | 42 | 42
|  |  |  | Power Factor | 0.9939 | 0.99549 | 0.99549 | 0.99711 | 0.99711
|  |  |  | ECC Rating (A) | 200 | 200 | 200 | 200 | 200
|  |  |  | 50 POE Load (A) | 42 | 42 | 42 | 40 | 40
Gympie Bulk | 339/2-5 | 339 Tee2 | 340 Tee2 | NCC Rating (A) | 155 | 155 | 403 | 403 | 403 | Rural | 170
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 3.5511e-06 | 3.5512e-06 | 2.4497e-06 | 2.4497e-06 | 2.4497e-06
|  |  |  | ECC Rating (A) | 155 | 155 | 403 | 403 | 403
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Gympie Bulk | 339-1 | Gympie BS | 339 Tee1 | NCC Rating (A) | 210 | 210 | 210 | 210 | 210 | Rural | 170 | 6
|  |  |  | 10 POE Load (A) | 155 | 151 | 149 | 149 | 146
|  |  |  | Power Factor | 0.9713 | 0.97173 | 0.97479 | 0.97479 | 0.97523
|  |  |  | ECC Rating (A) | 210 | 210 | 210 | 210 | 210
|  |  |  | 50 POE Load (A) | 145 | 149 | 148 | 146 | 146
Gympie Bulk | 339-2 | 339 Tee1 | Amamoor | NCC Rating (A) | 210 | 210 | 210 | 210 | 210 | Rural | 170
|  |  |  | 10 POE Load (A) | 155 | 151 | 149 | 149 | 147
|  |  |  | Power Factor | 0.97205 | 0.97244 | 0.97546 | 0.97546 | 0.97588
|  |  |  | ECC Rating (A) | 210 | 210 | 210 | 210 | 210
|  |  |  | 50 POE Load (A) | 145 | 149 | 149 | 147 | 147
Gympie Bulk | 339-3 | 339 Tee1 | 340 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0.00059379 | 0.00059231 | 0.00059413 | 0.00059183 | 0.00059183
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Gympie Bulk | 340-1 | Gympie BS | 340 Tee1 | NCC Rating (A) | 349 | 349 | 349 | 349 | 349 | Rural | 170
|  |  |  | 10 POE Load (A) | 62 | 72 | 71 | 69 | 69
|  |  |  | Power Factor | 0.96021 | 0.95607 | 0.95641 | 0.9571 | 0.9571
|  |  |  | ECC Rating (A) | 349 | 349 | 349 | 349 | 349
|  |  |  | 50 POE Load (A) | 128 | 149 | 148 | 146 | 144
Gympie Bulk | 340-2 | 340 Tee1 | 339 Tee1 | NCC Rating (A) | 349 | 349 | 349 | 349 | 349 | Rural | 170
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0.00010589 | 0.00010578 | 0.00010583 | 0.00010577 | 0.0001057
|  |  |  | ECC Rating (A) | 349 | 349 | 349 | 349 | 349
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Gympie Bulk | 340-4 | 340 Tee1 | 340 Tee2 | NCC Rating (A) | 349 | 349 | 349 | 349 | 349 | Rural | 170
|  |  |  | 10 POE Load (A) | 62 | 72 | 71 | 69 | 69
|  |  |  | Power Factor | 0.95967 | 0.95581 | 0.95613 | 0.95677 | 0.95677
|  |  |  | ECC Rating (A) | 349 | 349 | 349 | 349 | 349
|  |  |  | 50 POE Load (A) | 128 | 149 | 148 | 146 | 144
Gympie Bulk | 340-5 | 340 Tee2 | 340 Tee3 | NCC Rating (A) | 328 | 328 | 328 | 328 | 328 | Rural | 170
|  |  |  | 10 POE Load (A) | 3 | 3 | 3 | 3 | 3
|  |  |  | Power Factor | 0.00072412 | 0.00072412 | 0.00072412 | 0.00072412 | 0.00072412
|  |  |  | ECC Rating (A) | 328 | 328 | 328 | 328 | 328
|  |  |  | 50 POE Load (A) | 3 | 3 | 3 | 3 | 3
Gympie Bulk | 340-6 | 340 Tee3 | 339 Tee2 | NCC Rating (A) | 208 | 208 | 208 | 208 | 208 | Rural | 170
|  |  |  | 10 POE Load (A) | 2 | 2 | 2 | 2 | 2
|  |  |  | Power Factor | 0.00013902 | 0.00013902 | 0.00013902 | 0.00013902 | 0.00013902
|  |  |  | ECC Rating (A) | 208 | 208 | 208 | 208 | 208
|  |  |  | 50 POE Load (A) | 2 | 2 | 2 | 2 | 2
Gympie Bulk | 340-7 | 339 Tee2 | Kenilworth | NCC Rating (A) | 208 | 208 | 208 | 208 | 208 | Rural | 170
|  |  |  | 10 POE Load (A) | 2 | 2 | 2 | 2 | 2
|  |  |  | Power Factor | 0.00013861 | 0.00013861 | 0.00013861 | 0.00013861 | 0.00013861
|  |  |  | ECC Rating (A) | 208 | 208 | 208 | 208 | 208
|  |  |  | 50 POE Load (A) | 2 | 2 | 2 | 2 | 2
Gympie Bulk | 340-8 | 340 Tee3 | Black Mountain | NCC Rating (A) | 328 | 328 | 328 | 328 | 328 | Rural | 170
|  |  |  | 10 POE Load (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 1.7204e-05 | 1.7204e-05 | 1.7204e-05 | 1.7204e-05 | 1.7204e-05
|  |  |  | ECC Rating (A) | 328 | 328 | 328 | 328 | 328
|  |  |  | 50 POE Load (A) | 1 | 1 | 1 | 1 | 1
Gympie Bulk | 340-9 | 340 Tee2 | Gympie South | NCC Rating (A) | 403 | 403 | 403 | 403 | 403 | Rural | 170
|  |  |  | 10 POE Load (A) | 63 | 73 | 72 | 70 | 70
|  |  |  | Power Factor | 0.9437 | 0.94172 | 0.9419 | 0.94226 | 0.94226
|  |  |  | ECC Rating (A) | 403 | 403 | 403 | 403 | 403
|  |  |  | 50 POE Load (A) | 129 | 150 | 149 | 147 | 145
Gympie Bulk | 341-1 | Gympie BS | 341 Tee1 | NCC Rating (A) | 211 | 211 | 211 | 211 | 211 | Rural | 170 | 6
|  |  |  | 10 POE Load (A) | 213 | 212 | 211 | 209 | 208
|  |  |  | Power Factor | 0.98942 | 0.98958 | 0.98973 | 0.9899 | 0.99005
|  |  |  | ECC Rating (A) | 211 | 211 | 211 | 211 | 211
|  |  |  | 50 POE Load (A) | 461 | 461 | 461 | 461 | 461
Gympie Bulk | 341-3 | 341 Tee1 | Coondoo Ck Reg | NCC Rating (A) | 210 | 210 | 210 | 210 | 210 | Rural | 170
|  |  |  | 10 POE Load (A) | 178 | 176 | 173 | 171 | 169
|  |  |  | Power Factor | 0.98524 | 0.98546 | 0.98567 | 0.98589 | 0.9861
|  |  |  | ECC Rating (A) | 210 | 210 | 210 | 210 | 210
|  |  |  | 50 POE Load (A) | 461 | 461 | 461 | 461 | 461
Gympie Bulk | 341-4 | Coondoo Ck Reg | 341 Tee2 | NCC Rating (A) | 717 | 717 | 717 | 717 | 717 | Rural | 170
|  |  |  | 10 POE Load (A) | 169 | 167 | 165 | 163 | 161
|  |  |  | Power Factor | 0.98561 | 0.98582 | 0.98603 | 0.98624 | 0.98645
|  |  |  | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
|  |  |  | 50 POE Load (A) | 286 | 230 | 230 | 221 | 214
Gympie Bulk | 351-1 | Gympie BS | Gympie Sth | NCC Rating (A) | 355 | 355 | 355 | 355 | 355 | Rural | 170
|  |  |  | 10 POE Load (A) | 71 | 82 | 81 | 79 | 79
|  |  |  | Power Factor | 0.95497 | 0.95081 | 0.95116 | 0.95184 | 0.95184
|  |  |  | ECC Rating (A) | 355 | 355 | 355 | 355 | 355
|  |  |  | 50 POE Load (A) | 129 | 150 | 148 | 147 | 145
Gympie Bulk | 429-1 | Gympie BS | 429 Tee1 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
|  |  |  | 10 POE Load (A) | 295 | 294 | 293 | 290 | 288
|  |  |  | Power Factor | 0.93991 | 0.94026 | 0.94061 | 0.94084 | 0.94119
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 322 | 320 | 320 | 320 | 320
Gympie Bulk | 429-2 | 429 Tee1 | Goomboorian | NCC Rating (A) | 461 | 461 | 461 | 461 | 461 | Rural | 170
|  |  |  | 10 POE Load (A) | 54 | 54 | 54 | 52 | 52
|  |  |  | Power Factor | 0.99514 | 0.99514 | 0.99515 | 0.99526 | 0.99526
|  |  |  | ECC Rating (A) | 461 | 461 | 461 | 461 | 461
|  |  |  | 50 POE Load (A) | 50 | 48 | 48 | 48 | 48
Hays Inlet Bulk | 305-1 | Hays Inlet BS | Deception Bay | NCC Rating (A) | 759 | 759 | 759 | 759 | 759 | Urban | 430
|  |  |  | 10 POE Load (A) | 743 | 733 | 731 | 728 | 729
|  |  |  | Power Factor | 0.97363 | 0.97412 | 0.97416 | 0.9743 | 0.97415
|  |  |  | ECC Rating (A) | 759 | 759 | 759 | 759 | 759
|  |  |  | 50 POE Load (A) | 1120 | 1106 | 1107 | 1103 | 1111
Hays Inlet Bulk | 311-1 | Hays Inlet BS | Deception Bay | NCC Rating (A) | 623 | 623 | 623 | 623 | 623 | Urban | 210 | 3
|  |  |  | 10 POE Load (A) | 246 | 243 | 242 | 241 | 241
|  |  |  | Power Factor | 0.98356 | 0.98394 | 0.98397 | 0.98408 | 0.98396
|  |  |  | ECC Rating (A) | 623 | 623 | 623 | 623 | 623
|  |  |  | 50 POE Load (A) | 787 | 775 | 774 | 768 | 771
Hays Inlet Bulk | 3250-1 | Deception Bay | Burpengary | NCC Rating (A) | 713 | 713 | 713 | 713 | 713 | Urban | 430
|  |  |  | 10 POE Load (A) | 467 | 464 | 466 | 466 | 470
|  |  |  | Power Factor | 0.98093 | 0.98111 | 0.981 | 0.98094 | 0.98065
|  |  |  | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
|  |  |  | 50 POE Load (A) | 1001 | 994 | 997 | 999 | 1012
Hays Inlet Bulk | 325-1 | Hays Inlet BS | Scarborough | NCC Rating (A) | 529 | 529 | 529 | 529 | 529 | Urban | 70
|  |  |  | 10 POE Load (A) | 313 | 312 | 312 | 328 | 348
|  |  |  | Power Factor | 0.99336 | 0.99343 | 0.99348 | 0.9923 | 0.99082
|  |  |  | ECC Rating (A) | 529 | 529 | 529 | 529 | 529
|  |  |  | 50 POE Load (A) | 418 | 417 | 417 | 443 | 474
Hays Inlet Bulk | 3251-1 | Burpengary | Morayfield | NCC Rating (A) | 464 | 464 | 464 | 464 | 464 | Urban | 120 | 2
|  |  |  | 10 POE Load (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 1.0517e-05 | 1.0517e-05 | 1.0517e-05 | 1.0517e-05 | 1.0517e-05
|  |  |  | ECC Rating (A) | 464 | 464 | 464 | 464 | 464
|  |  |  | 50 POE Load (A) | 663 | 655 | 650 | 643 | 644
Hays Inlet Bulk | 326-1 | Redcliffe | Scarborough | NCC Rating (A) | 322 | 322 | 322 | 322 | 322 | Urban | 70
|  |  |  | 10 POE Load (A) | 51 | 52 | 54 | 39 | 27
|  |  |  | Power Factor | 0.99267 | 0.99345 | 0.99449 | 0.96826 | 0.84156
|  |  |  | ECC Rating (A) | 322 | 322 | 322 | 322 | 322
|  |  |  | 50 POE Load (A) | 348 | 348 | 350 | 351 | 355
Hays Inlet Bulk | 327-1 | Hays Inlet BS | Mango Hill Bus 1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
|  |  |  | 10 POE Load (A) | 403 | 399 | 399 | 395 | 399
|  |  |  | Power Factor | 0.98008 | 0.98045 | 0.98045 | 0.98082 | 0.98045
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 374 | 371 | 369 | 367 | 369
Hays Inlet Bulk | 329-1 | Redcliffe | Duffield Rd | NCC Rating (A) | 578 | 578 | 578 | 578 | 578 | Urban | 70
|  |  |  | 10 POE Load (A) | 112 | 112 | 113 | 136 | 163
|  |  |  | Power Factor | 0.99088 | 0.99096 | 0.99079 | 0.98548 | 0.97936
|  |  |  | ECC Rating (A) | 578 | 578 | 578 | 578 | 578
|  |  |  | 50 POE Load (A) | 260 | 258 | 258 | 296 | 336
Hays Inlet Bulk | 330-1 | Hays Inlet BS | Duffield Rd | NCC Rating (A) | 543 | 543 | 543 | 543 | 543 | Urban | 70
|  |  |  | 10 POE Load (A) | 270 | 269 | 268 | 278 | 290
|  |  |  | Power Factor | 0.98776 | 0.98787 | 0.98793 | 0.98713 | 0.98602
|  |  |  | ECC Rating (A) | 543 | 543 | 543 | 543 | 543
|  |  |  | 50 POE Load (A) | 407 | 404 | 403 | 418 | 439
Hays Inlet Bulk | 331-1 | Hays Inlet BS | Duffield Rd | NCC Rating (A) | 543 | 543 | 543 | 543 | 543 | Urban | 70
|  |  |  | 10 POE Load (A) | 272 | 270 | 269 | 279 | 291
|  |  |  | Power Factor | 0.98507 | 0.98519 | 0.98526 | 0.98437 | 0.98315
|  |  |  | ECC Rating (A) | 543 | 543 | 543 | 543 | 543
|  |  |  | 50 POE Load (A) | 408 | 405 | 404 | 419 | 440
Hays Inlet Bulk | 332-1 | Hays Inlet BS | Redcliffe | NCC Rating (A) | 524 | 524 | 524 | 524 | 524 | Urban | 70
|  |  |  | 10 POE Load (A) | 288 | 287 | 286 | 307 | 331
|  |  |  | Power Factor | 0.97848 | 0.97862 | 0.97871 | 0.97646 | 0.9737
|  |  |  | ECC Rating (A) | 524 | 524 | 524 | 524 | 524
|  |  |  | 50 POE Load (A) | 425 | 423 | 422 | 452 | 487
Hays Inlet Bulk | 451-1 | Narangba | Burpengary | NCC Rating (A) | 422 | 422 | 422 | 422 | 422 | Urban | 385
|  |  |  | 10 POE Load (A) | 18 | 15 | 12 | 8 | 6
|  |  |  | Power Factor | 0.96384 | 0.96509 | 0.96765 | 0.97347 | 0.43106
|  |  |  | ECC Rating (A) | 422 | 422 | 422 | 422 | 422
|  |  |  | 50 POE Load (A) | 523 | 523 | 527 | 533 | 533
Hays Inlet Bulk | 497-1 | Hays Inlet BS | Narangba | NCC Rating (A) | 713 | 713 | 713 | 713 | 713 | Urban | 385
|  |  |  | 10 POE Load (A) | 535 | 532 | 534 | 536 | 541
|  |  |  | Power Factor | 0.97273 | 0.97295 | 0.97277 | 0.97264 | 0.97219
|  |  |  | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
|  |  |  | 50 POE Load (A) | 991 | 984 | 986 | 988 | 1001
Jimboomba Bulk | 470-1 | Jimboomba BS | Logan Village | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Rural | 170
|  |  |  | 10 POE Load (A) | 464 | 470 | 478 | 478 | 482
|  |  |  | Power Factor | 0.97812 | 0.97747 | 0.97658 | 0.97658 | 0.9775
|  |  |  | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
|  |  |  | 50 POE Load (A) | 421 | 424 | 430 | 430 | 434
Jimboomba Bulk | 479-1 | Jimboomba BS | Nth Maclean | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 773 | 761 | 759 | 773 | 788
|  |  |  | Power Factor | 0.9674 | 0.97162 | 0.97178 | 0.9674 | 0.96637
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 668 | 660 | 658 | 668 | 680
Lockrose Bulk | 378-1 | Lockrose BS | 378 Tee1 | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
|  |  |  | 10 POE Load (A) | 158 | 157 | 182 | 179 | 179
|  |  |  | Power Factor | 0.98305 | 0.9836 | 0.97515 | 0.97854 | 0.97854
|  |  |  | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | 50 POE Load (A) | 269 | 268 | 322 | 318 | 318
Lockrose Bulk | 378-2 | 378 Tee1 | Glenmore Grove | NCC Rating (A) | 442 | 442 | 442 | 442 | 442 | Rural | 170
|  |  |  | 10 POE Load (A) | 42 | 44 | 44 | 43 | 43
|  |  |  | Power Factor | 0.99956 | 0.99953 | 0.99955 | 0.99953 | 0.99953
|  |  |  | ECC Rating (A) | 442 | 442 | 442 | 442 | 442
|  |  |  | 50 POE Load (A) | 41 | 42 | 43 | 42 | 42
Lockrose Bulk | 378-3 | 378 Tee1 | 378 Tee2 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 116 | 114 | 139 | 137 | 137
|  |  |  | Power Factor | 0.97566 | 0.9761 | 0.96585 | 0.97099 | 0.97099
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 228 | 226 | 280 | 277 | 277
Lockrose Bulk | 378-4 | 378 Tee2 | 532 Tee1 | NCC Rating (A) | 200 | 200 | 200 | 200 | 200 | Rural | 170
|  |  |  | 10 POE Load (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 6.0726e-05 | 6.0726e-05 | 6.0726e-05 | 6.0726e-05 | 6.0726e-05
|  |  |  | ECC Rating (A) | 200 | 200 | 200 | 200 | 200
|  |  |  | 50 POE Load (A) | 1 | 1 | 1 | 1 | 1
Lockrose Bulk | 378-5 | 378 Tee2 | Laidley | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 116 | 114 | 140 | 137 | 137
|  |  |  | Power Factor | 0.97872 | 0.97898 | 0.97155 | 0.97613 | 0.97613
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 229 | 227 | 280 | 277 | 277
Lockrose Bulk | 380-1 | Murrumba | 380 Tee1 | NCC Rating (A) | 200 | 200 | 200 | 200 | 200 | Rural | 170
|  |  |  | 10 POE Load (A) | 54 | 52 | 53 | 47 | 47
|  |  |  | Power Factor | 0.99627 | 0.99653 | 0.96711 | 0.99733 | 0.99733
|  |  |  | ECC Rating (A) | 200 | 200 | 200 | 200 | 200
|  |  |  | 50 POE Load (A) | 154 | 156 | 153 | 151 | 151
Lockrose Bulk | 380-2 | 380 Tee1 | Somerset Dam | NCC Rating (A) | 160 | 160 | 160 | 160 | 160 | Rural | 170
|  |  |  | 10 POE Load (A) | 7 | 7 | 7 | 7 | 7
|  |  |  | Power Factor | 0.99703 | 0.99704 | 0.99704 | 0.99704 | 0.99704
|  |  |  | ECC Rating (A) | 160 | 160 | 160 | 160 | 160
|  |  |  | 50 POE Load (A) | 8 | 7 | 8 | 7 | 7
Lockrose Bulk | 380-3 | 380 Tee1 | Toogoolahwah | NCC Rating (A) | 200 | 200 | 200 | 200 | 200 | Rural | 170
|  |  |  | 10 POE Load (A) | 47 | 45 | 47 | 40 | 40
|  |  |  | Power Factor | 0.99491 | 0.99503 | 0.95553 | 0.99562 | 0.99562
|  |  |  | ECC Rating (A) | 200 | 200 | 200 | 200 | 200
|  |  |  | 50 POE Load (A) | 147 | 149 | 146 | 145 | 145
Lockrose Bulk | 381-1 | Lockrose BS | 381 Tee1 | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
|  |  |  | 10 POE Load (A) | 168 | 166 | 167 | 167 | 165
|  |  |  | Power Factor | 0.9665 | 0.96698 | 0.95305 | 0.95315 | 0.95331
|  |  |  | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | 50 POE Load (A) | 313 | 308 | 309 | 305 | 305
Lockrose Bulk | 381-2 | 381 Tee1 | 382 Tee1 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 3.3487e-05 | 3.348e-05 | 3.3482e-05 | 3.3488e-05 | 3.3481e-05
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lockrose Bulk | 381-3 | 381 Tee1 | 381 Tee2 | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
|  |  |  | 10 POE Load (A) | 168 | 166 | 167 | 167 | 165
|  |  |  | Power Factor | 0.97007 | 0.97047 | 0.95697 | 0.95705 | 0.95717
|  |  |  | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | 50 POE Load (A) | 313 | 308 | 309 | 306 | 306
Lockrose Bulk | 381-4 | 381 Tee2 | 383 Tee1 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 3.386e-05 | 3.3873e-05 | 3.3868e-05 | 3.387e-05 | 3.3875e-05
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lockrose Bulk | 381-5 | 381 Tee2 | 381 Tee3 | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
|  |  |  | 10 POE Load (A) | 168 | 166 | 167 | 167 | 165
|  |  |  | Power Factor | 0.97075 | 0.97115 | 0.95774 | 0.95782 | 0.95792
|  |  |  | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | 50 POE Load (A) | 313 | 309 | 309 | 306 | 306
Lockrose Bulk | 381-6 | 381 Tee3 | Coominya TR2 | NCC Rating (A) | 403 | 403 | 403 | 403 | 403 | Rural | 170
|  |  |  | 10 POE Load (A) | 54 | 54 | 53 | 53 | 52
|  |  |  | Power Factor | 0.97115 | 0.97116 | 0.97146 | 0.97146 | 0.9716
|  |  |  | ECC Rating (A) | 403 | 403 | 403 | 403 | 403
|  |  |  | 50 POE Load (A) | 54 | 53 | 53 | 52 | 52
Lockrose Bulk | 381-7 | 381 Tee3 | 381 Tee4 | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
|  |  |  | 10 POE Load (A) | 114 | 112 | 114 | 114 | 113
|  |  |  | Power Factor | 0.97952 | 0.97993 | 0.96155 | 0.96161 | 0.96162
|  |  |  | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | 50 POE Load (A) | 259 | 256 | 256 | 254 | 254
Lockrose Bulk | 381-8 | 381 Tee4 | Coominya TR1 | NCC Rating (A) | 403 | 403 | 403 | 403 | 403 | Rural | 170
|  |  |  | 10 POE Load (A) | 54 | 54 | 53 | 53 | 52
|  |  |  | Power Factor | 0.97083 | 0.97084 | 0.97107 | 0.97091 | 0.97102
|  |  |  | ECC Rating (A) | 403 | 403 | 403 | 403 | 403
|  |  |  | 50 POE Load (A) | 54 | 53 | 53 | 52 | 52
Lockrose Bulk | 381-9 | 381 Tee4 | Paddys Gully | NCC Rating (A) | 155 | 155 | 155 | 155 | 155 | Rural | 170
|  |  |  | 10 POE Load (A) | 60 | 58 | 61 | 61 | 61
|  |  |  | Power Factor | 0.98606 | 0.98687 | 0.95219 | 0.95242 | 0.95257
|  |  |  | ECC Rating (A) | 155 | 155 | 155 | 155 | 155
|  |  |  | 50 POE Load (A) | 205 | 203 | 203 | 201 | 201
Lockrose Bulk | 382-1 | Lockrose BS | 382 Tee1 | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
|  |  |  | 10 POE Load (A) | 145 | 143 | 145 | 145 | 144
|  |  |  | Power Factor | 0.97789 | 0.97844 | 0.9613 | 0.96143 | 0.96155
|  |  |  | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | 50 POE Load (A) | 191 | 189 | 188 | 187 | 187
Lockrose Bulk | 382-2 | 382 Tee1 | 381 Tee1 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 1.9422e-05 | 1.9423e-05 | 1.942e-05 | 1.9425e-05 | 1.9423e-05
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lockrose Bulk | 382-3 | 382 Tee1 | Paddys Gully | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
|  |  |  | 10 POE Load (A) | 146 | 143 | 146 | 145 | 145
|  |  |  | Power Factor | 0.98748 | 0.98771 | 0.97335 | 0.97341 | 0.97344
|  |  |  | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | 50 POE Load (A) | 191 | 189 | 188 | 187 | 187
Lockrose Bulk | 3828-1 | Paddy's Gully | Esk | NCC Rating (A) | 154 | 154 | 154 | 154 | 154 | Rural | 170
|  |  |  | 10 POE Load (A) | 106 | 102 | 105 | 111 | 111
|  |  |  | Power Factor | 0.99115 | 0.99166 | 0.97632 | 0.95617 | 0.95619
|  |  |  | ECC Rating (A) | 154 | 154 | 154 | 154 | 154
|  |  |  | 50 POE Load (A) | 182 | 180 | 177 | 171 | 171
Lockrose Bulk | 3829-1 | Paddy's Gully | Murrumba | NCC Rating (A) | 155 | 155 | 155 | 155 | 155 | Rural | 170 | 2
|  |  |  | 10 POE Load (A) | 86 | 84 | 86 | 79 | 79
|  |  |  | Power Factor | 0.98194 | 0.98221 | 0.95685 | 0.98225 | 0.98226
|  |  |  | ECC Rating (A) | 155 | 155 | 155 | 155 | 155
|  |  |  | 50 POE Load (A) | 185 | 185 | 182 | 181 | 181
Lockrose Bulk | 3831-1 | Lockrose BS | Tarampa | NCC Rating (A) | 355 | 355 | 355 | 355 | 355 | Rural | 170
|  |  |  | 10 POE Load (A) | 149 | 147 | 145 | 145 | 143
|  |  |  | Power Factor | 0.96941 | 0.96964 | 0.96986 | 0.96986 | 0.96997
|  |  |  | ECC Rating (A) | 355 | 355 | 355 | 355 | 355
|  |  |  | 50 POE Load (A) | 136 | 134 | 134 | 132 | 132
Lockrose Bulk | 3832-1 | Tarampa | 3832 Tee1 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 3.7176e-05 | 3.7184e-05 | 3.7171e-05 | 3.7183e-05 | 3.7183e-05
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lockrose Bulk | 3832-3 | 3832 Tee1 | Lowood | NCC Rating (A) | 434 | 434 | 434 | 434 | 434 | Rural | 170
|  |  |  | 10 POE Load (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 5.5524e-06 | 5.5523e-06 | 5.5523e-06 | 5.5522e-06 | 5.5524e-06
|  |  |  | ECC Rating (A) | 434 | 434 | 434 | 434 | 434
|  |  |  | 50 POE Load (A) | 1 | 1 | 1 | 1 | 1
Lockrose Bulk | 3840-1 | Esk | Toogoolawah | NCC Rating (A) | 155 | 155 | 155 | 713 | 713 | Rural | 170
|  |  |  | 10 POE Load (A) | 44 | 42 | 45 | 52 | 52
|  |  |  | Power Factor | 0.99855 | 0.99861 | 0.96468 | 0.90972 | 0.90974
|  |  |  | ECC Rating (A) | 155 | 155 | 155 | 713 | 713
|  |  |  | 50 POE Load (A) | 127 | 125 | 124 | 118 | 118
Lockrose Bulk | 384-1 | Lockrose BS | 384 Tee1 | NCC Rating (A) | 451 | 451 | 451 | 451 | 451 | Rural | 170
|  |  |  | 10 POE Load (A) | 164 | 164 | 190 | 187 | 187
|  |  |  | Power Factor | 0.997 | 0.99712 | 0.9937 | 0.99534 | 0.99534
|  |  |  | ECC Rating (A) | 451 | 451 | 451 | 451 | 451
|  |  |  | 50 POE Load (A) | 272 | 271 | 326 | 322 | 322
Lockrose Bulk | 384-2 | 384 Tee1 | Glenmore Grove | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
|  |  |  | 10 POE Load (A) | 42 | 44 | 44 | 43 | 43
|  |  |  | Power Factor | 0.99963 | 0.9996 | 0.9996 | 0.99961 | 0.99961
|  |  |  | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | 50 POE Load (A) | 41 | 42 | 43 | 42 | 42
Lockrose Bulk | 384-3 | 384 Tee1 | Laidley1 | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Rural | 170
|  |  |  | 10 POE Load (A) | 122 | 120 | 146 | 144 | 144
|  |  |  | Power Factor | 0.99881 | 0.99887 | 0.99664 | 0.99808 | 0.99808
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | 50 POE Load (A) | 231 | 229 | 284 | 281 | 281
Lockrose Bulk | 3870-1 | Lockrose BS | Lowood | NCC Rating (A) | 703 | 703 | 703 | 703 | 703 | Rural | 170
|  |  |  | 10 POE Load (A) | 187 | 183 | 182 | 180 | 180
|  |  |  | Power Factor | 0.98091 | 0.98114 | 0.98133 | 0.9815 | 0.9815
|  |  |  | ECC Rating (A) | 703 | 703 | 703 | 703 | 703
|  |  |  | 50 POE Load (A) | 170 | 166 | 166 | 164 | 164
Lockrose Bulk | 3871-1 | Lowood | Wivenhoe | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
|  |  |  | 10 POE Load (A) | 130 | 128 | 128 | 126 | 126
|  |  |  | Power Factor | 0.98549 | 0.9855 | 0.98551 | 0.98567 | 0.98567
|  |  |  | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | 50 POE Load (A) | 118 | 116 | 116 | 116 | 116
Loganlea Bulk | 407-1 | Loganlea BS | Woodridge | NCC Rating (A) | 777 | 777 | 777 | 777 | 777 | Urban | 70
|  |  |  | 10 POE Load (A) | 330 | 325 | 321 | 315 | 314
|  |  |  | Power Factor | 0.99054 | 0.99086 | 0.99107 | 0.99138 | 0.99143
|  |  |  | ECC Rating (A) | 777 | 777 | 777 | 777 | 777
|  |  |  | 50 POE Load (A) | 580 | 569 | 564 | 562 | 558
Loganlea Bulk | 408-1 | Loganlea BS | Kingston | NCC Rating (A) | 529 | 529 | 529 | 529 | 529 | Urban | 280
|  |  |  | 10 POE Load (A) | 371 | 362 | 363 | 364 | 368
|  |  |  | Power Factor | 0.96262 | 0.96361 | 0.96349 | 0.96337 | 0.96299
|  |  |  | ECC Rating (A) | 529 | 529 | 529 | 529 | 529
|  |  |  | 50 POE Load (A) | 649 | 634 | 636 | 636 | 642
Loganlea Bulk | 409-1 | Loganlea BS | Woodridge | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
|  |  |  | 10 POE Load (A) | 295 | 290 | 287 | 281 | 281
|  |  |  | Power Factor | 0.99297 | 0.99322 | 0.9934 | 0.99365 | 0.99369
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 582 | 571 | 566 | 564 | 560
Loganlea Bulk | 418-1 | Loganlea BS | Tanah Merah | NCC Rating (A) | 631 | 631 | 631 | 631 | 631 | Urban | 70
|  |  |  | 10 POE Load (A) | 323 | 316 | 312 | 309 | 307
|  |  |  | Power Factor | 0.98821 | 0.98847 | 0.98861 | 0.98873 | 0.9888
|  |  |  | ECC Rating (A) | 631 | 631 | 631 | 631 | 631
|  |  |  | 50 POE Load (A) | 305 | 298 | 294 | 291 | 289
Loganlea Bulk | 452-1 | Loganlea BS | Kingston | NCC Rating (A) | 510 | 510 | 510 | 510 | 510 | Urban | 280
|  |  |  | 10 POE Load (A) | 301 | 294 | 295 | 296 | 298
|  |  |  | Power Factor | 0.96912 | 0.96999 | 0.96988 | 0.96977 | 0.96945
|  |  |  | ECC Rating (A) | 510 | 510 | 510 | 510 | 510
|  |  |  | 50 POE Load (A) | 653 | 637 | 639 | 639 | 645
Lytton Bulk | 3302-1 | Lytton BS | Fisherman Is B | NCC Rating (A) | 650 | 650 | 650 | 650 | 650 | Urban | 70
|  |  |  | 10 POE Load (A) | 210 | 298 | 329 | 343 | 342
|  |  |  | Power Factor | 0.92698 | 0.93389 | 0.93384 | 0.93408 | 0.93411
|  |  |  | ECC Rating (A) | 650 | 650 | 650 | 650 | 650
|  |  |  | 50 POE Load (A) | 412 | 593 | 657 | 690 | 686
Lytton Bulk | 3303-1 | Lytton BS | Fisherman Is B | NCC Rating (A) | 600 | 600 | 600 | 600 | 600 | Urban | 70 | 18.5
|  |  |  | 10 POE Load (A) | 210 | 297 | 328 | 342 | 341
|  |  |  | Power Factor | 0.92693 | 0.93385 | 0.9338 | 0.93404 | 0.93407
|  |  |  | ECC Rating (A) | 600 | 600 | 600 | 600 | 600
|  |  |  | 50 POE Load (A) | 412 | 593 | 658 | 690 | 686
Lytton Bulk | 490-1 | Lytton BS | Gibson Island | NCC Rating (A) | 628 | 628 | 628 | 628 | 628 | HighSec | 0
|  |  |  | 10 POE Load (A) | 158 | 186 | 184 | 181 | 180
|  |  |  | Power Factor | 0.97569 | 0.96346 | 0.96369 | 0.96404 | 0.96629
|  |  |  | ECC Rating (A) | 628 | 628 | 628 | 628 | 628
|  |  |  | 50 POE Load (A) | 306 | 360 | 357 | 353 | 349
Lytton Bulk | 491-1 | Lytton BS | Lytton | NCC Rating (A) | 450 | 450 | 450 | 450 | 450 | HighSec | 140 | 4.5
|  |  |  | 10 POE Load (A) | 247 | 261 | 287 | 283 | 281
|  |  |  | Power Factor | 0.99888 | 0.99763 | 0.99246 | 0.99371 | 0.99378
|  |  |  | ECC Rating (A) | 450 | 450 | 450 | 450 | 450
|  |  |  | 50 POE Load (A) | 492 | 519 | 571 | 563 | 559
Lytton Bulk | 492-1 | Lytton BS | Gibson Island | NCC Rating (A) | 463 | 463 | 463 | 463 | 463 | HighSec | 0
|  |  |  | 10 POE Load (A) | 152 | 178 | 177 | 174 | 173
|  |  |  | Power Factor | 0.99507 | 0.98912 | 0.98924 | 0.98941 | 0.99061
|  |  |  | ECC Rating (A) | 463 | 463 | 463 | 463 | 463
|  |  |  | 50 POE Load (A) | 306 | 361 | 357 | 353 | 350
Lytton Bulk | 493-1 | Lytton BS | Lytton | NCC Rating (A) | 536 | 536 | 536 | 536 | 536 | HighSec | 140 | 24.5
|  |  |  | 10 POE Load (A) | 248 | 262 | 287 | 284 | 282
|  |  |  | Power Factor | 0.97853 | 0.97382 | 0.95995 | 0.96291 | 0.96308
|  |  |  | ECC Rating (A) | 536 | 536 | 536 | 536 | 536
|  |  |  | 50 POE Load (A) | 491 | 519 | 570 | 562 | 558
Lytton Bulk | 494-1 | Fisherman Is B | Fishermans Is | NCC Rating (A) | 488 | 488 | 488 | 488 | 488 | Urban | 70
|  |  |  | 10 POE Load (A) | 87 | 170 | 201 | 215 | 215
|  |  |  | Power Factor | 0.99276 | 0.98691 | 0.98436 | 0.9836 | 0.9836
|  |  |  | ECC Rating (A) | 488 | 488 | 488 | 488 | 488
|  |  |  | 50 POE Load (A) | 171 | 337 | 399 | 430 | 428
Lytton Bulk | 495-1 | Fisherman Is B | Fisherman Is | NCC Rating (A) | 600 | 600 | 600 | 600 | 600 | Urban | 70
|  |  |  | 10 POE Load (A) | 89 | 173 | 205 | 219 | 219
|  |  |  | Power Factor | 0.95104 | 0.93442 | 0.92843 | 0.92665 | 0.92666
|  |  |  | ECC Rating (A) | 600 | 600 | 600 | 600 | 600
|  |  |  | 50 POE Load (A) | 170 | 336 | 398 | 428 | 426
Lytton Bulk | 560-1 | Lytton BS | 560 Tee1 | NCC Rating (A) | 527 | 527 | 527 | 527 | 527 | Urban | 70
|  |  |  | 10 POE Load (A) | 162 | 160 | 160 | 157 | 157
|  |  |  | Power Factor | 0.99006 | 0.99034 | 0.99043 | 0.99078 | 0.99078
|  |  |  | ECC Rating (A) | 527 | 527 | 527 | 527 | 527
|  |  |  | 50 POE Load (A) | 500 | 493 | 491 | 485 | 483
Lytton Bulk | 560-2 | 560 Tee1 | Tingalpa | NCC Rating (A) | 600 | 600 | 600 | 600 | 600 | Urban | 70
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 1.9405e-06 | 1.9406e-06 | 1.94e-06 | 1.94e-06 | 1.94e-06
|  |  |  | ECC Rating (A) | 600 | 600 | 600 | 600 | 600
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lytton Bulk | 560-3 | 560 Tee1 | 560 Tee2 | NCC Rating (A) | 600 | 600 | 600 | 600 | 600 | Urban | 70
|  |  |  | 10 POE Load (A) | 162 | 161 | 160 | 158 | 158
|  |  |  | Power Factor | 0.99167 | 0.99189 | 0.99196 | 0.99224 | 0.99224
|  |  |  | ECC Rating (A) | 600 | 600 | 600 | 600 | 600
|  |  |  | 50 POE Load (A) | 500 | 493 | 491 | 485 | 483
Lytton Bulk | 560-5 | Lota | 560 Tee2 | NCC Rating (A) | 704 | 704 | 704 | 704 | 704 | Urban | 70
|  |  |  | 10 POE Load (A) | 96 | 95 | 94 | 93 | 93
|  |  |  | Power Factor | 0.99187 | 0.99208 | 0.99215 | 0.99243 | 0.99243
|  |  |  | ECC Rating (A) | 704 | 704 | 704 | 704 | 704
|  |  |  | 50 POE Load (A) | 294 | 290 | 289 | 285 | 284
Lytton Bulk | 569-1 | Lytton BS | Lota | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Urban | 70
|  |  |  | 10 POE Load (A) | 335 | 331 | 330 | 325 | 325
|  |  |  | Power Factor | 0.96672 | 0.9672 | 0.96736 | 0.96799 | 0.96799
|  |  |  | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
|  |  |  | 50 POE Load (A) | 480 | 474 | 472 | 466 | 464
Lytton Bulk | 599-1 | Hemmant | Lindum | NCC Rating (A) | 443 | 443 | 443 | 443 | 443 | Urban | 70
|  |  |  | 10 POE Load (A) | 2 | 2 | 2 | 2 | 2
|  |  |  | Power Factor | 2.5275e-05 | 2.5275e-05 | 2.5275e-05 | 2.5275e-05 | 2.5275e-05
|  |  |  | ECC Rating (A) | 443 | 443 | 443 | 443 | 443
|  |  |  | 50 POE Load (A) | 2 | 2 | 2 | 2 | 2
Lytton Bulk | 681-1 | Lindum | Wynnum | NCC Rating (A) | 661 | 661 | 661 | 661 | 661 | Urban | 70
|  |  |  | 10 POE Load (A) | 208 | 206 | 206 | 204 | 203
|  |  |  | Power Factor | 0.97623 | 0.9764 | 0.9764 | 0.97658 | 0.97666
|  |  |  | ECC Rating (A) | 661 | 661 | 661 | 661 | 661
|  |  |  | 50 POE Load (A) | 401 | 398 | 398 | 392 | 392
Lytton Bulk | 682-1 | Lindum | Wynnum | NCC Rating (A) | 661 | 661 | 661 | 661 | 661 | Urban | 70
|  |  |  | 10 POE Load (A) | 199 | 197 | 197 | 196 | 195
|  |  |  | Power Factor | 0.97589 | 0.97606 | 0.97606 | 0.97624 | 0.97633
|  |  |  | ECC Rating (A) | 661 | 661 | 661 | 661 | 661
|  |  |  | 50 POE Load (A) | 403 | 399 | 399 | 393 | 393
Lytton Bulk | 687-1 | Lytton BS | 687 Tee1 | NCC Rating (A) | 758 | 758 | 758 | 758 | 758 | Urban | 70
|  |  |  | 10 POE Load (A) | 148 | 146 | 146 | 145 | 144
|  |  |  | Power Factor | 0.9944 | 0.99453 | 0.99453 | 0.99466 | 0.99472
|  |  |  | ECC Rating (A) | 758 | 758 | 758 | 758 | 758
|  |  |  | 50 POE Load (A) | 389 | 385 | 385 | 380 | 380
Lytton Bulk | 687-2 | 687 Tee1 | Lytton | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 70
|  |  |  | 10 POE Load (A) | 2 | 2 | 2 | 2 | 2
|  |  |  | Power Factor | 1.3251e-06 | 1.3252e-06 | 1.3252e-06 | 1.3252e-06 | 1.3252e-06
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | 50 POE Load (A) | 2 | 2 | 2 | 2 | 2
Lytton Bulk | 687-3 | 687 Tee1 | Lindum | NCC Rating (A) | 636 | 636 | 636 | 636 | 636 | Urban | 70
|  |  |  | 10 POE Load (A) | 148 | 146 | 146 | 145 | 145
|  |  |  | Power Factor | 0.99281 | 0.99294 | 0.99294 | 0.99307 | 0.99313
|  |  |  | ECC Rating (A) | 636 | 636 | 636 | 636 | 636
|  |  |  | 50 POE Load (A) | 389 | 386 | 386 | 380 | 380
Lytton Bulk | 688-1 | Lytton BS | Lindum | NCC Rating (A) | 636 | 636 | 636 | 636 | 636 | Urban | 70
|  |  |  | 10 POE Load (A) | 257 | 255 | 255 | 252 | 251
|  |  |  | Power Factor | 0.97251 | 0.97277 | 0.97277 | 0.97303 | 0.97316
|  |  |  | ECC Rating (A) | 636 | 636 | 636 | 636 | 636
|  |  |  | 50 POE Load (A) | 388 | 385 | 385 | 380 | 380
Meeandah Bulk | 3374-1 | Whinstanes | Hamilton Lands | NCC Rating (A) | 476 | 476 | 476 | 476 | 476 | Urban | 70
|  |  |  | 10 POE Load (A) | 51 | 46 | 44 | 43 | 41
|  |  |  | Power Factor | 0.92663 | 0.92751 | 0.92832 | 0.92906 | 0.93006
|  |  |  | ECC Rating (A) | 476 | 476 | 476 | 476 | 476
|  |  |  | 50 POE Load (A) | 166 | 163 | 161 | 159 | 157
Meeandah Bulk | 506-1 | Meeandah BS | Hamilton Lands | NCC Rating (A) | 720 | 720 | 720 | 720 | 720 | Urban | 70
|  |  |  | 10 POE Load (A) | 169 | 175 | 178 | 180 | 182
|  |  |  | Power Factor | 0.93327 | 0.93203 | 0.93157 | 0.93123 | 0.93076
|  |  |  | ECC Rating (A) | 720 | 720 | 720 | 720 | 720
|  |  |  | 50 POE Load (A) | 286 | 296 | 300 | 304 | 309
Meeandah Bulk | 513-1 | Meeandah BS | Hamilton Lands | NCC Rating (A) | 720 | 720 | 720 | 720 | 720 | Urban | 70
|  |  |  | 10 POE Load (A) | 167 | 174 | 176 | 178 | 181
|  |  |  | Power Factor | 0.93317 | 0.93194 | 0.93148 | 0.93114 | 0.93066
|  |  |  | ECC Rating (A) | 720 | 720 | 720 | 720 | 720
|  |  |  | 50 POE Load (A) | 285 | 295 | 300 | 303 | 309
Meeandah Bulk | 556-1 | Meeandah BS | Whinstanes | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
|  |  |  | 10 POE Load (A) | 121 | 122 | 122 | 122 | 123
|  |  |  | Power Factor | 0.93982 | 0.93917 | 0.93901 | 0.93892 | 0.93874
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 165 | 162 | 163 | 164 | 165
Meeandah Bulk | 609-1 | Meeandah BS | Myrtletown | NCC Rating (A) | 813 | 813 | 813 | 813 | 813 | Urban | 70
|  |  |  | 10 POE Load (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 2.9587e-06 | 2.9588e-06 | 2.9588e-06 | 2.9587e-06 | 2.9588e-06
|  |  |  | ECC Rating (A) | 813 | 813 | 813 | 813 | 813
|  |  |  | 50 POE Load (A) | 1 | 1 | 1 | 1 | 1
Meeandah Bulk | 610-1 | Meeandah BS | Myrtletown | NCC Rating (A) | 748 | 748 | 748 | 748 | 748 | Urban | 70
|  |  |  | 10 POE Load (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 8.8408e-06 | 8.8417e-06 | 8.8417e-06 | 8.8389e-06 | 8.8389e-06
|  |  |  | ECC Rating (A) | 748 | 748 | 748 | 748 | 748
|  |  |  | 50 POE Load (A) | 1 | 1 | 1 | 1 | 1
Molendinar Bulk | 3670-1 | Molendinar BS | Parkwood | NCC Rating (A) | 710 | 710 | 710 | 710 | 710 | Urban | 70
|  |  |  | 10 POE Load (A) | 364 | 374 | 380 | 376 | 376
|  |  |  | Power Factor | 0.96526 | 0.96485 | 0.96452 | 0.96485 | 0.96482
|  |  |  | ECC Rating (A) | 710 | 710 | 710 | 710 | 710
|  |  |  | 50 POE Load (A) | 578 | 588 | 596 | 591 | 591
Molendinar Bulk | 3671-1 | Molendinar BS | Parkwood | NCC Rating (A) | 708 | 708 | 708 | 708 | 708 | Urban | 70
|  |  |  | 10 POE Load (A) | 290 | 297 | 302 | 299 | 299
|  |  |  | Power Factor | 0.97378 | 0.97341 | 0.9731 | 0.9734 | 0.97338
|  |  |  | ECC Rating (A) | 708 | 708 | 708 | 708 | 708
|  |  |  | 50 POE Load (A) | 466 | 480 | 489 | 484 | 483
Molendinar Bulk | 389-1 | Parkwood | 389 Tee1 | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
|  |  |  | 10 POE Load (A) | 353 | 340 | 336 | 335 | 337
|  |  |  | Power Factor | 0.97098 | 0.97159 | 0.97175 | 0.97199 | 0.97187
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 757 | 745 | 743 | 737 | 742
Molendinar Bulk | 389-2 | F389 Tee1 | Labrador | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
|  |  |  | 10 POE Load (A) | 233 | 228 | 226 | 227 | 230
|  |  |  | Power Factor | 0.96302 | 0.96311 | 0.96318 | 0.96313 | 0.96289
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 401 | 397 | 396 | 394 | 397
Molendinar Bulk | 389-3 | F389 Tee1 | Hollywell | NCC Rating (A) | 631 | 631 | 631 | 631 | 631 | Urban | 70
|  |  |  | 10 POE Load (A) | 122 | 114 | 112 | 110 | 109
|  |  |  | Power Factor | 0.97864 | 0.97973 | 0.97988 | 0.98071 | 0.98111
|  |  |  | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
|  |  |  | 50 POE Load (A) | 676 | 668 | 668 | 662 | 664
Molendinar Bulk | 390-1 | Molendinar BS | F390 Tee1 | NCC Rating (A) | 637 | 637 | 637 | 637 | 637 | Urban | 70
|  |  |  | 10 POE Load (A) | 114 | 128 | 126 | 123 | 121
|  |  |  | Power Factor | 0.96007 | 0.95709 | 0.95698 | 0.95752 | 0.95788
|  |  |  | ECC Rating (A) | 637 | 637 | 637 | 637 | 637
|  |  |  | 50 POE Load (A) | 251 | 287 | 283 | 276 | 272
Molendinar Bulk | 390-2 | F390 Tee | Bundall | NCC Rating (A) | 653 | 653 | 653 | 653 | 653 | Urban | 70
|  |  |  | 10 POE Load (A) | 114 | 128 | 126 | 123 | 122
|  |  |  | Power Factor | 0.96119 | 0.95864 | 0.95848 | 0.95894 | 0.95925
|  |  |  | ECC Rating (A) | 653 | 653 | 653 | 653 | 653
|  |  |  | 50 POE Load (A) | 251 | 287 | 283 | 276 | 273
Molendinar Bulk | 390-3 | F390 Tee | Miami | NCC Rating (A) | 529 | 529 | 529 | 529 | 529 | Urban | 70
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 7.1417e-06 | 7.1416e-06 | 7.1421e-06 | 7.1414e-06 | 7.1424e-06
|  |  |  | ECC Rating (A) | 529 | 529 | 529 | 529 | 529
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Molendinar Bulk | 391-1 | Molendinar BS | Bundall | NCC Rating (A) | 623 | 623 | 623 | 623 | 623 | Urban | 70
|  |  |  | 10 POE Load (A) | 143 | 161 | 157 | 154 | 152
|  |  |  | Power Factor | 0.93755 | 0.93456 | 0.93453 | 0.93508 | 0.93544
|  |  |  | ECC Rating (A) | 623 | 623 | 623 | 623 | 623
|  |  |  | 50 POE Load (A) | 245 | 279 | 275 | 269 | 265
Molendinar Bulk | 392-1 | Molendinar BS | Gaven | NCC Rating (A) | 708 | 708 | 708 | 708 | 708 | Urban | 70
|  |  |  | 10 POE Load (A) | 269 | 265 | 263 | 259 | 257
|  |  |  | Power Factor | 0.97499 | 0.97554 | 0.97575 | 0.97628 | 0.9765
|  |  |  | ECC Rating (A) | 708 | 708 | 708 | 708 | 708
|  |  |  | 50 POE Load (A) | 508 | 499 | 495 | 488 | 483
Molendinar Bulk | 421-1 | Molendinar BS | Arundel | NCC Rating (A) | 673 | 673 | 673 | 673 | 673 | Urban | 450
|  |  |  | 10 POE Load (A) | 498 | 492 | 491 | 486 | 486
|  |  |  | Power Factor | 0.96746 | 0.96787 | 0.96795 | 0.96828 | 0.96819
|  |  |  | ECC Rating (A) | 712 | 712 | 712 | 712 | 712
|  |  |  | 50 POE Load (A) | 828 | 818 | 817 | 808 | 809
Molendinar Bulk | 458-1 | Molendinar BS | Labrador | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
|  |  |  | 10 POE Load (A) | 199 | 199 | 199 | 198 | 199
|  |  |  | Power Factor | 0.97517 | 0.97546 | 0.97553 | 0.97569 | 0.97554
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 410 | 404 | 402 | 402 | 406
Molendinar Bulk | 473-1 | Molendinar BS | Gaven | NCC Rating (A) | 717 | 717 | 717 | 717 | 717 | Urban | 70
|  |  |  | 10 POE Load (A) | 270 | 266 | 264 | 259 | 258
|  |  |  | Power Factor | 0.97664 | 0.97711 | 0.97729 | 0.97776 | 0.97794
|  |  |  | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
|  |  |  | 50 POE Load (A) | 509 | 499 | 496 | 488 | 483
Molendinar Bulk | 474A-1 | Arundel | Hollywell | NCC Rating (A) | 631 | 631 | 631 | 631 | 631 | Urban | 70
|  |  |  | 10 POE Load (A) | 602 | 603 | 605 | 601 | 602
|  |  |  | Power Factor | 0.96642 | 0.96687 | 0.96689 | 0.96714 | 0.96708
|  |  |  | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
|  |  |  | 50 POE Load (A) | 660 | 660 | 664 | 659 | 661
Molendinar Bulk | 474B-1 | Hope Is | Hollywell | NCC Rating (A) | 786 | 786 | 786 | 786 | 786 | Urban | 70
|  |  |  | 10 POE Load (A) | 4 | 4 | 4 | 4 | 4
|  |  |  | Power Factor | 4.5529e-06 | 4.5529e-06 | 4.5529e-06 | 4.5529e-06 | 4.5529e-06
|  |  |  | ECC Rating (A) | 786 | 786 | 786 | 786 | 786
|  |  |  | 50 POE Load (A) | 4 | 4 | 4 | 4 | 4
Molendinar Bulk | 486-1 | Molendinar BS | Arundel | NCC Rating (A) | 673 | 673 | 673 | 673 | 673 | Urban | 450
|  |  |  | 10 POE Load (A) | 499 | 493 | 492 | 486 | 486
|  |  |  | Power Factor | 0.96742 | 0.96782 | 0.96791 | 0.96823 | 0.96815
|  |  |  | ECC Rating (A) | 721 | 721 | 721 | 721 | 721
|  |  |  | 50 POE Load (A) | 828 | 818 | 818 | 808 | 810
Mudgeeraba Bulk | 3700-1 | Mudgeeraba BS | 3700 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 213 | 210 | 209 | 207 | 206
|  |  |  | Power Factor | 0.98364 | 0.98389 | 0.98398 | 0.98414 | 0.98422
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 417 | 412 | 412 | 406 | 406
Mudgeeraba Bulk | 3700-2 | 3700 Tee1 | 3701 Tee1 | NCC Rating (A) | 723 | 723 | 723 | 723 | 723 | Rural | 170
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 6.6122e-05 | 6.6085e-05 | 6.6093e-05 | 6.6111e-05 | 6.6091e-05
|  |  |  | ECC Rating (A) | 723 | 723 | 723 | 723 | 723
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Mudgeeraba Bulk | 3700-3 | 3700 Tee1 | 3700 Tee2 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 213 | 210 | 209 | 207 | 207
|  |  |  | Power Factor | 0.98474 | 0.98497 | 0.98504 | 0.98519 | 0.98526
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 417 | 412 | 412 | 406 | 406
Mudgeeraba Bulk | 3700-4 | 3700 Tee2 | 3702 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 8.6874e-06 | 8.6879e-06 | 8.6891e-06 | 8.687e-06 | 8.6882e-06
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Mudgeeraba Bulk | 3700-5 | 3700 Tee2 | Mudgeeraba Pkg | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 213 | 210 | 209 | 207 | 207
|  |  |  | Power Factor | 0.98532 | 0.98553 | 0.9856 | 0.98574 | 0.98581
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 417 | 412 | 412 | 406 | 406
Mudgeeraba Bulk | 3701-1 | Mudgeeraba | Mudgeeraba Pkg | NCC Rating (A) | 529 | 529 | 529 | 529 | 529 | Rural | 170
|  |  |  | 10 POE Load (A) | 230 | 227 | 226 | 224 | 223
|  |  |  | Power Factor | 0.97878 | 0.97906 | 0.97915 | 0.97934 | 0.97943
|  |  |  | ECC Rating (A) | 529 | 529 | 529 | 529 | 529
|  |  |  | 50 POE Load (A) | 416 | 410 | 410 | 405 | 405
Nambour Bulk | 307-1 | Nambour BS | 307 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 102 | 106 | 107 | 106 | 106
|  |  |  | Power Factor | 0.94942 | 0.94786 | 0.94747 | 0.94786 | 0.94786
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 695 | 689 | 690 | 677 | 677
Nambour Bulk | 307-2 | 307 Tee1 | Yandina | NCC Rating (A) | 755 | 755 | 755 | 755 | 755 | Rural | 170
|  |  |  | 10 POE Load (A) | 103 | 107 | 108 | 107 | 107
|  |  |  | Power Factor | 0.94643 | 0.94535 | 0.94507 | 0.94535 | 0.94535
|  |  |  | ECC Rating (A) | 755 | 755 | 755 | 755 | 755
|  |  |  | 50 POE Load (A) | 172 | 179 | 181 | 179 | 179
Nambour Bulk | 344-1 | Nambour BS | Maleny | NCC Rating (A) | 155 | 200 | 200 | 200 | 200 | Rural | 170
|  |  |  | 10 POE Load (A) | 145 | 137 | 137 | 135 | 135
|  |  |  | Power Factor | 0.99022 | 0.98495 | 0.98495 | 0.98519 | 0.98519
|  |  |  | ECC Rating (A) | 155 | 200 | 200 | 200 | 200
|  |  |  | 50 POE Load (A) | 137 | 129 | 129 | 128 | 128
Nambour Bulk | 345-1 | Nambour BS | Kenilworth | NCC Rating (A) | 208 | 208 | 208 | 208 | 208 | Rural | 170 | 4
|  |  |  | 10 POE Load (A) | 79 | 77 | 77 | 76 | 76
|  |  |  | Power Factor | 0.98908 | 0.98927 | 0.98927 | 0.98965 | 0.98965
|  |  |  | ECC Rating (A) | 208 | 208 | 208 | 208 | 208
|  |  |  | 50 POE Load (A) | 74 | 72 | 72 | 70 | 70
Nambour Bulk | 347-1 | Nambour BS | 347 Tee1 | NCC Rating (A) | 412 | 412 | 412 | 412 | 412 | Rural | 170
|  |  |  | 10 POE Load (A) | 211 | 209 | 209 | 207 | 208
|  |  |  | Power Factor | 0.96957 | 0.96987 | 0.96987 | 0.97016 | 0.97001
|  |  |  | ECC Rating (A) | 412 | 412 | 412 | 412 | 412
|  |  |  | 50 POE Load (A) | 462 | 458 | 458 | 453 | 455
Nambour Bulk | 347-2 | 347 Tee1 | Palmwoods Central | NCC Rating (A) | 357 | 357 | 357 | 357 | 357 | Rural | 170
|  |  |  | 10 POE Load (A) | 211 | 209 | 209 | 207 | 208
|  |  |  | Power Factor | 0.9701 | 0.97035 | 0.97035 | 0.9706 | 0.97048
|  |  |  | ECC Rating (A) | 357 | 357 | 357 | 357 | 357
|  |  |  | 50 POE Load (A) | 462 | 458 | 458 | 453 | 456
Nambour Bulk | 347-3 | 347 Tee1 | Landsborough | NCC Rating (A) | 412 | 412 | 412 | 412 | 412 | Rural | 170
|  |  |  | 10 POE Load (A) | 2 | 2 | 2 | 2 | 2
|  |  |  | Power Factor | 7.6424e-05 | 7.6423e-05 | 7.6423e-05 | 7.6423e-05 | 7.6423e-05
|  |  |  | ECC Rating (A) | 412 | 412 | 412 | 412 | 412
|  |  |  | 50 POE Load (A) | 241 | 239 | 239 | 237 | 239
Nambour Bulk | 348-1 | Nambour BS | Palmwoods Central | NCC Rating (A) | 403 | 403 | 403 | 403 | 403 | Rural | 170
|  |  |  | 10 POE Load (A) | 269 | 267 | 267 | 264 | 265
|  |  |  | Power Factor | 0.95877 | 0.95913 | 0.95913 | 0.9595 | 0.95932
|  |  |  | ECC Rating (A) | 403 | 403 | 403 | 403 | 403
|  |  |  | 50 POE Load (A) | 448 | 444 | 444 | 440 | 442
Nambour Bulk | 489-1 | Nambour BS | Yandina | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170 | 1.5
|  |  |  | 10 POE Load (A) | 93 | 97 | 98 | 97 | 97
|  |  |  | Power Factor | 0.99728 | 0.99757 | 0.99764 | 0.99757 | 0.99757
|  |  |  | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | 50 POE Load (A) | 305 | 305 | 306 | 301 | 301
Nudgee Bulk | 3280-1 | Hendra | Clayfield | NCC Rating (A) | 725 | 725 | 725 | 725 | 725 | Urban | 70
|  |  |  | 10 POE Load (A) | 171 | 170 | 170 | 169 | 170
|  |  |  | Power Factor | 0.97555 | 0.97564 | 0.97564 | 0.97573 | 0.97564
|  |  |  | ECC Rating (A) | 725 | 725 | 725 | 725 | 725
|  |  |  | 50 POE Load (A) | 336 | 334 | 334 | 333 | 335
Nudgee Bulk | 540-1 | Hendra | Nundah | NCC Rating (A) | 814 | 814 | 814 | 814 | 814 | Urban | 70
|  |  |  | 10 POE Load (A) | 211 | 208 | 206 | 215 | 216
|  |  |  | Power Factor | 0.99099 | 0.99137 | 0.99151 | 0.99053 | 0.9904
|  |  |  | ECC Rating (A) | 814 | 814 | 814 | 814 | 814
|  |  |  | 50 POE Load (A) | 400 | 396 | 395 | 392 | 392
Nudgee Bulk | 593-1 | Nudgee BS | Nundah | NCC Rating (A) | 696 | 696 | 696 | 696 | 696 | Urban | 100
|  |  |  | 10 POE Load (A) | 639 | 630 | 627 | 632 | 632
|  |  |  | Power Factor | 0.98156 | 0.98197 | 0.98211 | 0.9819 | 0.98184
|  |  |  | ECC Rating (A) | 696 | 696 | 696 | 696 | 696
|  |  |  | 50 POE Load (A) | 781 | 771 | 767 | 777 | 777
Nudgee Bulk | 604-1 | Nudgee BS | Geebung | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Urban | 70
|  |  |  | 10 POE Load (A) | 212 | 216 | 211 | 208 | 207
|  |  |  | Power Factor | 0.98863 | 0.98656 | 0.98869 | 0.98907 | 0.98919
|  |  |  | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | 50 POE Load (A) | 304 | 310 | 303 | 298 | 296
Nudgee Bulk | 605-1 | Nudgee BS | Geebung | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Urban | 70
|  |  |  | 10 POE Load (A) | 212 | 216 | 212 | 208 | 207
|  |  |  | Power Factor | 0.98865 | 0.98658 | 0.98871 | 0.98909 | 0.98921
|  |  |  | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | 50 POE Load (A) | 304 | 310 | 303 | 298 | 296
Nudgee Bulk | 622-1 | Nudgee BS | Hendra | NCC Rating (A) | 738 | 738 | 738 | 738 | 738 | Urban | 70
|  |  |  | 10 POE Load (A) | 430 | 423 | 421 | 430 | 430
|  |  |  | Power Factor | 0.97187 | 0.97235 | 0.97251 | 0.97206 | 0.97193
|  |  |  | ECC Rating (A) | 738 | 738 | 738 | 738 | 738
|  |  |  | 50 POE Load (A) | 706 | 696 | 692 | 705 | 705
Nudgee Bulk | 623-1 | Nudgee BS | Hendra | NCC Rating (A) | 738 | 738 | 738 | 738 | 738 | Urban | 70
|  |  |  | 10 POE Load (A) | 430 | 423 | 421 | 430 | 430
|  |  |  | Power Factor | 0.97187 | 0.97235 | 0.97251 | 0.97206 | 0.97193
|  |  |  | ECC Rating (A) | 738 | 738 | 738 | 738 | 738
|  |  |  | 50 POE Load (A) | 706 | 696 | 692 | 705 | 705
Nudgee Bulk | 636-1 | Hendra | Clayfield | NCC Rating (A) | 725 | 725 | 725 | 725 | 725 | Urban | 70
|  |  |  | 10 POE Load (A) | 172 | 171 | 171 | 170 | 171
|  |  |  | Power Factor | 0.97571 | 0.97581 | 0.97581 | 0.97589 | 0.9758
|  |  |  | ECC Rating (A) | 725 | 725 | 725 | 725 | 725
|  |  |  | 50 POE Load (A) | 336 | 334 | 334 | 333 | 334
Nudgee Bulk | 643-1 | Hendra | Hamilton | NCC Rating (A) | 711 | 711 | 711 | 711 | 711 | Urban | 70
|  |  |  | 10 POE Load (A) | 203 | 201 | 199 | 198 | 198
|  |  |  | Power Factor | 0.97132 | 0.97161 | 0.97181 | 0.9719 | 0.9719
|  |  |  | ECC Rating (A) | 711 | 711 | 711 | 711 | 711
|  |  |  | 50 POE Load (A) | 396 | 388 | 386 | 384 | 384
Sandgate Bulk | 664-1 | Geebung | Zillmere | NCC Rating (A) | 410 | 410 | 410 | 410 | 410 | Urban | 70
|  |  |  | 10 POE Load (A) | 25 | 25 | 25 | 25 | 25
|  |  |  | Power Factor | 7.3809e-05 | 7.3809e-05 | 7.3809e-05 | 7.3809e-05 | 7.3809e-05
|  |  |  | ECC Rating (A) | 410 | 410 | 410 | 410 | 410
|  |  |  | 50 POE Load (A) | 25 | 25 | 25 | 25 | 25
Nudgee Bulk | 674-1 | Hendra | Hamilton | NCC Rating (A) | 711 | 711 | 711 | 711 | 711 | Urban | 70
|  |  |  | 10 POE Load (A) | 203 | 200 | 198 | 197 | 197
|  |  |  | Power Factor | 0.97129 | 0.97159 | 0.97179 | 0.97187 | 0.97187
|  |  |  | ECC Rating (A) | 711 | 711 | 711 | 711 | 711
|  |  |  | 50 POE Load (A) | 396 | 388 | 386 | 384 | 384
Nudgee Bulk | 683-1 | Nudgee BS | Geebung | NCC Rating (A) | 478 | 478 | 478 | 478 | 478 | Urban | 70
|  |  |  | 10 POE Load (A) | 208 | 212 | 207 | 204 | 203
|  |  |  | Power Factor | 0.98388 | 0.98133 | 0.98396 | 0.98449 | 0.98467
|  |  |  | ECC Rating (A) | 478 | 478 | 478 | 478 | 478
|  |  |  | 50 POE Load (A) | 299 | 304 | 298 | 292 | 291
Postmans Ridge Bulk | 376-1 | Postmans Ridge BS | Helidon | NCC Rating (A) | 290 | 582 | 582 | 582 | 582 | Rural | 170
|  |  |  | 10 POE Load (A) | 54 | 52 | 52 | 50 | 50
|  |  |  | Power Factor | 0.9657 | 0.96587 | 0.96587 | 0.96624 | 0.96624
|  |  |  | ECC Rating (A) | 290 | 582 | 582 | 582 | 582
|  |  |  | 50 POE Load (A) | 51 | 49 | 49 | 47 | 47
Postmans Ridge Bulk | 379-1 | Postmans Ridge BS | Carpendale | NCC Rating (A) | 200 | 200 | 200 | 200 | 200 | Rural | 170
|  |  |  | 10 POE Load (A) | 33 | 33 | 33 | 33 | 33
|  |  |  | Power Factor | 0.98824 | 0.98824 | 0.98824 | 0.98824 | 0.98824
|  |  |  | ECC Rating (A) | 200 | 200 | 200 | 200 | 200
|  |  |  | 50 POE Load (A) | 31 | 29 | 29 | 29 | 29
Postmans Ridge Bulk | 379-2 | Carpendale | Tenthill | NCC Rating (A) | 154 | 154 | 154 | 154 | 154 | Rural | 170
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 1.8788e-05 | 1.8787e-05 | 1.8787e-05 | 1.8786e-05 | 1.8786e-05
|  |  |  | ECC Rating (A) | 154 | 154 | 154 | 154 | 154
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Raceview Bulk | 354-1 | Raceview BS | Roderick St | NCC Rating (A) | 497 | 497 | 497 | 497 | 497 | Urban | 70
|  |  |  | 10 POE Load (A) | 305 | 303 | 304 | 302 | 305
|  |  |  | Power Factor | 0.99411 | 0.99416 | 0.99415 | 0.99419 | 0.9941
|  |  |  | ECC Rating (A) | 497 | 497 | 497 | 497 | 497
|  |  |  | 50 POE Load (A) | 452 | 448 | 448 | 445 | 446
Raceview Bulk | 355-1 | Roderick St | Booval | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 70
|  |  |  | 10 POE Load (A) | 158 | 157 | 156 | 155 | 155
|  |  |  | Power Factor | 0.99902 | 0.99907 | 0.99909 | 0.99915 | 0.99914
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | 50 POE Load (A) | 456 | 452 | 452 | 449 | 451
Raceview Bulk | 361-1 | Raceview BS | Booval | NCC Rating (A) | 631 | 631 | 631 | 631 | 631 | Urban | 70
|  |  |  | 10 POE Load (A) | 348 | 347 | 349 | 349 | 354
|  |  |  | Power Factor | 0.97623 | 0.97622 | 0.97607 | 0.97599 | 0.97561
|  |  |  | ECC Rating (A) | 631 | 631 | 631 | 631 | 631
|  |  |  | 50 POE Load (A) | 557 | 556 | 559 | 560 | 567
Raceview Bulk | 362-1 | Raceview BS | 362 Tee1 | NCC Rating (A) | 357 | 357 | 357 | 357 | 357 | Rural | 170
|  |  |  | 10 POE Load (A) | 172 | 170 | 174 | 173 | 173
|  |  |  | Power Factor | 0.98676 | 0.98903 | 0.98831 | 0.98858 | 0.98858
|  |  |  | ECC Rating (A) | 357 | 357 | 357 | 357 | 357
|  |  |  | 50 POE Load (A) | 454 | 466 | 483 | 481 | 484
Raceview Bulk | 362-2 | 362 Tee1 | Flinders | NCC Rating (A) | 708 | 708 | 708 | 708 | 708 | Rural | 170
|  |  |  | 10 POE Load (A) | 26 | 23 | 22 | 22 | 22
|  |  |  | Power Factor | 0.0056663 | 0.011167 | 0.29267 | 0.31273 | 0.31968
|  |  |  | ECC Rating (A) | 708 | 708 | 708 | 708 | 708
|  |  |  | 50 POE Load (A) | 276 | 289 | 306 | 307 | 311
Raceview Bulk | 362-3 | 362 Tee1 | Kalbar | NCC Rating (A) | 708 | 708 | 708 | 708 | 708 | Rural | 170
|  |  |  | 10 POE Load (A) | 178 | 175 | 172 | 170 | 170
|  |  |  | Power Factor | 0.9737 | 0.979 | 0.97921 | 0.97952 | 0.97952
|  |  |  | ECC Rating (A) | 708 | 708 | 708 | 708 | 708
|  |  |  | 50 POE Load (A) | 309 | 305 | 304 | 299 | 297
Raceview Bulk | 363-1 | Raceview BS | 363 Tee1 | NCC Rating (A) | 351 | 351 | 351 | 351 | 351 | Rural | 170 | 5.5
|  |  |  | 10 POE Load (A) | 168 | 166 | 170 | 168 | 168
|  |  |  | Power Factor | 0.98805 | 0.99028 | 0.9895 | 0.9898 | 0.98979
|  |  |  | ECC Rating (A) | 351 | 351 | 351 | 351 | 351
|  |  |  | 50 POE Load (A) | 429 | 440 | 455 | 454 | 456
Raceview Bulk | 363-2 | 363 Tee1 | Flinders | NCC Rating (A) | 403 | 403 | 403 | 403 | 403 | Rural | 170
|  |  |  | 10 POE Load (A) | 23 | 24 | 29 | 29 | 29
|  |  |  | Power Factor | 0.83774 | 0.82821 | 0.8634 | 0.86523 | 0.86631
|  |  |  | ECC Rating (A) | 403 | 403 | 403 | 403 | 403
|  |  |  | 50 POE Load (A) | 270 | 282 | 297 | 297 | 300
Raceview Bulk | 363-3 | 363 Tee1 | Kalbar | NCC Rating (A) | 374 | 374 | 374 | 374 | 374 | Rural | 170
|  |  |  | 10 POE Load (A) | 148 | 145 | 144 | 142 | 142
|  |  |  | Power Factor | 0.9992 | 0.99945 | 0.99944 | 0.99939 | 0.99939
|  |  |  | ECC Rating (A) | 374 | 374 | 374 | 374 | 374
|  |  |  | 50 POE Load (A) | 331 | 326 | 324 | 319 | 316
Raceview Bulk | 3960-1 | Ipswich Sth | Yamanto | NCC Rating (A) | 711 | 711 | 711 | 711 | 711 | Urban | 70
|  |  |  | 10 POE Load (A) | 453 | 464 | 472 | 472 | 475
|  |  |  | Power Factor | 0.95296 | 0.95474 | 0.95358 | 0.95393 | 0.95379
|  |  |  | ECC Rating (A) | 711 | 711 | 711 | 711 | 711
|  |  |  | 50 POE Load (A) | 522 | 532 | 545 | 543 | 545
Raceview Bulk | 3972-1 | Yamanto | Flinders | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
|  |  |  | 10 POE Load (A) | 196 | 192 | 197 | 194 | 194
|  |  |  | Power Factor | 0.91274 | 0.91804 | 0.91654 | 0.91687 | 0.91667
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 437 | 464 | 475 | 478 | 485
Raceview Bulk | 3980-1 | Kalbar | Boonah | NCC Rating (A) | 713 | 713 | 713 | 713 | 713 | Rural | 170
|  |  |  | 10 POE Load (A) | 79 | 78 | 77 | 76 | 76
|  |  |  | Power Factor | 0.99042 | 0.9905 | 0.99066 | 0.99092 | 0.99091
|  |  |  | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
|  |  |  | 50 POE Load (A) | 142 | 140 | 140 | 138 | 136
Raceview Bulk | 401-1 | Kalbar | Boonah | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
|  |  |  | 10 POE Load (A) | 76 | 75 | 74 | 73 | 73
|  |  |  | Power Factor | 0.99018 | 0.9903 | 0.99045 | 0.99071 | 0.99071
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 143 | 141 | 141 | 139 | 137
Raceview Bulk | 411-1 | Raceview BS | Booval | NCC Rating (A) | 558 | 558 | 558 | 558 | 558 | Urban | 70
|  |  |  | 10 POE Load (A) | 294 | 294 | 295 | 295 | 299
|  |  |  | Power Factor | 0.98612 | 0.98611 | 0.986 | 0.98593 | 0.98566
|  |  |  | ECC Rating (A) | 558 | 558 | 558 | 558 | 558
|  |  |  | 50 POE Load (A) | 541 | 540 | 543 | 544 | 551
Raceview Bulk | 509A-1 | Raceview BS | Ipswich Sth | NCC Rating (A) | 721 | 721 | 721 | 721 | 721 | Urban | 70 | 2
|  |  |  | 10 POE Load (A) | 437 | 444 | 451 | 451 | 457
|  |  |  | Power Factor | 0.97419 | 0.97459 | 0.97388 | 0.97402 | 0.97383
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 784 | 798 | 812 | 813 | 823
Raceview Bulk | 509B-1 | Raceview BS | Cooneana | NCC Rating (A) | 455 | 455 | 455 | 455 | 455 | Rural | 170
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 8.6768e-06 | 8.6758e-06 | 8.6757e-06 | 8.6757e-06 | 8.6762e-06
|  |  |  | ECC Rating (A) | 455 | 455 | 455 | 455 | 455
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Raceview Bulk | 510A-1 | Raceview BS | Ipswich Sth | NCC Rating (A) | 721 | 721 | 721 | 721 | 721 | Urban | 70 | 2
|  |  |  | 10 POE Load (A) | 433 | 439 | 446 | 447 | 452
|  |  |  | Power Factor | 0.97416 | 0.97456 | 0.97385 | 0.97399 | 0.9738
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 784 | 798 | 812 | 813 | 823
Raceview Bulk | 510B-1 | Raceview BS | Cooneana | NCC Rating (A) | 426 | 426 | 426 | 426 | 426 | Rural | 170
|  |  |  | 10 POE Load (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 1.6338e-05 | 1.6338e-05 | 1.6338e-05 | 1.6338e-05 | 1.6338e-05
|  |  |  | ECC Rating (A) | 426 | 426 | 426 | 426 | 426
|  |  |  | 50 POE Load (A) | 1 | 1 | 1 | 1 | 1
Richlands Bulk | 3818-1 | Richlands BS | Wacol | NCC Rating (A) | 750 | 750 | 750 | 750 | 750 | Urban | 70
|  |  |  | 10 POE Load (A) | 111 | 135 | 133 | 130 | 128
|  |  |  | Power Factor | 0.98956 | 0.98151 | 0.98321 | 0.98344 | 0.98358
|  |  |  | ECC Rating (A) | 750 | 750 | 750 | 750 | 750
|  |  |  | 50 POE Load (A) | 215 | 266 | 261 | 256 | 252
Richlands Bulk | 454-1 | Richlands BS | Wacol Sth | NCC Rating (A) | 430 | 430 | 430 | 430 | 430 | Urban | 70
|  |  |  | 10 POE Load (A) | 208 | 217 | 215 | 211 | 210
|  |  |  | Power Factor | 0.97218 | 0.97047 | 0.97081 | 0.97126 | 0.97197
|  |  |  | ECC Rating (A) | 430 | 430 | 430 | 430 | 430
|  |  |  | 50 POE Load (A) | 395 | 413 | 408 | 402 | 398
Richlands Bulk | 455-1 | Richlands BS | Wacol Sth | NCC Rating (A) | 430 | 430 | 430 | 430 | 430 | Urban | 70
|  |  |  | 10 POE Load (A) | 209 | 219 | 216 | 212 | 211
|  |  |  | Power Factor | 0.97223 | 0.97052 | 0.97086 | 0.97131 | 0.97202
|  |  |  | ECC Rating (A) | 430 | 430 | 430 | 430 | 430
|  |  |  | 50 POE Load (A) | 395 | 413 | 408 | 402 | 398
Richlands Bulk | 543-1 | Inala | 543 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
|  |  |  | 10 POE Load (A) | 3 | 3 | 3 | 3 | 3
|  |  |  | Power Factor | 0.00012567 | 0.00012567 | 0.00012567 | 0.00012567 | 0.00012567
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 571 | 560 | 552 | 540 | 536
Richlands Bulk | 543-2 | 543 Tee1 | Coopers Plains | NCC Rating (A) | 348 | 348 | 348 | 348 | 348 | Urban | 70
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 5.5492e-06 | 5.5492e-06 | 5.5492e-06 | 5.5492e-06 | 5.5492e-06
|  |  |  | ECC Rating (A) | 348 | 348 | 348 | 348 | 348
|  |  |  | 50 POE Load (A) | 349 | 353 | 346 | 338 | 336
Richlands Bulk | 543-3 | 543 Tee1 | Heathwood | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
|  |  |  | 10 POE Load (A) | 2 | 2 | 2 | 2 | 2
|  |  |  | Power Factor | 8.8129e-05 | 8.8129e-05 | 8.8129e-05 | 8.8129e-05 | 8.8129e-05
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 572 | 560 | 552 | 541 | 537
Richlands Bulk | 616-1 | Richlands BS | Darra | NCC Rating (A) | 407 | 407 | 407 | 407 | 407 | Urban | 70
|  |  |  | 10 POE Load (A) | 275 | 283 | 286 | 283 | 283
|  |  |  | Power Factor | 0.90772 | 0.92935 | 0.93155 | 0.92876 | 0.92829
|  |  |  | ECC Rating (A) | 440 | 440 | 440 | 440 | 440
|  |  |  | 50 POE Load (A) | 406 | 419 | 425 | 420 | 419
Richlands Bulk | 617-1 | Richlands BS | Darra | NCC Rating (A) | 407 | 407 | 407 | 407 | 407 | Urban | 70
|  |  |  | 10 POE Load (A) | 284 | 292 | 296 | 292 | 292
|  |  |  | Power Factor | 0.90799 | 0.92959 | 0.93179 | 0.92899 | 0.92853
|  |  |  | ECC Rating (A) | 440 | 440 | 440 | 440 | 440
|  |  |  | 50 POE Load (A) | 412 | 425 | 431 | 426 | 425
Richlands Bulk | 618-1 | Richlands BS | Inala | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
|  |  |  | 10 POE Load (A) | 352 | 349 | 348 | 344 | 345
|  |  |  | Power Factor | 0.97304 | 0.97339 | 0.9735 | 0.97385 | 0.97373
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 683 | 671 | 665 | 656 | 654
Richlands Bulk | 619-1 | Richlands BS | Inala | NCC Rating (A) | 550 | 550 | 550 | 550 | 550 | Urban | 70
|  |  |  | 10 POE Load (A) | 227 | 225 | 225 | 222 | 223
|  |  |  | Power Factor | 0.97609 | 0.97638 | 0.97648 | 0.97677 | 0.97667
|  |  |  | ECC Rating (A) | 550 | 550 | 550 | 550 | 550
|  |  |  | 50 POE Load (A) | 683 | 671 | 665 | 656 | 654
Richlands Bulk | 620-1 | Richlands BS | Oxley | NCC Rating (A) | 324 | 324 | 324 | 324 | 324 | Urban | 70
|  |  |  | 10 POE Load (A) | 183 | 218 | 215 | 213 | 212
|  |  |  | Power Factor | 0.9689 | 0.96566 | 0.96596 | 0.96564 | 0.96574
|  |  |  | ECC Rating (A) | 359 | 359 | 359 | 359 | 359
|  |  |  | 50 POE Load (A) | 337 | 412 | 406 | 401 | 399
Richlands Bulk | 621-1 | Richlands BS | Oxley | NCC Rating (A) | 324 | 324 | 324 | 324 | 324 | Urban | 70
|  |  |  | 10 POE Load (A) | 174 | 207 | 205 | 202 | 201
|  |  |  | Power Factor | 0.96414 | 0.96065 | 0.96098 | 0.96063 | 0.96075
|  |  |  | ECC Rating (A) | 359 | 359 | 359 | 359 | 359
|  |  |  | 50 POE Load (A) | 337 | 412 | 406 | 400 | 399
Richlands Bulk | 641-1 | Darra | Jindalee | NCC Rating (A) | 703 | 703 | 703 | 703 | 703 | Urban | 70
|  |  |  | 10 POE Load (A) | 129 | 127 | 125 | 122 | 121
|  |  |  | Power Factor | 0.98454 | 0.98611 | 0.98464 | 0.98486 | 0.98494
|  |  |  | ECC Rating (A) | 703 | 703 | 703 | 703 | 703
|  |  |  | 50 POE Load (A) | 243 | 239 | 235 | 230 | 228
Richlands Bulk | 642-1 | Darra | Jindalee | NCC Rating (A) | 703 | 703 | 703 | 703 | 703 | Urban | 70
|  |  |  | 10 POE Load (A) | 127 | 124 | 122 | 120 | 119
|  |  |  | Power Factor | 0.98362 | 0.98523 | 0.98371 | 0.98394 | 0.98402
|  |  |  | ECC Rating (A) | 703 | 703 | 703 | 703 | 703
|  |  |  | 50 POE Load (A) | 243 | 239 | 235 | 230 | 228
Richlands Bulk | 679-1 | Richlands BS | Wacol | NCC Rating (A) | 605 | 605 | 605 | 605 | 605 | Urban | 70
|  |  |  | 10 POE Load (A) | 112 | 137 | 135 | 132 | 130
|  |  |  | Power Factor | 0.99007 | 0.98213 | 0.98382 | 0.98404 | 0.98419
|  |  |  | ECC Rating (A) | 605 | 605 | 605 | 605 | 605
|  |  |  | 50 POE Load (A) | 215 | 266 | 261 | 256 | 252
Richlands Bulk | 680-1 | Richlands BS | Wacol | NCC Rating (A) | 750 | 750 | 750 | 750 | 750 | Urban | 70
|  |  |  | 10 POE Load (A) | 226 | 277 | 272 | 266 | 263
|  |  |  | Power Factor | 0.98102 | 0.9675 | 0.97088 | 0.97147 | 0.97187
|  |  |  | ECC Rating (A) | 750 | 750 | 750 | 750 | 750
|  |  |  | 50 POE Load (A) | 214 | 266 | 261 | 255 | 252
Richlands Bulk | 700-1 | Richlands BS | Darra | NCC Rating (A) | 517 | 517 | 517 | 517 | 517 | Urban | 70
|  |  |  | 10 POE Load (A) | 217 | 224 | 226 | 224 | 223
|  |  |  | Power Factor | 0.93831 | 0.95587 | 0.95762 | 0.9554 | 0.95502
|  |  |  | ECC Rating (A) | 517 | 517 | 517 | 517 | 517
|  |  |  | 50 POE Load (A) | 321 | 332 | 336 | 332 | 332
Runcorn Bulk | 3440-1 | Runcorn BS | Sunnybank | NCC Rating (A) | 544 | 544 | 544 | 544 | 544 | Urban | 70
|  |  |  | 10 POE Load (A) | 452 | 446 | 442 | 435 | 447
|  |  |  | Power Factor | 0.99029 | 0.99047 | 0.99061 | 0.9926 | 0.99043
|  |  |  | ECC Rating (A) | 544 | 544 | 544 | 544 | 544
|  |  |  | 50 POE Load (A) | 516 | 509 | 505 | 498 | 513
Runcorn Bulk | 433-1 | Runcorn BS | Calamvale | NCC Rating (A) | 406 | 406 | 406 | 406 | 406 | Urban | 70
|  |  |  | 10 POE Load (A) | 2 | 2 | 2 | 2 | 2
|  |  |  | Power Factor | 1.7626e-05 | 1.7626e-05 | 1.7626e-05 | 1.7626e-05 | 1.7626e-05
|  |  |  | ECC Rating (A) | 406 | 406 | 406 | 406 | 406
|  |  |  | 50 POE Load (A) | 2 | 2 | 2 | 2 | 2
Runcorn Bulk | 434-1 | Runcorn | Calamvale | NCC Rating (A) | 406 | 406 | 406 | 406 | 406 | Urban | 70
|  |  |  | 10 POE Load (A) | 2 | 2 | 2 | 2 | 2
|  |  |  | Power Factor | 5.1614e-05 | 5.1614e-05 | 5.1614e-05 | 5.1614e-05 | 5.1614e-05
|  |  |  | ECC Rating (A) | 406 | 406 | 406 | 406 | 406
|  |  |  | 50 POE Load (A) | 2 | 2 | 2 | 2 | 2
Runcorn Bulk | 459A-1 | Upper Mt Gravatt | Sunnybank | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70
|  |  |  | 10 POE Load (A) | 96 | 94 | 94 | 92 | 95
|  |  |  | Power Factor | 0.93805 | 0.93837 | 0.93861 | 0.94367 | 0.93829
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 528 | 520 | 516 | 508 | 524
Runcorn Bulk | 459B-1 | Runcorn BS | Upper Mt Gravatt | NCC Rating (A) | 801 | 801 | 801 | 801 | 801 | Urban | 70
|  |  |  | 10 POE Load (A) | 94 | 93 | 92 | 91 | 94
|  |  |  | Power Factor | 0.94837 | 0.94885 | 0.94921 | 0.95405 | 0.94873
|  |  |  | ECC Rating (A) | 801 | 801 | 801 | 801 | 801
|  |  |  | 50 POE Load (A) | 527 | 519 | 516 | 507 | 523
Runcorn Bulk | 667-1 | Runcorn BS | Acacia Ridge | NCC Rating (A) | 426 | 426 | 426 | 426 | 426 | Urban | 70
|  |  |  | 10 POE Load (A) | 28 | 28 | 28 | 28 | 28
|  |  |  | Power Factor | 9.2863e-05 | 9.2863e-05 | 9.2863e-05 | 9.2863e-05 | 9.2863e-05
|  |  |  | ECC Rating (A) | 426 | 426 | 426 | 426 | 426
|  |  |  | 50 POE Load (A) | 28 | 28 | 28 | 28 | 28
Runcorn Bulk | 668-1 | Runcorn BS | Acacia Ridge | NCC Rating (A) | 426 | 426 | 426 | 426 | 426 | Urban | 70
|  |  |  | 10 POE Load (A) | 28 | 28 | 28 | 28 | 28
|  |  |  | Power Factor | 9.3774e-05 | 9.3774e-05 | 9.3774e-05 | 9.3774e-05 | 9.3774e-05
|  |  |  | ECC Rating (A) | 426 | 426 | 426 | 426 | 426
|  |  |  | 50 POE Load (A) | 28 | 28 | 28 | 28 | 28
Runcorn Bulk | 690-1 | Runcorn BS | Runcorn | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70
|  |  |  | 10 POE Load (A) | 231 | 229 | 229 | 228 | 229
|  |  |  | Power Factor | 0.98669 | 0.98685 | 0.98685 | 0.98693 | 0.98685
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 384 | 383 | 383 | 381 | 383
Runcorn Bulk | 691-1 | Runcorn BS | Runcorn | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70
|  |  |  | 10 POE Load (A) | 182 | 181 | 181 | 180 | 181
|  |  |  | Power Factor | 0.98714 | 0.9873 | 0.9873 | 0.98737 | 0.9873
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 385 | 383 | 383 | 382 | 383
Runcorn Bulk | 694-1 | Runcorn BS | Eight Mile Plains Bus 1 | NCC Rating (A) | 531 | 531 | 531 | 531 | 531 | Urban | 230
|  |  |  | 10 POE Load (A) | 325 | 315 | 310 | 325 | 341
|  |  |  | Power Factor | 0.96017 | 0.96126 | 0.9619 | 0.96017 | 0.95816
|  |  |  | ECC Rating (A) | 531 | 531 | 531 | 531 | 531
|  |  |  | 50 POE Load (A) | 645 | 630 | 622 | 654 | 690
Sandgate Bulk | 3290-1 | Sandgate BS | Bald Hills Bus 1 | NCC Rating (A) | 853 | 853 | 853 | 853 | 853 | Urban | 70
|  |  |  | 10 POE Load (A) | 171 | 168 | 166 | 164 | 163
|  |  |  | Power Factor | 0.99898 | 0.99885 | 0.99878 | 0.99871 | 0.99863
|  |  |  | ECC Rating (A) | 853 | 853 | 853 | 853 | 853
|  |  |  | 50 POE Load (A) | 321 | 314 | 310 | 303 | 303
Sandgate Bulk | 505-1 | Sandgate BS | Zilmere | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70
|  |  |  | 10 POE Load (A) | 306 | 301 | 299 | 295 | 295
|  |  |  | Power Factor | 0.97382 | 0.97552 | 0.97589 | 0.97651 | 0.97651
|  |  |  | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | 50 POE Load (A) | 400 | 394 | 391 | 386 | 386
Sandgate Bulk | 524-1 | Sandgate BS | Geebung | NCC Rating (A) | 453 | 453 | 453 | 453 | 453 | Urban | 70
|  |  |  | 10 POE Load (A) | 206 | 203 | 201 | 198 | 198
|  |  |  | Power Factor | 0.98655 | 0.98779 | 0.98806 | 0.98851 | 0.98851
|  |  |  | ECC Rating (A) | 453 | 453 | 453 | 453 | 453
|  |  |  | 50 POE Load (A) | 338 | 333 | 330 | 326 | 326
Sandgate Bulk | 524-2 | Geebung | Zillmere | NCC Rating (A) | 410 | 410 | 410 | 410 | 410 | Urban | 70
|  |  |  | 10 POE Load (A) | 211 | 208 | 206 | 203 | 203
|  |  |  | Power Factor | 0.96574 | 0.96708 | 0.96724 | 0.96748 | 0.96748
|  |  |  | ECC Rating (A) | 410 | 410 | 410 | 410 | 410
|  |  |  | 50 POE Load (A) | 343 | 338 | 335 | 331 | 331
Sandgate Bulk | 561-1 | Sandgate BS | Brighton TR1 | NCC Rating (A) | 786 | 786 | 786 | 786 | 786 | Urban | 70
|  |  |  | 10 POE Load (A) | 98 | 97 | 97 | 96 | 96
|  |  |  | Power Factor | 0.99627 | 0.99631 | 0.99631 | 0.9964 | 0.9964
|  |  |  | ECC Rating (A) | 786 | 786 | 786 | 786 | 786
|  |  |  | 50 POE Load (A) | 181 | 180 | 180 | 176 | 176
Sandgate Bulk | 656-1 | Sandgate BS | Brighton TR2 | NCC Rating (A) | 270 | 270 | 270 | 270 | 270 | Urban | 70
|  |  |  | 10 POE Load (A) | 94 | 93 | 93 | 92 | 92
|  |  |  | Power Factor | 0.99996 | 0.99996 | 0.99996 | 0.99997 | 0.99997
|  |  |  | ECC Rating (A) | 270 | 270 | 270 | 270 | 270
|  |  |  | 50 POE Load (A) | 183 | 181 | 181 | 178 | 178
Sandgate Bulk | 671-1 | Sandagate BS | Zillmere | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 70
|  |  |  | 10 POE Load (A) | 181 | 178 | 176 | 174 | 174
|  |  |  | Power Factor | 0.99279 | 0.99363 | 0.99379 | 0.99407 | 0.99407
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | 50 POE Load (A) | 296 | 292 | 289 | 286 | 286
Brendale Bulk | 310-3 | 310 Tee1 | 569 Tee1 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 2.0848e-06 | 2.0848e-06 | 2.0848e-06 | 2.0848e-06 | 2.0849e-06
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Stafford Bulk | 548-1 | Stafford BS | Enoggera | NCC Rating (A) | 836 | 836 | 836 | 836 | 836 | Urban | 150
|  |  |  | 10 POE Load (A) | 549 | 541 | 537 | 532 | 530
|  |  |  | Power Factor | 0.97912 | 0.97938 | 0.97955 | 0.97971 | 0.97981
|  |  |  | ECC Rating (A) | 963 | 963 | 963 | 963 | 963
|  |  |  | 50 POE Load (A) | 1020 | 1010 | 1000 | 990 | 988
Stafford Bulk | 550-1 | Stafford BS | Chermside | NCC Rating (A) | 668 | 668 | 668 | 668 | 668 | Urban | 70
|  |  |  | 10 POE Load (A) | 380 | 373 | 369 | 364 | 362
|  |  |  | Power Factor | 0.98163 | 0.98522 | 0.98544 | 0.98576 | 0.98539
|  |  |  | ECC Rating (A) | 789 | 789 | 789 | 789 | 789
|  |  |  | 50 POE Load (A) | 721 | 707 | 700 | 689 | 685
Stafford Bulk | 551-1 | Stafford BS | Chermside | NCC Rating (A) | 668 | 668 | 668 | 668 | 668 | Urban | 70
|  |  |  | 10 POE Load (A) | 379 | 372 | 368 | 363 | 361
|  |  |  | Power Factor | 0.98162 | 0.98522 | 0.98543 | 0.98575 | 0.98539
|  |  |  | ECC Rating (A) | 789 | 789 | 789 | 789 | 789
|  |  |  | 50 POE Load (A) | 721 | 707 | 700 | 689 | 685
Stafford Bulk | 567-1 | Stafford BS | Kedron | NCC Rating (A) | 576 | 576 | 576 | 576 | 576 | Urban | 70
|  |  |  | 10 POE Load (A) | 278 | 274 | 272 | 268 | 268
|  |  |  | Power Factor | 0.9781 | 0.97844 | 0.97869 | 0.97876 | 0.97876
|  |  |  | ECC Rating (A) | 576 | 576 | 576 | 576 | 576
|  |  |  | 50 POE Load (A) | 526 | 519 | 515 | 524 | 523
Stafford Bulk | 568-1 | Stafford BS | Kedron | NCC Rating (A) | 576 | 576 | 576 | 576 | 576 | Urban | 70
|  |  |  | 10 POE Load (A) | 280 | 276 | 274 | 270 | 270
|  |  |  | Power Factor | 0.97777 | 0.97812 | 0.97837 | 0.97897 | 0.97897
|  |  |  | ECC Rating (A) | 576 | 576 | 576 | 576 | 576
|  |  |  | 50 POE Load (A) | 526 | 519 | 515 | 525 | 523
Stafford Bulk | 594-1 | Stafford BS | Enoggera | NCC Rating (A) | 836 | 836 | 836 | 836 | 836 | Urban | 150
|  |  |  | 10 POE Load (A) | 545 | 538 | 534 | 529 | 526
|  |  |  | Power Factor | 0.9791 | 0.97936 | 0.97953 | 0.97969 | 0.97979
|  |  |  | ECC Rating (A) | 963 | 963 | 963 | 963 | 963
|  |  |  | 50 POE Load (A) | 1021 | 1010 | 1001 | 990 | 988
Stafford Bulk | 595-1 | Enoggera | Grovely | NCC Rating (A) | 720 | 720 | 720 | 720 | 720 | Urban | 70
|  |  |  | 10 POE Load (A) | 232 | 227 | 223 | 220 | 217
|  |  |  | Power Factor | 0.98266 | 0.98313 | 0.98344 | 0.98375 | 0.98397
|  |  |  | ECC Rating (A) | 720 | 720 | 720 | 720 | 720
|  |  |  | 50 POE Load (A) | 443 | 433 | 426 | 418 | 414
Stafford Bulk | 596-1 | Enoggera | Grovely | NCC Rating (A) | 720 | 720 | 720 | 720 | 720 | Urban | 70
|  |  |  | 10 POE Load (A) | 234 | 228 | 225 | 221 | 218
|  |  |  | Power Factor | 0.98271 | 0.98318 | 0.98349 | 0.98379 | 0.98402
|  |  |  | ECC Rating (A) | 720 | 720 | 720 | 720 | 720
|  |  |  | 50 POE Load (A) | 443 | 433 | 426 | 418 | 414
Stafford Bulk | 607-1 | Chermside | Zillmere | NCC Rating (A) | 416 | 416 | 416 | 416 | 416 | Urban | 70
|  |  |  | 10 POE Load (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 1.1685e-05 | 1.1685e-05 | 1.1685e-05 | 1.1685e-05 | 1.1685e-05
|  |  |  | ECC Rating (A) | 416 | 416 | 416 | 416 | 416
|  |  |  | 50 POE Load (A) | 1 | 1 | 1 | 1 | 1
Sunrise Hills Bulk | 308-1 | Perigian | 308 Tee1 | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
|  |  |  | 10 POE Load (A) | 562 | 553 | 550 | 542 | 540
|  |  |  | Power Factor | 0.94076 | 0.94335 | 0.9436 | 0.94441 | 0.94466
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 498 | 490 | 490 | 481 | 481
Sunrise Hills Bulk | 308-2 | 308 Tee1 | Coolum | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
|  |  |  | 10 POE Load (A) | 562 | 553 | 550 | 542 | 540
|  |  |  | Power Factor | 0.95038 | 0.95264 | 0.95283 | 0.95343 | 0.95362
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 498 | 490 | 490 | 481 | 481
Sunrise Hills Bulk | 308-3 | 308 Tee1 | 307 Tee2 | NCC Rating (A) | 529 | 529 | 529 | 529 | 529 | Urban | 70
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 2.6218e-05 | 2.6225e-05 | 2.6225e-05 | 2.622e-05 | 2.6225e-05
|  |  |  | ECC Rating (A) | 529 | 529 | 529 | 529 | 529
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Sunrise Hills Bulk | 3100-1 | Sunrise Hills BS | 3100 Tee1 | NCC Rating (A) | 793 | 793 | 793 | 793 | 793 | Urban | 70 | 7
|  |  |  | 10 POE Load (A) | 827 | 816 | 813 | 801 | 798
|  |  |  | Power Factor | 0.92405 | 0.92677 | 0.9272 | 0.92869 | 0.9291
|  |  |  | ECC Rating (A) | 793 | 793 | 793 | 793 | 793
|  |  |  | 50 POE Load (A) | 729 | 720 | 720 | 708 | 708
Sunrise Hills Bulk | 3100-2 | 3100 Tee1 | Peregian | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
|  |  |  | 10 POE Load (A) | 827 | 816 | 813 | 801 | 799
|  |  |  | Power Factor | 0.95835 | 0.96014 | 0.96038 | 0.96111 | 0.96135
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 729 | 720 | 720 | 708 | 708
Sunrise Hills Bulk | 343-1 | Sunrise Hills BS | 343 Tee1 | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Rural | 170
|  |  |  | 10 POE Load (A) | 449 | 444 | 442 | 438 | 437
|  |  |  | Power Factor | 0.97967 | 0.97997 | 0.98009 | 0.98039 | 0.98046
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 708 | 698 | 693 | 685 | 682
Sunrise Hills Bulk | 343-2 | 343 Tee1 | Tewantin | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Rural | 170
|  |  |  | 10 POE Load (A) | 165 | 163 | 162 | 160 | 159
|  |  |  | Power Factor | 0.95179 | 0.95227 | 0.95254 | 0.9529 | 0.95303
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 442 | 437 | 433 | 428 | 426
Sunrise Hills Bulk | 343-3 | 343 Tee1 | Cooroy | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Rural | 170
|  |  |  | 10 POE Load (A) | 287 | 284 | 284 | 282 | 282
|  |  |  | Power Factor | 0.99472 | 0.99481 | 0.99481 | 0.99485 | 0.99485
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | 50 POE Load (A) | 265 | 260 | 259 | 257 | 256
Sunrise Hills Bulk | 346-1 | Sunrise Hills BS | 346 Tee1 | NCC Rating (A) | 976 | 976 | 976 | 976 | 976 | Urban | 70
|  |  |  | 10 POE Load (A) | 311 | 307 | 305 | 301 | 301
|  |  |  | Power Factor | 0.97586 | 0.97618 | 0.97636 | 0.97674 | 0.97683
|  |  |  | ECC Rating (A) | 976 | 976 | 976 | 976 | 976
|  |  |  | 50 POE Load (A) | 442 | 436 | 432 | 427 | 425
Sunrise Hills Bulk | 346-2 | 346 Tee1 | Tewantin | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
|  |  |  | 10 POE Load (A) | 311 | 307 | 305 | 302 | 301
|  |  |  | Power Factor | 0.97586 | 0.97618 | 0.97636 | 0.97674 | 0.97683
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 442 | 436 | 432 | 427 | 425
Sunrise Hills Bulk | 346-3 | 346 Tee1 | 3100 Tee1 | NCC Rating (A) | 529 | 529 | 529 | 529 | 529 | Urban | 70
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0.00030746 | 0.00030705 | 0.00030777 | 0.00030722 | 0.00030738
|  |  |  | ECC Rating (A) | 529 | 529 | 529 | 529 | 529
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Sunrise Hills Bulk | 488-1 | Cooroy | 488 Tee1 | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170
|  |  |  | 10 POE Load (A) | 142 | 141 | 141 | 140 | 140
|  |  |  | Power Factor | 0.99579 | 0.99582 | 0.99582 | 0.9959 | 0.9959
|  |  |  | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
|  |  |  | 50 POE Load (A) | 132 | 129 | 128 | 128 | 127
Sunrise Hills Bulk | 488-3 | 488 Tee1 | 488 Tee2 | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
|  |  |  | 10 POE Load (A) | 142 | 141 | 141 | 140 | 140
|  |  |  | Power Factor | 0.99604 | 0.99608 | 0.99608 | 0.99615 | 0.99615
|  |  |  | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | 50 POE Load (A) | 132 | 129 | 128 | 128 | 127
Sunrise Hills Bulk | 488-4 | 488 Tee2 | Black Mtn | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
|  |  |  | 10 POE Load (A) | 64 | 63 | 62 | 61 | 61
|  |  |  | Power Factor | 0.98873 | 0.98884 | 0.98878 | 0.99025 | 0.99025
|  |  |  | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | 50 POE Load (A) | 58 | 57 | 57 | 56 | 55
Sunrise Hills Bulk | 488-5 | 488 Tee2 | 488 Tee3 | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
|  |  |  | 10 POE Load (A) | 79 | 79 | 79 | 79 | 79
|  |  |  | Power Factor | 0.99918 | 0.99918 | 0.99918 | 0.99918 | 0.99918
|  |  |  | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | 50 POE Load (A) | 74 | 72 | 72 | 71 | 71
Sunrise Hills Bulk | 488-6 | 488 Tee3 | Eumundi | NCC Rating (A) | 438 | 438 | 438 | 438 | 438 | Rural | 170
|  |  |  | 10 POE Load (A) | 79 | 79 | 79 | 79 | 79
|  |  |  | Power Factor | 0.9986 | 0.9986 | 0.9986 | 0.9986 | 0.9986
|  |  |  | ECC Rating (A) | 438 | 438 | 438 | 438 | 438
|  |  |  | 50 POE Load (A) | 74 | 72 | 72 | 72 | 72
Sunrise Hills Bulk | 488-7 | 488 Tee3 | Yandina | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
|  |  |  | 10 POE Load (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 3.6886e-05 | 3.6886e-05 | 3.6886e-05 | 3.6886e-05 | 3.6886e-05
|  |  |  | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | 50 POE Load (A) | 1 | 1 | 1 | 1 | 1
Tennyson Bulk | 3390-1 | Taringa | Indooroopilly | NCC Rating (A) | 728 | 728 | 728 | 728 | 728 | Urban | 70
|  |  |  | 10 POE Load (A) | 128 | 129 | 127 | 125 | 124
|  |  |  | Power Factor | 0.94224 | 0.94393 | 0.94432 | 0.94505 | 0.94517
|  |  |  | ECC Rating (A) | 728 | 728 | 728 | 728 | 728
|  |  |  | 50 POE Load (A) | 172 | 173 | 171 | 168 | 167
Tennyson Bulk | 3393-1 | Tennyson BS | St Lucia TR1 | NCC Rating (A) | 610 | 610 | 610 | 610 | 610 | Urban | 70
|  |  |  | 10 POE Load (A) | 119 | 117 | 116 | 114 | 113
|  |  |  | Power Factor | 0.99221 | 0.99234 | 0.9924 | 0.99254 | 0.99257
|  |  |  | ECC Rating (A) | 610 | 610 | 610 | 610 | 610
|  |  |  | 50 POE Load (A) | 227 | 224 | 222 | 218 | 216
Tennyson Bulk | 3394-1 | Tennyson BS | St Lucia TR2 | NCC Rating (A) | 610 | 610 | 610 | 610 | 610 | Urban | 70
|  |  |  | 10 POE Load (A) | 238 | 234 | 232 | 228 | 227
|  |  |  | Power Factor | 0.98568 | 0.98606 | 0.98622 | 0.98659 | 0.98667
|  |  |  | ECC Rating (A) | 610 | 610 | 610 | 610 | 610
|  |  |  | 50 POE Load (A) | 227 | 223 | 222 | 218 | 216
Tennyson Bulk | 3460-1 | Annerley | Buranda | NCC Rating (A) | 802 | 802 | 802 | 802 | 802 | Urban | 70
|  |  |  | 10 POE Load (A) | 178 | 253 | 254 | 254 | 257
|  |  |  | Power Factor | 0.97378 | 0.96533 | 0.96522 | 0.96522 | 0.96489
|  |  |  | ECC Rating (A) | 802 | 802 | 802 | 802 | 802
|  |  |  | 50 POE Load (A) | 339 | 488 | 489 | 491 | 495
Tennyson Bulk | 3461-1 | Annerley | Buranda | NCC Rating (A) | 802 | 802 | 802 | 802 | 802 | Urban | 70
|  |  |  | 10 POE Load (A) | 178 | 254 | 254 | 254 | 257
|  |  |  | Power Factor | 0.97381 | 0.96536 | 0.96525 | 0.96525 | 0.96492
|  |  |  | ECC Rating (A) | 802 | 802 | 802 | 802 | 802
|  |  |  | 50 POE Load (A) | 339 | 488 | 489 | 491 | 495
Tennyson Bulk | 410-1 | Sherwood | Indooroopilly | NCC Rating (A) | 400 | 400 | 400 | 400 | 400 | Urban | 70
|  |  |  | 10 POE Load (A) | 244 | 236 | 234 | 230 | 229
|  |  |  | Power Factor | 0.97645 | 0.97704 | 0.97731 | 0.97777 | 0.97788
|  |  |  | ECC Rating (A) | 400 | 400 | 400 | 400 | 400
|  |  |  | 50 POE Load (A) | 372 | 361 | 357 | 352 | 350
Tennyson Bulk | 460-1 | Tennyson BS | Sherwood | NCC Rating (A) | 762 | 762 | 762 | 762 | 762 | Urban | 70
|  |  |  | 10 POE Load (A) | 396 | 397 | 393 | 387 | 386
|  |  |  | Power Factor | 0.98001 | 0.97982 | 0.98011 | 0.98069 | 0.98081
|  |  |  | ECC Rating (A) | 762 | 762 | 762 | 762 | 762
|  |  |  | 50 POE Load (A) | 516 | 519 | 514 | 506 | 504
Tennyson Bulk | 480-1 | Taringa | St Lucia | NCC Rating (A) | 610 | 610 | 610 | 610 | 610 | Urban | 70
|  |  |  | 10 POE Load (A) | 117 | 115 | 114 | 112 | 111
|  |  |  | Power Factor | 0.99617 | 0.99626 | 0.99628 | 0.99636 | 0.99638
|  |  |  | ECC Rating (A) | 610 | 610 | 610 | 610 | 610
|  |  |  | 50 POE Load (A) | 227 | 223 | 221 | 218 | 216
Tennyson Bulk | 504-1 | Tennyson BS | Taringa | NCC Rating (A) | 601 | 601 | 601 | 601 | 601 | Urban | 70
|  |  |  | 10 POE Load (A) | 320 | 316 | 313 | 308 | 307
|  |  |  | Power Factor | 0.98594 | 0.98634 | 0.98655 | 0.98694 | 0.98701
|  |  |  | ECC Rating (A) | 601 | 601 | 601 | 601 | 601
|  |  |  | 50 POE Load (A) | 451 | 447 | 442 | 436 | 434
Tennyson Bulk | 507A-1 | Toowong | Indooroopilly | NCC Rating (A) | 735 | 735 | 735 | 735 | 735 | Urban | 70
|  |  |  | 10 POE Load (A) | 131 | 131 | 130 | 128 | 127
|  |  |  | Power Factor | 0.94778 | 0.94939 | 0.94978 | 0.95048 | 0.95059
|  |  |  | ECC Rating (A) | 735 | 735 | 735 | 735 | 735
|  |  |  | 50 POE Load (A) | 174 | 175 | 173 | 170 | 169
Tennyson Bulk | 507B-1 | Toowong | Taringa | NCC Rating (A) | 727 | 727 | 727 | 727 | 727 | Urban | 70
|  |  |  | 10 POE Load (A) | 129 | 129 | 128 | 126 | 125
|  |  |  | Power Factor | 0.9615 | 0.96289 | 0.96335 | 0.96422 | 0.96439
|  |  |  | ECC Rating (A) | 727 | 727 | 727 | 727 | 727
|  |  |  | 50 POE Load (A) | 172 | 173 | 171 | 168 | 167
Tennyson Bulk | 511-1 | Tennyson BS | Moorooka | NCC Rating (A) | 739 | 739 | 739 | 739 | 739 | Urban | 70
|  |  |  | 10 POE Load (A) | 169 | 168 | 168 | 167 | 167
|  |  |  | Power Factor | 0.97558 | 0.97567 | 0.97576 | 0.97585 | 0.97585
|  |  |  | ECC Rating (A) | 739 | 739 | 739 | 739 | 739
|  |  |  | 50 POE Load (A) | 153 | 152 | 151 | 150 | 151
Tennyson Bulk | 514-1 | Tennyson BS | Moorooka | NCC Rating (A) | 739 | 739 | 739 | 739 | 739 | Urban | 70
|  |  |  | 10 POE Load (A) | 169 | 168 | 168 | 167 | 167
|  |  |  | Power Factor | 0.97597 | 0.97606 | 0.97615 | 0.97623 | 0.97623
|  |  |  | ECC Rating (A) | 739 | 739 | 739 | 739 | 739
|  |  |  | 50 POE Load (A) | 153 | 152 | 151 | 150 | 151
Tennyson Bulk | 515-1 | Tennyson BS | Sherwood | NCC Rating (A) | 740 | 740 | 740 | 740 | 740 | Urban | 70
|  |  |  | 10 POE Load (A) | 420 | 421 | 417 | 410 | 409
|  |  |  | Power Factor | 0.98356 | 0.98339 | 0.98365 | 0.98418 | 0.98429
|  |  |  | ECC Rating (A) | 740 | 740 | 740 | 740 | 740
|  |  |  | 50 POE Load (A) | 547 | 551 | 545 | 537 | 535
Tennyson Bulk | 523A-1 | Tennyson BS | Rocklea | NCC Rating (A) | 650 | 650 | 650 | 650 | 650 | Urban | 70
|  |  |  | 10 POE Load (A) | 8 | 8 | 8 | 8 | 8
|  |  |  | Power Factor | 8.7628e-06 | 8.7628e-06 | 8.7628e-06 | 8.7628e-06 | 8.7628e-06
|  |  |  | ECC Rating (A) | 650 | 650 | 650 | 650 | 650
|  |  |  | 50 POE Load (A) | 8 | 8 | 8 | 8 | 8
Tennyson Bulk | 539-1 | Sherwood | Kenmore | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 260
|  |  |  | 10 POE Load (A) | 264 | 259 | 257 | 253 | 252
|  |  |  | Power Factor | 0.98318 | 0.98378 | 0.98413 | 0.98461 | 0.9847
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | 50 POE Load (A) | 558 | 547 | 541 | 533 | 531
Tennyson Bulk | 554-1 | Tennyson BS | Sherwood | NCC Rating (A) | 716 | 716 | 716 | 716 | 716 | Urban | 70
|  |  |  | 10 POE Load (A) | 446 | 447 | 443 | 435 | 434
|  |  |  | Power Factor | 0.9809 | 0.98072 | 0.98099 | 0.98152 | 0.98163
|  |  |  | ECC Rating (A) | 716 | 716 | 716 | 716 | 716
|  |  |  | 50 POE Load (A) | 567 | 571 | 565 | 556 | 554
Tennyson Bulk | 571-1 | Indooroopilly | Kenmore | NCC Rating (A) | 527 | 527 | 527 | 527 | 527 | Urban | 260
|  |  |  | 10 POE Load (A) | 341 | 335 | 332 | 326 | 325
|  |  |  | Power Factor | 0.97278 | 0.97347 | 0.97377 | 0.97434 | 0.97445
|  |  |  | ECC Rating (A) | 527 | 527 | 527 | 527 | 527
|  |  |  | 50 POE Load (A) | 550 | 538 | 533 | 525 | 523
Tennyson Bulk | 606-1 | Tennyson BS | Taringa | NCC Rating (A) | 601 | 601 | 601 | 601 | 601 | Urban | 70
|  |  |  | 10 POE Load (A) | 322 | 317 | 315 | 310 | 309
|  |  |  | Power Factor | 0.98597 | 0.98637 | 0.98658 | 0.98696 | 0.98704
|  |  |  | ECC Rating (A) | 601 | 601 | 601 | 601 | 601
|  |  |  | 50 POE Load (A) | 452 | 448 | 443 | 437 | 435
Tennyson Bulk | 637-1 | Tennyson BS | Annerley | NCC Rating (A) | 716 | 716 | 716 | 716 | 716 | Urban | 70
|  |  |  | 10 POE Load (A) | 328 | 402 | 403 | 402 | 405
|  |  |  | Power Factor | 0.98206 | 0.9761 | 0.97602 | 0.97603 | 0.97578
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 629 | 776 | 778 | 776 | 782
Tennyson Bulk | 638-1 | Tennyson BS | Annerley | NCC Rating (A) | 716 | 716 | 716 | 716 | 716 | Urban | 70
|  |  |  | 10 POE Load (A) | 329 | 404 | 405 | 404 | 407
|  |  |  | Power Factor | 0.98208 | 0.97612 | 0.97603 | 0.97604 | 0.97579
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 628 | 776 | 778 | 776 | 782
Tennyson Bulk | F703-1 | Sherwood | Indooroopilly | NCC Rating (A) | 400 | 400 | 400 | 400 | 400 | Urban | 70
|  |  |  | 10 POE Load (A) | 246 | 238 | 236 | 232 | 231
|  |  |  | Power Factor | 0.97678 | 0.97738 | 0.97764 | 0.97811 | 0.97821
|  |  |  | ECC Rating (A) | 400 | 400 | 400 | 400 | 400
|  |  |  | 50 POE Load (A) | 374 | 363 | 359 | 353 | 352
Victoria Park Bulk | 627-1 | Victoria Pk BS | Astor Tce | NCC Rating (A) | 415 | 415 | 415 | 415 | 415 | Urban | 70
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0.96802 | 0.96802 | 0.96802 | 0.96802 | 0.96802
|  |  |  | ECC Rating (A) | 415 | 415 | 415 | 415 | 415
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Victoria Park Bulk | 628-1 | Victoria Pk BS | Astor Tce | NCC Rating (A) | 415 | 415 | 415 | 415 | 415 | Urban | 70 | 2
|  |  |  | 10 POE Load (A) | 216 | 214 | 212 | 210 | 209
|  |  |  | Power Factor | 0.99432 | 0.99446 | 0.99455 | 0.99468 | 0.99472
|  |  |  | ECC Rating (A) | 415 | 415 | 415 | 415 | 415
|  |  |  | 50 POE Load (A) | 425 | 419 | 428 | 423 | 421
Victoria Park Bulk | 639-1 | Victoria Pk BS | Newmarket | NCC Rating (A) | 503 | 503 | 503 | 503 | 503 | Urban | 70
|  |  |  | 10 POE Load (A) | 212 | 208 | 205 | 203 | 202
|  |  |  | Power Factor | 0.97679 | 0.97715 | 0.97741 | 0.97714 | 0.97723
|  |  |  | ECC Rating (A) | 503 | 503 | 503 | 503 | 503
|  |  |  | 50 POE Load (A) | 401 | 394 | 391 | 384 | 382
Victoria Park Bulk | 649-1 | Victoria Pk BS | Astor Tce | NCC Rating (A) | 415 | 415 | 415 | 415 | 415 | Urban | 70 | 17
|  |  |  | 10 POE Load (A) | 219 | 216 | 215 | 212 | 211
|  |  |  | Power Factor | 0.99444 | 0.99458 | 0.99466 | 0.99479 | 0.99484
|  |  |  | ECC Rating (A) | 415 | 415 | 415 | 415 | 415
|  |  |  | 50 POE Load (A) | 424 | 419 | 428 | 423 | 421
Victoria Park Bulk | 653-1 | Victoria Pk BS | Newmarket | NCC Rating (A) | 503 | 503 | 503 | 503 | 503 | Urban | 70
|  |  |  | 10 POE Load (A) | 212 | 208 | 205 | 203 | 202
|  |  |  | Power Factor | 0.97679 | 0.97715 | 0.97741 | 0.97714 | 0.97723
|  |  |  | ECC Rating (A) | 503 | 503 | 503 | 503 | 503
|  |  |  | 50 POE Load (A) | 401 | 394 | 391 | 384 | 382
Victoria Park Bulk | 689-1 | Victoria Pk BS | Astor Tce | NCC Rating (A) | 538 | 538 | 538 | 538 | 538 | Urban | 70
|  |  |  | 10 POE Load (A) | 9 | 9 | 9 | 9 | 9
|  |  |  | Power Factor | 1.0298e-05 | 1.0298e-05 | 1.0298e-05 | 1.0298e-05 | 1.0298e-05
|  |  |  | ECC Rating (A) | 538 | 538 | 538 | 538 | 538
|  |  |  | 50 POE Load (A) | 9 | 9 | 9 | 9 | 9