## Note
Sub-Transmission Feeders Forecasts (Energex Distribution Annual Planning Report 2019-20 to 2023-24)
This workbook provides 5 year forecast capacity and loading information for sub-transmission feeders in the Energex network.
This workbook forms part of the Energex Distribution Annual Planning Report 2019-20 to 2023-24 (DAPR) and should be read in conjunction with the report document.
Energex Distribution Annual Planning Report is prepared and made available solely for information purposes. While care was taken in the preparation of the information in this report, and it is provided in good faith, Energex accepts no responsibility or liability (including without limitation, liability to any person by reason of negligence or negligent mis-statement) for any loss or damage that may be incurred by any person acting in reliance on this information or assumptions drawn from it, except to the extent that liability under any applicable Queensland or Commonwealth of Australia statute cannot be excluded.
It contains assumptions regarding, among other things, economic growth and load forecasts which may or may not prove to be correct. The forecasts included in the document involve subjective judgements and analysis which are subject to significant uncertainties and contingencies, many of which are out of the control of Energex. Energex makes no representation or warranty as to the accuracy, reliability, completeness or suitability for any particular purpose of the information in this document. All information should be independently investigated, reviewed, analysed and verified, and must not be relied upon in connection with any investment proposal or decision.
All financials presented in this document are correct at the time of writing and represent the existing organisational accounting treatment, which may be subject to change. Energy Queensland is finalising the alignment of its Cost Allocation Methodology between Ergon and Energex, potentially impacting the treatment of some Capital and Operational Project costs.
The following sections list the 33 kV feeders, their forecast loads and their capacity limitations. The feeder loads are calculated from load flow results using forecast substation demands. For the transmission and sub-transmission feeders, load flow studies are conducted for system normal and single contingency situations.
These tables show information about the feeder capacity, load at risk, and the compliance of each feeder with its security standard. To assess whether a feeder meets its security standard, four possible risk periods are considered: winter day, winter night, summer day and summer night. The highest risk period for each season is displayed for each year of the forward planning period.
The forecast and capacity cut-off date for the winter season is 1 June of each year, and for the summer season is 1 December of each year. For example, 2019 winter forecast includes all committed projects with a proposed commissioning date up to 1 June 2019, and the 2019/20 summer forecast includes all committed projects with a proposed commissioning date up to 1 December 2019.
Assessment of 33 kV feeders is performed under four possible risk periods: winter day, winter night, summer day and summer night.
Peak, reconciled, compensated load forecasts have been used in the 33 kV feeder analyses, with 50 PoE forecast load used for single contingency studies, and 10 PoE forecast load used for system normal studies.
Feeder capacities are shown for 2HEC, ECC and NCC. These ratings have also been adjusted for known committed project proposals. All load transfers associated with contingent condition include acceptable feeder voltage profiles.
Although the conductor rating is generally the limiting factor for feeder capacity, there are other significant items of plant, such as the feeder circuit breaker, that can also restrict capacity. Furthermore, other factors such as voltage constraints and load sharing between parallel underground feeders can sometimes de‑rate the capacity of the feeders due to thermal characteristic constraints. Each of these factors has been taken into account in the production of the forecast tables.
The tables also show, for each of the next five years, the compliance of each feeder with its security standard. The peak risk period is the one with the highest calculated load at risk (normal or contingency). Load at risk is calculated using the forecast loads, the feeder capacity, and the capacity of the network to allow the transfer of load away from the feeder to an alternative source of supply. A detailed explanation of the derivation of load at risk is provided in Section F.2.4. If there is no load at risk, then a feeder meets the security standard.
Interconnected or feeders that supply multiple customers are examined in the following tables. Feeders exclusively supplying a customer owned substation or dedicated to a customer are not included in these tables. For transmission and sub-transmission feeders, if there is any load at risk during normal or contingent conditions, the feeder is flagged as not meeting the security standard. Although this may in some cases arise due to inadequate supply for only short periods of time, this approach has been adopted as the best means of fully assessing whether the security standard is being met. As such it will provide evidence of benefits arising from such activities as the installation of remotely controlled switchgear to bolster remote transfer capabilities where these exist.
The 33 kV forecast tables provide load at risk based on a contingent event as described above. For contingencies where automatic transfers via auto change-over schemes are available, N-1 load at risk is shown only if the automatic transfers are not sufficient to fully restore supply to customers.
A definition of terms is shown in the table below.
Definition of Terms Feeder Capacity and Forecast Tables
Term | Definition
NCC Rating (A) | Normal Cyclic Capacity - the total capacity with all network components and equipment intact.
This is the maximum permissible peak daily loading for a given load cycle that a feeder can supply each day of its life. For overhead feeders, the NCC is the conductor rating with an assumed 1m/s wind, orthogonal to the line. For underground cables, the NCC assumes that there are sufficient temperature and current operating margins from the thermal inertia of the cable and its surroundings.
10 PoE Load (A) | Peak load forecast with 10% probability of being exceeded (one in every 10 years will be exceeded). Based on normal expected growth rates and weather corrected starting loads.
Power Factor (System Normal) | Lowest power factor along the feeder at 10 PoE Peak Load.
LARn (A) | Security standard load at risk under system normal condition, expressed in Amps.
LARn (MW) | Security standard load at risk under system normal condition, expressed in MW, assuming the nominal system voltages and lowest power factor.
(LARn (A) x Nominal Voltage x Power Factor (System Normal) x sqrt(3))
1000000
ECC Rating (A) | Emergency Cyclic Capacity – the long term firm delivery capacity under single contingency conditions.
Some underground cables are installed in close proximity to other circuits and are normally de‑rated to allow for the heat generated by the adjacent cables. ECC is the higher capacity available when any adjacent circuits have been unloaded. For overhead conductors which do not benefit from this phenomenon, the ECC is synonymous with the NCC.
50 PoE Load (A) | Peak load forecast with 50% probability of being exceeded (one in every two years will be exceeded). Based on normal expected growth rates & weather corrected starting loads.
Hours PA > 95% Peak Load | The forecast number of hours per annum where the load exceeded 95% of the peak 50 PoE demand.
Raw LAR (A) | The amount of load exceeding ECC rating. (Load – ECC Rating)
2-Hour Rating (A) | Two Hour Emergency Capacity (2HEC) – the short term firm delivery capacity under single contingency conditions.
For overhead feeders, the 2HEC is the conductor rating with an assumed 2m/s wind, orthogonal to the line (compared to the 1.0 m/s wind speed used for NCC ratings).
For underground cables, the 2HEC assumes that there are sufficient temperature and current operating margins immediately prior to the contingency to extract additional capacity from the thermal inertia of the cable and its surrounds.
Auto Trans Avail (A) | SCADA or automatically controlled load transfers that can be implemented within one minute. Examples include auto changeover switching to alternate feeders.
A blank entry indicates that this type of transfer is not considered as available in the evaluation of security standard compliance.
Remote Trans Avail (A) | Load transfers that can be implemented through SCADA switching procedures by the network control officer. It is assumed that this can generally be achieved within 30 minutes.
A blank entry indicates that this type of transfer is not considered as available in the evaluation of security standard compliance.
Manual Trans Avail (A) | Load transfers can also be deployed via manually controlled switchgear locally by field staff. It is assumed the implementation of manual switching procedures to isolate the faulted portion of the network whilst restoring supply to fault free portions can be fully implemented within three hours (urban) or four hours (rural).
Manual transfers are obtained from load flow studies performed on each 11 kV distribution feeder based on the forecast 2018/19 load, the sum of all available 11 kV transfers at a substation is multiplied by a 0.75 factor to account for diversity and to provide an error margin. The same amount of transfers is applied throughout the forward planning period.
A blank entry indicates that this type of transfer is not considered as available in the evaluation of security standard compliance.
POPS | Plant Overload Protection Scheme (POPS) consists of several applications which continuously monitor specific items of plant for overload conditions. If overload conditions are detected and validated, POPS will initiate predefined actions in order to relieve the overload condition.
Mobile Gen Reqd (A) | The amount of generation required under the contingency, capped at the maximum MVA allowable under the security standard requirements.
Where required, alternate supply from mobile generators can be sourced within 8 hours (urban) or 12hours (rural). These are generally smaller 500kVA units that do not require transport permits or police escorts and can be rapidly deployed. Up to 4 MVA (urban) or 10 MVA (rural) of mobile generation may be committed to a single contingency event.
LARc (A) | Security standards load at risk under single contingency condition, expressed in Amps.
LARc (MW) | Estimated generation / load reduction required to defer the forecast system limitation.
This is the security standard load at risk under single contingency condition, expressed in MW, assuming the nominal system voltages and the lowest power factor on the feeder under system normal condition.
(LARc (A) x Nominal Voltage x Power Factor (System Normal) x sqrt(3))
1000000
Customer Category | For security standard application, the general type of customer a sub-transmission, or transmission feeder is supplying.
The Load at Risk (LAR) is evaluated for both normal (LARn) and contingent (LARc) conditions. Under normal conditions, the loading on a substation is not to exceed the normal cyclic capacity (NCC) of the supplying feeders. Under contingent conditions, the loading of a substation is not to exceed the available supply, whilst taking into consideration the security of supply standards of the supplying feeder.
Load at risk is the shortfall between the feeder forecast load (either 10 PoE or 50 PoE) and the available supply. The equations for feeder LAR are as follows:
· LARn = 10 PoE – NCC where NCC is the normal cyclic capacity
· LARc = 50 PoE – available capacity – available supply (within security standard timeframe)
Network security standards are not being met if LARn or LARc is greater than 0.
Generally, there are two available capacities and four available sources of supply that can be deployed upon loss of a major network component such as a sub-transmission/transmission feeder.
Types of available capacity:
· Emergency Cyclic Capacity (ECC) – Some underground cables are installed in close proximity to other circuits and are normally de-rated to allow for the heat generated by the adjacent cables. ECC is the higher capacity available when any adjacent circuits have been unloaded. For overhead conductors which do not benefit from this phenomenon, the ECC is synonymous with the NCC.
· Two Hour Emergency Capacity (2HEC) – For overhead feeders, the 2HEC is the conductor rating with an assumed 2m/s wind, orthogonal to the line (compared to the 1.0 m/s wind speed used for NCC ratings). For underground cables, the 2HEC assumes that there are sufficient temperature and current operating margins immediately prior to the contingency to extract additional capacity from the thermal inertia of the cable and its surroundings. The philosophy of using 2HEC feeder ratings assumes that load is reduced to ECC (if appropriate) or NCC by the end of 2 hours at this capacity.
Types of available supply:
· Automatic Transfers (AT) – SCADA or automatically controlled load transfers that can be implemented within 1 minute. Examples include auto changeover switching to alternate feeders. Such capacity has been considered where it is available.
· Remote Transfers (RT) – Most of the transmission and sub-transmission network employs remotely controlled switchgear. Some load transfers can therefore be achieved through SCADA switching procedures.
· Manual Transfers (MT) – Load transfers can also be deployed via manually controlled switchgear. The implementation of manual switching procedures to isolate the faulted portion of the network whilst restoring supply to fault free portions can be fully implemented within 3 hours (urban) or 4 hours (rural) and is available for extended periods.
· Mobile Generation (MG) – Alternate supply from mobile generators can be sourced within 8 hours (urban) or 12 hours (rural). These are generally smaller 500 kVA units that do not require transport permits or police escorts and can be rapidly deployed. Up to 4 MVA (urban) or 10 MVA (rural) of mobile generation may be committed to a single contingency event.

## Index
Feeder names in ascending order
Index
357-1
357-2
357-3
358-1
364-1
365-1
365-2
365-3
366-1
366-2
366-3
367-1
368-1
369-1
370-1
387-1
3901-1
420-1
436-1
436-2
436-4
445-1
475-1
673-1
3400-1
3402-1
3403-1
3405-1
597-1
635-1
650-1
651-1
432-1
552-1
565-1
570-1
585-1
586-1
590-1
591-1
675-1
676-1
314-1
404-1
466-1
467-1
468-1
469-1
469-2
469-3
3590-1
3591-1
3600-1
3601-1
3620-1
402-1
402-2
402-3
405-1
405-3
419-1
426-1
427-1
453-1
496-1
324-1
428-1
447-1
477-1
477-2
477-3
608-1
527-1
631-1
632-1
647-1
660-1
661-1
662-1
663-1
692-1
693-1
303-1
309-1
309-2
309-3
310-1
310-2
310-3
333-1
3340-1
334-1
334-2
334-3
335-1
335-2
335-3
336-1
3364-1
337-1
342-1
349-1
464-1
406A-1
406B-1
478-1
481-1
482-1
542-1
3751-1
3755-1
3756-1
3756-2
3756-3
3756-4
393-1
395-1
396-1
397-1
397-3
397-4
397-5
321-1
322-1
323-1
323-2
323-3
350-1
412-1
417-1
431-1
448-1
448-2
448-3
457-1
461-1
499-1
3550-1
3570-1
3580-1
3580-2
3580-3
371-1
372-1
373-1
374-1
375-1
375-2
375-3
413-1
425-1
465-1
484-1
3640-1
3641-1
3642-1
394-1
3429-1
3430-1
584-4
612-1
613-1
648-1
648-2
648-3
3426-1
414-1
416-1
443-1
558-1
563-1
564-1
575C-1
581-1
645-1
677-1
377-1
377-2
377-3
377-4
377-5
3859-1
3860-1
487-1
487-2
487-3
487-6
487-8
487-9
531-1
532-1
533-1
3800-1
3801-1
3802-1
3803-1
3805-1
3806-1
3807-1
3808-1
3809-1
3880-1
3881-1
456-1
456-2
456-3
312-1
320-1
320-2
320-3
3329-1
3329-2
3329-3
3330-1
3330-2
3330-3
3331-1
3331-3
3359-1
3359-2
3359-3
3359-4
3359-5
3359-6
3359-7
338-1
3004-1
3005-1
3009-1
3011-1
339/2-1
339/2-2
339-1
339-2
339-3
340-1
340-2
340-4
340-5
340-6
340-7
340-8
340-9
341-1
341-2
341-3
341-4
351-1
429-1
429-2
429-3
305-1
311-1
3250-1
325-1
3251-1
326-1
327-1
329-1
330-1
331-1
332-1
451-1
497-1
470-1
479-1
378-1
378-2
378-3
378-4
378-5
380-1
380-2
380-3
381-1
381-2
381-3
381-4
381-5
381-6
381-7
381-8
381-9
382-1
382-2
382-3
3828-1
3829-1
3831-1
3832-1
3832-2
3832-3
3840-1
384-1
384-2
384-3
3870-1
3871-1
407-1
408-1
409-1
418-1
452-1
3302-1
3303-1
490-1
491-1
492-1
493-1
494-1
495-1
560-1
560-14
560-15
560-16
560-2
560-3
560-5
569-1
599-1
681-1
682-1
687-1
687-2
687-3
688-1
3374-1
506-1
513-1
553-1
556-1
609-1
610-1
3670-1
3671-1
389-1
389-2
389-3
390-1
390-2
390-3
391-1
392-1
421-1
458-1
473-1
474A-1
474B-1
486-1
3700-1
3700-2
3700-3
3700-4
3700-5
3701-1
307-1
307-2
344-1
345-1
347-1
347-2
347-3
348-1
489-1
3280-1
535-1
540-1
593-1
604-1
605-1
622-1
623-1
636-1
643-1
674-1
683-1
684-1
376-1
379-1
379-2
354-1
355-1
361-1
362-1
362-2
362-3
363-1
363-2
363-3
3960-1
3972-1
3980-1
401-1
411-1
509A-1
509B-1
510A-1
510B-1
3818-1
454-1
455-1
543-1
543-2
543-3
616-1
617-1
618-1
619-1
620-1
621-1
641-1
642-1
679-1
680-1
700-1
3440-1
433-1
434-1
459A-1
459B-1
667-1
668-1
690-1
691-1
694-1
3290-1
505-1
524-1
524-2
561-1
656-1
664-1
671-1
502-1
522-1
525-1
534-1
548-1
550-1
551-1
567-1
568-1
594-1
595-1
596-1
607-1
308-1
308-2
308-3
3100-1
343-1
343-2
343-3
346-1
346-2
346-3
488-1
488-3
488-4
488-5
488-6
488-7
3390-1
3393-1
3394-1
3460-1
3461-1
410-1
460-1
480-1
504-1
507A-1
507B-1
511-1
514-1
515-1
523A&B-1
523A-1
539-1
554-1
571-1
606-1
637-1
638-1
F703-1
627-1
628-1
639-1
649-1
653-1
659B-1
689-1

## 33kV Feeders-Summer
33 kV Fdr Sum | From | To | Fdr OOS | Parameter | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24
ABERMAIN Bulk Supply Point:
357-1 | Abermain BSP |  |  | NCC Rating (A) | 505 | 505 | 505 | 505 | 505
| (ABM) | (357 Tee1) |  | 10 PoE Load (A) | 167 | 166 | 165 | 165 | 163
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
357-2 |  | Redbank |  | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
| (357 Tee1) | (RBK) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
357-3 |  | Moggill |  | NCC Rating (A) | 710 | 710 | 710 | 710 | 710
| (357 Tee1) | (MGL) |  | 10 PoE Load (A) | 169 | 168 | 167 | 166 | 164
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
358-1 | Abermain BSP |  |  | NCC Rating (A) | 473 | 473 | 473 | 473 | 473
| (ABM) | (P14607-H) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
ABERMAIN Bulk Supply Point:
364-1 | Marburg | Rosewood |  | NCC Rating (A) | 155 | 155 | 155 | 155 | 155
| (MBG) | (RWD) |  | 10 PoE Load (A) | 89 | 94 | 106 | 115 | 122
|  |  |  | Power Factor (System Normal) | 1 | 1 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 365 | ECC Rating (A) |  |  | 155 | 155 | 155
|  |  |  | 50 PoE Load (A) |  |  | 158 | 173 | 185
|  |  |  | Raw LAR (A) |  |  | 3 | 18 | 30
|  |  |  | 2-Hour Rating (A) |  |  | 194 | 194 | 194
Auto Trans Avail (A)
Remote Trans Avail (A)
|  |  |  | Manual Trans Avail (A) |  |  | 16 | 16 | 17
|  |  |  | POPS Available |  |  | No | No | No
|  |  |  | Mobile Gen Reqd (A) |  |  | 0 | 2 | 13
|  |  |  | LARc (A) |  |  | 0 | 0 | 0
|  |  |  | LARc (MW) |  |  | 0 | 0 | 0
|  |  | 366 | ECC Rating (A) |  |  | 155 | 155 | 155
|  |  |  | 50 PoE Load (A) |  |  | 171 | 187 | 201
|  |  |  | Hours PA > 95% Peak Load |  |  |  |  | 0.5
|  |  |  | Raw LAR (A) |  |  | 16 | 32 | 46
|  |  |  | 2-Hour Rating (A) |  |  | 194 | 194 | 194
Auto Trans Avail (A)
Remote Trans Avail (A)
|  |  |  | Manual Trans Avail (A) |  |  | 18 | 18 | 20
|  |  |  | POPS Available |  |  | No | No | No
|  |  |  | Mobile Gen Reqd (A) |  |  | 0 | 14 | 26
|  |  |  | LARc (A) |  |  | 0 | 0 | 7
|  |  |  | LARc (MW) |  |  | 0 | 0 | 0.4
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | No
ABERMAIN Bulk Supply Point:
365-1 | Abermain BSP |  |  | NCC Rating (A) | 746 | 746 | 746 | 746 | 746
| (ABM) | (365 Tee1) |  | 10 PoE Load (A) | 376 | 393 | 434 | 467 | 493
|  |  |  | Power Factor (System Normal) | 0.91 | 0.91 | 0.9 | 0.9 | 0.89
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 366 | ECC Rating (A) |  |  | 746 | 746 | 746
|  |  |  | 50 PoE Load (A) |  |  | 791 | 863 | 919
|  |  |  | Hours PA > 95% Peak Load |  |  |  |  | 0.5
|  |  |  | Raw LAR (A) |  |  | 45 | 117 | 173
|  |  |  | 2-Hour Rating (A) |  |  | 871 | 871 | 871
Auto Trans Avail (A)
Remote Trans Avail (A)
|  |  |  | Manual Trans Avail (A) |  |  | 93 | 98 | 102
|  |  |  | POPS Available |  |  | No | No | No
|  |  |  | Mobile Gen Reqd (A) |  |  | 0 | 19 | 71
|  |  |  | LARc (A) |  |  | 0 | 0 | 48
|  |  |  | LARc (MW) |  |  | 0 | 0 | 2.4
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | No
365-2 |  |  |  | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
| (365 Tee1) | (366 Tee1) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
ABERMAIN Bulk Supply Point:
365-3 |  | Karrabin |  | NCC Rating (A) | 800 | 800 | 800 | 800 | 800
| (365 Tee1) | (KBN) |  | 10 PoE Load (A) | 377 | 394 | 435 | 468 | 493
|  |  |  | Power Factor (System Normal) | 0.93 | 0.93 | 0.93 | 0.92 | 0.92
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 366 | ECC Rating (A) |  |  |  | 800 | 800
|  |  |  | 50 PoE Load (A) |  |  |  | 863 | 919
|  |  |  | Hours PA > 95% Peak Load |  |  |  | 0.5 | 0.5
|  |  |  | Raw LAR (A) |  |  |  | 63 | 119
|  |  |  | 2-Hour Rating (A) |  |  |  | 800 | 800
Auto Trans Avail (A)
Remote Trans Avail (A)
|  |  |  | Manual Trans Avail (A) |  |  |  | 98 | 102
|  |  |  | POPS Available |  |  |  | No | No
|  |  |  | Mobile Gen Reqd (A) |  |  |  | 0 | 17
|  |  |  | LARc (A) |  |  |  | 63 | 119
|  |  |  | LARc (MW) |  |  |  | 3.3 | 6.3
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | No | No
366-1 | Abermain BSP |  |  | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
| (ABM) | (366 Tee1) |  | 10 PoE Load (A) | 411 | 430 | 474 | 510 | 538
|  |  |  | Power Factor (System Normal) | 0.91 | 0.91 | 0.9 | 0.9 | 0.89
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 365 | ECC Rating (A) |  |  |  | 818 | 818
|  |  |  | 50 PoE Load (A) |  |  |  | 862 | 916
|  |  |  | Hours PA > 95% Peak Load |  |  |  | 3.5 | 3.5
|  |  |  | Raw LAR (A) |  |  |  | 44 | 98
|  |  |  | 2-Hour Rating (A) |  |  |  | 818 | 818
Auto Trans Avail (A)
Remote Trans Avail (A)
|  |  |  | Manual Trans Avail (A) |  |  |  | 96 | 99
|  |  |  | POPS Available |  |  |  | No | No
|  |  |  | Mobile Gen Reqd (A) |  |  |  | 0 | 0
|  |  |  | LARc (A) |  |  |  | 44 | 98
|  |  |  | LARc (MW) |  |  |  | 2.3 | 5
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | No | No
ABERMAIN Bulk Supply Point:
366-2 |  | Karrabin |  | NCC Rating (A) | 758 | 758 | 758 | 758 | 758
| (366 Tee1) | (KBN) |  | 10 PoE Load (A) | 411 | 430 | 474 | 511 | 538
|  |  |  | Power Factor (System Normal) | 0.93 | 0.93 | 0.92 | 0.92 | 0.92
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 365 | ECC Rating (A) |  |  | 758 | 758 | 758
|  |  |  | 50 PoE Load (A) |  |  | 792 | 862 | 916
|  |  |  | Hours PA > 95% Peak Load |  |  |  | 3 | 3
|  |  |  | Raw LAR (A) |  |  | 34 | 104 | 158
|  |  |  | 2-Hour Rating (A) |  |  | 818 | 818 | 818
Auto Trans Avail (A)
Remote Trans Avail (A)
|  |  |  | Manual Trans Avail (A) |  |  | 93 | 96 | 99
|  |  |  | POPS Available |  |  | No | No | No
|  |  |  | Mobile Gen Reqd (A) |  |  | 0 | 8 | 59
|  |  |  | LARc (A) |  |  | 0 | 44 | 98
|  |  |  | LARc (MW) |  |  | 0 | 2.3 | 5.2
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | No | No
366-3 |  |  |  | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
| (366 Tee1) | (365 Tee1) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
ABERMAIN Bulk Supply Point:
367-1 | Abermain BSP | Mt Crosby West |  | NCC Rating (A) | 530 | 530 | 530 | 530 | 530
| (ABM) | (MCW) |  | 10 PoE Load (A) | 295 | 332 | 334 | 361 | 362
|  |  |  | Power Factor (System Normal) | 0.91 | 0.9 | 0.9 | 0.93 | 0.93
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 368-1 | ECC Rating (A) |  | 530 | 530 | 530 | 530
|  |  |  | 50 PoE Load (A) |  | 561 | 562 | 608 | 609
|  |  |  | Raw LAR (A) |  | 31 | 32 | 78 | 79
|  |  |  | 2-Hour Rating (A) |  | 663 | 663 | 663 | 663
Auto Trans Avail (A)
Remote Trans Avail (A)
|  |  |  | Manual Trans Avail (A) |  | 35 | 36 | 36 | 37
|  |  |  | POPS Available |  | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) |  | 0 | 0 | 42 | 42
|  |  |  | LARc (A) |  | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) |  | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
368-1 | Abermain BSP | Customer |  | NCC Rating (A) | 529 | 529 | 529 | 529 | 529
| (ABM) |  |  | 10 PoE Load (A) | 228 | 262 | 264 | 287 | 287
|  |  |  | Power Factor (System Normal) | 0.9 | 0.89 | 0.89 | 0.92 | 0.92
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 367-1 | ECC Rating (A) |  | 529 | 529 | 529 | 529
|  |  |  | 50 PoE Load (A) |  | 568 | 569 | 614 | 615
|  |  |  | Hours PA > 95% Peak Load |  | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Raw LAR (A) |  | 39 | 40 | 85 | 86
|  |  |  | 2-Hour Rating (A) |  | 570 | 570 | 570 | 570
Auto Trans Avail (A)
Remote Trans Avail (A)
|  |  |  | Manual Trans Avail (A) |  | 37 | 37 | 36 | 36
|  |  |  | POPS Available |  | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) |  | 0 | 0 | 0 | 0
|  |  |  | LARc (A) |  | 39 | 40 | 85 | 86
|  |  |  | LARc (MW) |  | 2 | 2 | 4.5 | 4.5
|  |  |  | Customer Category | HighSec | HighSec | HighSec | HighSec | HighSec
|  |  |  | Meets Sec Std | Yes | No | No | No | No
ABERMAIN Bulk Supply Point:
369-1 | Abermain BSP | Nth Ipswich |  | NCC Rating (A) | 499 | 499 | 499 | 499 | 499
| (ABM) | (NIP) |  | 10 PoE Load (A) | 224 | 225 | 227 | 230 | 231
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
370-1 | Abermain BSP | Nth Ipswich |  | NCC Rating (A) | 499 | 499 | 499 | 499 | 499
| (ABM) | (NIP) |  | 10 PoE Load (A) | 228 | 229 | 231 | 234 | 235
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
ABERMAIN Bulk Supply Point:
387-1 | Abermain BSP | Marburg |  | NCC Rating (A) | 290 | 290 | 290 | 290 | 290
| (ABM) | (MBG) |  | 10 PoE Load (A) | 180 | 185 | 198 | 210 | 218
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
ABERMAIN Bulk Supply Point:
3901-1 | Karrabin | Amberley |  | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
| (KBN) | (ABY) |  | 10 PoE Load (A) | 209 | 224 | 260 | 289 | 310
|  |  |  | Power Factor (System Normal) | 0.91 | 0.91 | 0.9 | 0.9 | 0.9
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 475-1 | ECC Rating (A) |  |  |  |  | 553
|  |  |  | 50 PoE Load (A) |  |  |  |  | 554
|  |  |  | Raw LAR (A) |  |  |  |  | 1
|  |  |  | 2-Hour Rating (A) |  |  |  |  | 664
Auto Trans Avail (A)
Remote Trans Avail (A)
|  |  |  | Manual Trans Avail (A) |  |  |  |  | 46
|  |  |  | POPS Available |  |  |  |  | No
|  |  |  | Mobile Gen Reqd (A) |  |  |  |  | 0
|  |  |  | LARc (A) |  |  |  |  | 0
|  |  |  | LARc (MW) |  |  |  |  | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
420-1 | Mt Crosby West | Customer |  | NCC Rating (A) | 349 | 349 | 349 | 349 | 349
| (MCW) |  |  | 10 PoE Load (A) | 23 | 49 | 49 | 67 | 67
|  |  |  | Power Factor (System Normal) | 0.12 | 0.56 | 0.55 | 0.89 | 0.89
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | HighSec | HighSec | HighSec | HighSec | HighSec
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
436-1 | Amberley |  |  | NCC Rating (A) | 351 | 351 | 351 | 351 | 351
| (ABY) | (436 Tee1) |  | 10 PoE Load (A) | 64 | 60 | 53 | 48 | 45
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.7 | 0.67
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
ABERMAIN Bulk Supply Point:
436-2 |  | Ebenezer |  | NCC Rating (A) | 403 | 403 | 403 | 403 | 403
| (436 Tee1) | (EZR) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
436-4 |  | Rosewood |  | NCC Rating (A) | 208 | 208 | 208 | 208 | 208
| (436 Tee1) | (RWD) |  | 10 PoE Load (A) | 64 | 60 | 53 | 49 | 46
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.95 | 0.66
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 387-1 | ECC Rating (A) | 208 | 208 | 208 | 208 | 208
|  |  |  | 50 PoE Load (A) | 227 | 228 | 235 | 243 | 249
|  |  |  | Raw LAR (A) | 19 | 20 | 27 | 35 | 41
|  |  |  | 2-Hour Rating (A) | 266 | 266 | 266 | 266 | 266
Auto Trans Avail (A)
Remote Trans Avail (A)
|  |  |  | Manual Trans Avail (A) | 58 | 59 | 60 | 62 | 63
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
445-1 | Abermain BSP | Moggill |  | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
| (ABM) | (MGL) |  | 10 PoE Load (A) | 229 | 228 | 227 | 226 | 224
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
ABERMAIN Bulk Supply Point:
475-1 | Karrabin | Amberley |  | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
| (KBN) | (ABY) |  | 10 PoE Load (A) | 207 | 222 | 258 | 286 | 307
|  |  |  | Power Factor (System Normal) | 0.91 | 0.91 | 0.91 | 0.9 | 0.9
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 3901-1 | ECC Rating (A) |  |  |  |  | 553
|  |  |  | 50 PoE Load (A) |  |  |  |  | 554
|  |  |  | Raw LAR (A) |  |  |  |  | 1
|  |  |  | 2-Hour Rating (A) |  |  |  |  | 664
Auto Trans Avail (A)
Remote Trans Avail (A)
|  |  |  | Manual Trans Avail (A) |  |  |  |  | 46
|  |  |  | POPS Available |  |  |  |  | No
|  |  |  | Mobile Gen Reqd (A) |  |  |  |  | 0
|  |  |  | LARc (A) |  |  |  |  | 0
|  |  |  | LARc (MW) |  |  |  |  | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
673-1 | Moggill | Kenmore |  | NCC Rating (A) | 636 | 636 | 636 | 636 | 636
| (MGL) | (KMR) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
ALGESTER Bulk Supply Point:
3400-1 | Algester BSP | Calamvale |  | NCC Rating (A) | 694 | 694 | 694 | 694 | 694
| (AGT) | (CMV) |  | 10 PoE Load (A) | 346 | 344 | 343 | 341 | 338
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3402-1 | Algester BSP | Acacia Ridge |  | NCC Rating (A) | 687 | 687 | 687 | 687 | 687
| (AGT) | (ARG) |  | 10 PoE Load (A) | 163 | 161 | 158 | 156 | 153
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3403-1 | Algester BSP | Acacia Ridge |  | NCC Rating (A) | 687 | 687 | 687 | 687 | 687
| (AGT) | (ARG) |  | 10 PoE Load (A) | 164 | 161 | 159 | 157 | 154
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3405-1 | Algester BSP | Calamvale |  | NCC Rating (A) | 694 | 694 | 694 | 694 | 694
| (AGT) | (CMV) |  | 10 PoE Load (A) | 347 | 345 | 343 | 342 | 339
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
ARCHERFIELD Bulk Supply Point:
597-1 | Rocklea | Salisbury |  | NCC Rating (A) | 700 | 700 | 700 | 700 | 700
| (RLA) | (SBY) |  | 10 PoE Load (A) | 188 | 184 | 181 | 177 | 176
|  |  |  | Power Factor (System Normal) | 0.94 | 0.94 | 0.94 | 0.94 | 0.94
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
635-1 | Archerfield BSP | Coopers Plains |  | NCC Rating (A) | 523 | 523 | 523 | 523 | 523
| (AFD) | (CPL) |  | 10 PoE Load (A) | 403 | 397 | 390 | 382 | 379
|  |  |  | Power Factor (System Normal) | 0.95 | 0.95 | 0.95 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
650-1 | Archerfield BSP | Rocklea |  | NCC Rating (A) | 650 | 650 | 650 | 650 | 650
| (AFD) | (RLA) |  | 10 PoE Load (A) | 249 | 244 | 240 | 235 | 233
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
651-1 | Archerfield BSP | Rocklea |  | NCC Rating (A) | 650 | 650 | 650 | 650 | 650
| (AFD) | (RLA) |  | 10 PoE Load (A) | 246 | 241 | 237 | 232 | 230
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
ASHGROVE WEST Bulk Supply Point:
432-1 | Ashgrove West BSP | Toowong |  | NCC Rating (A) | 476 | 476 | 476 | 476 | 476
| (AGW) | (TWG) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
552-1 | Ashgrove West BSP | Ashgrove |  | NCC Rating (A) | 598 | 598 | 598 | 598 | 598
| (AGW) | (AGE) |  | 10 PoE Load (A) | 173 | 171 | 169 | 169 | 167
|  |  |  | Power Factor (System Normal) | 1 | 1 | 1 | 1 | 1
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
565-1 | Ashgrove West BSP | Ashgrove |  | NCC Rating (A) | 851 | 851 | 851 | 851 | 851
| (AGW) | (AGE) |  | 10 PoE Load (A) | 119 | 118 | 117 | 116 | 115
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
570-1 | Ashgrove West BSP | Ashgrove |  | NCC Rating (A) | 598 | 598 | 598 | 598 | 598
| (AGW) | (AGE) |  | 10 PoE Load (A) | 169 | 167 | 165 | 165 | 163
|  |  |  | Power Factor (System Normal) | 1 | 1 | 1 | 1 | 1
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
585-1 | Ashgrove West BSP | The Gap |  | NCC Rating (A) | 622 | 622 | 622 | 622 | 622
| (AGW) | (GAP) |  | 10 PoE Load (A) | 161 | 159 | 157 | 156 | 153
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
ASHGROVE WEST Bulk Supply Point:
586-1 | Ashgrove West BSP | The Gap |  | NCC Rating (A) | 622 | 622 | 622 | 622 | 622
| (AGW) | (GAP) |  | 10 PoE Load (A) | 181 | 178 | 177 | 175 | 172
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
590-1 | Ashgrove West BSP | Toowong |  | NCC Rating (A) | 705 | 705 | 705 | 705 | 705
| (AGW) | (TWG) |  | 10 PoE Load (A) | 351 | 348 | 347 | 346 | 344
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
591-1 | Ashgrove West BSP | Toowong |  | NCC Rating (A) | 705 | 705 | 705 | 705 | 705
| (AGW) | (TWG) |  | 10 PoE Load (A) | 351 | 348 | 347 | 346 | 344
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
675-1 | Ashgrove | Newmarket |  | NCC Rating (A) | 492 | 492 | 492 | 492 | 492
| (AGE) | (NMK) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
676-1 | Ashgrove | Newmarket |  | NCC Rating (A) | 492 | 492 | 492 | 492 | 492
| (AGE) | (NMK) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
BEAUDESERT Bulk Supply Point:
314-1 | Beaudesert BSP | Jimboomba BSP |  | NCC Rating (A) | 512 | 512 | 512 | 512 | 512
| (BDS) | (JBB) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
404-1 | Beaudesert | Innisplain |  | NCC Rating (A) | 155 | 155 | 155 | 155 | 155
| (BDT) | (IPL) |  | 10 PoE Load (A) | 151 | 150 | 152 | 153 | 154
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 404-1 | ECC Rating (A)
|  |  |  | 50 PoE Load (A) | 113 | 113 | 114 | 115 | 115
|  |  |  | Raw LAR (A) | 113 | 113 | 114 | 115 | 115
2-Hour Rating (A)
Auto Trans Avail (A)
Remote Trans Avail (A)
|  |  |  | Manual Trans Avail (A) | 32 | 32 | 32 | 32 | 32
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 81 | 81 | 82 | 83 | 83
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
466-1 | Beaudesert BSP | Bromelton |  | NCC Rating (A) | 403 | 403 | 403 | 403 | 403
| (BDS) | (BTN) |  | 10 PoE Load (A) | 94 | 101 | 117 | 133 | 146
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.98 | 0.98 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
BEAUDESERT Bulk Supply Point:
467-1 | Beaudesert BSP | Bromelton |  | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
| (BDS) | (BTN) |  | 10 PoE Load (A) | 63 | 68 | 78 | 89 | 97
|  |  |  | Power Factor (System Normal) | 1 | 1 | 1 | 1 | 1
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
468-1 | Beaudesert BSP | Beaudesert |  | NCC Rating (A) | 579 | 579 | 579 | 579 | 579
| (BDS) | (BDT) |  | 10 PoE Load (A) | 351 | 350 | 357 | 363 | 368
|  |  |  | Power Factor (System Normal) | 0.91 | 0.92 | 0.91 | 0.91 | 0.91
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
469-1 | Beaudesert BSP |  |  | NCC Rating (A) | 537 | 537 | 537 | 537 | 537
| (BDS) | (469 Tee1) |  | 10 PoE Load (A) | 362 | 361 | 368 | 374 | 379
|  |  |  | Power Factor (System Normal) | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 468-1 | ECC Rating (A) | 537 | 537 | 537 | 537 | 537
|  |  |  | 50 PoE Load (A) | 600 | 599 | 610 | 620 | 627
|  |  |  | Raw LAR (A) | 63 | 62 | 73 | 83 | 90
|  |  |  | 2-Hour Rating (A) | 537 | 537 | 537 | 537 | 537
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) | 127 | 126 | 125 | 125 | 124
Manual Trans Avail (A)
|  |  |  | POPS Available | Yes | Yes | Yes | Yes | Yes
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
BEAUDESERT Bulk Supply Point:
469-2 |  | Beaudesert |  | NCC Rating (A) | 579 | 579 | 579 | 579 | 579
| (469 Tee1) | (BDT) |  | 10 PoE Load (A) | 219 | 220 | 227 | 234 | 240
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.95 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
469-3 |  | Mt Tamborine Bus 2 |  | NCC Rating (A) | 512 | 512 | 512 | 512 | 512
| (469 Tee1) | (MTBT2) |  | 10 PoE Load (A) | 146 | 145 | 144 | 144 | 143
|  |  |  | Power Factor (System Normal) | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
BEENLEIGH Bulk Supply Point:
3590-1 | Beenleigh BSP | Loganholme |  | NCC Rating (A) | 766 | 766 | 766 | 766 | 766
| (BLH) | (LHM) |  | 10 PoE Load (A) | 421 | 416 | 413 | 410 | 405
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3591-1 | Cornubia | Loganholme |  | NCC Rating (A) | 800 | 800 | 800 | 800 | 800
| (CNB) | (LHM) |  | 10 PoE Load (A) | 66 | 65 | 64 | 63 | 62
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3600-1 | Yatala | Stapylton |  | NCC Rating (A) | 713 | 713 | 713 | 713 | 713
| (YTA) | (STT) |  | 10 PoE Load (A) | 98 | 98 | 97 | 97 | 96
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3601-1 | Yatala | Stapylton |  | NCC Rating (A) | 713 | 713 | 713 | 713 | 713
| (YTA) | (STT) |  | 10 PoE Load (A) | 94 | 94 | 93 | 93 | 92
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
BEENLEIGH Bulk Supply Point:
3620-1 | Beenleigh BSP | Logan Village |  | NCC Rating (A) | 490 | 490 | 490 | 490 | 490
| (BLH) | (LGV) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
402-1 | Beenleigh BSP |  |  | NCC Rating (A) | 579 | 579 | 579 | 579 | 579
| (BLH) | (402 Tee1) |  | 10 PoE Load (A) | 251 | 249 | 249 | 249 | 248
|  |  |  | Power Factor (System Normal) | 0.94 | 0.94 | 0.94 | 0.94 | 0.94
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 402-1 | ECC Rating (A)
|  |  |  | 50 PoE Load (A) | 202 | 201 | 201 | 201 | 200
|  |  |  | Raw LAR (A) | 202 | 201 | 201 | 201 | 200
2-Hour Rating (A)
|  |  |  | Auto Trans Avail (A) | 131 | 129 | 128 | 128 | 127
Remote Trans Avail (A)
|  |  |  | Manual Trans Avail (A) | 17 | 17 | 17 | 17 | 17
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 54 | 54 | 55 | 56 | 56
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
BEENLEIGH Bulk Supply Point:
402-2 |  | Tamborine Village |  | NCC Rating (A) | 439 | 439 | 439 | 439 | 439
| (402 Tee1) | (TBV) |  | 10 PoE Load (A) | 93 | 93 | 94 | 95 | 96
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 402-2 | ECC Rating (A)
|  |  |  | 50 PoE Load (A) | 72 | 72 | 73 | 73 | 74
|  |  |  | Raw LAR (A) | 72 | 72 | 73 | 73 | 74
2-Hour Rating (A)
Auto Trans Avail (A)
Remote Trans Avail (A)
|  |  |  | Manual Trans Avail (A) | 17 | 17 | 17 | 17 | 17
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 54 | 54 | 55 | 56 | 56
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
402-3 |  | Mt Tamborine Bus 1 |  | NCC Rating (A) | 800 | 800 | 800 | 800 | 800
| (402 Tee1) | (MTBT1) |  | 10 PoE Load (A) | 158 | 156 | 155 | 154 | 152
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
405-1 | Beenleigh BSP |  |  | NCC Rating (A) | 807 | 807 | 807 | 807 | 807
| (BLH) | (405 Tee1) |  | 10 PoE Load (A) | 301 | 297 | 295 | 293 | 290
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
BEENLEIGH Bulk Supply Point:
405-3 |  | Cornubia |  | NCC Rating (A) | 774 | 774 | 774 | 774 | 774
| (405 Tee1) | (CNB) |  | 10 PoE Load (A) | 301 | 298 | 295 | 294 | 290
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
419-1 | Loganholme | Tanah Merah |  | NCC Rating (A) | 712 | 712 | 712 | 712 | 712
| (LHM) | (TMH) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
426-1 | Beenleigh BSP | Yatala |  | NCC Rating (A) | 740 | 740 | 740 | 740 | 740
| (BLH) | (YTA) |  | 10 PoE Load (A) | 98 | 98 | 97 | 96 | 96
|  |  |  | Power Factor (System Normal) | 0.55 | 0.55 | 0.55 | 0.55 | 0.55
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
427-1 | Beenleigh BSP | Yatala |  | NCC Rating (A) | 740 | 740 | 740 | 740 | 740
| (BLH) | (YTA) |  | 10 PoE Load (A) | 94 | 93 | 93 | 92 | 92
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
BEENLEIGH Bulk Supply Point:
453-1 | Beenleigh BSP | Beenleigh North |  | NCC Rating (A) | 800 | 800 | 800 | 800 | 800
| (BLH) | (BLN) |  | 10 PoE Load (A) | 700 | 700 | 704 | 708 | 709
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 453-1 | ECC Rating (A)
|  |  |  | 50 PoE Load (A) | 623 | 623 | 626 | 630 | 630
|  |  |  | Raw LAR (A) | 623 | 623 | 626 | 630 | 630
2-Hour Rating (A)
|  |  |  | Auto Trans Avail (A) | 332 | 333 | 335 | 337 | 337
|  |  |  | Remote Trans Avail (A) | 146 | 145 | 146 | 147 | 147
|  |  |  | Manual Trans Avail (A) | 87 | 87 | 87 | 87 | 87
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 58 | 58 | 59 | 60 | 60
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
496-1 | Beenleigh North | Bethania |  | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
| (BLN) | (BTA) |  | 10 PoE Load (A) | 387 | 388 | 390 | 393 | 393
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
BEERWAH Bulk Supply Point:
324-1 | Woodford | Kilcoy |  | NCC Rating (A) | 348 | 348 | 348 | 348 | 348
| (WFD) | (KCY) |  | 10 PoE Load (A) | 287 | 280 | 258 | 258 | 258
|  |  |  | Power Factor (System Normal) | 0.94 | 0.94 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 324-1 | ECC Rating (A)
|  |  |  | 50 PoE Load (A) | 192 | 189 | 189 | 189 | 188
|  |  |  | Raw LAR (A) | 192 | 189 | 189 | 189 | 188
2-Hour Rating (A)
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) | 38 | 38 | 38 | 38 | 38
|  |  |  | Manual Trans Avail (A) | 8 | 8 | 8 | 8 | 8
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 146 | 144 | 143 | 143 | 143
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
428-1 | Beerwah BSP | Woodford |  | NCC Rating (A) | 351 | 351 | 351 | 351 | 351
| (BWH) | (WFD) |  | 10 PoE Load (A) | 333 | 325 | 291 | 291 | 290
|  |  |  | Power Factor (System Normal) | 0.9 | 0.9 | 0.93 | 0.93 | 0.93
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
447-1 | Somerset Dam | Kilcoy |  | NCC Rating (A) | 155 | 155 | 155 | 155 | 155
| (SDM) | (KCY) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
BEERWAH Bulk Supply Point:
477-1 |  | Maleny |  | NCC Rating (A) | 155 | 155 | 155 | 155 | 155
| (477 Tee1) | (MLY) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
477-2 |  | Woodford |  | NCC Rating (A) | 300 | 300 | 300 | 300 | 300
| (477 Tee1) | (WFD) |  | 10 PoE Load (A) | 203 | 203 | 202 | 201 | 200
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.98 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
477-3 | Beerwah BSP |  |  | NCC Rating (A) | 711 | 711 | 711 | 711 | 711
| (BWH) | (477 Tee1) |  | 10 PoE Load (A) | 202 | 202 | 201 | 201 | 199
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
608-1 | Beerwah BSP | Landsborough |  | NCC Rating (A) | 412 | 412 | 412 | 412 | 412
| (BWH) | (LBH) |  | 10 PoE Load (A) | 231 | 247 | 265 | 271 | 275
|  |  |  | Power Factor (System Normal) | 0.98 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
BELMONT Bulk Supply Point:
527-1 | Mt Gravatt | Upper Mt Gravatt |  | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
| (MTG) | (UMG) |  | 10 PoE Load (A) | 105 | 105 | 105 | 104 | 103
|  |  |  | Power Factor (System Normal) | 1 | 1 | 1 | 1 | 1
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
631-1 | Belmont BSP | Mt Gravatt |  | NCC Rating (A) | 420 | 420 | 420 | 420 | 420
| (BBS) | (MTG) |  | 10 PoE Load (A) | 280 | 279 | 277 | 276 | 274
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
632-1 | Belmont BSP | Mt Gravatt |  | NCC Rating (A) | 420 | 420 | 420 | 420 | 420
| (BBS) | (MTG) |  | 10 PoE Load (A) | 278 | 277 | 275 | 274 | 272
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
BELMONT Bulk Supply Point:
647-1 | Belmont BSP | Eight Mile Plains Bus 2 |  | NCC Rating (A) | 479 | 479 | 479 | 479 | 479
| (BBS) | (EMPT3) |  | 10 PoE Load (A) | 305 | 304 | 302 | 301 | 298
|  |  |  | Power Factor (System Normal) | 0.9 | 0.9 | 0.9 | 0.9 | 0.91
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | F694(ACO) | ECC Rating (A) | 479 | 479 | 479 | 479 | 479
|  |  |  | 50 PoE Load (A) | 555 | 551 | 548 | 540 | 534
|  |  |  | Raw LAR (A) | 76 | 72 | 69 | 61 | 55
|  |  |  | 2-Hour Rating (A) | 561 | 561 | 561 | 561 | 561
Auto Trans Avail (A)
Remote Trans Avail (A)
|  |  |  | Manual Trans Avail (A) | 201 | 201 | 201 | 201 | 201
|  |  |  | POPS Available | Yes | Yes | Yes | Yes | Yes
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
660-1 | Belmont BSP | Scrub Road |  | NCC Rating (A) | 676 | 676 | 676 | 676 | 676
| (BBS) | (SRD) |  | 10 PoE Load (A) | 275 | 273 | 270 | 268 | 264
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
661-1 | Belmont BSP | Scrub Road |  | NCC Rating (A) | 676 | 676 | 676 | 676 | 676
| (BBS) | (SRD) |  | 10 PoE Load (A) | 278 | 276 | 273 | 271 | 267
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
BELMONT Bulk Supply Point:
662-1 | Belmont BSP | Upper Mt Gravatt |  | NCC Rating (A) | 656 | 656 | 656 | 656 | 656
| (BBS) | (UMG) |  | 10 PoE Load (A) | 225 | 225 | 223 | 223 | 221
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
663-1 | Belmont BSP | Upper Mt Gravatt |  | NCC Rating (A) | 656 | 656 | 656 | 656 | 656
| (BBS) | (UMG) |  | 10 PoE Load (A) | 228 | 227 | 226 | 225 | 223
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
692-1 | Belmont BSP | Holland Park East |  | NCC Rating (A) | 421 | 421 | 421 | 421 | 421
| (BBS) | (HPE) |  | 10 PoE Load (A) | 178 | 179 | 178 | 178 | 177
|  |  |  | Power Factor (System Normal) | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
693-1 | Belmont BSP | Holland Park East |  | NCC Rating (A) | 421 | 421 | 421 | 421 | 421
| (BBS) | (HPE) |  | 10 PoE Load (A) | 180 | 180 | 179 | 180 | 179
|  |  |  | Power Factor (System Normal) | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
BRENDALE Bulk Supply Point:
303-1 | Brendale BSP | Albany Creek |  | NCC Rating (A) | 725 | 725 | 725 | 725 | 725
| (BRD) | (ACR) |  | 10 PoE Load (A) | 258 | 256 | 254 | 254 | 251
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
309-1 | Brendale BSP |  |  | NCC Rating (A) | 627 | 627 | 627 | 627 | 627
| (BRD) | (309 Tee1) |  | 10 PoE Load (A) | 295 | 291 | 289 | 288 | 285
|  |  |  | Power Factor (System Normal) | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
309-2 |  | Samford |  | NCC Rating (A) | 711 | 711 | 711 | 711 | 711
| (309 Tee1) | (SMF) |  | 10 PoE Load (A) | 87 | 86 | 86 | 86 | 85
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
309-3 |  | Arana Hills |  | NCC Rating (A) | 700 | 700 | 700 | 700 | 700
| (309 Tee1) | (AHL) |  | 10 PoE Load (A) | 209 | 206 | 204 | 202 | 200
|  |  |  | Power Factor (System Normal) | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
310-1 | Brendale BSP |  |  | NCC Rating (A) | 627 | 627 | 627 | 627 | 627
| (BRD) | (310 Tee1) |  | 10 PoE Load (A) | 434 | 428 | 425 | 422 | 417
|  |  |  | Power Factor (System Normal) | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
BRENDALE Bulk Supply Point:
310-2 |  | Arana Hills |  | NCC Rating (A) | 792 | 792 | 792 | 792 | 792
| (310 Tee1) | (AHL) |  | 10 PoE Load (A) | 434 | 428 | 425 | 422 | 417
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
310-3 |  |  |  | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
| (310 Tee1) | (569 Tee1) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
333-1 | Brendale BSP | Lawnton |  | NCC Rating (A) | 732 | 732 | 732 | 732 | 732
| (BRD) | (LTN) |  | 10 PoE Load (A) | 326 | 325 | 326 | 327 | 327
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3340-1 | Brendale BSP | Strathpine |  | NCC Rating (A) | 512 | 512 | 512 | 512 | 512
| (BRD) | (SPE) |  | 10 PoE Load (A) | 152 | 150 | 148 | 147 | 144
|  |  |  | Power Factor (System Normal) | 0.94 | 0.94 | 0.94 | 0.94 | 0.94
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
334-1 | Lawnton |  |  | NCC Rating (A) | 578 | 578 | 578 | 578 | 578
| (LTN) | (334 Tee1) |  | 10 PoE Load (A) | 30 | 30 | 30 | 29 | 29
|  |  |  | Power Factor (System Normal) | 0.16 | 0.18 | 0.23 | 0.28 | 0.32
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
BRENDALE Bulk Supply Point:
334-2 |  | Whiteside |  | NCC Rating (A) | 750 | 750 | 750 | 750 | 750
| (334 Tee1) | (WSE) |  | 10 PoE Load (A) | 80 | 79 | 78 | 78 | 76
|  |  |  | Power Factor (System Normal) | 0.92 | 0.92 | 0.92 | 0.92 | 0.92
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
334-3 |  | North Pine Dam |  | NCC Rating (A) | 578 | 578 | 578 | 578 | 578
| (334 Tee1) | (NPD) |  | 10 PoE Load (A) | 78 | 78 | 79 | 79 | 80
|  |  |  | Power Factor (System Normal) | 1 | 1 | 1 | 1 | 1
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
335-1 | Brendale BSP |  |  | NCC Rating (A) | 485 | 485 | 485 | 485 | 485
| (BRD) | (335 Tee1) |  | 10 PoE Load (A) | 220 | 219 | 219 | 219 | 218
|  |  |  | Power Factor (System Normal) | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
335-2 |  | Whiteside |  | NCC Rating (A) | 750 | 750 | 750 | 750 | 750
| (335 Tee1) | (WSE) |  | 10 PoE Load (A) | 94 | 93 | 93 | 92 | 91
|  |  |  | Power Factor (System Normal) | 0.93 | 0.94 | 0.94 | 0.94 | 0.94
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
335-3 |  | North Pine Dam |  | NCC Rating (A) | 485 | 485 | 485 | 485 | 485
| (335 Tee1) | (NPD) |  | 10 PoE Load (A) | 126 | 126 | 127 | 128 | 128
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
BRENDALE Bulk Supply Point:
336-1 | Brendale BSP | Strathpine |  | NCC Rating (A) | 455 | 455 | 455 | 455 | 455
| (BRD) | (SPE) |  | 10 PoE Load (A) | 173 | 171 | 169 | 167 | 164
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3364-1 | Brendale BSP | Albany Creek |  | NCC Rating (A) | 725 | 725 | 725 | 725 | 725
| (BRD) | (ACR) |  | 10 PoE Load (A) | 264 | 262 | 261 | 260 | 257
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
337-1 | Brendale BSP | Strathpine |  | NCC Rating (A) | 490 | 490 | 490 | 490 | 490
| (BRD) | (SPE) |  | 10 PoE Load (A) | 143 | 142 | 140 | 138 | 136
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
342-1 | Brendale BSP | Bald Hills Bus 2 |  | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
| (BRD) | (BHLT3) |  | 10 PoE Load (A) | 177 | 175 | 173 | 172 | 170
|  |  |  | Power Factor (System Normal) | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
349-1 | Brendale BSP | Lawnton |  | NCC Rating (A) | 717 | 717 | 717 | 717 | 717
| (BRD) | (LTN) |  | 10 PoE Load (A) | 339 | 338 | 339 | 340 | 340
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.97 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
BRENDALE Bulk Supply Point:
464-1 | Brendale BSP | Samford |  | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
| (BRD) | (SMF) |  | 10 PoE Load (A) | 213 | 211 | 210 | 209 | 207
|  |  |  | Power Factor (System Normal) | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
BROWNS PLAINS Bulk Supply Point:
406A-1 | Bethania | Kingston |  | NCC Rating (A) | 529 | 529 | 529 | 529 | 529
| (BTA) | (KSN) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
406B-1 | Crestmead | Kingston |  | NCC Rating (A) | 780 | 780 | 780 | 780 | 780
| (CRM) | (KSN) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
478-1 | Browns Plains BSP | North Maclean |  | NCC Rating (A) | 800 | 800 | 800 | 800 | 800
| (BPN) | (NMC) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
481-1 | Browns Plains BSP | Crestmead |  | NCC Rating (A) | 705 | 705 | 705 | 705 | 705
| (BPN) | (CRM) |  | 10 PoE Load (A) | 245 | 243 | 242 | 241 | 240
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
482-1 | Browns Plains BSP | Crestmead |  | NCC Rating (A) | 704 | 704 | 704 | 704 | 704
| (BPN) | (CRM) |  | 10 PoE Load (A) | 247 | 244 | 243 | 243 | 241
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
BROWNS PLAINS Bulk Supply Point:
542-1 | Browns Plains BSP | Heathwood |  | NCC Rating (A) | 704 | 704 | 704 | 704 | 704
| (BPN) | (HWD) |  | 10 PoE Load (A) | 511 | 511 | 510 | 509 | 507
|  |  |  | Power Factor (System Normal) | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
BURLEIGH HEADS Bulk Supply Point:
3751-1 | Burleigh Heads BSP | Currumbin |  | NCC Rating (A) | 606 | 606 | 606 | 606 | 606
| (BHD) | (CRB) |  | 10 PoE Load (A) | 582 | 581 | 582 | 584 | 583
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 396-1 | ECC Rating (A) | 606 | 606 | 606 | 606 | 606
|  |  |  | 50 PoE Load (A) | 633 | 633 | 634 | 636 | 635
|  |  |  | Raw LAR (A) | 27 | 27 | 28 | 30 | 29
|  |  |  | 2-Hour Rating (A) | 800 | 800 | 800 | 800 | 800
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) | 52 | 55 | 55 | 56 | 56
Manual Trans Avail (A)
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 3755-1 | ECC Rating (A) | 695 | 695 | 695 | 695 | 695
|  |  |  | 50 PoE Load (A) | 923 | 922 | 924 | 926 | 926
|  |  |  | Raw LAR (A) | 228 | 227 | 229 | 231 | 231
|  |  |  | 2-Hour Rating (A) | 800 | 800 | 800 | 800 | 800
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) | 207 | 207 | 210 | 210 | 209
|  |  |  | Manual Trans Avail (A) | 15 | 18 | 17 | 14 | 14
|  |  |  | POPS Available | Yes | Yes | Yes | Yes | Yes
|  |  |  | Mobile Gen Reqd (A) | 6 | 2 | 2 | 7 | 8
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
BURLEIGH HEADS Bulk Supply Point:
3755-1 | Burleigh Heads BSP | Currumbin |  | NCC Rating (A) | 606 | 606 | 606 | 606 | 606
| (BHD) | (CRB) |  | 10 PoE Load (A) | 581 | 581 | 582 | 584 | 583
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 396-1 | ECC Rating (A) | 606 | 606 | 606 | 606 | 606
|  |  |  | 50 PoE Load (A) | 633 | 633 | 634 | 635 | 635
|  |  |  | Raw LAR (A) | 27 | 27 | 28 | 29 | 29
|  |  |  | 2-Hour Rating (A) | 800 | 800 | 800 | 800 | 800
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) | 52 | 55 | 55 | 56 | 56
Manual Trans Avail (A)
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 3751-1 | ECC Rating (A) | 695 | 695 | 695 | 695 | 695
|  |  |  | 50 PoE Load (A) | 923 | 922 | 924 | 926 | 925
|  |  |  | Raw LAR (A) | 228 | 227 | 229 | 231 | 230
|  |  |  | 2-Hour Rating (A) | 800 | 800 | 800 | 800 | 800
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) | 207 | 207 | 210 | 210 | 209
|  |  |  | Manual Trans Avail (A) | 15 | 18 | 17 | 14 | 14
|  |  |  | POPS Available | Yes | Yes | Yes | Yes | Yes
|  |  |  | Mobile Gen Reqd (A) | 6 | 2 | 2 | 7 | 7
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3756-1 | Burleigh Heads BSP |  |  | NCC Rating (A) | 715 | 715 | 715 | 715 | 715
| (BHD) | (3756 Tee1) |  | 10 PoE Load (A) | 182 | 182 | 182 | 183 | 182
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
BURLEIGH HEADS Bulk Supply Point:
3756-2 |  | Palm Beach |  | NCC Rating (A) | 532 | 532 | 532 | 532 | 532
| (3756 Tee1) | (PBH) |  | 10 PoE Load (A) | 137 | 138 | 139 | 140 | 140
|  |  |  | Power Factor (System Normal) | 1 | 1 | 1 | 1 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3756-3 |  |  |  | NCC Rating (A) | 636 | 636 | 636 | 636 | 636
| (3756 Tee1) | (3756 Tee2) |  | 10 PoE Load (A) | 58 | 63 | 56 | 56 | 56
|  |  |  | Power Factor (System Normal) | 0.99 | 0.9 | 0.99 | 0.99 | 1
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3756-4 |  | Currumbin |  | NCC Rating (A) | 717 | 717 | 717 | 717 | 717
| (3756 Tee2) | (CRB) |  | 10 PoE Load (A) | 58 | 63 | 56 | 56 | 56
|  |  |  | Power Factor (System Normal) | 0.99 | 0.89 | 0.99 | 0.99 | 1
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
BURLEIGH HEADS Bulk Supply Point:
393-1 | Currumbin | Kirra |  | NCC Rating (A) | 403 | 403 | 403 | 403 | 403
| (CRB) | (KRA) |  | 10 PoE Load (A) | 352 | 348 | 351 | 352 | 350
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 393-1 | ECC Rating (A)
|  |  |  | 50 PoE Load (A) | 317 | 316 | 316 | 317 | 316
|  |  |  | Raw LAR (A) | 317 | 316 | 316 | 317 | 316
2-Hour Rating (A)
|  |  |  | Auto Trans Avail (A) | 317 | 316 | 316 | 317 | 316
Remote Trans Avail (A)
Manual Trans Avail (A)
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
395-1 | Burleigh Heads BSP | Miami |  | NCC Rating (A) | 654 | 654 | 654 | 654 | 654
| (BHD) | (MAI) |  | 10 PoE Load (A) | 433 | 435 | 437 | 441 | 443
|  |  |  | Power Factor (System Normal) | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
396-1 | Burleigh Heads BSP | Palm Beach |  | NCC Rating (A) | 800 | 800 | 800 | 800 | 800
| (BHD) | (PBH) |  | 10 PoE Load (A) | 207 | 207 | 208 | 208 | 208
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
BURLEIGH HEADS Bulk Supply Point:
397-1 | Burleigh Heads BSP |  |  | NCC Rating (A) | 602 | 602 | 602 | 602 | 602
| (BHD) | (397 Tee1) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
397-3 |  |  |  | NCC Rating (A) | 529 | 529 | 529 | 529 | 529
| (397 Tee1) | (397 Tee2) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
397-4 |  |  |  | NCC Rating (A) | 362 | 362 | 362 | 362 | 362
| (397 Tee2) | (3700 Tee1) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
397-5 |  | Mudgeeraba BSP |  | NCC Rating (A) | 703 | 703 | 703 | 703 | 703
| (397 Tee2) | (MGB) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
CABOOLTURE Bulk Supply Point:
321-1 | Caboolture BSP | Caboolture West |  | NCC Rating (A) | 509 | 509 | 509 | 509 | 509
| (CBT) | (CBW) |  | 10 PoE Load (A) | 273 | 273 | 276 | 278 | 279
|  |  |  | Power Factor (System Normal) | 0.99 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
322-1 | Caboolture BSP | Caboolture West |  | NCC Rating (A) | 509 | 509 | 509 | 509 | 509
| (CBT) | (CBW) |  | 10 PoE Load (A) | 284 | 284 | 287 | 289 | 290
|  |  |  | Power Factor (System Normal) | 0.98 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
CABOOLTURE Bulk Supply Point:
323-1 | Caboolture West |  |  | NCC Rating (A) | 251 | 251 | 510 | 510 | 510
| (CBW) | (323 Tee1) |  | 10 PoE Load (A) | 79 | 78 | 77 | 77 | 76
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 323-1 | ECC Rating (A)
|  |  |  | 50 PoE Load (A) | 68 | 68 | 68 | 68 | 67
|  |  |  | Raw LAR (A) | 68 | 68 | 68 | 68 | 67
2-Hour Rating (A)
Auto Trans Avail (A)
Remote Trans Avail (A)
|  |  |  | Manual Trans Avail (A) | 37 | 37 | 37 | 37 | 37
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 31 | 31 | 30 | 30 | 30
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  | F477/F428(ACO) | ECC Rating (A) | 251 | 251
|  |  |  | 50 PoE Load (A) | 264 | 263
|  |  |  | Raw LAR (A) | 13 | 12
|  |  |  | 2-Hour Rating (A) | 298 | 298
Auto Trans Avail (A)
Remote Trans Avail (A)
Manual Trans Avail (A)
|  |  |  | POPS Available | No | No
|  |  |  | Mobile Gen Reqd (A) | 13 | 12
|  |  |  | LARc (A) | 0 | 0
|  |  |  | LARc (MW) | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
323-2 |  | Wamuran |  | NCC Rating (A) | 457 | 457 | 457 | 457 | 457
| (323 Tee1) | (WMR) |  | 10 PoE Load (A) | 79 | 78 | 77 | 77 | 77
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
CABOOLTURE Bulk Supply Point:
323-3 |  | Woodford |  | NCC Rating (A) | 251 | 251 | 271 | 271 | 271
| (323 Tee1) | (WFD) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
350-1 | Caboolture BSP | Ningi |  | NCC Rating (A) | 800 | 800 | 800 | 800 | 800
| (CBT) | (NGI) |  | 10 PoE Load (A) | 408 | 404 | 405 | 406 | 406
|  |  |  | Power Factor (System Normal) | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
412-1 | Caboolture BSP | Toorbul Point |  | NCC Rating (A) | 800 | 800 | 800 | 800 | 800
| (CBT) | (TPT) |  | 10 PoE Load (A) | 324 | 320 | 321 | 322 | 322
|  |  |  | Power Factor (System Normal) | 0.94 | 0.94 | 0.94 | 0.94 | 0.94
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
417-1 | Ningi | Toorbul Point |  | NCC Rating (A) | 800 | 800 | 800 | 800 | 800
| (NGI) | (TPT) |  | 10 PoE Load (A) | 238 | 235 | 236 | 237 | 237
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
431-1 | Toorbul Point | Bribie Island |  | NCC Rating (A) | 396 | 396 | 396 | 396 | 396
| (TPT) | (BIS) |  | 10 PoE Load (A) | 216 | 214 | 214 | 215 | 215
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
CABOOLTURE Bulk Supply Point:
448-1 | Morayfield North |  |  | NCC Rating (A) | 776 | 776 | 776 | 776 | 776
| (MFN) | (448 Tee1) |  | 10 PoE Load (A) | 582 | 595 | 613 | 625 | 632
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
448-2 |  | Morayfield |  | NCC Rating (A) | 698 | 698 | 698 | 698 | 698
| (448 Tee1) | (MFD) |  | 10 PoE Load (A) | 579 | 596 | 618 | 632 | 640
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
448-3 |  | Caboolture West |  | NCC Rating (A) | 485 | 485 | 485 | 485 | 485
| (448 Tee1) | (CBW) |  | 10 PoE Load (A) | 9 | 9 | 11 | 12 | 13
|  |  |  | Power Factor (System Normal) | 0.56 | 0 | 0.23 | 0.33 | 0.4
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
457-1 | Toorbul Point | Bribie Island |  | NCC Rating (A) | 402 | 402 | 402 | 402 | 402
| (TPT) | (BIS) |  | 10 PoE Load (A) | 215 | 212 | 213 | 214 | 214
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
CABOOLTURE Bulk Supply Point:
461-1 | Caboolture BSP | Morayfield North |  | NCC Rating (A) | 676 | 676 | 676 | 676 | 676
| (CBT) | (MFN) |  | 10 PoE Load (A) | 556 | 561 | 572 | 579 | 582
|  |  |  | Power Factor (System Normal) | 0.97 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 499-1 | ECC Rating (A) | 758 | 758 | 758 | 758 | 758
|  |  |  | 50 PoE Load (A) | 893 | 894 | 911 | 921 | 926
|  |  |  | Raw LAR (A) | 135 | 136 | 153 | 163 | 168
|  |  |  | 2-Hour Rating (A) | 1250 | 1250 | 1250 | 1250 | 1250
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) | 420 | 410 | 424 | 432 | 437
Manual Trans Avail (A)
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
499-1 | Caboolture BSP | Morayfield North |  | NCC Rating (A) | 676 | 676 | 676 | 676 | 676
| (CBT) | (MFN) |  | 10 PoE Load (A) | 560 | 565 | 576 | 583 | 586
|  |  |  | Power Factor (System Normal) | 0.97 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 461-1 | ECC Rating (A) | 758 | 758 | 758 | 758 | 758
|  |  |  | 50 PoE Load (A) | 895 | 895 | 912 | 922 | 927
|  |  |  | Raw LAR (A) | 137 | 137 | 154 | 164 | 169
|  |  |  | 2-Hour Rating (A) | 960 | 960 | 960 | 960 | 960
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) | 420 | 410 | 424 | 432 | 437
Manual Trans Avail (A)
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
CLEVELAND Bulk Supply Point:
3550-1 | Cleveland BSP | Victoria Point |  | NCC Rating (A) | 746 | 746 | 746 | 746 | 746
| (CVL) | (VPT) |  | 10 PoE Load (A) | 517 | 517 | 522 | 528 | 529
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3570-1 | Capalaba South | Capalaba |  | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
| (CPS) | (CPB) |  | 10 PoE Load (A) | 105 | 105 | 106 | 106 | 106
|  |  |  | Power Factor (System Normal) | 0.92 | 0.92 | 0.92 | 0.92 | 0.92
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3580-1 | Redland Bay |  |  | NCC Rating (A) | 717 | 717 | 717 | 717 | 717
| (RLB) | (3580 Tee1) |  | 10 PoE Load (A) | 56 | 57 | 60 | 62 | 63
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.95 | 0.95 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3580-2 |  | Mt Cotton |  | NCC Rating (A) | 527 | 527 | 527 | 527 | 527
| (3580 Tee1) | (MCN) |  | 10 PoE Load (A) | 56 | 57 | 59 | 62 | 63
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3580-3 |  | Cornubia |  | NCC Rating (A) | 717 | 717 | 717 | 717 | 717
| (3580 Tee1) | (CNB) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
CLEVELAND Bulk Supply Point:
371-1 | Cleveland BSP | Birkdale |  | NCC Rating (A) | 800 | 800 | 800 | 800 | 800
| (CVL) | (BKD) |  | 10 PoE Load (A) | 463 | 459 | 457 | 456 | 452
|  |  |  | Power Factor (System Normal) | 0.94 | 0.94 | 0.94 | 0.94 | 0.94
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
372-1 | Cleveland BSP | Raby Bay |  | NCC Rating (A) | 611 | 611 | 611 | 611 | 611
| (CVL) | (RBY) |  | 10 PoE Load (A) | 416 | 414 | 415 | 417 | 417
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 413-1 | ECC Rating (A) | 686 | 686 | 686 | 686 | 686
|  |  |  | 50 PoE Load (A) | 734 | 731 | 733 | 736 | 735
|  |  |  | Raw LAR (A) | 48 | 45 | 47 | 50 | 49
|  |  |  | 2-Hour Rating (A) | 1250 | 1250 | 1250 | 1250 | 1250
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) | 292 | 286 | 285 | 283 | 279
Manual Trans Avail (A)
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
373-1 | Raby Bay | Capalaba |  | NCC Rating (A) | 715 | 715 | 715 | 715 | 715
| (RBY) | (CPB) |  | 10 PoE Load (A) | 348 | 344 | 342 | 340 | 336
|  |  |  | Power Factor (System Normal) | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
CLEVELAND Bulk Supply Point:
374-1 | Cleveland BSP | Capalaba South |  | NCC Rating (A) | 800 | 800 | 800 | 800 | 800
| (CVL) | (CPS) |  | 10 PoE Load (A) | 401 | 397 | 395 | 393 | 388
|  |  |  | Power Factor (System Normal) | 0.94 | 0.94 | 0.94 | 0.94 | 0.94
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
375-1 | Cleveland BSP |  |  | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
| (CVL) | (375 Tee1) |  | 10 PoE Load (A) | 183 | 183 | 184 | 185 | 185
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
375-2 |  | Mt Cotton |  | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
| (375 Tee1) | (MCN) |  | 10 PoE Load (A) | 184 | 183 | 184 | 185 | 185
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
375-3 |  |  |  | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
| (375 Tee1) | (425 Tee1) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
CLEVELAND Bulk Supply Point:
413-1 | Cleveland BSP | Raby Bay |  | NCC Rating (A) | 611 | 611 | 611 | 611 | 611
| (CVL) | (RBY) |  | 10 PoE Load (A) | 421 | 419 | 420 | 422 | 422
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 372-1 | ECC Rating (A) | 686 | 686 | 686 | 686 | 686
|  |  |  | 50 PoE Load (A) | 734 | 732 | 734 | 737 | 736
|  |  |  | Raw LAR (A) | 48 | 46 | 48 | 51 | 50
|  |  |  | 2-Hour Rating (A) | 800 | 800 | 800 | 800 | 800
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) | 292 | 286 | 285 | 283 | 279
Manual Trans Avail (A)
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
425-1 | Cleveland BSP | Victoria Point |  | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
| (CVL) | (VPT) |  | 10 PoE Load (A) | 229 | 229 | 231 | 234 | 234
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 3550-1 | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 PoE Load (A) | 573 | 574 | 578 | 584 | 585
|  |  |  | Raw LAR (A) | 20 | 21 | 25 | 31 | 32
|  |  |  | 2-Hour Rating (A) | 663 | 663 | 663 | 663 | 663
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) | 161 | 162 | 167 | 172 | 180
Manual Trans Avail (A)
|  |  |  | POPS Available | Yes | Yes | Yes | Yes | Yes
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
CLEVELAND Bulk Supply Point:
465-1 | Victoria Point | Redland Bay |  | NCC Rating (A) | 508 | 508 | 508 | 508 | 508
| (VPT) | (RLB) |  | 10 PoE Load (A) | 277 | 277 | 281 | 285 | 286
|  |  |  | Power Factor (System Normal) | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
484-1 | Capalaba | Birkdale |  | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
| (CPB) | (BKD) |  | 10 PoE Load (A) | 136 | 136 | 136 | 137 | 137
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
COOMERA Bulk Supply Point:
3640-1 | Coomera BSP | Hope Island |  | NCC Rating (A) | 716 | 716 | 716 | 716 | 716
| (CMA) | (HIS) |  | 10 PoE Load (A) | 389 | 394 | 401 | 409 | 412
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.95 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3641-1 | Coomera BSP | Pimpama East |  | NCC Rating (A) | 713 | 713 | 713 | 713 | 713
| (CMA) | (PPE) |  | 10 PoE Load (A) | 299 | 325 | 342 | 359 | 373
|  |  |  | Power Factor (System Normal) | 0.97 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
COOMERA Bulk Supply Point:
3642-1 | Coomera BSP | Pimpama East |  | NCC Rating (A) | 713 | 713 | 713 | 713 | 713
| (CMA) | (PPE) |  | 10 PoE Load (A) | 302 | 328 | 345 | 362 | 376
|  |  |  | Power Factor (System Normal) | 0.97 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
394-1 | Coomera BSP | Hope Island |  | NCC Rating (A) | 716 | 716 | 716 | 716 | 716
| (CMA) | (HIS) |  | 10 PoE Load (A) | 399 | 403 | 410 | 418 | 422
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
COORPAROO Bulk Supply Point:
3429-1 | Coorparoo BSP | Holland Park |  | NCC Rating (A) | 735 | 735 | 735 | 735 | 735
| (CPR) | (HPK) |  | 10 PoE Load (A) | 210 | 215 | 214 | 215 | 214
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3430-1 | Coorparoo BSP | Holland Park |  | NCC Rating (A) | 735 | 735 | 735 | 735 | 735
| (CPR) | (HPK) |  | 10 PoE Load (A) | 214 | 210 | 210 | 211 | 210
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
584-4 |  | Coorparoo BSP |  | NCC Rating (A) | 721 | 721 | 721 | 721 | 721
| (584 Tee2) | (CPR) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
612-1 | Coorparoo BSP | Camp Hill |  | NCC Rating (A) | 766 | 766 | 766 | 766 | 766
| (CPR) | (CHL) |  | 10 PoE Load (A) | 324 | 325 | 324 | 325 | 323
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
613-1 | Coorparoo BSP | Camp Hill |  | NCC Rating (A) | 766 | 766 | 766 | 766 | 766
| (CPR) | (CHL) |  | 10 PoE Load (A) | 324 | 325 | 324 | 325 | 323
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
COORPAROO Bulk Supply Point:
648-1 | Scrub Road |  |  | NCC Rating (A) | 597 | 597 | 597 | 597 | 597
| (SRD) | (648 Tee1) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
648-2 |  |  |  | NCC Rating (A) | 348 | 348 | 348 | 348 | 348
| (648 Tee1) | (584 Tee1) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
648-3 |  | Camp Hill |  | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
| (648 Tee1) | (CHL) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
DOBOY Bulk Supply Point:
3426-1 | Queensport | Bulimba |  | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
| (QPT) | (BLB) |  | 10 PoE Load (A) | 286 | 285 | 284 | 284 | 313
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
414-1 | Doboy BSP | Tingalpa |  | NCC Rating (A) | 495 | 495 | 495 | 495 | 495
| (DBS) | (TGP) |  | 10 PoE Load (A) | 186 | 185 | 185 | 184 | 182
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
416-1 | Doboy BSP | Murarrie |  | NCC Rating (A) | 355 | 355 | 355 | 355 | 355
| (DBS) | (MRE) |  | 10 PoE Load (A) | 212 | 211 | 210 | 210 | 208
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
DOBOY Bulk Supply Point:
443-1 | Queensport | Bulimba |  | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
| (QPT) | (BLB) |  | 10 PoE Load (A) | 202 | 202 | 201 | 201 | 222
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
558-1 | Hemmant | Tingalpa |  | NCC Rating (A) | 680 | 680 | 680 | 680 | 680
| (HMT) | (TGP) |  | 10 PoE Load (A) | 250 | 248 | 245 | 244 | 241
|  |  |  | Power Factor (System Normal) | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
563-1 | Doboy BSP | Hemmant |  | NCC Rating (A) | 371 | 371 | 371 | 371 | 371
| (DBS) | (HMT) |  | 10 PoE Load (A) | 199 | 204 | 220 | 219 | 216
|  |  |  | Power Factor (System Normal) | 0.94 | 0.94 | 0.94 | 0.94 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
DOBOY Bulk Supply Point:
564-1 | Doboy BSP | Hemmant |  | NCC Rating (A) | 371 | 371 | 371 | 371 | 371
| (DBS) | (HMT) |  | 10 PoE Load (A) | 191 | 196 | 212 | 210 | 208
|  |  |  | Power Factor (System Normal) | 0.94 | 0.94 | 0.94 | 0.94 | 0.94
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
575C-1 | Doboy BSP | Murarrie |  | NCC Rating (A) | 355 | 355 | 355 | 355 | 355
| (DBS) | (MRE) |  | 10 PoE Load (A) | 202 | 200 | 200 | 199 | 198
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
581-1 | Doboy BSP | Queensport |  | NCC Rating (A) | 661 | 661 | 661 | 661 | 661
| (DBS) | (QPT) |  | 10 PoE Load (A) | 518 | 517 | 515 | 515 | 536
|  |  |  | Power Factor (System Normal) | 0.96 | 0.97 | 0.97 | 0.97 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 677-1 | ECC Rating (A) | 785 | 785 | 785 | 785 | 785
|  |  |  | 50 PoE Load (A) | 909 | 907 | 905 | 904 | 967
|  |  |  | Hours PA > 95% Peak Load |  |  |  |  | 3.5
|  |  |  | Raw LAR (A) | 124 | 122 | 120 | 119 | 182
|  |  |  | 2-Hour Rating (A) | 1295 | 1295 | 1295 | 1295 | 1295
Auto Trans Avail (A)
Remote Trans Avail (A)
|  |  |  | Manual Trans Avail (A) | 60 | 60 | 60 | 60 | 61
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 64 | 62 | 60 | 59 | 70
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 51
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 2.9
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | No
DOBOY Bulk Supply Point:
645-1 | Doboy BSP | Gibson Island |  | NCC Rating (A) | 433 | 433 | 433 | 433 | 433
| (DBS) | (GIS) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | HighSec | HighSec | HighSec | HighSec | HighSec
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
677-1 | Doboy BSP | Queensport |  | NCC Rating (A) | 661 | 661 | 661 | 661 | 661
| (DBS) | (QPT) |  | 10 PoE Load (A) | 517 | 515 | 514 | 513 | 534
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.97 | 0.97 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 581-1 | ECC Rating (A) | 785 | 785 | 785 | 785 | 785
|  |  |  | 50 PoE Load (A) | 909 | 906 | 904 | 903 | 967
|  |  |  | Hours PA > 95% Peak Load |  |  |  |  | 2
|  |  |  | Raw LAR (A) | 124 | 121 | 119 | 118 | 182
|  |  |  | 2-Hour Rating (A) | 1295 | 1295 | 1295 | 1295 | 1295
Auto Trans Avail (A)
Remote Trans Avail (A)
|  |  |  | Manual Trans Avail (A) | 60 | 60 | 60 | 60 | 61
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 64 | 61 | 59 | 58 | 70
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 51
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 2.9
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | No
GATTON Bulk Supply Point:
377-1 | Gatton BSP |  |  | NCC Rating (A) | 821 | 821 | 821 | 821 | 821
| (GBS) | (377 Tee1) |  | 10 PoE Load (A) | 300 | 336 | 336 | 334 | 331
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
377-2 |  |  |  | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
| (377 Tee1) | (487 Tee1) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
377-3 |  |  |  | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
| (377 Tee1) | (377 Tee2) |  | 10 PoE Load (A) | 300 | 336 | 336 | 334 | 331
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
377-4 |  | Gatton A |  | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
| (377 Tee2) | (GTN) |  | 10 PoE Load (A) | 300 | 336 | 336 | 334 | 331
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.97 | 0.97 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
377-5 |  | Glenore Grove |  | NCC Rating (A) | 355 | 355 | 355 | 355 | 355
| (377 Tee2) | (GGR) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
GATTON Bulk Supply Point:
3859-1 | Gatton BSP | Spring Creek |  | NCC Rating (A) | 764 | 764 | 764 | 764 | 764
| (GBS) | (SPC) |  | 10 PoE Load (A) | 46 | 45 | 45 | 45 | 44
|  |  |  | Power Factor (System Normal) | 0.87 | 0.87 | 0.88 | 0.88 | 0.88
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3860-1 | Gatton BSP | Spring Creek |  | NCC Rating (A) | 764 | 764 | 764 | 764 | 764
| (GBS) | (SPC) |  | 10 PoE Load (A) | 46 | 45 | 45 | 45 | 44
|  |  |  | Power Factor (System Normal) | 0.87 | 0.87 | 0.87 | 0.88 | 0.88
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
487-1 | Gatton BSP |  |  | NCC Rating (A) | 821 | 821 | 821 | 821 | 821
| (GBS) | (487 Tee1) |  | 10 PoE Load (A) | 292 | 320 | 322 | 321 | 317
|  |  |  | Power Factor (System Normal) | 0.98 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
487-2 |  |  |  | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
| (487 Tee1) | (377 Tee1) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
487-3 |  |  |  | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
| (487 Tee1) | (487 Tee2) |  | 10 PoE Load (A) | 292 | 321 | 323 | 321 | 318
|  |  |  | Power Factor (System Normal) | 0.98 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
GATTON Bulk Supply Point:
487-6 |  |  |  | NCC Rating (A) | 251 | 251 | 251 | 251 | 251
| (487 Tee3) | (487 Tee1) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
487-8 |  |  |  | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
| (487 Tee4) | (3844 Tee1) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
487-9 |  | Gatton A |  | NCC Rating (A) | 713 | 713 | 713 | 713 | 713
| (487 Tee2) | (GTN) |  | 10 PoE Load (A) | 212 | 242 | 241 | 239 | 237
|  |  |  | Power Factor (System Normal) | 0.99 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
GATTON Bulk Supply Point:
531-1 | Gatton A | Tenthill |  | NCC Rating (A) | 155 | 155 | 155 | 155 | 155
| (GTN) | (THL) |  | 10 PoE Load (A) | 101 | 101 | 99 | 98 | 97
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 531-1 | ECC Rating (A)
|  |  |  | 50 PoE Load (A) | 86 | 86 | 85 | 84 | 82
|  |  |  | Raw LAR (A) | 86 | 86 | 85 | 84 | 82
2-Hour Rating (A)
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) | 86 | 86 | 85 | 84 | 82
Manual Trans Avail (A)
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
532-1 | Tenthill |  |  | NCC Rating (A) | 208 | 208 | 208 | 208 | 208
| (THL) | (532 Tee1) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
GATTON Bulk Supply Point:
533-1 | Tenthill | Mt Sylvia |  | NCC Rating (A) | 78 | 78 | 78 | 78 | 78
| (THL) | (MSV) |  | 10 PoE Load (A) | 23 | 23 | 22 | 20 | 20
|  |  |  | Power Factor (System Normal) | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 533-1 | ECC Rating (A)
|  |  |  | 50 PoE Load (A) | 21 | 20 | 19 | 18 | 18
|  |  |  | Raw LAR (A) | 21 | 20 | 19 | 18 | 18
2-Hour Rating (A)
Auto Trans Avail (A)
Remote Trans Avail (A)
|  |  |  | Manual Trans Avail (A) | 7 | 7 | 7 | 7 | 7
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 14 | 13 | 12 | 11 | 11
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
GOODNA Bulk Supply Point:
3800-1 | Goodna BSP | Cooneana |  | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
| (GNA) | (CNA) |  | 10 PoE Load (A) | 79 | 84 | 97 | 111 | 123
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.97 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3801-1 | Goodna BSP | Carole Park Central |  | NCC Rating (A) | 720 | 720 | 720 | 720 | 720
| (GNA) | (CPC) |  | 10 PoE Load (A) | 264 | 263 | 265 | 266 | 265
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
GOODNA Bulk Supply Point:
3802-1 | Goodna BSP | Springfield |  | NCC Rating (A) | 592 | 592 | 592 | 592 | 592
| (GNA) | (SPF) |  | 10 PoE Load (A) | 414 | 423 | 447 | 467 | 482
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 3806-1 | ECC Rating (A) | 675 | 675 | 675 | 675 | 675
|  |  |  | 50 PoE Load (A) | 679 | 687 | 728 | 758 | 784
|  |  |  | Raw LAR (A) | 4 | 12 | 53 | 83 | 109
|  |  |  | 2-Hour Rating (A) | 800 | 800 | 800 | 800 | 800
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) | 158 | 155 | 178 | 192 | 205
Manual Trans Avail (A)
|  |  |  | POPS Available | Yes | Yes | Yes | Yes | Yes
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3803-1 | Goodna BSP | Carole Park |  | NCC Rating (A) | 502 | 502 | 502 | 502 | 502
| (GNA) | (CPK) |  | 10 PoE Load (A) | 253 | 254 | 264 | 270 | 275
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
GOODNA Bulk Supply Point:
3805-1 | Goodna BSP | Carole Park |  | NCC Rating (A) | 502 | 502 | 502 | 502 | 502
| (GNA) | (CPK) |  | 10 PoE Load (A) | 231 | 232 | 241 | 247 | 251
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3806-1 | Goodna BSP | Springfield |  | NCC Rating (A) | 592 | 592 | 592 | 592 | 592
| (GNA) | (SPF) |  | 10 PoE Load (A) | 412 | 421 | 445 | 465 | 480
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 3802-1 | ECC Rating (A) | 675 | 675 | 675 | 675 | 675
|  |  |  | 50 PoE Load (A) | 679 | 687 | 728 | 758 | 784
|  |  |  | Raw LAR (A) | 4 | 12 | 53 | 83 | 109
|  |  |  | 2-Hour Rating (A) | 800 | 800 | 800 | 800 | 800
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) | 158 | 155 | 178 | 192 | 205
Manual Trans Avail (A)
|  |  |  | POPS Available | Yes | Yes | Yes | Yes | Yes
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
GOODNA Bulk Supply Point:
3807-1 | Goodna BSP | Redbank |  | NCC Rating (A) | 748 | 748 | 748 | 748 | 748
| (GNA) | (RBK) |  | 10 PoE Load (A) | 260 | 459 | 459 | 459 | 457
|  |  |  | Power Factor (System Normal) | 0.95 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3808-1 | Goodna BSP | Carole Park Central |  | NCC Rating (A) | 700 | 700 | 700 | 700 | 700
| (GNA) | (CPC) |  | 10 PoE Load (A) | 264 | 263 | 266 | 266 | 266
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3809-1 | Goodna BSP | Cooneana |  | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
| (GNA) | (CNA) |  | 10 PoE Load (A) | 90 | 95 | 111 | 126 | 141
|  |  |  | Power Factor (System Normal) | 0.98 | 0.97 | 0.97 | 0.97 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3880-1 | Carole Park | Springfield Central |  | NCC Rating (A) | 742 | 742 | 742 | 742 | 742
| (CPK) | (SFC) |  | 10 PoE Load (A) | 174 | 179 | 204 | 221 | 236
|  |  |  | Power Factor (System Normal) | 1 | 1 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3881-1 | Springfield | Springfield Central |  | NCC Rating (A) | 742 | 742 | 742 | 742 | 742
| (SPF) | (SFC) |  | 10 PoE Load (A) | 197 | 203 | 230 | 248 | 264
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
GOODNA Bulk Supply Point:
456-1 | Wacol South |  |  | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
| (WSO) | (456 Tee1) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
456-2 |  | Carole Park Central |  | NCC Rating (A) | 441 | 441 | 441 | 441 | 441
| (456 Tee1) | (CPC) |  | 10 PoE Load (A) | 110 | 112 | 119 | 124 | 127
|  |  |  | Power Factor (System Normal) | 1 | 1 | 1 | 1 | 1
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
456-3 |  | Carole Park |  | NCC Rating (A) | 441 | 441 | 441 | 441 | 441
| (456 Tee1) | (CPK) |  | 10 PoE Load (A) | 111 | 112 | 119 | 124 | 127
|  |  |  | Power Factor (System Normal) | 1 | 1 | 1 | 1 | 1
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
GRIFFIN Bulk Supply Point:
312-1 | Kallangur | Narangba |  | NCC Rating (A) | 422 | 422 | 422 | 422 | 422
| (KLG) | (NRA) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
320-1 | Griffin BSP |  |  | NCC Rating (A) | 700 | 700 | 700 | 700 | 700
| (GFN) | (320 Tee1) |  | 10 PoE Load (A) | 388 | 392 | 397 | 401 | 409
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
GRIFFIN Bulk Supply Point:
320-2 |  | Mango Hill Bus 1 |  | NCC Rating (A) | 495 | 495 | 495 | 495 | 495
| (320 Tee1) | (MHLT2T3) |  | 10 PoE Load (A) | 317 | 321 | 325 | 328 | 328
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 3359 | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | 50 PoE Load (A) | 579 | 587 | 593 | 599 | 602
|  |  |  | Hours PA > 95% Peak Load | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  |  | Raw LAR (A) | 84 | 92 | 98 | 104 | 107
|  |  |  | 2-Hour Rating (A) | 495 | 495 | 495 | 495 | 495
Auto Trans Avail (A)
Remote Trans Avail (A)
|  |  |  | Manual Trans Avail (A) | 121 | 121 | 121 | 121 | 121
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (A) | 84 | 92 | 98 | 104 | 107
|  |  |  | LARc (MW) | 4.8 | 5.2 | 5.5 | 5.9 | 6.1
|  |  | F327(ACO) | ECC Rating (A) |  |  | 495 | 495 | 495
|  |  |  | 50 PoE Load (A) |  |  | 501 | 505 | 506
|  |  |  | Hours PA > 95% Peak Load |  |  | 0.5 | 0.5 | 0.5
|  |  |  | Raw LAR (A) |  |  | 6 | 10 | 11
|  |  |  | 2-Hour Rating (A) |  |  | 495 | 495 | 495
Auto Trans Avail (A)
Remote Trans Avail (A)
Manual Trans Avail (A)
|  |  |  | POPS Available |  |  | No | No | No
|  |  |  | Mobile Gen Reqd (A) |  |  | 6 | 10 | 11
|  |  |  | LARc (A) |  |  | 6 | 10 | 11
|  |  |  | LARc (MW) |  |  | 0.3 | 0.6 | 0.6
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | No | No | No | No | No
GRIFFIN Bulk Supply Point:
320-3 |  | Kallangur |  | NCC Rating (A) | 495 | 495 | 495 | 495 | 495
| (320 Tee1) | (KLG) |  | 10 PoE Load (A) | 81 | 81 | 82 | 83 | 91
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3329-1 | Griffin BSP |  |  | NCC Rating (A) | 700 | 700 | 700 | 700 | 700
| (GFN) | (3329 Tee1) |  | 10 PoE Load (A) | 408 | 412 | 417 | 422 | 434
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.99 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3329-2 |  |  |  | NCC Rating (A) | 748 | 748 | 748 | 748 | 748
| (3329 Tee1) | (3330 Tee1) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3329-3 |  | Kallangur |  | NCC Rating (A) | 711 | 711 | 711 | 711 | 711
| (3329 Tee1) | (KLG) |  | 10 PoE Load (A) | 409 | 412 | 417 | 422 | 435
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.99 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3330-1 | Griffin BSP |  |  | NCC Rating (A) | 717 | 717 | 717 | 717 | 717
| (GFN) | (3330 Tee1) |  | 10 PoE Load (A) | 210 | 212 | 214 | 217 | 223
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
GRIFFIN Bulk Supply Point:
3330-2 |  |  |  | NCC Rating (A) | 523 | 523 | 523 | 523 | 523
| (3330 Tee1) | (3329 Tee1) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3330-3 |  | APM |  | NCC Rating (A) | 717 | 717 | 717 | 717 | 717
| (3330 Tee1) | (APM) |  | 10 PoE Load (A) | 210 | 212 | 215 | 217 | 224
|  |  |  | Power Factor (System Normal) | 1 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3331-1 |  | Kallangur |  | NCC Rating (A) | 717 | 717 | 717 | 717 | 717
| (3331 Tee1) | (KLG) |  | 10 PoE Load (A) | 176 | 178 | 180 | 183 | 189
|  |  |  | Power Factor (System Normal) | 1 | 1 | 1 | 1 | 1
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3331-3 | APM |  |  | NCC Rating (A) | 717 | 717 | 717 | 717 | 717
| (APM) | (3331 Tee1) |  | 10 PoE Load (A) | 210 | 212 | 215 | 217 | 224
|  |  |  | Power Factor (System Normal) | 1 | 1 | 1 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3359-1 |  | Hays Inlet BSP |  | NCC Rating (A) | 700 | 700 | 700 | 700 | 700
| (3359 Tee1) | (HIL) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
GRIFFIN Bulk Supply Point:
3359-2 |  |  |  | NCC Rating (A) | 700 | 700 | 700 | 700 | 700
| (3359 Tee1) | (3359 Tee2) |  | 10 PoE Load (A) | 320 | 324 | 327 | 331 | 334
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.95 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3359-3 |  |  |  | NCC Rating (A) | 700 | 700 | 700 | 700 | 700
| (3359 Tee2) | (3359 Tee3) |  | 10 PoE Load (A) | 320 | 324 | 327 | 331 | 334
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.95 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3359-4 |  | Mango Hill Bus 1 |  | NCC Rating (A) | 762 | 762 | 762 | 762 | 762
| (3359 Tee3) | (MHLT2T3) |  | 10 PoE Load (A) | 320 | 324 | 328 | 331 | 335
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.95 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3359-5 |  |  |  | NCC Rating (A) | 495 | 495 | 553 | 553 | 553
| (3359 Tee2) | (P51001-D) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3359-6 |  |  |  | NCC Rating (A) | 495 | 495 | 582 | 582 | 582
| (3359 Tee3) | (X18574-E) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
GRIFFIN Bulk Supply Point:
3359-7 | Griffin BSP |  |  | NCC Rating (A) | 703 | 703 | 703 | 703 | 703
| (GFN) | (3359 Tee1) |  | 10 PoE Load (A) | 320 | 323 | 327 | 331 | 334
|  |  |  | Power Factor (System Normal) | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
338-1 | Griffin BSP | Strathpine |  | NCC Rating (A) | 348 | 348 | 348 | 348 | 348
| (GFN) | (SPE) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
GYMPIE Bulk Supply Point:
3004-1 | Coondoo Ck Regulator | Tin Can Bay |  | NCC Rating (A) | 127 | 127 | 127 | 127 | 127
| (CDC Reg) | (TCB) |  | 10 PoE Load (A) | 41 | 41 | 40 | 40 | 40
|  |  |  | Power Factor (System Normal) | 1 | 1 | 1 | 1 | 1
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3005-1 | Coondoo Ck Regulator | Tin Can Bay |  | NCC Rating (A) | 582 | 582 | 582 | 582 | 582
| (CDC Reg) | (TCB) |  | 10 PoE Load (A) | 95 | 95 | 95 | 95 | 95
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3009-1 | Gympie BSP | Gympie North |  | NCC Rating (A) | 700 | 700 | 700 | 700 | 700
| (GYM) | (GYN) |  | 10 PoE Load (A) | 149 | 148 | 146 | 145 | 143
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3011-1 | Gympie BSP | Gympie North |  | NCC Rating (A) | 700 | 700 | 700 | 700 | 700
| (GYM) | (GYN) |  | 10 PoE Load (A) | 149 | 148 | 146 | 145 | 143
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
339/2-1 | Amamoor |  |  | NCC Rating (A) | 155 | 155 | 155 | 155 | 155
| (AMR) | (339 Tee1) |  | 10 PoE Load (A) | 58 | 58 | 58 | 58 | 58
|  |  |  | Power Factor (System Normal) | 0.87 | 0.87 | 0.87 | 0.87 | 0.87
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
GYMPIE Bulk Supply Point:
339/2-2 |  | Imbil |  | NCC Rating (A) | 200 | 200 | 200 | 200 | 200
| (339 Tee1) | (IBL) |  | 10 PoE Load (A) | 46 | 46 | 46 | 46 | 46
|  |  |  | Power Factor (System Normal) | 0.86 | 0.86 | 0.86 | 0.86 | 0.86
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 339/2-2 | ECC Rating (A)
|  |  |  | 50 PoE Load (A) | 40 | 41 | 40 | 40 | 40
|  |  |  | Raw LAR (A) | 40 | 41 | 40 | 40 | 40
2-Hour Rating (A)
Auto Trans Avail (A)
Remote Trans Avail (A)
|  |  |  | Manual Trans Avail (A) | 9 | 9 | 9 | 9 | 9
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 32 | 32 | 32 | 32 | 32
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
339-1 | Gympie BSP |  |  | NCC Rating (A) | 742 | 742 | 742 | 742 | 742
| (GYM) | (339 Tee1) |  | 10 PoE Load (A) | 147 | 147 | 164 | 163 | 162
|  |  |  | Power Factor (System Normal) | 0.88 | 0.88 | 0.88 | 0.88 | 0.88
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 339-1 | ECC Rating (A)
|  |  |  | 50 PoE Load (A) | 131 | 131 | 144 | 143 | 142
|  |  |  | Raw LAR (A) | 131 | 131 | 144 | 143 | 142
2-Hour Rating (A)
Auto Trans Avail (A)
Remote Trans Avail (A)
|  |  |  | Manual Trans Avail (A) | 119 | 119 | 132 | 131 | 130
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 12 | 12 | 12 | 12 | 12
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
GYMPIE Bulk Supply Point:
339-2 |  | Amamoor |  | NCC Rating (A) | 210 | 210 | 210 | 210 | 210
| (339 Tee1) | (AMR) |  | 10 PoE Load (A) | 147 | 147 | 165 | 164 | 162
|  |  |  | Power Factor (System Normal) | 0.88 | 0.88 | 0.88 | 0.88 | 0.88
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
339-3 |  |  |  | NCC Rating (A) | 210 | 210 | 210 | 210 | 210
| (339 Tee1) | (340 Tee1) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
340-1 | Gympie BSP |  |  | NCC Rating (A) | 349 | 349 | 349 | 349 | 349
| (GYM) | (340 Tee1) |  | 10 PoE Load (A) | 64 | 64 | 63 | 63 | 62
|  |  |  | Power Factor (System Normal) | 0.96 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
340-2 |  |  |  | NCC Rating (A) | 349 | 349 | 349 | 349 | 349
| (340 Tee1) | (339 Tee1) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
340-4 |  |  |  | NCC Rating (A) | 349 | 349 | 349 | 349 | 349
| (340 Tee1) | (340 Tee2) |  | 10 PoE Load (A) | 64 | 64 | 64 | 63 | 63
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
GYMPIE Bulk Supply Point:
340-5 |  |  |  | NCC Rating (A) | 328 | 328 | 328 | 328 | 328
| (340 Tee2) | (340 Tee3) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
340-6 |  |  |  | NCC Rating (A) | 700 | 700 | 700 | 700 | 700
| (340 Tee3) | (339 Tee2) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
340-7 |  | Kenilworth |  | NCC Rating (A) | 208 | 208 | 208 | 208 | 208
| (339 Tee2) | (KWH) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
340-8 |  | Black Mountain |  | NCC Rating (A) | 328 | 328 | 328 | 328 | 328
| (340 Tee3) | (BMT) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
340-9 |  | Gympie South |  | NCC Rating (A) | 403 | 403 | 403 | 403 | 403
| (340 Tee2) | (GYS) |  | 10 PoE Load (A) | 65 | 65 | 65 | 64 | 64
|  |  |  | Power Factor (System Normal) | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
GYMPIE Bulk Supply Point:
341-1 | Gympie BSP |  |  | NCC Rating (A) | 211 | 211 | 211 | 211 | 211
| (GYM) | (341 Tee1) |  | 10 PoE Load (A) | 189 | 189 | 189 | 189 | 189
|  |  |  | Power Factor (System Normal) | 1 | 1 | 1 | 1 | 1
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 429 | ECC Rating (A) | 211 | 211 | 211 | 211 | 211
|  |  |  | 50 PoE Load (A) | 462 | 462 | 462 | 462 | 460
|  |  |  | Hours PA > 95% Peak Load | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  |  | Raw LAR (A) | 251 | 251 | 251 | 251 | 249
|  |  |  | 2-Hour Rating (A) | 278 | 278 | 278 | 278 | 278
Auto Trans Avail (A)
Remote Trans Avail (A)
Manual Trans Avail (A)
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 175 | 175 | 175 | 175 | 175
|  |  |  | LARc (A) | 184 | 184 | 184 | 184 | 182
|  |  |  | LARc (MW) | 10.5 | 10.5 | 10.5 | 10.5 | 10.4
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | No | No | No | No | No
341-2 |  | Customer |  | NCC Rating (A) | 410 | 410 | 410 | 410 | 410
| (341 Tee1) |  |  | 10 PoE Load (A) | 53 | 53 | 53 | 53 | 53
|  |  |  | Power Factor (System Normal) | 0.93 | 0.93 | 0.93 | 0.93 | 0.93
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
GYMPIE Bulk Supply Point:
341-3 |  | Coondoo Ck Regulator |  | NCC Rating (A) | 210 | 210 | 210 | 210 | 210
| (341 Tee1) | (CDC Reg) |  | 10 PoE Load (A) | 144 | 144 | 144 | 144 | 143
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 341-3 | ECC Rating (A)
|  |  |  | 50 PoE Load (A) | 121 | 121 | 121 | 121 | 120
|  |  |  | Raw LAR (A) | 121 | 121 | 121 | 121 | 120
2-Hour Rating (A)
Auto Trans Avail (A)
Remote Trans Avail (A)
Manual Trans Avail (A)
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 121 | 121 | 121 | 121 | 120
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
341-4 | Coondoo Ck Regulator |  |  | NCC Rating (A) | 717 | 717 | 717 | 717 | 717
| (CDC Reg) | (341 Tee2) |  | 10 PoE Load (A) | 135 | 135 | 135 | 135 | 134
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
351-1 | Gympie BSP | Gympie South |  | NCC Rating (A) | 355 | 355 | 355 | 355 | 355
| (GYM) | (GYS) |  | 10 PoE Load (A) | 74 | 74 | 73 | 73 | 72
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
GYMPIE Bulk Supply Point:
429-1 | Gympie BSP |  |  | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
| (GYM) | (429 Tee1) |  | 10 PoE Load (A) | 261 | 261 | 260 | 260 | 260
|  |  |  | Power Factor (System Normal) | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
429-2 |  | Goomboorian |  | NCC Rating (A) | 461 | 461 | 461 | 461 | 461
| (429 Tee1) | (GBN) |  | 10 PoE Load (A) | 46 | 46 | 46 | 46 | 46
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
429-3 |  | Customer |  | NCC Rating (A) | 410 | 410 | 410 | 410 | 410
| (429 Tee1) |  |  | 10 PoE Load (A) | 215 | 215 | 215 | 215 | 215
|  |  |  | Power Factor (System Normal) | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
HAYS INLET Bulk Supply Point:
HAYS INLET Bulk Supply Point:
305-1 | Hays Inlet BSP | Deception Bay |  | NCC Rating (A) | 759 | 759 | 759 | 759 | 759
| (HIL) | (DBY) |  | 10 PoE Load (A) | 702 | 713 | 717 | 723 | 725
|  |  |  | Power Factor (System Normal) | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | F448(ACO) | ECC Rating (A) | 759 | 759 | 759 | 759 | 759
|  |  |  | 50 PoE Load (A) | 871 | 890 | 891 | 902 | 907
|  |  |  | Raw LAR (A) | 112 | 131 | 132 | 143 | 148
|  |  |  | 2-Hour Rating (A) | 1291 | 1291 | 1291 | 1291 | 1291
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) | 68 | 72 | 73 | 74 | 77
|  |  |  | Manual Trans Avail (A) | 29 | 29 | 30 | 30 | 29
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 15 | 30 | 29 | 39 | 42
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 497-1 | ECC Rating (A) | 759 | 759 | 759 | 759 | 759
|  |  |  | 50 PoE Load (A) | 969 | 994 | 1003 | 1012 | 1016
|  |  |  | Raw LAR (A) | 210 | 235 | 244 | 253 | 257
|  |  |  | 2-Hour Rating (A) | 1291 | 1291 | 1291 | 1291 | 1291
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) | 339 | 363 | 366 | 198 | 199
|  |  |  | Manual Trans Avail (A) | 46 | 46 | 46 | 47 | 47
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 8 | 11
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 311-1 | ECC Rating (A) | 759 | 759 | 759 | 759 | 759
|  |  |  | 50 PoE Load (A) | 809 | 821 | 826 | 832 | 834
|  |  |  | Raw LAR (A) | 50 | 62 | 67 | 73 | 75
|  |  |  | 2-Hour Rating (A) | 1291 | 1291 | 1291 | 1291 | 1291
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) | 83 | 89 | 90 | 91 | 91
Manual Trans Avail (A)
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
HAYS INLET Bulk Supply Point:
311-1 | Hays Inlet BSP | Deception Bay |  | NCC Rating (A) | 623 | 623 | 623 | 623 | 623
| (HIL) | (DBY) |  | 10 PoE Load (A) | 234 | 237 | 239 | 240 | 241
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 305-1 | ECC Rating (A) | 623 | 623 | 623 | 623 | 623
|  |  |  | 50 PoE Load (A) | 703 | 714 | 719 | 725 | 726
|  |  |  | Raw LAR (A) | 80 | 91 | 96 | 102 | 103
|  |  |  | 2-Hour Rating (A) | 640 | 640 | 640 | 640 | 640
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) | 74 | 79 | 80 | 80 | 81
|  |  |  | Manual Trans Avail (A) | 28 | 28 | 29 | 29 | 29
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (A) | 63 | 74 | 79 | 85 | 86
|  |  |  | LARc (MW) | 3.5 | 4.1 | 4.4 | 4.7 | 4.8
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | No | No | No | No | No
HAYS INLET Bulk Supply Point:
3250-1 | Deception Bay | Burpengary |  | NCC Rating (A) | 713 | 713 | 713 | 713 | 713
| (DBY) | (BGY) |  | 10 PoE Load (A) | 428 | 440 | 444 | 449 | 451
|  |  |  | Power Factor (System Normal) | 0.97 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 497-1 | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
|  |  |  | 50 PoE Load (A) | 828 | 860 | 870 | 880 | 884
|  |  |  | Raw LAR (A) | 115 | 147 | 157 | 167 | 171
|  |  |  | 2-Hour Rating (A) | 800 | 800 | 800 | 800 | 800
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) | 379 | 404 | 408 | 259 | 260
|  |  |  | Manual Trans Avail (A) | 60 | 60 | 60 | 61 | 61
|  |  |  | POPS Available | Yes | Yes | Yes | Yes | Yes
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  | F448(ACO) | ECC Rating (A) |  | 713 | 713 | 713 | 713
|  |  |  | 50 PoE Load (A) |  | 719 | 726 | 738 | 745
|  |  |  | Raw LAR (A) |  | 6 | 13 | 25 | 32
|  |  |  | 2-Hour Rating (A) |  | 800 | 800 | 800 | 800
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) |  | 97 | 98 | 99 | 100
Manual Trans Avail (A)
|  |  |  | POPS Available |  | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) |  | 0 | 0 | 0 | 0
|  |  |  | LARc (A) |  | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) |  | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
325-1 | Hays Inlet BSP | Scarborough |  | NCC Rating (A) | 529 | 529 | 529 | 529 | 529
| (HIL) | (SBH) |  | 10 PoE Load (A) | 299 | 299 | 302 | 304 | 304
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
HAYS INLET Bulk Supply Point:
3251-1 | Burpengary | Morayfield |  | NCC Rating (A) | 464 | 464 | 464 | 464 | 464
| (BGY) | (MFD) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | F448(ACO) | ECC Rating (A) | 464 | 464 | 464 | 464 | 464
|  |  |  | 50 PoE Load (A) | 535 | 539 | 552 | 565 | 573
|  |  |  | Raw LAR (A) | 71 | 75 | 88 | 101 | 109
|  |  |  | 2-Hour Rating (A) | 664 | 664 | 664 | 664 | 664
Auto Trans Avail (A)
Remote Trans Avail (A)
|  |  |  | Manual Trans Avail (A) | 82 | 77 | 79 | 79 | 80
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 9 | 22 | 29
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
326-1 | Redcliffe | Scarborough |  | NCC Rating (A) | 322 | 322 | 322 | 322 | 322
| (RCF) | (SBH) |  | 10 PoE Load (A) | 33 | 35 | 38 | 42 | 45
|  |  |  | Power Factor (System Normal) | 1 | 1 | 1 | 1 | 1
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
HAYS INLET Bulk Supply Point:
327-1 | Hays Inlet BSP | Mango Hill Bus 2 |  | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
| (HIL) | (MHLT1) |  | 10 PoE Load (A) | 431 | 439 | 444 | 449 | 452
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
329-1 | Redcliffe | Duffield Road |  | NCC Rating (A) | 578 | 578 | 578 | 578 | 578
| (RCF) | (DRD) |  | 10 PoE Load (A) | 108 | 108 | 109 | 109 | 110
|  |  |  | Power Factor (System Normal) | 0.95 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
330-1 | Hays Inlet BSP | Duffield Road |  | NCC Rating (A) | 543 | 543 | 543 | 543 | 543
| (HIL) | (DRD) |  | 10 PoE Load (A) | 263 | 262 | 262 | 263 | 262
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
331-1 | Hays Inlet BSP | Duffield Road |  | NCC Rating (A) | 543 | 543 | 543 | 543 | 543
| (HIL) | (DRD) |  | 10 PoE Load (A) | 263 | 263 | 263 | 264 | 263
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
332-1 | Hays Inlet BSP | Redcliffe |  | NCC Rating (A) | 524 | 524 | 524 | 524 | 524
| (HIL) | (RCF) |  | 10 PoE Load (A) | 282 | 281 | 281 | 282 | 281
|  |  |  | Power Factor (System Normal) | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
HAYS INLET Bulk Supply Point:
451-1 | Narangba | Burpengary |  | NCC Rating (A) | 422 | 422 | 422 | 422 | 422
| (NRA) | (BGY) |  | 10 PoE Load (A) | 47 | 37 | 37 | 36 | 36
|  |  |  | Power Factor (System Normal) | 0.93 | 0.92 | 0.92 | 0.98 | 0.92
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 3250-1 | ECC Rating (A) | 422 | 422 | 422 | 422 | 422
|  |  |  | 50 PoE Load (A) | 423 | 425 | 429 | 433 | 435
|  |  |  | Raw LAR (A) | 1 | 3 | 7 | 11 | 13
|  |  |  | 2-Hour Rating (A) | 593 | 593 | 593 | 593 | 593
Auto Trans Avail (A)
Remote Trans Avail (A)
|  |  |  | Manual Trans Avail (A) | 57 | 57 | 57 | 58 | 58
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 497-1 | ECC Rating (A) |  | 422 | 422 | 422 | 422
|  |  |  | 50 PoE Load (A) |  | 439 | 445 | 451 | 454
|  |  |  | Raw LAR (A) |  | 17 | 23 | 29 | 32
|  |  |  | 2-Hour Rating (A) |  | 593 | 593 | 593 | 593
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) |  | 234 | 241 | 243 | 245
Manual Trans Avail (A)
|  |  |  | POPS Available |  | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) |  | 0 | 0 | 0 | 0
|  |  |  | LARc (A) |  | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) |  | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
HAYS INLET Bulk Supply Point:
497-1 | Hays Inlet BSP | Narangba |  | NCC Rating (A) | 713 | 713 | 713 | 713 | 713
| (HIL) | (NRA) |  | 10 PoE Load (A) | 479 | 496 | 502 | 507 | 509
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 3250-1 | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
|  |  |  | 50 PoE Load (A) | 822 | 852 | 861 | 871 | 875
|  |  |  | Raw LAR (A) | 109 | 139 | 148 | 158 | 162
|  |  |  | 2-Hour Rating (A) | 800 | 800 | 800 | 800 | 800
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) | 223 | 238 | 240 | 244 | 246
Manual Trans Avail (A)
|  |  |  | POPS Available | Yes | Yes | Yes | Yes | Yes
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
JIMBOOMBA Bulk Supply Point:
470-1 | Jimboomba BSP | Logan Village |  | NCC Rating (A) | 512 | 512 | 512 | 512 | 512
| (JBB) | (LGV) |  | 10 PoE Load (A) | 260 | 280 | 374 | 407 | 438
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.95 | 0.95 | 0.94
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
479-1 | Jimboomba BSP | North Maclean |  | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
| (JBB) | (NMC) |  | 10 PoE Load (A) | 625 | 650 | 668 | 698 | 721
|  |  |  | Power Factor (System Normal) | 0.97 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
LOCKROSE Bulk Supply Point:
378-1 | Lockrose BSP |  |  | NCC Rating (A) | 432 | 432 | 432 | 432 | 432
| (LRE) | (378 Tee1) |  | 10 PoE Load (A) | 232 | 234 | 263 | 264 | 265
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 378-1 | ECC Rating (A)
|  |  |  | 50 PoE Load (A) |  |  | 116 | 116 | 116
|  |  |  | Raw LAR (A) |  |  | 116 | 116 | 116
2-Hour Rating (A)
Auto Trans Avail (A)
Remote Trans Avail (A)
Manual Trans Avail (A)
|  |  |  | POPS Available |  |  | No | No | No
|  |  |  | Mobile Gen Reqd (A) |  |  | 116 | 116 | 116
|  |  |  | LARc (A) |  |  | 0 | 0 | 0
|  |  |  | LARc (MW) |  |  | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
378-2 |  | Glenore Grove |  | NCC Rating (A) | 800 | 800 | 818 | 818 | 818
| (378 Tee1) | (GGR) |  | 10 PoE Load (A) | 103 | 103 | 140 | 140 | 140
|  |  |  | Power Factor (System Normal) | 1 | 1 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
378-3 |  |  |  | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
| (378 Tee1) | (378 Tee2) |  | 10 PoE Load (A) | 131 | 133 | 123 | 125 | 126
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
LOCKROSE Bulk Supply Point:
378-4 |  |  |  | NCC Rating (A) | 200 | 200 | 200 | 200 | 200
| (378 Tee2) | (532 Tee1) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
378-5 |  | Laidley |  | NCC Rating (A) | 800 | 800 | 800 | 800 | 800
| (378 Tee2) | (LLY) |  | 10 PoE Load (A) | 132 | 133 | 123 | 125 | 126
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
LOCKROSE Bulk Supply Point:
380-1 | Murrumba |  |  | NCC Rating (A) | 155 | 200 | 200 | 200 | 200
| (MRB) | (380 Tee1) |  | 10 PoE Load (A) | 75 | 77 | 76 | 74 | 77
|  |  |  | Power Factor (System Normal) | 0.97 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 3828-1 | ECC Rating (A) | 155
|  |  |  | 50 PoE Load (A) | 184
|  |  |  | Raw LAR (A) | 29
|  |  |  | 2-Hour Rating (A) | 195
Auto Trans Avail (A)
Remote Trans Avail (A)
Manual Trans Avail (A)
|  |  |  | POPS Available | No
|  |  |  | Mobile Gen Reqd (A) | 29
|  |  |  | LARc (A) | 0
|  |  |  | LARc (MW) | 0
|  |  | 380-1 | ECC Rating (A)
|  |  |  | 50 PoE Load (A) | 7 | 7 | 7 | 7 | 7
|  |  |  | Raw LAR (A) | 7 | 7 | 7 | 7 | 7
2-Hour Rating (A)
Auto Trans Avail (A)
Remote Trans Avail (A)
Manual Trans Avail (A)
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 7 | 7 | 7 | 7 | 7
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 382 | ECC Rating (A) | 34 | 34
|  |  |  | 50 PoE Load (A) | 54 | 54
|  |  |  | Hours PA > 95% Peak Load | 5 | 5
|  |  |  | Raw LAR (A) | 20 | 19
|  |  |  | 2-Hour Rating (A) | 34 | 34
Auto Trans Avail (A)
Remote Trans Avail (A)
Manual Trans Avail (A)
|  |  |  | POPS Available | No | No
|  |  |  | Mobile Gen Reqd (A) | 20 | 19
|  |  |  | LARc (A) | 20 | 19
|  |  |  | LARc (MW) | 1.1 | 1.1
|  |  | 3829-1 | ECC Rating (A) | 44
|  |  |  | 50 PoE Load (A) | 61
|  |  |  | Hours PA > 95% Peak Load | 5
|  |  |  | Raw LAR (A) | 17
|  |  |  | 2-Hour Rating (A) | 44
Auto Trans Avail (A)
Remote Trans Avail (A)
Manual Trans Avail (A)
|  |  |  | POPS Available | No
|  |  |  | Mobile Gen Reqd (A) | 17
|  |  |  | LARc (A) | 17
|  |  |  | LARc (MW) | 1
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | No | No | Yes | Yes | Yes
LOCKROSE Bulk Supply Point:
380-2 |  | Somerset Dam |  | NCC Rating (A) | 155 | 160 | 160 | 160 | 160
| (380 Tee1) | (SDM) |  | 10 PoE Load (A) | 8 | 8 | 8 | 8 | 8
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
380-3 |  | Toogoolawah |  | NCC Rating (A) | 200 | 200 | 200 | 200 | 200
| (380 Tee1) | (TGW) |  | 10 PoE Load (A) | 67 | 70 | 69 | 67 | 69
|  |  |  | Power Factor (System Normal) | 0.97 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
381-1 | Lockrose BSP |  |  | NCC Rating (A) | 432 | 432 | 432 | 432 | 432
| (LRE) | (381 Tee1) |  | 10 PoE Load (A) | 203 | 201 | 212 | 211 | 210
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.94 | 0.94 | 0.94
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 382 | ECC Rating (A) | 226 | 226
|  |  |  | 50 PoE Load (A) | 322 | 321
|  |  |  | Hours PA > 95% Peak Load | 0.5 | 0.5
|  |  |  | Raw LAR (A) | 97 | 95
|  |  |  | 2-Hour Rating (A) | 226 | 226
Auto Trans Avail (A)
Remote Trans Avail (A)
Manual Trans Avail (A)
|  |  |  | POPS Available | Yes | Yes
|  |  |  | Mobile Gen Reqd (A) | 97 | 95
|  |  |  | LARc (A) | 97 | 95
|  |  |  | LARc (MW) | 5.5 | 5.4
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | No | No | Yes | Yes | Yes
LOCKROSE Bulk Supply Point:
381-2 |  |  |  | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
| (381 Tee1) | (382 Tee1) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
381-3 |  |  |  | NCC Rating (A) | 432 | 432 | 432 | 432 | 432
| (381 Tee1) | (381 Tee2) |  | 10 PoE Load (A) | 203 | 201 | 212 | 211 | 211
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.94 | 0.94 | 0.94
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 382 | ECC Rating (A) | 226 | 226
|  |  |  | 50 PoE Load (A) | 322 | 321
|  |  |  | Hours PA > 95% Peak Load | 0.5 | 0.5
|  |  |  | Raw LAR (A) | 97 | 95
|  |  |  | 2-Hour Rating (A) | 226 | 226
Auto Trans Avail (A)
Remote Trans Avail (A)
Manual Trans Avail (A)
|  |  |  | POPS Available | Yes | Yes
|  |  |  | Mobile Gen Reqd (A) | 97 | 95
|  |  |  | LARc (A) | 97 | 95
|  |  |  | LARc (MW) | 5.5 | 5.4
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | No | No | Yes | Yes | Yes
381-4 |  |  |  | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
| (381 Tee2) | (383 Tee1) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
LOCKROSE Bulk Supply Point:
381-5 |  |  |  | NCC Rating (A) | 293 | 293 | 553 | 553 | 553
| (381 Tee2) | (381 Tee3) |  | 10 PoE Load (A) | 203 | 202 | 212 | 211 | 211
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.95 | 0.95 | 0.94
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 382 | ECC Rating (A) | 226 | 226
|  |  |  | 50 PoE Load (A) | 322 | 321
|  |  |  | Hours PA > 95% Peak Load | 0.5 | 0.5
|  |  |  | Raw LAR (A) | 97 | 95
|  |  |  | 2-Hour Rating (A) | 226 | 226
Auto Trans Avail (A)
Remote Trans Avail (A)
Manual Trans Avail (A)
|  |  |  | POPS Available | Yes | Yes
|  |  |  | Mobile Gen Reqd (A) | 97 | 95
|  |  |  | LARc (A) | 97 | 95
|  |  |  | LARc (MW) | 5.5 | 5.4
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | No | No | Yes | Yes | Yes
381-6 |  | Coominya |  | NCC Rating (A) | 403 | 403 | 403 | 403 | 403
| (381 Tee3) | (CMY) |  | 10 PoE Load (A) | 76 | 75 | 74 | 74 | 73
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 381-6 | ECC Rating (A)
|  |  |  | 50 PoE Load (A) | 107 | 107 | 107 | 107 | 106
|  |  |  | Raw LAR (A) | 107 | 107 | 107 | 107 | 106
2-Hour Rating (A)
Auto Trans Avail (A)
Remote Trans Avail (A)
Manual Trans Avail (A)
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 107 | 107 | 107 | 107 | 106
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
LOCKROSE Bulk Supply Point:
381-7 |  |  |  | NCC Rating (A) | 155 | 155 | 582 | 582 | 582
| (381 Tee3) | (381 Tee4) |  | 10 PoE Load (A) | 75 | 74 | 139 | 138 | 138
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.93 | 0.93 | 0.93
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 382 | ECC Rating (A) | 156 | 156
|  |  |  | 50 PoE Load (A) | 254 | 252
|  |  |  | Hours PA > 95% Peak Load | 0.5 | 0.5
|  |  |  | Raw LAR (A) | 98 | 96
|  |  |  | 2-Hour Rating (A) | 156 | 156
Auto Trans Avail (A)
Remote Trans Avail (A)
Manual Trans Avail (A)
|  |  |  | POPS Available | Yes | Yes
|  |  |  | Mobile Gen Reqd (A) | 98 | 96
|  |  |  | LARc (A) | 98 | 96
|  |  |  | LARc (MW) | 5.6 | 5.5
|  |  | 381-7 | ECC Rating (A)
|  |  |  | 50 PoE Load (A) | 107 | 107 | 107 | 107 | 106
|  |  |  | Raw LAR (A) | 107 | 107 | 107 | 107 | 106
2-Hour Rating (A)
Auto Trans Avail (A)
Remote Trans Avail (A)
Manual Trans Avail (A)
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 107 | 107 | 107 | 107 | 106
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | No | No | Yes | Yes | Yes
LOCKROSE Bulk Supply Point:
381-8 |  | Coominya |  | NCC Rating (A) | 403 | 403 | 403 | 403 | 403
| (381 Tee4) | (CMY) |  | 10 PoE Load (A) | 52 | 52 | 51 | 51 | 51
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 381-8 | ECC Rating (A)
|  |  |  | 50 PoE Load (A) | 107 | 107 | 107 | 107 | 106
|  |  |  | Raw LAR (A) | 107 | 107 | 107 | 107 | 106
2-Hour Rating (A)
Auto Trans Avail (A)
Remote Trans Avail (A)
Manual Trans Avail (A)
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 107 | 107 | 107 | 107 | 106
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
381-9 |  | Paddy Gully |  | NCC Rating (A) | 155 | 155 | 200 | 200 | 200
| (381 Tee4) | (PGY) |  | 10 PoE Load (A) | 75 | 74 | 88 | 87 | 88
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.93 | 0.93 | 0.93
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 382 | ECC Rating (A) | 121 | 121 | 200 | 200 | 200
|  |  |  | 50 PoE Load (A) | 217 | 215 | 262 | 262 | 260
|  |  |  | Hours PA > 95% Peak Load | 0.5 | 0.5
|  |  |  | Raw LAR (A) | 96 | 95 | 62 | 62 | 60
|  |  |  | 2-Hour Rating (A) | 121 | 121 | 263 | 263 | 263
Auto Trans Avail (A)
Remote Trans Avail (A)
Manual Trans Avail (A)
|  |  |  | POPS Available | Yes | Yes | Yes | Yes | Yes
|  |  |  | Mobile Gen Reqd (A) | 96 | 95 | 62 | 62 | 60
|  |  |  | LARc (A) | 96 | 95 | 0 | 0 | 0
|  |  |  | LARc (MW) | 5.5 | 5.4 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | No | No | Yes | Yes | Yes
LOCKROSE Bulk Supply Point:
382-1 | Lockrose BSP |  |  | NCC Rating (A) | 432 | 432 | 432 | 432 | 432
| (LRE) | (382 Tee1) |  | 10 PoE Load (A) | 215 | 213 | 190 | 189 | 189
|  |  |  | Power Factor (System Normal) | 0.92 | 0.92 | 0.95 | 0.95 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
382-2 |  |  |  | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
| (382 Tee1) | (381 Tee1) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
382-3 |  | Paddy Gully |  | NCC Rating (A) | 432 | 432 | 432 | 432 | 432
| (382 Tee1) | (PGY) |  | 10 PoE Load (A) | 215 | 213 | 191 | 190 | 190
|  |  |  | Power Factor (System Normal) | 0.92 | 0.92 | 0.95 | 0.95 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
LOCKROSE Bulk Supply Point:
3828-1 | Paddy Gully | Esk |  | NCC Rating (A) | 155 | 155 | 155 | 403 | 403
| (PGY) | (ESK) |  | 10 PoE Load (A) | 127 | 122 | 120 | 118 | 121
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 382 | ECC Rating (A) | 80 | 80
|  |  |  | 50 PoE Load (A) | 96 | 95
|  |  |  | Hours PA > 95% Peak Load | 2 | 2
|  |  |  | Raw LAR (A) | 15 | 15
|  |  |  | 2-Hour Rating (A) | 80 | 80
Auto Trans Avail (A)
Remote Trans Avail (A)
Manual Trans Avail (A)
|  |  |  | POPS Available | No | No
|  |  |  | Mobile Gen Reqd (A) | 15 | 15
|  |  |  | LARc (A) | 15 | 15
|  |  |  | LARc (MW) | 0.8 | 0.8
|  |  | 3829-1 | ECC Rating (A) | 147 | 155 | 155
|  |  |  | 50 PoE Load (A) | 217 | 242 | 238
|  |  |  | Hours PA > 95% Peak Load | 2
|  |  |  | Raw LAR (A) | 70 | 87 | 83
|  |  |  | 2-Hour Rating (A) | 147 | 194 | 194
Auto Trans Avail (A)
Remote Trans Avail (A)
Manual Trans Avail (A)
|  |  |  | POPS Available | Yes | Yes | Yes
|  |  |  | Mobile Gen Reqd (A) | 70 | 87 | 83
|  |  |  | LARc (A) | 70 | 0 | 0
|  |  |  | LARc (MW) | 3.9 | 0 | 0
|  |  | 380 | ECC Rating (A) | 154 | 154 | 154 | 154
|  |  |  | 50 PoE Load (A) | 160 | 159 | 156 | 155
|  |  |  | Raw LAR (A) | 6 | 5 | 2 | 1
|  |  |  | 2-Hour Rating (A) | 194 | 194 | 194 | 194
Auto Trans Avail (A)
Remote Trans Avail (A)
Manual Trans Avail (A)
|  |  |  | POPS Available | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 6 | 5 | 2 | 1
|  |  |  | LARc (A) | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | No | No | Yes | Yes | Yes
LOCKROSE Bulk Supply Point:
3829-1 | Paddy Gully | Murrumba |  | NCC Rating (A) | 155 | 155 | 155 | 155 | 155
| (PGY) | (MRB) |  | 10 PoE Load (A) | 128 | 130 | 128 | 126 | 129
|  |  |  | Power Factor (System Normal) | 0.93 | 0.92 | 0.92 | 0.93 | 0.92
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 382 | ECC Rating (A) | 89 | 89
|  |  |  | 50 PoE Load (A) | 108 | 107
|  |  |  | Hours PA > 95% Peak Load | 0.5 | 0.5
|  |  |  | Raw LAR (A) | 20 | 19
|  |  |  | 2-Hour Rating (A) | 89 | 89
Auto Trans Avail (A)
Remote Trans Avail (A)
Manual Trans Avail (A)
|  |  |  | POPS Available | No | No
|  |  |  | Mobile Gen Reqd (A) | 20 | 19
|  |  |  | LARc (A) | 20 | 19
|  |  |  | LARc (MW) | 1 | 1
|  |  | 3828-1 | ECC Rating (A) | 155 | 155 | 155 | 155 | 155
|  |  |  | 50 PoE Load (A) | 237 | 230 | 226 | 225 | 224
|  |  |  | Raw LAR (A) | 82 | 75 | 71 | 70 | 69
|  |  |  | 2-Hour Rating (A) | 195 | 195 | 195 | 195 | 195
Auto Trans Avail (A)
Remote Trans Avail (A)
Manual Trans Avail (A)
|  |  |  | POPS Available | Yes | Yes | Yes | Yes | Yes
|  |  |  | Mobile Gen Reqd (A) | 82 | 75 | 71 | 70 | 69
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 3840-1 | ECC Rating (A) | 155 | 155
|  |  |  | 50 PoE Load (A) | 158 | 156
|  |  |  | Raw LAR (A) | 3 | 1
|  |  |  | 2-Hour Rating (A) | 195 | 195
Auto Trans Avail (A)
Remote Trans Avail (A)
Manual Trans Avail (A)
|  |  |  | POPS Available | No | No
|  |  |  | Mobile Gen Reqd (A) | 3 | 1
|  |  |  | LARc (A) | 0 | 0
|  |  |  | LARc (MW) | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | No | No | Yes | Yes | Yes
LOCKROSE Bulk Supply Point:
3831-1 | Lockrose BSP | Tarampa |  | NCC Rating (A) | 355 | 355 | 355 | 355 | 355
| (LRE) | (TRP) |  | 10 PoE Load (A) | 187 | 187 | 187 | 188 | 187
|  |  |  | Power Factor (System Normal) | 0.94 | 0.94 | 0.94 | 0.94 | 0.94
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 3831-1 | ECC Rating (A)
|  |  |  | 50 PoE Load (A) | 154 | 154 | 154 | 155 | 154
|  |  |  | Raw LAR (A) | 154 | 154 | 154 | 155 | 154
2-Hour Rating (A)
Auto Trans Avail (A)
Remote Trans Avail (A)
|  |  |  | Manual Trans Avail (A) | 76 | 76 | 76 | 76 | 76
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 78 | 79 | 78 | 79 | 78
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3832-1 | Tarampa |  |  | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
| (TRP) | (383 Tee1) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3832-2 |  |  |  | NCC Rating (A) | 155 | 155 | 155 | 155 | 155
| (3832 Tee1) | (381 Tee1) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
LOCKROSE Bulk Supply Point:
3832-3 |  | Lowood |  | NCC Rating (A) | 434 | 434 | 434 | 434 | 434
| (3832 Tee1) | (LWD) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3840-1 | Esk | Toogoolawah |  | NCC Rating (A) | 155 | 155 | 155 | 155 | 155
| (ESK) | (TGW) |  | 10 PoE Load (A) | 56 | 52 | 51 | 50 | 52
|  |  |  | Power Factor (System Normal) | 0.99 | 1 | 1 | 1 | 1
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 382 | ECC Rating (A) | 22 | 22
|  |  |  | 50 PoE Load (A) | 36 | 36
|  |  |  | Hours PA > 95% Peak Load | 3.5 | 3.5
|  |  |  | Raw LAR (A) | 15 | 14
|  |  |  | 2-Hour Rating (A) | 22 | 22
Auto Trans Avail (A)
Remote Trans Avail (A)
Manual Trans Avail (A)
|  |  |  | POPS Available | No | No
|  |  |  | Mobile Gen Reqd (A) | 15 | 14
|  |  |  | LARc (A) | 15 | 14
|  |  |  | LARc (MW) | 0.8 | 0.8
|  |  | 3829-1 | ECC Rating (A) | 87 | 155 | 155 | 155 | 155
|  |  |  | 50 PoE Load (A) | 157 | 182 | 178 | 177 | 175
|  |  |  | Hours PA > 95% Peak Load | 3.5
|  |  |  | Raw LAR (A) | 70 | 27 | 23 | 22 | 20
|  |  |  | 2-Hour Rating (A) | 87 | 194 | 194 | 194 | 194
Auto Trans Avail (A)
Remote Trans Avail (A)
Manual Trans Avail (A)
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 70 | 27 | 23 | 22 | 20
|  |  |  | LARc (A) | 70 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 4 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | No | No | Yes | Yes | Yes
LOCKROSE Bulk Supply Point:
384-1 | Lockrose BSP |  |  | NCC Rating (A) | 451 | 451 | 451 | 451 | 451
| (LRE) | (384 Tee1) |  | 10 PoE Load (A) | 243 | 245 | 219 | 221 | 222
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 384-1 | ECC Rating (A)
|  |  |  | 50 PoE Load (A) |  |  | 55 | 55 | 54
|  |  |  | Raw LAR (A) |  |  | 55 | 55 | 54
2-Hour Rating (A)
Auto Trans Avail (A)
Remote Trans Avail (A)
Manual Trans Avail (A)
|  |  |  | POPS Available |  |  | No | No | No
|  |  |  | Mobile Gen Reqd (A) |  |  | 55 | 55 | 54
|  |  |  | LARc (A) |  |  | 0 | 0 | 0
|  |  |  | LARc (MW) |  |  | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
384-2 |  | Glenore Grove |  | NCC Rating (A) | 293 | 293 | 293 | 293 | 293
| (384 Tee1) | (GGR) |  | 10 PoE Load (A) | 104 | 104 | 65 | 65 | 65
|  |  |  | Power Factor (System Normal) | 0.94 | 0.94 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
384-3 |  | Laidley |  | NCC Rating (A) | 495 | 495 | 495 | 495 | 495
| (384 Tee1) | (LLY) |  | 10 PoE Load (A) | 141 | 143 | 154 | 156 | 157
|  |  |  | Power Factor (System Normal) | 1 | 1 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
LOCKROSE Bulk Supply Point:
3870-1 | Lockrose BSP | Lowood |  | NCC Rating (A) | 703 | 703 | 703 | 703 | 703
| (LRE) | (LWD) |  | 10 PoE Load (A) | 216 | 216 | 216 | 216 | 214
|  |  |  | Power Factor (System Normal) | 0.94 | 0.94 | 0.94 | 0.94 | 0.94
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 3870-1 | ECC Rating (A)
|  |  |  | 50 PoE Load (A) | 174 | 174 | 174 | 173 | 173
|  |  |  | Raw LAR (A) | 174 | 174 | 174 | 173 | 173
2-Hour Rating (A)
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) | 119 | 119 | 119 | 119 | 119
Manual Trans Avail (A)
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 55 | 55 | 55 | 54 | 54
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3871-1 | Lowood | Wivenhoe |  | NCC Rating (A) | 432 | 432 | 432 | 432 | 432
| (LWD) | (WHO) |  | 10 PoE Load (A) | 152 | 152 | 152 | 152 | 151
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 3871-1 | ECC Rating (A)
|  |  |  | 50 PoE Load (A) | 119 | 119 | 119 | 119 | 119
|  |  |  | Raw LAR (A) | 119 | 119 | 119 | 119 | 119
2-Hour Rating (A)
Auto Trans Avail (A)
Remote Trans Avail (A)
|  |  |  | Manual Trans Avail (A) | 31 | 31 | 31 | 31 | 31
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 88 | 88 | 88 | 88 | 87
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
LOGANLEA Bulk Supply Point:
407-1 | Loganlea BSP | Woodridge |  | NCC Rating (A) | 777 | 777 | 777 | 777 | 777
| (LGL) | (WRG) |  | 10 PoE Load (A) | 335 | 330 | 326 | 322 | 317
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
408-1 | Loganlea BSP | Kingston |  | NCC Rating (A) | 529 | 529 | 529 | 529 | 529
| (LGL) | (KSN) |  | 10 PoE Load (A) | 359 | 358 | 357 | 358 | 356
|  |  |  | Power Factor (System Normal) | 0.94 | 0.94 | 0.94 | 0.94 | 0.94
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 452-1 | ECC Rating (A) | 529 | 529 | 529 | 529 | 529
|  |  |  | 50 PoE Load (A) | 584 | 581 | 581 | 581 | 581
|  |  |  | Raw LAR (A) | 55 | 52 | 52 | 52 | 52
|  |  |  | 2-Hour Rating (A) | 634 | 634 | 634 | 634 | 634
Auto Trans Avail (A)
Remote Trans Avail (A)
|  |  |  | Manual Trans Avail (A) | 192 | 192 | 192 | 192 | 192
|  |  |  | POPS Available | Yes | Yes | Yes | Yes | Yes
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
409-1 | Loganlea BSP | Woodridge |  | NCC Rating (A) | 780 | 780 | 780 | 780 | 780
| (LGL) | (WRG) |  | 10 PoE Load (A) | 300 | 295 | 292 | 288 | 284
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
LOGANLEA Bulk Supply Point:
418-1 | Loganlea BSP | Tanah Merah |  | NCC Rating (A) | 631 | 631 | 631 | 631 | 631
| (LGL) | (TMH) |  | 10 PoE Load (A) | 308 | 305 | 302 | 301 | 297
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
452-1 | Loganlea BSP | Kingston |  | NCC Rating (A) | 510 | 510 | 510 | 510 | 510
| (LGL) | (KSN) |  | 10 PoE Load (A) | 292 | 291 | 291 | 291 | 290
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 408-1 | ECC Rating (A) | 510 | 510 | 510 | 510 | 510
|  |  |  | 50 PoE Load (A) | 586 | 584 | 583 | 584 | 583
|  |  |  | Raw LAR (A) | 76 | 74 | 73 | 74 | 73
|  |  |  | 2-Hour Rating (A) | 663 | 663 | 663 | 663 | 663
Auto Trans Avail (A)
Remote Trans Avail (A)
|  |  |  | Manual Trans Avail (A) | 194 | 194 | 194 | 194 | 194
|  |  |  | POPS Available | Yes | Yes | Yes | Yes | Yes
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
LYTTON Bulk Supply Point:
3302-1 | Lytton BSP | Fisherman Is B |  | NCC Rating (A) | 650 | 650 | 650 | 650 | 650
| (LBS) | (FBS) |  | 10 PoE Load (A) | 200 | 225 | 224 | 250 | 297
|  |  |  | Power Factor (System Normal) | 0.9 | 0.9 | 0.9 | 0.89 | 0.89
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3303-1 | Lytton BSP | Fisherman Is B |  | NCC Rating (A) | 600 | 600 | 600 | 600 | 600
| (LBS) | (FBS) |  | 10 PoE Load (A) | 200 | 225 | 224 | 249 | 296
|  |  |  | Power Factor (System Normal) | 0.9 | 0.9 | 0.9 | 0.89 | 0.89
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
LYTTON Bulk Supply Point:
490-1 | Lytton BSP | Gibson Island |  | NCC Rating (A) | 628 | 628 | 628 | 628 | 628
| (LBS) | (GIS) |  | 10 PoE Load (A) | 167 | 167 | 167 | 168 | 166
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | HighSec | HighSec | HighSec | HighSec | HighSec
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
491-1 | Lytton BSP | Lytton A |  | NCC Rating (A) | 450 | 450 | 450 | 450 | 450
| (LBS) | (LYT) |  | 10 PoE Load (A) | 230 | 229 | 227 | 225 | 222
|  |  |  | Power Factor (System Normal) | 1 | 1 | 1 | 1 | 1
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 493-1 | ECC Rating (A) | 450 | 450
|  |  |  | 50 PoE Load (A) | 455 | 453
|  |  |  | Hours PA > 95% Peak Load | 48 | 48
|  |  |  | Raw LAR (A) | 5 | 3
|  |  |  | 2-Hour Rating (A) | 606 | 606
Auto Trans Avail (A)
Remote Trans Avail (A)
|  |  |  | Manual Trans Avail (A) | 46 | 46
|  |  |  | POPS Available | No | No
|  |  |  | Mobile Gen Reqd (A) | 0 | 0
|  |  |  | LARc (A) | 5 | 3
|  |  |  | LARc (MW) | 0.3 | 0.2
|  |  |  | Customer Category | HighSec | HighSec | HighSec | HighSec | HighSec
|  |  |  | Meets Sec Std | No | No | Yes | Yes | Yes
492-1 | Lytton BSP | Gibson Island |  | NCC Rating (A) | 463 | 463 | 463 | 463 | 463
| (LBS) | (GIS) |  | 10 PoE Load (A) | 161 | 161 | 161 | 161 | 159
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | HighSec | HighSec | HighSec | HighSec | HighSec
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
LYTTON Bulk Supply Point:
493-1 | Lytton BSP | Lytton A |  | NCC Rating (A) | 536 | 536 | 536 | 536 | 536
| (LBS) | (LYT) |  | 10 PoE Load (A) | 231 | 230 | 228 | 226 | 223
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | HighSec | HighSec | HighSec | HighSec | HighSec
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
494-1 | Fisherman Is B | Fisherman Is A |  | NCC Rating (A) | 488 | 488 | 488 | 488 | 488
| (FBS) | (FIS) |  | 10 PoE Load (A) | 83 | 107 | 106 | 131 | 179
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
495-1 | Fisherman Is B | Fisherman Is A |  | NCC Rating (A) | 600 | 600 | 600 | 600 | 600
| (FBS) | (FIS) |  | 10 PoE Load (A) | 84 | 109 | 108 | 133 | 182
|  |  |  | Power Factor (System Normal) | 0.87 | 0.87 | 0.87 | 0.87 | 0.86
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
LYTTON Bulk Supply Point:
560-1 | Lytton BSP |  |  | NCC Rating (A) | 527 | 527 | 527 | 527 | 527
| (LBS) | (560 Tee1) |  | 10 PoE Load (A) | 167 | 179 | 161 | 161 | 160
|  |  |  | Power Factor (System Normal) | 0.95 | 0.95 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
560-14 |  |  |  | NCC Rating (A) | 351 | 367 | 367 | 367 | 367
| (560 Tee1) | (560 Tee2) |  | 10 PoE Load (A) | 66 | 74 | 67 | 67 | 66
|  |  |  | Power Factor (System Normal) | 0.97 | 0.95 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
560-15 |  |  |  | NCC Rating (A) | 351 | 351 | 351 | 351 | 351
| (560 Tee1) | (560 Tee2) |  | 10 PoE Load (A) | 101 | 105 | 95 | 95 | 94
|  |  |  | Power Factor (System Normal) | 0.92 | 0.93 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
560-16 | Lota |  |  | NCC Rating (A) | 983 | 983 | 983 | 983 | 983
| (LTA) | (560 Tee1) |  | 10 PoE Load (A) | 170 | 182 | 163 | 163 | 162
|  |  |  | Power Factor (System Normal) | 0.94 | 0.94 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
560-2 |  | Tingalpa |  | NCC Rating (A) | 600 | 600 | 600 | 600 | 600
| (560 Tee1) | (TGP) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
LYTTON Bulk Supply Point:
560-3 |  |  |  | NCC Rating (A) | 600 | 600 | 600 | 600 | 600
| (560 Tee1) | (560 Tee2) |  | 10 PoE Load (A) | 167 | 179 | 161 | 161 | 160
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
560-5 | Lota |  |  | NCC Rating (A) | 704 | 704 | 704 | 704 | 704
| (LTA) | (560 Tee2) |  | 10 PoE Load (A) | 101 | 105 | 95 | 95 | 94
|  |  |  | Power Factor (System Normal) | 0.95 | 0.96 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
569-1 | Lytton BSP | Lota |  | NCC Rating (A) | 490 | 490 | 582 | 582 | 582
| (LBS) | (LTA) |  | 10 PoE Load (A) | 332 | 318 | 332 | 332 | 329
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.95 | 0.95 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
599-1 | Hemmant | Lindum |  | NCC Rating (A) | 443 | 443 | 443 | 443 | 443
| (HMT) | (LDM) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
681-1 | Lindum | Wynnum |  | NCC Rating (A) | 661 | 661 | 661 | 661 | 661
| (LDM) | (WNM) |  | 10 PoE Load (A) | 196 | 197 | 197 | 198 | 198
|  |  |  | Power Factor (System Normal) | 1 | 1 | 1 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
LYTTON Bulk Supply Point:
682-1 | Lindum | Wynnum |  | NCC Rating (A) | 661 | 661 | 661 | 661 | 661
| (LDM) | (WNM) |  | 10 PoE Load (A) | 188 | 188 | 189 | 190 | 190
|  |  |  | Power Factor (System Normal) | 1 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
687-1 | Lytton BSP |  |  | NCC Rating (A) | 758 | 758 | 758 | 758 | 758
| (LBS) | (687 Tee1) |  | 10 PoE Load (A) | 140 | 140 | 141 | 142 | 142
|  |  |  | Power Factor (System Normal) | 1 | 1 | 1 | 1 | 1
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
687-2 |  | Lytton A |  | NCC Rating (A) | 495 | 495 | 495 | 495 | 495
| (687 Tee1) | (LYT) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
687-3 |  | Lindum |  | NCC Rating (A) | 636 | 636 | 636 | 636 | 636
| (687 Tee1) | (LDM) |  | 10 PoE Load (A) | 140 | 140 | 141 | 141 | 141
|  |  |  | Power Factor (System Normal) | 1 | 1 | 1 | 1 | 1
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
688-1 | Lytton BSP | Lindum |  | NCC Rating (A) | 636 | 636 | 636 | 636 | 636
| (LBS) | (LDM) |  | 10 PoE Load (A) | 244 | 244 | 245 | 246 | 246
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
MEEANDAH Bulk Supply Point:
3374-1 | Whinstanes | Hamilton Lands |  | NCC Rating (A) | 476 | 476 | 700 | 700 | 700
| (WSS) | (HTL) |  | 10 PoE Load (A) | 81 | 111 | 82 | 80 | 77
|  |  |  | Power Factor (System Normal) | 0.78 | 1 | 1 | 1 | 1
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
506-1 | Meeandah BSP | Hamilton Lands |  | NCC Rating (A) | 720 | 720 | 720 | 720 | 720
| (MDH) | (HTL) |  | 10 PoE Load (A) | 135 | 210 | 204 | 210 | 215
|  |  |  | Power Factor (System Normal) | 0.9 | 0.99 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
513-1 | Meeandah BSP | Hamilton Lands |  | NCC Rating (A) | 720 | 720 | 720 | 720 | 720
| (MDH) | (HTL) |  | 10 PoE Load (A) | 134 | 208 | 202 | 208 | 213
|  |  |  | Power Factor (System Normal) | 0.9 | 0.99 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
553-1 | Hamilton Lands | Hendra |  | NCC Rating (A) | 476 | 476 | 476 | 476 | 476
| (HTL) | (HDA) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
556-1 | Meeandah BSP | Whinstanes |  | NCC Rating (A) | 476 | 700 | 700 | 700 | 700
| (MDH) | (WSS) |  | 10 PoE Load (A) | 216 | 139 | 166 | 168 | 169
|  |  |  | Power Factor (System Normal) | 1 | 0.98 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
MEEANDAH Bulk Supply Point:
609-1 | Meeandah BSP | Myrtletown BSP |  | NCC Rating (A) | 800 | 800 | 800 | 800 | 800
| (MDH) | (MTN) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
610-1 | Meeandah BSP | Myrtletown BSP |  | NCC Rating (A) | 748 | 748 | 748 | 748 | 748
| (MDH) | (MTN) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
MOLENDINAR Bulk Supply Point:
3670-1 | Molendinar BSP | Parkwood |  | NCC Rating (A) | 710 | 710 | 710 | 710 | 710
| (MDR) | (PKW) |  | 10 PoE Load (A) | 377 | 391 | 393 | 409 | 408
|  |  |  | Power Factor (System Normal) | 0.96 | 0.95 | 0.95 | 0.95 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3671-1 | Molendinar BSP | Parkwood |  | NCC Rating (A) | 708 | 708 | 708 | 708 | 708
| (MDR) | (PKW) |  | 10 PoE Load (A) | 300 | 311 | 312 | 325 | 325
|  |  |  | Power Factor (System Normal) | 0.97 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
389-1 | Parkwood |  |  | NCC Rating (A) | 780 | 780 | 780 | 780 | 780
| (PKW) | (389 Tee1) |  | 10 PoE Load (A) | 390 | 375 | 376 | 372 | 371
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
MOLENDINAR Bulk Supply Point:
389-2 |  | Labrador |  | NCC Rating (A) | 780 | 780 | 780 | 780 | 780
| (F389 Tee1) | (LDR) |  | 10 PoE Load (A) | 309 | 307 | 310 | 312 | 313
|  |  |  | Power Factor (System Normal) | 0.91 | 0.9 | 0.9 | 0.89 | 0.89
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
389-3 |  | Hollywell |  | NCC Rating (A) | 631 | 631 | 631 | 631 | 631
| (F389 Tee1) | (HWL) |  | 10 PoE Load (A) | 103 | 93 | 92 | 88 | 87
|  |  |  | Power Factor (System Normal) | 0.95 | 0.92 | 0.92 | 0.9 | 0.89
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
390-1 | Molendinar BSP |  |  | NCC Rating (A) | 637 | 637 | 637 | 637 | 637
| (MDR) | (F390 Tee1) |  | 10 PoE Load (A) | 138 | 141 | 145 | 145 | 144
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
390-2 |  | Bundall |  | NCC Rating (A) | 653 | 653 | 653 | 653 | 653
| (F390 Tee1) | (BDL) |  | 10 PoE Load (A) | 138 | 142 | 146 | 146 | 145
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
390-3 |  | Miami |  | NCC Rating (A) | 529 | 529 | 529 | 529 | 529
| (F390 Tee1) | (MAI) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
MOLENDINAR Bulk Supply Point:
391-1 | Molendinar BSP | Bundall |  | NCC Rating (A) | 623 | 623 | 623 | 623 | 623
| (MDR) | (BDL) |  | 10 PoE Load (A) | 172 | 176 | 181 | 181 | 179
|  |  |  | Power Factor (System Normal) | 0.98 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
392-1 | Molendinar BSP | Gaven |  | NCC Rating (A) | 708 | 708 | 708 | 708 | 708
| (MDR) | (GVN) |  | 10 PoE Load (A) | 249 | 244 | 243 | 243 | 240
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
421-1 | Molendinar BSP | Arundel |  | NCC Rating (A) | 673 | 673 | 673 | 673 | 673
| (MDR) | (ARL) |  | 10 PoE Load (A) | 512 | 508 | 507 | 511 | 508
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 486-1 | ECC Rating (A) | 721 | 721 | 721 | 721 | 721
|  |  |  | 50 PoE Load (A) | 815 | 817 | 825 | 831 | 827
|  |  |  | Raw LAR (A) | 94 | 96 | 104 | 110 | 106
|  |  |  | 2-Hour Rating (A) | 800 | 800 | 800 | 800 | 800
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) | 154 | 154 | 154 | 161 | 161
|  |  |  | Manual Trans Avail (A) | 86 | 94 | 91 | 91 | 89
|  |  |  | POPS Available | Yes | Yes | Yes | Yes | Yes
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
MOLENDINAR Bulk Supply Point:
458-1 | Molendinar BSP | Labrador |  | NCC Rating (A) | 780 | 780 | 780 | 780 | 780
| (MDR) | (LDR) |  | 10 PoE Load (A) | 220 | 221 | 222 | 225 | 225
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
473-1 | Molendinar BSP | Gaven |  | NCC Rating (A) | 717 | 717 | 717 | 717 | 717
| (MDR) | (GVN) |  | 10 PoE Load (A) | 249 | 245 | 244 | 243 | 241
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
MOLENDINAR Bulk Supply Point:
474A-1 | Arundel | Hollywell |  | NCC Rating (A) | 631 | 631 | 631 | 631 | 631
| (ARL) | (HWL) |  | 10 PoE Load (A) | 634 | 635 | 638 | 649 | 649
|  |  |  | Hours PA > 95% Peak Load | 6 | 6 | 6 | 6 | 6
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 3 | 4 | 7 | 18 | 18
|  |  |  | LARn (MW) | 0.2 | 0.2 | 0.4 | 1 | 1
|  |  | 3670-1 | ECC Rating (A) | 631 | 631 | 631 | 631 | 631
|  |  |  | 50 PoE Load (A) | 655 | 668 | 662 | 676 | 676
|  |  |  | Raw LAR (A) | 24 | 37 | 31 | 45 | 45
|  |  |  | 2-Hour Rating (A) | 800 | 800 | 800 | 800 | 800
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) | 149 | 141 | 137 | 138 | 139
Manual Trans Avail (A)
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 458-1 | ECC Rating (A) | 631 | 631 | 631 | 631 | 631
|  |  |  | 50 PoE Load (A) | 645 | 653 | 647 | 658 | 658
|  |  |  | Raw LAR (A) | 14 | 22 | 16 | 27 | 27
|  |  |  | 2-Hour Rating (A) | 800 | 800 | 800 | 800 | 800
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) | 36 | 39 | 37 | 44 | 46
|  |  |  | Manual Trans Avail (A) | 51 | 58 | 58 | 59 | 58
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 3671-1 | ECC Rating (A) |  | 631 |  | 631 | 631
|  |  |  | 50 PoE Load (A) |  | 633 |  | 640 | 639
|  |  |  | Raw LAR (A) |  | 2 |  | 9 | 8
|  |  |  | 2-Hour Rating (A) |  | 800 |  | 800 | 800
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) |  | 136 |  | 138 | 134
Manual Trans Avail (A)
|  |  |  | POPS Available |  | No |  | No | No
|  |  |  | Mobile Gen Reqd (A) |  | 0 |  | 0 | 0
|  |  |  | LARc (A) |  | 0 |  | 0 | 0
|  |  |  | LARc (MW) |  | 0 |  | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | No | No | No | No | No
MOLENDINAR Bulk Supply Point:
474B-1 | Hope Island | Hollywell |  | NCC Rating (A) | 786 | 786 | 786 | 786 | 786
| (HIS) | (HWL) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
486-1 | Molendinar BSP | Arundel |  | NCC Rating (A) | 673 | 673 | 673 | 673 | 673
| (MDR) | (ARL) |  | 10 PoE Load (A) | 512 | 508 | 508 | 511 | 509
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 421-1 | ECC Rating (A) | 721 | 721 | 721 | 721 | 721
|  |  |  | 50 PoE Load (A) | 815 | 817 | 826 | 832 | 827
|  |  |  | Raw LAR (A) | 94 | 96 | 105 | 111 | 106
|  |  |  | 2-Hour Rating (A) | 800 | 800 | 800 | 800 | 800
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) | 154 | 154 | 160 | 167 | 161
|  |  |  | Manual Trans Avail (A) | 86 | 94 | 91 | 91 | 89
|  |  |  | POPS Available | Yes | Yes | Yes | Yes | Yes
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
MUDGEERABA Bulk Supply Point:
3700-1 | Mudgeeraba BSP |  |  | NCC Rating (A) | 800 | 800 | 800 | 800 | 800
| (MGB) | (3700 Tee1) |  | 10 PoE Load (A) | 198 | 199 | 200 | 202 | 203
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3700-2 |  |  |  | NCC Rating (A) | 723 | 723 | 723 | 723 | 723
| (3700 Tee1) | (3701 Tee1) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3700-3 |  |  |  | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
| (3700 Tee1) | (3700 Tee2) |  | 10 PoE Load (A) | 199 | 199 | 200 | 202 | 203
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3700-4 |  |  |  | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
| (3700 Tee2) | (3702 Tee1) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3700-5 |  | Mudgeeraba West Pkg |  | NCC Rating (A) | 800 | 800 | 800 | 800 | 800
| (3700 Tee2) | (MGP) |  | 10 PoE Load (A) | 199 | 199 | 200 | 202 | 203
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
MUDGEERABA Bulk Supply Point:
3701-1 | Mudgeeraba BSP | Mudgeeraba West Pkg |  | NCC Rating (A) | 529 | 529 | 529 | 529 | 529
| (MGB) | (MGP) |  | 10 PoE Load (A) | 216 | 217 | 218 | 220 | 221
|  |  |  | Power Factor (System Normal) | 0.93 | 0.93 | 0.93 | 0.93 | 0.93
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
NAMBOUR Bulk Supply Point:
307-1 | Nambour |  |  | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
| (NBR) | (307 Tee1) |  | 10 PoE Load (A) | 84 | 85 | 85 | 86 | 86
|  |  |  | Power Factor (System Normal) | 0.94 | 0.94 | 0.94 | 0.94 | 0.94
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
307-2 |  | Yandina |  | NCC Rating (A) | 755 | 755 | 755 | 755 | 755
| (307 Tee1) | (YDA) |  | 10 PoE Load (A) | 85 | 86 | 86 | 87 | 87
|  |  |  | Power Factor (System Normal) | 0.94 | 0.94 | 0.94 | 0.94 | 0.94
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
344-1 | Nambour | Maleny |  | NCC Rating (A) | 155 | 155 | 155 | 155 | 155
| (NBR) | (MLY) |  | 10 PoE Load (A) | 131 | 132 | 132 | 132 | 131
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 344-1 | ECC Rating (A)
|  |  |  | 50 PoE Load (A) | 117 | 117 | 117 | 117 | 117
|  |  |  | Raw LAR (A) | 117 | 117 | 117 | 117 | 117
2-Hour Rating (A)
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) | 117 | 117 | 117 | 117 | 117
Manual Trans Avail (A)
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
NAMBOUR Bulk Supply Point:
345-1 | Nambour | Kenilworth |  | NCC Rating (A) | 208 | 208 | 208 | 208 | 208
| (NBR) | (KWH) |  | 10 PoE Load (A) | 84 | 84 | 82 | 81 | 80
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 345-1 | ECC Rating (A)
|  |  |  | 50 PoE Load (A) | 77 | 76 | 75 | 74 | 73
|  |  |  | Raw LAR (A) | 77 | 76 | 75 | 74 | 73
2-Hour Rating (A)
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) | 77 | 76 | 75 | 74 | 73
Manual Trans Avail (A)
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
347-1 | Nambour |  |  | NCC Rating (A) | 412 | 412 | 412 | 412 | 412
| (NBR) | (347 Tee1) |  | 10 PoE Load (A) | 171 | 171 | 172 | 173 | 174
|  |  |  | Power Factor (System Normal) | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
NAMBOUR Bulk Supply Point:
347-2 |  | Palmwoods Central |  | NCC Rating (A) | 357 | 357 | 357 | 357 | 357
| (347 Tee1) | (PWC) |  | 10 PoE Load (A) | 171 | 172 | 173 | 174 | 174
|  |  |  | Power Factor (System Normal) | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 348-1 | ECC Rating (A) | 357 | 357 | 357 | 357 | 357
|  |  |  | 50 PoE Load (A) | 365 | 366 | 368 | 371 | 371
|  |  |  | Raw LAR (A) | 8 | 9 | 11 | 14 | 14
|  |  |  | 2-Hour Rating (A) | 427 | 427 | 427 | 427 | 427
Auto Trans Avail (A)
Remote Trans Avail (A)
|  |  |  | Manual Trans Avail (A) | 91 | 91 | 91 | 91 | 91
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
347-3 |  | Landsborough |  | NCC Rating (A) | 403 | 403 | 403 | 403 | 403
| (347 Tee1) | (LBH) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
348-1 | Nambour | Palmwoods Central |  | NCC Rating (A) | 403 | 403 | 403 | 403 | 403
| (NBR) | (PWC) |  | 10 PoE Load (A) | 219 | 220 | 221 | 223 | 223
|  |  |  | Power Factor (System Normal) | 0.94 | 0.94 | 0.94 | 0.94 | 0.94
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
NAMBOUR Bulk Supply Point:
489-1 | Nambour | Yandina |  | NCC Rating (A) | 293 | 293 | 293 | 293 | 293
| (NBR) | (YDA) |  | 10 PoE Load (A) | 77 | 77 | 78 | 79 | 79
|  |  |  | Power Factor (System Normal) | 1 | 1 | 1 | 1 | 1
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
NUDGEE Bulk Supply Point:
3280-1 | Hendra | Clayfield |  | NCC Rating (A) |  |  | 725 | 725 | 725
| (HDA) | (CFD) |  | 10 PoE Load (A) |  |  | 173 | 171 | 169
|  |  |  | Power Factor (System Normal) |  |  | 0.95 | 0.95 | 0.95
|  |  |  | LARn (A) |  |  | 0 | 0 | 0
|  |  |  | LARn (MW) |  |  | 0 | 0 | 0
|  |  |  | Customer Category |  |  | Urban | Urban | Urban
|  |  |  | Meets Sec Std |  |  | Yes | Yes | Yes
535-1 | Hendra | Nundah |  | NCC Rating (A) | 285 | 285
| (HDA) | (NDH) |  | 10 PoE Load (A) | 87 | 85
|  |  |  | Power Factor (System Normal) | 1 | 1
|  |  |  | LARn (A) | 0 | 0
|  |  |  | LARn (MW) | 0 | 0
|  |  |  | Customer Category | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes
540-1 | Hendra | Nundah |  | NCC Rating (A) | 285 | 285 | 704 | 704 | 704
| (HDA) | (NDH) |  | 10 PoE Load (A) | 87 | 85 | 237 | 235 | 232
|  |  |  | Power Factor (System Normal) | 1 | 1 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
NUDGEE Bulk Supply Point:
593-1 | Nudgee BSP | Nundah |  | NCC Rating (A) | 696 | 696 | 696 | 696 | 696
| (NGE) | (NDH) |  | 10 PoE Load (A) | 567 | 564 | 637 | 634 | 627
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 622-1 | ECC Rating (A) |  |  | 696 | 696 | 696
|  |  |  | 50 PoE Load (A) |  |  | 758 | 756 | 748
|  |  |  | Raw LAR (A) |  |  | 62 | 60 | 52
|  |  |  | 2-Hour Rating (A) |  |  | 800 | 800 | 800
Auto Trans Avail (A)
Remote Trans Avail (A)
|  |  |  | Manual Trans Avail (A) |  |  | 112 | 112 | 112
|  |  |  | POPS Available |  |  | No | No | No
|  |  |  | Mobile Gen Reqd (A) |  |  | 0 | 0 | 0
|  |  |  | LARc (A) |  |  | 0 | 0 | 0
|  |  |  | LARc (MW) |  |  | 0 | 0 | 0
|  |  | 623-1 | ECC Rating (A) |  |  | 696 | 696 | 696
|  |  |  | 50 PoE Load (A) |  |  | 758 | 756 | 748
|  |  |  | Raw LAR (A) |  |  | 62 | 60 | 52
|  |  |  | 2-Hour Rating (A) |  |  | 800 | 800 | 800
Auto Trans Avail (A)
Remote Trans Avail (A)
|  |  |  | Manual Trans Avail (A) |  |  | 112 | 112 | 112
|  |  |  | POPS Available |  |  | No | No | No
|  |  |  | Mobile Gen Reqd (A) |  |  | 0 | 0 | 0
|  |  |  | LARc (A) |  |  | 0 | 0 | 0
|  |  |  | LARc (MW) |  |  | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
604-1 | Nudgee BSP | Geebung |  | NCC Rating (A) | 432 | 432 | 432 | 432 | 432
| (NGE) | (GBG) |  | 10 PoE Load (A) | 219 | 215 | 213 | 209 | 205
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
NUDGEE Bulk Supply Point:
605-1 | Nudgee BSP | Geebung |  | NCC Rating (A) | 432 | 432 | 432 | 432 | 432
| (NGE) | (GBG) |  | 10 PoE Load (A) | 219 | 216 | 213 | 209 | 205
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
622-1 | Nudgee BSP | Hendra |  | NCC Rating (A) | 738 | 738 | 738 | 738 | 738
| (NGE) | (HDA) |  | 10 PoE Load (A) | 304 | 301 | 434 | 431 | 426
|  |  |  | Power Factor (System Normal) | 0.92 | 0.92 | 0.95 | 0.95 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
623-1 | Nudgee BSP | Hendra |  | NCC Rating (A) | 738 | 738 | 738 | 738 | 738
| (NGE) | (HDA) |  | 10 PoE Load (A) | 304 | 301 | 434 | 431 | 426
|  |  |  | Power Factor (System Normal) | 0.92 | 0.92 | 0.95 | 0.95 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
636-1 | Hendra | Clayfield |  | NCC Rating (A) | 302 | 302 | 725 | 725 | 725
| (HDA) | (CFD) |  | 10 PoE Load (A) |  |  | 173 | 171 | 169
|  |  |  | Power Factor (System Normal) |  |  | 0.95 | 0.95 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
643-1 | Hendra | Hamilton |  | NCC Rating (A) | 711 | 711 | 711 | 711 | 711
| (HDA) | (HTN) |  | 10 PoE Load (A) | 203 | 200 | 202 | 202 | 202
|  |  |  | Power Factor (System Normal) | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
NUDGEE Bulk Supply Point:
674-1 | Hendra | Hamilton |  | NCC Rating (A) | 711 | 711 | 711 | 711 | 711
| (HDA) | (HTN) |  | 10 PoE Load (A) | 202 | 200 | 201 | 202 | 201
|  |  |  | Power Factor (System Normal) | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
683-1 | Nudgee BSP | Geebung |  | NCC Rating (A) | 478 | 478 | 478 | 478 | 478
| (NGE) | (GBG) |  | 10 PoE Load (A) | 214 | 211 | 209 | 205 | 201
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
684-1 | Nudgee BSP | Geebung |  | NCC Rating (A) | 525 | 525 | 525 | 525 | 525
| (NGE) | (GBG) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
POSTMANS RIDGE Bulk Supply Point:
376-1 | Postmans Ridge BSP | Helidon |  | NCC Rating (A) | 290 | 290 | 290 | 290 | 290
| (PRG) | (HDN) |  | 10 PoE Load (A) | 63 | 63 | 63 | 63 | 63
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 376-1 | ECC Rating (A)
|  |  |  | 50 PoE Load (A) | 55 | 54 | 54 | 54 | 54
|  |  |  | Raw LAR (A) | 55 | 54 | 54 | 54 | 54
2-Hour Rating (A)
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) | 55 | 54 | 54 | 54 | 54
Manual Trans Avail (A)
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
379-1 | Postmans Ridge BSP | Carpendale |  | NCC Rating (A) | 200 | 200 | 200 | 200 | 200
| (PRG) | (CPD) |  | 10 PoE Load (A) | 36 | 36 | 36 | 36 | 36
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 379-1 | ECC Rating (A)
|  |  |  | 50 PoE Load (A) | 32 | 32 | 32 | 32 | 32
|  |  |  | Raw LAR (A) | 32 | 32 | 32 | 32 | 32
2-Hour Rating (A)
Auto Trans Avail (A)
Remote Trans Avail (A)
|  |  |  | Manual Trans Avail (A) | 23 | 23 | 23 | 23 | 23
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 9 | 9 | 9 | 9 | 9
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
POSTMANS RIDGE Bulk Supply Point:
379-2 | Carpendale | Tenthill |  | NCC Rating (A) | 155 | 155 | 155 | 155 | 155
| (CPD) | (THL) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
RACEVIEW Bulk Supply Point:
354-1 | Raceview BSP | Roderick St |  | NCC Rating (A) | 497 | 497 | 497 | 497 | 497
| (RVW) | (RST) |  | 10 PoE Load (A) | 347 | 346 | 349 | 351 | 353
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
355-1 | Roderick St | Booval |  | NCC Rating (A) | 495 | 495 | 495 | 495 | 495
| (RST) | (BVL) |  | 10 PoE Load (A) | 184 | 183 | 185 | 187 | 188
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
361-1 | Raceview BSP | Booval |  | NCC Rating (A) | 631 | 631 | 631 | 631 | 631
| (RVW) | (BVL) |  | 10 PoE Load (A) | 389 | 388 | 390 | 392 | 392
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
RACEVIEW Bulk Supply Point:
362-1 | Raceview BSP |  |  | NCC Rating (A) | 357 | 357 | 357 | 357 | 357
| (RVW) | (362 Tee1) |  | 10 PoE Load (A) | 156 | 155 | 155 | 155 | 154
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 3960-1 | ECC Rating (A) |  |  |  | 357 | 357
|  |  |  | 50 PoE Load (A) |  |  |  | 360 | 361
|  |  |  | Raw LAR (A) |  |  |  | 3 | 4
|  |  |  | 2-Hour Rating (A) |  |  |  | 427 | 427
Auto Trans Avail (A)
Remote Trans Avail (A)
|  |  |  | Manual Trans Avail (A) |  |  |  | 80 | 79
|  |  |  | POPS Available |  |  |  | No | No
|  |  |  | Mobile Gen Reqd (A) |  |  |  | 0 | 0
|  |  |  | LARc (A) |  |  |  | 0 | 0
|  |  |  | LARc (MW) |  |  |  | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
362-2 |  | Flinders |  | NCC Rating (A) | 708 | 708 | 708 | 708 | 708
| (362 Tee1) | (FDS) |  | 10 PoE Load (A) | 46 | 46 | 44 | 43 | 42
|  |  |  | Power Factor (System Normal) | 0.6 | 0.6 | 0.59 | 0.58 | 0.58
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
362-3 |  | Kalbar |  | NCC Rating (A) | 708 | 708 | 708 | 708 | 708
| (362 Tee1) | (KBR) |  | 10 PoE Load (A) | 193 | 192 | 190 | 189 | 187
|  |  |  | Power Factor (System Normal) | 0.94 | 0.94 | 0.94 | 0.94 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
RACEVIEW Bulk Supply Point:
363-1 | Raceview BSP |  |  | NCC Rating (A) | 351 | 351 | 351 | 351 | 351
| (RVW) | (363 Tee1) |  | 10 PoE Load (A) | 155 | 154 | 153 | 153 | 153
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
363-2 |  | Flinders |  | NCC Rating (A) | 403 | 403 | 403 | 403 | 403
| (363 Tee1) | (FDS) |  | 10 PoE Load (A) | 11 | 11 | 11 | 11 | 11
|  |  |  | Power Factor (System Normal) | 0.71 | 0.69 | 0.64 | 0.58 | 0.38
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
363-3 |  | Kalbar |  | NCC Rating (A) | 374 | 374 | 374 | 374 | 374
| (363 Tee1) | (KBR) |  | 10 PoE Load (A) | 161 | 160 | 158 | 157 | 156
|  |  |  | Power Factor (System Normal) | 1 | 1 | 1 | 1 | 1
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
RACEVIEW Bulk Supply Point:
3960-1 | Ipswich South | Yamanto |  | NCC Rating (A) | 711 | 711 | 711 | 711 | 711
| (IPS) | (YMT) |  | 10 PoE Load (A) | 408 | 408 | 412 | 418 | 421
|  |  |  | Power Factor (System Normal) | 0.93 | 0.93 | 0.93 | 0.93 | 0.93
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3972-1 | Yamanto | Flinders |  | NCC Rating (A) | 800 | 800 | 800 | 800 | 800
| (YMT) | (FDS) |  | 10 PoE Load (A) | 157 | 156 | 155 | 154 | 152
|  |  |  | Power Factor (System Normal) | 0.88 | 0.88 | 0.88 | 0.88 | 0.88
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3980-1 | Kalbar | Boonah |  | NCC Rating (A) | 713 | 713 | 713 | 713 | 713
| (KBR) | (BNH) |  | 10 PoE Load (A) | 86 | 85 | 84 | 83 | 82
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
401-1 | Kalbar | Boonah |  | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
| (KBR) | (BNH) |  | 10 PoE Load (A) | 83 | 82 | 81 | 81 | 79
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
411-1 | Raceview BSP | Booval |  | NCC Rating (A) | 558 | 558 | 558 | 558 | 558
| (RVW) | (BVL) |  | 10 PoE Load (A) | 329 | 329 | 330 | 332 | 332
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
RACEVIEW Bulk Supply Point:
509A-1 | Raceview BSP | Ipswich South |  | NCC Rating (A) | 721 | 721 | 721 | 721 | 721
| (RVW) | (IPS) |  | 10 PoE Load (A) | 414 | 416 | 425 | 434 | 441
|  |  |  | Power Factor (System Normal) | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
509B-1 | Raceview BSP | Cooneana |  | NCC Rating (A) | 455 | 455 | 455 | 455 | 455
| (RVW) | (CNA) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
RACEVIEW Bulk Supply Point:
510A-1 | Raceview BSP | Ipswich South |  | NCC Rating (A) | 721 | 721 | 721 | 721 | 721
| (RVW) | (IPS) |  | 10 PoE Load (A) | 410 | 412 | 420 | 430 | 436
|  |  |  | Power Factor (System Normal) | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
510B-1 | Raceview BSP | Cooneana |  | NCC Rating (A) | 426 | 426 | 426 | 426 | 426
| (RVW) | (CNA) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
RICHLANDS Bulk Supply Point:
3818-1 | Richlands BSP | Wacol |  | NCC Rating (A) | 750 | 750 | 750 | 750 | 750
| (RLD) | (WCL) |  | 10 PoE Load (A) | 136 | 134 | 132 | 130 | 128
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
454-1 | Richlands BSP | Wacol South |  | NCC Rating (A) | 430 | 430 | 430 | 430 | 430
| (RLD) | (WSO) |  | 10 PoE Load (A) | 199 | 195 | 193 | 190 | 186
|  |  |  | Power Factor (System Normal) | 0.95 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
455-1 | Richlands BSP | Wacol South |  | NCC Rating (A) | 430 | 430 | 430 | 430 | 430
| (RLD) | (WSO) |  | 10 PoE Load (A) | 200 | 196 | 194 | 191 | 188
|  |  |  | Power Factor (System Normal) | 0.95 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
543-1 | Inala |  |  | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
| (INA) | (543 Tee1) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
543-2 |  | Coopers Plains |  | NCC Rating (A) | 348 | 348 | 348 | 348 | 348
| (543 Tee1) | (CPL) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
RICHLANDS Bulk Supply Point:
543-3 |  | Heathwood |  | NCC Rating (A) | 807 | 807 | 807 | 807 | 807
| (543 Tee1) | (HWD) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
616-1 | Richlands BSP | Darra |  | NCC Rating (A) | 407 | 407 | 407 | 407 | 407
| (RLD) | (DRA) |  | 10 PoE Load (A) | 255 | 252 | 251 | 249 | 247
|  |  |  | Power Factor (System Normal) | 0.94 | 0.94 | 0.94 | 0.93 | 0.93
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
617-1 | Richlands BSP | Darra |  | NCC Rating (A) | 407 | 407 | 407 | 407 | 407
| (RLD) | (DRA) |  | 10 PoE Load (A) | 263 | 261 | 259 | 257 | 255
|  |  |  | Power Factor (System Normal) | 0.94 | 0.94 | 0.94 | 0.93 | 0.93
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
618-1 | Richlands BSP | Inala |  | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
| (RLD) | (INA) |  | 10 PoE Load (A) | 382 | 382 | 383 | 383 | 382
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
RICHLANDS Bulk Supply Point:
619-1 | Richlands BSP | Inala |  | NCC Rating (A) | 550 | 550 | 550 | 550 | 550
| (RLD) | (INA) |  | 10 PoE Load (A) | 247 | 247 | 247 | 248 | 247
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 618-1 | ECC Rating (A) | 550 | 550 | 550 | 550 | 550
|  |  |  | 50 PoE Load (A) | 575 | 574 | 576 | 576 | 575
|  |  |  | Raw LAR (A) | 25 | 24 | 26 | 26 | 25
|  |  |  | 2-Hour Rating (A) | 663 | 663 | 663 | 663 | 663
Auto Trans Avail (A)
Remote Trans Avail (A)
|  |  |  | Manual Trans Avail (A) | 134 | 134 | 134 | 134 | 134
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
620-1 | Richlands BSP | Oxley |  | NCC Rating (A) | 324 | 324 | 324 | 324 | 324
| (RLD) | (OXL) |  | 10 PoE Load (A) | 185 | 183 | 181 | 179 | 177
|  |  |  | Power Factor (System Normal) | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
621-1 | Richlands BSP | Oxley |  | NCC Rating (A) | 324 | 324 | 324 | 324 | 324
| (RLD) | (OXL) |  | 10 PoE Load (A) | 176 | 174 | 173 | 171 | 169
|  |  |  | Power Factor (System Normal) | 0.94 | 0.94 | 0.94 | 0.94 | 0.94
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
RICHLANDS Bulk Supply Point:
641-1 | Darra | Jindalee |  | NCC Rating (A) | 703 | 703 | 703 | 703 | 703
| (DRA) | (JDL) |  | 10 PoE Load (A) | 167 | 164 | 163 | 161 | 159
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
642-1 | Darra | Jindalee |  | NCC Rating (A) | 703 | 703 | 703 | 703 | 703
| (DRA) | (JDL) |  | 10 PoE Load (A) | 164 | 161 | 159 | 158 | 155
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
679-1 | Richlands BSP | Wacol |  | NCC Rating (A) | 605 | 605 | 605 | 605 | 605
| (RLD) | (WCL) |  | 10 PoE Load (A) | 138 | 136 | 134 | 132 | 130
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
680-1 | Richlands BSP | Wacol |  | NCC Rating (A) | 750 | 750 | 750 | 750 | 750
| (RLD) | (WCL) |  | 10 PoE Load (A) | 129 | 127 | 125 | 124 | 122
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
700-1 | Richlands BSP | Darra |  | NCC Rating (A) | 517 | 517 | 517 | 517 | 517
| (RLD) | (DRA) |  | 10 PoE Load (A) | 201 | 200 | 198 | 197 | 195
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
RUNCORN Bulk Supply Point:
3440-1 | Runcorn BSP | Sunnybank |  | NCC Rating (A) | 544 | 544 | 544 | 544 | 544
| (RBS) | (SBK) |  | 10 PoE Load (A) | 458 | 454 | 451 | 449 | 445
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
433-1 | Runcorn BSP | Calamvale |  | NCC Rating (A) | 406 | 406 | 406 | 406 | 406
| (RBS) | (CMV) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
434-1 | Runcorn | Calamvale |  | NCC Rating (A) | 406 | 406 | 406 | 406 | 406
| (RCN) | (CMV) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
459A-1 | Upper Mt Gravatt | Sunnybank |  | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
| (UMG) | (SBK) |  | 10 PoE Load (A) | 97 | 96 | 95 | 95 | 94
|  |  |  | Power Factor (System Normal) | 0.91 | 0.91 | 0.91 | 0.91 | 0.91
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
459B-1 | Runcorn BSP | Upper Mt Gravatt |  | NCC Rating (A) | 801 | 801 | 801 | 801 | 801
| (RBS) | (UMG) |  | 10 PoE Load (A) | 95 | 94 | 94 | 93 | 92
|  |  |  | Power Factor (System Normal) | 0.92 | 0.92 | 0.92 | 0.92 | 0.92
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
RUNCORN Bulk Supply Point:
667-1 | Runcorn BSP | Acacia Ridge |  | NCC Rating (A) | 426 | 426 | 426 | 426 | 426
| (RBS) | (ARG) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
668-1 | Runcorn BSP | Acacia Ridge |  | NCC Rating (A) | 426 | 426 | 426 | 426 | 426
| (RBS) | (ARG) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
690-1 | Runcorn BSP | Runcorn |  | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
| (RBS) | (RCN) |  | 10 PoE Load (A) | 297 | 295 | 294 | 294 | 292
|  |  |  | Power Factor (System Normal) | 0.92 | 0.92 | 0.92 | 0.92 | 0.92
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
691-1 | Runcorn BSP | Runcorn |  | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
| (RBS) | (RCN) |  | 10 PoE Load (A) | 235 | 233 | 233 | 232 | 231
|  |  |  | Power Factor (System Normal) | 0.92 | 0.92 | 0.92 | 0.92 | 0.92
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
694-1 | Runcorn BSP | Eight Mile Plains Bus 1 |  | NCC Rating (A) | 531 | 531 | 531 | 531 | 531
| (RBS) | (EMPT2) |  | 10 PoE Load (A) | 266 | 264 | 263 | 262 | 260
|  |  |  | Power Factor (System Normal) | 0.94 | 0.94 | 0.94 | 0.94 | 0.94
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
SANDGATE Bulk Supply Point:
3290-1 | Sandgate BSP | Bald Hills Bus 1 |  | NCC Rating (A) | 800 | 800 | 800 | 800 | 800
| (SGT) | (BHLT1T2) |  | 10 PoE Load (A) | 140 | 139 | 138 | 137 | 135
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
505-1 | Sandgate BSP | Zillmere |  | NCC Rating (A) | 700 | 700 | 700 | 700 | 700
| (SGT) | (ZMR) |  | 10 PoE Load (A) | 288 | 285 | 277 | 274 | 271
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
524-1 | Sandgate BSP | Geebung |  | NCC Rating (A) | 453 | 453 | 453 | 453 | 453
| (SGT) | (GBG) |  | 10 PoE Load (A) | 195 | 193 | 188 | 186 | 183
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
524-2 | Geebung | Zillmere |  | NCC Rating (A) | 410 | 410 | 410 | 410 | 410
| (GBG) | (ZMR) |  | 10 PoE Load (A) | 201 | 199 | 194 | 192 | 189
|  |  |  | Power Factor (System Normal) | 0.95 | 0.95 | 0.95 | 0.96 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
561-1 | Sandgate BSP | Brighton |  | NCC Rating (A) | 251 | 700 | 700 | 700 | 700
| (SGT) | (BRT) |  | 10 PoE Load (A) | 90 | 91 | 91 | 91 | 90
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
SANDGATE Bulk Supply Point:
656-1 | Sandgate BSP | Brighton |  | NCC Rating (A) | 270 | 270 | 270 | 270 | 270
| (SGT) | (BRT) |  | 10 PoE Load (A) | 89 | 88 | 87 | 87 | 87
|  |  |  | Power Factor (System Normal) | 0.98 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
664-1 | Geebung | Zillmere |  | NCC Rating (A) | 410 | 410 | 410 | 410 | 410
| (GBG) | (ZMR) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
671-1 | Sandgate BSP | Zillmere |  | NCC Rating (A) | 495 | 495 | 507 | 507 | 507
| (SGT) | (ZMR) |  | 10 PoE Load (A) | 161 | 159 | 165 | 163 | 161
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
STAFFORD Bulk Supply Point:
502-1 | Kedron | Clayfield |  | NCC Rating (A) | 304 | 304
| (KRN) | (CFD) |  | 10 PoE Load (A) | 175 | 174
|  |  |  | Power Factor (System Normal) | 0.94 | 0.94
|  |  |  | LARn (A) | 0 | 0
|  |  |  | LARn (MW) | 0 | 0
|  |  | 534-1 | ECC Rating (A) | 304 | 304
|  |  |  | 50 PoE Load (A) | 313 | 311
|  |  |  | Raw LAR (A) | 9 | 7
|  |  |  | 2-Hour Rating (A) | 375 | 375
Auto Trans Avail (A)
Remote Trans Avail (A)
Manual Trans Avail (A)
|  |  |  | POPS Available | No | No
|  |  |  | Mobile Gen Reqd (A) | 9 | 7
|  |  |  | LARc (A) | 0 | 0
|  |  |  | LARc (MW) | 0 | 0
|  |  |  | Customer Category | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes
522-1 | Kedron | Chermside |  | NCC Rating (A) | 281 | 281
| (KRN) | (CSE) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0
|  |  |  | LARn (MW) | 0 | 0
|  |  |  | Customer Category | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes
525-1 | Chermside | Zillmere |  | NCC Rating (A) | 311 | 311
| (CSE) | (ZMR) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0
|  |  |  | LARn (MW) | 0 | 0
|  |  |  | Customer Category | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes
STAFFORD Bulk Supply Point:
534-1 | Kedron | Clayfield |  | NCC Rating (A) | 304 | 304
| (KRN) | (CFD) |  | 10 PoE Load (A) | 174 | 173
|  |  |  | Power Factor (System Normal) | 0.94 | 0.95
|  |  |  | LARn (A) | 0 | 0
|  |  |  | LARn (MW) | 0 | 0
|  |  | 502-1 | ECC Rating (A) | 304 | 304
|  |  |  | 50 PoE Load (A) | 313 | 311
|  |  |  | Raw LAR (A) | 9 | 7
|  |  |  | 2-Hour Rating (A) | 375 | 375
Auto Trans Avail (A)
Remote Trans Avail (A)
Manual Trans Avail (A)
|  |  |  | POPS Available | No | No
|  |  |  | Mobile Gen Reqd (A) | 9 | 7
|  |  |  | LARc (A) | 0 | 0
|  |  |  | LARc (MW) | 0 | 0
|  |  |  | Customer Category | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes
548-1 | Stafford BSP | Enoggera |  | NCC Rating (A) | 836 | 836 | 836 | 836 | 836
| (SFD) | (ENG) |  | 10 PoE Load (A) | 545 | 542 | 536 | 535 | 530
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 594-1 | ECC Rating (A) | 963 | 963
|  |  |  | 50 PoE Load (A) | 970 | 965
|  |  |  | Raw LAR (A) | 7 | 2
|  |  |  | 2-Hour Rating (A) | 1200 | 1200
Auto Trans Avail (A)
Remote Trans Avail (A)
|  |  |  | Manual Trans Avail (A) | 224 | 224
|  |  |  | POPS Available | No | No
|  |  |  | Mobile Gen Reqd (A) | 0 | 0
|  |  |  | LARc (A) | 0 | 0
|  |  |  | LARc (MW) | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
STAFFORD Bulk Supply Point:
550-1 | Stafford BSP | Chermside |  | NCC Rating (A) | 668 | 668 | 668 | 668 | 668
| (SFD) | (CSE) |  | 10 PoE Load (A) | 399 | 399 | 394 | 397 | 392
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
551-1 | Stafford BSP | Chermside |  | NCC Rating (A) | 668 | 668 | 668 | 668 | 668
| (SFD) | (CSE) |  | 10 PoE Load (A) | 398 | 399 | 394 | 396 | 391
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
567-1 | Stafford BSP | Kedron |  | NCC Rating (A) | 576 | 576 | 576 | 576 | 576
| (SFD) | (KRN) |  | 10 PoE Load (A) | 432 | 432 | 258 | 258 | 256
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 568-1 | ECC Rating (A) | 643 | 643
|  |  |  | 50 PoE Load (A) | 774 | 775
|  |  |  | Raw LAR (A) | 131 | 132
|  |  |  | 2-Hour Rating (A) | 818 | 818
Auto Trans Avail (A)
Remote Trans Avail (A)
|  |  |  | Manual Trans Avail (A) | 225 | 225
|  |  |  | POPS Available | No | No
|  |  |  | Mobile Gen Reqd (A) | 0 | 0
|  |  |  | LARc (A) | 0 | 0
|  |  |  | LARc (MW) | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
STAFFORD Bulk Supply Point:
568-1 | Stafford BSP | Kedron |  | NCC Rating (A) | 576 | 576 | 576 | 576 | 576
| (SFD) | (KRN) |  | 10 PoE Load (A) | 435 | 435 | 260 | 260 | 258
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 567-1 | ECC Rating (A) | 643 | 643
|  |  |  | 50 PoE Load (A) | 775 | 775
|  |  |  | Raw LAR (A) | 132 | 132
|  |  |  | 2-Hour Rating (A) | 818 | 818
Auto Trans Avail (A)
Remote Trans Avail (A)
|  |  |  | Manual Trans Avail (A) | 225 | 225
|  |  |  | POPS Available | No | No
|  |  |  | Mobile Gen Reqd (A) | 0 | 0
|  |  |  | LARc (A) | 0 | 0
|  |  |  | LARc (MW) | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
594-1 | Stafford BSP | Enoggera |  | NCC Rating (A) | 836 | 836 | 836 | 836 | 836
| (SFD) | (ENG) |  | 10 PoE Load (A) | 541 | 538 | 533 | 531 | 527
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 548-1 | ECC Rating (A) | 963 | 963
|  |  |  | 50 PoE Load (A) | 971 | 965
|  |  |  | Raw LAR (A) | 8 | 2
|  |  |  | 2-Hour Rating (A) | 1200 | 1200
Auto Trans Avail (A)
Remote Trans Avail (A)
|  |  |  | Manual Trans Avail (A) | 224 | 224
|  |  |  | POPS Available | No | No
|  |  |  | Mobile Gen Reqd (A) | 0 | 0
|  |  |  | LARc (A) | 0 | 0
|  |  |  | LARc (MW) | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
STAFFORD Bulk Supply Point:
595-1 | Enoggera | Grovely |  | NCC Rating (A) | 720 | 720 | 720 | 720 | 720
| (ENG) | (GLY) |  | 10 PoE Load (A) | 228 | 226 | 223 | 223 | 220
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
596-1 | Enoggera | Grovely |  | NCC Rating (A) | 720 | 720 | 720 | 720 | 720
| (ENG) | (GLY) |  | 10 PoE Load (A) | 229 | 227 | 224 | 224 | 221
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
607-1 | Chermside | Zillmere |  | NCC Rating (A) | 311 | 311 | 311 | 311 | 311
| (CSE) | (ZMR) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
SUNRISE HILLS Bulk Supply Point:
308-1 | Peregian |  |  | NCC Rating (A) | 780 | 780 | 780 | 780 | 780
| (PGN) | (308 Tee1) |  | 10 PoE Load (A) | 487 | 493 | 493 | 494 | 492
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
308-2 |  | Coolum |  | NCC Rating (A) | 780 | 780 | 780 | 780 | 780
| (308 Tee1) | (CLM) |  | 10 PoE Load (A) | 487 | 493 | 493 | 494 | 492
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
308-3 |  |  |  | NCC Rating (A) | 529 | 529 | 529 | 529 | 529
| (308 Tee1) | (307 Tee2) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
SUNRISE HILLS Bulk Supply Point:
3100-1 | Sunrise Hills BSP | Peregian |  | NCC Rating (A) | 780 | 780 | 780 | 780 | 780
| (SRH) | (PGN) |  | 10 PoE Load (A) | 705 | 714 | 716 | 720 | 718
|  |  |  | Power Factor (System Normal) | 0.94 | 0.94 | 0.94 | 0.94 | 0.94
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 3100-1 | ECC Rating (A)
|  |  |  | 50 PoE Load (A) | 592 | 598 | 599 | 602 | 601
|  |  |  | Raw LAR (A) | 592 | 598 | 599 | 602 | 601
2-Hour Rating (A)
|  |  |  | Auto Trans Avail (A) | 592 | 598 | 599 | 602 | 601
Remote Trans Avail (A)
Manual Trans Avail (A)
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
343-1 | Sunrise Hills BSP |  |  | NCC Rating (A) | 780 | 780 | 780 | 780 | 780
| (SRH) | (343 Tee1) |  | 10 PoE Load (A) | 414 | 411 | 425 | 424 | 421
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 343-1 | ECC Rating (A)
|  |  |  | 50 PoE Load (A) | 230 | 230 | 230 | 230 | 230
|  |  |  | Raw LAR (A) | 230 | 230 | 230 | 230 | 230
2-Hour Rating (A)
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) | 230 | 230 | 230 | 230 | 230
Manual Trans Avail (A)
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
SUNRISE HILLS Bulk Supply Point:
343-2 |  | Tewantin |  | NCC Rating (A) | 780 | 780 | 780 | 780 | 780
| (343 Tee1) | (TWT) |  | 10 PoE Load (A) | 154 | 152 | 159 | 158 | 156
|  |  |  | Power Factor (System Normal) | 0.94 | 0.94 | 0.94 | 0.94 | 0.94
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
343-3 |  | Cooroy |  | NCC Rating (A) | 495 | 495 | 495 | 495 | 495
| (343 Tee1) | (CRY) |  | 10 PoE Load (A) | 266 | 266 | 266 | 267 | 266
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
346-1 | Sunrise Hills BSP |  |  | NCC Rating (A) | 800 | 800 | 800 | 800 | 800
| (SRH) | (346 Tee1) |  | 10 PoE Load (A) | 287 | 284 | 297 | 296 | 293
|  |  |  | Power Factor (System Normal) | 0.95 | 0.95 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
346-2 |  | Tewantin |  | NCC Rating (A) | 780 | 780 | 780 | 780 | 780
| (346 Tee1) | (TWT) |  | 10 PoE Load (A) | 288 | 285 | 297 | 296 | 293
|  |  |  | Power Factor (System Normal) | 0.95 | 0.95 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
346-3 |  |  |  | NCC Rating (A) | 529 | 529 | 529 | 529 | 529
| (346 Tee1) | (3100 Tee1) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
SUNRISE HILLS Bulk Supply Point:
488-1 | Cooroy |  |  | NCC Rating (A) | 582 | 582 | 582 | 582 | 582
| (CRY) | (488 Tee1) |  | 10 PoE Load (A) | 162 | 162 | 161 | 161 | 161
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 488-1 | ECC Rating (A)
|  |  |  | 50 PoE Load (A) | 139 | 139 | 139 | 139 | 139
|  |  |  | Raw LAR (A) | 139 | 139 | 139 | 139 | 139
2-Hour Rating (A)
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) | 139 | 139 | 139 | 139 | 139
Manual Trans Avail (A)
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
488-3 |  |  |  | NCC Rating (A) | 293 | 293 | 293 | 293 | 293
| (488 Tee1) | (488 Tee2) |  | 10 PoE Load (A) | 162 | 162 | 161 | 162 | 161
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
488-4 |  | Black Mountain |  | NCC Rating (A) | 293 | 293 | 293 | 293 | 293
| (488 Tee2) | (BMT) |  | 10 PoE Load (A) | 97 | 97 | 96 | 96 | 95
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
SUNRISE HILLS Bulk Supply Point:
488-5 |  |  |  | NCC Rating (A) | 293 | 293 | 403 | 403 | 403
| (488 Tee2) | (488 Tee3) |  | 10 PoE Load (A) | 66 | 66 | 67 | 67 | 67
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 488-5 | ECC Rating (A)
|  |  |  | 50 PoE Load (A) | 58 | 58 | 59 | 59 | 59
|  |  |  | Raw LAR (A) | 58 | 58 | 59 | 59 | 59
2-Hour Rating (A)
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) | 58 | 58 | 59 | 59 | 59
Manual Trans Avail (A)
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
488-6 |  | Eumundi |  | NCC Rating (A) | 438 | 438 | 438 | 438 | 438
| (488 Tee3) | (EMD) |  | 10 PoE Load (A) | 66 | 67 | 67 | 67 | 67
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 488-6 | ECC Rating (A)
|  |  |  | 50 PoE Load (A) | 58 | 58 | 59 | 59 | 59
|  |  |  | Raw LAR (A) | 58 | 58 | 59 | 59 | 59
2-Hour Rating (A)
Auto Trans Avail (A)
Remote Trans Avail (A)
Manual Trans Avail (A)
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 58 | 58 | 59 | 59 | 59
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
SUNRISE HILLS Bulk Supply Point:
488-7 |  | Yandina |  | NCC Rating (A) | 293 | 293
| (488 Tee3) | (YDA) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0
|  |  |  | LARn (MW) | 0 | 0
|  |  |  | Customer Category | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes
TENNYSON Bulk Supply Point:
3390-1 | Taringa | Indooroopilly |  | NCC Rating (A) | 728 | 728 | 728 | 728 | 728
| (TRG) | (IDY) |  | 10 PoE Load (A) | 136 | 134 | 132 | 131 | 129
|  |  |  | Power Factor (System Normal) | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3393-1 | Tennyson BSP | St Lucia |  | NCC Rating (A) | 610 | 610 | 610 | 610 | 610
| (TSN) | (STL) |  | 10 PoE Load (A) | 161 | 159 | 157 | 155 | 153
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3394-1 | Tennyson BSP | St Lucia |  | NCC Rating (A) | 610 | 610 | 610 | 610 | 610
| (TSN) | (STL) |  | 10 PoE Load (A) | 152 | 150 | 149 | 147 | 144
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3460-1 | Annerley | Buranda |  | NCC Rating (A) | 800 | 800 | 800 | 800 | 800
| (ALY) | (BDA) |  | 10 PoE Load (A) | 177 | 178 | 179 | 195 | 211
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
3461-1 | Annerley | Buranda |  | NCC Rating (A) | 800 | 800 | 800 | 800 | 800
| (ALY) | (BDA) |  | 10 PoE Load (A) | 177 | 179 | 179 | 195 | 211
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
TENNYSON Bulk Supply Point:
410-1 | Sherwood | Indooroopilly |  | NCC Rating (A) | 400 | 400 | 400 | 400 | 400
| (SHW) | (IDY) |  | 10 PoE Load (A) | 258 | 255 | 252 | 250 | 246
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
460-1 | Tennyson BSP | Sherwood |  | NCC Rating (A) | 763 | 763 | 763 | 763 | 763
| (TSN) | (SHW) |  | 10 PoE Load (A) | 428 | 424 | 419 | 416 | 411
|  |  |  | Power Factor (System Normal) | 0.97 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
480-1 | Taringa | St Lucia |  | NCC Rating (A) | 610 | 610 | 610 | 610 | 610
| (TRG) | (STL) |  | 10 PoE Load (A) | 163 | 161 | 159 | 157 | 155
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
504-1 | Tennyson BSP | Taringa |  | NCC Rating (A) | 601 | 601 | 601 | 601 | 601
| (TSN) | (TRG) |  | 10 PoE Load (A) | 346 | 343 | 340 | 337 | 333
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
507A-1 | Toowong | Indooroopilly |  | NCC Rating (A) | 735 | 735 | 735 | 735 | 735
| (TWG) | (IDY) |  | 10 PoE Load (A) | 139 | 137 | 135 | 134 | 132
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
TENNYSON Bulk Supply Point:
507B-1 | Toowong | Taringa |  | NCC Rating (A) | 727 | 727 | 727 | 727 | 727
| (TWG) | (TRG) |  | 10 PoE Load (A) | 137 | 135 | 134 | 132 | 130
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
511-1 | Tennyson BSP | Moorooka |  | NCC Rating (A) | 739 | 739 | 739 | 739 | 739
| (TSN) | (MRK) |  | 10 PoE Load (A) | 155 | 155 | 154 | 154 | 154
|  |  |  | Power Factor (System Normal) | 0.94 | 0.94 | 0.94 | 0.94 | 0.94
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
514-1 | Tennyson BSP | Moorooka |  | NCC Rating (A) | 739 | 739 | 739 | 739 | 739
| (TSN) | (MRK) |  | 10 PoE Load (A) | 156 | 155 | 157 | 158 | 157
|  |  |  | Power Factor (System Normal) | 0.94 | 0.94 | 0.94 | 0.94 | 0.94
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
515-1 | Tennyson BSP | Sherwood |  | NCC Rating (A) | 740 | 740 | 740 | 740 | 740
| (TSN) | (SHW) |  | 10 PoE Load (A) | 453 | 448 | 444 | 440 | 435
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
523A&B-1 | Tennyson BSP | Rocklea |  | NCC Rating (A) | 602 | 602
| (TSN) | (RLA) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0
|  |  |  | LARn (MW) | 0 | 0
|  |  |  | Customer Category | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes
TENNYSON Bulk Supply Point:
523A-1 | Tennyson BSP | Rocklea |  | NCC Rating (A) |  |  | 650 | 650 | 650
| (TSN) | (RLA) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) |  |  | 0 | 0 | 0
|  |  |  | LARn (MW) |  |  | 0 | 0 | 0
|  |  |  | Customer Category |  |  | Urban | Urban | Urban
|  |  |  | Meets Sec Std |  |  | Yes | Yes | Yes
539-1 | Sherwood | Kenmore |  | NCC Rating (A) | 495 | 495 | 495 | 495 | 495
| (SHW) | (KMR) |  | 10 PoE Load (A) | 288 | 284 | 281 | 278 | 273
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 571-1 | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | 50 PoE Load (A) | 590 | 581 | 574 | 568 | 559
|  |  |  | Raw LAR (A) | 95 | 86 | 79 | 73 | 64
|  |  |  | 2-Hour Rating (A) | 495 | 495 | 495 | 495 | 495
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) | 306 | 302 | 299 | 296 | 292
Manual Trans Avail (A)
|  |  |  | POPS Available | Yes | Yes | Yes | Yes | Yes
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
554-1 | Tennyson BSP | Sherwood |  | NCC Rating (A) | 716 | 716 | 716 | 716 | 716
| (TSN) | (SHW) |  | 10 PoE Load (A) | 482 | 477 | 472 | 468 | 462
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
TENNYSON Bulk Supply Point:
571-1 | Indooroopilly | Kenmore |  | NCC Rating (A) | 527 | 527 | 527 | 527 | 527
| (IDY) | (KMR) |  | 10 PoE Load (A) | 372 | 367 | 363 | 359 | 353
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 539-1 | ECC Rating (A) | 527 | 527 | 527 | 527 | 527
|  |  |  | 50 PoE Load (A) | 581 | 573 | 565 | 560 | 551
|  |  |  | Raw LAR (A) | 54 | 46 | 38 | 33 | 24
|  |  |  | 2-Hour Rating (A) | 527 | 527 | 527 | 527 | 527
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) | 306 | 302 | 299 | 296 | 292
Manual Trans Avail (A)
|  |  |  | POPS Available | Yes | Yes | Yes | Yes | Yes
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
606-1 | Tennyson BSP | Taringa |  | NCC Rating (A) | 601 | 601 | 601 | 601 | 601
| (TSN) | (TRG) |  | 10 PoE Load (A) | 348 | 345 | 341 | 339 | 335
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
637-1 | Tennyson BSP | Annerley |  | NCC Rating (A) | 716 | 716 | 716 | 716 | 716
| (TSN) | (ALY) |  | 10 PoE Load (A) | 325 | 327 | 328 | 345 | 360
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.97 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
TENNYSON Bulk Supply Point:
638-1 | Tennyson BSP | Annerley |  | NCC Rating (A) | 716 | 716 | 716 | 716 | 716
| (TSN) | (ALY) |  | 10 PoE Load (A) | 326 | 329 | 330 | 346 | 361
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.97 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F703-1 | Sherwood | Indooroopilly |  | NCC Rating (A) | 400 | 400 | 400 | 400 | 400
| (SHW) | (IDY) |  | 10 PoE Load (A) | 260 | 257 | 255 | 252 | 249
|  |  |  | Power Factor (System Normal) | 0.97 | 0.99 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
VICTORIA PARK Bulk Supply Point:
627-1 | Victoria Park BSP | Astor Terrace |  | NCC Rating (A) | 415 | 415 | 415 | 415 | 415
| (VPK) | (ATC) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
628-1 | Victoria Park BSP | Astor Terrace |  | NCC Rating (A) | 415 | 415 | 415 | 415 | 415
| (VPK) | (ATC) |  | 10 PoE Load (A) | 238 | 238 | 238 | 239 | 238
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 649-1 | ECC Rating (A) | 415 | 415 | 415 | 415 | 415
|  |  |  | 50 PoE Load (A) | 464 | 464 | 464 | 465 | 463
|  |  |  | Raw LAR (A) | 49 | 49 | 49 | 50 | 48
|  |  |  | 2-Hour Rating (A) | 415 | 415 | 415 | 415 | 415
|  |  |  | Auto Trans Avail (A) | 242 | 242 | 242 | 242 | 241
Remote Trans Avail (A)
Manual Trans Avail (A)
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
639-1 | Victoria Park BSP | Newmarket |  | NCC Rating (A) | 503 | 503 | 503 | 503 | 503
| (VPK) | (NMK) |  | 10 PoE Load (A) | 220 | 218 | 216 | 214 | 211
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
VICTORIA PARK Bulk Supply Point:
649-1 | Victoria Park BSP | Astor Terrace |  | NCC Rating (A) | 415 | 415 | 415 | 415 | 415
| (VPK) | (ATC) |  | 10 PoE Load (A) | 241 | 241 | 241 | 241 | 241
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | 628-1 | ECC Rating (A) | 415 | 415 | 415 | 415 | 415
|  |  |  | 50 PoE Load (A) | 464 | 463 | 464 | 465 | 463
|  |  |  | Raw LAR (A) | 49 | 48 | 49 | 50 | 48
|  |  |  | 2-Hour Rating (A) | 415 | 415 | 415 | 415 | 415
|  |  |  | Auto Trans Avail (A) | 242 | 242 | 242 | 242 | 241
Remote Trans Avail (A)
Manual Trans Avail (A)
|  |  |  | POPS Available | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
653-1 | Victoria Park BSP | Newmarket |  | NCC Rating (A) | 503 | 503 | 503 | 503 | 503
| (VPK) | (NMK) |  | 10 PoE Load (A) | 220 | 218 | 216 | 214 | 211
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
659B-1 | Victoria Park BSP | Clayfield |  | NCC Rating (A) | 330 | 330
| (VPK) | (CFD) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0
|  |  |  | LARn (MW) | 0 | 0
|  |  |  | Customer Category | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes
VICTORIA PARK Bulk Supply Point:
689-1 | Victoria Park BSP | Astor Terrace |  | NCC Rating (A) | 538 | 538 | 538 | 538 | 538
| (VPK) | (ATC) |  | 10 PoE Load (A)
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes