## Explanatory Notes
Transmission and Sub-Transmission Feeders Limitations and Proposed Solutions - Capacity
(Energex Distribution Annual Planning Report 2023/24 - 2027/28)
This workbook provides 5 year forecast transmission and sub-transmission feeders limitations and proposed solutions in the Energex network.
https://www.energex.com.au/about-us/company-reports,-plans-and-charters
Energex Distribution Annual Planning Report is prepared and made available solely for information purposes. While care was taken in the preparation of the information in this report, and it is provided in good faith, Energex accepts no responsibility or liability (including without limitation, liability to any person by reason of negligence or negligent mis-statement) for any loss or damage that may be incurred by any person acting in reliance on this information or assumptions drawn from it, except to the extent that liability under any applicable Queensland or Commonwealth of Australia statute cannot be excluded.
It contains assumptions regarding, among other things, economic growth and load forecasts which may or may not prove to be correct. The forecasts included in the document involve subjective judgements and analysis which are subject to significant uncertainties and contingencies, many of which are out of the control of Energex. Furthermore, forecasted data is subject to ongoing variation as new information becomes available. Energex makes no representation or warranty as to the accuracy, reliability, completeness or suitability for any particular purpose of the information in this document. All information should be independently investigated, reviewed, analysed and verified, and must not be relied upon in connection with any investment proposal or decision.
All financials presented in this document are correct at the time of writing and represent the existing organisational accounting treatment, which may be subject to change.
Field | Notes
Constraint primary driver | Categories perscribed by AER: Capacity, Reliability, Asset condition, Performance, Safety, Environment, Power quality, Voltage
Location of constraint (start) | Location of substation / Location of feeder start point
Location of constraint (end) | Location of feeder end point
Asset ID | Consistent wirh RIN Sustained Interruptions sheet from Category Analysis template where applicable as not every feeder has sustained interruptions.
Network Element | Categories perscribed by AER: Transmission connection point, Zone substation, Sub-transmission line, Feeder
Residential customers affected | The total number of residential customers supplied by the asset.
% of Residential customers affected | The percentage of total number of residential customers supplied by the asset that experiences outage after all network load transfer capacities (where applicable) are exhausted, on the year that the proposed network investment is forecast to be commissioned.
Asset rating (MVA) | Normal cyclic rating of substations or feeders in MVA, calculated based on nominal voltage.
Asset rating (MW) | Normal cyclic rating of substations or feeders in MVA, calculated based on nominal voltage. Since asset thermal rating is not voltage dependent, the rating in MW is made the same as the rating in MVA.
10% PoE Forecast Demand (MVA) | Forecast 10% PoE demand in MVA under system normal conditions.
50% PoE Forecast Demand (MVA) | Forecast 50% PoE demand in MVA. For meshed feeders, 50% PoE load is based on N-1 scenarios where adjacent feeder is taken out of service. For single radial feeders, the 50% PoE load entered is the sum of all load supplied by the feeder.
10% PoE Forecast Demand (MW) | Forecast 10% PoE demand in MW under system normal conditions.
50% PoE Forecast Demand (MW) | Forecast 50% PoE demand in MW. For meshed feeders, 50% PoE load is based on N-1 scenarios where adjacent feeder is taken out of service. For single radial feeders, the 50% PoE load entered is the sum of all load supplied by the feeder.
Voltage level (kV) | Highest operational voltage level of the assets
Maximum Load at Risk and Energy at Risk - For Capacity and Voltage driven projects | Energex's network security standards take into account a range of actions to defer or avoid investments such as contracted non-network solutions, automated, remote and manual load transfer schemes and the deployment of a mobile substation and/or mobile generation (available supply). Load at risk is the shortfall between the forecast load (either 10 PoE or 50 PoE) and the available supply. The general equations for LAR are as follows: • LARn = 10 PoE – NCC where NCC is the normal cyclic capacity • LARc = 50 PoE – available capacity – available supply (within security standard timeframe) Network security standards are not being met if LARn or LARc is greater than 0. The Energy at Risk are calculated after all of the available supply within the security standard timeframes have been applied. For further information, please refer to Appendix C, Appendix E and Appendix F.
Preferred network investment | A possible network investment option that can mitigate the identified limitation.
Preferred network investment capital cost | Estimated capital cost of the possible network investment option.
Preferred annual network investment operating cost | Estimated capital cost associated with the possible network investment option. Where incremental changes in OPEX cost is low or where the proposed works result in a reduction in OPEX, $0.0 is entered. e.g. incremental change to existing SCADA systems, a reduction in network asset, etc.
Preferred network investment cost accuracy (+%) | The accuracy range of the estimated captial costs.
Preferred network investment cost accuracy (-%) | The accuracy range of the estimated capital costs.
Proposed timing | Proposed timing of the network investment option.
Demand reduction required to defer investment by 1 year (MVA) | The load reduction required to enable Energex to meet the prescribed network security standards for the network element if the proposed timing is deferred by 1 year.
Demand reduction required to defer investment by 1 year (MW) | The load reduction required to enable Energex to meet the prescribed network security standards for the network element if the proposed timing is deferred by 1 year.
Annual deferral value | This is calculated based on Energex's Regulated pre - tax real WACC.
Load transfer capability (MVA) | Available capacity to temporarily de-load the network asset to adjacent network, this includes automated, remote and manual load transfer schemes.
Load transfer capability (MW) | Available capacity to temporarily de-load the network asset to adjacent network, this includes automated, remote and manual load transfer schemes.
Emergency generation (MVA) | The capacity of contracted embedded generators to provide network support.
Emergency generation (MW) | The capacity of contracted embedded generators to provide network support.
Historic use of existing emergency response (MW) | Uncleansed 30-minute interval recorded contracted embedded generation data for the past 3 years.
Historic load trace | Uncleansed 30-minute interval recorded load data for the past 3 years. Where the data is recorded in Amps, it is converted to MVA using the nominal voltage level.
Historic asset rating (MVA) | Normal cyclic rating of substations or feeders in MVA, calculated based on nominal voltage.
Energex comment: | Additional comments on the limitations.
Status of network investment | Shows whether the proposed network investment option is committed or not committed.

## Limitations
AER Rule | Field Name |  | Limitation 1 | Limitation 2 | Limitation 3 | Limitation 4 | Limitation 5 | Limitation 6 | Limitation 7 | Limitation 8 | Limitation 9 | Limitation 10
DT001 | Constraint primary driver |  | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity
DT002 | Location of constraint (start) |  | -27.448,153.111 | -27.448,153.111 | -27.855,153.293 | -27.855,153.293 | -27.965,152.993 | -27.640174,152.687503 | -27.065188,152.963122 | -27.630686,152.778882 | -27.630686,152.778882 | -27.43422,153.142538
DT003 | Location of constraint (end) |  | -27.457, 153.088 | -27.457, 153.088 | -27.811,153.335 | -27.811,153.335 | -27.810,153.0451 | -27.670155,152.595063 | -27.097975,152.951817 | -27.638754,152.76099 | -27.638754,152.76099 | -27.393651,153.165147
DT004 | Asset ID |  | 581 | 677 | 3641 | 3642 | 314 | 436 | 499 | 509A | 510A | 3303
DT005 | Network Element |  | Sub-transmission line | Sub-transmission line | Sub-transmission line | Sub-transmission line | Sub-transmission line | Sub-transmission line | Sub-transmission line | Sub-transmission line | Sub-transmission line | Sub-transmission line
DT006 | Residential customers affected |  | 4509.7087 | 4509.7087 | 14004 | 14004 | 9959 | 666.6667 | 9398.9071 | 8627.451 | 8627.451 | 0
DT006_a | % of Residential customers affected (%) |  | 20.6 | 20.6 | 100 | 100 | 42.4 | 48 | 18.3 | 5.1 | 5.1 | NA
DT007 | Asset rating (MVA) | 2024 | 37.8 | 37.8 | 40.7534 | 40.7534 | 21 | 11.9 | 38.7 | 41.2 | 41.2 | 34.29
|  | 2025 | 37.8 | 37.8 | 40.7534 | 40.7534 | 21 | 11.9 | 38.7 | 41.2 | 41.2 | 34.29
|  | 2026 | 37.8 | 37.8 | 40.7534 | 40.7534 | 21 | 11.9 | 38.7 | 41.2 | 41.2 | 34.29
|  | 2027 | 37.8 | 37.8 | 40.7534 | 40.7534 | 21 | 11.9 | 38.7 | 41.2 | 41.2 | 34.29
|  | 2028 | 37.8 | 37.8 | 40.7534 | 40.7534 | 21 | 11.9 | 38.7 | 41.2 | 41.2 | 34.29
DT007_a | Asset rating (MW) | 2024 | 36.288 | 36.288 | 39.5308 | 39.5308 | 20.37 | 11.543 | 37.152 | 40.376 | 40.376 | 45.7
|  | 2025 | 36.288 | 36.288 | 39.5308 | 39.5308 | 20.37 | 11.543 | 37.152 | 40.376 | 40.376 | 45.7
|  | 2026 | 36.288 | 36.288 | 39.5308 | 39.5308 | 20.37 | 11.543 | 37.152 | 40.376 | 40.376 | 45.7
|  | 2027 | 36.288 | 36.288 | 39.5308 | 39.5308 | 20.37 | 11.543 | 37.152 | 40.376 | 40.376 | 45.7
|  | 2028 | 36.288 | 36.288 | 39.5308 | 39.5308 | 20.37 | 11.543 | 37.152 | 40.376 | 40.376 | 45.7
DT008 | 10% PoE Forecast Demand (MVA) | 2024 | 30.1714 | 30.1714 | 22.5143 | 22.5143 | 0 | 4.2286 | 34.7429 | 24.9714 | 24.7429 | 12
|  | 2025 | 29.7143 | 29.7143 | 24.8571 | 24.8571 | 0 | 4.4571 | 34 | 25.3714 | 25.0857 | 16.9714
|  | 2026 | 29.4857 | 29.4857 | 25.1429 | 25.1429 | 0 | 4.7429 | 33.6571 | 25.7714 | 25.4857 | 18.7429
|  | 2027 | 29.0857 | 29.0857 | 25.6 | 25.6 | 0 | 5.0286 | 33.3143 | 25.7714 | 25.5429 | 19.5429
|  | 2028 | 29.0286 | 29.0286 | 26.2286 | 26.2286 | 0 | 5.3714 | 33.2 | 26.1143 | 25.8286 | 19.4857
| 50% PoE Forecast Demand (MVA) | 2024 | 54.9714 | 54.9857 | 41.03 | 42.8571 | 21 | 13.4892 | 59.3297 | 44.8116 | 44.8116 | 23.5429
|  | 2025 | 54.2426 | 54.2426 | 45.17 | 47.8857 | 21 | 14.1179 | 57.8436 | 45.6118 | 45.6118 | 33.8857
|  | 2026 | 53.6711 | 53.6711 | 45.69 | 48.4 | 21 | 14.518 | 57.3863 | 46.412 | 46.412 | 37.6
|  | 2027 | 52.8709 | 52.8709 | 46.41 | 49.3143 | 21 | 15.2039 | 56.6857 | 46.4692 | 46.4692 | 39.4286
|  | 2028 | 52.8137 | 52.7565 | 47.5 | 50.6857 | 21 | 16.0041 | 56.5714 | 47.0408 | 47.0408 | 39.2
DT008_a | 10% PoE Forecast Demand (MW) | 2024 | 28.9646 | 28.9646 | 22.064 | 22.064 | 0 | 3.6789 | 33.7006 | 24.2223 | 24.0006 | 11.16
|  | 2025 | 28.5257 | 28.5257 | 24.1114 | 24.1114 | 0 | 3.8777 | 32.98 | 24.6103 | 24.3331 | 15.7834
|  | 2026 | 28.3063 | 28.3063 | 24.3886 | 24.3886 | 0 | 4.1263 | 32.6474 | 24.9983 | 24.7211 | 17.4309
|  | 2027 | 27.9223 | 27.9223 | 24.832 | 24.832 | 0 | 4.3749 | 32.3149 | 24.9983 | 24.7766 | 18.1749
|  | 2028 | 27.8674 | 27.8674 | 25.4417 | 25.4417 | 0 | 4.6731 | 32.204 | 25.3309 | 25.0537 | 18.1217
| 50% PoE Forecast Demand (MW) | 2024 | 52.7726 | 52.7726 | 40.2094 | 42 | 20.37 | 11.7356 | 57.5498 | 43.4673 | 43.4673 | 21.8949
|  | 2025 | 52.0729 | 52.0729 | 43.8149 | 46.4491 | 20.37 | 12.2826 | 56.1083 | 44.2435 | 44.2435 | 31.5137
|  | 2026 | 51.5242 | 51.5242 | 44.3193 | 46.948 | 20.37 | 12.6307 | 55.6647 | 45.0197 | 45.0197 | 34.968
|  | 2027 | 50.756 | 50.756 | 45.0177 | 47.8349 | 20.37 | 13.2274 | 54.9851 | 45.0751 | 45.0751 | 36.6686
|  | 2028 | 50.7011 | 50.7011 | 46.075 | 49.1651 | 20.37 | 13.9236 | 54.8743 | 45.6295 | 45.6295 | 36.456
DT009 | Voltage level (kV) |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33
DT010 | Maximum Load at risk (MW) | 2024 | 2.3 | 2.3 | 40.2094 | 0 | 0 | 0 | 4.3 | 0 | 0 | 0
|  | 2025 | 1.6 | 1.6 | 43.8149 | 0.74914 | 0 | 0 | 2.9 | 0 | 0 | 0
|  | 2026 | 1 | 1 | 44.3193 | 1.248 | 10.62 | 0 | 2.4 | 0.5 | 0.5 | 0
|  | 2027 | 0.3 | 0.3 | 45.0177 | 2.1349 | 10.72 | 0 | 1.8 | 0.6 | 0.6 | 1.1
|  | 2028 | 0.2 | 0.2 | 46.075 | 3.4651 | 11.08 | 0.8 | 1.7 | 1.1 | 1.1 | 0.8
DT011 | Energy at risk (MWh) | 2024 | 51.0649 | 100.7154 | 306.2857 | 0 | 0 | 0 | 22.6823 | 0 | 0 | 0
|  | 2025 | 43.7048 | 86.0139 | 343.9908 | 1.8855 | 0 | 0 | 10.2646 | 0 | 0 | 0
|  | 2026 | 39.2032 | 75.806 | 348.7267 | 2.9329 | 98.8774 | 0 | 7.4487 | 0.54117 | 0.54854 | 0
|  | 2027 | 32.6089 | 62.4446 | 355.2841 | 6.0327 | 98.97 | 0.001971 | 3.5431 | 0.59812 | 0.6055 | 2.1404
|  | 2028 | 31.8592 | 61.5774 | 365.2113 | 14.4683 | 102.303 | 5.0633 | 3.0008 | 1.1676 | 1.1751 | 1.4033
DT012 | Preferred network investment |  | Establish new 11kV feeder | Establish new 11kV feeder | Establish new 33kV feeder (PPE-STT) | Install plant overload protection scheme | Establish new 33kV feeder (JBB-BDS) | Install plant overload protection scheme | Install a plant overload protection scheme | Install a plant overload protection scheme | Install a plant overload protection scheme | Replace underground feeder tails.
DT013 | Preferred network investment capital cost |  | 1318770 | NA | 6383000 | 150000 | 16168425.68 | 150000 | 150000 | 150000 | NA | 750000
DT013_a | Preferred annual network investment operating cost |  | 1300 | NA | 27600 | 0 | 49400 | 0 | 0 | 0 | NA | 2900
DT014 | Preferred network investment cost accuracy (+%) |  | 40 | NA | 40 | 40 | 40 | 40 | 40 | 40 | NA | 40
DT014_a | Preferred network investment cost accuracy (-%) |  | 40 | NA | 40 | 40 | 40 | 40 | 40 | 40 | NA | 40
DT015 | Proposed timing |  | 2025-10-01 | 2025-10-01 | 2027-10-01 | 2025-10-01 | 2027-03-01 | 2027-10-01 | 2025-10-01 | 2027-10-01 | 2027-10-01 | 2026-10-01
DT016 | Demand reduction required to defer investment by 1 year (MVA) |  | 1.0417 | 1.0417 | 49.2784 | 0.82474 | 10.6 | 0.8 | 2.4742 | 1.1 | 1.1 | 1.1
DT016_a | Demand reduction required to defer investment by 1 year (MW) |  | 1 | 1 | 47.8 | 0.8 | 10.2 | 0.8 | 2.4 | 1.067 | 1.067 | 1.023
DT017 | Annual deferral value |  | 35870.544 | NA | 173617.6 | 4080 | 439781.1785 | 4080 | 4080 | 4080 | NA | 20400
DT017 | Load transfer capability (MVA) |  | 9.7 | 9.7 | 7.4 | 7.4 | 7.6 | 2.34 | 12 | 12 | 12 | 3.5
DT017_a | Load transfer capability (MW) |  | 9.7 | 9.7 | 7.2 | 7.2 | 7.3 | 2.0358 | 11.64 | 11.64 | 11.64 | 3.255
DT018 | Emergency generation (MVA) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DT018_a | Emergency generation (MW) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DT019 | Historic use of existing emergency response (MVA) |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
DT019_a | Historic use of existing emergency response (MW) |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
DT020 | Historic load trace |  | Historical Load Trace | Historical Load Trace | Historical Load Trace | Historical Load Trace | Historical Load Trace | Historical Load Trace | Historical Load Trace | Historical Load Trace | Historical Load Trace | Historical Load Trace
DT021 | Historic asset rating (MVA) |  | Historic Asset Rating | Historic Asset Rating | Historic Asset Rating | Historic Asset Rating | Historic Asset Rating | Historic Asset Rating | Historic Asset Rating | Historic Asset Rating | Historic Asset Rating | Historic Asset Rating
DT021_a | Historic asset rating (MW) |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| Energex comment: |  | The proposed solution for this feeder limitation will also solve the issue with limitation 2 | The proposed solution for this limitation is a single feeder to solve limitations 1 and 2. As such, the cost has not been shown twice. | This is a VCR driven project due to the load at risk for the loss of both 3641 and 3642. These feeders are on construct as double circuit on same poles, therefore a pole failure will lead to the loss of both feeders. | There is a breach of the 2 hour rating of the feeder 3641 and 3642 under N-1. The establishment of POPS will remove this limitation. | F314 is a normally open feeder providing backup supply to SSBDS for the loss of F7351. F314 is restricted to supply up to 21 MVA of load due to excessive voltage drop. The proposed solution for this limitation is a single feeder. This solution will provide enough capacity to supply SSBDS for loss of F7351. | There is a breach of the 2 hour rating of the feeder 436 under N-1. The establishment of POPS will remove this limitation. | There is a breach of the 2 hour rating of the feeder 499 under N-1. The establishment of POPS will remove this limitation. | There is a breach of the 2 hour rating of the feeder 509A and 510A under N-1. The establishment of POPS will remove this limitation. | The proposed solution for F509A will resolve this limitation. As such, the cost has not been shown twice. | The feeder tail at SSFBS is limiting the feeder rating.
| Project status: |  | Not committed | Not committed | Not committed | Not committed | Not committed | Not committed | Not committed | Not committed | Not committed | Not committed

## Historic Data 581
33 kV feeder 581
Date | Time | Historic use of existing emergency response (MW) | Historic load trace (MVA) | Historic asset rating (MVA)
2020-07-01 | 44013 | 0 | 8.4874 | 39.95
2020-07-01 00:30 | 44013.0208 | 0 | 8.0564 | 39.95
2020-07-01 01:00 | 44013.0417 | 0 | 7.788 | 39.95
2020-07-01 01:30 | 44013.0625 | 0 | 7.6476 | 39.95
2020-07-01 02:00 | 44013.0833 | 0 | 7.6466 | 39.95
2020-07-01 02:30 | 44013.1042 | 0 | 7.5563 | 39.95
2020-07-01 03:00 | 44013.125 | 0 | 7.6544 | 39.95
2020-07-01 03:30 | 44013.1458 | 0 | 7.5666 | 39.95
2020-07-01 04:00 | 44013.1667 | 0 | 7.9019 | 39.95
2020-07-01 04:30 | 44013.1875 | 0 | 8.2645 | 39.95
2020-07-01 05:00 | 44013.2083 | 0 | 9.0459 | 39.95
2020-07-01 05:30 | 44013.2292 | 0 | 9.852 | 39.95
2020-07-01 06:00 | 44013.25 | 0 | 10.9317 | 39.95
2020-07-01 06:30 | 44013.2708 | 0 | 11.9421 | 39.95
2020-07-01 07:00 | 44013.2917 | 0 | 12.8908 | 39.95
2020-07-01 07:30 | 44013.3125 | 0 | 12.98 | 39.95
2020-07-01 08:00 | 44013.3333 | 0 | 12.5734 | 39.95
2020-07-01 08:30 | 44013.3542 | 0 | 12.2636 | 39.95
2020-07-01 09:00 | 44013.375 | 0 | 12.1505 | 39.95
2020-07-01 09:30 | 44013.3958 | 0 | 11.3174 | 39.95
2020-07-01 10:00 | 44013.4167 | 0 | 11.0337 | 39.95
2020-07-01 10:30 | 44013.4375 | 0 | 10.7059 | 39.95
2020-07-01 11:00 | 44013.4583 | 0 | 10.1762 | 39.95
2020-07-01 11:30 | 44013.4792 | 0 | 9.7482 | 39.95
2020-07-01 12:00 | 44013.5 | 0 | 10.2026 | 39.95
2020-07-01 12:30 | 44013.5208 | 0 | 9.6628 | 39.95
2020-07-01 13:00 | 44013.5417 | 0 | 10.0374 | 39.95
2020-07-01 13:30 | 44013.5625 | 0 | 10.2845 | 39.95
2020-07-01 14:00 | 44013.5833 | 0 | 9.9533 | 39.95
2020-07-01 14:30 | 44013.6042 | 0 | 10.3028 | 39.95
2020-07-01 15:00 | 44013.625 | 0 | 10.6411 | 39.95
2020-07-01 15:30 | 44013.6458 | 0 | 10.9965 | 39.95
2020-07-01 16:00 | 44013.6667 | 0 | 11.5223 | 39.95
2020-07-01 16:30 | 44013.6875 | 0 | 12.191 | 39.95
2020-07-01 17:00 | 44013.7083 | 0 | 12.9248 | 39.95
2020-07-01 17:30 | 44013.7292 | 0 | 13.8357 | 39.95
2020-07-01 18:00 | 44013.75 | 0 | 14.1039 | 39.95
2020-07-01 18:30 | 44013.7708 | 0 | 14.185 | 39.95
2020-07-01 19:00 | 44013.7917 | 0 | 13.9748 | 39.95
2020-07-01 19:30 | 44013.8125 | 0 | 13.7598 | 39.95
2020-07-01 20:00 | 44013.8333 | 0 | 13.7033 | 39.95
2020-07-01 20:30 | 44013.8542 | 0 | 13.0635 | 39.95
2020-07-01 21:00 | 44013.875 | 0 | 12.3926 | 39.95
2020-07-01 21:30 | 44013.8958 | 0 | 11.8624 | 39.95
2020-07-01 22:00 | 44013.9167 | 0 | 11.3203 | 39.95
2020-07-01 22:30 | 44013.9375 | 0 | 10.3861 | 39.95
2020-07-01 23:00 | 44013.9583 | 0 | 9.758 | 39.95
2020-07-01 23:30 | 44013.9792 | 0 | 9.2228 | 39.95
2020-07-02 | 44014 | 0 | 8.42 | 39.95
2020-07-02 00:30 | 44014.0208 | 0 | 8.2453 | 39.95
2020-07-02 01:00 | 44014.0417 | 0 | 7.83 | 39.95
2020-07-02 01:30 | 44014.0625 | 0 | 7.6894 | 39.95
2020-07-02 02:00 | 44014.0833 | 0 | 7.7331 | 39.95
2020-07-02 02:30 | 44014.1042 | 0 | 7.5866 | 39.95
2020-07-02 03:00 | 44014.125 | 0 | 7.6842 | 39.95
2020-07-02 03:30 | 44014.1458 | 0 | 7.8486 | 39.95
2020-07-02 04:00 | 44014.1667 | 0 | 7.97 | 39.95
2020-07-02 04:30 | 44014.1875 | 0 | 8.3655 | 39.95
2020-07-02 05:00 | 44014.2083 | 0 | 9.0519 | 39.95
2020-07-02 05:30 | 44014.2292 | 0 | 9.7719 | 39.95
2020-07-02 06:00 | 44014.25 | 0 | 10.7834 | 39.95
2020-07-02 06:30 | 44014.2708 | 0 | 11.9321 | 39.95
2020-07-02 07:00 | 44014.2917 | 0 | 12.5231 | 39.95
2020-07-02 07:30 | 44014.3125 | 0 | 12.4481 | 39.95
2020-07-02 08:00 | 44014.3333 | 0 | 12.3245 | 39.95
2020-07-02 08:30 | 44014.3542 | 0 | 11.8096 | 39.95
2020-07-02 09:00 | 44014.375 | 0 | 11.2537 | 39.95
2020-07-02 09:30 | 44014.3958 | 0 | 10.5082 | 39.95
2020-07-02 10:00 | 44014.4167 | 0 | 10.0198 | 39.95
2020-07-02 10:30 | 44014.4375 | 0 | 9.7851 | 39.95
2020-07-02 11:00 | 44014.4583 | 0 | 9.5086 | 39.95
2020-07-02 11:30 | 44014.4792 | 0 | 9.2351 | 39.95
2020-07-02 12:00 | 44014.5 | 0 | 9.1578 | 39.95
2020-07-02 12:30 | 44014.5208 | 0 | 9.2434 | 39.95
2020-07-02 13:00 | 44014.5417 | 0 | 9.1466 | 39.95
2020-07-02 13:30 | 44014.5625 | 0 | 9.3035 | 39.95
2020-07-02 14:00 | 44014.5833 | 0 | 9.7761 | 39.95
2020-07-02 14:30 | 44014.6042 | 0 | 10.5826 | 39.95
2020-07-02 15:00 | 44014.625 | 0 | 10.9089 | 39.95
2020-07-02 15:30 | 44014.6458 | 0 | 10.8991 | 39.95
2020-07-02 16:00 | 44014.6667 | 0 | 11.5256 | 39.95
2020-07-02 16:30 | 44014.6875 | 0 | 11.9439 | 39.95
2020-07-02 17:00 | 44014.7083 | 0 | 12.3114 | 39.95
2020-07-02 17:30 | 44014.7292 | 0 | 12.9686 | 39.95
2020-07-02 18:00 | 44014.75 | 0 | 12.9488 | 39.95
2020-07-02 18:30 | 44014.7708 | 0 | 13.0714 | 39.95
2020-07-02 19:00 | 44014.7917 | 0 | 12.9933 | 39.95
2020-07-02 19:30 | 44014.8125 | 0 | 12.6454 | 39.95
2020-07-02 20:00 | 44014.8333 | 0 | 12.5153 | 39.95
2020-07-02 20:30 | 44014.8542 | 0 | 11.8604 | 39.95
2020-07-02 21:00 | 44014.875 | 0 | 11.3825 | 39.95
2020-07-02 21:30 | 44014.8958 | 0 | 10.9418 | 39.95
2020-07-02 22:00 | 44014.9167 | 0 | 10.7438 | 39.95
2020-07-02 22:30 | 44014.9375 | 0 | 10.1464 | 39.95
2020-07-02 23:00 | 44014.9583 | 0 | 9.486 | 39.95
2020-07-02 23:30 | 44014.9792 | 0 | 9.0435 | 39.95
2020-07-03 | 44015 | 0 | 8.5389 | 39.95
2020-07-03 00:30 | 44015.0208 | 0 | 7.9612 | 39.95
2020-07-03 01:00 | 44015.0417 | 0 | 7.7313 | 39.95
2020-07-03 01:30 | 44015.0625 | 0 | 7.6044 | 39.95
2020-07-03 02:00 | 44015.0833 | 0 | 7.5122 | 39.95
2020-07-03 02:30 | 44015.1042 | 0 | 7.5015 | 39.95
2020-07-03 03:00 | 44015.125 | 0 | 7.4511 | 39.95
2020-07-03 03:30 | 44015.1458 | 0 | 7.3414 | 39.95
2020-07-03 04:00 | 44015.1667 | 0 | 7.4168 | 39.95
2020-07-03 04:30 | 44015.1875 | 0 | 7.6131 | 39.95
2020-07-03 05:00 | 44015.2083 | 0 | 7.7615 | 39.95
2020-07-03 05:30 | 44015.2292 | 0 | 7.989 | 39.95
2020-07-03 06:00 | 44015.25 | 0 | 8.4519 | 39.95
2020-07-03 06:30 | 44015.2708 | 0 | 8.9214 | 39.95
2020-07-03 07:00 | 44015.2917 | 0 | 9.3253 | 39.95
2020-07-03 07:30 | 44015.3125 | 0 | 9.3579 | 39.95
2020-07-03 08:00 | 44015.3333 | 0 | 9.3596 | 39.95
2020-07-03 08:30 | 44015.3542 | 0 | 9.2545 | 39.95
2020-07-03 09:00 | 44015.375 | 0 | 8.9169 | 39.95
2020-07-03 09:30 | 44015.3958 | 0 | 8.565 | 39.95
2020-07-03 10:00 | 44015.4167 | 0 | 8.0759 | 39.95
2020-07-03 10:30 | 44015.4375 | 0 | 7.7 | 39.95
2020-07-03 11:00 | 44015.4583 | 0 | 7.3824 | 39.95
2020-07-03 11:30 | 44015.4792 | 0 | 7.2995 | 39.95
2020-07-03 12:00 | 44015.5 | 0 | 7.0808 | 39.95
2020-07-03 12:30 | 44015.5208 | 0 | 6.8344 | 39.95
2020-07-03 13:00 | 44015.5417 | 0 | 7.0299 | 39.95
2020-07-03 13:30 | 44015.5625 | 0 | 7.165 | 39.95
2020-07-03 14:00 | 44015.5833 | 0 | 7.4671 | 39.95
2020-07-03 14:30 | 44015.6042 | 0 | 8.13 | 39.95
2020-07-03 15:00 | 44015.625 | 0 | 8.4646 | 39.95
2020-07-03 15:30 | 44015.6458 | 0 | 8.8563 | 39.95
2020-07-03 16:00 | 44015.6667 | 0 | 9.6152 | 39.95
2020-07-03 16:30 | 44015.6875 | 0 | 10.4755 | 39.95
2020-07-03 17:00 | 44015.7083 | 0 | 11.2612 | 39.95
2020-07-03 17:30 | 44015.7292 | 0 | 12.1766 | 39.95
2020-07-03 18:00 | 44015.75 | 0 | 12.4259 | 39.95
2020-07-03 18:30 | 44015.7708 | 0 | 12.4881 | 39.95
2020-07-03 19:00 | 44015.7917 | 0 | 12.0446 | 39.95
2020-07-03 19:30 | 44015.8125 | 0 | 11.8615 | 39.95
2020-07-03 20:00 | 44015.8333 | 0 | 11.831 | 39.95
2020-07-03 20:30 | 44015.8542 | 0 | 11.43 | 39.95
2020-07-03 21:00 | 44015.875 | 0 | 10.9139 | 39.95
2020-07-03 21:30 | 44015.8958 | 0 | 10.6531 | 39.95
2020-07-03 22:00 | 44015.9167 | 0 | 10.2855 | 39.95
2020-07-03 22:30 | 44015.9375 | 0 | 9.4704 | 39.95
2020-07-03 23:00 | 44015.9583 | 0 | 8.9963 | 39.95
2020-07-03 23:30 | 44015.9792 | 0 | 8.5551 | 39.95
2020-07-04 | 44016 | 0 | 7.8634 | 39.95
2020-07-04 00:30 | 44016.0208 | 0 | 7.6243 | 39.95
2020-07-04 01:00 | 44016.0417 | 0 | 7.4681 | 39.95
2020-07-04 01:30 | 44016.0625 | 0 | 7.4065 | 39.95
2020-07-04 02:00 | 44016.0833 | 0 | 7.2678 | 39.95
2020-07-04 02:30 | 44016.1042 | 0 | 7.2116 | 39.95
2020-07-04 03:00 | 44016.125 | 0 | 7.1297 | 39.95
2020-07-04 03:30 | 44016.1458 | 0 | 7.0539 | 39.95
2020-07-04 04:00 | 44016.1667 | 0 | 7.17 | 39.95
2020-07-04 04:30 | 44016.1875 | 0 | 7.2232 | 39.95
2020-07-04 05:00 | 44016.2083 | 0 | 7.2558 | 39.95
2020-07-04 05:30 | 44016.2292 | 0 | 7.5434 | 39.95
2020-07-04 06:00 | 44016.25 | 0 | 8.0154 | 39.95
2020-07-04 06:30 | 44016.2708 | 0 | 8.5154 | 39.95
2020-07-04 07:00 | 44016.2917 | 0 | 9.1164 | 39.95
2020-07-04 07:30 | 44016.3125 | 0 | 9.3244 | 39.95
2020-07-04 08:00 | 44016.3333 | 0 | 9.3495 | 39.95
2020-07-04 08:30 | 44016.3542 | 0 | 9.2315 | 39.95
2020-07-04 09:00 | 44016.375 | 0 | 8.9189 | 39.95
2020-07-04 09:30 | 44016.3958 | 0 | 8.4886 | 39.95
2020-07-04 10:00 | 44016.4167 | 0 | 7.9176 | 39.95
2020-07-04 10:30 | 44016.4375 | 0 | 7.4589 | 39.95
2020-07-04 11:00 | 44016.4583 | 0 | 7.0747 | 39.95
2020-07-04 11:30 | 44016.4792 | 0 | 6.7302 | 39.95
2020-07-04 12:00 | 44016.5 | 0 | 6.5639 | 39.95
2020-07-04 12:30 | 44016.5208 | 0 | 7.4992 | 39.95
2020-07-04 13:00 | 44016.5417 | 0 | 6.752 | 39.95
2020-07-04 13:30 | 44016.5625 | 0 | 6.6801 | 39.95
2020-07-04 14:00 | 44016.5833 | 0 | 7.7605 | 39.95
2020-07-04 14:30 | 44016.6042 | 0 | 7.9848 | 39.95
2020-07-04 15:00 | 44016.625 | 0 | 8.1356 | 39.95
2020-07-04 15:30 | 44016.6458 | 0 | 8.8014 | 39.95
2020-07-04 16:00 | 44016.6667 | 0 | 9.4346 | 39.95
2020-07-04 16:30 | 44016.6875 | 0 | 10.4711 | 39.95
2020-07-04 17:00 | 44016.7083 | 0 | 11.6082 | 39.95
2020-07-04 17:30 | 44016.7292 | 0 | 12.8064 | 39.95
2020-07-04 18:00 | 44016.75 | 0 | 13.1633 | 39.95
2020-07-04 18:30 | 44016.7708 | 0 | 13.3136 | 39.95
2020-07-04 19:00 | 44016.7917 | 0 | 13.079 | 39.95
2020-07-04 19:30 | 44016.8125 | 0 | 12.8697 | 39.95
2020-07-04 20:00 | 44016.8333 | 0 | 12.9864 | 39.95
2020-07-04 20:30 | 44016.8542 | 0 | 12.3135 | 39.95
2020-07-04 21:00 | 44016.875 | 0 | 11.7176 | 39.95
2020-07-04 21:30 | 44016.8958 | 0 | 11.0892 | 39.95
2020-07-04 22:00 | 44016.9167 | 0 | 10.5056 | 39.95
2020-07-04 22:30 | 44016.9375 | 0 | 9.692 | 39.95
2020-07-04 23:00 | 44016.9583 | 0 | 9.0027 | 39.95
2020-07-04 23:30 | 44016.9792 | 0 | 8.423 | 39.95
2020-07-05 | 44017 | 0 | 8.0005 | 39.95
2020-07-05 00:30 | 44017.0208 | 0 | 7.7876 | 39.95
2020-07-05 01:00 | 44017.0417 | 0 | 7.4157 | 39.95
2020-07-05 01:30 | 44017.0625 | 0 | 7.3522 | 39.95
2020-07-05 02:00 | 44017.0833 | 0 | 7.4249 | 39.95
2020-07-05 02:30 | 44017.1042 | 0 | 7.2688 | 39.95
2020-07-05 03:00 | 44017.125 | 0 | 7.3241 | 39.95
2020-07-05 03:30 | 44017.1458 | 0 | 7.4024 | 39.95
2020-07-05 04:00 | 44017.1667 | 0 | 7.6331 | 39.95
2020-07-05 04:30 | 44017.1875 | 0 | 8.2144 | 39.95
2020-07-05 05:00 | 44017.2083 | 0 | 8.9258 | 39.95
2020-07-05 05:30 | 44017.2292 | 0 | 9.9536 | 39.95
2020-07-05 06:00 | 44017.25 | 0 | 11.2338 | 39.95
2020-07-05 06:30 | 44017.2708 | 0 | 12.4864 | 39.95
2020-07-05 07:00 | 44017.2917 | 0 | 13.8136 | 39.95
2020-07-05 07:30 | 44017.3125 | 0 | 14.073 | 39.95
2020-07-05 08:00 | 44017.3333 | 0 | 13.7914 | 39.95
2020-07-05 08:30 | 44017.3542 | 0 | 13.2596 | 39.95
2020-07-05 09:00 | 44017.375 | 0 | 12.2686 | 39.95
2020-07-05 09:30 | 44017.3958 | 0 | 11.2676 | 39.95
2020-07-05 10:00 | 44017.4167 | 0 | 10.6327 | 39.95
2020-07-05 10:30 | 44017.4375 | 0 | 10.2881 | 39.95
2020-07-05 11:00 | 44017.4583 | 0 | 9.9156 | 39.95
2020-07-05 11:30 | 44017.4792 | 0 | 9.5689 | 39.95
2020-07-05 12:00 | 44017.5 | 0 | 9.4118 | 39.95
2020-07-05 12:30 | 44017.5208 | 0 | 9.3197 | 39.95
2020-07-05 13:00 | 44017.5417 | 0 | 9.3788 | 39.95
2020-07-05 13:30 | 44017.5625 | 0 | 9.5826 | 39.95
2020-07-05 14:00 | 44017.5833 | 0 | 9.8627 | 39.95
2020-07-05 14:30 | 44017.6042 | 0 | 10.2958 | 39.95
2020-07-05 15:00 | 44017.625 | 0 | 10.9395 | 39.95
2020-07-05 15:30 | 44017.6458 | 0 | 11.1375 | 39.95
2020-07-05 16:00 | 44017.6667 | 0 | 11.5036 | 39.95
2020-07-05 16:30 | 44017.6875 | 0 | 12.3595 | 39.95
2020-07-05 17:00 | 44017.7083 | 0 | 13.3444 | 39.95
2020-07-05 17:30 | 44017.7292 | 0 | 14.5483 | 39.95
2020-07-05 18:00 | 44017.75 | 0 | 15.0382 | 39.95
2020-07-05 18:30 | 44017.7708 | 0 | 15.162 | 39.95
2020-07-05 19:00 | 44017.7917 | 0 | 14.8402 | 39.95
2020-07-05 19:30 | 44017.8125 | 0 | 14.504 | 39.95
2020-07-05 20:00 | 44017.8333 | 0 | 14.4635 | 39.95
2020-07-05 20:30 | 44017.8542 | 0 | 13.7831 | 39.95
2020-07-05 21:00 | 44017.875 | 0 | 13.0622 | 39.95
2020-07-05 21:30 | 44017.8958 | 0 | 12.3578 | 39.95
2020-07-05 22:00 | 44017.9167 | 0 | 11.8532 | 39.95
2020-07-05 22:30 | 44017.9375 | 0 | 11.0773 | 39.95
2020-07-05 23:00 | 44017.9583 | 0 | 10.1852 | 39.95
2020-07-05 23:30 | 44017.9792 | 0 | 9.4848 | 39.95
2020-07-06 | 44018 | 0 | 8.8685 | 39.95
2020-07-06 00:30 | 44018.0208 | 0 | 8.3921 | 39.95
2020-07-06 01:00 | 44018.0417 | 0 | 8.1082 | 39.95
2020-07-06 01:30 | 44018.0625 | 0 | 7.923 | 39.95
2020-07-06 02:00 | 44018.0833 | 0 | 7.8718 | 39.95
2020-07-06 02:30 | 44018.1042 | 0 | 7.6759 | 39.95
2020-07-06 03:00 | 44018.125 | 0 | 7.7211 | 39.95
2020-07-06 03:30 | 44018.1458 | 0 | 7.8684 | 39.95
2020-07-06 04:00 | 44018.1667 | 0 | 8.0445 | 39.95
2020-07-06 04:30 | 44018.1875 | 0 | 8.6329 | 39.95
2020-07-06 05:00 | 44018.2083 | 0 | 9.4685 | 39.95
2020-07-06 05:30 | 44018.2292 | 0 | 10.2211 | 39.95
2020-07-06 06:00 | 44018.25 | 0 | 11.6685 | 39.95
2020-07-06 06:30 | 44018.2708 | 0 | 13.0842 | 39.95
2020-07-06 07:00 | 44018.2917 | 0 | 14.1288 | 39.95
2020-07-06 07:30 | 44018.3125 | 0 | 14.2892 | 39.95
2020-07-06 08:00 | 44018.3333 | 0 | 13.7512 | 39.95
2020-07-06 08:30 | 44018.3542 | 0 | 12.9698 | 39.95
2020-07-06 09:00 | 44018.375 | 0 | 12.1266 | 39.95
2020-07-06 09:30 | 44018.3958 | 0 | 11.2395 | 39.95
2020-07-06 10:00 | 44018.4167 | 0 | 10.617 | 39.95
2020-07-06 10:30 | 44018.4375 | 0 | 10.1734 | 39.95
2020-07-06 11:00 | 44018.4583 | 0 | 9.7431 | 39.95
2020-07-06 11:30 | 44018.4792 | 0 | 9.4443 | 39.95
2020-07-06 12:00 | 44018.5 | 0 | 9.2739 | 39.95
2020-07-06 12:30 | 44018.5208 | 0 | 9.2123 | 39.95
2020-07-06 13:00 | 44018.5417 | 0 | 9.3821 | 39.95
2020-07-06 13:30 | 44018.5625 | 0 | 9.4648 | 39.95
2020-07-06 14:00 | 44018.5833 | 0 | 9.7649 | 39.95
2020-07-06 14:30 | 44018.6042 | 0 | 10.1923 | 39.95
2020-07-06 15:00 | 44018.625 | 0 | 10.5575 | 39.95
2020-07-06 15:30 | 44018.6458 | 0 | 10.8445 | 39.95
2020-07-06 16:00 | 44018.6667 | 0 | 11.5651 | 39.95
2020-07-06 16:30 | 44018.6875 | 0 | 12.4628 | 39.95
2020-07-06 17:00 | 44018.7083 | 0 | 13.1808 | 39.95
2020-07-06 17:30 | 44018.7292 | 0 | 14.2087 | 39.95
2020-07-06 18:00 | 44018.75 | 0 | 14.4479 | 39.95
2020-07-06 18:30 | 44018.7708 | 0 | 14.7783 | 39.95
2020-07-06 19:00 | 44018.7917 | 0 | 14.6705 | 39.95
2020-07-06 19:30 | 44018.8125 | 0 | 14.1622 | 39.95
2020-07-06 20:00 | 44018.8333 | 0 | 14.0064 | 39.95
2020-07-06 20:30 | 44018.8542 | 0 | 13.4344 | 39.95
2020-07-06 21:00 | 44018.875 | 0 | 12.7405 | 39.95
2020-07-06 21:30 | 44018.8958 | 0 | 12.1533 | 39.95
2020-07-06 22:00 | 44018.9167 | 0 | 11.3499 | 39.95
2020-07-06 22:30 | 44018.9375 | 0 | 10.4974 | 39.95
2020-07-06 23:00 | 44018.9583 | 0 | 9.7204 | 39.95
2020-07-06 23:30 | 44018.9792 | 0 | 9.1797 | 39.95
2020-07-07 | 44019 | 0 | 8.5855 | 39.95
2020-07-07 00:30 | 44019.0208 | 0 | 8.1692 | 39.95
2020-07-07 01:00 | 44019.0417 | 0 | 7.9573 | 39.95
2020-07-07 01:30 | 44019.0625 | 0 | 7.7355 | 39.95
2020-07-07 02:00 | 44019.0833 | 0 | 7.7467 | 39.95
2020-07-07 02:30 | 44019.1042 | 0 | 7.6256 | 39.95
2020-07-07 03:00 | 44019.125 | 0 | 7.5786 | 39.95
2020-07-07 03:30 | 44019.1458 | 0 | 7.6788 | 39.95
2020-07-07 04:00 | 44019.1667 | 0 | 7.9478 | 39.95
2020-07-07 04:30 | 44019.1875 | 0 | 8.4277 | 39.95
2020-07-07 05:00 | 44019.2083 | 0 | 9.1425 | 39.95
2020-07-07 05:30 | 44019.2292 | 0 | 9.8074 | 39.95
2020-07-07 06:00 | 44019.25 | 0 | 11.1422 | 39.95
2020-07-07 06:30 | 44019.2708 | 0 | 12.132 | 39.95
2020-07-07 07:00 | 44019.2917 | 0 | 13.1516 | 39.95
2020-07-07 07:30 | 44019.3125 | 0 | 13.0131 | 39.95
2020-07-07 08:00 | 44019.3333 | 0 | 12.6621 | 39.95
2020-07-07 08:30 | 44019.3542 | 0 | 11.913 | 39.95
2020-07-07 09:00 | 44019.375 | 0 | 11.3036 | 39.95
2020-07-07 09:30 | 44019.3958 | 0 | 10.735 | 39.95
2020-07-07 10:00 | 44019.4167 | 0 | 10.0784 | 39.95
2020-07-07 10:30 | 44019.4375 | 0 | 9.6189 | 39.95
2020-07-07 11:00 | 44019.4583 | 0 | 9.3338 | 39.95
2020-07-07 11:30 | 44019.4792 | 0 | 9.1894 | 39.95
2020-07-07 12:00 | 44019.5 | 0 | 8.8619 | 39.95
2020-07-07 12:30 | 44019.5208 | 0 | 8.8544 | 39.95
2020-07-07 13:00 | 44019.5417 | 0 | 9.6092 | 39.95
2020-07-07 13:30 | 44019.5625 | 0 | 10.2706 | 39.95
2020-07-07 14:00 | 44019.5833 | 0 | 10.0827 | 39.95
2020-07-07 14:30 | 44019.6042 | 0 | 10.2624 | 39.95
2020-07-07 15:00 | 44019.625 | 0 | 10.2865 | 39.95
2020-07-07 15:30 | 44019.6458 | 0 | 11.234 | 39.95
2020-07-07 16:00 | 44019.6667 | 0 | 11.5944 | 39.95
2020-07-07 16:30 | 44019.6875 | 0 | 12.3231 | 39.95
2020-07-07 17:00 | 44019.7083 | 0 | 13.1048 | 39.95
2020-07-07 17:30 | 44019.7292 | 0 | 14.1166 | 39.95
2020-07-07 18:00 | 44019.75 | 0 | 14.2673 | 39.95
2020-07-07 18:30 | 44019.7708 | 0 | 14.5995 | 39.95
2020-07-07 19:00 | 44019.7917 | 0 | 14.2615 | 39.95
2020-07-07 19:30 | 44019.8125 | 0 | 13.883 | 39.95
2020-07-07 20:00 | 44019.8333 | 0 | 13.7314 | 39.95
2020-07-07 20:30 | 44019.8542 | 0 | 13.1004 | 39.95
2020-07-07 21:00 | 44019.875 | 0 | 12.4186 | 39.95
2020-07-07 21:30 | 44019.8958 | 0 | 11.8186 | 39.95
2020-07-07 22:00 | 44019.9167 | 0 | 11.2343 | 39.95
2020-07-07 22:30 | 44019.9375 | 0 | 10.6653 | 39.95
2020-07-07 23:00 | 44019.9583 | 0 | 10.0118 | 39.95
2020-07-07 23:30 | 44019.9792 | 0 | 9.3525 | 39.95
2020-07-08 | 44020 | 0 | 8.6449 | 39.95
2020-07-08 00:30 | 44020.0208 | 0 | 8.0482 | 39.95
2020-07-08 01:00 | 44020.0417 | 0 | 7.7852 | 39.95
2020-07-08 01:30 | 44020.0625 | 0 | 7.6974 | 39.95
2020-07-08 02:00 | 44020.0833 | 0 | 7.6008 | 39.95
2020-07-08 02:30 | 44020.1042 | 0 | 7.5196 | 39.95
2020-07-08 03:00 | 44020.125 | 0 | 7.5327 | 39.95
2020-07-08 03:30 | 44020.1458 | 0 | 7.5281 | 39.95
2020-07-08 04:00 | 44020.1667 | 0 | 7.7667 | 39.95
2020-07-08 04:30 | 44020.1875 | 0 | 8.1432 | 39.95
2020-07-08 05:00 | 44020.2083 | 0 | 8.9269 | 39.95
2020-07-08 05:30 | 44020.2292 | 0 | 9.6962 | 39.95
2020-07-08 06:00 | 44020.25 | 0 | 10.6923 | 39.95
2020-07-08 06:30 | 44020.2708 | 0 | 11.6475 | 39.95
2020-07-08 07:00 | 44020.2917 | 0 | 12.3764 | 39.95
2020-07-08 07:30 | 44020.3125 | 0 | 12.7681 | 39.95
2020-07-08 08:00 | 44020.3333 | 0 | 13.003 | 39.95
2020-07-08 08:30 | 44020.3542 | 0 | 12.8342 | 39.95
2020-07-08 09:00 | 44020.375 | 0 | 12.6849 | 39.95
2020-07-08 09:30 | 44020.3958 | 0 | 12.5076 | 39.95
2020-07-08 10:00 | 44020.4167 | 0 | 12.4711 | 39.95
2020-07-08 10:30 | 44020.4375 | 0 | 12.6683 | 39.95
2020-07-08 11:00 | 44020.4583 | 0 | 11.7527 | 39.95
2020-07-08 11:30 | 44020.4792 | 0 | 11.6456 | 39.95
2020-07-08 12:00 | 44020.5 | 0 | 11.1703 | 39.95
2020-07-08 12:30 | 44020.5208 | 0 | 12.0356 | 39.95
2020-07-08 13:00 | 44020.5417 | 0 | 12.3048 | 39.95
2020-07-08 13:30 | 44020.5625 | 0 | 11.5585 | 39.95
2020-07-08 14:00 | 44020.5833 | 0 | 11.6728 | 39.95
2020-07-08 14:30 | 44020.6042 | 0 | 12.025 | 39.95
2020-07-08 15:00 | 44020.625 | 0 | 12.559 | 39.95
2020-07-08 15:30 | 44020.6458 | 0 | 12.0857 | 39.95
2020-07-08 16:00 | 44020.6667 | 0 | 12.5329 | 39.95
2020-07-08 16:30 | 44020.6875 | 0 | 13.2348 | 39.95
2020-07-08 17:00 | 44020.7083 | 0 | 14.0588 | 39.95
2020-07-08 17:30 | 44020.7292 | 0 | 14.8889 | 39.95
2020-07-08 18:00 | 44020.75 | 0 | 14.8349 | 39.95
2020-07-08 18:30 | 44020.7708 | 0 | 14.9454 | 39.95
2020-07-08 19:00 | 44020.7917 | 0 | 14.5925 | 39.95
2020-07-08 19:30 | 44020.8125 | 0 | 14.2692 | 39.95
2020-07-08 20:00 | 44020.8333 | 0 | 14.3709 | 39.95
2020-07-08 20:30 | 44020.8542 | 0 | 13.3831 | 39.95
2020-07-08 21:00 | 44020.875 | 0 | 12.9983 | 39.95
2020-07-08 21:30 | 44020.8958 | 0 | 12.2239 | 39.95
2020-07-08 22:00 | 44020.9167 | 0 | 11.5901 | 39.95
2020-07-08 22:30 | 44020.9375 | 0 | 10.7038 | 39.95
2020-07-08 23:00 | 44020.9583 | 0 | 10.0543 | 39.95
2020-07-08 23:30 | 44020.9792 | 0 | 9.3154 | 39.95
2020-07-09 | 44021 | 0 | 8.6642 | 39.95
2020-07-09 00:30 | 44021.0208 | 0 | 8.0029 | 39.95
2020-07-09 01:00 | 44021.0417 | 0 | 7.8132 | 39.95
2020-07-09 01:30 | 44021.0625 | 0 | 7.5721 | 39.95
2020-07-09 02:00 | 44021.0833 | 0 | 7.5633 | 39.95
2020-07-09 02:30 | 44021.1042 | 0 | 7.6057 | 39.95
2020-07-09 03:00 | 44021.125 | 0 | 7.5652 | 39.95
2020-07-09 03:30 | 44021.1458 | 0 | 7.6792 | 39.95
2020-07-09 04:00 | 44021.1667 | 0 | 7.8123 | 39.95
2020-07-09 04:30 | 44021.1875 | 0 | 8.3235 | 39.95
2020-07-09 05:00 | 44021.2083 | 0 | 8.9389 | 39.95
2020-07-09 05:30 | 44021.2292 | 0 | 9.7841 | 39.95
2020-07-09 06:00 | 44021.25 | 0 | 10.8385 | 39.95
2020-07-09 06:30 | 44021.2708 | 0 | 11.6535 | 39.95
2020-07-09 07:00 | 44021.2917 | 0 | 12.4796 | 39.95
2020-07-09 07:30 | 44021.3125 | 0 | 12.6868 | 39.95
2020-07-09 08:00 | 44021.3333 | 0 | 12.199 | 39.95
2020-07-09 08:30 | 44021.3542 | 0 | 11.8598 | 39.95
2020-07-09 09:00 | 44021.375 | 0 | 11.1021 | 39.95
2020-07-09 09:30 | 44021.3958 | 0 | 10.8443 | 39.95
2020-07-09 10:00 | 44021.4167 | 0 | 10.8119 | 39.95
2020-07-09 10:30 | 44021.4375 | 0 | 10.4017 | 39.95
2020-07-09 11:00 | 44021.4583 | 0 | 11.0511 | 39.95
2020-07-09 11:30 | 44021.4792 | 0 | 10.4379 | 39.95
2020-07-09 12:00 | 44021.5 | 0 | 10.0941 | 39.95
2020-07-09 12:30 | 44021.5208 | 0 | 10.4162 | 39.95
2020-07-09 13:00 | 44021.5417 | 0 | 9.5403 | 39.95
2020-07-09 13:30 | 44021.5625 | 0 | 9.7047 | 39.95
2020-07-09 14:00 | 44021.5833 | 0 | 9.8476 | 39.95
2020-07-09 14:30 | 44021.6042 | 0 | 9.7657 | 39.95
2020-07-09 15:00 | 44021.625 | 0 | 10.5738 | 39.95
2020-07-09 15:30 | 44021.6458 | 0 | 11.0603 | 39.95
2020-07-09 16:00 | 44021.6667 | 0 | 11.5588 | 39.95
2020-07-09 16:30 | 44021.6875 | 0 | 11.9362 | 39.95
2020-07-09 17:00 | 44021.7083 | 0 | 12.6154 | 39.95
2020-07-09 17:30 | 44021.7292 | 0 | 13.3332 | 39.95
2020-07-09 18:00 | 44021.75 | 0 | 13.5111 | 39.95
2020-07-09 18:30 | 44021.7708 | 0 | 13.5219 | 39.95
2020-07-09 19:00 | 44021.7917 | 0 | 13.4326 | 39.95
2020-07-09 19:30 | 44021.8125 | 0 | 13.2944 | 39.95
2020-07-09 20:00 | 44021.8333 | 0 | 13.2004 | 39.95
2020-07-09 20:30 | 44021.8542 | 0 | 12.6497 | 39.95
2020-07-09 21:00 | 44021.875 | 0 | 12.0336 | 39.95
2020-07-09 21:30 | 44021.8958 | 0 | 11.568 | 39.95
2020-07-09 22:00 | 44021.9167 | 0 | 11.2061 | 39.95
2020-07-09 22:30 | 44021.9375 | 0 | 10.4745 | 39.95
2020-07-09 23:00 | 44021.9583 | 0 | 9.8523 | 39.95
2020-07-09 23:30 | 44021.9792 | 0 | 9.2096 | 39.95
2020-07-10 | 44022 | 0 | 8.7915 | 39.95
2020-07-10 00:30 | 44022.0208 | 0 | 8.1753 | 39.95
2020-07-10 01:00 | 44022.0417 | 0 | 7.9276 | 39.95
2020-07-10 01:30 | 44022.0625 | 0 | 7.7806 | 39.95
2020-07-10 02:00 | 44022.0833 | 0 | 7.6985 | 39.95
2020-07-10 02:30 | 44022.1042 | 0 | 7.6271 | 39.95
2020-07-10 03:00 | 44022.125 | 0 | 7.5228 | 39.95
2020-07-10 03:30 | 44022.1458 | 0 | 7.4446 | 39.95
2020-07-10 04:00 | 44022.1667 | 0 | 7.4936 | 39.95
2020-07-10 04:30 | 44022.1875 | 0 | 7.6248 | 39.95
2020-07-10 05:00 | 44022.2083 | 0 | 7.782 | 39.95
2020-07-10 05:30 | 44022.2292 | 0 | 7.9571 | 39.95
2020-07-10 06:00 | 44022.25 | 0 | 8.3046 | 39.95
2020-07-10 06:30 | 44022.2708 | 0 | 8.8941 | 39.95
2020-07-10 07:00 | 44022.2917 | 0 | 9.4572 | 39.95
2020-07-10 07:30 | 44022.3125 | 0 | 9.5947 | 39.95
2020-07-10 08:00 | 44022.3333 | 0 | 10.1607 | 39.95
2020-07-10 08:30 | 44022.3542 | 0 | 9.8736 | 39.95
2020-07-10 09:00 | 44022.375 | 0 | 9.2136 | 39.95
2020-07-10 09:30 | 44022.3958 | 0 | 8.7072 | 39.95
2020-07-10 10:00 | 44022.4167 | 0 | 8.1986 | 39.95
2020-07-10 10:30 | 44022.4375 | 0 | 7.9793 | 39.95
2020-07-10 11:00 | 44022.4583 | 0 | 8.5034 | 39.95
2020-07-10 11:30 | 44022.4792 | 0 | 8.6242 | 39.95
2020-07-10 12:00 | 44022.5 | 0 | 8.6089 | 39.95
2020-07-10 12:30 | 44022.5208 | 0 | 8.7711 | 39.95
2020-07-10 13:00 | 44022.5417 | 0 | 7.8813 | 39.95
2020-07-10 13:30 | 44022.5625 | 0 | 7.5349 | 39.95
2020-07-10 14:00 | 44022.5833 | 0 | 7.9028 | 39.95
2020-07-10 14:30 | 44022.6042 | 0 | 8.3207 | 39.95
2020-07-10 15:00 | 44022.625 | 0 | 8.4194 | 39.95
2020-07-10 15:30 | 44022.6458 | 0 | 9.0115 | 39.95
2020-07-10 16:00 | 44022.6667 | 0 | 9.4065 | 39.95
2020-07-10 16:30 | 44022.6875 | 0 | 10.2718 | 39.95
2020-07-10 17:00 | 44022.7083 | 0 | 10.8474 | 39.95
2020-07-10 17:30 | 44022.7292 | 0 | 11.5238 | 39.95
2020-07-10 18:00 | 44022.75 | 0 | 11.7176 | 39.95
2020-07-10 18:30 | 44022.7708 | 0 | 11.8093 | 39.95
2020-07-10 19:00 | 44022.7917 | 0 | 11.4732 | 39.95
2020-07-10 19:30 | 44022.8125 | 0 | 11.0965 | 39.95
2020-07-10 20:00 | 44022.8333 | 0 | 11.0923 | 39.95
2020-07-10 20:30 | 44022.8542 | 0 | 10.5995 | 39.95
2020-07-10 21:00 | 44022.875 | 0 | 10.172 | 39.95
2020-07-10 21:30 | 44022.8958 | 0 | 9.8892 | 39.95
2020-07-10 22:00 | 44022.9167 | 0 | 9.4468 | 39.95
2020-07-10 22:30 | 44022.9375 | 0 | 8.8516 | 39.95
2020-07-10 23:00 | 44022.9583 | 0 | 8.4705 | 39.95
2020-07-10 23:30 | 44022.9792 | 0 | 8.1351 | 39.95
2020-07-11 | 44023 | 0 | 7.6217 | 39.95
2020-07-11 00:30 | 44023.0208 | 0 | 7.3492 | 39.95
2020-07-11 01:00 | 44023.0417 | 0 | 7.1408 | 39.95
2020-07-11 01:30 | 44023.0625 | 0 | 6.9631 | 39.95
2020-07-11 02:00 | 44023.0833 | 0 | 6.9264 | 39.95
2020-07-11 02:30 | 44023.1042 | 0 | 6.8142 | 39.95
2020-07-11 03:00 | 44023.125 | 0 | 6.7528 | 39.95
2020-07-11 03:30 | 44023.1458 | 0 | 6.7067 | 39.95
2020-07-11 04:00 | 44023.1667 | 0 | 6.6547 | 39.95
2020-07-11 04:30 | 44023.1875 | 0 | 6.7807 | 39.95
2020-07-11 05:00 | 44023.2083 | 0 | 6.8487 | 39.95
2020-07-11 05:30 | 44023.2292 | 0 | 7.0832 | 39.95
2020-07-11 06:00 | 44023.25 | 0 | 7.4654 | 39.95
2020-07-11 06:30 | 44023.2708 | 0 | 7.5709 | 39.95
2020-07-11 07:00 | 44023.2917 | 0 | 7.9761 | 39.95
2020-07-11 07:30 | 44023.3125 | 0 | 7.9458 | 39.95
2020-07-11 08:00 | 44023.3333 | 0 | 8.406 | 39.95
2020-07-11 08:30 | 44023.3542 | 0 | 8.1473 | 39.95
2020-07-11 09:00 | 44023.375 | 0 | 7.8401 | 39.95
2020-07-11 09:30 | 44023.3958 | 0 | 8.1752 | 39.95
2020-07-11 10:00 | 44023.4167 | 0 | 7.938 | 39.95
2020-07-11 10:30 | 44023.4375 | 0 | 7.3464 | 39.95
2020-07-11 11:00 | 44023.4583 | 0 | 7.1834 | 39.95
2020-07-11 11:30 | 44023.4792 | 0 | 8.9422 | 39.95
2020-07-11 12:00 | 44023.5 | 0 | 9.1719 | 39.95
2020-07-11 12:30 | 44023.5208 | 0 | 9.4888 | 39.95
2020-07-11 13:00 | 44023.5417 | 0 | 9.2716 | 39.95
2020-07-11 13:30 | 44023.5625 | 0 | 9.5102 | 39.95
2020-07-11 14:00 | 44023.5833 | 0 | 9.858 | 39.95
2020-07-11 14:30 | 44023.6042 | 0 | 9.9889 | 39.95
2020-07-11 15:00 | 44023.625 | 0 | 10.0613 | 39.95
2020-07-11 15:30 | 44023.6458 | 0 | 10.3313 | 39.95
2020-07-11 16:00 | 44023.6667 | 0 | 10.8844 | 39.95
2020-07-11 16:30 | 44023.6875 | 0 | 11.7952 | 39.95
2020-07-11 17:00 | 44023.7083 | 0 | 12.3526 | 39.95
2020-07-11 17:30 | 44023.7292 | 0 | 12.6971 | 39.95
2020-07-11 18:00 | 44023.75 | 0 | 12.6644 | 39.95
2020-07-11 18:30 | 44023.7708 | 0 | 12.6849 | 39.95
2020-07-11 19:00 | 44023.7917 | 0 | 12.3172 | 39.95
2020-07-11 19:30 | 44023.8125 | 0 | 11.8051 | 39.95
2020-07-11 20:00 | 44023.8333 | 0 | 11.6501 | 39.95
2020-07-11 20:30 | 44023.8542 | 0 | 10.9695 | 39.95
2020-07-11 21:00 | 44023.875 | 0 | 10.3418 | 39.95
2020-07-11 21:30 | 44023.8958 | 0 | 9.9102 | 39.95
2020-07-11 22:00 | 44023.9167 | 0 | 9.4857 | 39.95
2020-07-11 22:30 | 44023.9375 | 0 | 8.8702 | 39.95
2020-07-11 23:00 | 44023.9583 | 0 | 8.2853 | 39.95
2020-07-11 23:30 | 44023.9792 | 0 | 7.9089 | 39.95
2020-07-12 | 44024 | 0 | 7.5042 | 39.95
2020-07-12 00:30 | 44024.0208 | 0 | 7.3381 | 39.95
2020-07-12 01:00 | 44024.0417 | 0 | 7.1906 | 39.95
2020-07-12 01:30 | 44024.0625 | 0 | 6.9221 | 39.95
2020-07-12 02:00 | 44024.0833 | 0 | 6.9051 | 39.95
2020-07-12 02:30 | 44024.1042 | 0 | 6.9216 | 39.95
2020-07-12 03:00 | 44024.125 | 0 | 6.9632 | 39.95
2020-07-12 03:30 | 44024.1458 | 0 | 6.9566 | 39.95
2020-07-12 04:00 | 44024.1667 | 0 | 7.3069 | 39.95
2020-07-12 04:30 | 44024.1875 | 0 | 7.6844 | 39.95
2020-07-12 05:00 | 44024.2083 | 0 | 8.3988 | 39.95
2020-07-12 05:30 | 44024.2292 | 0 | 9.239 | 39.95
2020-07-12 06:00 | 44024.25 | 0 | 10.3525 | 39.95
2020-07-12 06:30 | 44024.2708 | 0 | 11.5668 | 39.95
2020-07-12 07:00 | 44024.2917 | 0 | 12.7109 | 39.95
2020-07-12 07:30 | 44024.3125 | 0 | 13.1181 | 39.95
2020-07-12 08:00 | 44024.3333 | 0 | 12.9269 | 39.95
2020-07-12 08:30 | 44024.3542 | 0 | 13.1189 | 39.95
2020-07-12 09:00 | 44024.375 | 0 | 12.5538 | 39.95
2020-07-12 09:30 | 44024.3958 | 0 | 12.237 | 39.95
2020-07-12 10:00 | 44024.4167 | 0 | 11.1147 | 39.95
2020-07-12 10:30 | 44024.4375 | 0 | 10.606 | 39.95
2020-07-12 11:00 | 44024.4583 | 0 | 9.9074 | 39.95
2020-07-12 11:30 | 44024.4792 | 0 | 9.2425 | 39.95
2020-07-12 12:00 | 44024.5 | 0 | 9.5128 | 39.95
2020-07-12 12:30 | 44024.5208 | 0 | 9.563 | 39.95
2020-07-12 13:00 | 44024.5417 | 0 | 10.4697 | 39.95
2020-07-12 13:30 | 44024.5625 | 0 | 9.6775 | 39.95
2020-07-12 14:00 | 44024.5833 | 0 | 9.5524 | 39.95
2020-07-12 14:30 | 44024.6042 | 0 | 9.8413 | 39.95
2020-07-12 15:00 | 44024.625 | 0 | 10.4523 | 39.95
2020-07-12 15:30 | 44024.6458 | 0 | 10.8212 | 39.95
2020-07-12 16:00 | 44024.6667 | 0 | 11.5145 | 39.95
2020-07-12 16:30 | 44024.6875 | 0 | 12.342 | 39.95
2020-07-12 17:00 | 44024.7083 | 0 | 13.4127 | 39.95
2020-07-12 17:30 | 44024.7292 | 0 | 14.5613 | 39.95
2020-07-12 18:00 | 44024.75 | 0 | 15.1264 | 39.95
2020-07-12 18:30 | 44024.7708 | 0 | 15.2865 | 39.95
2020-07-12 19:00 | 44024.7917 | 0 | 15.0582 | 39.95
2020-07-12 19:30 | 44024.8125 | 0 | 14.8266 | 39.95
2020-07-12 20:00 | 44024.8333 | 0 | 14.6701 | 39.95
2020-07-12 20:30 | 44024.8542 | 0 | 13.9808 | 39.95
2020-07-12 21:00 | 44024.875 | 0 | 13.2521 | 39.95
2020-07-12 21:30 | 44024.8958 | 0 | 12.6271 | 39.95
2020-07-12 22:00 | 44024.9167 | 0 | 11.9453 | 39.95
2020-07-12 22:30 | 44024.9375 | 0 | 10.771 | 39.95
2020-07-12 23:00 | 44024.9583 | 0 | 10.1042 | 39.95
2020-07-12 23:30 | 44024.9792 | 0 | 9.3099 | 39.95
2020-07-13 | 44025 | 0 | 8.781 | 39.95
2020-07-13 00:30 | 44025.0208 | 0 | 8.2564 | 39.95
2020-07-13 01:00 | 44025.0417 | 0 | 7.9988 | 39.95
2020-07-13 01:30 | 44025.0625 | 0 | 7.8932 | 39.95
2020-07-13 02:00 | 44025.0833 | 0 | 7.6767 | 39.95
2020-07-13 02:30 | 44025.1042 | 0 | 7.561 | 39.95
2020-07-13 03:00 | 44025.125 | 0 | 7.689 | 39.95
2020-07-13 03:30 | 44025.1458 | 0 | 7.842 | 39.95
2020-07-13 04:00 | 44025.1667 | 0 | 7.9096 | 39.95
2020-07-13 04:30 | 44025.1875 | 0 | 8.4132 | 39.95
2020-07-13 05:00 | 44025.2083 | 0 | 9.5279 | 39.95
2020-07-13 05:30 | 44025.2292 | 0 | 10.4258 | 39.95
2020-07-13 06:00 | 44025.25 | 0 | 12.221 | 39.95
2020-07-13 06:30 | 44025.2708 | 0 | 14.0459 | 39.95
2020-07-13 07:00 | 44025.2917 | 0 | 15.289 | 39.95
2020-07-13 07:30 | 44025.3125 | 0 | 15.1393 | 39.95
2020-07-13 08:00 | 44025.3333 | 0 | 14.313 | 39.95
2020-07-13 08:30 | 44025.3542 | 0 | 13.2389 | 39.95
2020-07-13 09:00 | 44025.375 | 0 | 12.3951 | 39.95
2020-07-13 09:30 | 44025.3958 | 0 | 11.4228 | 39.95
2020-07-13 10:00 | 44025.4167 | 0 | 10.9042 | 39.95
2020-07-13 10:30 | 44025.4375 | 0 | 10.5796 | 39.95
2020-07-13 11:00 | 44025.4583 | 0 | 10.1571 | 39.95
2020-07-13 11:30 | 44025.4792 | 0 | 9.9468 | 39.95
2020-07-13 12:00 | 44025.5 | 0 | 9.7286 | 39.95
2020-07-13 12:30 | 44025.5208 | 0 | 9.6128 | 39.95
2020-07-13 13:00 | 44025.5417 | 0 | 9.6854 | 39.95
2020-07-13 13:30 | 44025.5625 | 0 | 9.7367 | 39.95
2020-07-13 14:00 | 44025.5833 | 0 | 10.1433 | 39.95
2020-07-13 14:30 | 44025.6042 | 0 | 10.4852 | 39.95
2020-07-13 15:00 | 44025.625 | 0 | 10.9159 | 39.95
2020-07-13 15:30 | 44025.6458 | 0 | 11.5079 | 39.95
2020-07-13 16:00 | 44025.6667 | 0 | 12.4116 | 39.95
2020-07-13 16:30 | 44025.6875 | 0 | 13.6575 | 39.95
2020-07-13 17:00 | 44025.7083 | 0 | 15.4726 | 39.95
2020-07-13 17:30 | 44025.7292 | 0 | 17.1558 | 39.95
2020-07-13 18:00 | 44025.75 | 0 | 17.8153 | 39.95
2020-07-13 18:30 | 44025.7708 | 0 | 18.2471 | 39.95
2020-07-13 19:00 | 44025.7917 | 0 | 18.1243 | 39.95
2020-07-13 19:30 | 44025.8125 | 0 | 17.6722 | 39.95
2020-07-13 20:00 | 44025.8333 | 0 | 17.2401 | 39.95
2020-07-13 20:30 | 44025.8542 | 0 | 16.2978 | 39.95
2020-07-13 21:00 | 44025.875 | 0 | 15.3728 | 39.95
2020-07-13 21:30 | 44025.8958 | 0 | 14.4204 | 39.95
2020-07-13 22:00 | 44025.9167 | 0 | 13.3475 | 39.95
2020-07-13 22:30 | 44025.9375 | 0 | 11.7698 | 39.95
2020-07-13 23:00 | 44025.9583 | 0 | 10.6406 | 39.95
2020-07-13 23:30 | 44025.9792 | 0 | 9.9374 | 39.95
2020-07-14 | 44026 | 0 | 9.3546 | 39.95
2020-07-14 00:30 | 44026.0208 | 0 | 8.7585 | 39.95
2020-07-14 01:00 | 44026.0417 | 0 | 8.5092 | 39.95
2020-07-14 01:30 | 44026.0625 | 0 | 8.3714 | 39.95
2020-07-14 02:00 | 44026.0833 | 0 | 8.19 | 39.95
2020-07-14 02:30 | 44026.1042 | 0 | 8.0979 | 39.95
2020-07-14 03:00 | 44026.125 | 0 | 8.1476 | 39.95
2020-07-14 03:30 | 44026.1458 | 0 | 8.1426 | 39.95
2020-07-14 04:00 | 44026.1667 | 0 | 8.4557 | 39.95
2020-07-14 04:30 | 44026.1875 | 0 | 8.9235 | 39.95
2020-07-14 05:00 | 44026.2083 | 0 | 9.9442 | 39.95
2020-07-14 05:30 | 44026.2292 | 0 | 11.0702 | 39.95
2020-07-14 06:00 | 44026.25 | 0 | 12.764 | 39.95
2020-07-14 06:30 | 44026.2708 | 0 | 14.3294 | 39.95
2020-07-14 07:00 | 44026.2917 | 0 | 15.4824 | 39.95
2020-07-14 07:30 | 44026.3125 | 0 | 15.1898 | 39.95
2020-07-14 08:00 | 44026.3333 | 0 | 14.3679 | 39.95
2020-07-14 08:30 | 44026.3542 | 0 | 13.1932 | 39.95
2020-07-14 09:00 | 44026.375 | 0 | 12.0824 | 39.95
2020-07-14 09:30 | 44026.3958 | 0 | 11.1741 | 39.95
2020-07-14 10:00 | 44026.4167 | 0 | 10.6171 | 39.95
2020-07-14 10:30 | 44026.4375 | 0 | 10.1516 | 39.95
2020-07-14 11:00 | 44026.4583 | 0 | 9.6137 | 39.95
2020-07-14 11:30 | 44026.4792 | 0 | 9.4783 | 39.95
2020-07-14 12:00 | 44026.5 | 0 | 9.3355 | 39.95
2020-07-14 12:30 | 44026.5208 | 0 | 9.1522 | 39.95
2020-07-14 13:00 | 44026.5417 | 0 | 9.2235 | 39.95
2020-07-14 13:30 | 44026.5625 | 0 | 9.5743 | 39.95
2020-07-14 14:00 | 44026.5833 | 0 | 9.7654 | 39.95
2020-07-14 14:30 | 44026.6042 | 0 | 10.0025 | 39.95
2020-07-14 15:00 | 44026.625 | 0 | 10.392 | 39.95
2020-07-14 15:30 | 44026.6458 | 0 | 10.9776 | 39.95
2020-07-14 16:00 | 44026.6667 | 0 | 11.6595 | 39.95
2020-07-14 16:30 | 44026.6875 | 0 | 12.4759 | 39.95
2020-07-14 17:00 | 44026.7083 | 0 | 13.2084 | 39.95
2020-07-14 17:30 | 44026.7292 | 0 | 14.7307 | 39.95
2020-07-14 18:00 | 44026.75 | 0 | 15.014 | 39.95
2020-07-14 18:30 | 44026.7708 | 0 | 15.6366 | 39.95
2020-07-14 19:00 | 44026.7917 | 0 | 15.5667 | 39.95
2020-07-14 19:30 | 44026.8125 | 0 | 15.2697 | 39.95
2020-07-14 20:00 | 44026.8333 | 0 | 15.0246 | 39.95
2020-07-14 20:30 | 44026.8542 | 0 | 14.3361 | 39.95
2020-07-14 21:00 | 44026.875 | 0 | 13.5101 | 39.95
2020-07-14 21:30 | 44026.8958 | 0 | 12.7513 | 39.95
2020-07-14 22:00 | 44026.9167 | 0 | 12.0179 | 39.95
2020-07-14 22:30 | 44026.9375 | 0 | 11.1562 | 39.95
2020-07-14 23:00 | 44026.9583 | 0 | 10.4238 | 39.95
2020-07-14 23:30 | 44026.9792 | 0 | 9.7255 | 39.95
2020-07-15 | 44027 | 0 | 8.9915 | 39.95
2020-07-15 00:30 | 44027.0208 | 0 | 8.4969 | 39.95
2020-07-15 01:00 | 44027.0417 | 0 | 8.2388 | 39.95
2020-07-15 01:30 | 44027.0625 | 0 | 8.0374 | 39.95
2020-07-15 02:00 | 44027.0833 | 0 | 7.8997 | 39.95
2020-07-15 02:30 | 44027.1042 | 0 | 7.9192 | 39.95
2020-07-15 03:00 | 44027.125 | 0 | 7.8718 | 39.95
2020-07-15 03:30 | 44027.1458 | 0 | 7.8928 | 39.95
2020-07-15 04:00 | 44027.1667 | 0 | 8.1524 | 39.95
2020-07-15 04:30 | 44027.1875 | 0 | 8.6802 | 39.95
2020-07-15 05:00 | 44027.2083 | 0 | 9.6195 | 39.95
2020-07-15 05:30 | 44027.2292 | 0 | 10.6773 | 39.95
2020-07-15 06:00 | 44027.25 | 0 | 12.1849 | 39.95
2020-07-15 06:30 | 44027.2708 | 0 | 13.7901 | 39.95
2020-07-15 07:00 | 44027.2917 | 0 | 15.0847 | 39.95
2020-07-15 07:30 | 44027.3125 | 0 | 14.6756 | 39.95
2020-07-15 08:00 | 44027.3333 | 0 | 13.5961 | 39.95
2020-07-15 08:30 | 44027.3542 | 0 | 12.5521 | 39.95
2020-07-15 09:00 | 44027.375 | 0 | 11.7484 | 39.95
2020-07-15 09:30 | 44027.3958 | 0 | 10.9608 | 39.95
2020-07-15 10:00 | 44027.4167 | 0 | 10.4406 | 39.95
2020-07-15 10:30 | 44027.4375 | 0 | 10.0929 | 39.95
2020-07-15 11:00 | 44027.4583 | 0 | 9.5191 | 39.95
2020-07-15 11:30 | 44027.4792 | 0 | 9.3477 | 39.95
2020-07-15 12:00 | 44027.5 | 0 | 9.107 | 39.95
2020-07-15 12:30 | 44027.5208 | 0 | 9.0187 | 39.95
2020-07-15 13:00 | 44027.5417 | 0 | 9.1509 | 39.95
2020-07-15 13:30 | 44027.5625 | 0 | 9.4691 | 39.95
2020-07-15 14:00 | 44027.5833 | 0 | 9.816 | 39.95
2020-07-15 14:30 | 44027.6042 | 0 | 9.8836 | 39.95
2020-07-15 15:00 | 44027.625 | 0 | 10.1865 | 39.95
2020-07-15 15:30 | 44027.6458 | 0 | 10.6645 | 39.95
2020-07-15 16:00 | 44027.6667 | 0 | 11.3272 | 39.95
2020-07-15 16:30 | 44027.6875 | 0 | 12.1967 | 39.95
2020-07-15 17:00 | 44027.7083 | 0 | 13.3807 | 39.95
2020-07-15 17:30 | 44027.7292 | 0 | 14.5559 | 39.95
2020-07-15 18:00 | 44027.75 | 0 | 15.058 | 39.95
2020-07-15 18:30 | 44027.7708 | 0 | 15.3719 | 39.95
2020-07-15 19:00 | 44027.7917 | 0 | 15.4018 | 39.95
2020-07-15 19:30 | 44027.8125 | 0 | 15.0254 | 39.95
2020-07-15 20:00 | 44027.8333 | 0 | 14.8059 | 39.95
2020-07-15 20:30 | 44027.8542 | 0 | 14.2749 | 39.95
2020-07-15 21:00 | 44027.875 | 0 | 13.5578 | 39.95
2020-07-15 21:30 | 44027.8958 | 0 | 13.1289 | 39.95
2020-07-15 22:00 | 44027.9167 | 0 | 12.134 | 39.95
2020-07-15 22:30 | 44027.9375 | 0 | 11.1062 | 39.95
2020-07-15 23:00 | 44027.9583 | 0 | 10.2033 | 39.95
2020-07-15 23:30 | 44027.9792 | 0 | 9.511 | 39.95
2020-07-16 | 44028 | 0 | 8.8386 | 39.95
2020-07-16 00:30 | 44028.0208 | 0 | 8.4547 | 39.95
2020-07-16 01:00 | 44028.0417 | 0 | 8.1995 | 39.95
2020-07-16 01:30 | 44028.0625 | 0 | 8.0616 | 39.95
2020-07-16 02:00 | 44028.0833 | 0 | 7.9571 | 39.95
2020-07-16 02:30 | 44028.1042 | 0 | 7.8692 | 39.95
2020-07-16 03:00 | 44028.125 | 0 | 7.8925 | 39.95
2020-07-16 03:30 | 44028.1458 | 0 | 7.8684 | 39.95
2020-07-16 04:00 | 44028.1667 | 0 | 8.2232 | 39.95
2020-07-16 04:30 | 44028.1875 | 0 | 8.666 | 39.95
2020-07-16 05:00 | 44028.2083 | 0 | 9.4494 | 39.95
2020-07-16 05:30 | 44028.2292 | 0 | 10.4098 | 39.95
2020-07-16 06:00 | 44028.25 | 0 | 11.737 | 39.95
2020-07-16 06:30 | 44028.2708 | 0 | 13.3743 | 39.95
2020-07-16 07:00 | 44028.2917 | 0 | 14.6645 | 39.95
2020-07-16 07:30 | 44028.3125 | 0 | 14.3358 | 39.95
2020-07-16 08:00 | 44028.3333 | 0 | 13.3967 | 39.95
2020-07-16 08:30 | 44028.3542 | 0 | 12.7373 | 39.95
2020-07-16 09:00 | 44028.375 | 0 | 11.7036 | 39.95
2020-07-16 09:30 | 44028.3958 | 0 | 10.941 | 39.95
2020-07-16 10:00 | 44028.4167 | 0 | 10.3287 | 39.95
2020-07-16 10:30 | 44028.4375 | 0 | 9.8207 | 39.95
2020-07-16 11:00 | 44028.4583 | 0 | 9.4069 | 39.95
2020-07-16 11:30 | 44028.4792 | 0 | 9.2944 | 39.95
2020-07-16 12:00 | 44028.5 | 0 | 8.9385 | 39.95
2020-07-16 12:30 | 44028.5208 | 0 | 8.8697 | 39.95
2020-07-16 13:00 | 44028.5417 | 0 | 8.8952 | 39.95
2020-07-16 13:30 | 44028.5625 | 0 | 9.0701 | 39.95
2020-07-16 14:00 | 44028.5833 | 0 | 9.4498 | 39.95
2020-07-16 14:30 | 44028.6042 | 0 | 9.5956 | 39.95
2020-07-16 15:00 | 44028.625 | 0 | 10.0722 | 39.95
2020-07-16 15:30 | 44028.6458 | 0 | 10.8592 | 39.95
2020-07-16 16:00 | 44028.6667 | 0 | 11.4055 | 39.95
2020-07-16 16:30 | 44028.6875 | 0 | 12.1589 | 39.95
2020-07-16 17:00 | 44028.7083 | 0 | 12.5563 | 39.95
2020-07-16 17:30 | 44028.7292 | 0 | 13.573 | 39.95
2020-07-16 18:00 | 44028.75 | 0 | 13.908 | 39.95
2020-07-16 18:30 | 44028.7708 | 0 | 14.2171 | 39.95
2020-07-16 19:00 | 44028.7917 | 0 | 14.0436 | 39.95
2020-07-16 19:30 | 44028.8125 | 0 | 13.9022 | 39.95
2020-07-16 20:00 | 44028.8333 | 0 | 13.8601 | 39.95
2020-07-16 20:30 | 44028.8542 | 0 | 13.1471 | 39.95
2020-07-16 21:00 | 44028.875 | 0 | 12.8114 | 39.95
2020-07-16 21:30 | 44028.8958 | 0 | 12.4287 | 39.95
2020-07-16 22:00 | 44028.9167 | 0 | 11.8558 | 39.95
2020-07-16 22:30 | 44028.9375 | 0 | 10.925 | 39.95
2020-07-16 23:00 | 44028.9583 | 0 | 10.3583 | 39.95
2020-07-16 23:30 | 44028.9792 | 0 | 9.6054 | 39.95
2020-07-17 | 44029 | 0 | 9.0123 | 39.95
2020-07-17 00:30 | 44029.0208 | 0 | 8.5238 | 39.95
2020-07-17 01:00 | 44029.0417 | 0 | 8.1736 | 39.95
2020-07-17 01:30 | 44029.0625 | 0 | 7.9459 | 39.95
2020-07-17 02:00 | 44029.0833 | 0 | 7.9058 | 39.95
2020-07-17 02:30 | 44029.1042 | 0 | 7.8635 | 39.95
2020-07-17 03:00 | 44029.125 | 0 | 7.7758 | 39.95
2020-07-17 03:30 | 44029.1458 | 0 | 7.7271 | 39.95
2020-07-17 04:00 | 44029.1667 | 0 | 7.7288 | 39.95
2020-07-17 04:30 | 44029.1875 | 0 | 7.8878 | 39.95
2020-07-17 05:00 | 44029.2083 | 0 | 8.2611 | 39.95
2020-07-17 05:30 | 44029.2292 | 0 | 8.5045 | 39.95
2020-07-17 06:00 | 44029.25 | 0 | 8.8493 | 39.95
2020-07-17 06:30 | 44029.2708 | 0 | 9.4127 | 39.95
2020-07-17 07:00 | 44029.2917 | 0 | 10.0505 | 39.95
2020-07-17 07:30 | 44029.3125 | 0 | 10.0917 | 39.95
2020-07-17 08:00 | 44029.3333 | 0 | 10.0485 | 39.95
2020-07-17 08:30 | 44029.3542 | 0 | 9.8469 | 39.95
2020-07-17 09:00 | 44029.375 | 0 | 9.277 | 39.95
2020-07-17 09:30 | 44029.3958 | 0 | 8.7458 | 39.95
2020-07-17 10:00 | 44029.4167 | 0 | 8.0821 | 39.95
2020-07-17 10:30 | 44029.4375 | 0 | 7.8977 | 39.95
2020-07-17 11:00 | 44029.4583 | 0 | 7.2578 | 39.95
2020-07-17 11:30 | 44029.4792 | 0 | 6.9438 | 39.95
2020-07-17 12:00 | 44029.5 | 0 | 6.8714 | 39.95
2020-07-17 12:30 | 44029.5208 | 0 | 6.5905 | 39.95
2020-07-17 13:00 | 44029.5417 | 0 | 6.8183 | 39.95
2020-07-17 13:30 | 44029.5625 | 0 | 7.0128 | 39.95
2020-07-17 14:00 | 44029.5833 | 0 | 7.3405 | 39.95
2020-07-17 14:30 | 44029.6042 | 0 | 7.6623 | 39.95
2020-07-17 15:00 | 44029.625 | 0 | 7.962 | 39.95
2020-07-17 15:30 | 44029.6458 | 0 | 8.535 | 39.95
2020-07-17 16:00 | 44029.6667 | 0 | 9.2757 | 39.95
2020-07-17 16:30 | 44029.6875 | 0 | 9.9893 | 39.95
2020-07-17 17:00 | 44029.7083 | 0 | 10.5566 | 39.95
2020-07-17 17:30 | 44029.7292 | 0 | 11.3668 | 39.95
2020-07-17 18:00 | 44029.75 | 0 | 11.6229 | 39.95
2020-07-17 18:30 | 44029.7708 | 0 | 11.8385 | 39.95
2020-07-17 19:00 | 44029.7917 | 0 | 11.7328 | 39.95
2020-07-17 19:30 | 44029.8125 | 0 | 11.4372 | 39.95
2020-07-17 20:00 | 44029.8333 | 0 | 11.1878 | 39.95
2020-07-17 20:30 | 44029.8542 | 0 | 10.7519 | 39.95
2020-07-17 21:00 | 44029.875 | 0 | 10.4006 | 39.95
2020-07-17 21:30 | 44029.8958 | 0 | 10.1671 | 39.95
2020-07-17 22:00 | 44029.9167 | 0 | 9.8394 | 39.95
2020-07-17 22:30 | 44029.9375 | 0 | 9.2347 | 39.95
2020-07-17 23:00 | 44029.9583 | 0 | 8.7624 | 39.95
2020-07-17 23:30 | 44029.9792 | 0 | 8.268 | 39.95
2020-07-18 | 44030 | 0 | 7.8874 | 39.95
2020-07-18 00:30 | 44030.0208 | 0 | 7.4325 | 39.95
2020-07-18 01:00 | 44030.0417 | 0 | 7.3222 | 39.95
2020-07-18 01:30 | 44030.0625 | 0 | 7.0867 | 39.95
2020-07-18 02:00 | 44030.0833 | 0 | 7.0908 | 39.95
2020-07-18 02:30 | 44030.1042 | 0 | 7.1042 | 39.95
2020-07-18 03:00 | 44030.125 | 0 | 6.9947 | 39.95
2020-07-18 03:30 | 44030.1458 | 0 | 6.8119 | 39.95
2020-07-18 04:00 | 44030.1667 | 0 | 6.8049 | 39.95
2020-07-18 04:30 | 44030.1875 | 0 | 6.8967 | 39.95
2020-07-18 05:00 | 44030.2083 | 0 | 7.0427 | 39.95
2020-07-18 05:30 | 44030.2292 | 0 | 7.3382 | 39.95
2020-07-18 06:00 | 44030.25 | 0 | 7.7384 | 39.95
2020-07-18 06:30 | 44030.2708 | 0 | 8.1198 | 39.95
2020-07-18 07:00 | 44030.2917 | 0 | 8.5857 | 39.95
2020-07-18 07:30 | 44030.3125 | 0 | 8.7463 | 39.95
2020-07-18 08:00 | 44030.3333 | 0 | 8.8525 | 39.95
2020-07-18 08:30 | 44030.3542 | 0 | 8.6927 | 39.95
2020-07-18 09:00 | 44030.375 | 0 | 8.2646 | 39.95
2020-07-18 09:30 | 44030.3958 | 0 | 7.7887 | 39.95
2020-07-18 10:00 | 44030.4167 | 0 | 7.4036 | 39.95
2020-07-18 10:30 | 44030.4375 | 0 | 7.147 | 39.95
2020-07-18 11:00 | 44030.4583 | 0 | 6.6174 | 39.95
2020-07-18 11:30 | 44030.4792 | 0 | 6.3833 | 39.95
2020-07-18 12:00 | 44030.5 | 0 | 6.2899 | 39.95
2020-07-18 12:30 | 44030.5208 | 0 | 6.1798 | 39.95
2020-07-18 13:00 | 44030.5417 | 0 | 6.2784 | 39.95
2020-07-18 13:30 | 44030.5625 | 0 | 6.3683 | 39.95
2020-07-18 14:00 | 44030.5833 | 0 | 6.9474 | 39.95
2020-07-18 14:30 | 44030.6042 | 0 | 7.3925 | 39.95
2020-07-18 15:00 | 44030.625 | 0 | 7.8266 | 39.95
2020-07-18 15:30 | 44030.6458 | 0 | 8.4062 | 39.95
2020-07-18 16:00 | 44030.6667 | 0 | 9.2014 | 39.95
2020-07-18 16:30 | 44030.6875 | 0 | 9.9702 | 39.95
2020-07-18 17:00 | 44030.7083 | 0 | 10.7346 | 39.95
2020-07-18 17:30 | 44030.7292 | 0 | 11.8149 | 39.95
2020-07-18 18:00 | 44030.75 | 0 | 12.3214 | 39.95
2020-07-18 18:30 | 44030.7708 | 0 | 12.396 | 39.95
2020-07-18 19:00 | 44030.7917 | 0 | 12.0399 | 39.95
2020-07-18 19:30 | 44030.8125 | 0 | 11.7158 | 39.95
2020-07-18 20:00 | 44030.8333 | 0 | 11.516 | 39.95
2020-07-18 20:30 | 44030.8542 | 0 | 10.9325 | 39.95
2020-07-18 21:00 | 44030.875 | 0 | 10.4056 | 39.95
2020-07-18 21:30 | 44030.8958 | 0 | 10.0392 | 39.95
2020-07-18 22:00 | 44030.9167 | 0 | 9.5751 | 39.95
2020-07-18 22:30 | 44030.9375 | 0 | 8.8658 | 39.95
2020-07-18 23:00 | 44030.9583 | 0 | 8.3666 | 39.95
2020-07-18 23:30 | 44030.9792 | 0 | 7.8898 | 39.95
2020-07-19 | 44031 | 0 | 7.6401 | 39.95
2020-07-19 00:30 | 44031.0208 | 0 | 7.3334 | 39.95
2020-07-19 01:00 | 44031.0417 | 0 | 7.1322 | 39.95
2020-07-19 01:30 | 44031.0625 | 0 | 6.9943 | 39.95
2020-07-19 02:00 | 44031.0833 | 0 | 7.0621 | 39.95
2020-07-19 02:30 | 44031.1042 | 0 | 7.0144 | 39.95
2020-07-19 03:00 | 44031.125 | 0 | 6.9517 | 39.95
2020-07-19 03:30 | 44031.1458 | 0 | 7.0908 | 39.95
2020-07-19 04:00 | 44031.1667 | 0 | 7.2046 | 39.95
2020-07-19 04:30 | 44031.1875 | 0 | 7.8259 | 39.95
2020-07-19 05:00 | 44031.2083 | 0 | 8.6552 | 39.95
2020-07-19 05:30 | 44031.2292 | 0 | 9.6709 | 39.95
2020-07-19 06:00 | 44031.25 | 0 | 11.091 | 39.95
2020-07-19 06:30 | 44031.2708 | 0 | 12.477 | 39.95
2020-07-19 07:00 | 44031.2917 | 0 | 13.5399 | 39.95
2020-07-19 07:30 | 44031.3125 | 0 | 13.4645 | 39.95
2020-07-19 08:00 | 44031.3333 | 0 | 12.7604 | 39.95
2020-07-19 08:30 | 44031.3542 | 0 | 12.0129 | 39.95
2020-07-19 09:00 | 44031.375 | 0 | 11.0975 | 39.95
2020-07-19 09:30 | 44031.3958 | 0 | 10.3842 | 39.95
2020-07-19 10:00 | 44031.4167 | 0 | 9.9602 | 39.95
2020-07-19 10:30 | 44031.4375 | 0 | 9.632 | 39.95
2020-07-19 11:00 | 44031.4583 | 0 | 9.1237 | 39.95
2020-07-19 11:30 | 44031.4792 | 0 | 9.1026 | 39.95
2020-07-19 12:00 | 44031.5 | 0 | 9.0671 | 39.95
2020-07-19 12:30 | 44031.5208 | 0 | 8.8857 | 39.95
2020-07-19 13:00 | 44031.5417 | 0 | 9.0892 | 39.95
2020-07-19 13:30 | 44031.5625 | 0 | 9.2976 | 39.95
2020-07-19 14:00 | 44031.5833 | 0 | 9.5548 | 39.95
2020-07-19 14:30 | 44031.6042 | 0 | 9.9062 | 39.95
2020-07-19 15:00 | 44031.625 | 0 | 10.4073 | 39.95
2020-07-19 15:30 | 44031.6458 | 0 | 10.8504 | 39.95
2020-07-19 16:00 | 44031.6667 | 0 | 11.3746 | 39.95
2020-07-19 16:30 | 44031.6875 | 0 | 11.931 | 39.95
2020-07-19 17:00 | 44031.7083 | 0 | 12.7676 | 39.95
2020-07-19 17:30 | 44031.7292 | 0 | 13.9229 | 39.95
2020-07-19 18:00 | 44031.75 | 0 | 14.5164 | 39.95
2020-07-19 18:30 | 44031.7708 | 0 | 14.5813 | 39.95
2020-07-19 19:00 | 44031.7917 | 0 | 14.2276 | 39.95
2020-07-19 19:30 | 44031.8125 | 0 | 13.79 | 39.95
2020-07-19 20:00 | 44031.8333 | 0 | 13.5217 | 39.95
2020-07-19 20:30 | 44031.8542 | 0 | 12.9565 | 39.95
2020-07-19 21:00 | 44031.875 | 0 | 12.3598 | 39.95
2020-07-19 21:30 | 44031.8958 | 0 | 11.9357 | 39.95
2020-07-19 22:00 | 44031.9167 | 0 | 11.4268 | 39.95
2020-07-19 22:30 | 44031.9375 | 0 | 10.2479 | 39.95
2020-07-19 23:00 | 44031.9583 | 0 | 9.5261 | 39.95
2020-07-19 23:30 | 44031.9792 | 0 | 8.9332 | 39.95
2020-07-20 | 44032 | 0 | 8.2823 | 39.95
2020-07-20 00:30 | 44032.0208 | 0 | 7.8189 | 39.95
2020-07-20 01:00 | 44032.0417 | 0 | 7.5805 | 39.95
2020-07-20 01:30 | 44032.0625 | 0 | 7.4145 | 39.95
2020-07-20 02:00 | 44032.0833 | 0 | 7.3682 | 39.95
2020-07-20 02:30 | 44032.1042 | 0 | 7.3727 | 39.95
2020-07-20 03:00 | 44032.125 | 0 | 7.3864 | 39.95
2020-07-20 03:30 | 44032.1458 | 0 | 7.4231 | 39.95
2020-07-20 04:00 | 44032.1667 | 0 | 7.523 | 39.95
2020-07-20 04:30 | 44032.1875 | 0 | 8.0266 | 39.95
2020-07-20 05:00 | 44032.2083 | 0 | 8.9058 | 39.95
2020-07-20 05:30 | 44032.2292 | 0 | 9.6688 | 39.95
2020-07-20 06:00 | 44032.25 | 0 | 11.1963 | 39.95
2020-07-20 06:30 | 44032.2708 | 0 | 12.5575 | 39.95
2020-07-20 07:00 | 44032.2917 | 0 | 13.685 | 39.95
2020-07-20 07:30 | 44032.3125 | 0 | 13.8293 | 39.95
2020-07-20 08:00 | 44032.3333 | 0 | 13.3502 | 39.95
2020-07-20 08:30 | 44032.3542 | 0 | 12.9614 | 39.95
2020-07-20 09:00 | 44032.375 | 0 | 12.0962 | 39.95
2020-07-20 09:30 | 44032.3958 | 0 | 11.32 | 39.95
2020-07-20 10:00 | 44032.4167 | 0 | 11.1212 | 39.95
2020-07-20 10:30 | 44032.4375 | 0 | 10.2081 | 39.95
2020-07-20 11:00 | 44032.4583 | 0 | 9.4878 | 39.95
2020-07-20 11:30 | 44032.4792 | 0 | 8.9854 | 39.95
2020-07-20 12:00 | 44032.5 | 0 | 9.4214 | 39.95
2020-07-20 12:30 | 44032.5208 | 0 | 10.0773 | 39.95
2020-07-20 13:00 | 44032.5417 | 0 | 9.9854 | 39.95
2020-07-20 13:30 | 44032.5625 | 0 | 10.1034 | 39.95
2020-07-20 14:00 | 44032.5833 | 0 | 9.9528 | 39.95
2020-07-20 14:30 | 44032.6042 | 0 | 11.0063 | 39.95
2020-07-20 15:00 | 44032.625 | 0 | 11.0032 | 39.95
2020-07-20 15:30 | 44032.6458 | 0 | 11.3472 | 39.95
2020-07-20 16:00 | 44032.6667 | 0 | 11.9391 | 39.95
2020-07-20 16:30 | 44032.6875 | 0 | 12.6679 | 39.95
2020-07-20 17:00 | 44032.7083 | 0 | 13.5186 | 39.95
2020-07-20 17:30 | 44032.7292 | 0 | 14.6154 | 39.95
2020-07-20 18:00 | 44032.75 | 0 | 14.8777 | 39.95
2020-07-20 18:30 | 44032.7708 | 0 | 15.1455 | 39.95
2020-07-20 19:00 | 44032.7917 | 0 | 14.9025 | 39.95
2020-07-20 19:30 | 44032.8125 | 0 | 14.3824 | 39.95
2020-07-20 20:00 | 44032.8333 | 0 | 14.2236 | 39.95
2020-07-20 20:30 | 44032.8542 | 0 | 13.6483 | 39.95
2020-07-20 21:00 | 44032.875 | 0 | 12.814 | 39.95
2020-07-20 21:30 | 44032.8958 | 0 | 12.2396 | 39.95
2020-07-20 22:00 | 44032.9167 | 0 | 11.4486 | 39.95
2020-07-20 22:30 | 44032.9375 | 0 | 10.5654 | 39.95
2020-07-20 23:00 | 44032.9583 | 0 | 9.7466 | 39.95
2020-07-20 23:30 | 44032.9792 | 0 | 9.1106 | 39.95
2020-07-21 | 44033 | 0 | 8.4955 | 39.95
2020-07-21 00:30 | 44033.0208 | 0 | 8.1591 | 39.95
2020-07-21 01:00 | 44033.0417 | 0 | 7.8683 | 39.95
2020-07-21 01:30 | 44033.0625 | 0 | 7.7317 | 39.95
2020-07-21 02:00 | 44033.0833 | 0 | 7.6579 | 39.95
2020-07-21 02:30 | 44033.1042 | 0 | 7.665 | 39.95
2020-07-21 03:00 | 44033.125 | 0 | 7.6109 | 39.95
2020-07-21 03:30 | 44033.1458 | 0 | 7.6395 | 39.95
2020-07-21 04:00 | 44033.1667 | 0 | 7.9878 | 39.95
2020-07-21 04:30 | 44033.1875 | 0 | 8.4189 | 39.95
2020-07-21 05:00 | 44033.2083 | 0 | 9.0731 | 39.95
2020-07-21 05:30 | 44033.2292 | 0 | 10.083 | 39.95
2020-07-21 06:00 | 44033.25 | 0 | 11.2778 | 39.95
2020-07-21 06:30 | 44033.2708 | 0 | 12.7005 | 39.95
2020-07-21 07:00 | 44033.2917 | 0 | 13.9534 | 39.95
2020-07-21 07:30 | 44033.3125 | 0 | 13.9919 | 39.95
2020-07-21 08:00 | 44033.3333 | 0 | 13.9168 | 39.95
2020-07-21 08:30 | 44033.3542 | 0 | 13.8888 | 39.95
2020-07-21 09:00 | 44033.375 | 0 | 13.4048 | 39.95
2020-07-21 09:30 | 44033.3958 | 0 | 13.1493 | 39.95
2020-07-21 10:00 | 44033.4167 | 0 | 13.4348 | 39.95
2020-07-21 10:30 | 44033.4375 | 0 | 13.3916 | 39.95
2020-07-21 11:00 | 44033.4583 | 0 | 12.9748 | 39.95
2020-07-21 11:30 | 44033.4792 | 0 | 12.5001 | 39.95
2020-07-21 12:00 | 44033.5 | 0 | 11.8782 | 39.95
2020-07-21 12:30 | 44033.5208 | 0 | 12.0772 | 39.95
2020-07-21 13:00 | 44033.5417 | 0 | 12.2142 | 39.95
2020-07-21 13:30 | 44033.5625 | 0 | 12.4086 | 39.95
2020-07-21 14:00 | 44033.5833 | 0 | 12.5214 | 39.95
2020-07-21 14:30 | 44033.6042 | 0 | 12.1534 | 39.95
2020-07-21 15:00 | 44033.625 | 0 | 12.1507 | 39.95
2020-07-21 15:30 | 44033.6458 | 0 | 12.6151 | 39.95
2020-07-21 16:00 | 44033.6667 | 0 | 12.9383 | 39.95
2020-07-21 16:30 | 44033.6875 | 0 | 13.6812 | 39.95
2020-07-21 17:00 | 44033.7083 | 0 | 14.3821 | 39.95
2020-07-21 17:30 | 44033.7292 | 0 | 15.2329 | 39.95
2020-07-21 18:00 | 44033.75 | 0 | 15.6431 | 39.95
2020-07-21 18:30 | 44033.7708 | 0 | 15.8995 | 39.95
2020-07-21 19:00 | 44033.7917 | 0 | 15.5203 | 39.95
2020-07-21 19:30 | 44033.8125 | 0 | 15.1451 | 39.95
2020-07-21 20:00 | 44033.8333 | 0 | 14.7167 | 39.95
2020-07-21 20:30 | 44033.8542 | 0 | 14.0604 | 39.95
2020-07-21 21:00 | 44033.875 | 0 | 13.4365 | 39.95
2020-07-21 21:30 | 44033.8958 | 0 | 12.8011 | 39.95
2020-07-21 22:00 | 44033.9167 | 0 | 11.8765 | 39.95
2020-07-21 22:30 | 44033.9375 | 0 | 11.0279 | 39.95
2020-07-21 23:00 | 44033.9583 | 0 | 10.0258 | 39.95
2020-07-21 23:30 | 44033.9792 | 0 | 9.3453 | 39.95
2020-07-22 | 44034 | 0 | 8.7958 | 39.95
2020-07-22 00:30 | 44034.0208 | 0 | 8.42 | 39.95
2020-07-22 01:00 | 44034.0417 | 0 | 8.0877 | 39.95
2020-07-22 01:30 | 44034.0625 | 0 | 7.8765 | 39.95
2020-07-22 02:00 | 44034.0833 | 0 | 7.7394 | 39.95
2020-07-22 02:30 | 44034.1042 | 0 | 7.6958 | 39.95
2020-07-22 03:00 | 44034.125 | 0 | 7.7261 | 39.95
2020-07-22 03:30 | 44034.1458 | 0 | 7.7286 | 39.95
2020-07-22 04:00 | 44034.1667 | 0 | 7.9027 | 39.95
2020-07-22 04:30 | 44034.1875 | 0 | 8.4049 | 39.95
2020-07-22 05:00 | 44034.2083 | 0 | 9.247 | 39.95
2020-07-22 05:30 | 44034.2292 | 0 | 10.1279 | 39.95
2020-07-22 06:00 | 44034.25 | 0 | 11.5302 | 39.95
2020-07-22 06:30 | 44034.2708 | 0 | 12.8563 | 39.95
2020-07-22 07:00 | 44034.2917 | 0 | 13.9909 | 39.95
2020-07-22 07:30 | 44034.3125 | 0 | 14.4008 | 39.95
2020-07-22 08:00 | 44034.3333 | 0 | 14.2398 | 39.95
2020-07-22 08:30 | 44034.3542 | 0 | 14.01 | 39.95
2020-07-22 09:00 | 44034.375 | 0 | 14.0102 | 39.95
2020-07-22 09:30 | 44034.3958 | 0 | 13.7279 | 39.95
2020-07-22 10:00 | 44034.4167 | 0 | 13.4879 | 39.95
2020-07-22 10:30 | 44034.4375 | 0 | 13.3806 | 39.95
2020-07-22 11:00 | 44034.4583 | 0 | 13.038 | 39.95
2020-07-22 11:30 | 44034.4792 | 0 | 12.7478 | 39.95
2020-07-22 12:00 | 44034.5 | 0 | 12.8577 | 39.95
2020-07-22 12:30 | 44034.5208 | 0 | 12.7467 | 39.95
2020-07-22 13:00 | 44034.5417 | 0 | 12.7034 | 39.95
2020-07-22 13:30 | 44034.5625 | 0 | 13.0144 | 39.95
2020-07-22 14:00 | 44034.5833 | 0 | 13.3662 | 39.95
2020-07-22 14:30 | 44034.6042 | 0 | 13.3029 | 39.95
2020-07-22 15:00 | 44034.625 | 0 | 13.1835 | 39.95
2020-07-22 15:30 | 44034.6458 | 0 | 13.691 | 39.95
2020-07-22 16:00 | 44034.6667 | 0 | 14.056 | 39.95
2020-07-22 16:30 | 44034.6875 | 0 | 14.6095 | 39.95
2020-07-22 17:00 | 44034.7083 | 0 | 15.4455 | 39.95
2020-07-22 17:30 | 44034.7292 | 0 | 16.2081 | 39.95
2020-07-22 18:00 | 44034.75 | 0 | 16.4093 | 39.95
2020-07-22 18:30 | 44034.7708 | 0 | 16.5555 | 39.95
2020-07-22 19:00 | 44034.7917 | 0 | 16.44 | 39.95
2020-07-22 19:30 | 44034.8125 | 0 | 15.9305 | 39.95
2020-07-22 20:00 | 44034.8333 | 0 | 15.3231 | 39.95
2020-07-22 20:30 | 44034.8542 | 0 | 14.5954 | 39.95
2020-07-22 21:00 | 44034.875 | 0 | 13.8698 | 39.95
2020-07-22 21:30 | 44034.8958 | 0 | 13.0907 | 39.95
2020-07-22 22:00 | 44034.9167 | 0 | 12.2846 | 39.95
2020-07-22 22:30 | 44034.9375 | 0 | 11.0428 | 39.95
2020-07-22 23:00 | 44034.9583 | 0 | 10.2389 | 39.95
2020-07-22 23:30 | 44034.9792 | 0 | 9.5838 | 39.95
2020-07-23 | 44035 | 0 | 8.9466 | 39.95
2020-07-23 00:30 | 44035.0208 | 0 | 8.5723 | 39.95
2020-07-23 01:00 | 44035.0417 | 0 | 8.1701 | 39.95
2020-07-23 01:30 | 44035.0625 | 0 | 7.9027 | 39.95
2020-07-23 02:00 | 44035.0833 | 0 | 7.9116 | 39.95
2020-07-23 02:30 | 44035.1042 | 0 | 7.7845 | 39.95
2020-07-23 03:00 | 44035.125 | 0 | 7.8 | 39.95
2020-07-23 03:30 | 44035.1458 | 0 | 7.8408 | 39.95
2020-07-23 04:00 | 44035.1667 | 0 | 7.8828 | 39.95
2020-07-23 04:30 | 44035.1875 | 0 | 8.4765 | 39.95
2020-07-23 05:00 | 44035.2083 | 0 | 9.2783 | 39.95
2020-07-23 05:30 | 44035.2292 | 0 | 10.2066 | 39.95
2020-07-23 06:00 | 44035.25 | 0 | 11.3011 | 39.95
2020-07-23 06:30 | 44035.2708 | 0 | 12.8279 | 39.95
2020-07-23 07:00 | 44035.2917 | 0 | 13.8458 | 39.95
2020-07-23 07:30 | 44035.3125 | 0 | 14.3415 | 39.95
2020-07-23 08:00 | 44035.3333 | 0 | 14.2927 | 39.95
2020-07-23 08:30 | 44035.3542 | 0 | 13.5932 | 39.95
2020-07-23 09:00 | 44035.375 | 0 | 13.2293 | 39.95
2020-07-23 09:30 | 44035.3958 | 0 | 13.505 | 39.95
2020-07-23 10:00 | 44035.4167 | 0 | 12.6937 | 39.95
2020-07-23 10:30 | 44035.4375 | 0 | 12.3956 | 39.95
2020-07-23 11:00 | 44035.4583 | 0 | 12.2103 | 39.95
2020-07-23 11:30 | 44035.4792 | 0 | 11.362 | 39.95
2020-07-23 12:00 | 44035.5 | 0 | 9.8959 | 39.95
2020-07-23 12:30 | 44035.5208 | 0 | 10.2675 | 39.95
2020-07-23 13:00 | 44035.5417 | 0 | 9.6474 | 39.95
2020-07-23 13:30 | 44035.5625 | 0 | 9.8383 | 39.95
2020-07-23 14:00 | 44035.5833 | 0 | 10.034 | 39.95
2020-07-23 14:30 | 44035.6042 | 0 | 10.1696 | 39.95
2020-07-23 15:00 | 44035.625 | 0 | 11.1112 | 39.95
2020-07-23 15:30 | 44035.6458 | 0 | 11.7723 | 39.95
2020-07-23 16:00 | 44035.6667 | 0 | 12.0924 | 39.95
2020-07-23 16:30 | 44035.6875 | 0 | 12.7157 | 39.95
2020-07-23 17:00 | 44035.7083 | 0 | 13.2791 | 39.95
2020-07-23 17:30 | 44035.7292 | 0 | 14.0422 | 39.95
2020-07-23 18:00 | 44035.75 | 0 | 14.1466 | 39.95
2020-07-23 18:30 | 44035.7708 | 0 | 14.4856 | 39.95
2020-07-23 19:00 | 44035.7917 | 0 | 14.3226 | 39.95
2020-07-23 19:30 | 44035.8125 | 0 | 14.0751 | 39.95
2020-07-23 20:00 | 44035.8333 | 0 | 13.8424 | 39.95
2020-07-23 20:30 | 44035.8542 | 0 | 13.3556 | 39.95
2020-07-23 21:00 | 44035.875 | 0 | 12.8314 | 39.95
2020-07-23 21:30 | 44035.8958 | 0 | 12.2435 | 39.95
2020-07-23 22:00 | 44035.9167 | 0 | 11.6526 | 39.95
2020-07-23 22:30 | 44035.9375 | 0 | 10.9209 | 39.95
2020-07-23 23:00 | 44035.9583 | 0 | 10.145 | 39.95
2020-07-23 23:30 | 44035.9792 | 0 | 9.5257 | 39.95
2020-07-24 | 44036 | 0 | 8.9691 | 39.95
2020-07-24 00:30 | 44036.0208 | 0 | 8.4288 | 39.95
2020-07-24 01:00 | 44036.0417 | 0 | 7.9847 | 39.95
2020-07-24 01:30 | 44036.0625 | 0 | 7.8858 | 39.95
2020-07-24 02:00 | 44036.0833 | 0 | 7.7533 | 39.95
2020-07-24 02:30 | 44036.1042 | 0 | 7.8122 | 39.95
2020-07-24 03:00 | 44036.125 | 0 | 7.6473 | 39.95
2020-07-24 03:30 | 44036.1458 | 0 | 7.5555 | 39.95
2020-07-24 04:00 | 44036.1667 | 0 | 7.6817 | 39.95
2020-07-24 04:30 | 44036.1875 | 0 | 7.9307 | 39.95
2020-07-24 05:00 | 44036.2083 | 0 | 8.169 | 39.95
2020-07-24 05:30 | 44036.2292 | 0 | 8.5672 | 39.95
2020-07-24 06:00 | 44036.25 | 0 | 8.8596 | 39.95
2020-07-24 06:30 | 44036.2708 | 0 | 9.4924 | 39.95
2020-07-24 07:00 | 44036.2917 | 0 | 10.2616 | 39.95
2020-07-24 07:30 | 44036.3125 | 0 | 10.6316 | 39.95
2020-07-24 08:00 | 44036.3333 | 0 | 11.406 | 39.95
2020-07-24 08:30 | 44036.3542 | 0 | 11.8145 | 39.95
2020-07-24 09:00 | 44036.375 | 0 | 12.1034 | 39.95
2020-07-24 09:30 | 44036.3958 | 0 | 11.8868 | 39.95
2020-07-24 10:00 | 44036.4167 | 0 | 11.6654 | 39.95
2020-07-24 10:30 | 44036.4375 | 0 | 11.1907 | 39.95
2020-07-24 11:00 | 44036.4583 | 0 | 11.2538 | 39.95
2020-07-24 11:30 | 44036.4792 | 0 | 10.7094 | 39.95
2020-07-24 12:00 | 44036.5 | 0 | 10.4658 | 39.95
2020-07-24 12:30 | 44036.5208 | 0 | 9.9337 | 39.95
2020-07-24 13:00 | 44036.5417 | 0 | 9.4112 | 39.95
2020-07-24 13:30 | 44036.5625 | 0 | 9.7433 | 39.95
2020-07-24 14:00 | 44036.5833 | 0 | 10.0778 | 39.95
2020-07-24 14:30 | 44036.6042 | 0 | 10.8894 | 39.95
2020-07-24 15:00 | 44036.625 | 0 | 11.1705 | 39.95
2020-07-24 15:30 | 44036.6458 | 0 | 11.063 | 39.95
2020-07-24 16:00 | 44036.6667 | 0 | 11.1601 | 39.95
2020-07-24 16:30 | 44036.6875 | 0 | 11.7005 | 39.95
2020-07-24 17:00 | 44036.7083 | 0 | 12.1884 | 39.95
2020-07-24 17:30 | 44036.7292 | 0 | 12.6865 | 39.95
2020-07-24 18:00 | 44036.75 | 0 | 12.8573 | 39.95
2020-07-24 18:30 | 44036.7708 | 0 | 12.9677 | 39.95
2020-07-24 19:00 | 44036.7917 | 0 | 12.5909 | 39.95
2020-07-24 19:30 | 44036.8125 | 0 | 12.1317 | 39.95
2020-07-24 20:00 | 44036.8333 | 0 | 11.9371 | 39.95
2020-07-24 20:30 | 44036.8542 | 0 | 11.4634 | 39.95
2020-07-24 21:00 | 44036.875 | 0 | 10.9814 | 39.95
2020-07-24 21:30 | 44036.8958 | 0 | 10.4722 | 39.95
2020-07-24 22:00 | 44036.9167 | 0 | 9.9285 | 39.95
2020-07-24 22:30 | 44036.9375 | 0 | 9.3978 | 39.95
2020-07-24 23:00 | 44036.9583 | 0 | 8.9911 | 39.95
2020-07-24 23:30 | 44036.9792 | 0 | 8.4322 | 39.95
2020-07-25 | 44037 | 0 | 7.9576 | 39.95
2020-07-25 00:30 | 44037.0208 | 0 | 7.4619 | 39.95
2020-07-25 01:00 | 44037.0417 | 0 | 7.2594 | 39.95
2020-07-25 01:30 | 44037.0625 | 0 | 7.1237 | 39.95
2020-07-25 02:00 | 44037.0833 | 0 | 7.1527 | 39.95
2020-07-25 02:30 | 44037.1042 | 0 | 7.1705 | 39.95
2020-07-25 03:00 | 44037.125 | 0 | 7.0152 | 39.95
2020-07-25 03:30 | 44037.1458 | 0 | 6.8946 | 39.95
2020-07-25 04:00 | 44037.1667 | 0 | 6.7675 | 39.95
2020-07-25 04:30 | 44037.1875 | 0 | 6.8714 | 39.95
2020-07-25 05:00 | 44037.2083 | 0 | 7.0438 | 39.95
2020-07-25 05:30 | 44037.2292 | 0 | 7.2593 | 39.95
2020-07-25 06:00 | 44037.25 | 0 | 7.4863 | 39.95
2020-07-25 06:30 | 44037.2708 | 0 | 7.6655 | 39.95
2020-07-25 07:00 | 44037.2917 | 0 | 8.057 | 39.95
2020-07-25 07:30 | 44037.3125 | 0 | 8.4604 | 39.95
2020-07-25 08:00 | 44037.3333 | 0 | 8.908 | 39.95
2020-07-25 08:30 | 44037.3542 | 0 | 9.1101 | 39.95
2020-07-25 09:00 | 44037.375 | 0 | 9.0744 | 39.95
2020-07-25 09:30 | 44037.3958 | 0 | 8.7017 | 39.95
2020-07-25 10:00 | 44037.4167 | 0 | 8.3692 | 39.95
2020-07-25 10:30 | 44037.4375 | 0 | 8.833 | 39.95
2020-07-25 11:00 | 44037.4583 | 0 | 9.8577 | 39.95
2020-07-25 11:30 | 44037.4792 | 0 | 9.5731 | 39.95
2020-07-25 12:00 | 44037.5 | 0 | 9.036 | 39.95
2020-07-25 12:30 | 44037.5208 | 0 | 7.2829 | 39.95
2020-07-25 13:00 | 44037.5417 | 0 | 7.1435 | 39.95
2020-07-25 13:30 | 44037.5625 | 0 | 7.4095 | 39.95
2020-07-25 14:00 | 44037.5833 | 0 | 7.2332 | 39.95
2020-07-25 14:30 | 44037.6042 | 0 | 7.5161 | 39.95
2020-07-25 15:00 | 44037.625 | 0 | 8.0547 | 39.95
2020-07-25 15:30 | 44037.6458 | 0 | 8.9394 | 39.95
2020-07-25 16:00 | 44037.6667 | 0 | 10.425 | 39.95
2020-07-25 16:30 | 44037.6875 | 0 | 11.1366 | 39.95
2020-07-25 17:00 | 44037.7083 | 0 | 11.4786 | 39.95
2020-07-25 17:30 | 44037.7292 | 0 | 12.2014 | 39.95
2020-07-25 18:00 | 44037.75 | 0 | 12.6622 | 39.95
2020-07-25 18:30 | 44037.7708 | 0 | 12.7445 | 39.95
2020-07-25 19:00 | 44037.7917 | 0 | 12.4988 | 39.95
2020-07-25 19:30 | 44037.8125 | 0 | 12.1043 | 39.95
2020-07-25 20:00 | 44037.8333 | 0 | 12.066 | 39.95
2020-07-25 20:30 | 44037.8542 | 0 | 11.4553 | 39.95
2020-07-25 21:00 | 44037.875 | 0 | 10.8809 | 39.95
2020-07-25 21:30 | 44037.8958 | 0 | 10.4352 | 39.95
2020-07-25 22:00 | 44037.9167 | 0 | 9.9154 | 39.95
2020-07-25 22:30 | 44037.9375 | 0 | 9.1939 | 39.95
2020-07-25 23:00 | 44037.9583 | 0 | 8.6229 | 39.95
2020-07-25 23:30 | 44037.9792 | 0 | 8.1858 | 39.95
2020-07-26 | 44038 | 0 | 7.6879 | 39.95
2020-07-26 00:30 | 44038.0208 | 0 | 7.3811 | 39.95
2020-07-26 01:00 | 44038.0417 | 0 | 7.175 | 39.95
2020-07-26 01:30 | 44038.0625 | 0 | 7.197 | 39.95
2020-07-26 02:00 | 44038.0833 | 0 | 7.1613 | 39.95
2020-07-26 02:30 | 44038.1042 | 0 | 7.2405 | 39.95
2020-07-26 03:00 | 44038.125 | 0 | 7.1429 | 39.95
2020-07-26 03:30 | 44038.1458 | 0 | 7.1394 | 39.95
2020-07-26 04:00 | 44038.1667 | 0 | 7.4556 | 39.95
2020-07-26 04:30 | 44038.1875 | 0 | 7.8854 | 39.95
2020-07-26 05:00 | 44038.2083 | 0 | 8.6713 | 39.95
2020-07-26 05:30 | 44038.2292 | 0 | 9.654 | 39.95
2020-07-26 06:00 | 44038.25 | 0 | 11.1346 | 39.95
2020-07-26 06:30 | 44038.2708 | 0 | 12.4528 | 39.95
2020-07-26 07:00 | 44038.2917 | 0 | 13.4603 | 39.95
2020-07-26 07:30 | 44038.3125 | 0 | 13.0727 | 39.95
2020-07-26 08:00 | 44038.3333 | 0 | 12.3387 | 39.95
2020-07-26 08:30 | 44038.3542 | 0 | 11.672 | 39.95
2020-07-26 09:00 | 44038.375 | 0 | 10.9429 | 39.95
2020-07-26 09:30 | 44038.3958 | 0 | 11.3761 | 39.95
2020-07-26 10:00 | 44038.4167 | 0 | 10.9527 | 39.95
2020-07-26 10:30 | 44038.4375 | 0 | 11.43 | 39.95
2020-07-26 11:00 | 44038.4583 | 0 | 11.5073 | 39.95
2020-07-26 11:30 | 44038.4792 | 0 | 12.0008 | 39.95
2020-07-26 12:00 | 44038.5 | 0 | 10.4932 | 39.95
2020-07-26 12:30 | 44038.5208 | 0 | 9.8422 | 39.95
2020-07-26 13:00 | 44038.5417 | 0 | 10.8511 | 39.95
2020-07-26 13:30 | 44038.5625 | 0 | 9.7669 | 39.95
2020-07-26 14:00 | 44038.5833 | 0 | 10.4783 | 39.95
2020-07-26 14:30 | 44038.6042 | 0 | 11.1419 | 39.95
2020-07-26 15:00 | 44038.625 | 0 | 11.2361 | 39.95
2020-07-26 15:30 | 44038.6458 | 0 | 11.7205 | 39.95
2020-07-26 16:00 | 44038.6667 | 0 | 12.105 | 39.95
2020-07-26 16:30 | 44038.6875 | 0 | 12.9319 | 39.95
2020-07-26 17:00 | 44038.7083 | 0 | 13.6065 | 39.95
2020-07-26 17:30 | 44038.7292 | 0 | 14.8472 | 39.95
2020-07-26 18:00 | 44038.75 | 0 | 15.2724 | 39.95
2020-07-26 18:30 | 44038.7708 | 0 | 15.5365 | 39.95
2020-07-26 19:00 | 44038.7917 | 0 | 15.6225 | 39.95
2020-07-26 19:30 | 44038.8125 | 0 | 15.0565 | 39.95
2020-07-26 20:00 | 44038.8333 | 0 | 14.5466 | 39.95
2020-07-26 20:30 | 44038.8542 | 0 | 13.7757 | 39.95
2020-07-26 21:00 | 44038.875 | 0 | 13.0229 | 39.95
2020-07-26 21:30 | 44038.8958 | 0 | 12.4754 | 39.95
2020-07-26 22:00 | 44038.9167 | 0 | 11.6421 | 39.95
2020-07-26 22:30 | 44038.9375 | 0 | 10.67 | 39.95
2020-07-26 23:00 | 44038.9583 | 0 | 9.9803 | 39.95
2020-07-26 23:30 | 44038.9792 | 0 | 9.2825 | 39.95
2020-07-27 | 44039 | 0 | 8.5925 | 39.95
2020-07-27 00:30 | 44039.0208 | 0 | 8.1985 | 39.95
2020-07-27 01:00 | 44039.0417 | 0 | 7.9887 | 39.95
2020-07-27 01:30 | 44039.0625 | 0 | 7.7459 | 39.95
2020-07-27 02:00 | 44039.0833 | 0 | 7.7501 | 39.95
2020-07-27 02:30 | 44039.1042 | 0 | 7.7283 | 39.95
2020-07-27 03:00 | 44039.125 | 0 | 7.597 | 39.95
2020-07-27 03:30 | 44039.1458 | 0 | 7.6534 | 39.95
2020-07-27 04:00 | 44039.1667 | 0 | 7.7596 | 39.95
2020-07-27 04:30 | 44039.1875 | 0 | 8.3654 | 39.95
2020-07-27 05:00 | 44039.2083 | 0 | 9.136 | 39.95
2020-07-27 05:30 | 44039.2292 | 0 | 10.0977 | 39.95
2020-07-27 06:00 | 44039.25 | 0 | 11.4342 | 39.95
2020-07-27 06:30 | 44039.2708 | 0 | 12.8251 | 39.95
2020-07-27 07:00 | 44039.2917 | 0 | 13.417 | 39.95
2020-07-27 07:30 | 44039.3125 | 0 | 13.1985 | 39.95
2020-07-27 08:00 | 44039.3333 | 0 | 12.3027 | 39.95
2020-07-27 08:30 | 44039.3542 | 0 | 11.6612 | 39.95
2020-07-27 09:00 | 44039.375 | 0 | 10.8362 | 39.95
2020-07-27 09:30 | 44039.3958 | 0 | 10.0121 | 39.95
2020-07-27 10:00 | 44039.4167 | 0 | 9.4576 | 39.95
2020-07-27 10:30 | 44039.4375 | 0 | 9.1874 | 39.95
2020-07-27 11:00 | 44039.4583 | 0 | 8.9699 | 39.95
2020-07-27 11:30 | 44039.4792 | 0 | 8.6646 | 39.95
2020-07-27 12:00 | 44039.5 | 0 | 8.4797 | 39.95
2020-07-27 12:30 | 44039.5208 | 0 | 8.5256 | 39.95
2020-07-27 13:00 | 44039.5417 | 0 | 8.5547 | 39.95
2020-07-27 13:30 | 44039.5625 | 0 | 8.9025 | 39.95
2020-07-27 14:00 | 44039.5833 | 0 | 9.1423 | 39.95
2020-07-27 14:30 | 44039.6042 | 0 | 9.4765 | 39.95
2020-07-27 15:00 | 44039.625 | 0 | 9.8009 | 39.95
2020-07-27 15:30 | 44039.6458 | 0 | 10.3855 | 39.95
2020-07-27 16:00 | 44039.6667 | 0 | 11.0372 | 39.95
2020-07-27 16:30 | 44039.6875 | 0 | 11.7331 | 39.95
2020-07-27 17:00 | 44039.7083 | 0 | 12.7015 | 39.95
2020-07-27 17:30 | 44039.7292 | 0 | 13.828 | 39.95
2020-07-27 18:00 | 44039.75 | 0 | 14.4803 | 39.95
2020-07-27 18:30 | 44039.7708 | 0 | 14.9954 | 39.95
2020-07-27 19:00 | 44039.7917 | 0 | 14.8462 | 39.95
2020-07-27 19:30 | 44039.8125 | 0 | 14.4531 | 39.95
2020-07-27 20:00 | 44039.8333 | 0 | 14.4226 | 39.95
2020-07-27 20:30 | 44039.8542 | 0 | 13.8378 | 39.95
2020-07-27 21:00 | 44039.875 | 0 | 13.059 | 39.95
2020-07-27 21:30 | 44039.8958 | 0 | 12.3086 | 39.95
2020-07-27 22:00 | 44039.9167 | 0 | 11.6637 | 39.95
2020-07-27 22:30 | 44039.9375 | 0 | 10.7132 | 39.95
2020-07-27 23:00 | 44039.9583 | 0 | 9.7864 | 39.95
2020-07-27 23:30 | 44039.9792 | 0 | 9.1029 | 39.95
2020-07-28 | 44040 | 0 | 8.3443 | 39.95
2020-07-28 00:30 | 44040.0208 | 0 | 8.0402 | 39.95
2020-07-28 01:00 | 44040.0417 | 0 | 7.6139 | 39.95
2020-07-28 01:30 | 44040.0625 | 0 | 7.4928 | 39.95
2020-07-28 02:00 | 44040.0833 | 0 | 7.5034 | 39.95
2020-07-28 02:30 | 44040.1042 | 0 | 7.4512 | 39.95
2020-07-28 03:00 | 44040.125 | 0 | 7.4822 | 39.95
2020-07-28 03:30 | 44040.1458 | 0 | 7.5104 | 39.95
2020-07-28 04:00 | 44040.1667 | 0 | 7.7955 | 39.95
2020-07-28 04:30 | 44040.1875 | 0 | 8.4362 | 39.95
2020-07-28 05:00 | 44040.2083 | 0 | 9.1817 | 39.95
2020-07-28 05:30 | 44040.2292 | 0 | 10.2945 | 39.95
2020-07-28 06:00 | 44040.25 | 0 | 11.8002 | 39.95
2020-07-28 06:30 | 44040.2708 | 0 | 13.3632 | 39.95
2020-07-28 07:00 | 44040.2917 | 0 | 14.4322 | 39.95
2020-07-28 07:30 | 44040.3125 | 0 | 13.9101 | 39.95
2020-07-28 08:00 | 44040.3333 | 0 | 12.9578 | 39.95
2020-07-28 08:30 | 44040.3542 | 0 | 12.0196 | 39.95
2020-07-28 09:00 | 44040.375 | 0 | 11.0109 | 39.95
2020-07-28 09:30 | 44040.3958 | 0 | 10.3985 | 39.95
2020-07-28 10:00 | 44040.4167 | 0 | 10.024 | 39.95
2020-07-28 10:30 | 44040.4375 | 0 | 9.6563 | 39.95
2020-07-28 11:00 | 44040.4583 | 0 | 9.2434 | 39.95
2020-07-28 11:30 | 44040.4792 | 0 | 9.1994 | 39.95
2020-07-28 12:00 | 44040.5 | 0 | 8.8978 | 39.95
2020-07-28 12:30 | 44040.5208 | 0 | 8.8551 | 39.95
2020-07-28 13:00 | 44040.5417 | 0 | 8.9017 | 39.95
2020-07-28 13:30 | 44040.5625 | 0 | 9.116 | 39.95
2020-07-28 14:00 | 44040.5833 | 0 | 9.5324 | 39.95
2020-07-28 14:30 | 44040.6042 | 0 | 9.7751 | 39.95
2020-07-28 15:00 | 44040.625 | 0 | 10.2701 | 39.95
2020-07-28 15:30 | 44040.6458 | 0 | 10.5798 | 39.95
2020-07-28 16:00 | 44040.6667 | 0 | 11.2537 | 39.95
2020-07-28 16:30 | 44040.6875 | 0 | 11.9952 | 39.95
2020-07-28 17:00 | 44040.7083 | 0 | 12.5629 | 39.95
2020-07-28 17:30 | 44040.7292 | 0 | 13.6965 | 39.95
2020-07-28 18:00 | 44040.75 | 0 | 14.0262 | 39.95
2020-07-28 18:30 | 44040.7708 | 0 | 14.4989 | 39.95
2020-07-28 19:00 | 44040.7917 | 0 | 14.1816 | 39.95
2020-07-28 19:30 | 44040.8125 | 0 | 14.0018 | 39.95
2020-07-28 20:00 | 44040.8333 | 0 | 13.8857 | 39.95
2020-07-28 20:30 | 44040.8542 | 0 | 13.3971 | 39.95
2020-07-28 21:00 | 44040.875 | 0 | 12.7355 | 39.95
2020-07-28 21:30 | 44040.8958 | 0 | 12.2119 | 39.95
2020-07-28 22:00 | 44040.9167 | 0 | 11.4922 | 39.95
2020-07-28 22:30 | 44040.9375 | 0 | 10.675 | 39.95
2020-07-28 23:00 | 44040.9583 | 0 | 9.9209 | 39.95
2020-07-28 23:30 | 44040.9792 | 0 | 9.2256 | 39.95
2020-07-29 | 44041 | 0 | 8.5764 | 39.95
2020-07-29 00:30 | 44041.0208 | 0 | 8.0779 | 39.95
2020-07-29 01:00 | 44041.0417 | 0 | 7.8919 | 39.95
2020-07-29 01:30 | 44041.0625 | 0 | 7.7218 | 39.95
2020-07-29 02:00 | 44041.0833 | 0 | 7.6416 | 39.95
2020-07-29 02:30 | 44041.1042 | 0 | 7.6068 | 39.95
2020-07-29 03:00 | 44041.125 | 0 | 7.6127 | 39.95
2020-07-29 03:30 | 44041.1458 | 0 | 7.6911 | 39.95
2020-07-29 04:00 | 44041.1667 | 0 | 7.984 | 39.95
2020-07-29 04:30 | 44041.1875 | 0 | 8.6133 | 39.95
2020-07-29 05:00 | 44041.2083 | 0 | 9.2587 | 39.95
2020-07-29 05:30 | 44041.2292 | 0 | 10.1975 | 39.95
2020-07-29 06:00 | 44041.25 | 0 | 11.6014 | 39.95
2020-07-29 06:30 | 44041.2708 | 0 | 12.9985 | 39.95
2020-07-29 07:00 | 44041.2917 | 0 | 13.8566 | 39.95
2020-07-29 07:30 | 44041.3125 | 0 | 13.4265 | 39.95
2020-07-29 08:00 | 44041.3333 | 0 | 12.7777 | 39.95
2020-07-29 08:30 | 44041.3542 | 0 | 11.9553 | 39.95
2020-07-29 09:00 | 44041.375 | 0 | 11.0907 | 39.95
2020-07-29 09:30 | 44041.3958 | 0 | 10.2602 | 39.95
2020-07-29 10:00 | 44041.4167 | 0 | 9.8895 | 39.95
2020-07-29 10:30 | 44041.4375 | 0 | 9.5831 | 39.95
2020-07-29 11:00 | 44041.4583 | 0 | 9.3598 | 39.95
2020-07-29 11:30 | 44041.4792 | 0 | 9.2321 | 39.95
2020-07-29 12:00 | 44041.5 | 0 | 9.0071 | 39.95
2020-07-29 12:30 | 44041.5208 | 0 | 9.1015 | 39.95
2020-07-29 13:00 | 44041.5417 | 0 | 9.0948 | 39.95
2020-07-29 13:30 | 44041.5625 | 0 | 9.6313 | 39.95
2020-07-29 14:00 | 44041.5833 | 0 | 10.638 | 39.95
2020-07-29 14:30 | 44041.6042 | 0 | 10.9184 | 39.95
2020-07-29 15:00 | 44041.625 | 0 | 11.5849 | 39.95
2020-07-29 15:30 | 44041.6458 | 0 | 11.5268 | 39.95
2020-07-29 16:00 | 44041.6667 | 0 | 11.6109 | 39.95
2020-07-29 16:30 | 44041.6875 | 0 | 12.003 | 39.95
2020-07-29 17:00 | 44041.7083 | 0 | 12.5596 | 39.95
2020-07-29 17:30 | 44041.7292 | 0 | 13.5839 | 39.95
2020-07-29 18:00 | 44041.75 | 0 | 14.1578 | 39.95
2020-07-29 18:30 | 44041.7708 | 0 | 14.4061 | 39.95
2020-07-29 19:00 | 44041.7917 | 0 | 14.124 | 39.95
2020-07-29 19:30 | 44041.8125 | 0 | 13.8843 | 39.95
2020-07-29 20:00 | 44041.8333 | 0 | 13.8384 | 39.95
2020-07-29 20:30 | 44041.8542 | 0 | 13.2946 | 39.95
2020-07-29 21:00 | 44041.875 | 0 | 12.6172 | 39.95
2020-07-29 21:30 | 44041.8958 | 0 | 12.0203 | 39.95
2020-07-29 22:00 | 44041.9167 | 0 | 11.5165 | 39.95
2020-07-29 22:30 | 44041.9375 | 0 | 10.6683 | 39.95
2020-07-29 23:00 | 44041.9583 | 0 | 9.6941 | 39.95
2020-07-29 23:30 | 44041.9792 | 0 | 9.0473 | 39.95
2020-07-30 | 44042 | 0 | 8.4434 | 39.95
2020-07-30 00:30 | 44042.0208 | 0 | 8.1478 | 39.95
2020-07-30 01:00 | 44042.0417 | 0 | 7.9369 | 39.95
2020-07-30 01:30 | 44042.0625 | 0 | 7.7043 | 39.95
2020-07-30 02:00 | 44042.0833 | 0 | 7.7499 | 39.95
2020-07-30 02:30 | 44042.1042 | 0 | 7.729 | 39.95
2020-07-30 03:00 | 44042.125 | 0 | 7.6057 | 39.95
2020-07-30 03:30 | 44042.1458 | 0 | 7.7387 | 39.95
2020-07-30 04:00 | 44042.1667 | 0 | 8.054 | 39.95
2020-07-30 04:30 | 44042.1875 | 0 | 8.3854 | 39.95
2020-07-30 05:00 | 44042.2083 | 0 | 9.0549 | 39.95
2020-07-30 05:30 | 44042.2292 | 0 | 10.0872 | 39.95
2020-07-30 06:00 | 44042.25 | 0 | 11.4341 | 39.95
2020-07-30 06:30 | 44042.2708 | 0 | 12.7458 | 39.95
2020-07-30 07:00 | 44042.2917 | 0 | 13.5272 | 39.95
2020-07-30 07:30 | 44042.3125 | 0 | 13.1068 | 39.95
2020-07-30 08:00 | 44042.3333 | 0 | 12.3131 | 39.95
2020-07-30 08:30 | 44042.3542 | 0 | 11.5449 | 39.95
2020-07-30 09:00 | 44042.375 | 0 | 10.9661 | 39.95
2020-07-30 09:30 | 44042.3958 | 0 | 10.0898 | 39.95
2020-07-30 10:00 | 44042.4167 | 0 | 9.6612 | 39.95
2020-07-30 10:30 | 44042.4375 | 0 | 9.4049 | 39.95
2020-07-30 11:00 | 44042.4583 | 0 | 9.0643 | 39.95
2020-07-30 11:30 | 44042.4792 | 0 | 9.0064 | 39.95
2020-07-30 12:00 | 44042.5 | 0 | 9.486 | 39.95
2020-07-30 12:30 | 44042.5208 | 0 | 9.1555 | 39.95
2020-07-30 13:00 | 44042.5417 | 0 | 9.2103 | 39.95
2020-07-30 13:30 | 44042.5625 | 0 | 9.5816 | 39.95
2020-07-30 14:00 | 44042.5833 | 0 | 9.3433 | 39.95
2020-07-30 14:30 | 44042.6042 | 0 | 9.5771 | 39.95
2020-07-30 15:00 | 44042.625 | 0 | 9.9405 | 39.95
2020-07-30 15:30 | 44042.6458 | 0 | 10.53 | 39.95
2020-07-30 16:00 | 44042.6667 | 0 | 11.129 | 39.95
2020-07-30 16:30 | 44042.6875 | 0 | 11.8018 | 39.95
2020-07-30 17:00 | 44042.7083 | 0 | 12.3808 | 39.95
2020-07-30 17:30 | 44042.7292 | 0 | 13.1778 | 39.95
2020-07-30 18:00 | 44042.75 | 0 | 13.5182 | 39.95
2020-07-30 18:30 | 44042.7708 | 0 | 13.8716 | 39.95
2020-07-30 19:00 | 44042.7917 | 0 | 13.6247 | 39.95
2020-07-30 19:30 | 44042.8125 | 0 | 13.3963 | 39.95
2020-07-30 20:00 | 44042.8333 | 0 | 13.3743 | 39.95
2020-07-30 20:30 | 44042.8542 | 0 | 12.8408 | 39.95
2020-07-30 21:00 | 44042.875 | 0 | 12.2684 | 39.95
2020-07-30 21:30 | 44042.8958 | 0 | 11.8972 | 39.95
2020-07-30 22:00 | 44042.9167 | 0 | 11.2426 | 39.95
2020-07-30 22:30 | 44042.9375 | 0 | 10.5659 | 39.95
2020-07-30 23:00 | 44042.9583 | 0 | 9.659 | 39.95
2020-07-30 23:30 | 44042.9792 | 0 | 9.144 | 39.95
2020-07-31 | 44043 | 0 | 8.4798 | 39.95
2020-07-31 00:30 | 44043.0208 | 0 | 7.9913 | 39.95
2020-07-31 01:00 | 44043.0417 | 0 | 7.9986 | 39.95
2020-07-31 01:30 | 44043.0625 | 0 | 7.8577 | 39.95
2020-07-31 02:00 | 44043.0833 | 0 | 7.7111 | 39.95
2020-07-31 02:30 | 44043.1042 | 0 | 7.674 | 39.95
2020-07-31 03:00 | 44043.125 | 0 | 7.5886 | 39.95
2020-07-31 03:30 | 44043.1458 | 0 | 7.6028 | 39.95
2020-07-31 04:00 | 44043.1667 | 0 | 7.6755 | 39.95
2020-07-31 04:30 | 44043.1875 | 0 | 7.9382 | 39.95
2020-07-31 05:00 | 44043.2083 | 0 | 8.1065 | 39.95
2020-07-31 05:30 | 44043.2292 | 0 | 8.3922 | 39.95
2020-07-31 06:00 | 44043.25 | 0 | 8.85 | 39.95
2020-07-31 06:30 | 44043.2708 | 0 | 9.5067 | 39.95
2020-07-31 07:00 | 44043.2917 | 0 | 9.9471 | 39.95
2020-07-31 07:30 | 44043.3125 | 0 | 9.9836 | 39.95
2020-07-31 08:00 | 44043.3333 | 0 | 9.9788 | 39.95
2020-07-31 08:30 | 44043.3542 | 0 | 9.8482 | 39.95
2020-07-31 09:00 | 44043.375 | 0 | 8.9508 | 39.95
2020-07-31 09:30 | 44043.3958 | 0 | 8.6297 | 39.95
2020-07-31 10:00 | 44043.4167 | 0 | 8.4303 | 39.95
2020-07-31 10:30 | 44043.4375 | 0 | 7.8529 | 39.95
2020-07-31 11:00 | 44043.4583 | 0 | 8.5647 | 39.95
2020-07-31 11:30 | 44043.4792 | 0 | 8.4432 | 39.95
2020-07-31 12:00 | 44043.5 | 0 | 8.1762 | 39.95
2020-07-31 12:30 | 44043.5208 | 0 | 7.81 | 39.95
2020-07-31 13:00 | 44043.5417 | 0 | 9.4179 | 39.95
2020-07-31 13:30 | 44043.5625 | 0 | 8.4975 | 39.95
2020-07-31 14:00 | 44043.5833 | 0 | 7.648 | 39.95
2020-07-31 14:30 | 44043.6042 | 0 | 8.1515 | 39.95
2020-07-31 15:00 | 44043.625 | 0 | 8.1052 | 39.95
2020-07-31 15:30 | 44043.6458 | 0 | 8.5196 | 39.95
2020-07-31 16:00 | 44043.6667 | 0 | 9.1279 | 39.95
2020-07-31 16:30 | 44043.6875 | 0 | 10.03 | 39.95
2020-07-31 17:00 | 44043.7083 | 0 | 10.6809 | 39.95
2020-07-31 17:30 | 44043.7292 | 0 | 11.5582 | 39.95
2020-07-31 18:00 | 44043.75 | 0 | 11.9449 | 39.95
2020-07-31 18:30 | 44043.7708 | 0 | 11.9884 | 39.95
2020-07-31 19:00 | 44043.7917 | 0 | 11.9446 | 39.95
2020-07-31 19:30 | 44043.8125 | 0 | 11.6029 | 39.95
2020-07-31 20:00 | 44043.8333 | 0 | 11.3816 | 39.95
2020-07-31 20:30 | 44043.8542 | 0 | 11.0225 | 39.95
2020-07-31 21:00 | 44043.875 | 0 | 10.5356 | 39.95
2020-07-31 21:30 | 44043.8958 | 0 | 10.2624 | 39.95
2020-07-31 22:00 | 44043.9167 | 0 | 9.7807 | 39.95
2020-07-31 22:30 | 44043.9375 | 0 | 9.2856 | 39.95
2020-07-31 23:00 | 44043.9583 | 0 | 8.8585 | 39.95
2020-07-31 23:30 | 44043.9792 | 0 | 8.2981 | 39.95
2020-08-01 | 44044 | 0 | 7.8938 | 39.95
2020-08-01 00:30 | 44044.0208 | 0 | 7.5368 | 39.95
2020-08-01 01:00 | 44044.0417 | 0 | 7.2469 | 39.95
2020-08-01 01:30 | 44044.0625 | 0 | 7.127 | 39.95
2020-08-01 02:00 | 44044.0833 | 0 | 7.1464 | 39.95
2020-08-01 02:30 | 44044.1042 | 0 | 7.0395 | 39.95
2020-08-01 03:00 | 44044.125 | 0 | 6.8813 | 39.95
2020-08-01 03:30 | 44044.1458 | 0 | 6.8979 | 39.95
2020-08-01 04:00 | 44044.1667 | 0 | 6.7851 | 39.95
2020-08-01 04:30 | 44044.1875 | 0 | 6.9254 | 39.95
2020-08-01 05:00 | 44044.2083 | 0 | 7.0631 | 39.95
2020-08-01 05:30 | 44044.2292 | 0 | 7.334 | 39.95
2020-08-01 06:00 | 44044.25 | 0 | 7.769 | 39.95
2020-08-01 06:30 | 44044.2708 | 0 | 8.0967 | 39.95
2020-08-01 07:00 | 44044.2917 | 0 | 8.3637 | 39.95
2020-08-01 07:30 | 44044.3125 | 0 | 8.2392 | 39.95
2020-08-01 08:00 | 44044.3333 | 0 | 8.2892 | 39.95
2020-08-01 08:30 | 44044.3542 | 0 | 8.2291 | 39.95
2020-08-01 09:00 | 44044.375 | 0 | 7.7103 | 39.95
2020-08-01 09:30 | 44044.3958 | 0 | 7.4742 | 39.95
2020-08-01 10:00 | 44044.4167 | 0 | 7.0631 | 39.95
2020-08-01 10:30 | 44044.4375 | 0 | 6.7354 | 39.95
2020-08-01 11:00 | 44044.4583 | 0 | 6.323 | 39.95
2020-08-01 11:30 | 44044.4792 | 0 | 6.2921 | 39.95
2020-08-01 12:00 | 44044.5 | 0 | 6.4148 | 39.95
2020-08-01 12:30 | 44044.5208 | 0 | 6.3764 | 39.95
2020-08-01 13:00 | 44044.5417 | 0 | 6.7179 | 39.95
2020-08-01 13:30 | 44044.5625 | 0 | 6.8463 | 39.95
2020-08-01 14:00 | 44044.5833 | 0 | 7.6993 | 39.95
2020-08-01 14:30 | 44044.6042 | 0 | 7.1427 | 39.95
2020-08-01 15:00 | 44044.625 | 0 | 7.5611 | 39.95
2020-08-01 15:30 | 44044.6458 | 0 | 8.4213 | 39.95
2020-08-01 16:00 | 44044.6667 | 0 | 8.9943 | 39.95
2020-08-01 16:30 | 44044.6875 | 0 | 9.9456 | 39.95
2020-08-01 17:00 | 44044.7083 | 0 | 10.8097 | 39.95
2020-08-01 17:30 | 44044.7292 | 0 | 11.7646 | 39.95
2020-08-01 18:00 | 44044.75 | 0 | 12.3448 | 39.95
2020-08-01 18:30 | 44044.7708 | 0 | 12.4112 | 39.95
2020-08-01 19:00 | 44044.7917 | 0 | 11.9739 | 39.95
2020-08-01 19:30 | 44044.8125 | 0 | 11.7124 | 39.95
2020-08-01 20:00 | 44044.8333 | 0 | 11.4746 | 39.95
2020-08-01 20:30 | 44044.8542 | 0 | 11.0246 | 39.95
2020-08-01 21:00 | 44044.875 | 0 | 10.5005 | 39.95
2020-08-01 21:30 | 44044.8958 | 0 | 10.0236 | 39.95
2020-08-01 22:00 | 44044.9167 | 0 | 9.6249 | 39.95
2020-08-01 22:30 | 44044.9375 | 0 | 8.9142 | 39.95
2020-08-01 23:00 | 44044.9583 | 0 | 8.2903 | 39.95
2020-08-01 23:30 | 44044.9792 | 0 | 7.8707 | 39.95
2020-08-02 | 44045 | 0 | 7.4847 | 39.95
2020-08-02 00:30 | 44045.0208 | 0 | 7.255 | 39.95
2020-08-02 01:00 | 44045.0417 | 0 | 7.0406 | 39.95
2020-08-02 01:30 | 44045.0625 | 0 | 7.0453 | 39.95
2020-08-02 02:00 | 44045.0833 | 0 | 7.0594 | 39.95
2020-08-02 02:30 | 44045.1042 | 0 | 7.036 | 39.95
2020-08-02 03:00 | 44045.125 | 0 | 7.0794 | 39.95
2020-08-02 03:30 | 44045.1458 | 0 | 7.1383 | 39.95
2020-08-02 04:00 | 44045.1667 | 0 | 7.3411 | 39.95
2020-08-02 04:30 | 44045.1875 | 0 | 7.7992 | 39.95
2020-08-02 05:00 | 44045.2083 | 0 | 8.74 | 39.95
2020-08-02 05:30 | 44045.2292 | 0 | 9.5954 | 39.95
2020-08-02 06:00 | 44045.25 | 0 | 10.9512 | 39.95
2020-08-02 06:30 | 44045.2708 | 0 | 12.2129 | 39.95
2020-08-02 07:00 | 44045.2917 | 0 | 13.0708 | 39.95
2020-08-02 07:30 | 44045.3125 | 0 | 12.7983 | 39.95
2020-08-02 08:00 | 44045.3333 | 0 | 12.2942 | 39.95
2020-08-02 08:30 | 44045.3542 | 0 | 11.9872 | 39.95
2020-08-02 09:00 | 44045.375 | 0 | 11.8207 | 39.95
2020-08-02 09:30 | 44045.3958 | 0 | 11.4876 | 39.95
2020-08-02 10:00 | 44045.4167 | 0 | 10.721 | 39.95
2020-08-02 10:30 | 44045.4375 | 0 | 10.4103 | 39.95
2020-08-02 11:00 | 44045.4583 | 0 | 9.9487 | 39.95
2020-08-02 11:30 | 44045.4792 | 0 | 9.7616 | 39.95
2020-08-02 12:00 | 44045.5 | 0 | 9.5241 | 39.95
2020-08-02 12:30 | 44045.5208 | 0 | 8.9507 | 39.95
2020-08-02 13:00 | 44045.5417 | 0 | 9.1444 | 39.95
2020-08-02 13:30 | 44045.5625 | 0 | 9.986 | 39.95
2020-08-02 14:00 | 44045.5833 | 0 | 10.0368 | 39.95
2020-08-02 14:30 | 44045.6042 | 0 | 11.048 | 39.95
2020-08-02 15:00 | 44045.625 | 0 | 10.4836 | 39.95
2020-08-02 15:30 | 44045.6458 | 0 | 10.2096 | 39.95
2020-08-02 16:00 | 44045.6667 | 0 | 11.4869 | 39.95
2020-08-02 16:30 | 44045.6875 | 0 | 12.0366 | 39.95
2020-08-02 17:00 | 44045.7083 | 0 | 12.634 | 39.95
2020-08-02 17:30 | 44045.7292 | 0 | 13.6975 | 39.95
2020-08-02 18:00 | 44045.75 | 0 | 14.2515 | 39.95
2020-08-02 18:30 | 44045.7708 | 0 | 14.6449 | 39.95
2020-08-02 19:00 | 44045.7917 | 0 | 14.2244 | 39.95
2020-08-02 19:30 | 44045.8125 | 0 | 14.0702 | 39.95
2020-08-02 20:00 | 44045.8333 | 0 | 13.8435 | 39.95
2020-08-02 20:30 | 44045.8542 | 0 | 13.0426 | 39.95
2020-08-02 21:00 | 44045.875 | 0 | 12.3279 | 39.95
2020-08-02 21:30 | 44045.8958 | 0 | 11.8893 | 39.95
2020-08-02 22:00 | 44045.9167 | 0 | 11.4714 | 39.95
2020-08-02 22:30 | 44045.9375 | 0 | 10.6642 | 39.95
2020-08-02 23:00 | 44045.9583 | 0 | 9.872 | 39.95
2020-08-02 23:30 | 44045.9792 | 0 | 9.254 | 39.95
2020-08-03 | 44046 | 0 | 8.6044 | 39.95
2020-08-03 00:30 | 44046.0208 | 0 | 8.0994 | 39.95
2020-08-03 01:00 | 44046.0417 | 0 | 7.9744 | 39.95
2020-08-03 01:30 | 44046.0625 | 0 | 7.9042 | 39.95
2020-08-03 02:00 | 44046.0833 | 0 | 7.8156 | 39.95
2020-08-03 02:30 | 44046.1042 | 0 | 7.7882 | 39.95
2020-08-03 03:00 | 44046.125 | 0 | 7.7717 | 39.95
2020-08-03 03:30 | 44046.1458 | 0 | 7.8322 | 39.95
2020-08-03 04:00 | 44046.1667 | 0 | 7.8775 | 39.95
2020-08-03 04:30 | 44046.1875 | 0 | 8.371 | 39.95
2020-08-03 05:00 | 44046.2083 | 0 | 9.0159 | 39.95
2020-08-03 05:30 | 44046.2292 | 0 | 9.76 | 39.95
2020-08-03 06:00 | 44046.25 | 0 | 11.1667 | 39.95
2020-08-03 06:30 | 44046.2708 | 0 | 12.2264 | 39.95
2020-08-03 07:00 | 44046.2917 | 0 | 12.8129 | 39.95
2020-08-03 07:30 | 44046.3125 | 0 | 12.7644 | 39.95
2020-08-03 08:00 | 44046.3333 | 0 | 12.6848 | 39.95
2020-08-03 08:30 | 44046.3542 | 0 | 12.4557 | 39.95
2020-08-03 09:00 | 44046.375 | 0 | 12.0323 | 39.95
2020-08-03 09:30 | 44046.3958 | 0 | 11.4358 | 39.95
2020-08-03 10:00 | 44046.4167 | 0 | 10.9917 | 39.95
2020-08-03 10:30 | 44046.4375 | 0 | 10.7543 | 39.95
2020-08-03 11:00 | 44046.4583 | 0 | 9.9653 | 39.95
2020-08-03 11:30 | 44046.4792 | 0 | 8.9777 | 39.95
2020-08-03 12:00 | 44046.5 | 0 | 9.6271 | 39.95
2020-08-03 12:30 | 44046.5208 | 0 | 9.1292 | 39.95
2020-08-03 13:00 | 44046.5417 | 0 | 9.3084 | 39.95
2020-08-03 13:30 | 44046.5625 | 0 | 10.1182 | 39.95
2020-08-03 14:00 | 44046.5833 | 0 | 9.7363 | 39.95
2020-08-03 14:30 | 44046.6042 | 0 | 10.1587 | 39.95
2020-08-03 15:00 | 44046.625 | 0 | 10.2015 | 39.95
2020-08-03 15:30 | 44046.6458 | 0 | 10.5435 | 39.95
2020-08-03 16:00 | 44046.6667 | 0 | 11.1882 | 39.95
2020-08-03 16:30 | 44046.6875 | 0 | 12.0285 | 39.95
2020-08-03 17:00 | 44046.7083 | 0 | 12.6822 | 39.95
2020-08-03 17:30 | 44046.7292 | 0 | 13.6117 | 39.95
2020-08-03 18:00 | 44046.75 | 0 | 14.106 | 39.95
2020-08-03 18:30 | 44046.7708 | 0 | 14.4804 | 39.95
2020-08-03 19:00 | 44046.7917 | 0 | 14.1052 | 39.95
2020-08-03 19:30 | 44046.8125 | 0 | 13.8791 | 39.95
2020-08-03 20:00 | 44046.8333 | 0 | 13.5971 | 39.95
2020-08-03 20:30 | 44046.8542 | 0 | 13.3566 | 39.95
2020-08-03 21:00 | 44046.875 | 0 | 12.7209 | 39.95
2020-08-03 21:30 | 44046.8958 | 0 | 12.1824 | 39.95
2020-08-03 22:00 | 44046.9167 | 0 | 11.5793 | 39.95
2020-08-03 22:30 | 44046.9375 | 0 | 10.5281 | 39.95
2020-08-03 23:00 | 44046.9583 | 0 | 9.701 | 39.95
2020-08-03 23:30 | 44046.9792 | 0 | 9.2376 | 39.95
2020-08-04 | 44047 | 0 | 8.7351 | 39.95
2020-08-04 00:30 | 44047.0208 | 0 | 8.3444 | 39.95
2020-08-04 01:00 | 44047.0417 | 0 | 8.1026 | 39.95
2020-08-04 01:30 | 44047.0625 | 0 | 7.9893 | 39.95
2020-08-04 02:00 | 44047.0833 | 0 | 7.9661 | 39.95
2020-08-04 02:30 | 44047.1042 | 0 | 7.9653 | 39.95
2020-08-04 03:00 | 44047.125 | 0 | 7.9206 | 39.95
2020-08-04 03:30 | 44047.1458 | 0 | 7.8076 | 39.95
2020-08-04 04:00 | 44047.1667 | 0 | 7.9602 | 39.95
2020-08-04 04:30 | 44047.1875 | 0 | 8.4368 | 39.95
2020-08-04 05:00 | 44047.2083 | 0 | 9.1363 | 39.95
2020-08-04 05:30 | 44047.2292 | 0 | 10.1527 | 39.95
2020-08-04 06:00 | 44047.25 | 0 | 11.4522 | 39.95
2020-08-04 06:30 | 44047.2708 | 0 | 12.7704 | 39.95
2020-08-04 07:00 | 44047.2917 | 0 | 13.4717 | 39.95
2020-08-04 07:30 | 44047.3125 | 0 | 13.2888 | 39.95
2020-08-04 08:00 | 44047.3333 | 0 | 12.4605 | 39.95
2020-08-04 08:30 | 44047.3542 | 0 | 11.5042 | 39.95
2020-08-04 09:00 | 44047.375 | 0 | 10.7098 | 39.95
2020-08-04 09:30 | 44047.3958 | 0 | 10.1301 | 39.95
2020-08-04 10:00 | 44047.4167 | 0 | 9.7299 | 39.95
2020-08-04 10:30 | 44047.4375 | 0 | 9.441 | 39.95
2020-08-04 11:00 | 44047.4583 | 0 | 9.2334 | 39.95
2020-08-04 11:30 | 44047.4792 | 0 | 9.063 | 39.95
2020-08-04 12:00 | 44047.5 | 0 | 9.1882 | 39.95
2020-08-04 12:30 | 44047.5208 | 0 | 9.2896 | 39.95
2020-08-04 13:00 | 44047.5417 | 0 | 9.3623 | 39.95
2020-08-04 13:30 | 44047.5625 | 0 | 9.8979 | 39.95
2020-08-04 14:00 | 44047.5833 | 0 | 10.103 | 39.95
2020-08-04 14:30 | 44047.6042 | 0 | 10.0606 | 39.95
2020-08-04 15:00 | 44047.625 | 0 | 10.5481 | 39.95
2020-08-04 15:30 | 44047.6458 | 0 | 11.1612 | 39.95
2020-08-04 16:00 | 44047.6667 | 0 | 11.4555 | 39.95
2020-08-04 16:30 | 44047.6875 | 0 | 11.9608 | 39.95
2020-08-04 17:00 | 44047.7083 | 0 | 12.6031 | 39.95
2020-08-04 17:30 | 44047.7292 | 0 | 13.5302 | 39.95
2020-08-04 18:00 | 44047.75 | 0 | 13.9799 | 39.95
2020-08-04 18:30 | 44047.7708 | 0 | 13.9944 | 39.95
2020-08-04 19:00 | 44047.7917 | 0 | 13.6413 | 39.95
2020-08-04 19:30 | 44047.8125 | 0 | 13.5038 | 39.95
2020-08-04 20:00 | 44047.8333 | 0 | 13.307 | 39.95
2020-08-04 20:30 | 44047.8542 | 0 | 12.9067 | 39.95
2020-08-04 21:00 | 44047.875 | 0 | 12.3109 | 39.95
2020-08-04 21:30 | 44047.8958 | 0 | 11.7305 | 39.95
2020-08-04 22:00 | 44047.9167 | 0 | 11.408 | 39.95
2020-08-04 22:30 | 44047.9375 | 0 | 10.5927 | 39.95
2020-08-04 23:00 | 44047.9583 | 0 | 9.8785 | 39.95
2020-08-04 23:30 | 44047.9792 | 0 | 9.2227 | 39.95
2020-08-05 | 44048 | 0 | 8.7108 | 39.95
2020-08-05 00:30 | 44048.0208 | 0 | 8.2846 | 39.95
2020-08-05 01:00 | 44048.0417 | 0 | 8.1572 | 39.95
2020-08-05 01:30 | 44048.0625 | 0 | 7.981 | 39.95
2020-08-05 02:00 | 44048.0833 | 0 | 7.8835 | 39.95
2020-08-05 02:30 | 44048.1042 | 0 | 7.744 | 39.95
2020-08-05 03:00 | 44048.125 | 0 | 7.7668 | 39.95
2020-08-05 03:30 | 44048.1458 | 0 | 7.7585 | 39.95
2020-08-05 04:00 | 44048.1667 | 0 | 7.9672 | 39.95
2020-08-05 04:30 | 44048.1875 | 0 | 8.5229 | 39.95
2020-08-05 05:00 | 44048.2083 | 0 | 9.062 | 39.95
2020-08-05 05:30 | 44048.2292 | 0 | 10.1071 | 39.95
2020-08-05 06:00 | 44048.25 | 0 | 11.4425 | 39.95
2020-08-05 06:30 | 44048.2708 | 0 | 12.7144 | 39.95
2020-08-05 07:00 | 44048.2917 | 0 | 13.3309 | 39.95
2020-08-05 07:30 | 44048.3125 | 0 | 13.2587 | 39.95
2020-08-05 08:00 | 44048.3333 | 0 | 12.2532 | 39.95
2020-08-05 08:30 | 44048.3542 | 0 | 11.4877 | 39.95
2020-08-05 09:00 | 44048.375 | 0 | 10.7414 | 39.95
2020-08-05 09:30 | 44048.3958 | 0 | 10.1152 | 39.95
2020-08-05 10:00 | 44048.4167 | 0 | 9.6514 | 39.95
2020-08-05 10:30 | 44048.4375 | 0 | 9.3321 | 39.95
2020-08-05 11:00 | 44048.4583 | 0 | 9.1105 | 39.95
2020-08-05 11:30 | 44048.4792 | 0 | 9.0274 | 39.95
2020-08-05 12:00 | 44048.5 | 0 | 8.7834 | 39.95
2020-08-05 12:30 | 44048.5208 | 0 | 8.8222 | 39.95
2020-08-05 13:00 | 44048.5417 | 0 | 8.995 | 39.95
2020-08-05 13:30 | 44048.5625 | 0 | 9.2134 | 39.95
2020-08-05 14:00 | 44048.5833 | 0 | 9.5409 | 39.95
2020-08-05 14:30 | 44048.6042 | 0 | 9.7394 | 39.95
2020-08-05 15:00 | 44048.625 | 0 | 10.0147 | 39.95
2020-08-05 15:30 | 44048.6458 | 0 | 10.6011 | 39.95
2020-08-05 16:00 | 44048.6667 | 0 | 11.2911 | 39.95
2020-08-05 16:30 | 44048.6875 | 0 | 11.8685 | 39.95
2020-08-05 17:00 | 44048.7083 | 0 | 12.3371 | 39.95
2020-08-05 17:30 | 44048.7292 | 0 | 13.358 | 39.95
2020-08-05 18:00 | 44048.75 | 0 | 13.6489 | 39.95
2020-08-05 18:30 | 44048.7708 | 0 | 14.0324 | 39.95
2020-08-05 19:00 | 44048.7917 | 0 | 13.7017 | 39.95
2020-08-05 19:30 | 44048.8125 | 0 | 13.4309 | 39.95
2020-08-05 20:00 | 44048.8333 | 0 | 13.2377 | 39.95
2020-08-05 20:30 | 44048.8542 | 0 | 12.789 | 39.95
2020-08-05 21:00 | 44048.875 | 0 | 12.068 | 39.95
2020-08-05 21:30 | 44048.8958 | 0 | 11.8148 | 39.95
2020-08-05 22:00 | 44048.9167 | 0 | 11.3071 | 39.95
2020-08-05 22:30 | 44048.9375 | 0 | 10.5397 | 39.95
2020-08-05 23:00 | 44048.9583 | 0 | 9.8117 | 39.95
2020-08-05 23:30 | 44048.9792 | 0 | 9.2689 | 39.95
2020-08-06 | 44049 | 0 | 8.5317 | 39.95
2020-08-06 00:30 | 44049.0208 | 0 | 8.1466 | 39.95
2020-08-06 01:00 | 44049.0417 | 0 | 7.991 | 39.95
2020-08-06 01:30 | 44049.0625 | 0 | 7.8286 | 39.95
2020-08-06 02:00 | 44049.0833 | 0 | 7.7229 | 39.95
2020-08-06 02:30 | 44049.1042 | 0 | 7.6908 | 39.95
2020-08-06 03:00 | 44049.125 | 0 | 7.575 | 39.95
2020-08-06 03:30 | 44049.1458 | 0 | 7.4054 | 39.95
2020-08-06 04:00 | 44049.1667 | 0 | 7.7469 | 39.95
2020-08-06 04:30 | 44049.1875 | 0 | 8.035 | 39.95
2020-08-06 05:00 | 44049.2083 | 0 | 8.483 | 39.95
2020-08-06 05:30 | 44049.2292 | 0 | 9.3296 | 39.95
2020-08-06 06:00 | 44049.25 | 0 | 10.4992 | 39.95
2020-08-06 06:30 | 44049.2708 | 0 | 11.453 | 39.95
2020-08-06 07:00 | 44049.2917 | 0 | 12.1461 | 39.95
2020-08-06 07:30 | 44049.3125 | 0 | 11.8513 | 39.95
2020-08-06 08:00 | 44049.3333 | 0 | 11.6752 | 39.95
2020-08-06 08:30 | 44049.3542 | 0 | 11.0221 | 39.95
2020-08-06 09:00 | 44049.375 | 0 | 10.1532 | 39.95
2020-08-06 09:30 | 44049.3958 | 0 | 10.4236 | 39.95
2020-08-06 10:00 | 44049.4167 | 0 | 9.8311 | 39.95
2020-08-06 10:30 | 44049.4375 | 0 | 10.5431 | 39.95
2020-08-06 11:00 | 44049.4583 | 0 | 9.8415 | 39.95
2020-08-06 11:30 | 44049.4792 | 0 | 10.0631 | 39.95
2020-08-06 12:00 | 44049.5 | 0 | 11.0063 | 39.95
2020-08-06 12:30 | 44049.5208 | 0 | 11.8147 | 39.95
2020-08-06 13:00 | 44049.5417 | 0 | 12.0936 | 39.95
2020-08-06 13:30 | 44049.5625 | 0 | 12.1057 | 39.95
2020-08-06 14:00 | 44049.5833 | 0 | 12.0707 | 39.95
2020-08-06 14:30 | 44049.6042 | 0 | 11.7971 | 39.95
2020-08-06 15:00 | 44049.625 | 0 | 12.1828 | 39.95
2020-08-06 15:30 | 44049.6458 | 0 | 12.5115 | 39.95
2020-08-06 16:00 | 44049.6667 | 0 | 12.4933 | 39.95
2020-08-06 16:30 | 44049.6875 | 0 | 12.663 | 39.95
2020-08-06 17:00 | 44049.7083 | 0 | 12.874 | 39.95
2020-08-06 17:30 | 44049.7292 | 0 | 13.4632 | 39.95
2020-08-06 18:00 | 44049.75 | 0 | 13.6788 | 39.95
2020-08-06 18:30 | 44049.7708 | 0 | 13.7754 | 39.95
2020-08-06 19:00 | 44049.7917 | 0 | 13.4741 | 39.95
2020-08-06 19:30 | 44049.8125 | 0 | 13.2654 | 39.95
2020-08-06 20:00 | 44049.8333 | 0 | 12.9448 | 39.95
2020-08-06 20:30 | 44049.8542 | 0 | 12.4596 | 39.95
2020-08-06 21:00 | 44049.875 | 0 | 11.8657 | 39.95
2020-08-06 21:30 | 44049.8958 | 0 | 11.4886 | 39.95
2020-08-06 22:00 | 44049.9167 | 0 | 10.9978 | 39.95
2020-08-06 22:30 | 44049.9375 | 0 | 10.179 | 39.95
2020-08-06 23:00 | 44049.9583 | 0 | 9.5096 | 39.95
2020-08-06 23:30 | 44049.9792 | 0 | 9.1667 | 39.95
2020-08-07 | 44050 | 0 | 8.5217 | 39.95
2020-08-07 00:30 | 44050.0208 | 0 | 8.0524 | 39.95
2020-08-07 01:00 | 44050.0417 | 0 | 7.7965 | 39.95
2020-08-07 01:30 | 44050.0625 | 0 | 7.5874 | 39.95
2020-08-07 02:00 | 44050.0833 | 0 | 7.5205 | 39.95
2020-08-07 02:30 | 44050.1042 | 0 | 7.4312 | 39.95
2020-08-07 03:00 | 44050.125 | 0 | 7.3269 | 39.95
2020-08-07 03:30 | 44050.1458 | 0 | 7.2955 | 39.95
2020-08-07 04:00 | 44050.1667 | 0 | 7.381 | 39.95
2020-08-07 04:30 | 44050.1875 | 0 | 7.6605 | 39.95
2020-08-07 05:00 | 44050.2083 | 0 | 7.822 | 39.95
2020-08-07 05:30 | 44050.2292 | 0 | 7.96 | 39.95
2020-08-07 06:00 | 44050.25 | 0 | 8.4886 | 39.95
2020-08-07 06:30 | 44050.2708 | 0 | 8.7322 | 39.95
2020-08-07 07:00 | 44050.2917 | 0 | 9.1524 | 39.95
2020-08-07 07:30 | 44050.3125 | 0 | 8.9387 | 39.95
2020-08-07 08:00 | 44050.3333 | 0 | 9.0934 | 39.95
2020-08-07 08:30 | 44050.3542 | 0 | 9.0892 | 39.95
2020-08-07 09:00 | 44050.375 | 0 | 9.3016 | 39.95
2020-08-07 09:30 | 44050.3958 | 0 | 8.3659 | 39.95
2020-08-07 10:00 | 44050.4167 | 0 | 7.8157 | 39.95
2020-08-07 10:30 | 44050.4375 | 0 | 8.4445 | 39.95
2020-08-07 11:00 | 44050.4583 | 0 | 9.4638 | 39.95
2020-08-07 11:30 | 44050.4792 | 0 | 9.4226 | 39.95
2020-08-07 12:00 | 44050.5 | 0 | 10.1707 | 39.95
2020-08-07 12:30 | 44050.5208 | 0 | 9.3587 | 39.95
2020-08-07 13:00 | 44050.5417 | 0 | 7.243 | 39.95
2020-08-07 13:30 | 44050.5625 | 0 | 7.1431 | 39.95
2020-08-07 14:00 | 44050.5833 | 0 | 7.3698 | 39.95
2020-08-07 14:30 | 44050.6042 | 0 | 7.977 | 39.95
2020-08-07 15:00 | 44050.625 | 0 | 8.6626 | 39.95
2020-08-07 15:30 | 44050.6458 | 0 | 8.7728 | 39.95
2020-08-07 16:00 | 44050.6667 | 0 | 9.2254 | 39.95
2020-08-07 16:30 | 44050.6875 | 0 | 9.8318 | 39.95
2020-08-07 17:00 | 44050.7083 | 0 | 10.3903 | 39.95
2020-08-07 17:30 | 44050.7292 | 0 | 11.0011 | 39.95
2020-08-07 18:00 | 44050.75 | 0 | 11.5984 | 39.95
2020-08-07 18:30 | 44050.7708 | 0 | 11.6127 | 39.95
2020-08-07 19:00 | 44050.7917 | 0 | 11.3632 | 39.95
2020-08-07 19:30 | 44050.8125 | 0 | 11.1421 | 39.95
2020-08-07 20:00 | 44050.8333 | 0 | 11.0153 | 39.95
2020-08-07 20:30 | 44050.8542 | 0 | 10.4749 | 39.95
2020-08-07 21:00 | 44050.875 | 0 | 10.0588 | 39.95
2020-08-07 21:30 | 44050.8958 | 0 | 9.9063 | 39.95
2020-08-07 22:00 | 44050.9167 | 0 | 9.6287 | 39.95
2020-08-07 22:30 | 44050.9375 | 0 | 9.089 | 39.95
2020-08-07 23:00 | 44050.9583 | 0 | 8.6332 | 39.95
2020-08-07 23:30 | 44050.9792 | 0 | 8.1846 | 39.95
2020-08-08 | 44051 | 0 | 7.7877 | 39.95
2020-08-08 00:30 | 44051.0208 | 0 | 7.4326 | 39.95
2020-08-08 01:00 | 44051.0417 | 0 | 7.2189 | 39.95
2020-08-08 01:30 | 44051.0625 | 0 | 7.0356 | 39.95
2020-08-08 02:00 | 44051.0833 | 0 | 7.0982 | 39.95
2020-08-08 02:30 | 44051.1042 | 0 | 7.0067 | 39.95
2020-08-08 03:00 | 44051.125 | 0 | 6.869 | 39.95
2020-08-08 03:30 | 44051.1458 | 0 | 6.7836 | 39.95
2020-08-08 04:00 | 44051.1667 | 0 | 6.7148 | 39.95
2020-08-08 04:30 | 44051.1875 | 0 | 6.7239 | 39.95
2020-08-08 05:00 | 44051.2083 | 0 | 6.9924 | 39.95
2020-08-08 05:30 | 44051.2292 | 0 | 7.184 | 39.95
2020-08-08 06:00 | 44051.25 | 0 | 7.4628 | 39.95
2020-08-08 06:30 | 44051.2708 | 0 | 7.7199 | 39.95
2020-08-08 07:00 | 44051.2917 | 0 | 7.9898 | 39.95
2020-08-08 07:30 | 44051.3125 | 0 | 7.941 | 39.95
2020-08-08 08:00 | 44051.3333 | 0 | 7.8164 | 39.95
2020-08-08 08:30 | 44051.3542 | 0 | 7.6469 | 39.95
2020-08-08 09:00 | 44051.375 | 0 | 7.5446 | 39.95
2020-08-08 09:30 | 44051.3958 | 0 | 7.0322 | 39.95
2020-08-08 10:00 | 44051.4167 | 0 | 6.7757 | 39.95
2020-08-08 10:30 | 44051.4375 | 0 | 6.6221 | 39.95
2020-08-08 11:00 | 44051.4583 | 0 | 6.6502 | 39.95
2020-08-08 11:30 | 44051.4792 | 0 | 6.7085 | 39.95
2020-08-08 12:00 | 44051.5 | 0 | 5.7898 | 39.95
2020-08-08 12:30 | 44051.5208 | 0 | 5.8532 | 39.95
2020-08-08 13:00 | 44051.5417 | 0 | 5.9667 | 39.95
2020-08-08 13:30 | 44051.5625 | 0 | 6.0933 | 39.95
2020-08-08 14:00 | 44051.5833 | 0 | 6.5922 | 39.95
2020-08-08 14:30 | 44051.6042 | 0 | 7.09 | 39.95
2020-08-08 15:00 | 44051.625 | 0 | 7.6263 | 39.95
2020-08-08 15:30 | 44051.6458 | 0 | 8.1645 | 39.95
2020-08-08 16:00 | 44051.6667 | 0 | 9.0121 | 39.95
2020-08-08 16:30 | 44051.6875 | 0 | 10.0734 | 39.95
2020-08-08 17:00 | 44051.7083 | 0 | 11.3521 | 39.95
2020-08-08 17:30 | 44051.7292 | 0 | 12.5619 | 39.95
2020-08-08 18:00 | 44051.75 | 0 | 13.1324 | 39.95
2020-08-08 18:30 | 44051.7708 | 0 | 13.3715 | 39.95
2020-08-08 19:00 | 44051.7917 | 0 | 13.0892 | 39.95
2020-08-08 19:30 | 44051.8125 | 0 | 12.5582 | 39.95
2020-08-08 20:00 | 44051.8333 | 0 | 12.4241 | 39.95
2020-08-08 20:30 | 44051.8542 | 0 | 11.7974 | 39.95
2020-08-08 21:00 | 44051.875 | 0 | 11.211 | 39.95
2020-08-08 21:30 | 44051.8958 | 0 | 10.872 | 39.95
2020-08-08 22:00 | 44051.9167 | 0 | 10.3188 | 39.95
2020-08-08 22:30 | 44051.9375 | 0 | 9.4473 | 39.95
2020-08-08 23:00 | 44051.9583 | 0 | 8.7039 | 39.95
2020-08-08 23:30 | 44051.9792 | 0 | 8.201 | 39.95
2020-08-09 | 44052 | 0 | 7.8295 | 39.95
2020-08-09 00:30 | 44052.0208 | 0 | 7.6098 | 39.95
2020-08-09 01:00 | 44052.0417 | 0 | 7.2846 | 39.95
2020-08-09 01:30 | 44052.0625 | 0 | 7.2133 | 39.95
2020-08-09 02:00 | 44052.0833 | 0 | 7.1726 | 39.95
2020-08-09 02:30 | 44052.1042 | 0 | 7.1967 | 39.95
2020-08-09 03:00 | 44052.125 | 0 | 7.2377 | 39.95
2020-08-09 03:30 | 44052.1458 | 0 | 7.2936 | 39.95
2020-08-09 04:00 | 44052.1667 | 0 | 7.5635 | 39.95
2020-08-09 04:30 | 44052.1875 | 0 | 7.9132 | 39.95
2020-08-09 05:00 | 44052.2083 | 0 | 8.5367 | 39.95
2020-08-09 05:30 | 44052.2292 | 0 | 9.4643 | 39.95
2020-08-09 06:00 | 44052.25 | 0 | 10.6465 | 39.95
2020-08-09 06:30 | 44052.2708 | 0 | 12.2635 | 39.95
2020-08-09 07:00 | 44052.2917 | 0 | 13.0335 | 39.95
2020-08-09 07:30 | 44052.3125 | 0 | 12.974 | 39.95
2020-08-09 08:00 | 44052.3333 | 0 | 12.1548 | 39.95
2020-08-09 08:30 | 44052.3542 | 0 | 10.9632 | 39.95
2020-08-09 09:00 | 44052.375 | 0 | 10.4373 | 39.95
2020-08-09 09:30 | 44052.3958 | 0 | 11.066 | 39.95
2020-08-09 10:00 | 44052.4167 | 0 | 9.8446 | 39.95
2020-08-09 10:30 | 44052.4375 | 0 | 9.4858 | 39.95
2020-08-09 11:00 | 44052.4583 | 0 | 9.0797 | 39.95
2020-08-09 11:30 | 44052.4792 | 0 | 10.4287 | 39.95
2020-08-09 12:00 | 44052.5 | 0 | 8.4152 | 39.95
2020-08-09 12:30 | 44052.5208 | 0 | 8.4102 | 39.95
2020-08-09 13:00 | 44052.5417 | 0 | 8.516 | 39.95
2020-08-09 13:30 | 44052.5625 | 0 | 8.5495 | 39.95
2020-08-09 14:00 | 44052.5833 | 0 | 8.8246 | 39.95
2020-08-09 14:30 | 44052.6042 | 0 | 8.8548 | 39.95
2020-08-09 15:00 | 44052.625 | 0 | 9.3414 | 39.95
2020-08-09 15:30 | 44052.6458 | 0 | 9.7856 | 39.95
2020-08-09 16:00 | 44052.6667 | 0 | 10.4822 | 39.95
2020-08-09 16:30 | 44052.6875 | 0 | 11.5115 | 39.95
2020-08-09 17:00 | 44052.7083 | 0 | 12.7274 | 39.95
2020-08-09 17:30 | 44052.7292 | 0 | 14.4917 | 39.95
2020-08-09 18:00 | 44052.75 | 0 | 15.5402 | 39.95
2020-08-09 18:30 | 44052.7708 | 0 | 16.0502 | 39.95
2020-08-09 19:00 | 44052.7917 | 0 | 15.5671 | 39.95
2020-08-09 19:30 | 44052.8125 | 0 | 14.939 | 39.95
2020-08-09 20:00 | 44052.8333 | 0 | 14.5267 | 39.95
2020-08-09 20:30 | 44052.8542 | 0 | 13.8192 | 39.95
2020-08-09 21:00 | 44052.875 | 0 | 12.8641 | 39.95
2020-08-09 21:30 | 44052.8958 | 0 | 12.2384 | 39.95
2020-08-09 22:00 | 44052.9167 | 0 | 11.3267 | 39.95
2020-08-09 22:30 | 44052.9375 | 0 | 10.2108 | 39.95
2020-08-09 23:00 | 44052.9583 | 0 | 9.4442 | 39.95
2020-08-09 23:30 | 44052.9792 | 0 | 8.7175 | 39.95
2020-08-10 | 44053 | 0 | 8.1986 | 39.95
2020-08-10 00:30 | 44053.0208 | 0 | 7.738 | 39.95
2020-08-10 01:00 | 44053.0417 | 0 | 7.5093 | 39.95
2020-08-10 01:30 | 44053.0625 | 0 | 7.3753 | 39.95
2020-08-10 02:00 | 44053.0833 | 0 | 7.4034 | 39.95
2020-08-10 02:30 | 44053.1042 | 0 | 7.3306 | 39.95
2020-08-10 03:00 | 44053.125 | 0 | 7.3568 | 39.95
2020-08-10 03:30 | 44053.1458 | 0 | 7.3734 | 39.95
2020-08-10 04:00 | 44053.1667 | 0 | 7.465 | 39.95
2020-08-10 04:30 | 44053.1875 | 0 | 7.9696 | 39.95
2020-08-10 05:00 | 44053.2083 | 0 | 8.7368 | 39.95
2020-08-10 05:30 | 44053.2292 | 0 | 9.5577 | 39.95
2020-08-10 06:00 | 44053.25 | 0 | 11.0728 | 39.95
2020-08-10 06:30 | 44053.2708 | 0 | 12.4926 | 39.95
2020-08-10 07:00 | 44053.2917 | 0 | 13.1238 | 39.95
2020-08-10 07:30 | 44053.3125 | 0 | 12.4468 | 39.95
2020-08-10 08:00 | 44053.3333 | 0 | 11.5962 | 39.95
2020-08-10 08:30 | 44053.3542 | 0 | 10.5622 | 39.95
2020-08-10 09:00 | 44053.375 | 0 | 9.7405 | 39.95
2020-08-10 09:30 | 44053.3958 | 0 | 9.2235 | 39.95
2020-08-10 10:00 | 44053.4167 | 0 | 8.5988 | 39.95
2020-08-10 10:30 | 44053.4375 | 0 | 8.2087 | 39.95
2020-08-10 11:00 | 44053.4583 | 0 | 7.8732 | 39.95
2020-08-10 11:30 | 44053.4792 | 0 | 7.8414 | 39.95
2020-08-10 12:00 | 44053.5 | 0 | 8.5717 | 39.95
2020-08-10 12:30 | 44053.5208 | 0 | 7.8696 | 39.95
2020-08-10 13:00 | 44053.5417 | 0 | 7.8228 | 39.95
2020-08-10 13:30 | 44053.5625 | 0 | 8.5503 | 39.95
2020-08-10 14:00 | 44053.5833 | 0 | 10.3668 | 39.95
2020-08-10 14:30 | 44053.6042 | 0 | 9.936 | 39.95
2020-08-10 15:00 | 44053.625 | 0 | 9.6402 | 39.95
2020-08-10 15:30 | 44053.6458 | 0 | 10.0037 | 39.95
2020-08-10 16:00 | 44053.6667 | 0 | 10.1824 | 39.95
2020-08-10 16:30 | 44053.6875 | 0 | 10.7679 | 39.95
2020-08-10 17:00 | 44053.7083 | 0 | 11.4007 | 39.95
2020-08-10 17:30 | 44053.7292 | 0 | 12.5881 | 39.95
2020-08-10 18:00 | 44053.75 | 0 | 13.2965 | 39.95
2020-08-10 18:30 | 44053.7708 | 0 | 13.5184 | 39.95
2020-08-10 19:00 | 44053.7917 | 0 | 13.1263 | 39.95
2020-08-10 19:30 | 44053.8125 | 0 | 12.8918 | 39.95
2020-08-10 20:00 | 44053.8333 | 0 | 12.7888 | 39.95
2020-08-10 20:30 | 44053.8542 | 0 | 12.3402 | 39.95
2020-08-10 21:00 | 44053.875 | 0 | 11.5829 | 39.95
2020-08-10 21:30 | 44053.8958 | 0 | 11.0302 | 39.95
2020-08-10 22:00 | 44053.9167 | 0 | 10.4401 | 39.95
2020-08-10 22:30 | 44053.9375 | 0 | 9.4642 | 39.95
2020-08-10 23:00 | 44053.9583 | 0 | 8.8381 | 39.95
2020-08-10 23:30 | 44053.9792 | 0 | 8.3427 | 39.95
2020-08-11 | 44054 | 0 | 7.7537 | 39.95
2020-08-11 00:30 | 44054.0208 | 0 | 7.4236 | 39.95
2020-08-11 01:00 | 44054.0417 | 0 | 7.2244 | 39.95
2020-08-11 01:30 | 44054.0625 | 0 | 7.0774 | 39.95
2020-08-11 02:00 | 44054.0833 | 0 | 7.0647 | 39.95
2020-08-11 02:30 | 44054.1042 | 0 | 6.992 | 39.95
2020-08-11 03:00 | 44054.125 | 0 | 7.061 | 39.95
2020-08-11 03:30 | 44054.1458 | 0 | 7.0291 | 39.95
2020-08-11 04:00 | 44054.1667 | 0 | 7.2061 | 39.95
2020-08-11 04:30 | 44054.1875 | 0 | 7.6312 | 39.95
2020-08-11 05:00 | 44054.2083 | 0 | 8.3205 | 39.95
2020-08-11 05:30 | 44054.2292 | 0 | 9.1997 | 39.95
2020-08-11 06:00 | 44054.25 | 0 | 10.5122 | 39.95
2020-08-11 06:30 | 44054.2708 | 0 | 11.6323 | 39.95
2020-08-11 07:00 | 44054.2917 | 0 | 12.1676 | 39.95
2020-08-11 07:30 | 44054.3125 | 0 | 11.981 | 39.95
2020-08-11 08:00 | 44054.3333 | 0 | 11.2231 | 39.95
2020-08-11 08:30 | 44054.3542 | 0 | 10.8182 | 39.95
2020-08-11 09:00 | 44054.375 | 0 | 9.8708 | 39.95
2020-08-11 09:30 | 44054.3958 | 0 | 9.0819 | 39.95
2020-08-11 10:00 | 44054.4167 | 0 | 8.3911 | 39.95
2020-08-11 10:30 | 44054.4375 | 0 | 8.1237 | 39.95
2020-08-11 11:00 | 44054.4583 | 0 | 7.9015 | 39.95
2020-08-11 11:30 | 44054.4792 | 0 | 8.7912 | 39.95
2020-08-11 12:00 | 44054.5 | 0 | 8.0552 | 39.95
2020-08-11 12:30 | 44054.5208 | 0 | 8.0934 | 39.95
2020-08-11 13:00 | 44054.5417 | 0 | 8.5302 | 39.95
2020-08-11 13:30 | 44054.5625 | 0 | 8.4305 | 39.95
2020-08-11 14:00 | 44054.5833 | 0 | 8.7024 | 39.95
2020-08-11 14:30 | 44054.6042 | 0 | 8.8653 | 39.95
2020-08-11 15:00 | 44054.625 | 0 | 9.4432 | 39.95
2020-08-11 15:30 | 44054.6458 | 0 | 9.4822 | 39.95
2020-08-11 16:00 | 44054.6667 | 0 | 10.2264 | 39.95
2020-08-11 16:30 | 44054.6875 | 0 | 10.6657 | 39.95
2020-08-11 17:00 | 44054.7083 | 0 | 11.2587 | 39.95
2020-08-11 17:30 | 44054.7292 | 0 | 12.4014 | 39.95
2020-08-11 18:00 | 44054.75 | 0 | 13.1432 | 39.95
2020-08-11 18:30 | 44054.7708 | 0 | 13.397 | 39.95
2020-08-11 19:00 | 44054.7917 | 0 | 13.0286 | 39.95
2020-08-11 19:30 | 44054.8125 | 0 | 12.59 | 39.95
2020-08-11 20:00 | 44054.8333 | 0 | 12.4554 | 39.95
2020-08-11 20:30 | 44054.8542 | 0 | 11.7786 | 39.95
2020-08-11 21:00 | 44054.875 | 0 | 11.3141 | 39.95
2020-08-11 21:30 | 44054.8958 | 0 | 10.8498 | 39.95
2020-08-11 22:00 | 44054.9167 | 0 | 10.4144 | 39.95
2020-08-11 22:30 | 44054.9375 | 0 | 9.5069 | 39.95
2020-08-11 23:00 | 44054.9583 | 0 | 8.8018 | 39.95
2020-08-11 23:30 | 44054.9792 | 0 | 8.2481 | 39.95
2020-08-12 | 44055 | 0 | 7.87 | 39.95
2020-08-12 00:30 | 44055.0208 | 0 | 7.3137 | 39.95
2020-08-12 01:00 | 44055.0417 | 0 | 7.1668 | 39.95
2020-08-12 01:30 | 44055.0625 | 0 | 7.0998 | 39.95
2020-08-12 02:00 | 44055.0833 | 0 | 7.1018 | 39.95
2020-08-12 02:30 | 44055.1042 | 0 | 7.0458 | 39.95
2020-08-12 03:00 | 44055.125 | 0 | 7.0666 | 39.95
2020-08-12 03:30 | 44055.1458 | 0 | 7.0515 | 39.95
2020-08-12 04:00 | 44055.1667 | 0 | 7.1358 | 39.95
2020-08-12 04:30 | 44055.1875 | 0 | 7.5263 | 39.95
2020-08-12 05:00 | 44055.2083 | 0 | 8.1446 | 39.95
2020-08-12 05:30 | 44055.2292 | 0 | 8.9105 | 39.95
2020-08-12 06:00 | 44055.25 | 0 | 10.1612 | 39.95
2020-08-12 06:30 | 44055.2708 | 0 | 11.0869 | 39.95
2020-08-12 07:00 | 44055.2917 | 0 | 11.5577 | 39.95
2020-08-12 07:30 | 44055.3125 | 0 | 11.2167 | 39.95
2020-08-12 08:00 | 44055.3333 | 0 | 10.869 | 39.95
2020-08-12 08:30 | 44055.3542 | 0 | 9.7723 | 39.95
2020-08-12 09:00 | 44055.375 | 0 | 9.1882 | 39.95
2020-08-12 09:30 | 44055.3958 | 0 | 8.7411 | 39.95
2020-08-12 10:00 | 44055.4167 | 0 | 8.2593 | 39.95
2020-08-12 10:30 | 44055.4375 | 0 | 7.9726 | 39.95
2020-08-12 11:00 | 44055.4583 | 0 | 7.9783 | 39.95
2020-08-12 11:30 | 44055.4792 | 0 | 7.7784 | 39.95
2020-08-12 12:00 | 44055.5 | 0 | 7.6697 | 39.95
2020-08-12 12:30 | 44055.5208 | 0 | 7.8833 | 39.95
2020-08-12 13:00 | 44055.5417 | 0 | 7.9308 | 39.95
2020-08-12 13:30 | 44055.5625 | 0 | 8.3526 | 39.95
2020-08-12 14:00 | 44055.5833 | 0 | 8.5667 | 39.95
2020-08-12 14:30 | 44055.6042 | 0 | 8.8079 | 39.95
2020-08-12 15:00 | 44055.625 | 0 | 9.0937 | 39.95
2020-08-12 15:30 | 44055.6458 | 0 | 9.6736 | 39.95
2020-08-12 16:00 | 44055.6667 | 0 | 10.2061 | 39.95
2020-08-12 16:30 | 44055.6875 | 0 | 10.8284 | 39.95
2020-08-12 17:00 | 44055.7083 | 0 | 11.2501 | 39.95
2020-08-12 17:30 | 44055.7292 | 0 | 11.8673 | 39.95
2020-08-12 18:00 | 44055.75 | 0 | 12.43 | 39.95
2020-08-12 18:30 | 44055.7708 | 0 | 12.4802 | 39.95
2020-08-12 19:00 | 44055.7917 | 0 | 12.1054 | 39.95
2020-08-12 19:30 | 44055.8125 | 0 | 11.8178 | 39.95
2020-08-12 20:00 | 44055.8333 | 0 | 11.8082 | 39.95
2020-08-12 20:30 | 44055.8542 | 0 | 11.2198 | 39.95
2020-08-12 21:00 | 44055.875 | 0 | 10.6975 | 39.95
2020-08-12 21:30 | 44055.8958 | 0 | 10.3045 | 39.95
2020-08-12 22:00 | 44055.9167 | 0 | 9.9136 | 39.95
2020-08-12 22:30 | 44055.9375 | 0 | 9.2047 | 39.95
2020-08-12 23:00 | 44055.9583 | 0 | 8.6441 | 39.95
2020-08-12 23:30 | 44055.9792 | 0 | 8.2308 | 39.95
2020-08-13 | 44056 | 0 | 7.67 | 39.95
2020-08-13 00:30 | 44056.0208 | 0 | 7.2148 | 39.95
2020-08-13 01:00 | 44056.0417 | 0 | 7.0098 | 39.95
2020-08-13 01:30 | 44056.0625 | 0 | 6.9138 | 39.95
2020-08-13 02:00 | 44056.0833 | 0 | 6.8559 | 39.95
2020-08-13 02:30 | 44056.1042 | 0 | 6.7388 | 39.95
2020-08-13 03:00 | 44056.125 | 0 | 6.7148 | 39.95
2020-08-13 03:30 | 44056.1458 | 0 | 6.6811 | 39.95
2020-08-13 04:00 | 44056.1667 | 0 | 6.7112 | 39.95
2020-08-13 04:30 | 44056.1875 | 0 | 6.9085 | 39.95
2020-08-13 05:00 | 44056.2083 | 0 | 7.2845 | 39.95
2020-08-13 05:30 | 44056.2292 | 0 | 7.6397 | 39.95
2020-08-13 06:00 | 44056.25 | 0 | 8.1064 | 39.95
2020-08-13 06:30 | 44056.2708 | 0 | 8.3769 | 39.95
2020-08-13 07:00 | 44056.2917 | 0 | 8.9214 | 39.95
2020-08-13 07:30 | 44056.3125 | 0 | 9.0207 | 39.95
2020-08-13 08:00 | 44056.3333 | 0 | 9.1526 | 39.95
2020-08-13 08:30 | 44056.3542 | 0 | 9.1376 | 39.95
2020-08-13 09:00 | 44056.375 | 0 | 8.2594 | 39.95
2020-08-13 09:30 | 44056.3958 | 0 | 7.5529 | 39.95
2020-08-13 10:00 | 44056.4167 | 0 | 7.4365 | 39.95
2020-08-13 10:30 | 44056.4375 | 0 | 7.1072 | 39.95
2020-08-13 11:00 | 44056.4583 | 0 | 6.7028 | 39.95
2020-08-13 11:30 | 44056.4792 | 0 | 6.6085 | 39.95
2020-08-13 12:00 | 44056.5 | 0 | 6.2384 | 39.95
2020-08-13 12:30 | 44056.5208 | 0 | 6.3202 | 39.95
2020-08-13 13:00 | 44056.5417 | 0 | 6.3686 | 39.95
2020-08-13 13:30 | 44056.5625 | 0 | 6.714 | 39.95
2020-08-13 14:00 | 44056.5833 | 0 | 7.0071 | 39.95
2020-08-13 14:30 | 44056.6042 | 0 | 7.4226 | 39.95
2020-08-13 15:00 | 44056.625 | 0 | 7.7813 | 39.95
2020-08-13 15:30 | 44056.6458 | 0 | 8.2634 | 39.95
2020-08-13 16:00 | 44056.6667 | 0 | 8.9137 | 39.95
2020-08-13 16:30 | 44056.6875 | 0 | 9.7127 | 39.95
2020-08-13 17:00 | 44056.7083 | 0 | 10.0666 | 39.95
2020-08-13 17:30 | 44056.7292 | 0 | 10.8142 | 39.95
2020-08-13 18:00 | 44056.75 | 0 | 11.1402 | 39.95
2020-08-13 18:30 | 44056.7708 | 0 | 11.1307 | 39.95
2020-08-13 19:00 | 44056.7917 | 0 | 10.8869 | 39.95
2020-08-13 19:30 | 44056.8125 | 0 | 10.7029 | 39.95
2020-08-13 20:00 | 44056.8333 | 0 | 10.525 | 39.95
2020-08-13 20:30 | 44056.8542 | 0 | 10.0557 | 39.95
2020-08-13 21:00 | 44056.875 | 0 | 9.6587 | 39.95
2020-08-13 21:30 | 44056.8958 | 0 | 9.508 | 39.95
2020-08-13 22:00 | 44056.9167 | 0 | 9.0994 | 39.95
2020-08-13 22:30 | 44056.9375 | 0 | 8.6291 | 39.95
2020-08-13 23:00 | 44056.9583 | 0 | 8.1826 | 39.95
2020-08-13 23:30 | 44056.9792 | 0 | 7.8427 | 39.95
2020-08-14 | 44057 | 0 | 7.3937 | 39.95
2020-08-14 00:30 | 44057.0208 | 0 | 6.926 | 39.95
2020-08-14 01:00 | 44057.0417 | 0 | 6.7685 | 39.95
2020-08-14 01:30 | 44057.0625 | 0 | 6.6868 | 39.95
2020-08-14 02:00 | 44057.0833 | 0 | 6.6626 | 39.95
2020-08-14 02:30 | 44057.1042 | 0 | 6.6196 | 39.95
2020-08-14 03:00 | 44057.125 | 0 | 6.5658 | 39.95
2020-08-14 03:30 | 44057.1458 | 0 | 6.6516 | 39.95
2020-08-14 04:00 | 44057.1667 | 0 | 6.7557 | 39.95
2020-08-14 04:30 | 44057.1875 | 0 | 6.7799 | 39.95
2020-08-14 05:00 | 44057.2083 | 0 | 6.9681 | 39.95
2020-08-14 05:30 | 44057.2292 | 0 | 7.2417 | 39.95
2020-08-14 06:00 | 44057.25 | 0 | 7.5988 | 39.95
2020-08-14 06:30 | 44057.2708 | 0 | 7.8957 | 39.95
2020-08-14 07:00 | 44057.2917 | 0 | 8.4474 | 39.95
2020-08-14 07:30 | 44057.3125 | 0 | 8.2892 | 39.95
2020-08-14 08:00 | 44057.3333 | 0 | 9.1885 | 39.95
2020-08-14 08:30 | 44057.3542 | 0 | 9.2812 | 39.95
2020-08-14 09:00 | 44057.375 | 0 | 8.4246 | 39.95
2020-08-14 09:30 | 44057.3958 | 0 | 8.4383 | 39.95
2020-08-14 10:00 | 44057.4167 | 0 | 8.6987 | 39.95
2020-08-14 10:30 | 44057.4375 | 0 | 7.6557 | 39.95
2020-08-14 11:00 | 44057.4583 | 0 | 6.222 | 39.95
2020-08-14 11:30 | 44057.4792 | 0 | 8.5007 | 39.95
2020-08-14 12:00 | 44057.5 | 0 | 7.835 | 39.95
2020-08-14 12:30 | 44057.5208 | 0 | 8.2003 | 39.95
2020-08-14 13:00 | 44057.5417 | 0 | 6.9119 | 39.95
2020-08-14 13:30 | 44057.5625 | 0 | 6.6889 | 39.95
2020-08-14 14:00 | 44057.5833 | 0 | 9.3177 | 39.95
2020-08-14 14:30 | 44057.6042 | 0 | 9.6547 | 39.95
2020-08-14 15:00 | 44057.625 | 0 | 9.1936 | 39.95
2020-08-14 15:30 | 44057.6458 | 0 | 9.3589 | 39.95
2020-08-14 16:00 | 44057.6667 | 0 | 9.5156 | 39.95
2020-08-14 16:30 | 44057.6875 | 0 | 10.1001 | 39.95
2020-08-14 17:00 | 44057.7083 | 0 | 10.0833 | 39.95
2020-08-14 17:30 | 44057.7292 | 0 | 10.647 | 39.95
2020-08-14 18:00 | 44057.75 | 0 | 10.9187 | 39.95
2020-08-14 18:30 | 44057.7708 | 0 | 11.021 | 39.95
2020-08-14 19:00 | 44057.7917 | 0 | 10.7471 | 39.95
2020-08-14 19:30 | 44057.8125 | 0 | 10.5307 | 39.95
2020-08-14 20:00 | 44057.8333 | 0 | 10.4302 | 39.95
2020-08-14 20:30 | 44057.8542 | 0 | 9.999 | 39.95
2020-08-14 21:00 | 44057.875 | 0 | 9.5888 | 39.95
2020-08-14 21:30 | 44057.8958 | 0 | 9.4523 | 39.95
2020-08-14 22:00 | 44057.9167 | 0 | 9.1502 | 39.95
2020-08-14 22:30 | 44057.9375 | 0 | 8.6542 | 39.95
2020-08-14 23:00 | 44057.9583 | 0 | 8.2789 | 39.95
2020-08-14 23:30 | 44057.9792 | 0 | 7.7826 | 39.95
2020-08-15 | 44058 | 0 | 7.354 | 39.95
2020-08-15 00:30 | 44058.0208 | 0 | 7.0607 | 39.95
2020-08-15 01:00 | 44058.0417 | 0 | 6.8367 | 39.95
2020-08-15 01:30 | 44058.0625 | 0 | 6.7539 | 39.95
2020-08-15 02:00 | 44058.0833 | 0 | 6.7311 | 39.95
2020-08-15 02:30 | 44058.1042 | 0 | 6.6328 | 39.95
2020-08-15 03:00 | 44058.125 | 0 | 6.6533 | 39.95
2020-08-15 03:30 | 44058.1458 | 0 | 6.5303 | 39.95
2020-08-15 04:00 | 44058.1667 | 0 | 6.4521 | 39.95
2020-08-15 04:30 | 44058.1875 | 0 | 6.4841 | 39.95
2020-08-15 05:00 | 44058.2083 | 0 | 6.6069 | 39.95
2020-08-15 05:30 | 44058.2292 | 0 | 6.8528 | 39.95
2020-08-15 06:00 | 44058.25 | 0 | 7.1229 | 39.95
2020-08-15 06:30 | 44058.2708 | 0 | 7.1873 | 39.95
2020-08-15 07:00 | 44058.2917 | 0 | 7.2208 | 39.95
2020-08-15 07:30 | 44058.3125 | 0 | 7.1854 | 39.95
2020-08-15 08:00 | 44058.3333 | 0 | 7.0066 | 39.95
2020-08-15 08:30 | 44058.3542 | 0 | 6.8905 | 39.95
2020-08-15 09:00 | 44058.375 | 0 | 6.4669 | 39.95
2020-08-15 09:30 | 44058.3958 | 0 | 6.1477 | 39.95
2020-08-15 10:00 | 44058.4167 | 0 | 5.9126 | 39.95
2020-08-15 10:30 | 44058.4375 | 0 | 5.6927 | 39.95
2020-08-15 11:00 | 44058.4583 | 0 | 5.6313 | 39.95
2020-08-15 11:30 | 44058.4792 | 0 | 5.8363 | 39.95
2020-08-15 12:00 | 44058.5 | 0 | 5.1847 | 39.95
2020-08-15 12:30 | 44058.5208 | 0 | 5.1554 | 39.95
2020-08-15 13:00 | 44058.5417 | 0 | 5.7064 | 39.95
2020-08-15 13:30 | 44058.5625 | 0 | 5.7722 | 39.95
2020-08-15 14:00 | 44058.5833 | 0 | 6.2675 | 39.95
2020-08-15 14:30 | 44058.6042 | 0 | 6.4399 | 39.95
2020-08-15 15:00 | 44058.625 | 0 | 7.0918 | 39.95
2020-08-15 15:30 | 44058.6458 | 0 | 7.6183 | 39.95
2020-08-15 16:00 | 44058.6667 | 0 | 8.2999 | 39.95
2020-08-15 16:30 | 44058.6875 | 0 | 9.4481 | 39.95
2020-08-15 17:00 | 44058.7083 | 0 | 10.1989 | 39.95
2020-08-15 17:30 | 44058.7292 | 0 | 11.112 | 39.95
2020-08-15 18:00 | 44058.75 | 0 | 11.8553 | 39.95
2020-08-15 18:30 | 44058.7708 | 0 | 11.9634 | 39.95
2020-08-15 19:00 | 44058.7917 | 0 | 11.7203 | 39.95
2020-08-15 19:30 | 44058.8125 | 0 | 11.3282 | 39.95
2020-08-15 20:00 | 44058.8333 | 0 | 11.2906 | 39.95
2020-08-15 20:30 | 44058.8542 | 0 | 10.632 | 39.95
2020-08-15 21:00 | 44058.875 | 0 | 10.1801 | 39.95
2020-08-15 21:30 | 44058.8958 | 0 | 9.8298 | 39.95
2020-08-15 22:00 | 44058.9167 | 0 | 9.3965 | 39.95
2020-08-15 22:30 | 44058.9375 | 0 | 8.6156 | 39.95
2020-08-15 23:00 | 44058.9583 | 0 | 8.1441 | 39.95
2020-08-15 23:30 | 44058.9792 | 0 | 7.775 | 39.95
2020-08-16 | 44059 | 0 | 7.3171 | 39.95
2020-08-16 00:30 | 44059.0208 | 0 | 7.066 | 39.95
2020-08-16 01:00 | 44059.0417 | 0 | 6.8726 | 39.95
2020-08-16 01:30 | 44059.0625 | 0 | 6.9103 | 39.95
2020-08-16 02:00 | 44059.0833 | 0 | 6.8357 | 39.95
2020-08-16 02:30 | 44059.1042 | 0 | 6.8601 | 39.95
2020-08-16 03:00 | 44059.125 | 0 | 6.9807 | 39.95
2020-08-16 03:30 | 44059.1458 | 0 | 6.992 | 39.95
2020-08-16 04:00 | 44059.1667 | 0 | 7.1244 | 39.95
2020-08-16 04:30 | 44059.1875 | 0 | 7.4296 | 39.95
2020-08-16 05:00 | 44059.2083 | 0 | 8.134 | 39.95
2020-08-16 05:30 | 44059.2292 | 0 | 8.917 | 39.95
2020-08-16 06:00 | 44059.25 | 0 | 10.1888 | 39.95
2020-08-16 06:30 | 44059.2708 | 0 | 11.4639 | 39.95
2020-08-16 07:00 | 44059.2917 | 0 | 11.978 | 39.95
2020-08-16 07:30 | 44059.3125 | 0 | 11.5805 | 39.95
2020-08-16 08:00 | 44059.3333 | 0 | 10.7831 | 39.95
2020-08-16 08:30 | 44059.3542 | 0 | 9.9859 | 39.95
2020-08-16 09:00 | 44059.375 | 0 | 9.2093 | 39.95
2020-08-16 09:30 | 44059.3958 | 0 | 8.5401 | 39.95
2020-08-16 10:00 | 44059.4167 | 0 | 8.1616 | 39.95
2020-08-16 10:30 | 44059.4375 | 0 | 7.7115 | 39.95
2020-08-16 11:00 | 44059.4583 | 0 | 7.5484 | 39.95
2020-08-16 11:30 | 44059.4792 | 0 | 7.3276 | 39.95
2020-08-16 12:00 | 44059.5 | 0 | 7.2897 | 39.95
2020-08-16 12:30 | 44059.5208 | 0 | 7.4628 | 39.95
2020-08-16 13:00 | 44059.5417 | 0 | 7.5259 | 39.95
2020-08-16 13:30 | 44059.5625 | 0 | 7.7663 | 39.95
2020-08-16 14:00 | 44059.5833 | 0 | 8.1518 | 39.95
2020-08-16 14:30 | 44059.6042 | 0 | 8.3388 | 39.95
2020-08-16 15:00 | 44059.625 | 0 | 8.7232 | 39.95
2020-08-16 15:30 | 44059.6458 | 0 | 9.3902 | 39.95
2020-08-16 16:00 | 44059.6667 | 0 | 10.0604 | 39.95
2020-08-16 16:30 | 44059.6875 | 0 | 10.9098 | 39.95
2020-08-16 17:00 | 44059.7083 | 0 | 11.654 | 39.95
2020-08-16 17:30 | 44059.7292 | 0 | 12.869 | 39.95
2020-08-16 18:00 | 44059.75 | 0 | 13.6531 | 39.95
2020-08-16 18:30 | 44059.7708 | 0 | 13.939 | 39.95
2020-08-16 19:00 | 44059.7917 | 0 | 13.619 | 39.95
2020-08-16 19:30 | 44059.8125 | 0 | 13.5637 | 39.95
2020-08-16 20:00 | 44059.8333 | 0 | 13.2368 | 39.95
2020-08-16 20:30 | 44059.8542 | 0 | 12.5116 | 39.95
2020-08-16 21:00 | 44059.875 | 0 | 12.0387 | 39.95
2020-08-16 21:30 | 44059.8958 | 0 | 11.4089 | 39.95
2020-08-16 22:00 | 44059.9167 | 0 | 10.7448 | 39.95
2020-08-16 22:30 | 44059.9375 | 0 | 10.0479 | 39.95
2020-08-16 23:00 | 44059.9583 | 0 | 9.4562 | 39.95
2020-08-16 23:30 | 44059.9792 | 0 | 8.9224 | 39.95
2020-08-17 | 44060 | 0 | 8.3064 | 39.95
2020-08-17 00:30 | 44060.0208 | 0 | 7.8031 | 39.95
2020-08-17 01:00 | 44060.0417 | 0 | 7.5614 | 39.95
2020-08-17 01:30 | 44060.0625 | 0 | 7.4515 | 39.95
2020-08-17 02:00 | 44060.0833 | 0 | 7.4275 | 39.95
2020-08-17 02:30 | 44060.1042 | 0 | 7.3582 | 39.95
2020-08-17 03:00 | 44060.125 | 0 | 7.433 | 39.95
2020-08-17 03:30 | 44060.1458 | 0 | 7.4127 | 39.95
2020-08-17 04:00 | 44060.1667 | 0 | 7.6014 | 39.95
2020-08-17 04:30 | 44060.1875 | 0 | 8.1059 | 39.95
2020-08-17 05:00 | 44060.2083 | 0 | 8.8785 | 39.95
2020-08-17 05:30 | 44060.2292 | 0 | 9.8271 | 39.95
2020-08-17 06:00 | 44060.25 | 0 | 11.1973 | 39.95
2020-08-17 06:30 | 44060.2708 | 0 | 12.4228 | 39.95
2020-08-17 07:00 | 44060.2917 | 0 | 13.2194 | 39.95
2020-08-17 07:30 | 44060.3125 | 0 | 12.5877 | 39.95
2020-08-17 08:00 | 44060.3333 | 0 | 11.4402 | 39.95
2020-08-17 08:30 | 44060.3542 | 0 | 10.5404 | 39.95
2020-08-17 09:00 | 44060.375 | 0 | 9.7527 | 39.95
2020-08-17 09:30 | 44060.3958 | 0 | 9.2408 | 39.95
2020-08-17 10:00 | 44060.4167 | 0 | 8.8955 | 39.95
2020-08-17 10:30 | 44060.4375 | 0 | 8.5071 | 39.95
2020-08-17 11:00 | 44060.4583 | 0 | 8.339 | 39.95
2020-08-17 11:30 | 44060.4792 | 0 | 8.4008 | 39.95
2020-08-17 12:00 | 44060.5 | 0 | 8.1326 | 39.95
2020-08-17 12:30 | 44060.5208 | 0 | 8.2952 | 39.95
2020-08-17 13:00 | 44060.5417 | 0 | 8.7105 | 39.95
2020-08-17 13:30 | 44060.5625 | 0 | 10.197 | 39.95
2020-08-17 14:00 | 44060.5833 | 0 | 11.0479 | 39.95
2020-08-17 14:30 | 44060.6042 | 0 | 11.1439 | 39.95
2020-08-17 15:00 | 44060.625 | 0 | 10.8723 | 39.95
2020-08-17 15:30 | 44060.6458 | 0 | 10.9648 | 39.95
2020-08-17 16:00 | 44060.6667 | 0 | 10.8327 | 39.95
2020-08-17 16:30 | 44060.6875 | 0 | 11.6476 | 39.95
2020-08-17 17:00 | 44060.7083 | 0 | 12.3169 | 39.95
2020-08-17 17:30 | 44060.7292 | 0 | 13.2997 | 39.95
2020-08-17 18:00 | 44060.75 | 0 | 14.0128 | 39.95
2020-08-17 18:30 | 44060.7708 | 0 | 14.1997 | 39.95
2020-08-17 19:00 | 44060.7917 | 0 | 13.9222 | 39.95
2020-08-17 19:30 | 44060.8125 | 0 | 13.6063 | 39.95
2020-08-17 20:00 | 44060.8333 | 0 | 13.3897 | 39.95
2020-08-17 20:30 | 44060.8542 | 0 | 12.7513 | 39.95
2020-08-17 21:00 | 44060.875 | 0 | 12.1028 | 39.95
2020-08-17 21:30 | 44060.8958 | 0 | 11.6316 | 39.95
2020-08-17 22:00 | 44060.9167 | 0 | 11.1409 | 39.95
2020-08-17 22:30 | 44060.9375 | 0 | 10.2208 | 39.95
2020-08-17 23:00 | 44060.9583 | 0 | 9.5581 | 39.95
2020-08-17 23:30 | 44060.9792 | 0 | 8.9921 | 39.95
2020-08-18 | 44061 | 0 | 8.3984 | 39.95
2020-08-18 00:30 | 44061.0208 | 0 | 7.8555 | 39.95
2020-08-18 01:00 | 44061.0417 | 0 | 7.6361 | 39.95
2020-08-18 01:30 | 44061.0625 | 0 | 7.6412 | 39.95
2020-08-18 02:00 | 44061.0833 | 0 | 7.4888 | 39.95
2020-08-18 02:30 | 44061.1042 | 0 | 7.4928 | 39.95
2020-08-18 03:00 | 44061.125 | 0 | 7.4776 | 39.95
2020-08-18 03:30 | 44061.1458 | 0 | 7.6154 | 39.95
2020-08-18 04:00 | 44061.1667 | 0 | 7.8915 | 39.95
2020-08-18 04:30 | 44061.1875 | 0 | 8.3777 | 39.95
2020-08-18 05:00 | 44061.2083 | 0 | 8.9949 | 39.95
2020-08-18 05:30 | 44061.2292 | 0 | 9.9268 | 39.95
2020-08-18 06:00 | 44061.25 | 0 | 10.9138 | 39.95
2020-08-18 06:30 | 44061.2708 | 0 | 11.9436 | 39.95
2020-08-18 07:00 | 44061.2917 | 0 | 12.2549 | 39.95
2020-08-18 07:30 | 44061.3125 | 0 | 11.8625 | 39.95
2020-08-18 08:00 | 44061.3333 | 0 | 11.2487 | 39.95
2020-08-18 08:30 | 44061.3542 | 0 | 10.4522 | 39.95
2020-08-18 09:00 | 44061.375 | 0 | 9.5799 | 39.95
2020-08-18 09:30 | 44061.3958 | 0 | 9.1039 | 39.95
2020-08-18 10:00 | 44061.4167 | 0 | 8.7893 | 39.95
2020-08-18 10:30 | 44061.4375 | 0 | 8.5776 | 39.95
2020-08-18 11:00 | 44061.4583 | 0 | 8.3465 | 39.95
2020-08-18 11:30 | 44061.4792 | 0 | 8.3879 | 39.95
2020-08-18 12:00 | 44061.5 | 0 | 8.2213 | 39.95
2020-08-18 12:30 | 44061.5208 | 0 | 8.2542 | 39.95
2020-08-18 13:00 | 44061.5417 | 0 | 8.5154 | 39.95
2020-08-18 13:30 | 44061.5625 | 0 | 8.7003 | 39.95
2020-08-18 14:00 | 44061.5833 | 0 | 9.2576 | 39.95
2020-08-18 14:30 | 44061.6042 | 0 | 10.0745 | 39.95
2020-08-18 15:00 | 44061.625 | 0 | 10.8618 | 39.95
2020-08-18 15:30 | 44061.6458 | 0 | 10.5509 | 39.95
2020-08-18 16:00 | 44061.6667 | 0 | 10.9509 | 39.95
2020-08-18 16:30 | 44061.6875 | 0 | 11.6575 | 39.95
2020-08-18 17:00 | 44061.7083 | 0 | 12.6571 | 39.95
2020-08-18 17:30 | 44061.7292 | 0 | 13.7036 | 39.95
2020-08-18 18:00 | 44061.75 | 0 | 14.1272 | 39.95
2020-08-18 18:30 | 44061.7708 | 0 | 14.3919 | 39.95
2020-08-18 19:00 | 44061.7917 | 0 | 14.229 | 39.95
2020-08-18 19:30 | 44061.8125 | 0 | 13.906 | 39.95
2020-08-18 20:00 | 44061.8333 | 0 | 13.554 | 39.95
2020-08-18 20:30 | 44061.8542 | 0 | 12.9562 | 39.95
2020-08-18 21:00 | 44061.875 | 0 | 12.4371 | 39.95
2020-08-18 21:30 | 44061.8958 | 0 | 12.1171 | 39.95
2020-08-18 22:00 | 44061.9167 | 0 | 11.4368 | 39.95
2020-08-18 22:30 | 44061.9375 | 0 | 10.6033 | 39.95
2020-08-18 23:00 | 44061.9583 | 0 | 10.0069 | 39.95
2020-08-18 23:30 | 44061.9792 | 0 | 9.4486 | 39.95
2020-08-19 | 44062 | 0 | 8.9008 | 39.95
2020-08-19 00:30 | 44062.0208 | 0 | 8.4395 | 39.95
2020-08-19 01:00 | 44062.0417 | 0 | 8.2165 | 39.95
2020-08-19 01:30 | 44062.0625 | 0 | 8.1185 | 39.95
2020-08-19 02:00 | 44062.0833 | 0 | 7.9466 | 39.95
2020-08-19 02:30 | 44062.1042 | 0 | 7.4888 | 39.95
2020-08-19 03:00 | 44062.125 | 0 | 7.5408 | 39.95
2020-08-19 03:30 | 44062.1458 | 0 | 7.4014 | 39.95
2020-08-19 04:00 | 44062.1667 | 0 | 7.6642 | 39.95
2020-08-19 04:30 | 44062.1875 | 0 | 8.0013 | 39.95
2020-08-19 05:00 | 44062.2083 | 0 | 8.769 | 39.95
2020-08-19 05:30 | 44062.2292 | 0 | 9.4289 | 39.95
2020-08-19 06:00 | 44062.25 | 0 | 10.4107 | 39.95
2020-08-19 06:30 | 44062.2708 | 0 | 11.3099 | 39.95
2020-08-19 07:00 | 44062.2917 | 0 | 11.5419 | 39.95
2020-08-19 07:30 | 44062.3125 | 0 | 11.0051 | 39.95
2020-08-19 08:00 | 44062.3333 | 0 | 10.8259 | 39.95
2020-08-19 08:30 | 44062.3542 | 0 | 10.1606 | 39.95
2020-08-19 09:00 | 44062.375 | 0 | 9.6741 | 39.95
2020-08-19 09:30 | 44062.3958 | 0 | 9.0464 | 39.95
2020-08-19 10:00 | 44062.4167 | 0 | 8.6529 | 39.95
2020-08-19 10:30 | 44062.4375 | 0 | 8.5138 | 39.95
2020-08-19 11:00 | 44062.4583 | 0 | 8.4884 | 39.95
2020-08-19 11:30 | 44062.4792 | 0 | 8.3335 | 39.95
2020-08-19 12:00 | 44062.5 | 0 | 8.168 | 39.95
2020-08-19 12:30 | 44062.5208 | 0 | 8.2111 | 39.95
2020-08-19 13:00 | 44062.5417 | 0 | 8.4504 | 39.95
2020-08-19 13:30 | 44062.5625 | 0 | 8.967 | 39.95
2020-08-19 14:00 | 44062.5833 | 0 | 9.2943 | 39.95
2020-08-19 14:30 | 44062.6042 | 0 | 9.4115 | 39.95
2020-08-19 15:00 | 44062.625 | 0 | 9.791 | 39.95
2020-08-19 15:30 | 44062.6458 | 0 | 10.2886 | 39.95
2020-08-19 16:00 | 44062.6667 | 0 | 10.9963 | 39.95
2020-08-19 16:30 | 44062.6875 | 0 | 11.6233 | 39.95
2020-08-19 17:00 | 44062.7083 | 0 | 12.1516 | 39.95
2020-08-19 17:30 | 44062.7292 | 0 | 13.1868 | 39.95
2020-08-19 18:00 | 44062.75 | 0 | 13.5281 | 39.95
2020-08-19 18:30 | 44062.7708 | 0 | 13.7852 | 39.95
2020-08-19 19:00 | 44062.7917 | 0 | 13.6003 | 39.95
2020-08-19 19:30 | 44062.8125 | 0 | 13.2862 | 39.95
2020-08-19 20:00 | 44062.8333 | 0 | 13.078 | 39.95
2020-08-19 20:30 | 44062.8542 | 0 | 12.5784 | 39.95
2020-08-19 21:00 | 44062.875 | 0 | 12.0771 | 39.95
2020-08-19 21:30 | 44062.8958 | 0 | 11.7523 | 39.95
2020-08-19 22:00 | 44062.9167 | 0 | 11.2708 | 39.95
2020-08-19 22:30 | 44062.9375 | 0 | 10.4817 | 39.95
2020-08-19 23:00 | 44062.9583 | 0 | 9.7607 | 39.95
2020-08-19 23:30 | 44062.9792 | 0 | 9.0788 | 39.95
2020-08-20 | 44063 | 0 | 8.4395 | 39.95
2020-08-20 00:30 | 44063.0208 | 0 | 7.9412 | 39.95
2020-08-20 01:00 | 44063.0417 | 0 | 7.8202 | 39.95
2020-08-20 01:30 | 44063.0625 | 0 | 7.6673 | 39.95
2020-08-20 02:00 | 44063.0833 | 0 | 7.6192 | 39.95
2020-08-20 02:30 | 44063.1042 | 0 | 7.5297 | 39.95
2020-08-20 03:00 | 44063.125 | 0 | 7.6509 | 39.95
2020-08-20 03:30 | 44063.1458 | 0 | 7.6174 | 39.95
2020-08-20 04:00 | 44063.1667 | 0 | 7.9043 | 39.95
2020-08-20 04:30 | 44063.1875 | 0 | 8.2534 | 39.95
2020-08-20 05:00 | 44063.2083 | 0 | 8.9291 | 39.95
2020-08-20 05:30 | 44063.2292 | 0 | 9.8869 | 39.95
2020-08-20 06:00 | 44063.25 | 0 | 10.9873 | 39.95
2020-08-20 06:30 | 44063.2708 | 0 | 11.8718 | 39.95
2020-08-20 07:00 | 44063.2917 | 0 | 12.5644 | 39.95
2020-08-20 07:30 | 44063.3125 | 0 | 12.8662 | 39.95
2020-08-20 08:00 | 44063.3333 | 0 | 11.1463 | 39.95
2020-08-20 08:30 | 44063.3542 | 0 | 10.58 | 39.95
2020-08-20 09:00 | 44063.375 | 0 | 9.8838 | 39.95
2020-08-20 09:30 | 44063.3958 | 0 | 9.4399 | 39.95
2020-08-20 10:00 | 44063.4167 | 0 | 8.7207 | 39.95
2020-08-20 10:30 | 44063.4375 | 0 | 8.6378 | 39.95
2020-08-20 11:00 | 44063.4583 | 0 | 8.7596 | 39.95
2020-08-20 11:30 | 44063.4792 | 0 | 8.3023 | 39.95
2020-08-20 12:00 | 44063.5 | 0 | 8.0471 | 39.95
2020-08-20 12:30 | 44063.5208 | 0 | 7.9448 | 39.95
2020-08-20 13:00 | 44063.5417 | 0 | 8.1388 | 39.95
2020-08-20 13:30 | 44063.5625 | 0 | 8.4081 | 39.95
2020-08-20 14:00 | 44063.5833 | 0 | 8.6298 | 39.95
2020-08-20 14:30 | 44063.6042 | 0 | 9.4414 | 39.95
2020-08-20 15:00 | 44063.625 | 0 | 9.6553 | 39.95
2020-08-20 15:30 | 44063.6458 | 0 | 10.0516 | 39.95
2020-08-20 16:00 | 44063.6667 | 0 | 10.4001 | 39.95
2020-08-20 16:30 | 44063.6875 | 0 | 11.3823 | 39.95
2020-08-20 17:00 | 44063.7083 | 0 | 11.8058 | 39.95
2020-08-20 17:30 | 44063.7292 | 0 | 12.5555 | 39.95
2020-08-20 18:00 | 44063.75 | 0 | 12.8242 | 39.95
2020-08-20 18:30 | 44063.7708 | 0 | 13.1579 | 39.95
2020-08-20 19:00 | 44063.7917 | 0 | 12.8743 | 39.95
2020-08-20 19:30 | 44063.8125 | 0 | 12.6717 | 39.95
2020-08-20 20:00 | 44063.8333 | 0 | 12.5356 | 39.95
2020-08-20 20:30 | 44063.8542 | 0 | 11.9235 | 39.95
2020-08-20 21:00 | 44063.875 | 0 | 11.758 | 39.95
2020-08-20 21:30 | 44063.8958 | 0 | 11.4976 | 39.95
2020-08-20 22:00 | 44063.9167 | 0 | 10.9152 | 39.95
2020-08-20 22:30 | 44063.9375 | 0 | 10.187 | 39.95
2020-08-20 23:00 | 44063.9583 | 0 | 9.6946 | 39.95
2020-08-20 23:30 | 44063.9792 | 0 | 9.1821 | 39.95
2020-08-21 | 44064 | 0 | 8.5966 | 39.95
2020-08-21 00:30 | 44064.0208 | 0 | 7.9754 | 39.95
2020-08-21 01:00 | 44064.0417 | 0 | 7.714 | 39.95
2020-08-21 01:30 | 44064.0625 | 0 | 7.5668 | 39.95
2020-08-21 02:00 | 44064.0833 | 0 | 7.4628 | 39.95
2020-08-21 02:30 | 44064.1042 | 0 | 7.4534 | 39.95
2020-08-21 03:00 | 44064.125 | 0 | 7.3056 | 39.95
2020-08-21 03:30 | 44064.1458 | 0 | 7.3083 | 39.95
2020-08-21 04:00 | 44064.1667 | 0 | 7.4779 | 39.95
2020-08-21 04:30 | 44064.1875 | 0 | 7.6268 | 39.95
2020-08-21 05:00 | 44064.2083 | 0 | 7.8236 | 39.95
2020-08-21 05:30 | 44064.2292 | 0 | 8.1648 | 39.95
2020-08-21 06:00 | 44064.25 | 0 | 8.5568 | 39.95
2020-08-21 06:30 | 44064.2708 | 0 | 8.8105 | 39.95
2020-08-21 07:00 | 44064.2917 | 0 | 8.9516 | 39.95
2020-08-21 07:30 | 44064.3125 | 0 | 8.6459 | 39.95
2020-08-21 08:00 | 44064.3333 | 0 | 8.3583 | 39.95
2020-08-21 08:30 | 44064.3542 | 0 | 7.9929 | 39.95
2020-08-21 09:00 | 44064.375 | 0 | 8.8925 | 39.95
2020-08-21 09:30 | 44064.3958 | 0 | 8.721 | 39.95
2020-08-21 10:00 | 44064.4167 | 0 | 8.8197 | 39.95
2020-08-21 10:30 | 44064.4375 | 0 | 8.89 | 39.95
2020-08-21 11:00 | 44064.4583 | 0 | 8.1597 | 39.95
2020-08-21 11:30 | 44064.4792 | 0 | 6.4723 | 39.95
2020-08-21 12:00 | 44064.5 | 0 | 6.3667 | 39.95
2020-08-21 12:30 | 44064.5208 | 0 | 6.2754 | 39.95
2020-08-21 13:00 | 44064.5417 | 0 | 6.3723 | 39.95
2020-08-21 13:30 | 44064.5625 | 0 | 6.7791 | 39.95
2020-08-21 14:00 | 44064.5833 | 0 | 7.0574 | 39.95
2020-08-21 14:30 | 44064.6042 | 0 | 7.2857 | 39.95
2020-08-21 15:00 | 44064.625 | 0 | 7.9676 | 39.95
2020-08-21 15:30 | 44064.6458 | 0 | 8.2536 | 39.95
2020-08-21 16:00 | 44064.6667 | 0 | 8.8884 | 39.95
2020-08-21 16:30 | 44064.6875 | 0 | 9.7134 | 39.95
2020-08-21 17:00 | 44064.7083 | 0 | 10.3632 | 39.95
2020-08-21 17:30 | 44064.7292 | 0 | 11.0705 | 39.95
2020-08-21 18:00 | 44064.75 | 0 | 11.4569 | 39.95
2020-08-21 18:30 | 44064.7708 | 0 | 11.659 | 39.95
2020-08-21 19:00 | 44064.7917 | 0 | 11.4474 | 39.95
2020-08-21 19:30 | 44064.8125 | 0 | 11.1289 | 39.95
2020-08-21 20:00 | 44064.8333 | 0 | 10.9501 | 39.95
2020-08-21 20:30 | 44064.8542 | 0 | 10.558 | 39.95
2020-08-21 21:00 | 44064.875 | 0 | 10.2192 | 39.95
2020-08-21 21:30 | 44064.8958 | 0 | 9.8375 | 39.95
2020-08-21 22:00 | 44064.9167 | 0 | 9.5966 | 39.95
2020-08-21 22:30 | 44064.9375 | 0 | 9.0127 | 39.95
2020-08-21 23:00 | 44064.9583 | 0 | 8.4673 | 39.95
2020-08-21 23:30 | 44064.9792 | 0 | 7.9814 | 39.95
2020-08-22 | 44065 | 0 | 7.561 | 39.95
2020-08-22 00:30 | 44065.0208 | 0 | 7.1503 | 39.95
2020-08-22 01:00 | 44065.0417 | 0 | 7.057 | 39.95
2020-08-22 01:30 | 44065.0625 | 0 | 6.9248 | 39.95
2020-08-22 02:00 | 44065.0833 | 0 | 6.9027 | 39.95
2020-08-22 02:30 | 44065.1042 | 0 | 6.8748 | 39.95
2020-08-22 03:00 | 44065.125 | 0 | 6.7554 | 39.95
2020-08-22 03:30 | 44065.1458 | 0 | 6.6756 | 39.95
2020-08-22 04:00 | 44065.1667 | 0 | 6.6495 | 39.95
2020-08-22 04:30 | 44065.1875 | 0 | 6.7034 | 39.95
2020-08-22 05:00 | 44065.2083 | 0 | 6.8604 | 39.95
2020-08-22 05:30 | 44065.2292 | 0 | 7.1727 | 39.95
2020-08-22 06:00 | 44065.25 | 0 | 7.5644 | 39.95
2020-08-22 06:30 | 44065.2708 | 0 | 7.7459 | 39.95
2020-08-22 07:00 | 44065.2917 | 0 | 7.8405 | 39.95
2020-08-22 07:30 | 44065.3125 | 0 | 7.714 | 39.95
2020-08-22 08:00 | 44065.3333 | 0 | 7.8239 | 39.95
2020-08-22 08:30 | 44065.3542 | 0 | 7.5928 | 39.95
2020-08-22 09:00 | 44065.375 | 0 | 7.1566 | 39.95
2020-08-22 09:30 | 44065.3958 | 0 | 6.8537 | 39.95
2020-08-22 10:00 | 44065.4167 | 0 | 6.4338 | 39.95
2020-08-22 10:30 | 44065.4375 | 0 | 6.0367 | 39.95
2020-08-22 11:00 | 44065.4583 | 0 | 5.6692 | 39.95
2020-08-22 11:30 | 44065.4792 | 0 | 5.6017 | 39.95
2020-08-22 12:00 | 44065.5 | 0 | 5.5514 | 39.95
2020-08-22 12:30 | 44065.5208 | 0 | 5.4994 | 39.95
2020-08-22 13:00 | 44065.5417 | 0 | 5.6413 | 39.95
2020-08-22 13:30 | 44065.5625 | 0 | 5.9146 | 39.95
2020-08-22 14:00 | 44065.5833 | 0 | 6.3405 | 39.95
2020-08-22 14:30 | 44065.6042 | 0 | 6.6451 | 39.95
2020-08-22 15:00 | 44065.625 | 0 | 7.117 | 39.95
2020-08-22 15:30 | 44065.6458 | 0 | 7.7265 | 39.95
2020-08-22 16:00 | 44065.6667 | 0 | 8.5738 | 39.95
2020-08-22 16:30 | 44065.6875 | 0 | 9.5865 | 39.95
2020-08-22 17:00 | 44065.7083 | 0 | 10.4741 | 39.95
2020-08-22 17:30 | 44065.7292 | 0 | 11.4546 | 39.95
2020-08-22 18:00 | 44065.75 | 0 | 12.4605 | 39.95
2020-08-22 18:30 | 44065.7708 | 0 | 12.6452 | 39.95
2020-08-22 19:00 | 44065.7917 | 0 | 12.3256 | 39.95
2020-08-22 19:30 | 44065.8125 | 0 | 12.1829 | 39.95
2020-08-22 20:00 | 44065.8333 | 0 | 12.0928 | 39.95
2020-08-22 20:30 | 44065.8542 | 0 | 11.3913 | 39.95
2020-08-22 21:00 | 44065.875 | 0 | 10.8516 | 39.95
2020-08-22 21:30 | 44065.8958 | 0 | 10.392 | 39.95
2020-08-22 22:00 | 44065.9167 | 0 | 9.8496 | 39.95
2020-08-22 22:30 | 44065.9375 | 0 | 8.8114 | 39.95
2020-08-22 23:00 | 44065.9583 | 0 | 8.3225 | 39.95
2020-08-22 23:30 | 44065.9792 | 0 | 7.7423 | 39.95
2020-08-23 | 44066 | 0 | 7.3601 | 39.95
2020-08-23 00:30 | 44066.0208 | 0 | 7.2392 | 39.95
2020-08-23 01:00 | 44066.0417 | 0 | 7.072 | 39.95
2020-08-23 01:30 | 44066.0625 | 0 | 6.9817 | 39.95
2020-08-23 02:00 | 44066.0833 | 0 | 7.0813 | 39.95
2020-08-23 02:30 | 44066.1042 | 0 | 7.0068 | 39.95
2020-08-23 03:00 | 44066.125 | 0 | 7.0721 | 39.95
2020-08-23 03:30 | 44066.1458 | 0 | 7.0815 | 39.95
2020-08-23 04:00 | 44066.1667 | 0 | 7.5043 | 39.95
2020-08-23 04:30 | 44066.1875 | 0 | 7.8381 | 39.95
2020-08-23 05:00 | 44066.2083 | 0 | 8.5968 | 39.95
2020-08-23 05:30 | 44066.2292 | 0 | 9.5541 | 39.95
2020-08-23 06:00 | 44066.25 | 0 | 10.9418 | 39.95
2020-08-23 06:30 | 44066.2708 | 0 | 12.4529 | 39.95
2020-08-23 07:00 | 44066.2917 | 0 | 13.1522 | 39.95
2020-08-23 07:30 | 44066.3125 | 0 | 12.3341 | 39.95
2020-08-23 08:00 | 44066.3333 | 0 | 11.4956 | 39.95
2020-08-23 08:30 | 44066.3542 | 0 | 10.5028 | 39.95
2020-08-23 09:00 | 44066.375 | 0 | 9.8269 | 39.95
2020-08-23 09:30 | 44066.3958 | 0 | 9.3085 | 39.95
2020-08-23 10:00 | 44066.4167 | 0 | 8.9884 | 39.95
2020-08-23 10:30 | 44066.4375 | 0 | 8.7132 | 39.95
2020-08-23 11:00 | 44066.4583 | 0 | 8.2449 | 39.95
2020-08-23 11:30 | 44066.4792 | 0 | 8.1719 | 39.95
2020-08-23 12:00 | 44066.5 | 0 | 8.0078 | 39.95
2020-08-23 12:30 | 44066.5208 | 0 | 7.8368 | 39.95
2020-08-23 13:00 | 44066.5417 | 0 | 8.1184 | 39.95
2020-08-23 13:30 | 44066.5625 | 0 | 8.3414 | 39.95
2020-08-23 14:00 | 44066.5833 | 0 | 8.5949 | 39.95
2020-08-23 14:30 | 44066.6042 | 0 | 8.8847 | 39.95
2020-08-23 15:00 | 44066.625 | 0 | 9.1809 | 39.95
2020-08-23 15:30 | 44066.6458 | 0 | 9.7001 | 39.95
2020-08-23 16:00 | 44066.6667 | 0 | 10.3867 | 39.95
2020-08-23 16:30 | 44066.6875 | 0 | 11.2872 | 39.95
2020-08-23 17:00 | 44066.7083 | 0 | 11.9082 | 39.95
2020-08-23 17:30 | 44066.7292 | 0 | 13.1552 | 39.95
2020-08-23 18:00 | 44066.75 | 0 | 14.0346 | 39.95
2020-08-23 18:30 | 44066.7708 | 0 | 14.2872 | 39.95
2020-08-23 19:00 | 44066.7917 | 0 | 14.2346 | 39.95
2020-08-23 19:30 | 44066.8125 | 0 | 13.8423 | 39.95
2020-08-23 20:00 | 44066.8333 | 0 | 13.4434 | 39.95
2020-08-23 20:30 | 44066.8542 | 0 | 12.9566 | 39.95
2020-08-23 21:00 | 44066.875 | 0 | 12.4222 | 39.95
2020-08-23 21:30 | 44066.8958 | 0 | 11.9711 | 39.95
2020-08-23 22:00 | 44066.9167 | 0 | 11.0836 | 39.95
2020-08-23 22:30 | 44066.9375 | 0 | 10.3455 | 39.95
2020-08-23 23:00 | 44066.9583 | 0 | 9.5524 | 39.95
2020-08-23 23:30 | 44066.9792 | 0 | 9.0894 | 39.95
2020-08-24 | 44067 | 0 | 8.4915 | 39.95
2020-08-24 00:30 | 44067.0208 | 0 | 8.2107 | 39.95
2020-08-24 01:00 | 44067.0417 | 0 | 7.8888 | 39.95
2020-08-24 01:30 | 44067.0625 | 0 | 7.7021 | 39.95
2020-08-24 02:00 | 44067.0833 | 0 | 7.7364 | 39.95
2020-08-24 02:30 | 44067.1042 | 0 | 7.6992 | 39.95
2020-08-24 03:00 | 44067.125 | 0 | 7.6972 | 39.95
2020-08-24 03:30 | 44067.1458 | 0 | 7.6974 | 39.95
2020-08-24 04:00 | 44067.1667 | 0 | 7.8931 | 39.95
2020-08-24 04:30 | 44067.1875 | 0 | 8.5071 | 39.95
2020-08-24 05:00 | 44067.2083 | 0 | 9.1902 | 39.95
2020-08-24 05:30 | 44067.2292 | 0 | 10.2356 | 39.95
2020-08-24 06:00 | 44067.25 | 0 | 11.8316 | 39.95
2020-08-24 06:30 | 44067.2708 | 0 | 13.1578 | 39.95
2020-08-24 07:00 | 44067.2917 | 0 | 13.6446 | 39.95
2020-08-24 07:30 | 44067.3125 | 0 | 13.0355 | 39.95
2020-08-24 08:00 | 44067.3333 | 0 | 12.0846 | 39.95
2020-08-24 08:30 | 44067.3542 | 0 | 11.0437 | 39.95
2020-08-24 09:00 | 44067.375 | 0 | 10.1682 | 39.95
2020-08-24 09:30 | 44067.3958 | 0 | 9.4681 | 39.95
2020-08-24 10:00 | 44067.4167 | 0 | 8.8918 | 39.95
2020-08-24 10:30 | 44067.4375 | 0 | 8.626 | 39.95
2020-08-24 11:00 | 44067.4583 | 0 | 8.3984 | 39.95
2020-08-24 11:30 | 44067.4792 | 0 | 8.291 | 39.95
2020-08-24 12:00 | 44067.5 | 0 | 8.2386 | 39.95
2020-08-24 12:30 | 44067.5208 | 0 | 8.0972 | 39.95
2020-08-24 13:00 | 44067.5417 | 0 | 8.3792 | 39.95
2020-08-24 13:30 | 44067.5625 | 0 | 8.4638 | 39.95
2020-08-24 14:00 | 44067.5833 | 0 | 8.7297 | 39.95
2020-08-24 14:30 | 44067.6042 | 0 | 8.9277 | 39.95
2020-08-24 15:00 | 44067.625 | 0 | 9.3024 | 39.95
2020-08-24 15:30 | 44067.6458 | 0 | 9.92 | 39.95
2020-08-24 16:00 | 44067.6667 | 0 | 10.4405 | 39.95
2020-08-24 16:30 | 44067.6875 | 0 | 11.5422 | 39.95
2020-08-24 17:00 | 44067.7083 | 0 | 12.2563 | 39.95
2020-08-24 17:30 | 44067.7292 | 0 | 13.4318 | 39.95
2020-08-24 18:00 | 44067.75 | 0 | 14.1425 | 39.95
2020-08-24 18:30 | 44067.7708 | 0 | 14.4788 | 39.95
2020-08-24 19:00 | 44067.7917 | 0 | 14.1403 | 39.95
2020-08-24 19:30 | 44067.8125 | 0 | 13.8906 | 39.95
2020-08-24 20:00 | 44067.8333 | 0 | 13.8019 | 39.95
2020-08-24 20:30 | 44067.8542 | 0 | 13.1911 | 39.95
2020-08-24 21:00 | 44067.875 | 0 | 12.6711 | 39.95
2020-08-24 21:30 | 44067.8958 | 0 | 11.9816 | 39.95
2020-08-24 22:00 | 44067.9167 | 0 | 11.354 | 39.95
2020-08-24 22:30 | 44067.9375 | 0 | 10.52 | 39.95
2020-08-24 23:00 | 44067.9583 | 0 | 9.7624 | 39.95
2020-08-24 23:30 | 44067.9792 | 0 | 9.1522 | 39.95
2020-08-25 | 44068 | 0 | 8.4755 | 39.95
2020-08-25 00:30 | 44068.0208 | 0 | 8.0169 | 39.95
2020-08-25 01:00 | 44068.0417 | 0 | 7.9207 | 39.95
2020-08-25 01:30 | 44068.0625 | 0 | 7.7443 | 39.95
2020-08-25 02:00 | 44068.0833 | 0 | 7.7455 | 39.95
2020-08-25 02:30 | 44068.1042 | 0 | 7.6265 | 39.95
2020-08-25 03:00 | 44068.125 | 0 | 7.7719 | 39.95
2020-08-25 03:30 | 44068.1458 | 0 | 7.8611 | 39.95
2020-08-25 04:00 | 44068.1667 | 0 | 8.094 | 39.95
2020-08-25 04:30 | 44068.1875 | 0 | 8.6337 | 39.95
2020-08-25 05:00 | 44068.2083 | 0 | 9.4329 | 39.95
2020-08-25 05:30 | 44068.2292 | 0 | 10.3417 | 39.95
2020-08-25 06:00 | 44068.25 | 0 | 11.7421 | 39.95
2020-08-25 06:30 | 44068.2708 | 0 | 12.9484 | 39.95
2020-08-25 07:00 | 44068.2917 | 0 | 14.0258 | 39.95
2020-08-25 07:30 | 44068.3125 | 0 | 13.6182 | 39.95
2020-08-25 08:00 | 44068.3333 | 0 | 12.1666 | 39.95
2020-08-25 08:30 | 44068.3542 | 0 | 11.1644 | 39.95
2020-08-25 09:00 | 44068.375 | 0 | 10.4719 | 39.95
2020-08-25 09:30 | 44068.3958 | 0 | 10.0603 | 39.95
2020-08-25 10:00 | 44068.4167 | 0 | 10.5195 | 39.95
2020-08-25 10:30 | 44068.4375 | 0 | 10.9353 | 39.95
2020-08-25 11:00 | 44068.4583 | 0 | 10.0996 | 39.95
2020-08-25 11:30 | 44068.4792 | 0 | 10.5142 | 39.95
2020-08-25 12:00 | 44068.5 | 0 | 11.3715 | 39.95
2020-08-25 12:30 | 44068.5208 | 0 | 9.5269 | 39.95
2020-08-25 13:00 | 44068.5417 | 0 | 9.3102 | 39.95
2020-08-25 13:30 | 44068.5625 | 0 | 9.77 | 39.95
2020-08-25 14:00 | 44068.5833 | 0 | 10.5721 | 39.95
2020-08-25 14:30 | 44068.6042 | 0 | 10.2395 | 39.95
2020-08-25 15:00 | 44068.625 | 0 | 10.0315 | 39.95
2020-08-25 15:30 | 44068.6458 | 0 | 10.3974 | 39.95
2020-08-25 16:00 | 44068.6667 | 0 | 11.0649 | 39.95
2020-08-25 16:30 | 44068.6875 | 0 | 11.9237 | 39.95
2020-08-25 17:00 | 44068.7083 | 0 | 12.6074 | 39.95
2020-08-25 17:30 | 44068.7292 | 0 | 13.5822 | 39.95
2020-08-25 18:00 | 44068.75 | 0 | 14.2633 | 39.95
2020-08-25 18:30 | 44068.7708 | 0 | 14.7181 | 39.95
2020-08-25 19:00 | 44068.7917 | 0 | 14.5772 | 39.95
2020-08-25 19:30 | 44068.8125 | 0 | 14.187 | 39.95
2020-08-25 20:00 | 44068.8333 | 0 | 14.0768 | 39.95
2020-08-25 20:30 | 44068.8542 | 0 | 13.4473 | 39.95
2020-08-25 21:00 | 44068.875 | 0 | 12.7942 | 39.95
2020-08-25 21:30 | 44068.8958 | 0 | 12.2731 | 39.95
2020-08-25 22:00 | 44068.9167 | 0 | 11.4853 | 39.95
2020-08-25 22:30 | 44068.9375 | 0 | 10.6315 | 39.95
2020-08-25 23:00 | 44068.9583 | 0 | 9.9382 | 39.95
2020-08-25 23:30 | 44068.9792 | 0 | 9.4274 | 39.95
2020-08-26 | 44069 | 0 | 8.8123 | 39.95
2020-08-26 00:30 | 44069.0208 | 0 | 8.2907 | 39.95
2020-08-26 01:00 | 44069.0417 | 0 | 8.1235 | 39.95
2020-08-26 01:30 | 44069.0625 | 0 | 7.798 | 39.95
2020-08-26 02:00 | 44069.0833 | 0 | 7.7386 | 39.95
2020-08-26 02:30 | 44069.1042 | 0 | 7.7157 | 39.95
2020-08-26 03:00 | 44069.125 | 0 | 7.7141 | 39.95
2020-08-26 03:30 | 44069.1458 | 0 | 7.6674 | 39.95
2020-08-26 04:00 | 44069.1667 | 0 | 7.7907 | 39.95
2020-08-26 04:30 | 44069.1875 | 0 | 8.3418 | 39.95
2020-08-26 05:00 | 44069.2083 | 0 | 9.3692 | 39.95
2020-08-26 05:30 | 44069.2292 | 0 | 10.2523 | 39.95
2020-08-26 06:00 | 44069.25 | 0 | 11.3511 | 39.95
2020-08-26 06:30 | 44069.2708 | 0 | 12.454 | 39.95
2020-08-26 07:00 | 44069.2917 | 0 | 12.8281 | 39.95
2020-08-26 07:30 | 44069.3125 | 0 | 12.3174 | 39.95
2020-08-26 08:00 | 44069.3333 | 0 | 11.6463 | 39.95
2020-08-26 08:30 | 44069.3542 | 0 | 10.5417 | 39.95
2020-08-26 09:00 | 44069.375 | 0 | 9.7292 | 39.95
2020-08-26 09:30 | 44069.3958 | 0 | 9.1967 | 39.95
2020-08-26 10:00 | 44069.4167 | 0 | 9.192 | 39.95
2020-08-26 10:30 | 44069.4375 | 0 | 9.2229 | 39.95
2020-08-26 11:00 | 44069.4583 | 0 | 9.628 | 39.95
2020-08-26 11:30 | 44069.4792 | 0 | 9.5318 | 39.95
2020-08-26 12:00 | 44069.5 | 0 | 9.5854 | 39.95
2020-08-26 12:30 | 44069.5208 | 0 | 9.3412 | 39.95
2020-08-26 13:00 | 44069.5417 | 0 | 8.2123 | 39.95
2020-08-26 13:30 | 44069.5625 | 0 | 8.2225 | 39.95
2020-08-26 14:00 | 44069.5833 | 0 | 8.776 | 39.95
2020-08-26 14:30 | 44069.6042 | 0 | 9.1649 | 39.95
2020-08-26 15:00 | 44069.625 | 0 | 10.0398 | 39.95
2020-08-26 15:30 | 44069.6458 | 0 | 10.0598 | 39.95
2020-08-26 16:00 | 44069.6667 | 0 | 11.1664 | 39.95
2020-08-26 16:30 | 44069.6875 | 0 | 11.1985 | 39.95
2020-08-26 17:00 | 44069.7083 | 0 | 12.0505 | 39.95
2020-08-26 17:30 | 44069.7292 | 0 | 13.141 | 39.95
2020-08-26 18:00 | 44069.75 | 0 | 13.8 | 39.95
2020-08-26 18:30 | 44069.7708 | 0 | 14.2669 | 39.95
2020-08-26 19:00 | 44069.7917 | 0 | 14.0488 | 39.95
2020-08-26 19:30 | 44069.8125 | 0 | 13.7759 | 39.95
2020-08-26 20:00 | 44069.8333 | 0 | 13.7193 | 39.95
2020-08-26 20:30 | 44069.8542 | 0 | 13.1494 | 39.95
2020-08-26 21:00 | 44069.875 | 0 | 12.6807 | 39.95
2020-08-26 21:30 | 44069.8958 | 0 | 12.1957 | 39.95
2020-08-26 22:00 | 44069.9167 | 0 | 11.5919 | 39.95
2020-08-26 22:30 | 44069.9375 | 0 | 10.7025 | 39.95
2020-08-26 23:00 | 44069.9583 | 0 | 9.8095 | 39.95
2020-08-26 23:30 | 44069.9792 | 0 | 9.2322 | 39.95
2020-08-27 | 44070 | 0 | 8.4948 | 39.95
2020-08-27 00:30 | 44070.0208 | 0 | 8.0509 | 39.95
2020-08-27 01:00 | 44070.0417 | 0 | 7.9297 | 39.95
2020-08-27 01:30 | 44070.0625 | 0 | 7.7493 | 39.95
2020-08-27 02:00 | 44070.0833 | 0 | 7.6975 | 39.95
2020-08-27 02:30 | 44070.1042 | 0 | 7.671 | 39.95
2020-08-27 03:00 | 44070.125 | 0 | 7.6993 | 39.95
2020-08-27 03:30 | 44070.1458 | 0 | 7.7309 | 39.95
2020-08-27 04:00 | 44070.1667 | 0 | 7.947 | 39.95
2020-08-27 04:30 | 44070.1875 | 0 | 8.4701 | 39.95
2020-08-27 05:00 | 44070.2083 | 0 | 9.2949 | 39.95
2020-08-27 05:30 | 44070.2292 | 0 | 9.9502 | 39.95
2020-08-27 06:00 | 44070.25 | 0 | 11.3006 | 39.95
2020-08-27 06:30 | 44070.2708 | 0 | 12.3074 | 39.95
2020-08-27 07:00 | 44070.2917 | 0 | 12.5619 | 39.95
2020-08-27 07:30 | 44070.3125 | 0 | 11.9765 | 39.95
2020-08-27 08:00 | 44070.3333 | 0 | 8.9464 | 39.95
2020-08-27 08:30 | 44070.3542 | 0 | 0.40199 | 39.95
2020-08-27 09:00 | 44070.375 | 0 | 0.40199 | 39.95
2020-08-27 09:30 | 44070.3958 | 0 | 0.40199 | 39.95
2020-08-27 10:00 | 44070.4167 | 0 | 0.40199 | 39.95
2020-08-27 10:30 | 44070.4375 | 0 | 0.40199 | 39.95
2020-08-27 11:00 | 44070.4583 | 0 | 0.40199 | 39.95
2020-08-27 11:30 | 44070.4792 | 0 | 0.40199 | 39.95
2020-08-27 12:00 | 44070.5 | 0 | 0.40199 | 39.95
2020-08-27 12:30 | 44070.5208 | 0 | 0.40199 | 39.95
2020-08-27 13:00 | 44070.5417 | 0 | 0.95806 | 39.95
2020-08-27 13:30 | 44070.5625 | 0 | 7.971 | 39.95
2020-08-27 14:00 | 44070.5833 | 0 | 8.3876 | 39.95
2020-08-27 14:30 | 44070.6042 | 0 | 8.8235 | 39.95
2020-08-27 15:00 | 44070.625 | 0 | 9.3817 | 39.95
2020-08-27 15:30 | 44070.6458 | 0 | 9.7995 | 39.95
2020-08-27 16:00 | 44070.6667 | 0 | 10.5014 | 39.95
2020-08-27 16:30 | 44070.6875 | 0 | 11.1457 | 39.95
2020-08-27 17:00 | 44070.7083 | 0 | 11.5817 | 39.95
2020-08-27 17:30 | 44070.7292 | 0 | 12.3336 | 39.95
2020-08-27 18:00 | 44070.75 | 0 | 12.7312 | 39.95
2020-08-27 18:30 | 44070.7708 | 0 | 13.0594 | 39.95
2020-08-27 19:00 | 44070.7917 | 0 | 12.9326 | 39.95
2020-08-27 19:30 | 44070.8125 | 0 | 12.6662 | 39.95
2020-08-27 20:00 | 44070.8333 | 0 | 12.4152 | 39.95
2020-08-27 20:30 | 44070.8542 | 0 | 11.8747 | 39.95
2020-08-27 21:00 | 44070.875 | 0 | 11.4693 | 39.95
2020-08-27 21:30 | 44070.8958 | 0 | 11.2349 | 39.95
2020-08-27 22:00 | 44070.9167 | 0 | 10.6518 | 39.95
2020-08-27 22:30 | 44070.9375 | 0 | 9.9982 | 39.95
2020-08-27 23:00 | 44070.9583 | 0 | 9.4899 | 39.95
2020-08-27 23:30 | 44070.9792 | 0 | 8.9992 | 39.95
2020-08-28 | 44071 | 0 | 8.4542 | 39.95
2020-08-28 00:30 | 44071.0208 | 0 | 7.8763 | 39.95
2020-08-28 01:00 | 44071.0417 | 0 | 7.7643 | 39.95
2020-08-28 01:30 | 44071.0625 | 0 | 7.7084 | 39.95
2020-08-28 02:00 | 44071.0833 | 0 | 7.5445 | 39.95
2020-08-28 02:30 | 44071.1042 | 0 | 7.3532 | 39.95
2020-08-28 03:00 | 44071.125 | 0 | 7.5301 | 39.95
2020-08-28 03:30 | 44071.1458 | 0 | 7.539 | 39.95
2020-08-28 04:00 | 44071.1667 | 0 | 7.5414 | 39.95
2020-08-28 04:30 | 44071.1875 | 0 | 7.8031 | 39.95
2020-08-28 05:00 | 44071.2083 | 0 | 8.0809 | 39.95
2020-08-28 05:30 | 44071.2292 | 0 | 8.3843 | 39.95
2020-08-28 06:00 | 44071.25 | 0 | 8.6415 | 39.95
2020-08-28 06:30 | 44071.2708 | 0 | 8.9183 | 39.95
2020-08-28 07:00 | 44071.2917 | 0 | 8.9611 | 39.95
2020-08-28 07:30 | 44071.3125 | 0 | 8.8247 | 39.95
2020-08-28 08:00 | 44071.3333 | 0 | 8.8067 | 39.95
2020-08-28 08:30 | 44071.3542 | 0 | 8.4933 | 39.95
2020-08-28 09:00 | 44071.375 | 0 | 7.9811 | 39.95
2020-08-28 09:30 | 44071.3958 | 0 | 7.8643 | 39.95
2020-08-28 10:00 | 44071.4167 | 0 | 7.4997 | 39.95
2020-08-28 10:30 | 44071.4375 | 0 | 7.8182 | 39.95
2020-08-28 11:00 | 44071.4583 | 0 | 8.4504 | 39.95
2020-08-28 11:30 | 44071.4792 | 0 | 7.1692 | 39.95
2020-08-28 12:00 | 44071.5 | 0 | 6.503 | 39.95
2020-08-28 12:30 | 44071.5208 | 0 | 6.5187 | 39.95
2020-08-28 13:00 | 44071.5417 | 0 | 7.2705 | 39.95
2020-08-28 13:30 | 44071.5625 | 0 | 6.9174 | 39.95
2020-08-28 14:00 | 44071.5833 | 0 | 6.8642 | 39.95
2020-08-28 14:30 | 44071.6042 | 0 | 7.3648 | 39.95
2020-08-28 15:00 | 44071.625 | 0 | 7.6622 | 39.95
2020-08-28 15:30 | 44071.6458 | 0 | 8.0967 | 39.95
2020-08-28 16:00 | 44071.6667 | 0 | 8.79 | 39.95
2020-08-28 16:30 | 44071.6875 | 0 | 9.4869 | 39.95
2020-08-28 17:00 | 44071.7083 | 0 | 10.0683 | 39.95
2020-08-28 17:30 | 44071.7292 | 0 | 10.7763 | 39.95
2020-08-28 18:00 | 44071.75 | 0 | 11.332 | 39.95
2020-08-28 18:30 | 44071.7708 | 0 | 11.5383 | 39.95
2020-08-28 19:00 | 44071.7917 | 0 | 11.4584 | 39.95
2020-08-28 19:30 | 44071.8125 | 0 | 11.2611 | 39.95
2020-08-28 20:00 | 44071.8333 | 0 | 11.0527 | 39.95
2020-08-28 20:30 | 44071.8542 | 0 | 10.5648 | 39.95
2020-08-28 21:00 | 44071.875 | 0 | 10.1277 | 39.95
2020-08-28 21:30 | 44071.8958 | 0 | 9.953 | 39.95
2020-08-28 22:00 | 44071.9167 | 0 | 9.6714 | 39.95
2020-08-28 22:30 | 44071.9375 | 0 | 9.0393 | 39.95
2020-08-28 23:00 | 44071.9583 | 0 | 8.5252 | 39.95
2020-08-28 23:30 | 44071.9792 | 0 | 8.0435 | 39.95
2020-08-29 | 44072 | 0 | 7.6263 | 39.95
2020-08-29 00:30 | 44072.0208 | 0 | 7.2721 | 39.95
2020-08-29 01:00 | 44072.0417 | 0 | 7.1018 | 39.95
2020-08-29 01:30 | 44072.0625 | 0 | 6.9845 | 39.95
2020-08-29 02:00 | 44072.0833 | 0 | 6.9062 | 39.95
2020-08-29 02:30 | 44072.1042 | 0 | 6.7908 | 39.95
2020-08-29 03:00 | 44072.125 | 0 | 6.7538 | 39.95
2020-08-29 03:30 | 44072.1458 | 0 | 6.7202 | 39.95
2020-08-29 04:00 | 44072.1667 | 0 | 6.657 | 39.95
2020-08-29 04:30 | 44072.1875 | 0 | 6.7037 | 39.95
2020-08-29 05:00 | 44072.2083 | 0 | 6.9046 | 39.95
2020-08-29 05:30 | 44072.2292 | 0 | 6.927 | 39.95
2020-08-29 06:00 | 44072.25 | 0 | 7.2213 | 39.95
2020-08-29 06:30 | 44072.2708 | 0 | 7.4892 | 39.95
2020-08-29 07:00 | 44072.2917 | 0 | 7.3297 | 39.95
2020-08-29 07:30 | 44072.3125 | 0 | 8.0159 | 39.95
2020-08-29 08:00 | 44072.3333 | 0 | 8.5898 | 39.95
2020-08-29 08:30 | 44072.3542 | 0 | 8.6668 | 39.95
2020-08-29 09:00 | 44072.375 | 0 | 7.7732 | 39.95
2020-08-29 09:30 | 44072.3958 | 0 | 7.6464 | 39.95
2020-08-29 10:00 | 44072.4167 | 0 | 7.863 | 39.95
2020-08-29 10:30 | 44072.4375 | 0 | 7.8192 | 39.95
2020-08-29 11:00 | 44072.4583 | 0 | 7.1146 | 39.95
2020-08-29 11:30 | 44072.4792 | 0 | 7.2104 | 39.95
2020-08-29 12:00 | 44072.5 | 0 | 5.8004 | 39.95
2020-08-29 12:30 | 44072.5208 | 0 | 5.8972 | 39.95
2020-08-29 13:00 | 44072.5417 | 0 | 5.7101 | 39.95
2020-08-29 13:30 | 44072.5625 | 0 | 5.8105 | 39.95
2020-08-29 14:00 | 44072.5833 | 0 | 6.3737 | 39.95
2020-08-29 14:30 | 44072.6042 | 0 | 7.7969 | 39.95
2020-08-29 15:00 | 44072.625 | 0 | 7.4574 | 39.95
2020-08-29 15:30 | 44072.6458 | 0 | 7.4678 | 39.95
2020-08-29 16:00 | 44072.6667 | 0 | 8.3308 | 39.95
2020-08-29 16:30 | 44072.6875 | 0 | 9.4241 | 39.95
2020-08-29 17:00 | 44072.7083 | 0 | 9.9645 | 39.95
2020-08-29 17:30 | 44072.7292 | 0 | 10.9302 | 39.95
2020-08-29 18:00 | 44072.75 | 0 | 11.6737 | 39.95
2020-08-29 18:30 | 44072.7708 | 0 | 11.9274 | 39.95
2020-08-29 19:00 | 44072.7917 | 0 | 11.5197 | 39.95
2020-08-29 19:30 | 44072.8125 | 0 | 11.2109 | 39.95
2020-08-29 20:00 | 44072.8333 | 0 | 11.1661 | 39.95
2020-08-29 20:30 | 44072.8542 | 0 | 10.5351 | 39.95
2020-08-29 21:00 | 44072.875 | 0 | 10.0296 | 39.95
2020-08-29 21:30 | 44072.8958 | 0 | 9.7145 | 39.95
2020-08-29 22:00 | 44072.9167 | 0 | 9.2592 | 39.95
2020-08-29 22:30 | 44072.9375 | 0 | 8.6103 | 39.95
2020-08-29 23:00 | 44072.9583 | 0 | 8.0728 | 39.95
2020-08-29 23:30 | 44072.9792 | 0 | 7.637 | 39.95
2020-08-30 | 44073 | 0 | 7.3321 | 39.95
2020-08-30 00:30 | 44073.0208 | 0 | 7.0652 | 39.95
2020-08-30 01:00 | 44073.0417 | 0 | 6.9212 | 39.95
2020-08-30 01:30 | 44073.0625 | 0 | 6.8485 | 39.95
2020-08-30 02:00 | 44073.0833 | 0 | 6.8786 | 39.95
2020-08-30 02:30 | 44073.1042 | 0 | 7.0072 | 39.95
2020-08-30 03:00 | 44073.125 | 0 | 6.9693 | 39.95
2020-08-30 03:30 | 44073.1458 | 0 | 7.1318 | 39.95
2020-08-30 04:00 | 44073.1667 | 0 | 7.3811 | 39.95
2020-08-30 04:30 | 44073.1875 | 0 | 7.688 | 39.95
2020-08-30 05:00 | 44073.2083 | 0 | 8.3859 | 39.95
2020-08-30 05:30 | 44073.2292 | 0 | 9.3397 | 39.95
2020-08-30 06:00 | 44073.25 | 0 | 10.3632 | 39.95
2020-08-30 06:30 | 44073.2708 | 0 | 11.4158 | 39.95
2020-08-30 07:00 | 44073.2917 | 0 | 11.7462 | 39.95
2020-08-30 07:30 | 44073.3125 | 0 | 11.1881 | 39.95
2020-08-30 08:00 | 44073.3333 | 0 | 10.7154 | 39.95
2020-08-30 08:30 | 44073.3542 | 0 | 10.0244 | 39.95
2020-08-30 09:00 | 44073.375 | 0 | 9.5406 | 39.95
2020-08-30 09:30 | 44073.3958 | 0 | 9.1488 | 39.95
2020-08-30 10:00 | 44073.4167 | 0 | 8.7916 | 39.95
2020-08-30 10:30 | 44073.4375 | 0 | 8.5722 | 39.95
2020-08-30 11:00 | 44073.4583 | 0 | 8.4417 | 39.95
2020-08-30 11:30 | 44073.4792 | 0 | 8.4119 | 39.95
2020-08-30 12:00 | 44073.5 | 0 | 8.4455 | 39.95
2020-08-30 12:30 | 44073.5208 | 0 | 8.3117 | 39.95
2020-08-30 13:00 | 44073.5417 | 0 | 8.6271 | 39.95
2020-08-30 13:30 | 44073.5625 | 0 | 8.9515 | 39.95
2020-08-30 14:00 | 44073.5833 | 0 | 9.2165 | 39.95
2020-08-30 14:30 | 44073.6042 | 0 | 9.5896 | 39.95
2020-08-30 15:00 | 44073.625 | 0 | 10.1237 | 39.95
2020-08-30 15:30 | 44073.6458 | 0 | 10.4501 | 39.95
2020-08-30 16:00 | 44073.6667 | 0 | 10.9814 | 39.95
2020-08-30 16:30 | 44073.6875 | 0 | 11.5718 | 39.95
2020-08-30 17:00 | 44073.7083 | 0 | 12.0188 | 39.95
2020-08-30 17:30 | 44073.7292 | 0 | 12.9374 | 39.95
2020-08-30 18:00 | 44073.75 | 0 | 13.5951 | 39.95
2020-08-30 18:30 | 44073.7708 | 0 | 13.8679 | 39.95
2020-08-30 19:00 | 44073.7917 | 0 | 13.6131 | 39.95
2020-08-30 19:30 | 44073.8125 | 0 | 13.122 | 39.95
2020-08-30 20:00 | 44073.8333 | 0 | 12.8054 | 39.95
2020-08-30 20:30 | 44073.8542 | 0 | 12.1552 | 39.95
2020-08-30 21:00 | 44073.875 | 0 | 11.6758 | 39.95
2020-08-30 21:30 | 44073.8958 | 0 | 11.2917 | 39.95
2020-08-30 22:00 | 44073.9167 | 0 | 10.5561 | 39.95
2020-08-30 22:30 | 44073.9375 | 0 | 9.9023 | 39.95
2020-08-30 23:00 | 44073.9583 | 0 | 9.4336 | 39.95
2020-08-30 23:30 | 44073.9792 | 0 | 8.8415 | 39.95
2020-08-31 | 44074 | 0 | 8.1896 | 39.95
2020-08-31 00:30 | 44074.0208 | 0 | 7.8186 | 39.95
2020-08-31 01:00 | 44074.0417 | 0 | 7.7439 | 39.95
2020-08-31 01:30 | 44074.0625 | 0 | 7.5316 | 39.95
2020-08-31 02:00 | 44074.0833 | 0 | 7.4592 | 39.95
2020-08-31 02:30 | 44074.1042 | 0 | 7.4591 | 39.95
2020-08-31 03:00 | 44074.125 | 0 | 7.431 | 39.95
2020-08-31 03:30 | 44074.1458 | 0 | 7.3345 | 39.95
2020-08-31 04:00 | 44074.1667 | 0 | 7.543 | 39.95
2020-08-31 04:30 | 44074.1875 | 0 | 7.9655 | 39.95
2020-08-31 05:00 | 44074.2083 | 0 | 8.7263 | 39.95
2020-08-31 05:30 | 44074.2292 | 0 | 9.4985 | 39.95
2020-08-31 06:00 | 44074.25 | 0 | 10.4729 | 39.95
2020-08-31 06:30 | 44074.2708 | 0 | 11.2358 | 39.95
2020-08-31 07:00 | 44074.2917 | 0 | 11.5889 | 39.95
2020-08-31 07:30 | 44074.3125 | 0 | 11.0986 | 39.95
2020-08-31 08:00 | 44074.3333 | 0 | 10.4363 | 39.95
2020-08-31 08:30 | 44074.3542 | 0 | 9.8367 | 39.95
2020-08-31 09:00 | 44074.375 | 0 | 9.3705 | 39.95
2020-08-31 09:30 | 44074.3958 | 0 | 9.0797 | 39.95
2020-08-31 10:00 | 44074.4167 | 0 | 8.5937 | 39.95
2020-08-31 10:30 | 44074.4375 | 0 | 8.4921 | 39.95
2020-08-31 11:00 | 44074.4583 | 0 | 8.4844 | 39.95
2020-08-31 11:30 | 44074.4792 | 0 | 8.5144 | 39.95
2020-08-31 12:00 | 44074.5 | 0 | 8.6709 | 39.95
2020-08-31 12:30 | 44074.5208 | 0 | 9.1972 | 39.95
2020-08-31 13:00 | 44074.5417 | 0 | 9.6374 | 39.95
2020-08-31 13:30 | 44074.5625 | 0 | 10.3242 | 39.95
2020-08-31 14:00 | 44074.5833 | 0 | 10.4485 | 39.95
2020-08-31 14:30 | 44074.6042 | 0 | 10.2903 | 39.95
2020-08-31 15:00 | 44074.625 | 0 | 10.0883 | 39.95
2020-08-31 15:30 | 44074.6458 | 0 | 10.623 | 39.95
2020-08-31 16:00 | 44074.6667 | 0 | 11.1527 | 39.95
2020-08-31 16:30 | 44074.6875 | 0 | 11.7738 | 39.95
2020-08-31 17:00 | 44074.7083 | 0 | 12.1386 | 39.95
2020-08-31 17:30 | 44074.7292 | 0 | 13.1146 | 39.95
2020-08-31 18:00 | 44074.75 | 0 | 13.5991 | 39.95
2020-08-31 18:30 | 44074.7708 | 0 | 13.7658 | 39.95
2020-08-31 19:00 | 44074.7917 | 0 | 13.3826 | 39.95
2020-08-31 19:30 | 44074.8125 | 0 | 13.316 | 39.95
2020-08-31 20:00 | 44074.8333 | 0 | 13.0626 | 39.95
2020-08-31 20:30 | 44074.8542 | 0 | 12.5579 | 39.95
2020-08-31 21:00 | 44074.875 | 0 | 11.7466 | 39.95
2020-08-31 21:30 | 44074.8958 | 0 | 11.4137 | 39.95
2020-08-31 22:00 | 44074.9167 | 0 | 10.8168 | 39.95
2020-08-31 22:30 | 44074.9375 | 0 | 10.0085 | 39.95
2020-08-31 23:00 | 44074.9583 | 0 | 9.3808 | 39.95
2020-08-31 23:30 | 44074.9792 | 0 | 8.7893 | 39.95
2020-09-01 | 44075 | 0 | 8.1958 | 39.95
2020-09-01 00:30 | 44075.0208 | 0 | 7.9137 | 39.95
2020-09-01 01:00 | 44075.0417 | 0 | 7.7029 | 39.95
2020-09-01 01:30 | 44075.0625 | 0 | 7.6768 | 39.95
2020-09-01 02:00 | 44075.0833 | 0 | 7.6041 | 39.95
2020-09-01 02:30 | 44075.1042 | 0 | 7.4273 | 39.95
2020-09-01 03:00 | 44075.125 | 0 | 7.4702 | 39.95
2020-09-01 03:30 | 44075.1458 | 0 | 7.4649 | 39.95
2020-09-01 04:00 | 44075.1667 | 0 | 7.7705 | 39.95
2020-09-01 04:30 | 44075.1875 | 0 | 8.2173 | 39.95
2020-09-01 05:00 | 44075.2083 | 0 | 8.8989 | 39.95
2020-09-01 05:30 | 44075.2292 | 0 | 9.7231 | 39.95
2020-09-01 06:00 | 44075.25 | 0 | 10.6181 | 39.95
2020-09-01 06:30 | 44075.2708 | 0 | 11.1568 | 39.95
2020-09-01 07:00 | 44075.2917 | 0 | 11.4735 | 39.95
2020-09-01 07:30 | 44075.3125 | 0 | 10.9324 | 39.95
2020-09-01 08:00 | 44075.3333 | 0 | 10.7367 | 39.95
2020-09-01 08:30 | 44075.3542 | 0 | 10.0298 | 39.95
2020-09-01 09:00 | 44075.375 | 0 | 10.5228 | 39.95
2020-09-01 09:30 | 44075.3958 | 0 | 11.5289 | 39.95
2020-09-01 10:00 | 44075.4167 | 0 | 10.6605 | 39.95
2020-09-01 10:30 | 44075.4375 | 0 | 9.5403 | 39.95
2020-09-01 11:00 | 44075.4583 | 0 | 10.5258 | 39.95
2020-09-01 11:30 | 44075.4792 | 0 | 10.1088 | 39.95
2020-09-01 12:00 | 44075.5 | 0 | 10.4786 | 39.95
2020-09-01 12:30 | 44075.5208 | 0 | 9.7506 | 39.95
2020-09-01 13:00 | 44075.5417 | 0 | 9.446 | 39.95
2020-09-01 13:30 | 44075.5625 | 0 | 9.7349 | 39.95
2020-09-01 14:00 | 44075.5833 | 0 | 9.5225 | 39.95
2020-09-01 14:30 | 44075.6042 | 0 | 9.6989 | 39.95
2020-09-01 15:00 | 44075.625 | 0 | 10.1781 | 39.95
2020-09-01 15:30 | 44075.6458 | 0 | 11.0045 | 39.95
2020-09-01 16:00 | 44075.6667 | 0 | 11.4254 | 39.95
2020-09-01 16:30 | 44075.6875 | 0 | 12.0885 | 39.95
2020-09-01 17:00 | 44075.7083 | 0 | 12.5621 | 39.95
2020-09-01 17:30 | 44075.7292 | 0 | 13.118 | 39.95
2020-09-01 18:00 | 44075.75 | 0 | 13.6374 | 39.95
2020-09-01 18:30 | 44075.7708 | 0 | 14.0504 | 39.95
2020-09-01 19:00 | 44075.7917 | 0 | 13.8154 | 39.95
2020-09-01 19:30 | 44075.8125 | 0 | 13.2465 | 39.95
2020-09-01 20:00 | 44075.8333 | 0 | 13.0181 | 39.95
2020-09-01 20:30 | 44075.8542 | 0 | 12.5208 | 39.95
2020-09-01 21:00 | 44075.875 | 0 | 11.9579 | 39.95
2020-09-01 21:30 | 44075.8958 | 0 | 11.5047 | 39.95
2020-09-01 22:00 | 44075.9167 | 0 | 10.8967 | 39.95
2020-09-01 22:30 | 44075.9375 | 0 | 10.0249 | 39.95
2020-09-01 23:00 | 44075.9583 | 0 | 9.455 | 39.95
2020-09-01 23:30 | 44075.9792 | 0 | 8.9527 | 39.95
2020-09-02 | 44076 | 0 | 8.4059 | 39.95
2020-09-02 00:30 | 44076.0208 | 0 | 7.9328 | 39.95
2020-09-02 01:00 | 44076.0417 | 0 | 7.8274 | 39.95
2020-09-02 01:30 | 44076.0625 | 0 | 7.6934 | 39.95
2020-09-02 02:00 | 44076.0833 | 0 | 7.5949 | 39.95
2020-09-02 02:30 | 44076.1042 | 0 | 7.513 | 39.95
2020-09-02 03:00 | 44076.125 | 0 | 7.489 | 39.95
2020-09-02 03:30 | 44076.1458 | 0 | 7.502 | 39.95
2020-09-02 04:00 | 44076.1667 | 0 | 7.7349 | 39.95
2020-09-02 04:30 | 44076.1875 | 0 | 8.2026 | 39.95
2020-09-02 05:00 | 44076.2083 | 0 | 9.0276 | 39.95
2020-09-02 05:30 | 44076.2292 | 0 | 9.6308 | 39.95
2020-09-02 06:00 | 44076.25 | 0 | 10.4513 | 39.95
2020-09-02 06:30 | 44076.2708 | 0 | 11.3151 | 39.95
2020-09-02 07:00 | 44076.2917 | 0 | 11.8572 | 39.95
2020-09-02 07:30 | 44076.3125 | 0 | 11.7919 | 39.95
2020-09-02 08:00 | 44076.3333 | 0 | 11.496 | 39.95
2020-09-02 08:30 | 44076.3542 | 0 | 11.5371 | 39.95
2020-09-02 09:00 | 44076.375 | 0 | 10.9606 | 39.95
2020-09-02 09:30 | 44076.3958 | 0 | 10.3149 | 39.95
2020-09-02 10:00 | 44076.4167 | 0 | 10.372 | 39.95
2020-09-02 10:30 | 44076.4375 | 0 | 11.2855 | 39.95
2020-09-02 11:00 | 44076.4583 | 0 | 10.3332 | 39.95
2020-09-02 11:30 | 44076.4792 | 0 | 9.2512 | 39.95
2020-09-02 12:00 | 44076.5 | 0 | 9.0488 | 39.95
2020-09-02 12:30 | 44076.5208 | 0 | 9.2217 | 39.95
2020-09-02 13:00 | 44076.5417 | 0 | 9.0227 | 39.95
2020-09-02 13:30 | 44076.5625 | 0 | 9.5818 | 39.95
2020-09-02 14:00 | 44076.5833 | 0 | 9.8622 | 39.95
2020-09-02 14:30 | 44076.6042 | 0 | 10.3932 | 39.95
2020-09-02 15:00 | 44076.625 | 0 | 10.9314 | 39.95
2020-09-02 15:30 | 44076.6458 | 0 | 11.032 | 39.95
2020-09-02 16:00 | 44076.6667 | 0 | 11.6591 | 39.95
2020-09-02 16:30 | 44076.6875 | 0 | 12.0676 | 39.95
2020-09-02 17:00 | 44076.7083 | 0 | 12.4494 | 39.95
2020-09-02 17:30 | 44076.7292 | 0 | 12.8286 | 39.95
2020-09-02 18:00 | 44076.75 | 0 | 13.2767 | 39.95
2020-09-02 18:30 | 44076.7708 | 0 | 13.443 | 39.95
2020-09-02 19:00 | 44076.7917 | 0 | 13.0055 | 39.95
2020-09-02 19:30 | 44076.8125 | 0 | 12.9511 | 39.95
2020-09-02 20:00 | 44076.8333 | 0 | 12.8897 | 39.95
2020-09-02 20:30 | 44076.8542 | 0 | 12.1626 | 39.95
2020-09-02 21:00 | 44076.875 | 0 | 11.9286 | 39.95
2020-09-02 21:30 | 44076.8958 | 0 | 11.5475 | 39.95
2020-09-02 22:00 | 44076.9167 | 0 | 10.9677 | 39.95
2020-09-02 22:30 | 44076.9375 | 0 | 10.1313 | 39.95
2020-09-02 23:00 | 44076.9583 | 0 | 9.508 | 39.95
2020-09-02 23:30 | 44076.9792 | 0 | 9.0144 | 39.95
2020-09-03 | 44077 | 0 | 8.3739 | 39.95
2020-09-03 00:30 | 44077.0208 | 0 | 7.8595 | 39.95
2020-09-03 01:00 | 44077.0417 | 0 | 7.8145 | 39.95
2020-09-03 01:30 | 44077.0625 | 0 | 7.6934 | 39.95
2020-09-03 02:00 | 44077.0833 | 0 | 7.5799 | 39.95
2020-09-03 02:30 | 44077.1042 | 0 | 7.5394 | 39.95
2020-09-03 03:00 | 44077.125 | 0 | 7.5408 | 39.95
2020-09-03 03:30 | 44077.1458 | 0 | 7.5468 | 39.95
2020-09-03 04:00 | 44077.1667 | 0 | 7.7179 | 39.95
2020-09-03 04:30 | 44077.1875 | 0 | 8.2832 | 39.95
2020-09-03 05:00 | 44077.2083 | 0 | 8.8822 | 39.95
2020-09-03 05:30 | 44077.2292 | 0 | 9.5964 | 39.95
2020-09-03 06:00 | 44077.25 | 0 | 10.3143 | 39.95
2020-09-03 06:30 | 44077.2708 | 0 | 11.0018 | 39.95
2020-09-03 07:00 | 44077.2917 | 0 | 11.4743 | 39.95
2020-09-03 07:30 | 44077.3125 | 0 | 11.8669 | 39.95
2020-09-03 08:00 | 44077.3333 | 0 | 11.1731 | 39.95
2020-09-03 08:30 | 44077.3542 | 0 | 10.8434 | 39.95
2020-09-03 09:00 | 44077.375 | 0 | 11.1403 | 39.95
2020-09-03 09:30 | 44077.3958 | 0 | 11.139 | 39.95
2020-09-03 10:00 | 44077.4167 | 0 | 10.0474 | 39.95
2020-09-03 10:30 | 44077.4375 | 0 | 9.2485 | 39.95
2020-09-03 11:00 | 44077.4583 | 0 | 9.1034 | 39.95
2020-09-03 11:30 | 44077.4792 | 0 | 9.1389 | 39.95
2020-09-03 12:00 | 44077.5 | 0 | 8.984 | 39.95
2020-09-03 12:30 | 44077.5208 | 0 | 8.9875 | 39.95
2020-09-03 13:00 | 44077.5417 | 0 | 8.8817 | 39.95
2020-09-03 13:30 | 44077.5625 | 0 | 9.0377 | 39.95
2020-09-03 14:00 | 44077.5833 | 0 | 10.0969 | 39.95
2020-09-03 14:30 | 44077.6042 | 0 | 10.4771 | 39.95
2020-09-03 15:00 | 44077.625 | 0 | 10.5296 | 39.95
2020-09-03 15:30 | 44077.6458 | 0 | 10.5689 | 39.95
2020-09-03 16:00 | 44077.6667 | 0 | 11.0803 | 39.95
2020-09-03 16:30 | 44077.6875 | 0 | 11.8126 | 39.95
2020-09-03 17:00 | 44077.7083 | 0 | 12.0058 | 39.95
2020-09-03 17:30 | 44077.7292 | 0 | 12.4969 | 39.95
2020-09-03 18:00 | 44077.75 | 0 | 12.8892 | 39.95
2020-09-03 18:30 | 44077.7708 | 0 | 12.9602 | 39.95
2020-09-03 19:00 | 44077.7917 | 0 | 12.7657 | 39.95
2020-09-03 19:30 | 44077.8125 | 0 | 12.5656 | 39.95
2020-09-03 20:00 | 44077.8333 | 0 | 12.3417 | 39.95
2020-09-03 20:30 | 44077.8542 | 0 | 11.7389 | 39.95
2020-09-03 21:00 | 44077.875 | 0 | 11.4023 | 39.95
2020-09-03 21:30 | 44077.8958 | 0 | 11.1129 | 39.95
2020-09-03 22:00 | 44077.9167 | 0 | 10.5603 | 39.95
2020-09-03 22:30 | 44077.9375 | 0 | 9.8658 | 39.95
2020-09-03 23:00 | 44077.9583 | 0 | 9.3422 | 39.95
2020-09-03 23:30 | 44077.9792 | 0 | 9.025 | 39.95
2020-09-04 | 44078 | 0 | 8.4572 | 39.95
2020-09-04 00:30 | 44078.0208 | 0 | 8.0165 | 39.95
2020-09-04 01:00 | 44078.0417 | 0 | 7.7355 | 39.95
2020-09-04 01:30 | 44078.0625 | 0 | 7.6918 | 39.95
2020-09-04 02:00 | 44078.0833 | 0 | 7.5771 | 39.95
2020-09-04 02:30 | 44078.1042 | 0 | 7.4698 | 39.95
2020-09-04 03:00 | 44078.125 | 0 | 7.4142 | 39.95
2020-09-04 03:30 | 44078.1458 | 0 | 7.356 | 39.95
2020-09-04 04:00 | 44078.1667 | 0 | 7.473 | 39.95
2020-09-04 04:30 | 44078.1875 | 0 | 7.5305 | 39.95
2020-09-04 05:00 | 44078.2083 | 0 | 7.8136 | 39.95
2020-09-04 05:30 | 44078.2292 | 0 | 7.9923 | 39.95
2020-09-04 06:00 | 44078.25 | 0 | 8.2906 | 39.95
2020-09-04 06:30 | 44078.2708 | 0 | 8.3738 | 39.95
2020-09-04 07:00 | 44078.2917 | 0 | 8.449 | 39.95
2020-09-04 07:30 | 44078.3125 | 0 | 8.487 | 39.95
2020-09-04 08:00 | 44078.3333 | 0 | 8.4071 | 39.95
2020-09-04 08:30 | 44078.3542 | 0 | 8.1947 | 39.95
2020-09-04 09:00 | 44078.375 | 0 | 7.8727 | 39.95
2020-09-04 09:30 | 44078.3958 | 0 | 7.3444 | 39.95
2020-09-04 10:00 | 44078.4167 | 0 | 7.0925 | 39.95
2020-09-04 10:30 | 44078.4375 | 0 | 6.9994 | 39.95
2020-09-04 11:00 | 44078.4583 | 0 | 6.7801 | 39.95
2020-09-04 11:30 | 44078.4792 | 0 | 6.6477 | 39.95
2020-09-04 12:00 | 44078.5 | 0 | 6.5599 | 39.95
2020-09-04 12:30 | 44078.5208 | 0 | 6.6161 | 39.95
2020-09-04 13:00 | 44078.5417 | 0 | 6.6058 | 39.95
2020-09-04 13:30 | 44078.5625 | 0 | 7.2421 | 39.95
2020-09-04 14:00 | 44078.5833 | 0 | 7.3568 | 39.95
2020-09-04 14:30 | 44078.6042 | 0 | 8.0526 | 39.95
2020-09-04 15:00 | 44078.625 | 0 | 8.1551 | 39.95
2020-09-04 15:30 | 44078.6458 | 0 | 8.7621 | 39.95
2020-09-04 16:00 | 44078.6667 | 0 | 9.3149 | 39.95
2020-09-04 16:30 | 44078.6875 | 0 | 9.878 | 39.95
2020-09-04 17:00 | 44078.7083 | 0 | 10.2725 | 39.95
2020-09-04 17:30 | 44078.7292 | 0 | 10.8778 | 39.95
2020-09-04 18:00 | 44078.75 | 0 | 11.293 | 39.95
2020-09-04 18:30 | 44078.7708 | 0 | 11.3838 | 39.95
2020-09-04 19:00 | 44078.7917 | 0 | 11.0512 | 39.95
2020-09-04 19:30 | 44078.8125 | 0 | 10.7949 | 39.95
2020-09-04 20:00 | 44078.8333 | 0 | 10.5801 | 39.95
2020-09-04 20:30 | 44078.8542 | 0 | 10.222 | 39.95
2020-09-04 21:00 | 44078.875 | 0 | 9.7906 | 39.95
2020-09-04 21:30 | 44078.8958 | 0 | 9.6156 | 39.95
2020-09-04 22:00 | 44078.9167 | 0 | 9.2819 | 39.95
2020-09-04 22:30 | 44078.9375 | 0 | 8.7631 | 39.95
2020-09-04 23:00 | 44078.9583 | 0 | 8.2987 | 39.95
2020-09-04 23:30 | 44078.9792 | 0 | 7.8724 | 39.95
2020-09-05 | 44079 | 0 | 7.5364 | 39.95
2020-09-05 00:30 | 44079.0208 | 0 | 7.196 | 39.95
2020-09-05 01:00 | 44079.0417 | 0 | 7.0251 | 39.95
2020-09-05 01:30 | 44079.0625 | 0 | 7.0008 | 39.95
2020-09-05 02:00 | 44079.0833 | 0 | 6.9262 | 39.95
2020-09-05 02:30 | 44079.1042 | 0 | 6.8431 | 39.95
2020-09-05 03:00 | 44079.125 | 0 | 6.7063 | 39.95
2020-09-05 03:30 | 44079.1458 | 0 | 6.6719 | 39.95
2020-09-05 04:00 | 44079.1667 | 0 | 6.5452 | 39.95
2020-09-05 04:30 | 44079.1875 | 0 | 6.6882 | 39.95
2020-09-05 05:00 | 44079.2083 | 0 | 6.6944 | 39.95
2020-09-05 05:30 | 44079.2292 | 0 | 6.8691 | 39.95
2020-09-05 06:00 | 44079.25 | 0 | 7.1144 | 39.95
2020-09-05 06:30 | 44079.2708 | 0 | 7.2051 | 39.95
2020-09-05 07:00 | 44079.2917 | 0 | 7.5204 | 39.95
2020-09-05 07:30 | 44079.3125 | 0 | 7.3918 | 39.95
2020-09-05 08:00 | 44079.3333 | 0 | 7.7319 | 39.95
2020-09-05 08:30 | 44079.3542 | 0 | 7.4005 | 39.95
2020-09-05 09:00 | 44079.375 | 0 | 7.1371 | 39.95
2020-09-05 09:30 | 44079.3958 | 0 | 7.5643 | 39.95
2020-09-05 10:00 | 44079.4167 | 0 | 8.7306 | 39.95
2020-09-05 10:30 | 44079.4375 | 0 | 7.8641 | 39.95
2020-09-05 11:00 | 44079.4583 | 0 | 7.3794 | 39.95
2020-09-05 11:30 | 44079.4792 | 0 | 9.8004 | 39.95
2020-09-05 12:00 | 44079.5 | 0 | 9.6433 | 39.95
2020-09-05 12:30 | 44079.5208 | 0 | 9.2024 | 39.95
2020-09-05 13:00 | 44079.5417 | 0 | 8.8342 | 39.95
2020-09-05 13:30 | 44079.5625 | 0 | 8.6772 | 39.95
2020-09-05 14:00 | 44079.5833 | 0 | 8.974 | 39.95
2020-09-05 14:30 | 44079.6042 | 0 | 9.1661 | 39.95
2020-09-05 15:00 | 44079.625 | 0 | 8.9229 | 39.95
2020-09-05 15:30 | 44079.6458 | 0 | 8.9791 | 39.95
2020-09-05 16:00 | 44079.6667 | 0 | 9.1205 | 39.95
2020-09-05 16:30 | 44079.6875 | 0 | 9.7673 | 39.95
2020-09-05 17:00 | 44079.7083 | 0 | 10.0871 | 39.95
2020-09-05 17:30 | 44079.7292 | 0 | 10.8477 | 39.95
2020-09-05 18:00 | 44079.75 | 0 | 11.2228 | 39.95
2020-09-05 18:30 | 44079.7708 | 0 | 11.6011 | 39.95
2020-09-05 19:00 | 44079.7917 | 0 | 11.2148 | 39.95
2020-09-05 19:30 | 44079.8125 | 0 | 10.7888 | 39.95
2020-09-05 20:00 | 44079.8333 | 0 | 10.6683 | 39.95
2020-09-05 20:30 | 44079.8542 | 0 | 10.1875 | 39.95
2020-09-05 21:00 | 44079.875 | 0 | 9.7483 | 39.95
2020-09-05 21:30 | 44079.8958 | 0 | 9.4903 | 39.95
2020-09-05 22:00 | 44079.9167 | 0 | 9.0143 | 39.95
2020-09-05 22:30 | 44079.9375 | 0 | 8.4241 | 39.95
2020-09-05 23:00 | 44079.9583 | 0 | 7.9807 | 39.95
2020-09-05 23:30 | 44079.9792 | 0 | 7.549 | 39.95
2020-09-06 | 44080 | 0 | 7.2848 | 39.95
2020-09-06 00:30 | 44080.0208 | 0 | 7.0369 | 39.95
2020-09-06 01:00 | 44080.0417 | 0 | 6.8622 | 39.95
2020-09-06 01:30 | 44080.0625 | 0 | 6.9008 | 39.95
2020-09-06 02:00 | 44080.0833 | 0 | 6.8531 | 39.95
2020-09-06 02:30 | 44080.1042 | 0 | 6.9357 | 39.95
2020-09-06 03:00 | 44080.125 | 0 | 6.8582 | 39.95
2020-09-06 03:30 | 44080.1458 | 0 | 6.9285 | 39.95
2020-09-06 04:00 | 44080.1667 | 0 | 7.2706 | 39.95
2020-09-06 04:30 | 44080.1875 | 0 | 7.6894 | 39.95
2020-09-06 05:00 | 44080.2083 | 0 | 8.4105 | 39.95
2020-09-06 05:30 | 44080.2292 | 0 | 9.0369 | 39.95
2020-09-06 06:00 | 44080.25 | 0 | 9.7153 | 39.95
2020-09-06 06:30 | 44080.2708 | 0 | 10.4196 | 39.95
2020-09-06 07:00 | 44080.2917 | 0 | 10.7151 | 39.95
2020-09-06 07:30 | 44080.3125 | 0 | 10.3648 | 39.95
2020-09-06 08:00 | 44080.3333 | 0 | 10.0487 | 39.95
2020-09-06 08:30 | 44080.3542 | 0 | 9.6937 | 39.95
2020-09-06 09:00 | 44080.375 | 0 | 9.1013 | 39.95
2020-09-06 09:30 | 44080.3958 | 0 | 8.7641 | 39.95
2020-09-06 10:00 | 44080.4167 | 0 | 8.7491 | 39.95
2020-09-06 10:30 | 44080.4375 | 0 | 8.747 | 39.95
2020-09-06 11:00 | 44080.4583 | 0 | 9.3687 | 39.95
2020-09-06 11:30 | 44080.4792 | 0 | 9.5319 | 39.95
2020-09-06 12:00 | 44080.5 | 0 | 9.5309 | 39.95
2020-09-06 12:30 | 44080.5208 | 0 | 8.9595 | 39.95
2020-09-06 13:00 | 44080.5417 | 0 | 9.3085 | 39.95
2020-09-06 13:30 | 44080.5625 | 0 | 9.6241 | 39.95
2020-09-06 14:00 | 44080.5833 | 0 | 10.7975 | 39.95
2020-09-06 14:30 | 44080.6042 | 0 | 11.1386 | 39.95
2020-09-06 15:00 | 44080.625 | 0 | 11.3333 | 39.95
2020-09-06 15:30 | 44080.6458 | 0 | 11.3275 | 39.95
2020-09-06 16:00 | 44080.6667 | 0 | 11.4492 | 39.95
2020-09-06 16:30 | 44080.6875 | 0 | 11.839 | 39.95
2020-09-06 17:00 | 44080.7083 | 0 | 12.3795 | 39.95
2020-09-06 17:30 | 44080.7292 | 0 | 13.0662 | 39.95
2020-09-06 18:00 | 44080.75 | 0 | 13.5678 | 39.95
2020-09-06 18:30 | 44080.7708 | 0 | 13.6185 | 39.95
2020-09-06 19:00 | 44080.7917 | 0 | 13.3129 | 39.95
2020-09-06 19:30 | 44080.8125 | 0 | 13.0102 | 39.95
2020-09-06 20:00 | 44080.8333 | 0 | 12.6488 | 39.95
2020-09-06 20:30 | 44080.8542 | 0 | 12.0026 | 39.95
2020-09-06 21:00 | 44080.875 | 0 | 11.5009 | 39.95
2020-09-06 21:30 | 44080.8958 | 0 | 11.0924 | 39.95
2020-09-06 22:00 | 44080.9167 | 0 | 10.5642 | 39.95
2020-09-06 22:30 | 44080.9375 | 0 | 9.8226 | 39.95
2020-09-06 23:00 | 44080.9583 | 0 | 9.1231 | 39.95
2020-09-06 23:30 | 44080.9792 | 0 | 8.6644 | 39.95
2020-09-07 | 44081 | 0 | 8.0567 | 39.95
2020-09-07 00:30 | 44081.0208 | 0 | 7.7704 | 39.95
2020-09-07 01:00 | 44081.0417 | 0 | 7.558 | 39.95
2020-09-07 01:30 | 44081.0625 | 0 | 7.5368 | 39.95
2020-09-07 02:00 | 44081.0833 | 0 | 7.4463 | 39.95
2020-09-07 02:30 | 44081.1042 | 0 | 7.3984 | 39.95
2020-09-07 03:00 | 44081.125 | 0 | 7.3133 | 39.95
2020-09-07 03:30 | 44081.1458 | 0 | 7.3753 | 39.95
2020-09-07 04:00 | 44081.1667 | 0 | 7.5179 | 39.95
2020-09-07 04:30 | 44081.1875 | 0 | 8.1055 | 39.95
2020-09-07 05:00 | 44081.2083 | 0 | 8.7563 | 39.95
2020-09-07 05:30 | 44081.2292 | 0 | 9.4256 | 39.95
2020-09-07 06:00 | 44081.25 | 0 | 10.3295 | 39.95
2020-09-07 06:30 | 44081.2708 | 0 | 11.063 | 39.95
2020-09-07 07:00 | 44081.2917 | 0 | 11.779 | 39.95
2020-09-07 07:30 | 44081.3125 | 0 | 11.4824 | 39.95
2020-09-07 08:00 | 44081.3333 | 0 | 10.145 | 39.95
2020-09-07 08:30 | 44081.3542 | 0 | 9.7635 | 39.95
2020-09-07 09:00 | 44081.375 | 0 | 10.2865 | 39.95
2020-09-07 09:30 | 44081.3958 | 0 | 10.0021 | 39.95
2020-09-07 10:00 | 44081.4167 | 0 | 9.5292 | 39.95
2020-09-07 10:30 | 44081.4375 | 0 | 9.6027 | 39.95
2020-09-07 11:00 | 44081.4583 | 0 | 9.8373 | 39.95
2020-09-07 11:30 | 44081.4792 | 0 | 9.5945 | 39.95
2020-09-07 12:00 | 44081.5 | 0 | 10.2787 | 39.95
2020-09-07 12:30 | 44081.5208 | 0 | 9.9072 | 39.95
2020-09-07 13:00 | 44081.5417 | 0 | 10.1482 | 39.95
2020-09-07 13:30 | 44081.5625 | 0 | 9.9382 | 39.95
2020-09-07 14:00 | 44081.5833 | 0 | 9.8237 | 39.95
2020-09-07 14:30 | 44081.6042 | 0 | 10.1786 | 39.95
2020-09-07 15:00 | 44081.625 | 0 | 9.6777 | 39.95
2020-09-07 15:30 | 44081.6458 | 0 | 10.2265 | 39.95
2020-09-07 16:00 | 44081.6667 | 0 | 10.9582 | 39.95
2020-09-07 16:30 | 44081.6875 | 0 | 11.3868 | 39.95
2020-09-07 17:00 | 44081.7083 | 0 | 11.8228 | 39.95
2020-09-07 17:30 | 44081.7292 | 0 | 12.5465 | 39.95
2020-09-07 18:00 | 44081.75 | 0 | 13.2709 | 39.95
2020-09-07 18:30 | 44081.7708 | 0 | 13.5262 | 39.95
2020-09-07 19:00 | 44081.7917 | 0 | 13.3757 | 39.95
2020-09-07 19:30 | 44081.8125 | 0 | 13.103 | 39.95
2020-09-07 20:00 | 44081.8333 | 0 | 12.7966 | 39.95
2020-09-07 20:30 | 44081.8542 | 0 | 12.2832 | 39.95
2020-09-07 21:00 | 44081.875 | 0 | 11.6772 | 39.95
2020-09-07 21:30 | 44081.8958 | 0 | 11.433 | 39.95
2020-09-07 22:00 | 44081.9167 | 0 | 10.7677 | 39.95
2020-09-07 22:30 | 44081.9375 | 0 | 9.9332 | 39.95
2020-09-07 23:00 | 44081.9583 | 0 | 9.2764 | 39.95
2020-09-07 23:30 | 44081.9792 | 0 | 8.9107 | 39.95
2020-09-08 | 44082 | 0 | 8.9107 | 39.95
2020-09-08 00:30 | 44082.0208 | 0 | 8.3269 | 39.95
2020-09-08 01:00 | 44082.0417 | 0 | 7.5963 | 39.95
2020-09-08 01:30 | 44082.0625 | 0 | 7.5396 | 39.95
2020-09-08 02:00 | 44082.0833 | 0 | 7.5007 | 39.95
2020-09-08 02:30 | 44082.1042 | 0 | 7.3321 | 39.95
2020-09-08 03:00 | 44082.125 | 0 | 7.2453 | 39.95
2020-09-08 03:30 | 44082.1458 | 0 | 7.3702 | 39.95
2020-09-08 04:00 | 44082.1667 | 0 | 7.6349 | 39.95
2020-09-08 04:30 | 44082.1875 | 0 | 7.996 | 39.95
2020-09-08 05:00 | 44082.2083 | 0 | 8.6422 | 39.95
2020-09-08 05:30 | 44082.2292 | 0 | 9.1845 | 39.95
2020-09-08 06:00 | 44082.25 | 0 | 10.1591 | 39.95
2020-09-08 06:30 | 44082.2708 | 0 | 10.914 | 39.95
2020-09-08 07:00 | 44082.2917 | 0 | 11.1308 | 39.95
2020-09-08 07:30 | 44082.3125 | 0 | 10.5232 | 39.95
2020-09-08 08:00 | 44082.3333 | 0 | 10.3079 | 39.95
2020-09-08 08:30 | 44082.3542 | 0 | 9.6003 | 39.95
2020-09-08 09:00 | 44082.375 | 0 | 9.8373 | 39.95
2020-09-08 09:30 | 44082.3958 | 0 | 9.3436 | 39.95
2020-09-08 10:00 | 44082.4167 | 0 | 9.4239 | 39.95
2020-09-08 10:30 | 44082.4375 | 0 | 9.0298 | 39.95
2020-09-08 11:00 | 44082.4583 | 0 | 9.0473 | 39.95
2020-09-08 11:30 | 44082.4792 | 0 | 9.0843 | 39.95
2020-09-08 12:00 | 44082.5 | 0 | 9.4343 | 39.95
2020-09-08 12:30 | 44082.5208 | 0 | 9.1623 | 39.95
2020-09-08 13:00 | 44082.5417 | 0 | 9.0365 | 39.95
2020-09-08 13:30 | 44082.5625 | 0 | 9.0535 | 39.95
2020-09-08 14:00 | 44082.5833 | 0 | 9.1471 | 39.95
2020-09-08 14:30 | 44082.6042 | 0 | 9.7285 | 39.95
2020-09-08 15:00 | 44082.625 | 0 | 9.5884 | 39.95
2020-09-08 15:30 | 44082.6458 | 0 | 10.1544 | 39.95
2020-09-08 16:00 | 44082.6667 | 0 | 10.7191 | 39.95
2020-09-08 16:30 | 44082.6875 | 0 | 11.3514 | 39.95
2020-09-08 17:00 | 44082.7083 | 0 | 11.9856 | 39.95
2020-09-08 17:30 | 44082.7292 | 0 | 12.6275 | 39.95
2020-09-08 18:00 | 44082.75 | 0 | 13.2973 | 39.95
2020-09-08 18:30 | 44082.7708 | 0 | 13.6188 | 39.95
2020-09-08 19:00 | 44082.7917 | 0 | 13.1631 | 39.95
2020-09-08 19:30 | 44082.8125 | 0 | 12.8031 | 39.95
2020-09-08 20:00 | 44082.8333 | 0 | 12.7527 | 39.95
2020-09-08 20:30 | 44082.8542 | 0 | 12.073 | 39.95
2020-09-08 21:00 | 44082.875 | 0 | 11.454 | 39.95
2020-09-08 21:30 | 44082.8958 | 0 | 11.2329 | 39.95
2020-09-08 22:00 | 44082.9167 | 0 | 10.6734 | 39.95
2020-09-08 22:30 | 44082.9375 | 0 | 9.8751 | 39.95
2020-09-08 23:00 | 44082.9583 | 0 | 9.2112 | 39.95
2020-09-08 23:30 | 44082.9792 | 0 | 8.6352 | 39.95
2020-09-09 | 44083 | 0 | 8.1663 | 39.95
2020-09-09 00:30 | 44083.0208 | 0 | 7.8367 | 39.95
2020-09-09 01:00 | 44083.0417 | 0 | 7.6797 | 39.95
2020-09-09 01:30 | 44083.0625 | 0 | 7.5492 | 39.95
2020-09-09 02:00 | 44083.0833 | 0 | 7.4986 | 39.95
2020-09-09 02:30 | 44083.1042 | 0 | 7.3717 | 39.95
2020-09-09 03:00 | 44083.125 | 0 | 7.3388 | 39.95
2020-09-09 03:30 | 44083.1458 | 0 | 7.3646 | 39.95
2020-09-09 04:00 | 44083.1667 | 0 | 7.7914 | 39.95
2020-09-09 04:30 | 44083.1875 | 0 | 8.1547 | 39.95
2020-09-09 05:00 | 44083.2083 | 0 | 8.8203 | 39.95
2020-09-09 05:30 | 44083.2292 | 0 | 9.3878 | 39.95
2020-09-09 06:00 | 44083.25 | 0 | 10.3756 | 39.95
2020-09-09 06:30 | 44083.2708 | 0 | 11.242 | 39.95
2020-09-09 07:00 | 44083.2917 | 0 | 11.9267 | 39.95
2020-09-09 07:30 | 44083.3125 | 0 | 11.2204 | 39.95
2020-09-09 08:00 | 44083.3333 | 0 | 11.4363 | 39.95
2020-09-09 08:30 | 44083.3542 | 0 | 11.2926 | 39.95
2020-09-09 09:00 | 44083.375 | 0 | 10.6773 | 39.95
2020-09-09 09:30 | 44083.3958 | 0 | 10.9539 | 39.95
2020-09-09 10:00 | 44083.4167 | 0 | 11.7667 | 39.95
2020-09-09 10:30 | 44083.4375 | 0 | 11.4211 | 39.95
2020-09-09 11:00 | 44083.4583 | 0 | 10.9988 | 39.95
2020-09-09 11:30 | 44083.4792 | 0 | 11.2769 | 39.95
2020-09-09 12:00 | 44083.5 | 0 | 11.7591 | 39.95
2020-09-09 12:30 | 44083.5208 | 0 | 11.7645 | 39.95
2020-09-09 13:00 | 44083.5417 | 0 | 11.7301 | 39.95
2020-09-09 13:30 | 44083.5625 | 0 | 11.9516 | 39.95
2020-09-09 14:00 | 44083.5833 | 0 | 11.4501 | 39.95
2020-09-09 14:30 | 44083.6042 | 0 | 11.392 | 39.95
2020-09-09 15:00 | 44083.625 | 0 | 11.7623 | 39.95
2020-09-09 15:30 | 44083.6458 | 0 | 12.0584 | 39.95
2020-09-09 16:00 | 44083.6667 | 0 | 12.2472 | 39.95
2020-09-09 16:30 | 44083.6875 | 0 | 12.9688 | 39.95
2020-09-09 17:00 | 44083.7083 | 0 | 13.2427 | 39.95
2020-09-09 17:30 | 44083.7292 | 0 | 13.8595 | 39.95
2020-09-09 18:00 | 44083.75 | 0 | 14.252 | 39.95
2020-09-09 18:30 | 44083.7708 | 0 | 14.4098 | 39.95
2020-09-09 19:00 | 44083.7917 | 0 | 13.8534 | 39.95
2020-09-09 19:30 | 44083.8125 | 0 | 13.6116 | 39.95
2020-09-09 20:00 | 44083.8333 | 0 | 13.3807 | 39.95
2020-09-09 20:30 | 44083.8542 | 0 | 12.8551 | 39.95
2020-09-09 21:00 | 44083.875 | 0 | 12.4164 | 39.95
2020-09-09 21:30 | 44083.8958 | 0 | 11.8686 | 39.95
2020-09-09 22:00 | 44083.9167 | 0 | 11.1954 | 39.95
2020-09-09 22:30 | 44083.9375 | 0 | 10.134 | 39.95
2020-09-09 23:00 | 44083.9583 | 0 | 9.4292 | 39.95
2020-09-09 23:30 | 44083.9792 | 0 | 8.904 | 39.95
2020-09-10 | 44084 | 0 | 8.4749 | 39.95
2020-09-10 00:30 | 44084.0208 | 0 | 7.9981 | 39.95
2020-09-10 01:00 | 44084.0417 | 0 | 7.8218 | 39.95
2020-09-10 01:30 | 44084.0625 | 0 | 7.8163 | 39.95
2020-09-10 02:00 | 44084.0833 | 0 | 7.5978 | 39.95
2020-09-10 02:30 | 44084.1042 | 0 | 7.5505 | 39.95
2020-09-10 03:00 | 44084.125 | 0 | 7.5931 | 39.95
2020-09-10 03:30 | 44084.1458 | 0 | 7.5801 | 39.95
2020-09-10 04:00 | 44084.1667 | 0 | 7.7855 | 39.95
2020-09-10 04:30 | 44084.1875 | 0 | 8.3044 | 39.95
2020-09-10 05:00 | 44084.2083 | 0 | 8.7952 | 39.95
2020-09-10 05:30 | 44084.2292 | 0 | 9.5474 | 39.95
2020-09-10 06:00 | 44084.25 | 0 | 10.3322 | 39.95
2020-09-10 06:30 | 44084.2708 | 0 | 10.7601 | 39.95
2020-09-10 07:00 | 44084.2917 | 0 | 11.4268 | 39.95
2020-09-10 07:30 | 44084.3125 | 0 | 11.0183 | 39.95
2020-09-10 08:00 | 44084.3333 | 0 | 10.4858 | 39.95
2020-09-10 08:30 | 44084.3542 | 0 | 10.108 | 39.95
2020-09-10 09:00 | 44084.375 | 0 | 9.9702 | 39.95
2020-09-10 09:30 | 44084.3958 | 0 | 10.5978 | 39.95
2020-09-10 10:00 | 44084.4167 | 0 | 9.5373 | 39.95
2020-09-10 10:30 | 44084.4375 | 0 | 9.5461 | 39.95
2020-09-10 11:00 | 44084.4583 | 0 | 9.1113 | 39.95
2020-09-10 11:30 | 44084.4792 | 0 | 8.888 | 39.95
2020-09-10 12:00 | 44084.5 | 0 | 9.1405 | 39.95
2020-09-10 12:30 | 44084.5208 | 0 | 9.1122 | 39.95
2020-09-10 13:00 | 44084.5417 | 0 | 9.7657 | 39.95
2020-09-10 13:30 | 44084.5625 | 0 | 9.5113 | 39.95
2020-09-10 14:00 | 44084.5833 | 0 | 8.4996 | 39.95
2020-09-10 14:30 | 44084.6042 | 0 | 9.2478 | 39.95
2020-09-10 15:00 | 44084.625 | 0 | 9.9381 | 39.95
2020-09-10 15:30 | 44084.6458 | 0 | 10.1951 | 39.95
2020-09-10 16:00 | 44084.6667 | 0 | 11.0551 | 39.95
2020-09-10 16:30 | 44084.6875 | 0 | 11.3596 | 39.95
2020-09-10 17:00 | 44084.7083 | 0 | 11.7117 | 39.95
2020-09-10 17:30 | 44084.7292 | 0 | 12.4293 | 39.95
2020-09-10 18:00 | 44084.75 | 0 | 12.8769 | 39.95
2020-09-10 18:30 | 44084.7708 | 0 | 13.1405 | 39.95
2020-09-10 19:00 | 44084.7917 | 0 | 12.7956 | 39.95
2020-09-10 19:30 | 44084.8125 | 0 | 12.5901 | 39.95
2020-09-10 20:00 | 44084.8333 | 0 | 12.4352 | 39.95
2020-09-10 20:30 | 44084.8542 | 0 | 11.7834 | 39.95
2020-09-10 21:00 | 44084.875 | 0 | 11.5978 | 39.95
2020-09-10 21:30 | 44084.8958 | 0 | 11.2855 | 39.95
2020-09-10 22:00 | 44084.9167 | 0 | 10.8106 | 39.95
2020-09-10 22:30 | 44084.9375 | 0 | 10.0678 | 39.95
2020-09-10 23:00 | 44084.9583 | 0 | 9.545 | 39.95
2020-09-10 23:30 | 44084.9792 | 0 | 9.0114 | 39.95
2020-09-11 | 44085 | 0 | 8.4054 | 39.95
2020-09-11 00:30 | 44085.0208 | 0 | 7.8607 | 39.95
2020-09-11 01:00 | 44085.0417 | 0 | 7.7843 | 39.95
2020-09-11 01:30 | 44085.0625 | 0 | 7.5985 | 39.95
2020-09-11 02:00 | 44085.0833 | 0 | 7.584 | 39.95
2020-09-11 02:30 | 44085.1042 | 0 | 7.5148 | 39.95
2020-09-11 03:00 | 44085.125 | 0 | 7.4701 | 39.95
2020-09-11 03:30 | 44085.1458 | 0 | 7.3848 | 39.95
2020-09-11 04:00 | 44085.1667 | 0 | 7.4758 | 39.95
2020-09-11 04:30 | 44085.1875 | 0 | 7.6755 | 39.95
2020-09-11 05:00 | 44085.2083 | 0 | 7.8835 | 39.95
2020-09-11 05:30 | 44085.2292 | 0 | 8.0946 | 39.95
2020-09-11 06:00 | 44085.25 | 0 | 8.3152 | 39.95
2020-09-11 06:30 | 44085.2708 | 0 | 8.3767 | 39.95
2020-09-11 07:00 | 44085.2917 | 0 | 8.3412 | 39.95
2020-09-11 07:30 | 44085.3125 | 0 | 8.1268 | 39.95
2020-09-11 08:00 | 44085.3333 | 0 | 8.0919 | 39.95
2020-09-11 08:30 | 44085.3542 | 0 | 7.814 | 39.95
2020-09-11 09:00 | 44085.375 | 0 | 8.1482 | 39.95
2020-09-11 09:30 | 44085.3958 | 0 | 8.6227 | 39.95
2020-09-11 10:00 | 44085.4167 | 0 | 7.7496 | 39.95
2020-09-11 10:30 | 44085.4375 | 0 | 8.3823 | 39.95
2020-09-11 11:00 | 44085.4583 | 0 | 7.076 | 39.95
2020-09-11 11:30 | 44085.4792 | 0 | 6.7301 | 39.95
2020-09-11 12:00 | 44085.5 | 0 | 6.7164 | 39.95
2020-09-11 12:30 | 44085.5208 | 0 | 7.0798 | 39.95
2020-09-11 13:00 | 44085.5417 | 0 | 7.3195 | 39.95
2020-09-11 13:30 | 44085.5625 | 0 | 7.1872 | 39.95
2020-09-11 14:00 | 44085.5833 | 0 | 6.9749 | 39.95
2020-09-11 14:30 | 44085.6042 | 0 | 7.4018 | 39.95
2020-09-11 15:00 | 44085.625 | 0 | 7.7165 | 39.95
2020-09-11 15:30 | 44085.6458 | 0 | 8.1945 | 39.95
2020-09-11 16:00 | 44085.6667 | 0 | 8.632 | 39.95
2020-09-11 16:30 | 44085.6875 | 0 | 9.4735 | 39.95
2020-09-11 17:00 | 44085.7083 | 0 | 9.9299 | 39.95
2020-09-11 17:30 | 44085.7292 | 0 | 10.5675 | 39.95
2020-09-11 18:00 | 44085.75 | 0 | 11.0324 | 39.95
2020-09-11 18:30 | 44085.7708 | 0 | 11.2799 | 39.95
2020-09-11 19:00 | 44085.7917 | 0 | 10.9202 | 39.95
2020-09-11 19:30 | 44085.8125 | 0 | 10.7271 | 39.95
2020-09-11 20:00 | 44085.8333 | 0 | 10.6244 | 39.95
2020-09-11 20:30 | 44085.8542 | 0 | 10.1607 | 39.95
2020-09-11 21:00 | 44085.875 | 0 | 9.8153 | 39.95
2020-09-11 21:30 | 44085.8958 | 0 | 9.6252 | 39.95
2020-09-11 22:00 | 44085.9167 | 0 | 9.1763 | 39.95
2020-09-11 22:30 | 44085.9375 | 0 | 8.7615 | 39.95
2020-09-11 23:00 | 44085.9583 | 0 | 8.3007 | 39.95
2020-09-11 23:30 | 44085.9792 | 0 | 7.9241 | 39.95
2020-09-12 | 44086 | 0 | 7.3918 | 39.95
2020-09-12 00:30 | 44086.0208 | 0 | 7.1352 | 39.95
2020-09-12 01:00 | 44086.0417 | 0 | 7.005 | 39.95
2020-09-12 01:30 | 44086.0625 | 0 | 6.8859 | 39.95
2020-09-12 02:00 | 44086.0833 | 0 | 6.843 | 39.95
2020-09-12 02:30 | 44086.1042 | 0 | 6.7631 | 39.95
2020-09-12 03:00 | 44086.125 | 0 | 6.6529 | 39.95
2020-09-12 03:30 | 44086.1458 | 0 | 6.6108 | 39.95
2020-09-12 04:00 | 44086.1667 | 0 | 6.6831 | 39.95
2020-09-12 04:30 | 44086.1875 | 0 | 6.5991 | 39.95
2020-09-12 05:00 | 44086.2083 | 0 | 6.6887 | 39.95
2020-09-12 05:30 | 44086.2292 | 0 | 6.832 | 39.95
2020-09-12 06:00 | 44086.25 | 0 | 6.8933 | 39.95
2020-09-12 06:30 | 44086.2708 | 0 | 6.9268 | 39.95
2020-09-12 07:00 | 44086.2917 | 0 | 6.83 | 39.95
2020-09-12 07:30 | 44086.3125 | 0 | 6.7146 | 39.95
2020-09-12 08:00 | 44086.3333 | 0 | 6.6195 | 39.95
2020-09-12 08:30 | 44086.3542 | 0 | 6.5789 | 39.95
2020-09-12 09:00 | 44086.375 | 0 | 6.5455 | 39.95
2020-09-12 09:30 | 44086.3958 | 0 | 6.7573 | 39.95
2020-09-12 10:00 | 44086.4167 | 0 | 7.4515 | 39.95
2020-09-12 10:30 | 44086.4375 | 0 | 8.2732 | 39.95
2020-09-12 11:00 | 44086.4583 | 0 | 9.3375 | 39.95
2020-09-12 11:30 | 44086.4792 | 0 | 8.9273 | 39.95
2020-09-12 12:00 | 44086.5 | 0 | 8.0252 | 39.95
2020-09-12 12:30 | 44086.5208 | 0 | 7.3031 | 39.95
2020-09-12 13:00 | 44086.5417 | 0 | 6.9439 | 39.95
2020-09-12 13:30 | 44086.5625 | 0 | 6.3122 | 39.95
2020-09-12 14:00 | 44086.5833 | 0 | 5.9909 | 39.95
2020-09-12 14:30 | 44086.6042 | 0 | 6.7427 | 39.95
2020-09-12 15:00 | 44086.625 | 0 | 7.1816 | 39.95
2020-09-12 15:30 | 44086.6458 | 0 | 7.763 | 39.95
2020-09-12 16:00 | 44086.6667 | 0 | 8.4836 | 39.95
2020-09-12 16:30 | 44086.6875 | 0 | 9.2552 | 39.95
2020-09-12 17:00 | 44086.7083 | 0 | 9.9855 | 39.95
2020-09-12 17:30 | 44086.7292 | 0 | 10.8373 | 39.95
2020-09-12 18:00 | 44086.75 | 0 | 11.4683 | 39.95
2020-09-12 18:30 | 44086.7708 | 0 | 11.6911 | 39.95
2020-09-12 19:00 | 44086.7917 | 0 | 11.3511 | 39.95
2020-09-12 19:30 | 44086.8125 | 0 | 10.5705 | 39.95
2020-09-12 20:00 | 44086.8333 | 0 | 10.1348 | 39.95
2020-09-12 20:30 | 44086.8542 | 0 | 9.8781 | 39.95
2020-09-12 21:00 | 44086.875 | 0 | 9.7832 | 39.95
2020-09-12 21:30 | 44086.8958 | 0 | 9.4481 | 39.95
2020-09-12 22:00 | 44086.9167 | 0 | 8.9869 | 39.95
2020-09-12 22:30 | 44086.9375 | 0 | 8.2407 | 39.95
2020-09-12 23:00 | 44086.9583 | 0 | 7.7781 | 39.95
2020-09-12 23:30 | 44086.9792 | 0 | 7.4736 | 39.95
2020-09-13 | 44087 | 0 | 7.1475 | 39.95
2020-09-13 00:30 | 44087.0208 | 0 | 6.9399 | 39.95
2020-09-13 01:00 | 44087.0417 | 0 | 6.7758 | 39.95
2020-09-13 01:30 | 44087.0625 | 0 | 6.7278 | 39.95
2020-09-13 02:00 | 44087.0833 | 0 | 6.7816 | 39.95
2020-09-13 02:30 | 44087.1042 | 0 | 6.8097 | 39.95
2020-09-13 03:00 | 44087.125 | 0 | 6.8039 | 39.95
2020-09-13 03:30 | 44087.1458 | 0 | 6.8768 | 39.95
2020-09-13 04:00 | 44087.1667 | 0 | 7.2178 | 39.95
2020-09-13 04:30 | 44087.1875 | 0 | 7.5785 | 39.95
2020-09-13 05:00 | 44087.2083 | 0 | 8.3036 | 39.95
2020-09-13 05:30 | 44087.2292 | 0 | 8.9176 | 39.95
2020-09-13 06:00 | 44087.25 | 0 | 9.677 | 39.95
2020-09-13 06:30 | 44087.2708 | 0 | 10.3209 | 39.95
2020-09-13 07:00 | 44087.2917 | 0 | 10.6883 | 39.95
2020-09-13 07:30 | 44087.3125 | 0 | 10.4436 | 39.95
2020-09-13 08:00 | 44087.3333 | 0 | 9.9512 | 39.95
2020-09-13 08:30 | 44087.3542 | 0 | 9.5578 | 39.95
2020-09-13 09:00 | 44087.375 | 0 | 9.1641 | 39.95
2020-09-13 09:30 | 44087.3958 | 0 | 9.0222 | 39.95
2020-09-13 10:00 | 44087.4167 | 0 | 8.6311 | 39.95
2020-09-13 10:30 | 44087.4375 | 0 | 8.6206 | 39.95
2020-09-13 11:00 | 44087.4583 | 0 | 8.533 | 39.95
2020-09-13 11:30 | 44087.4792 | 0 | 8.6704 | 39.95
2020-09-13 12:00 | 44087.5 | 0 | 8.7375 | 39.95
2020-09-13 12:30 | 44087.5208 | 0 | 8.7845 | 39.95
2020-09-13 13:00 | 44087.5417 | 0 | 9.3083 | 39.95
2020-09-13 13:30 | 44087.5625 | 0 | 9.4704 | 39.95
2020-09-13 14:00 | 44087.5833 | 0 | 9.3632 | 39.95
2020-09-13 14:30 | 44087.6042 | 0 | 9.8568 | 39.95
2020-09-13 15:00 | 44087.625 | 0 | 10.0541 | 39.95
2020-09-13 15:30 | 44087.6458 | 0 | 10.2982 | 39.95
2020-09-13 16:00 | 44087.6667 | 0 | 10.7239 | 39.95
2020-09-13 16:30 | 44087.6875 | 0 | 11.3828 | 39.95
2020-09-13 17:00 | 44087.7083 | 0 | 11.5664 | 39.95
2020-09-13 17:30 | 44087.7292 | 0 | 12.5957 | 39.95
2020-09-13 18:00 | 44087.75 | 0 | 13.3607 | 39.95
2020-09-13 18:30 | 44087.7708 | 0 | 13.5571 | 39.95
2020-09-13 19:00 | 44087.7917 | 0 | 13.2242 | 39.95
2020-09-13 19:30 | 44087.8125 | 0 | 12.8039 | 39.95
2020-09-13 20:00 | 44087.8333 | 0 | 12.669 | 39.95
2020-09-13 20:30 | 44087.8542 | 0 | 11.9997 | 39.95
2020-09-13 21:00 | 44087.875 | 0 | 11.5638 | 39.95
2020-09-13 21:30 | 44087.8958 | 0 | 10.9724 | 39.95
2020-09-13 22:00 | 44087.9167 | 0 | 10.4527 | 39.95
2020-09-13 22:30 | 44087.9375 | 0 | 9.5572 | 39.95
2020-09-13 23:00 | 44087.9583 | 0 | 8.9664 | 39.95
2020-09-13 23:30 | 44087.9792 | 0 | 8.6156 | 39.95
2020-09-14 | 44088 | 0 | 8.1572 | 39.95
2020-09-14 00:30 | 44088.0208 | 0 | 7.7204 | 39.95
2020-09-14 01:00 | 44088.0417 | 0 | 7.4478 | 39.95
2020-09-14 01:30 | 44088.0625 | 0 | 7.4777 | 39.95
2020-09-14 02:00 | 44088.0833 | 0 | 7.3938 | 39.95
2020-09-14 02:30 | 44088.1042 | 0 | 7.3902 | 39.95
2020-09-14 03:00 | 44088.125 | 0 | 7.2785 | 39.95
2020-09-14 03:30 | 44088.1458 | 0 | 7.3362 | 39.95
2020-09-14 04:00 | 44088.1667 | 0 | 7.4353 | 39.95
2020-09-14 04:30 | 44088.1875 | 0 | 8.0597 | 39.95
2020-09-14 05:00 | 44088.2083 | 0 | 8.6359 | 39.95
2020-09-14 05:30 | 44088.2292 | 0 | 9.1222 | 39.95
2020-09-14 06:00 | 44088.25 | 0 | 10.044 | 39.95
2020-09-14 06:30 | 44088.2708 | 0 | 10.4031 | 39.95
2020-09-14 07:00 | 44088.2917 | 0 | 10.6345 | 39.95
2020-09-14 07:30 | 44088.3125 | 0 | 10.5143 | 39.95
2020-09-14 08:00 | 44088.3333 | 0 | 9.9877 | 39.95
2020-09-14 08:30 | 44088.3542 | 0 | 10.1781 | 39.95
2020-09-14 09:00 | 44088.375 | 0 | 9.5674 | 39.95
2020-09-14 09:30 | 44088.3958 | 0 | 9.5779 | 39.95
2020-09-14 10:00 | 44088.4167 | 0 | 8.8259 | 39.95
2020-09-14 10:30 | 44088.4375 | 0 | 8.7497 | 39.95
2020-09-14 11:00 | 44088.4583 | 0 | 8.5453 | 39.95
2020-09-14 11:30 | 44088.4792 | 0 | 8.5979 | 39.95
2020-09-14 12:00 | 44088.5 | 0 | 8.9423 | 39.95
2020-09-14 12:30 | 44088.5208 | 0 | 8.9566 | 39.95
2020-09-14 13:00 | 44088.5417 | 0 | 9.2153 | 39.95
2020-09-14 13:30 | 44088.5625 | 0 | 9.8967 | 39.95
2020-09-14 14:00 | 44088.5833 | 0 | 10.0633 | 39.95
2020-09-14 14:30 | 44088.6042 | 0 | 10.4761 | 39.95
2020-09-14 15:00 | 44088.625 | 0 | 10.7939 | 39.95
2020-09-14 15:30 | 44088.6458 | 0 | 11.2165 | 39.95
2020-09-14 16:00 | 44088.6667 | 0 | 11.1702 | 39.95
2020-09-14 16:30 | 44088.6875 | 0 | 11.8847 | 39.95
2020-09-14 17:00 | 44088.7083 | 0 | 12.3139 | 39.95
2020-09-14 17:30 | 44088.7292 | 0 | 13.0061 | 39.95
2020-09-14 18:00 | 44088.75 | 0 | 13.575 | 39.95
2020-09-14 18:30 | 44088.7708 | 0 | 13.6998 | 39.95
2020-09-14 19:00 | 44088.7917 | 0 | 13.3289 | 39.95
2020-09-14 19:30 | 44088.8125 | 0 | 13.057 | 39.95
2020-09-14 20:00 | 44088.8333 | 0 | 12.8105 | 39.95
2020-09-14 20:30 | 44088.8542 | 0 | 12.1647 | 39.95
2020-09-14 21:00 | 44088.875 | 0 | 11.4785 | 39.95
2020-09-14 21:30 | 44088.8958 | 0 | 11.2052 | 39.95
2020-09-14 22:00 | 44088.9167 | 0 | 10.543 | 39.95
2020-09-14 22:30 | 44088.9375 | 0 | 9.8206 | 39.95
2020-09-14 23:00 | 44088.9583 | 0 | 9.1772 | 39.95
2020-09-14 23:30 | 44088.9792 | 0 | 8.602 | 39.95
2020-09-15 | 44089 | 0 | 8.0589 | 39.95
2020-09-15 00:30 | 44089.0208 | 0 | 7.6916 | 39.95
2020-09-15 01:00 | 44089.0417 | 0 | 7.58 | 39.95
2020-09-15 01:30 | 44089.0625 | 0 | 7.634 | 39.95
2020-09-15 02:00 | 44089.0833 | 0 | 7.4181 | 39.95
2020-09-15 02:30 | 44089.1042 | 0 | 7.4795 | 39.95
2020-09-15 03:00 | 44089.125 | 0 | 7.4237 | 39.95
2020-09-15 03:30 | 44089.1458 | 0 | 7.4443 | 39.95
2020-09-15 04:00 | 44089.1667 | 0 | 7.7108 | 39.95
2020-09-15 04:30 | 44089.1875 | 0 | 8.059 | 39.95
2020-09-15 05:00 | 44089.2083 | 0 | 8.5595 | 39.95
2020-09-15 05:30 | 44089.2292 | 0 | 9.1512 | 39.95
2020-09-15 06:00 | 44089.25 | 0 | 10.0217 | 39.95
2020-09-15 06:30 | 44089.2708 | 0 | 10.8336 | 39.95
2020-09-15 07:00 | 44089.2917 | 0 | 11.4294 | 39.95
2020-09-15 07:30 | 44089.3125 | 0 | 11.8362 | 39.95
2020-09-15 08:00 | 44089.3333 | 0 | 11.2892 | 39.95
2020-09-15 08:30 | 44089.3542 | 0 | 10.4888 | 39.95
2020-09-15 09:00 | 44089.375 | 0 | 10.0236 | 39.95
2020-09-15 09:30 | 44089.3958 | 0 | 9.5254 | 39.95
2020-09-15 10:00 | 44089.4167 | 0 | 10.6423 | 39.95
2020-09-15 10:30 | 44089.4375 | 0 | 9.1607 | 39.95
2020-09-15 11:00 | 44089.4583 | 0 | 8.8551 | 39.95
2020-09-15 11:30 | 44089.4792 | 0 | 8.4522 | 39.95
2020-09-15 12:00 | 44089.5 | 0 | 8.7029 | 39.95
2020-09-15 12:30 | 44089.5208 | 0 | 8.7333 | 39.95
2020-09-15 13:00 | 44089.5417 | 0 | 8.9363 | 39.95
2020-09-15 13:30 | 44089.5625 | 0 | 9.3091 | 39.95
2020-09-15 14:00 | 44089.5833 | 0 | 9.7464 | 39.95
2020-09-15 14:30 | 44089.6042 | 0 | 9.9905 | 39.95
2020-09-15 15:00 | 44089.625 | 0 | 10.3832 | 39.95
2020-09-15 15:30 | 44089.6458 | 0 | 10.8115 | 39.95
2020-09-15 16:00 | 44089.6667 | 0 | 11.3318 | 39.95
2020-09-15 16:30 | 44089.6875 | 0 | 11.8944 | 39.95
2020-09-15 17:00 | 44089.7083 | 0 | 12.2411 | 39.95
2020-09-15 17:30 | 44089.7292 | 0 | 12.871 | 39.95
2020-09-15 18:00 | 44089.75 | 0 | 13.621 | 39.95
2020-09-15 18:30 | 44089.7708 | 0 | 14.0301 | 39.95
2020-09-15 19:00 | 44089.7917 | 0 | 13.4804 | 39.95
2020-09-15 19:30 | 44089.8125 | 0 | 13.1604 | 39.95
2020-09-15 20:00 | 44089.8333 | 0 | 13.0034 | 39.95
2020-09-15 20:30 | 44089.8542 | 0 | 12.3503 | 39.95
2020-09-15 21:00 | 44089.875 | 0 | 11.9477 | 39.95
2020-09-15 21:30 | 44089.8958 | 0 | 11.5387 | 39.95
2020-09-15 22:00 | 44089.9167 | 0 | 10.8013 | 39.95
2020-09-15 22:30 | 44089.9375 | 0 | 10.0977 | 39.95
2020-09-15 23:00 | 44089.9583 | 0 | 9.518 | 39.95
2020-09-15 23:30 | 44089.9792 | 0 | 8.8877 | 39.95
2020-09-16 | 44090 | 0 | 8.3428 | 39.95
2020-09-16 00:30 | 44090.0208 | 0 | 7.8911 | 39.95
2020-09-16 01:00 | 44090.0417 | 0 | 7.8983 | 39.95
2020-09-16 01:30 | 44090.0625 | 0 | 7.8368 | 39.95
2020-09-16 02:00 | 44090.0833 | 0 | 7.591 | 39.95
2020-09-16 02:30 | 44090.1042 | 0 | 7.649 | 39.95
2020-09-16 03:00 | 44090.125 | 0 | 7.664 | 39.95
2020-09-16 03:30 | 44090.1458 | 0 | 7.6357 | 39.95
2020-09-16 04:00 | 44090.1667 | 0 | 7.83 | 39.95
2020-09-16 04:30 | 44090.1875 | 0 | 8.2165 | 39.95
2020-09-16 05:00 | 44090.2083 | 0 | 8.8651 | 39.95
2020-09-16 05:30 | 44090.2292 | 0 | 9.5096 | 39.95
2020-09-16 06:00 | 44090.25 | 0 | 10.1498 | 39.95
2020-09-16 06:30 | 44090.2708 | 0 | 10.5168 | 39.95
2020-09-16 07:00 | 44090.2917 | 0 | 10.7424 | 39.95
2020-09-16 07:30 | 44090.3125 | 0 | 10.6261 | 39.95
2020-09-16 08:00 | 44090.3333 | 0 | 10.2194 | 39.95
2020-09-16 08:30 | 44090.3542 | 0 | 9.724 | 39.95
2020-09-16 09:00 | 44090.375 | 0 | 9.2613 | 39.95
2020-09-16 09:30 | 44090.3958 | 0 | 9.2377 | 39.95
2020-09-16 10:00 | 44090.4167 | 0 | 8.9831 | 39.95
2020-09-16 10:30 | 44090.4375 | 0 | 8.9888 | 39.95
2020-09-16 11:00 | 44090.4583 | 0 | 8.8028 | 39.95
2020-09-16 11:30 | 44090.4792 | 0 | 8.9592 | 39.95
2020-09-16 12:00 | 44090.5 | 0 | 8.9013 | 39.95
2020-09-16 12:30 | 44090.5208 | 0 | 8.98 | 39.95
2020-09-16 13:00 | 44090.5417 | 0 | 9.2626 | 39.95
2020-09-16 13:30 | 44090.5625 | 0 | 9.6084 | 39.95
2020-09-16 14:00 | 44090.5833 | 0 | 9.8824 | 39.95
2020-09-16 14:30 | 44090.6042 | 0 | 10.2528 | 39.95
2020-09-16 15:00 | 44090.625 | 0 | 10.4835 | 39.95
2020-09-16 15:30 | 44090.6458 | 0 | 10.9957 | 39.95
2020-09-16 16:00 | 44090.6667 | 0 | 11.6293 | 39.95
2020-09-16 16:30 | 44090.6875 | 0 | 12.0895 | 39.95
2020-09-16 17:00 | 44090.7083 | 0 | 12.6962 | 39.95
2020-09-16 17:30 | 44090.7292 | 0 | 12.9571 | 39.95
2020-09-16 18:00 | 44090.75 | 0 | 13.5225 | 39.95
2020-09-16 18:30 | 44090.7708 | 0 | 13.887 | 39.95
2020-09-16 19:00 | 44090.7917 | 0 | 13.4602 | 39.95
2020-09-16 19:30 | 44090.8125 | 0 | 13.0457 | 39.95
2020-09-16 20:00 | 44090.8333 | 0 | 12.7967 | 39.95
2020-09-16 20:30 | 44090.8542 | 0 | 12.4222 | 39.95
2020-09-16 21:00 | 44090.875 | 0 | 11.8878 | 39.95
2020-09-16 21:30 | 44090.8958 | 0 | 11.4236 | 39.95
2020-09-16 22:00 | 44090.9167 | 0 | 10.8782 | 39.95
2020-09-16 22:30 | 44090.9375 | 0 | 10.1249 | 39.95
2020-09-16 23:00 | 44090.9583 | 0 | 9.4915 | 39.95
2020-09-16 23:30 | 44090.9792 | 0 | 8.9197 | 39.95
2020-09-17 | 44091 | 0 | 8.2914 | 39.95
2020-09-17 00:30 | 44091.0208 | 0 | 7.9053 | 39.95
2020-09-17 01:00 | 44091.0417 | 0 | 7.891 | 39.95
2020-09-17 01:30 | 44091.0625 | 0 | 7.74 | 39.95
2020-09-17 02:00 | 44091.0833 | 0 | 7.6993 | 39.95
2020-09-17 02:30 | 44091.1042 | 0 | 7.7326 | 39.95
2020-09-17 03:00 | 44091.125 | 0 | 7.6152 | 39.95
2020-09-17 03:30 | 44091.1458 | 0 | 7.6584 | 39.95
2020-09-17 04:00 | 44091.1667 | 0 | 7.8558 | 39.95
2020-09-17 04:30 | 44091.1875 | 0 | 8.2259 | 39.95
2020-09-17 05:00 | 44091.2083 | 0 | 8.8289 | 39.95
2020-09-17 05:30 | 44091.2292 | 0 | 9.4026 | 39.95
2020-09-17 06:00 | 44091.25 | 0 | 9.8873 | 39.95
2020-09-17 06:30 | 44091.2708 | 0 | 10.3389 | 39.95
2020-09-17 07:00 | 44091.2917 | 0 | 10.612 | 39.95
2020-09-17 07:30 | 44091.3125 | 0 | 10.7734 | 39.95
2020-09-17 08:00 | 44091.3333 | 0 | 11.0755 | 39.95
2020-09-17 08:30 | 44091.3542 | 0 | 10.9039 | 39.95
2020-09-17 09:00 | 44091.375 | 0 | 11.2068 | 39.95
2020-09-17 09:30 | 44091.3958 | 0 | 10.2386 | 39.95
2020-09-17 10:00 | 44091.4167 | 0 | 10.564 | 39.95
2020-09-17 10:30 | 44091.4375 | 0 | 10.39 | 39.95
2020-09-17 11:00 | 44091.4583 | 0 | 9.6531 | 39.95
2020-09-17 11:30 | 44091.4792 | 0 | 10.0849 | 39.95
2020-09-17 12:00 | 44091.5 | 0 | 9.4385 | 39.95
2020-09-17 12:30 | 44091.5208 | 0 | 9.8522 | 39.95
2020-09-17 13:00 | 44091.5417 | 0 | 10.1642 | 39.95
2020-09-17 13:30 | 44091.5625 | 0 | 10.2826 | 39.95
2020-09-17 14:00 | 44091.5833 | 0 | 10.3218 | 39.95
2020-09-17 14:30 | 44091.6042 | 0 | 10.4591 | 39.95
2020-09-17 15:00 | 44091.625 | 0 | 11.1554 | 39.95
2020-09-17 15:30 | 44091.6458 | 0 | 11.5275 | 39.95
2020-09-17 16:00 | 44091.6667 | 0 | 11.6378 | 39.95
2020-09-17 16:30 | 44091.6875 | 0 | 12.3074 | 39.95
2020-09-17 17:00 | 44091.7083 | 0 | 12.3314 | 39.95
2020-09-17 17:30 | 44091.7292 | 0 | 12.6198 | 39.95
2020-09-17 18:00 | 44091.75 | 0 | 12.9364 | 39.95
2020-09-17 18:30 | 44091.7708 | 0 | 13.0307 | 39.95
2020-09-17 19:00 | 44091.7917 | 0 | 12.7442 | 39.95
2020-09-17 19:30 | 44091.8125 | 0 | 12.4635 | 39.95
2020-09-17 20:00 | 44091.8333 | 0 | 12.2531 | 39.95
2020-09-17 20:30 | 44091.8542 | 0 | 11.7764 | 39.95
2020-09-17 21:00 | 44091.875 | 0 | 11.392 | 39.95
2020-09-17 21:30 | 44091.8958 | 0 | 11.0637 | 39.95
2020-09-17 22:00 | 44091.9167 | 0 | 10.587 | 39.95
2020-09-17 22:30 | 44091.9375 | 0 | 10.0442 | 39.95
2020-09-17 23:00 | 44091.9583 | 0 | 9.6025 | 39.95
2020-09-17 23:30 | 44091.9792 | 0 | 9.1282 | 39.95
2020-09-18 | 44092 | 0 | 8.5419 | 39.95
2020-09-18 00:30 | 44092.0208 | 0 | 8.0592 | 39.95
2020-09-18 01:00 | 44092.0417 | 0 | 7.8593 | 39.95
2020-09-18 01:30 | 44092.0625 | 0 | 7.7454 | 39.95
2020-09-18 02:00 | 44092.0833 | 0 | 7.6024 | 39.95
2020-09-18 02:30 | 44092.1042 | 0 | 7.4347 | 39.95
2020-09-18 03:00 | 44092.125 | 0 | 7.5485 | 39.95
2020-09-18 03:30 | 44092.1458 | 0 | 7.3993 | 39.95
2020-09-18 04:00 | 44092.1667 | 0 | 7.5097 | 39.95
2020-09-18 04:30 | 44092.1875 | 0 | 7.5839 | 39.95
2020-09-18 05:00 | 44092.2083 | 0 | 7.7144 | 39.95
2020-09-18 05:30 | 44092.2292 | 0 | 7.9077 | 39.95
2020-09-18 06:00 | 44092.25 | 0 | 8.0546 | 39.95
2020-09-18 06:30 | 44092.2708 | 0 | 7.9802 | 39.95
2020-09-18 07:00 | 44092.2917 | 0 | 7.9708 | 39.95
2020-09-18 07:30 | 44092.3125 | 0 | 8.0526 | 39.95
2020-09-18 08:00 | 44092.3333 | 0 | 8.0012 | 39.95
2020-09-18 08:30 | 44092.3542 | 0 | 7.6238 | 39.95
2020-09-18 09:00 | 44092.375 | 0 | 7.9659 | 39.95
2020-09-18 09:30 | 44092.3958 | 0 | 6.9511 | 39.95
2020-09-18 10:00 | 44092.4167 | 0 | 7.5451 | 39.95
2020-09-18 10:30 | 44092.4375 | 0 | 7.5846 | 39.95
2020-09-18 11:00 | 44092.4583 | 0 | 6.9608 | 39.95
2020-09-18 11:30 | 44092.4792 | 0 | 6.7963 | 39.95
2020-09-18 12:00 | 44092.5 | 0 | 6.5269 | 39.95
2020-09-18 12:30 | 44092.5208 | 0 | 6.0538 | 39.95
2020-09-18 13:00 | 44092.5417 | 0 | 6.2521 | 39.95
2020-09-18 13:30 | 44092.5625 | 0 | 6.3105 | 39.95
2020-09-18 14:00 | 44092.5833 | 0 | 7.052 | 39.95
2020-09-18 14:30 | 44092.6042 | 0 | 7.445 | 39.95
2020-09-18 15:00 | 44092.625 | 0 | 8.3451 | 39.95
2020-09-18 15:30 | 44092.6458 | 0 | 8.4202 | 39.95
2020-09-18 16:00 | 44092.6667 | 0 | 8.7984 | 39.95
2020-09-18 16:30 | 44092.6875 | 0 | 9.78 | 39.95
2020-09-18 17:00 | 44092.7083 | 0 | 10.1445 | 39.95
2020-09-18 17:30 | 44092.7292 | 0 | 10.4709 | 39.95
2020-09-18 18:00 | 44092.75 | 0 | 10.837 | 39.95
2020-09-18 18:30 | 44092.7708 | 0 | 11.0883 | 39.95
2020-09-18 19:00 | 44092.7917 | 0 | 10.8291 | 39.95
2020-09-18 19:30 | 44092.8125 | 0 | 10.5783 | 39.95
2020-09-18 20:00 | 44092.8333 | 0 | 10.3277 | 39.95
2020-09-18 20:30 | 44092.8542 | 0 | 10.0048 | 39.95
2020-09-18 21:00 | 44092.875 | 0 | 9.5418 | 39.95
2020-09-18 21:30 | 44092.8958 | 0 | 9.4262 | 39.95
2020-09-18 22:00 | 44092.9167 | 0 | 9.1223 | 39.95
2020-09-18 22:30 | 44092.9375 | 0 | 8.5689 | 39.95
2020-09-18 23:00 | 44092.9583 | 0 | 8.1562 | 39.95
2020-09-18 23:30 | 44092.9792 | 0 | 7.87 | 39.95
2020-09-19 | 44093 | 0 | 7.3839 | 39.95
2020-09-19 00:30 | 44093.0208 | 0 | 7.1929 | 39.95
2020-09-19 01:00 | 44093.0417 | 0 | 6.9582 | 39.95
2020-09-19 01:30 | 44093.0625 | 0 | 6.964 | 39.95
2020-09-19 02:00 | 44093.0833 | 0 | 6.8337 | 39.95
2020-09-19 02:30 | 44093.1042 | 0 | 6.925 | 39.95
2020-09-19 03:00 | 44093.125 | 0 | 6.702 | 39.95
2020-09-19 03:30 | 44093.1458 | 0 | 6.6235 | 39.95
2020-09-19 04:00 | 44093.1667 | 0 | 6.6365 | 39.95
2020-09-19 04:30 | 44093.1875 | 0 | 6.6775 | 39.95
2020-09-19 05:00 | 44093.2083 | 0 | 6.823 | 39.95
2020-09-19 05:30 | 44093.2292 | 0 | 6.8916 | 39.95
2020-09-19 06:00 | 44093.25 | 0 | 6.9397 | 39.95
2020-09-19 06:30 | 44093.2708 | 0 | 7.1005 | 39.95
2020-09-19 07:00 | 44093.2917 | 0 | 6.7093 | 39.95
2020-09-19 07:30 | 44093.3125 | 0 | 6.6514 | 39.95
2020-09-19 08:00 | 44093.3333 | 0 | 7.7202 | 39.95
2020-09-19 08:30 | 44093.3542 | 0 | 8.3887 | 39.95
2020-09-19 09:00 | 44093.375 | 0 | 7.9061 | 39.95
2020-09-19 09:30 | 44093.3958 | 0 | 7.0096 | 39.95
2020-09-19 10:00 | 44093.4167 | 0 | 7.6236 | 39.95
2020-09-19 10:30 | 44093.4375 | 0 | 7.7884 | 39.95
2020-09-19 11:00 | 44093.4583 | 0 | 6.635 | 39.95
2020-09-19 11:30 | 44093.4792 | 0 | 7.4863 | 39.95
2020-09-19 12:00 | 44093.5 | 0 | 6.2816 | 39.95
2020-09-19 12:30 | 44093.5208 | 0 | 6.3818 | 39.95
2020-09-19 13:00 | 44093.5417 | 0 | 6.0433 | 39.95
2020-09-19 13:30 | 44093.5625 | 0 | 6.9417 | 39.95
2020-09-19 14:00 | 44093.5833 | 0 | 7.2187 | 39.95
2020-09-19 14:30 | 44093.6042 | 0 | 7.3072 | 39.95
2020-09-19 15:00 | 44093.625 | 0 | 7.98 | 39.95
2020-09-19 15:30 | 44093.6458 | 0 | 8.3972 | 39.95
2020-09-19 16:00 | 44093.6667 | 0 | 9.1529 | 39.95
2020-09-19 16:30 | 44093.6875 | 0 | 9.9411 | 39.95
2020-09-19 17:00 | 44093.7083 | 0 | 10.413 | 39.95
2020-09-19 17:30 | 44093.7292 | 0 | 10.8554 | 39.95
2020-09-19 18:00 | 44093.75 | 0 | 11.4329 | 39.95
2020-09-19 18:30 | 44093.7708 | 0 | 11.7472 | 39.95
2020-09-19 19:00 | 44093.7917 | 0 | 11.4879 | 39.95
2020-09-19 19:30 | 44093.8125 | 0 | 11.0587 | 39.95
2020-09-19 20:00 | 44093.8333 | 0 | 10.6594 | 39.95
2020-09-19 20:30 | 44093.8542 | 0 | 10.2343 | 39.95
2020-09-19 21:00 | 44093.875 | 0 | 9.8429 | 39.95
2020-09-19 21:30 | 44093.8958 | 0 | 9.5919 | 39.95
2020-09-19 22:00 | 44093.9167 | 0 | 9.3527 | 39.95
2020-09-19 22:30 | 44093.9375 | 0 | 8.5251 | 39.95
2020-09-19 23:00 | 44093.9583 | 0 | 8.1317 | 39.95
2020-09-19 23:30 | 44093.9792 | 0 | 7.8087 | 39.95
2020-09-20 | 44094 | 0 | 7.4536 | 39.95
2020-09-20 00:30 | 44094.0208 | 0 | 7.2988 | 39.95
2020-09-20 01:00 | 44094.0417 | 0 | 7.1669 | 39.95
2020-09-20 01:30 | 44094.0625 | 0 | 7.1612 | 39.95
2020-09-20 02:00 | 44094.0833 | 0 | 7.1464 | 39.95
2020-09-20 02:30 | 44094.1042 | 0 | 7.1967 | 39.95
2020-09-20 03:00 | 44094.125 | 0 | 7.1948 | 39.95
2020-09-20 03:30 | 44094.1458 | 0 | 7.1576 | 39.95
2020-09-20 04:00 | 44094.1667 | 0 | 7.445 | 39.95
2020-09-20 04:30 | 44094.1875 | 0 | 8.0886 | 39.95
2020-09-20 05:00 | 44094.2083 | 0 | 8.6665 | 39.95
2020-09-20 05:30 | 44094.2292 | 0 | 9.1657 | 39.95
2020-09-20 06:00 | 44094.25 | 0 | 9.5456 | 39.95
2020-09-20 06:30 | 44094.2708 | 0 | 9.9787 | 39.95
2020-09-20 07:00 | 44094.2917 | 0 | 10.2286 | 39.95
2020-09-20 07:30 | 44094.3125 | 0 | 10.5337 | 39.95
2020-09-20 08:00 | 44094.3333 | 0 | 10.6919 | 39.95
2020-09-20 08:30 | 44094.3542 | 0 | 10.3715 | 39.95
2020-09-20 09:00 | 44094.375 | 0 | 10.0719 | 39.95
2020-09-20 09:30 | 44094.3958 | 0 | 10.0159 | 39.95
2020-09-20 10:00 | 44094.4167 | 0 | 9.9457 | 39.95
2020-09-20 10:30 | 44094.4375 | 0 | 9.8726 | 39.95
2020-09-20 11:00 | 44094.4583 | 0 | 10.0206 | 39.95
2020-09-20 11:30 | 44094.4792 | 0 | 9.9019 | 39.95
2020-09-20 12:00 | 44094.5 | 0 | 9.7405 | 39.95
2020-09-20 12:30 | 44094.5208 | 0 | 10.17 | 39.95
2020-09-20 13:00 | 44094.5417 | 0 | 10.641 | 39.95
2020-09-20 13:30 | 44094.5625 | 0 | 10.6818 | 39.95
2020-09-20 14:00 | 44094.5833 | 0 | 11.0589 | 39.95
2020-09-20 14:30 | 44094.6042 | 0 | 11.5342 | 39.95
2020-09-20 15:00 | 44094.625 | 0 | 12.0584 | 39.95
2020-09-20 15:30 | 44094.6458 | 0 | 12.482 | 39.95
2020-09-20 16:00 | 44094.6667 | 0 | 12.9325 | 39.95
2020-09-20 16:30 | 44094.6875 | 0 | 13.4547 | 39.95
2020-09-20 17:00 | 44094.7083 | 0 | 13.4606 | 39.95
2020-09-20 17:30 | 44094.7292 | 0 | 13.6441 | 39.95
2020-09-20 18:00 | 44094.75 | 0 | 14.2915 | 39.95
2020-09-20 18:30 | 44094.7708 | 0 | 14.4884 | 39.95
2020-09-20 19:00 | 44094.7917 | 0 | 14.1454 | 39.95
2020-09-20 19:30 | 44094.8125 | 0 | 13.7505 | 39.95
2020-09-20 20:00 | 44094.8333 | 0 | 13.5628 | 39.95
2020-09-20 20:30 | 44094.8542 | 0 | 12.9789 | 39.95
2020-09-20 21:00 | 44094.875 | 0 | 12.4276 | 39.95
2020-09-20 21:30 | 44094.8958 | 0 | 12.0815 | 39.95
2020-09-20 22:00 | 44094.9167 | 0 | 11.4464 | 39.95
2020-09-20 22:30 | 44094.9375 | 0 | 10.8571 | 39.95
2020-09-20 23:00 | 44094.9583 | 0 | 10.1894 | 39.95
2020-09-20 23:30 | 44094.9792 | 0 | 9.6742 | 39.95
2020-09-21 | 44095 | 0 | 8.9557 | 39.95
2020-09-21 00:30 | 44095.0208 | 0 | 8.5644 | 39.95
2020-09-21 01:00 | 44095.0417 | 0 | 8.308 | 39.95
2020-09-21 01:30 | 44095.0625 | 0 | 8.2276 | 39.95
2020-09-21 02:00 | 44095.0833 | 0 | 8.0946 | 39.95
2020-09-21 02:30 | 44095.1042 | 0 | 8.1346 | 39.95
2020-09-21 03:00 | 44095.125 | 0 | 8.0545 | 39.95
2020-09-21 03:30 | 44095.1458 | 0 | 8.1217 | 39.95
2020-09-21 04:00 | 44095.1667 | 0 | 8.2876 | 39.95
2020-09-21 04:30 | 44095.1875 | 0 | 8.7869 | 39.95
2020-09-21 05:00 | 44095.2083 | 0 | 9.4863 | 39.95
2020-09-21 05:30 | 44095.2292 | 0 | 9.9979 | 39.95
2020-09-21 06:00 | 44095.25 | 0 | 10.7054 | 39.95
2020-09-21 06:30 | 44095.2708 | 0 | 11.0491 | 39.95
2020-09-21 07:00 | 44095.2917 | 0 | 11.0565 | 39.95
2020-09-21 07:30 | 44095.3125 | 0 | 11.5752 | 39.95
2020-09-21 08:00 | 44095.3333 | 0 | 11.5483 | 39.95
2020-09-21 08:30 | 44095.3542 | 0 | 12.132 | 39.95
2020-09-21 09:00 | 44095.375 | 0 | 11.5258 | 39.95
2020-09-21 09:30 | 44095.3958 | 0 | 11.4314 | 39.95
2020-09-21 10:00 | 44095.4167 | 0 | 11.6113 | 39.95
2020-09-21 10:30 | 44095.4375 | 0 | 11.4243 | 39.95
2020-09-21 11:00 | 44095.4583 | 0 | 10.9513 | 39.95
2020-09-21 11:30 | 44095.4792 | 0 | 11.4321 | 39.95
2020-09-21 12:00 | 44095.5 | 0 | 12.6648 | 39.95
2020-09-21 12:30 | 44095.5208 | 0 | 13.2908 | 39.95
2020-09-21 13:00 | 44095.5417 | 0 | 12.3433 | 39.95
2020-09-21 13:30 | 44095.5625 | 0 | 12.5175 | 39.95
2020-09-21 14:00 | 44095.5833 | 0 | 12.9016 | 39.95
2020-09-21 14:30 | 44095.6042 | 0 | 12.8906 | 39.95
2020-09-21 15:00 | 44095.625 | 0 | 12.1953 | 39.95
2020-09-21 15:30 | 44095.6458 | 0 | 11.71 | 39.95
2020-09-21 16:00 | 44095.6667 | 0 | 12.2881 | 39.95
2020-09-21 16:30 | 44095.6875 | 0 | 13.2496 | 39.95
2020-09-21 17:00 | 44095.7083 | 0 | 13.5335 | 39.95
2020-09-21 17:30 | 44095.7292 | 0 | 13.8337 | 39.95
2020-09-21 18:00 | 44095.75 | 0 | 14.3304 | 39.95
2020-09-21 18:30 | 44095.7708 | 0 | 14.7774 | 39.95
2020-09-21 19:00 | 44095.7917 | 0 | 14.4061 | 39.95
2020-09-21 19:30 | 44095.8125 | 0 | 13.9609 | 39.95
2020-09-21 20:00 | 44095.8333 | 0 | 13.7416 | 39.95
2020-09-21 20:30 | 44095.8542 | 0 | 13.2461 | 39.95
2020-09-21 21:00 | 44095.875 | 0 | 12.8129 | 39.95
2020-09-21 21:30 | 44095.8958 | 0 | 12.2682 | 39.95
2020-09-21 22:00 | 44095.9167 | 0 | 11.6943 | 39.95
2020-09-21 22:30 | 44095.9375 | 0 | 10.8875 | 39.95
2020-09-21 23:00 | 44095.9583 | 0 | 10.4744 | 39.95
2020-09-21 23:30 | 44095.9792 | 0 | 9.836 | 39.95
2020-09-22 | 44096 | 0 | 9.1373 | 39.95
2020-09-22 00:30 | 44096.0208 | 0 | 8.7232 | 39.95
2020-09-22 01:00 | 44096.0417 | 0 | 8.516 | 39.95
2020-09-22 01:30 | 44096.0625 | 0 | 8.4771 | 39.95
2020-09-22 02:00 | 44096.0833 | 0 | 8.4361 | 39.95
2020-09-22 02:30 | 44096.1042 | 0 | 8.3394 | 39.95
2020-09-22 03:00 | 44096.125 | 0 | 8.3057 | 39.95
2020-09-22 03:30 | 44096.1458 | 0 | 8.3245 | 39.95
2020-09-22 04:00 | 44096.1667 | 0 | 8.5743 | 39.95
2020-09-22 04:30 | 44096.1875 | 0 | 8.9913 | 39.95
2020-09-22 05:00 | 44096.2083 | 0 | 9.5996 | 39.95
2020-09-22 05:30 | 44096.2292 | 0 | 10.1368 | 39.95
2020-09-22 06:00 | 44096.25 | 0 | 10.8187 | 39.95
2020-09-22 06:30 | 44096.2708 | 0 | 11.3352 | 39.95
2020-09-22 07:00 | 44096.2917 | 0 | 12.3675 | 39.95
2020-09-22 07:30 | 44096.3125 | 0 | 12.7907 | 39.95
2020-09-22 08:00 | 44096.3333 | 0 | 12.5971 | 39.95
2020-09-22 08:30 | 44096.3542 | 0 | 12.4679 | 39.95
2020-09-22 09:00 | 44096.375 | 0 | 12.7633 | 39.95
2020-09-22 09:30 | 44096.3958 | 0 | 12.2919 | 39.95
2020-09-22 10:00 | 44096.4167 | 0 | 12.5343 | 39.95
2020-09-22 10:30 | 44096.4375 | 0 | 11.6846 | 39.95
2020-09-22 11:00 | 44096.4583 | 0 | 10.827 | 39.95
2020-09-22 11:30 | 44096.4792 | 0 | 10.1434 | 39.95
2020-09-22 12:00 | 44096.5 | 0 | 10.2257 | 39.95
2020-09-22 12:30 | 44096.5208 | 0 | 12.326 | 39.95
2020-09-22 13:00 | 44096.5417 | 0 | 11.55 | 39.95
2020-09-22 13:30 | 44096.5625 | 0 | 12.6053 | 39.95
2020-09-22 14:00 | 44096.5833 | 0 | 13.075 | 39.95
2020-09-22 14:30 | 44096.6042 | 0 | 12.289 | 39.95
2020-09-22 15:00 | 44096.625 | 0 | 12.2008 | 39.95
2020-09-22 15:30 | 44096.6458 | 0 | 12.2225 | 39.95
2020-09-22 16:00 | 44096.6667 | 0 | 12.9639 | 39.95
2020-09-22 16:30 | 44096.6875 | 0 | 13.1489 | 39.95
2020-09-22 17:00 | 44096.7083 | 0 | 13.461 | 39.95
2020-09-22 17:30 | 44096.7292 | 0 | 13.9098 | 39.95
2020-09-22 18:00 | 44096.75 | 0 | 14.3763 | 39.95
2020-09-22 18:30 | 44096.7708 | 0 | 14.7208 | 39.95
2020-09-22 19:00 | 44096.7917 | 0 | 14.339 | 39.95
2020-09-22 19:30 | 44096.8125 | 0 | 14.0833 | 39.95
2020-09-22 20:00 | 44096.8333 | 0 | 13.6933 | 39.95
2020-09-22 20:30 | 44096.8542 | 0 | 13.0889 | 39.95
2020-09-22 21:00 | 44096.875 | 0 | 12.5865 | 39.95
2020-09-22 21:30 | 44096.8958 | 0 | 12.2475 | 39.95
2020-09-22 22:00 | 44096.9167 | 0 | 11.5719 | 39.95
2020-09-22 22:30 | 44096.9375 | 0 | 10.7713 | 39.95
2020-09-22 23:00 | 44096.9583 | 0 | 10.1173 | 39.95
2020-09-22 23:30 | 44096.9792 | 0 | 9.5398 | 39.95
2020-09-23 | 44097 | 0 | 8.8448 | 39.95
2020-09-23 00:30 | 44097.0208 | 0 | 8.2899 | 39.95
2020-09-23 01:00 | 44097.0417 | 0 | 8.0464 | 39.95
2020-09-23 01:30 | 44097.0625 | 0 | 7.8684 | 39.95
2020-09-23 02:00 | 44097.0833 | 0 | 7.8723 | 39.95
2020-09-23 02:30 | 44097.1042 | 0 | 7.7923 | 39.95
2020-09-23 03:00 | 44097.125 | 0 | 7.738 | 39.95
2020-09-23 03:30 | 44097.1458 | 0 | 7.7571 | 39.95
2020-09-23 04:00 | 44097.1667 | 0 | 8.0272 | 39.95
2020-09-23 04:30 | 44097.1875 | 0 | 8.3247 | 39.95
2020-09-23 05:00 | 44097.2083 | 0 | 8.9386 | 39.95
2020-09-23 05:30 | 44097.2292 | 0 | 9.4108 | 39.95
2020-09-23 06:00 | 44097.25 | 0 | 9.9996 | 39.95
2020-09-23 06:30 | 44097.2708 | 0 | 10.1157 | 39.95
2020-09-23 07:00 | 44097.2917 | 0 | 10.3855 | 39.95
2020-09-23 07:30 | 44097.3125 | 0 | 10.0029 | 39.95
2020-09-23 08:00 | 44097.3333 | 0 | 10.716 | 39.95
2020-09-23 08:30 | 44097.3542 | 0 | 10.123 | 39.95
2020-09-23 09:00 | 44097.375 | 0 | 9.3617 | 39.95
2020-09-23 09:30 | 44097.3958 | 0 | 9.4441 | 39.95
2020-09-23 10:00 | 44097.4167 | 0 | 9.3743 | 39.95
2020-09-23 10:30 | 44097.4375 | 0 | 9.1396 | 39.95
2020-09-23 11:00 | 44097.4583 | 0 | 9.2422 | 39.95
2020-09-23 11:30 | 44097.4792 | 0 | 9.4318 | 39.95
2020-09-23 12:00 | 44097.5 | 0 | 9.5064 | 39.95
2020-09-23 12:30 | 44097.5208 | 0 | 9.6784 | 39.95
2020-09-23 13:00 | 44097.5417 | 0 | 9.7262 | 39.95
2020-09-23 13:30 | 44097.5625 | 0 | 10.0682 | 39.95
2020-09-23 14:00 | 44097.5833 | 0 | 10.5839 | 39.95
2020-09-23 14:30 | 44097.6042 | 0 | 10.8969 | 39.95
2020-09-23 15:00 | 44097.625 | 0 | 11.1982 | 39.95
2020-09-23 15:30 | 44097.6458 | 0 | 11.6648 | 39.95
2020-09-23 16:00 | 44097.6667 | 0 | 12.0793 | 39.95
2020-09-23 16:30 | 44097.6875 | 0 | 12.7336 | 39.95
2020-09-23 17:00 | 44097.7083 | 0 | 12.7461 | 39.95
2020-09-23 17:30 | 44097.7292 | 0 | 12.9684 | 39.95
2020-09-23 18:00 | 44097.75 | 0 | 13.4859 | 39.95
2020-09-23 18:30 | 44097.7708 | 0 | 13.6022 | 39.95
2020-09-23 19:00 | 44097.7917 | 0 | 13.3248 | 39.95
2020-09-23 19:30 | 44097.8125 | 0 | 13.0306 | 39.95
2020-09-23 20:00 | 44097.8333 | 0 | 12.7406 | 39.95
2020-09-23 20:30 | 44097.8542 | 0 | 12.1715 | 39.95
2020-09-23 21:00 | 44097.875 | 0 | 11.6944 | 39.95
2020-09-23 21:30 | 44097.8958 | 0 | 11.454 | 39.95
2020-09-23 22:00 | 44097.9167 | 0 | 11.009 | 39.95
2020-09-23 22:30 | 44097.9375 | 0 | 10.1696 | 39.95
2020-09-23 23:00 | 44097.9583 | 0 | 9.7012 | 39.95
2020-09-23 23:30 | 44097.9792 | 0 | 9.1606 | 39.95
2020-09-24 | 44098 | 0 | 8.5199 | 39.95
2020-09-24 00:30 | 44098.0208 | 0 | 8.1113 | 39.95
2020-09-24 01:00 | 44098.0417 | 0 | 7.9711 | 39.95
2020-09-24 01:30 | 44098.0625 | 0 | 7.9039 | 39.95
2020-09-24 02:00 | 44098.0833 | 0 | 7.8237 | 39.95
2020-09-24 02:30 | 44098.1042 | 0 | 7.7159 | 39.95
2020-09-24 03:00 | 44098.125 | 0 | 7.662 | 39.95
2020-09-24 03:30 | 44098.1458 | 0 | 7.7642 | 39.95
2020-09-24 04:00 | 44098.1667 | 0 | 7.9062 | 39.95
2020-09-24 04:30 | 44098.1875 | 0 | 8.3121 | 39.95
2020-09-24 05:00 | 44098.2083 | 0 | 8.7959 | 39.95
2020-09-24 05:30 | 44098.2292 | 0 | 9.1382 | 39.95
2020-09-24 06:00 | 44098.25 | 0 | 9.5721 | 39.95
2020-09-24 06:30 | 44098.2708 | 0 | 9.7463 | 39.95
2020-09-24 07:00 | 44098.2917 | 0 | 10.009 | 39.95
2020-09-24 07:30 | 44098.3125 | 0 | 9.9546 | 39.95
2020-09-24 08:00 | 44098.3333 | 0 | 9.9587 | 39.95
2020-09-24 08:30 | 44098.3542 | 0 | 9.9358 | 39.95
2020-09-24 09:00 | 44098.375 | 0 | 9.4706 | 39.95
2020-09-24 09:30 | 44098.3958 | 0 | 9.631 | 39.95
2020-09-24 10:00 | 44098.4167 | 0 | 9.5548 | 39.95
2020-09-24 10:30 | 44098.4375 | 0 | 9.4652 | 39.95
2020-09-24 11:00 | 44098.4583 | 0 | 9.5454 | 39.95
2020-09-24 11:30 | 44098.4792 | 0 | 9.4691 | 39.95
2020-09-24 12:00 | 44098.5 | 0 | 9.5006 | 39.95
2020-09-24 12:30 | 44098.5208 | 0 | 9.6163 | 39.95
2020-09-24 13:00 | 44098.5417 | 0 | 9.9279 | 39.95
2020-09-24 13:30 | 44098.5625 | 0 | 10.1037 | 39.95
2020-09-24 14:00 | 44098.5833 | 0 | 10.3705 | 39.95
2020-09-24 14:30 | 44098.6042 | 0 | 10.9017 | 39.95
2020-09-24 15:00 | 44098.625 | 0 | 11.2992 | 39.95
2020-09-24 15:30 | 44098.6458 | 0 | 12.0314 | 39.95
2020-09-24 16:00 | 44098.6667 | 0 | 12.4546 | 39.95
2020-09-24 16:30 | 44098.6875 | 0 | 12.8302 | 39.95
2020-09-24 17:00 | 44098.7083 | 0 | 13.1257 | 39.95
2020-09-24 17:30 | 44098.7292 | 0 | 13.3108 | 39.95
2020-09-24 18:00 | 44098.75 | 0 | 13.409 | 39.95
2020-09-24 18:30 | 44098.7708 | 0 | 13.6099 | 39.95
2020-09-24 19:00 | 44098.7917 | 0 | 13.4424 | 39.95
2020-09-24 19:30 | 44098.8125 | 0 | 13.0718 | 39.95
2020-09-24 20:00 | 44098.8333 | 0 | 12.8553 | 39.95
2020-09-24 20:30 | 44098.8542 | 0 | 12.3532 | 39.95
2020-09-24 21:00 | 44098.875 | 0 | 11.8453 | 39.95
2020-09-24 21:30 | 44098.8958 | 0 | 11.5253 | 39.95
2020-09-24 22:00 | 44098.9167 | 0 | 11.1369 | 39.95
2020-09-24 22:30 | 44098.9375 | 0 | 10.4991 | 39.95
2020-09-24 23:00 | 44098.9583 | 0 | 10.0106 | 39.95
2020-09-24 23:30 | 44098.9792 | 0 | 9.726 | 39.95
2020-09-25 | 44099 | 0 | 9.127 | 39.95
2020-09-25 00:30 | 44099.0208 | 0 | 8.663 | 39.95
2020-09-25 01:00 | 44099.0417 | 0 | 8.4396 | 39.95
2020-09-25 01:30 | 44099.0625 | 0 | 8.0519 | 39.95
2020-09-25 02:00 | 44099.0833 | 0 | 7.9746 | 39.95
2020-09-25 02:30 | 44099.1042 | 0 | 7.6709 | 39.95
2020-09-25 03:00 | 44099.125 | 0 | 7.4926 | 39.95
2020-09-25 03:30 | 44099.1458 | 0 | 7.5799 | 39.95
2020-09-25 04:00 | 44099.1667 | 0 | 7.4869 | 39.95
2020-09-25 04:30 | 44099.1875 | 0 | 7.5485 | 39.95
2020-09-25 05:00 | 44099.2083 | 0 | 7.7685 | 39.95
2020-09-25 05:30 | 44099.2292 | 0 | 7.8871 | 39.95
2020-09-25 06:00 | 44099.25 | 0 | 7.8369 | 39.95
2020-09-25 06:30 | 44099.2708 | 0 | 7.6131 | 39.95
2020-09-25 07:00 | 44099.2917 | 0 | 7.4265 | 39.95
2020-09-25 07:30 | 44099.3125 | 0 | 7.2319 | 39.95
2020-09-25 08:00 | 44099.3333 | 0 | 7.2134 | 39.95
2020-09-25 08:30 | 44099.3542 | 0 | 6.8907 | 39.95
2020-09-25 09:00 | 44099.375 | 0 | 6.4055 | 39.95
2020-09-25 09:30 | 44099.3958 | 0 | 6.0397 | 39.95
2020-09-25 10:00 | 44099.4167 | 0 | 5.8564 | 39.95
2020-09-25 10:30 | 44099.4375 | 0 | 5.609 | 39.95
2020-09-25 11:00 | 44099.4583 | 0 | 5.4454 | 39.95
2020-09-25 11:30 | 44099.4792 | 0 | 5.338 | 39.95
2020-09-25 12:00 | 44099.5 | 0 | 5.2575 | 39.95
2020-09-25 12:30 | 44099.5208 | 0 | 5.2797 | 39.95
2020-09-25 13:00 | 44099.5417 | 0 | 5.3769 | 39.95
2020-09-25 13:30 | 44099.5625 | 0 | 5.6411 | 39.95
2020-09-25 14:00 | 44099.5833 | 0 | 5.8158 | 39.95
2020-09-25 14:30 | 44099.6042 | 0 | 6.4426 | 39.95
2020-09-25 15:00 | 44099.625 | 0 | 6.8718 | 39.95
2020-09-25 15:30 | 44099.6458 | 0 | 7.515 | 39.95
2020-09-25 16:00 | 44099.6667 | 0 | 8.228 | 39.95
2020-09-25 16:30 | 44099.6875 | 0 | 8.9585 | 39.95
2020-09-25 17:00 | 44099.7083 | 0 | 9.5251 | 39.95
2020-09-25 17:30 | 44099.7292 | 0 | 9.9561 | 39.95
2020-09-25 18:00 | 44099.75 | 0 | 10.4662 | 39.95
2020-09-25 18:30 | 44099.7708 | 0 | 10.7624 | 39.95
2020-09-25 19:00 | 44099.7917 | 0 | 10.4117 | 39.95
2020-09-25 19:30 | 44099.8125 | 0 | 10.2488 | 39.95
2020-09-25 20:00 | 44099.8333 | 0 | 10.0381 | 39.95
2020-09-25 20:30 | 44099.8542 | 0 | 9.698 | 39.95
2020-09-25 21:00 | 44099.875 | 0 | 9.3085 | 39.95
2020-09-25 21:30 | 44099.8958 | 0 | 9.0763 | 39.95
2020-09-25 22:00 | 44099.9167 | 0 | 8.7478 | 39.95
2020-09-25 22:30 | 44099.9375 | 0 | 8.2401 | 39.95
2020-09-25 23:00 | 44099.9583 | 0 | 7.9555 | 39.95
2020-09-25 23:30 | 44099.9792 | 0 | 7.5441 | 39.95
2020-09-26 | 44100 | 0 | 7.2337 | 39.95
2020-09-26 00:30 | 44100.0208 | 0 | 6.9638 | 39.95
2020-09-26 01:00 | 44100.0417 | 0 | 6.7654 | 39.95
2020-09-26 01:30 | 44100.0625 | 0 | 6.724 | 39.95
2020-09-26 02:00 | 44100.0833 | 0 | 6.7816 | 39.95
2020-09-26 02:30 | 44100.1042 | 0 | 6.7147 | 39.95
2020-09-26 03:00 | 44100.125 | 0 | 6.6811 | 39.95
2020-09-26 03:30 | 44100.1458 | 0 | 6.6105 | 39.95
2020-09-26 04:00 | 44100.1667 | 0 | 6.4633 | 39.95
2020-09-26 04:30 | 44100.1875 | 0 | 6.5472 | 39.95
2020-09-26 05:00 | 44100.2083 | 0 | 6.6385 | 39.95
2020-09-26 05:30 | 44100.2292 | 0 | 6.7407 | 39.95
2020-09-26 06:00 | 44100.25 | 0 | 6.7017 | 39.95
2020-09-26 06:30 | 44100.2708 | 0 | 6.3884 | 39.95
2020-09-26 07:00 | 44100.2917 | 0 | 6.1385 | 39.95
2020-09-26 07:30 | 44100.3125 | 0 | 5.9573 | 39.95
2020-09-26 08:00 | 44100.3333 | 0 | 5.9682 | 39.95
2020-09-26 08:30 | 44100.3542 | 0 | 5.676 | 39.95
2020-09-26 09:00 | 44100.375 | 0 | 5.3798 | 39.95
2020-09-26 09:30 | 44100.3958 | 0 | 5.2907 | 39.95
2020-09-26 10:00 | 44100.4167 | 0 | 5.1046 | 39.95
2020-09-26 10:30 | 44100.4375 | 0 | 4.8704 | 39.95
2020-09-26 11:00 | 44100.4583 | 0 | 4.8888 | 39.95
2020-09-26 11:30 | 44100.4792 | 0 | 4.7249 | 39.95
2020-09-26 12:00 | 44100.5 | 0 | 4.6435 | 39.95
2020-09-26 12:30 | 44100.5208 | 0 | 4.7029 | 39.95
2020-09-26 13:00 | 44100.5417 | 0 | 4.9751 | 39.95
2020-09-26 13:30 | 44100.5625 | 0 | 5.2202 | 39.95
2020-09-26 14:00 | 44100.5833 | 0 | 5.5707 | 39.95
2020-09-26 14:30 | 44100.6042 | 0 | 6.1233 | 39.95
2020-09-26 15:00 | 44100.625 | 0 | 6.7426 | 39.95
2020-09-26 15:30 | 44100.6458 | 0 | 7.3619 | 39.95
2020-09-26 16:00 | 44100.6667 | 0 | 8.0216 | 39.95
2020-09-26 16:30 | 44100.6875 | 0 | 8.9103 | 39.95
2020-09-26 17:00 | 44100.7083 | 0 | 9.4823 | 39.95
2020-09-26 17:30 | 44100.7292 | 0 | 10.0346 | 39.95
2020-09-26 18:00 | 44100.75 | 0 | 10.7915 | 39.95
2020-09-26 18:30 | 44100.7708 | 0 | 10.8965 | 39.95
2020-09-26 19:00 | 44100.7917 | 0 | 10.8068 | 39.95
2020-09-26 19:30 | 44100.8125 | 0 | 10.3592 | 39.95
2020-09-26 20:00 | 44100.8333 | 0 | 10.1145 | 39.95
2020-09-26 20:30 | 44100.8542 | 0 | 9.6156 | 39.95
2020-09-26 21:00 | 44100.875 | 0 | 9.3047 | 39.95
2020-09-26 21:30 | 44100.8958 | 0 | 8.9808 | 39.95
2020-09-26 22:00 | 44100.9167 | 0 | 8.6663 | 39.95
2020-09-26 22:30 | 44100.9375 | 0 | 8.0472 | 39.95
2020-09-26 23:00 | 44100.9583 | 0 | 7.6046 | 39.95
2020-09-26 23:30 | 44100.9792 | 0 | 7.241 | 39.95
2020-09-27 | 44101 | 0 | 7.1483 | 39.95
2020-09-27 00:30 | 44101.0208 | 0 | 6.951 | 39.95
2020-09-27 01:00 | 44101.0417 | 0 | 6.7513 | 39.95
2020-09-27 01:30 | 44101.0625 | 0 | 6.709 | 39.95
2020-09-27 02:00 | 44101.0833 | 0 | 6.8079 | 39.95
2020-09-27 02:30 | 44101.1042 | 0 | 6.804 | 39.95
2020-09-27 03:00 | 44101.125 | 0 | 6.8654 | 39.95
2020-09-27 03:30 | 44101.1458 | 0 | 6.9829 | 39.95
2020-09-27 04:00 | 44101.1667 | 0 | 7.1424 | 39.95
2020-09-27 04:30 | 44101.1875 | 0 | 7.4408 | 39.95
2020-09-27 05:00 | 44101.2083 | 0 | 8.0104 | 39.95
2020-09-27 05:30 | 44101.2292 | 0 | 8.5796 | 39.95
2020-09-27 06:00 | 44101.25 | 0 | 9.206 | 39.95
2020-09-27 06:30 | 44101.2708 | 0 | 9.4836 | 39.95
2020-09-27 07:00 | 44101.2917 | 0 | 9.4097 | 39.95
2020-09-27 07:30 | 44101.3125 | 0 | 9.2025 | 39.95
2020-09-27 08:00 | 44101.3333 | 0 | 8.9886 | 39.95
2020-09-27 08:30 | 44101.3542 | 0 | 8.6705 | 39.95
2020-09-27 09:00 | 44101.375 | 0 | 8.4139 | 39.95
2020-09-27 09:30 | 44101.3958 | 0 | 8.7677 | 39.95
2020-09-27 10:00 | 44101.4167 | 0 | 9.0798 | 39.95
2020-09-27 10:30 | 44101.4375 | 0 | 9.7524 | 39.95
2020-09-27 11:00 | 44101.4583 | 0 | 11.0027 | 39.95
2020-09-27 11:30 | 44101.4792 | 0 | 9.3352 | 39.95
2020-09-27 12:00 | 44101.5 | 0 | 9.9576 | 39.95
2020-09-27 12:30 | 44101.5208 | 0 | 8.7058 | 39.95
2020-09-27 13:00 | 44101.5417 | 0 | 9.6757 | 39.95
2020-09-27 13:30 | 44101.5625 | 0 | 9.6235 | 39.95
2020-09-27 14:00 | 44101.5833 | 0 | 9.2493 | 39.95
2020-09-27 14:30 | 44101.6042 | 0 | 9.9785 | 39.95
2020-09-27 15:00 | 44101.625 | 0 | 10.2031 | 39.95
2020-09-27 15:30 | 44101.6458 | 0 | 10.7447 | 39.95
2020-09-27 16:00 | 44101.6667 | 0 | 10.9401 | 39.95
2020-09-27 16:30 | 44101.6875 | 0 | 10.983 | 39.95
2020-09-27 17:00 | 44101.7083 | 0 | 11.4566 | 39.95
2020-09-27 17:30 | 44101.7292 | 0 | 12.065 | 39.95
2020-09-27 18:00 | 44101.75 | 0 | 12.7873 | 39.95
2020-09-27 18:30 | 44101.7708 | 0 | 13.0757 | 39.95
2020-09-27 19:00 | 44101.7917 | 0 | 12.8784 | 39.95
2020-09-27 19:30 | 44101.8125 | 0 | 12.5338 | 39.95
2020-09-27 20:00 | 44101.8333 | 0 | 12.3105 | 39.95
2020-09-27 20:30 | 44101.8542 | 0 | 11.8846 | 39.95
2020-09-27 21:00 | 44101.875 | 0 | 11.2753 | 39.95
2020-09-27 21:30 | 44101.8958 | 0 | 10.9132 | 39.95
2020-09-27 22:00 | 44101.9167 | 0 | 10.3081 | 39.95
2020-09-27 22:30 | 44101.9375 | 0 | 9.6578 | 39.95
2020-09-27 23:00 | 44101.9583 | 0 | 9.1399 | 39.95
2020-09-27 23:30 | 44101.9792 | 0 | 8.6481 | 39.95
2020-09-28 | 44102 | 0 | 8.2482 | 39.95
2020-09-28 00:30 | 44102.0208 | 0 | 7.9129 | 39.95
2020-09-28 01:00 | 44102.0417 | 0 | 7.5631 | 39.95
2020-09-28 01:30 | 44102.0625 | 0 | 7.6508 | 39.95
2020-09-28 02:00 | 44102.0833 | 0 | 7.4789 | 39.95
2020-09-28 02:30 | 44102.1042 | 0 | 7.5711 | 39.95
2020-09-28 03:00 | 44102.125 | 0 | 7.4514 | 39.95
2020-09-28 03:30 | 44102.1458 | 0 | 7.3474 | 39.95
2020-09-28 04:00 | 44102.1667 | 0 | 7.5897 | 39.95
2020-09-28 04:30 | 44102.1875 | 0 | 7.9132 | 39.95
2020-09-28 05:00 | 44102.2083 | 0 | 8.5537 | 39.95
2020-09-28 05:30 | 44102.2292 | 0 | 9.116 | 39.95
2020-09-28 06:00 | 44102.25 | 0 | 9.5525 | 39.95
2020-09-28 06:30 | 44102.2708 | 0 | 10.2392 | 39.95
2020-09-28 07:00 | 44102.2917 | 0 | 10.5125 | 39.95
2020-09-28 07:30 | 44102.3125 | 0 | 10.1321 | 39.95
2020-09-28 08:00 | 44102.3333 | 0 | 10.4638 | 39.95
2020-09-28 08:30 | 44102.3542 | 0 | 9.481 | 39.95
2020-09-28 09:00 | 44102.375 | 0 | 10.3811 | 39.95
2020-09-28 09:30 | 44102.3958 | 0 | 9.8529 | 39.95
2020-09-28 10:00 | 44102.4167 | 0 | 10.5265 | 39.95
2020-09-28 10:30 | 44102.4375 | 0 | 9.9382 | 39.95
2020-09-28 11:00 | 44102.4583 | 0 | 9.2724 | 39.95
2020-09-28 11:30 | 44102.4792 | 0 | 9.7895 | 39.95
2020-09-28 12:00 | 44102.5 | 0 | 9.2602 | 39.95
2020-09-28 12:30 | 44102.5208 | 0 | 9.3479 | 39.95
2020-09-28 13:00 | 44102.5417 | 0 | 10.2302 | 39.95
2020-09-28 13:30 | 44102.5625 | 0 | 10.6073 | 39.95
2020-09-28 14:00 | 44102.5833 | 0 | 10.1145 | 39.95
2020-09-28 14:30 | 44102.6042 | 0 | 10.2251 | 39.95
2020-09-28 15:00 | 44102.625 | 0 | 10.0435 | 39.95
2020-09-28 15:30 | 44102.6458 | 0 | 10.6582 | 39.95
2020-09-28 16:00 | 44102.6667 | 0 | 10.6009 | 39.95
2020-09-28 16:30 | 44102.6875 | 0 | 11.0384 | 39.95
2020-09-28 17:00 | 44102.7083 | 0 | 11.5016 | 39.95
2020-09-28 17:30 | 44102.7292 | 0 | 12.014 | 39.95
2020-09-28 18:00 | 44102.75 | 0 | 12.835 | 39.95
2020-09-28 18:30 | 44102.7708 | 0 | 13.2303 | 39.95
2020-09-28 19:00 | 44102.7917 | 0 | 12.8578 | 39.95
2020-09-28 19:30 | 44102.8125 | 0 | 12.6552 | 39.95
2020-09-28 20:00 | 44102.8333 | 0 | 12.5479 | 39.95
2020-09-28 20:30 | 44102.8542 | 0 | 12.1392 | 39.95
2020-09-28 21:00 | 44102.875 | 0 | 11.47 | 39.95
2020-09-28 21:30 | 44102.8958 | 0 | 10.9709 | 39.95
2020-09-28 22:00 | 44102.9167 | 0 | 10.537 | 39.95
2020-09-28 22:30 | 44102.9375 | 0 | 9.8446 | 39.95
2020-09-28 23:00 | 44102.9583 | 0 | 9.2116 | 39.95
2020-09-28 23:30 | 44102.9792 | 0 | 8.7507 | 39.95
2020-09-29 | 44103 | 0 | 8.1566 | 39.95
2020-09-29 00:30 | 44103.0208 | 0 | 7.7306 | 39.95
2020-09-29 01:00 | 44103.0417 | 0 | 7.4763 | 39.95
2020-09-29 01:30 | 44103.0625 | 0 | 7.4814 | 39.95
2020-09-29 02:00 | 44103.0833 | 0 | 7.4888 | 39.95
2020-09-29 02:30 | 44103.1042 | 0 | 7.4146 | 39.95
2020-09-29 03:00 | 44103.125 | 0 | 7.4012 | 39.95
2020-09-29 03:30 | 44103.1458 | 0 | 7.4668 | 39.95
2020-09-29 04:00 | 44103.1667 | 0 | 7.7795 | 39.95
2020-09-29 04:30 | 44103.1875 | 0 | 8.0848 | 39.95
2020-09-29 05:00 | 44103.2083 | 0 | 8.6815 | 39.95
2020-09-29 05:30 | 44103.2292 | 0 | 9.2454 | 39.95
2020-09-29 06:00 | 44103.25 | 0 | 10.1697 | 39.95
2020-09-29 06:30 | 44103.2708 | 0 | 10.0995 | 39.95
2020-09-29 07:00 | 44103.2917 | 0 | 10.1242 | 39.95
2020-09-29 07:30 | 44103.3125 | 0 | 10.1178 | 39.95
2020-09-29 08:00 | 44103.3333 | 0 | 9.7996 | 39.95
2020-09-29 08:30 | 44103.3542 | 0 | 9.3986 | 39.95
2020-09-29 09:00 | 44103.375 | 0 | 8.8494 | 39.95
2020-09-29 09:30 | 44103.3958 | 0 | 9.0553 | 39.95
2020-09-29 10:00 | 44103.4167 | 0 | 9.3273 | 39.95
2020-09-29 10:30 | 44103.4375 | 0 | 9.4302 | 39.95
2020-09-29 11:00 | 44103.4583 | 0 | 9.5021 | 39.95
2020-09-29 11:30 | 44103.4792 | 0 | 9.0962 | 39.95
2020-09-29 12:00 | 44103.5 | 0 | 10.0639 | 39.95
2020-09-29 12:30 | 44103.5208 | 0 | 9.1986 | 39.95
2020-09-29 13:00 | 44103.5417 | 0 | 9.3535 | 39.95
2020-09-29 13:30 | 44103.5625 | 0 | 10.323 | 39.95
2020-09-29 14:00 | 44103.5833 | 0 | 9.7701 | 39.95
2020-09-29 14:30 | 44103.6042 | 0 | 10.0461 | 39.95
2020-09-29 15:00 | 44103.625 | 0 | 11.0176 | 39.95
2020-09-29 15:30 | 44103.6458 | 0 | 10.5387 | 39.95
2020-09-29 16:00 | 44103.6667 | 0 | 10.8161 | 39.95
2020-09-29 16:30 | 44103.6875 | 0 | 11.5452 | 39.95
2020-09-29 17:00 | 44103.7083 | 0 | 11.9796 | 39.95
2020-09-29 17:30 | 44103.7292 | 0 | 12.3018 | 39.95
2020-09-29 18:00 | 44103.75 | 0 | 12.8948 | 39.95
2020-09-29 18:30 | 44103.7708 | 0 | 13.0736 | 39.95
2020-09-29 19:00 | 44103.7917 | 0 | 12.7273 | 39.95
2020-09-29 19:30 | 44103.8125 | 0 | 12.525 | 39.95
2020-09-29 20:00 | 44103.8333 | 0 | 12.5023 | 39.95
2020-09-29 20:30 | 44103.8542 | 0 | 11.9305 | 39.95
2020-09-29 21:00 | 44103.875 | 0 | 11.3731 | 39.95
2020-09-29 21:30 | 44103.8958 | 0 | 10.9595 | 39.95
2020-09-29 22:00 | 44103.9167 | 0 | 10.4032 | 39.95
2020-09-29 22:30 | 44103.9375 | 0 | 9.7883 | 39.95
2020-09-29 23:00 | 44103.9583 | 0 | 9.192 | 39.95
2020-09-29 23:30 | 44103.9792 | 0 | 8.739 | 39.95
2020-09-30 | 44104 | 0 | 8.2485 | 39.95
2020-09-30 00:30 | 44104.0208 | 0 | 7.818 | 39.95
2020-09-30 01:00 | 44104.0417 | 0 | 7.6637 | 39.95
2020-09-30 01:30 | 44104.0625 | 0 | 7.6133 | 39.95
2020-09-30 02:00 | 44104.0833 | 0 | 7.5615 | 39.95
2020-09-30 02:30 | 44104.1042 | 0 | 7.5577 | 39.95
2020-09-30 03:00 | 44104.125 | 0 | 7.5263 | 39.95
2020-09-30 03:30 | 44104.1458 | 0 | 7.634 | 39.95
2020-09-30 04:00 | 44104.1667 | 0 | 7.7722 | 39.95
2020-09-30 04:30 | 44104.1875 | 0 | 8.1364 | 39.95
2020-09-30 05:00 | 44104.2083 | 0 | 8.6189 | 39.95
2020-09-30 05:30 | 44104.2292 | 0 | 9.0612 | 39.95
2020-09-30 06:00 | 44104.25 | 0 | 9.6657 | 39.95
2020-09-30 06:30 | 44104.2708 | 0 | 9.6906 | 39.95
2020-09-30 07:00 | 44104.2917 | 0 | 9.7684 | 39.95
2020-09-30 07:30 | 44104.3125 | 0 | 9.9873 | 39.95
2020-09-30 08:00 | 44104.3333 | 0 | 9.6925 | 39.95
2020-09-30 08:30 | 44104.3542 | 0 | 9.4982 | 39.95
2020-09-30 09:00 | 44104.375 | 0 | 9.0295 | 39.95
2020-09-30 09:30 | 44104.3958 | 0 | 9.1324 | 39.95
2020-09-30 10:00 | 44104.4167 | 0 | 8.8879 | 39.95
2020-09-30 10:30 | 44104.4375 | 0 | 8.8572 | 39.95
2020-09-30 11:00 | 44104.4583 | 0 | 8.9212 | 39.95
2020-09-30 11:30 | 44104.4792 | 0 | 8.8364 | 39.95
2020-09-30 12:00 | 44104.5 | 0 | 8.7822 | 39.95
2020-09-30 12:30 | 44104.5208 | 0 | 9.2689 | 39.95
2020-09-30 13:00 | 44104.5417 | 0 | 9.206 | 39.95
2020-09-30 13:30 | 44104.5625 | 0 | 9.5808 | 39.95
2020-09-30 14:00 | 44104.5833 | 0 | 9.967 | 39.95
2020-09-30 14:30 | 44104.6042 | 0 | 11.4875 | 39.95
2020-09-30 15:00 | 44104.625 | 0 | 12.4717 | 39.95
2020-09-30 15:30 | 44104.6458 | 0 | 10.3443 | 39.95
2020-09-30 16:00 | 44104.6667 | 0 | 12.0331 | 39.95
2020-09-30 16:30 | 44104.6875 | 0 | 11.7084 | 39.95
2020-09-30 17:00 | 44104.7083 | 0 | 12.1673 | 39.95
2020-09-30 17:30 | 44104.7292 | 0 | 12.5758 | 39.95
2020-09-30 18:00 | 44104.75 | 0 | 12.9788 | 39.95
2020-09-30 18:30 | 44104.7708 | 0 | 13.2413 | 39.95
2020-09-30 19:00 | 44104.7917 | 0 | 13.0027 | 39.95
2020-09-30 19:30 | 44104.8125 | 0 | 12.7382 | 39.95
2020-09-30 20:00 | 44104.8333 | 0 | 12.7403 | 39.95
2020-09-30 20:30 | 44104.8542 | 0 | 12.1877 | 39.95
2020-09-30 21:00 | 44104.875 | 0 | 11.5216 | 39.95
2020-09-30 21:30 | 44104.8958 | 0 | 11.1925 | 39.95
2020-09-30 22:00 | 44104.9167 | 0 | 10.6658 | 39.95
2020-09-30 22:30 | 44104.9375 | 0 | 9.8098 | 39.95
2020-09-30 23:00 | 44104.9583 | 0 | 9.1584 | 39.95
2020-09-30 23:30 | 44104.9792 | 0 | 8.7705 | 39.95
2020-10-01 | 44105 | 0 | 8.2872 | 39.95
2020-10-01 00:30 | 44105.0208 | 0 | 8.0171 | 39.95
2020-10-01 01:00 | 44105.0417 | 0 | 7.7002 | 39.95
2020-10-01 01:30 | 44105.0625 | 0 | 7.7549 | 39.95
2020-10-01 02:00 | 44105.0833 | 0 | 7.6749 | 39.95
2020-10-01 02:30 | 44105.1042 | 0 | 7.5819 | 39.95
2020-10-01 03:00 | 44105.125 | 0 | 7.6211 | 39.95
2020-10-01 03:30 | 44105.1458 | 0 | 7.6321 | 39.95
2020-10-01 04:00 | 44105.1667 | 0 | 7.6603 | 39.95
2020-10-01 04:30 | 44105.1875 | 0 | 8.1196 | 39.95
2020-10-01 05:00 | 44105.2083 | 0 | 8.7617 | 39.95
2020-10-01 05:30 | 44105.2292 | 0 | 9.082 | 39.95
2020-10-01 06:00 | 44105.25 | 0 | 9.5009 | 39.95
2020-10-01 06:30 | 44105.2708 | 0 | 9.7016 | 39.95
2020-10-01 07:00 | 44105.2917 | 0 | 9.7631 | 39.95
2020-10-01 07:30 | 44105.3125 | 0 | 9.9011 | 39.95
2020-10-01 08:00 | 44105.3333 | 0 | 9.8075 | 39.95
2020-10-01 08:30 | 44105.3542 | 0 | 9.5226 | 39.95
2020-10-01 09:00 | 44105.375 | 0 | 9.3425 | 39.95
2020-10-01 09:30 | 44105.3958 | 0 | 9.2568 | 39.95
2020-10-01 10:00 | 44105.4167 | 0 | 9.3556 | 39.95
2020-10-01 10:30 | 44105.4375 | 0 | 9.4899 | 39.95
2020-10-01 11:00 | 44105.4583 | 0 | 9.3959 | 39.95
2020-10-01 11:30 | 44105.4792 | 0 | 9.4172 | 39.95
2020-10-01 12:00 | 44105.5 | 0 | 9.3523 | 39.95
2020-10-01 12:30 | 44105.5208 | 0 | 9.0839 | 39.95
2020-10-01 13:00 | 44105.5417 | 0 | 9.3224 | 39.95
2020-10-01 13:30 | 44105.5625 | 0 | 9.589 | 39.95
2020-10-01 14:00 | 44105.5833 | 0 | 9.7897 | 39.95
2020-10-01 14:30 | 44105.6042 | 0 | 10.3155 | 39.95
2020-10-01 15:00 | 44105.625 | 0 | 10.944 | 39.95
2020-10-01 15:30 | 44105.6458 | 0 | 11.3974 | 39.95
2020-10-01 16:00 | 44105.6667 | 0 | 11.7766 | 39.95
2020-10-01 16:30 | 44105.6875 | 0 | 12.1325 | 39.95
2020-10-01 17:00 | 44105.7083 | 0 | 12.1674 | 39.95
2020-10-01 17:30 | 44105.7292 | 0 | 12.3028 | 39.95
2020-10-01 18:00 | 44105.75 | 0 | 12.3672 | 39.95
2020-10-01 18:30 | 44105.7708 | 0 | 12.9308 | 39.95
2020-10-01 19:00 | 44105.7917 | 0 | 12.7331 | 39.95
2020-10-01 19:30 | 44105.8125 | 0 | 12.5827 | 39.95
2020-10-01 20:00 | 44105.8333 | 0 | 12.4799 | 39.95
2020-10-01 20:30 | 44105.8542 | 0 | 11.8722 | 39.95
2020-10-01 21:00 | 44105.875 | 0 | 11.5773 | 39.95
2020-10-01 21:30 | 44105.8958 | 0 | 11.3607 | 39.95
2020-10-01 22:00 | 44105.9167 | 0 | 11.0345 | 39.95
2020-10-01 22:30 | 44105.9375 | 0 | 10.2633 | 39.95
2020-10-01 23:00 | 44105.9583 | 0 | 9.6603 | 39.95
2020-10-01 23:30 | 44105.9792 | 0 | 9.1618 | 39.95
2020-10-02 | 44106 | 0 | 8.5383 | 39.95
2020-10-02 00:30 | 44106.0208 | 0 | 8.1619 | 39.95
2020-10-02 01:00 | 44106.0417 | 0 | 7.8165 | 39.95
2020-10-02 01:30 | 44106.0625 | 0 | 7.7384 | 39.95
2020-10-02 02:00 | 44106.0833 | 0 | 7.5911 | 39.95
2020-10-02 02:30 | 44106.1042 | 0 | 7.595 | 39.95
2020-10-02 03:00 | 44106.125 | 0 | 7.4887 | 39.95
2020-10-02 03:30 | 44106.1458 | 0 | 7.4388 | 39.95
2020-10-02 04:00 | 44106.1667 | 0 | 7.4684 | 39.95
2020-10-02 04:30 | 44106.1875 | 0 | 7.5689 | 39.95
2020-10-02 05:00 | 44106.2083 | 0 | 7.6491 | 39.95
2020-10-02 05:30 | 44106.2292 | 0 | 7.6934 | 39.95
2020-10-02 06:00 | 44106.25 | 0 | 7.7403 | 39.95
2020-10-02 06:30 | 44106.2708 | 0 | 7.5052 | 39.95
2020-10-02 07:00 | 44106.2917 | 0 | 7.3399 | 39.95
2020-10-02 07:30 | 44106.3125 | 0 | 7.5493 | 39.95
2020-10-02 08:00 | 44106.3333 | 0 | 7.8876 | 39.95
2020-10-02 08:30 | 44106.3542 | 0 | 8.1622 | 39.95
2020-10-02 09:00 | 44106.375 | 0 | 8.5845 | 39.95
2020-10-02 09:30 | 44106.3958 | 0 | 8.1874 | 39.95
2020-10-02 10:00 | 44106.4167 | 0 | 7.3568 | 39.95
2020-10-02 10:30 | 44106.4375 | 0 | 6.7935 | 39.95
2020-10-02 11:00 | 44106.4583 | 0 | 6.6216 | 39.95
2020-10-02 11:30 | 44106.4792 | 0 | 6.5424 | 39.95
2020-10-02 12:00 | 44106.5 | 0 | 6.7169 | 39.95
2020-10-02 12:30 | 44106.5208 | 0 | 6.8906 | 39.95
2020-10-02 13:00 | 44106.5417 | 0 | 7.3745 | 39.95
2020-10-02 13:30 | 44106.5625 | 0 | 7.6873 | 39.95
2020-10-02 14:00 | 44106.5833 | 0 | 7.6157 | 39.95
2020-10-02 14:30 | 44106.6042 | 0 | 7.7864 | 39.95
2020-10-02 15:00 | 44106.625 | 0 | 8.0897 | 39.95
2020-10-02 15:30 | 44106.6458 | 0 | 8.5946 | 39.95
2020-10-02 16:00 | 44106.6667 | 0 | 9.0283 | 39.95
2020-10-02 16:30 | 44106.6875 | 0 | 9.6207 | 39.95
2020-10-02 17:00 | 44106.7083 | 0 | 9.9641 | 39.95
2020-10-02 17:30 | 44106.7292 | 0 | 10.2714 | 39.95
2020-10-02 18:00 | 44106.75 | 0 | 10.8023 | 39.95
2020-10-02 18:30 | 44106.7708 | 0 | 10.9298 | 39.95
2020-10-02 19:00 | 44106.7917 | 0 | 10.7848 | 39.95
2020-10-02 19:30 | 44106.8125 | 0 | 10.3956 | 39.95
2020-10-02 20:00 | 44106.8333 | 0 | 10.2801 | 39.95
2020-10-02 20:30 | 44106.8542 | 0 | 9.8597 | 39.95
2020-10-02 21:00 | 44106.875 | 0 | 9.5108 | 39.95
2020-10-02 21:30 | 44106.8958 | 0 | 9.2496 | 39.95
2020-10-02 22:00 | 44106.9167 | 0 | 9.0647 | 39.95
2020-10-02 22:30 | 44106.9375 | 0 | 8.4808 | 39.95
2020-10-02 23:00 | 44106.9583 | 0 | 8.0237 | 39.95
2020-10-02 23:30 | 44106.9792 | 0 | 7.6525 | 39.95
2020-10-03 | 44107 | 0 | 7.3377 | 39.95
2020-10-03 00:30 | 44107.0208 | 0 | 7.0867 | 39.95
2020-10-03 01:00 | 44107.0417 | 0 | 6.869 | 39.95
2020-10-03 01:30 | 44107.0625 | 0 | 6.8915 | 39.95
2020-10-03 02:00 | 44107.0833 | 0 | 6.8561 | 39.95
2020-10-03 02:30 | 44107.1042 | 0 | 6.8709 | 39.95
2020-10-03 03:00 | 44107.125 | 0 | 6.7258 | 39.95
2020-10-03 03:30 | 44107.1458 | 0 | 6.655 | 39.95
2020-10-03 04:00 | 44107.1667 | 0 | 6.575 | 39.95
2020-10-03 04:30 | 44107.1875 | 0 | 6.5826 | 39.95
2020-10-03 05:00 | 44107.2083 | 0 | 6.7595 | 39.95
2020-10-03 05:30 | 44107.2292 | 0 | 6.7202 | 39.95
2020-10-03 06:00 | 44107.25 | 0 | 6.6468 | 39.95
2020-10-03 06:30 | 44107.2708 | 0 | 6.3942 | 39.95
2020-10-03 07:00 | 44107.2917 | 0 | 6.2218 | 39.95
2020-10-03 07:30 | 44107.3125 | 0 | 6.1132 | 39.95
2020-10-03 08:00 | 44107.3333 | 0 | 6.6901 | 39.95
2020-10-03 08:30 | 44107.3542 | 0 | 8.001 | 39.95
2020-10-03 09:00 | 44107.375 | 0 | 7.5007 | 39.95
2020-10-03 09:30 | 44107.3958 | 0 | 6.3604 | 39.95
2020-10-03 10:00 | 44107.4167 | 0 | 5.9343 | 39.95
2020-10-03 10:30 | 44107.4375 | 0 | 5.4078 | 39.95
2020-10-03 11:00 | 44107.4583 | 0 | 5.2203 | 39.95
2020-10-03 11:30 | 44107.4792 | 0 | 5.2744 | 39.95
2020-10-03 12:00 | 44107.5 | 0 | 5.2183 | 39.95
2020-10-03 12:30 | 44107.5208 | 0 | 5.3786 | 39.95
2020-10-03 13:00 | 44107.5417 | 0 | 5.5331 | 39.95
2020-10-03 13:30 | 44107.5625 | 0 | 5.8163 | 39.95
2020-10-03 14:00 | 44107.5833 | 0 | 6.0415 | 39.95
2020-10-03 14:30 | 44107.6042 | 0 | 6.598 | 39.95
2020-10-03 15:00 | 44107.625 | 0 | 7.1379 | 39.95
2020-10-03 15:30 | 44107.6458 | 0 | 7.7389 | 39.95
2020-10-03 16:00 | 44107.6667 | 0 | 8.2993 | 39.95
2020-10-03 16:30 | 44107.6875 | 0 | 9.0058 | 39.95
2020-10-03 17:00 | 44107.7083 | 0 | 9.3912 | 39.95
2020-10-03 17:30 | 44107.7292 | 0 | 9.8228 | 39.95
2020-10-03 18:00 | 44107.75 | 0 | 10.3908 | 39.95
2020-10-03 18:30 | 44107.7708 | 0 | 10.6227 | 39.95
2020-10-03 19:00 | 44107.7917 | 0 | 10.5018 | 39.95
2020-10-03 19:30 | 44107.8125 | 0 | 10.1164 | 39.95
2020-10-03 20:00 | 44107.8333 | 0 | 9.9492 | 39.95
2020-10-03 20:30 | 44107.8542 | 0 | 9.5841 | 39.95
2020-10-03 21:00 | 44107.875 | 0 | 9.2487 | 39.95
2020-10-03 21:30 | 44107.8958 | 0 | 9.0743 | 39.95
2020-10-03 22:00 | 44107.9167 | 0 | 8.8817 | 39.95
2020-10-03 22:30 | 44107.9375 | 0 | 8.2944 | 39.95
2020-10-03 23:00 | 44107.9583 | 0 | 7.7525 | 39.95
2020-10-03 23:30 | 44107.9792 | 0 | 7.6357 | 39.95
2020-10-04 | 44108 | 0 | 7.2433 | 39.95
2020-10-04 00:30 | 44108.0208 | 0 | 7.0142 | 39.95
2020-10-04 01:00 | 44108.0417 | 0 | 6.8709 | 39.95
2020-10-04 01:30 | 44108.0625 | 0 | 6.7015 | 39.95
2020-10-04 02:00 | 44108.0833 | 0 | 6.7854 | 39.95
2020-10-04 02:30 | 44108.1042 | 0 | 6.6998 | 39.95
2020-10-04 03:00 | 44108.125 | 0 | 6.752 | 39.95
2020-10-04 03:30 | 44108.1458 | 0 | 6.6587 | 39.95
2020-10-04 04:00 | 44108.1667 | 0 | 6.6962 | 39.95
2020-10-04 04:30 | 44108.1875 | 0 | 6.8508 | 39.95
2020-10-04 05:00 | 44108.2083 | 0 | 7.0533 | 39.95
2020-10-04 05:30 | 44108.2292 | 0 | 7.1932 | 39.95
2020-10-04 06:00 | 44108.25 | 0 | 7.1241 | 39.95
2020-10-04 06:30 | 44108.2708 | 0 | 6.9525 | 39.95
2020-10-04 07:00 | 44108.2917 | 0 | 6.893 | 39.95
2020-10-04 07:30 | 44108.3125 | 0 | 6.52 | 39.95
2020-10-04 08:00 | 44108.3333 | 0 | 6.8025 | 39.95
2020-10-04 08:30 | 44108.3542 | 0 | 6.7349 | 39.95
2020-10-04 09:00 | 44108.375 | 0 | 6.5955 | 39.95
2020-10-04 09:30 | 44108.3958 | 0 | 6.5255 | 39.95
2020-10-04 10:00 | 44108.4167 | 0 | 6.6125 | 39.95
2020-10-04 10:30 | 44108.4375 | 0 | 6.8896 | 39.95
2020-10-04 11:00 | 44108.4583 | 0 | 6.5371 | 39.95
2020-10-04 11:30 | 44108.4792 | 0 | 6.4451 | 39.95
2020-10-04 12:00 | 44108.5 | 0 | 6.3087 | 39.95
2020-10-04 12:30 | 44108.5208 | 0 | 6.4075 | 39.95
2020-10-04 13:00 | 44108.5417 | 0 | 6.6109 | 39.95
2020-10-04 13:30 | 44108.5625 | 0 | 6.8481 | 39.95
2020-10-04 14:00 | 44108.5833 | 0 | 7.2939 | 39.95
2020-10-04 14:30 | 44108.6042 | 0 | 7.7819 | 39.95
2020-10-04 15:00 | 44108.625 | 0 | 8.2843 | 39.95
2020-10-04 15:30 | 44108.6458 | 0 | 8.9716 | 39.95
2020-10-04 16:00 | 44108.6667 | 0 | 9.652 | 39.95
2020-10-04 16:30 | 44108.6875 | 0 | 10.4308 | 39.95
2020-10-04 17:00 | 44108.7083 | 0 | 10.921 | 39.95
2020-10-04 17:30 | 44108.7292 | 0 | 11.3865 | 39.95
2020-10-04 18:00 | 44108.75 | 0 | 12.1109 | 39.95
2020-10-04 18:30 | 44108.7708 | 0 | 12.413 | 39.95
2020-10-04 19:00 | 44108.7917 | 0 | 11.9964 | 39.95
2020-10-04 19:30 | 44108.8125 | 0 | 11.5662 | 39.95
2020-10-04 20:00 | 44108.8333 | 0 | 11.4304 | 39.95
2020-10-04 20:30 | 44108.8542 | 0 | 10.9769 | 39.95
2020-10-04 21:00 | 44108.875 | 0 | 10.3283 | 39.95
2020-10-04 21:30 | 44108.8958 | 0 | 9.9232 | 39.95
2020-10-04 22:00 | 44108.9167 | 0 | 9.4694 | 39.95
2020-10-04 22:30 | 44108.9375 | 0 | 8.8637 | 39.95
2020-10-04 23:00 | 44108.9583 | 0 | 8.3168 | 39.95
2020-10-04 23:30 | 44108.9792 | 0 | 7.9506 | 39.95
2020-10-05 | 44109 | 0 | 7.5408 | 39.95
2020-10-05 00:30 | 44109.0208 | 0 | 7.2504 | 39.95
2020-10-05 01:00 | 44109.0417 | 0 | 7.0951 | 39.95
2020-10-05 01:30 | 44109.0625 | 0 | 7.0161 | 39.95
2020-10-05 02:00 | 44109.0833 | 0 | 7.1076 | 39.95
2020-10-05 02:30 | 44109.1042 | 0 | 7.1055 | 39.95
2020-10-05 03:00 | 44109.125 | 0 | 7.1074 | 39.95
2020-10-05 03:30 | 44109.1458 | 0 | 7.1428 | 39.95
2020-10-05 04:00 | 44109.1667 | 0 | 7.2639 | 39.95
2020-10-05 04:30 | 44109.1875 | 0 | 7.6859 | 39.95
2020-10-05 05:00 | 44109.2083 | 0 | 8.2709 | 39.95
2020-10-05 05:30 | 44109.2292 | 0 | 8.634 | 39.95
2020-10-05 06:00 | 44109.25 | 0 | 9.3257 | 39.95
2020-10-05 06:30 | 44109.2708 | 0 | 9.8568 | 39.95
2020-10-05 07:00 | 44109.2917 | 0 | 10.6902 | 39.95
2020-10-05 07:30 | 44109.3125 | 0 | 10.2317 | 39.95
2020-10-05 08:00 | 44109.3333 | 0 | 10.7162 | 39.95
2020-10-05 08:30 | 44109.3542 | 0 | 11.5271 | 39.95
2020-10-05 09:00 | 44109.375 | 0 | 11.5543 | 39.95
2020-10-05 09:30 | 44109.3958 | 0 | 11.6032 | 39.95
2020-10-05 10:00 | 44109.4167 | 0 | 11.073 | 39.95
2020-10-05 10:30 | 44109.4375 | 0 | 10.8043 | 39.95
2020-10-05 11:00 | 44109.4583 | 0 | 9.8552 | 39.95
2020-10-05 11:30 | 44109.4792 | 0 | 9.3212 | 39.95
2020-10-05 12:00 | 44109.5 | 0 | 9.3968 | 39.95
2020-10-05 12:30 | 44109.5208 | 0 | 9.4796 | 39.95
2020-10-05 13:00 | 44109.5417 | 0 | 9.4396 | 39.95
2020-10-05 13:30 | 44109.5625 | 0 | 9.895 | 39.95
2020-10-05 14:00 | 44109.5833 | 0 | 10.4458 | 39.95
2020-10-05 14:30 | 44109.6042 | 0 | 10.6582 | 39.95
2020-10-05 15:00 | 44109.625 | 0 | 10.8616 | 39.95
2020-10-05 15:30 | 44109.6458 | 0 | 11.2885 | 39.95
2020-10-05 16:00 | 44109.6667 | 0 | 11.6022 | 39.95
2020-10-05 16:30 | 44109.6875 | 0 | 12.3374 | 39.95
2020-10-05 17:00 | 44109.7083 | 0 | 12.6344 | 39.95
2020-10-05 17:30 | 44109.7292 | 0 | 13.0616 | 39.95
2020-10-05 18:00 | 44109.75 | 0 | 13.5678 | 39.95
2020-10-05 18:30 | 44109.7708 | 0 | 13.9044 | 39.95
2020-10-05 19:00 | 44109.7917 | 0 | 13.4383 | 39.95
2020-10-05 19:30 | 44109.8125 | 0 | 13.1784 | 39.95
2020-10-05 20:00 | 44109.8333 | 0 | 12.7928 | 39.95
2020-10-05 20:30 | 44109.8542 | 0 | 12.4183 | 39.95
2020-10-05 21:00 | 44109.875 | 0 | 11.7953 | 39.95
2020-10-05 21:30 | 44109.8958 | 0 | 11.4733 | 39.95
2020-10-05 22:00 | 44109.9167 | 0 | 10.9459 | 39.95
2020-10-05 22:30 | 44109.9375 | 0 | 10.1184 | 39.95
2020-10-05 23:00 | 44109.9583 | 0 | 9.3498 | 39.95
2020-10-05 23:30 | 44109.9792 | 0 | 9.0087 | 39.95
2020-10-06 | 44110 | 0 | 8.4581 | 39.95
2020-10-06 00:30 | 44110.0208 | 0 | 7.9692 | 39.95
2020-10-06 01:00 | 44110.0417 | 0 | 7.8014 | 39.95
2020-10-06 01:30 | 44110.0625 | 0 | 7.714 | 39.95
2020-10-06 02:00 | 44110.0833 | 0 | 7.6506 | 39.95
2020-10-06 02:30 | 44110.1042 | 0 | 7.5968 | 39.95
2020-10-06 03:00 | 44110.125 | 0 | 7.5073 | 39.95
2020-10-06 03:30 | 44110.1458 | 0 | 7.53 | 39.95
2020-10-06 04:00 | 44110.1667 | 0 | 7.733 | 39.95
2020-10-06 04:30 | 44110.1875 | 0 | 8.083 | 39.95
2020-10-06 05:00 | 44110.2083 | 0 | 8.6737 | 39.95
2020-10-06 05:30 | 44110.2292 | 0 | 8.9835 | 39.95
2020-10-06 06:00 | 44110.25 | 0 | 9.4915 | 39.95
2020-10-06 06:30 | 44110.2708 | 0 | 9.8688 | 39.95
2020-10-06 07:00 | 44110.2917 | 0 | 10.3033 | 39.95
2020-10-06 07:30 | 44110.3125 | 0 | 10.2523 | 39.95
2020-10-06 08:00 | 44110.3333 | 0 | 10.3106 | 39.95
2020-10-06 08:30 | 44110.3542 | 0 | 10.824 | 39.95
2020-10-06 09:00 | 44110.375 | 0 | 10.8165 | 39.95
2020-10-06 09:30 | 44110.3958 | 0 | 10.9894 | 39.95
2020-10-06 10:00 | 44110.4167 | 0 | 10.9103 | 39.95
2020-10-06 10:30 | 44110.4375 | 0 | 10.6109 | 39.95
2020-10-06 11:00 | 44110.4583 | 0 | 9.9299 | 39.95
2020-10-06 11:30 | 44110.4792 | 0 | 10.3381 | 39.95
2020-10-06 12:00 | 44110.5 | 0 | 9.3672 | 39.95
2020-10-06 12:30 | 44110.5208 | 0 | 9.4075 | 39.95
2020-10-06 13:00 | 44110.5417 | 0 | 9.449 | 39.95
2020-10-06 13:30 | 44110.5625 | 0 | 9.8261 | 39.95
2020-10-06 14:00 | 44110.5833 | 0 | 10.1186 | 39.95
2020-10-06 14:30 | 44110.6042 | 0 | 10.3461 | 39.95
2020-10-06 15:00 | 44110.625 | 0 | 10.7757 | 39.95
2020-10-06 15:30 | 44110.6458 | 0 | 11.1702 | 39.95
2020-10-06 16:00 | 44110.6667 | 0 | 11.9039 | 39.95
2020-10-06 16:30 | 44110.6875 | 0 | 12.2212 | 39.95
2020-10-06 17:00 | 44110.7083 | 0 | 12.4463 | 39.95
2020-10-06 17:30 | 44110.7292 | 0 | 12.8773 | 39.95
2020-10-06 18:00 | 44110.75 | 0 | 13.5803 | 39.95
2020-10-06 18:30 | 44110.7708 | 0 | 14.0027 | 39.95
2020-10-06 19:00 | 44110.7917 | 0 | 13.73 | 39.95
2020-10-06 19:30 | 44110.8125 | 0 | 13.0961 | 39.95
2020-10-06 20:00 | 44110.8333 | 0 | 12.9617 | 39.95
2020-10-06 20:30 | 44110.8542 | 0 | 12.4228 | 39.95
2020-10-06 21:00 | 44110.875 | 0 | 11.7662 | 39.95
2020-10-06 21:30 | 44110.8958 | 0 | 11.4343 | 39.95
2020-10-06 22:00 | 44110.9167 | 0 | 10.8644 | 39.95
2020-10-06 22:30 | 44110.9375 | 0 | 9.9959 | 39.95
2020-10-06 23:00 | 44110.9583 | 0 | 9.5819 | 39.95
2020-10-06 23:30 | 44110.9792 | 0 | 9.0983 | 39.95
2020-10-07 | 44111 | 0 | 8.5413 | 39.95
2020-10-07 00:30 | 44111.0208 | 0 | 8.149 | 39.95
2020-10-07 01:00 | 44111.0417 | 0 | 7.9578 | 39.95
2020-10-07 01:30 | 44111.0625 | 0 | 7.8108 | 39.95
2020-10-07 02:00 | 44111.0833 | 0 | 7.7867 | 39.95
2020-10-07 02:30 | 44111.1042 | 0 | 7.6729 | 39.95
2020-10-07 03:00 | 44111.125 | 0 | 7.5931 | 39.95
2020-10-07 03:30 | 44111.1458 | 0 | 7.6918 | 39.95
2020-10-07 04:00 | 44111.1667 | 0 | 7.7255 | 39.95
2020-10-07 04:30 | 44111.1875 | 0 | 8.2357 | 39.95
2020-10-07 05:00 | 44111.2083 | 0 | 8.7229 | 39.95
2020-10-07 05:30 | 44111.2292 | 0 | 8.9992 | 39.95
2020-10-07 06:00 | 44111.25 | 0 | 9.8114 | 39.95
2020-10-07 06:30 | 44111.2708 | 0 | 10.2229 | 39.95
2020-10-07 07:00 | 44111.2917 | 0 | 10.8227 | 39.95
2020-10-07 07:30 | 44111.3125 | 0 | 10.1268 | 39.95
2020-10-07 08:00 | 44111.3333 | 0 | 10.4203 | 39.95
2020-10-07 08:30 | 44111.3542 | 0 | 9.5553 | 39.95
2020-10-07 09:00 | 44111.375 | 0 | 9.3648 | 39.95
2020-10-07 09:30 | 44111.3958 | 0 | 9.729 | 39.95
2020-10-07 10:00 | 44111.4167 | 0 | 9.9409 | 39.95
2020-10-07 10:30 | 44111.4375 | 0 | 9.8279 | 39.95
2020-10-07 11:00 | 44111.4583 | 0 | 10.0343 | 39.95
2020-10-07 11:30 | 44111.4792 | 0 | 10.2021 | 39.95
2020-10-07 12:00 | 44111.5 | 0 | 9.7328 | 39.95
2020-10-07 12:30 | 44111.5208 | 0 | 9.5193 | 39.95
2020-10-07 13:00 | 44111.5417 | 0 | 10.2413 | 39.95
2020-10-07 13:30 | 44111.5625 | 0 | 11.0511 | 39.95
2020-10-07 14:00 | 44111.5833 | 0 | 11.8196 | 39.95
2020-10-07 14:30 | 44111.6042 | 0 | 12.2177 | 39.95
2020-10-07 15:00 | 44111.625 | 0 | 11.7982 | 39.95
2020-10-07 15:30 | 44111.6458 | 0 | 11.0399 | 39.95
2020-10-07 16:00 | 44111.6667 | 0 | 11.6509 | 39.95
2020-10-07 16:30 | 44111.6875 | 0 | 12.3461 | 39.95
2020-10-07 17:00 | 44111.7083 | 0 | 12.742 | 39.95
2020-10-07 17:30 | 44111.7292 | 0 | 13.0432 | 39.95
2020-10-07 18:00 | 44111.75 | 0 | 13.5245 | 39.95
2020-10-07 18:30 | 44111.7708 | 0 | 13.8181 | 39.95
2020-10-07 19:00 | 44111.7917 | 0 | 13.3844 | 39.95
2020-10-07 19:30 | 44111.8125 | 0 | 13.3927 | 39.95
2020-10-07 20:00 | 44111.8333 | 0 | 13.0007 | 39.95
2020-10-07 20:30 | 44111.8542 | 0 | 12.6033 | 39.95
2020-10-07 21:00 | 44111.875 | 0 | 11.8879 | 39.95
2020-10-07 21:30 | 44111.8958 | 0 | 11.6596 | 39.95
2020-10-07 22:00 | 44111.9167 | 0 | 11.1068 | 39.95
2020-10-07 22:30 | 44111.9375 | 0 | 10.2986 | 39.95
2020-10-07 23:00 | 44111.9583 | 0 | 9.5488 | 39.95
2020-10-07 23:30 | 44111.9792 | 0 | 9.0806 | 39.95
2020-10-08 | 44112 | 0 | 8.4673 | 39.95
2020-10-08 00:30 | 44112.0208 | 0 | 8.0863 | 39.95
2020-10-08 01:00 | 44112.0417 | 0 | 7.9186 | 39.95
2020-10-08 01:30 | 44112.0625 | 0 | 7.8463 | 39.95
2020-10-08 02:00 | 44112.0833 | 0 | 7.7715 | 39.95
2020-10-08 02:30 | 44112.1042 | 0 | 7.714 | 39.95
2020-10-08 03:00 | 44112.125 | 0 | 7.6973 | 39.95
2020-10-08 03:30 | 44112.1458 | 0 | 7.6601 | 39.95
2020-10-08 04:00 | 44112.1667 | 0 | 7.7645 | 39.95
2020-10-08 04:30 | 44112.1875 | 0 | 8.2358 | 39.95
2020-10-08 05:00 | 44112.2083 | 0 | 8.5635 | 39.95
2020-10-08 05:30 | 44112.2292 | 0 | 9.2906 | 39.95
2020-10-08 06:00 | 44112.25 | 0 | 9.5717 | 39.95
2020-10-08 06:30 | 44112.2708 | 0 | 10.0679 | 39.95
2020-10-08 07:00 | 44112.2917 | 0 | 10.4835 | 39.95
2020-10-08 07:30 | 44112.3125 | 0 | 10.364 | 39.95
2020-10-08 08:00 | 44112.3333 | 0 | 10.208 | 39.95
2020-10-08 08:30 | 44112.3542 | 0 | 10.305 | 39.95
2020-10-08 09:00 | 44112.375 | 0 | 10.0459 | 39.95
2020-10-08 09:30 | 44112.3958 | 0 | 10.1819 | 39.95
2020-10-08 10:00 | 44112.4167 | 0 | 10.2023 | 39.95
2020-10-08 10:30 | 44112.4375 | 0 | 9.9993 | 39.95
2020-10-08 11:00 | 44112.4583 | 0 | 10.0627 | 39.95
2020-10-08 11:30 | 44112.4792 | 0 | 10.1168 | 39.95
2020-10-08 12:00 | 44112.5 | 0 | 10.1334 | 39.95
2020-10-08 12:30 | 44112.5208 | 0 | 10.1353 | 39.95
2020-10-08 13:00 | 44112.5417 | 0 | 10.4691 | 39.95
2020-10-08 13:30 | 44112.5625 | 0 | 10.9227 | 39.95
2020-10-08 14:00 | 44112.5833 | 0 | 11.3901 | 39.95
2020-10-08 14:30 | 44112.6042 | 0 | 11.8651 | 39.95
2020-10-08 15:00 | 44112.625 | 0 | 13.7934 | 39.95
2020-10-08 15:30 | 44112.6458 | 0 | 13.3624 | 39.95
2020-10-08 16:00 | 44112.6667 | 0 | 13.0526 | 39.95
2020-10-08 16:30 | 44112.6875 | 0 | 13.1341 | 39.95
2020-10-08 17:00 | 44112.7083 | 0 | 13.2132 | 39.95
2020-10-08 17:30 | 44112.7292 | 0 | 13.2717 | 39.95
2020-10-08 18:00 | 44112.75 | 0 | 13.6749 | 39.95
2020-10-08 18:30 | 44112.7708 | 0 | 14.0175 | 39.95
2020-10-08 19:00 | 44112.7917 | 0 | 13.6169 | 39.95
2020-10-08 19:30 | 44112.8125 | 0 | 13.454 | 39.95
2020-10-08 20:00 | 44112.8333 | 0 | 13.2079 | 39.95
2020-10-08 20:30 | 44112.8542 | 0 | 12.8093 | 39.95
2020-10-08 21:00 | 44112.875 | 0 | 12.2924 | 39.95
2020-10-08 21:30 | 44112.8958 | 0 | 12.1061 | 39.95
2020-10-08 22:00 | 44112.9167 | 0 | 11.575 | 39.95
2020-10-08 22:30 | 44112.9375 | 0 | 10.7104 | 39.95
2020-10-08 23:00 | 44112.9583 | 0 | 10.0791 | 39.95
2020-10-08 23:30 | 44112.9792 | 0 | 9.5957 | 39.95
2020-10-09 | 44113 | 0 | 8.9411 | 39.95
2020-10-09 00:30 | 44113.0208 | 0 | 8.5188 | 39.95
2020-10-09 01:00 | 44113.0417 | 0 | 8.2586 | 39.95
2020-10-09 01:30 | 44113.0625 | 0 | 8.2443 | 39.95
2020-10-09 02:00 | 44113.0833 | 0 | 8.0225 | 39.95
2020-10-09 02:30 | 44113.1042 | 0 | 7.7718 | 39.95
2020-10-09 03:00 | 44113.125 | 0 | 7.7756 | 39.95
2020-10-09 03:30 | 44113.1458 | 0 | 7.9225 | 39.95
2020-10-09 04:00 | 44113.1667 | 0 | 7.9749 | 39.95
2020-10-09 04:30 | 44113.1875 | 0 | 8.1719 | 39.95
2020-10-09 05:00 | 44113.2083 | 0 | 8.3248 | 39.95
2020-10-09 05:30 | 44113.2292 | 0 | 8.2854 | 39.95
2020-10-09 06:00 | 44113.25 | 0 | 8.3618 | 39.95
2020-10-09 06:30 | 44113.2708 | 0 | 8.2629 | 39.95
2020-10-09 07:00 | 44113.2917 | 0 | 8.1533 | 39.95
2020-10-09 07:30 | 44113.3125 | 0 | 8.0525 | 39.95
2020-10-09 08:00 | 44113.3333 | 0 | 8.2986 | 39.95
2020-10-09 08:30 | 44113.3542 | 0 | 7.8608 | 39.95
2020-10-09 09:00 | 44113.375 | 0 | 7.5258 | 39.95
2020-10-09 09:30 | 44113.3958 | 0 | 7.5208 | 39.95
2020-10-09 10:00 | 44113.4167 | 0 | 7.7212 | 39.95
2020-10-09 10:30 | 44113.4375 | 0 | 7.6251 | 39.95
2020-10-09 11:00 | 44113.4583 | 0 | 7.1942 | 39.95
2020-10-09 11:30 | 44113.4792 | 0 | 7.2116 | 39.95
2020-10-09 12:00 | 44113.5 | 0 | 7.0886 | 39.95
2020-10-09 12:30 | 44113.5208 | 0 | 7.3197 | 39.95
2020-10-09 13:00 | 44113.5417 | 0 | 7.5756 | 39.95
2020-10-09 13:30 | 44113.5625 | 0 | 7.467 | 39.95
2020-10-09 14:00 | 44113.5833 | 0 | 7.8743 | 39.95
2020-10-09 14:30 | 44113.6042 | 0 | 8.3106 | 39.95
2020-10-09 15:00 | 44113.625 | 0 | 8.8889 | 39.95
2020-10-09 15:30 | 44113.6458 | 0 | 9.2126 | 39.95
2020-10-09 16:00 | 44113.6667 | 0 | 9.8216 | 39.95
2020-10-09 16:30 | 44113.6875 | 0 | 10.3589 | 39.95
2020-10-09 17:00 | 44113.7083 | 0 | 10.6472 | 39.95
2020-10-09 17:30 | 44113.7292 | 0 | 10.7961 | 39.95
2020-10-09 18:00 | 44113.75 | 0 | 11.2135 | 39.95
2020-10-09 18:30 | 44113.7708 | 0 | 11.5417 | 39.95
2020-10-09 19:00 | 44113.7917 | 0 | 11.3805 | 39.95
2020-10-09 19:30 | 44113.8125 | 0 | 11.1553 | 39.95
2020-10-09 20:00 | 44113.8333 | 0 | 10.9052 | 39.95
2020-10-09 20:30 | 44113.8542 | 0 | 10.5138 | 39.95
2020-10-09 21:00 | 44113.875 | 0 | 10.1237 | 39.95
2020-10-09 21:30 | 44113.8958 | 0 | 9.8802 | 39.95
2020-10-09 22:00 | 44113.9167 | 0 | 9.4825 | 39.95
2020-10-09 22:30 | 44113.9375 | 0 | 8.8489 | 39.95
2020-10-09 23:00 | 44113.9583 | 0 | 8.4218 | 39.95
2020-10-09 23:30 | 44113.9792 | 0 | 8.1587 | 39.95
2020-10-10 | 44114 | 0 | 7.5705 | 39.95
2020-10-10 00:30 | 44114.0208 | 0 | 7.2504 | 39.95
2020-10-10 01:00 | 44114.0417 | 0 | 7.0609 | 39.95
2020-10-10 01:30 | 44114.0625 | 0 | 7.1241 | 39.95
2020-10-10 02:00 | 44114.0833 | 0 | 7.0458 | 39.95
2020-10-10 02:30 | 44114.1042 | 0 | 7.0609 | 39.95
2020-10-10 03:00 | 44114.125 | 0 | 7.0497 | 39.95
2020-10-10 03:30 | 44114.1458 | 0 | 6.9212 | 39.95
2020-10-10 04:00 | 44114.1667 | 0 | 6.822 | 39.95
2020-10-10 04:30 | 44114.1875 | 0 | 6.8358 | 39.95
2020-10-10 05:00 | 44114.2083 | 0 | 6.8597 | 39.95
2020-10-10 05:30 | 44114.2292 | 0 | 6.897 | 39.95
2020-10-10 06:00 | 44114.25 | 0 | 6.7778 | 39.95
2020-10-10 06:30 | 44114.2708 | 0 | 6.6606 | 39.95
2020-10-10 07:00 | 44114.2917 | 0 | 6.5063 | 39.95
2020-10-10 07:30 | 44114.3125 | 0 | 6.7616 | 39.95
2020-10-10 08:00 | 44114.3333 | 0 | 6.953 | 39.95
2020-10-10 08:30 | 44114.3542 | 0 | 7.3084 | 39.95
2020-10-10 09:00 | 44114.375 | 0 | 6.5906 | 39.95
2020-10-10 09:30 | 44114.3958 | 0 | 6.2998 | 39.95
2020-10-10 10:00 | 44114.4167 | 0 | 6.3802 | 39.95
2020-10-10 10:30 | 44114.4375 | 0 | 6.3025 | 39.95
2020-10-10 11:00 | 44114.4583 | 0 | 5.9399 | 39.95
2020-10-10 11:30 | 44114.4792 | 0 | 6.2255 | 39.95
2020-10-10 12:00 | 44114.5 | 0 | 6.3019 | 39.95
2020-10-10 12:30 | 44114.5208 | 0 | 6.4651 | 39.95
2020-10-10 13:00 | 44114.5417 | 0 | 6.369 | 39.95
2020-10-10 13:30 | 44114.5625 | 0 | 6.7485 | 39.95
2020-10-10 14:00 | 44114.5833 | 0 | 7.2781 | 39.95
2020-10-10 14:30 | 44114.6042 | 0 | 7.6457 | 39.95
2020-10-10 15:00 | 44114.625 | 0 | 8.2363 | 39.95
2020-10-10 15:30 | 44114.6458 | 0 | 8.834 | 39.95
2020-10-10 16:00 | 44114.6667 | 0 | 9.4217 | 39.95
2020-10-10 16:30 | 44114.6875 | 0 | 10.4412 | 39.95
2020-10-10 17:00 | 44114.7083 | 0 | 10.8706 | 39.95
2020-10-10 17:30 | 44114.7292 | 0 | 11.2356 | 39.95
2020-10-10 18:00 | 44114.75 | 0 | 11.8033 | 39.95
2020-10-10 18:30 | 44114.7708 | 0 | 12.2097 | 39.95
2020-10-10 19:00 | 44114.7917 | 0 | 11.8696 | 39.95
2020-10-10 19:30 | 44114.8125 | 0 | 11.542 | 39.95
2020-10-10 20:00 | 44114.8333 | 0 | 11.2007 | 39.95
2020-10-10 20:30 | 44114.8542 | 0 | 10.8235 | 39.95
2020-10-10 21:00 | 44114.875 | 0 | 10.2577 | 39.95
2020-10-10 21:30 | 44114.8958 | 0 | 9.9473 | 39.95
2020-10-10 22:00 | 44114.9167 | 0 | 9.4686 | 39.95
2020-10-10 22:30 | 44114.9375 | 0 | 8.8306 | 39.95
2020-10-10 23:00 | 44114.9583 | 0 | 8.3203 | 39.95
2020-10-10 23:30 | 44114.9792 | 0 | 7.9477 | 39.95
2020-10-11 | 44115 | 0 | 7.6902 | 39.95
2020-10-11 00:30 | 44115.0208 | 0 | 7.5276 | 39.95
2020-10-11 01:00 | 44115.0417 | 0 | 7.3884 | 39.95
2020-10-11 01:30 | 44115.0625 | 0 | 7.3938 | 39.95
2020-10-11 02:00 | 44115.0833 | 0 | 7.3289 | 39.95
2020-10-11 02:30 | 44115.1042 | 0 | 7.2878 | 39.95
2020-10-11 03:00 | 44115.125 | 0 | 7.3122 | 39.95
2020-10-11 03:30 | 44115.1458 | 0 | 7.5224 | 39.95
2020-10-11 04:00 | 44115.1667 | 0 | 7.683 | 39.95
2020-10-11 04:30 | 44115.1875 | 0 | 7.8914 | 39.95
2020-10-11 05:00 | 44115.2083 | 0 | 8.4011 | 39.95
2020-10-11 05:30 | 44115.2292 | 0 | 9.1065 | 39.95
2020-10-11 06:00 | 44115.25 | 0 | 9.7076 | 39.95
2020-10-11 06:30 | 44115.2708 | 0 | 10.4118 | 39.95
2020-10-11 07:00 | 44115.2917 | 0 | 11.3159 | 39.95
2020-10-11 07:30 | 44115.3125 | 0 | 11.1239 | 39.95
2020-10-11 08:00 | 44115.3333 | 0 | 11.6106 | 39.95
2020-10-11 08:30 | 44115.3542 | 0 | 10.9813 | 39.95
2020-10-11 09:00 | 44115.375 | 0 | 11.1327 | 39.95
2020-10-11 09:30 | 44115.3958 | 0 | 10.4485 | 39.95
2020-10-11 10:00 | 44115.4167 | 0 | 11.4766 | 39.95
2020-10-11 10:30 | 44115.4375 | 0 | 11.983 | 39.95
2020-10-11 11:00 | 44115.4583 | 0 | 12.1283 | 39.95
2020-10-11 11:30 | 44115.4792 | 0 | 11.3114 | 39.95
2020-10-11 12:00 | 44115.5 | 0 | 10.1253 | 39.95
2020-10-11 12:30 | 44115.5208 | 0 | 10.0739 | 39.95
2020-10-11 13:00 | 44115.5417 | 0 | 10.1763 | 39.95
2020-10-11 13:30 | 44115.5625 | 0 | 10.5124 | 39.95
2020-10-11 14:00 | 44115.5833 | 0 | 10.3588 | 39.95
2020-10-11 14:30 | 44115.6042 | 0 | 10.6487 | 39.95
2020-10-11 15:00 | 44115.625 | 0 | 10.8857 | 39.95
2020-10-11 15:30 | 44115.6458 | 0 | 11.3784 | 39.95
2020-10-11 16:00 | 44115.6667 | 0 | 11.9141 | 39.95
2020-10-11 16:30 | 44115.6875 | 0 | 12.4899 | 39.95
2020-10-11 17:00 | 44115.7083 | 0 | 12.6786 | 39.95
2020-10-11 17:30 | 44115.7292 | 0 | 12.9067 | 39.95
2020-10-11 18:00 | 44115.75 | 0 | 13.4763 | 39.95
2020-10-11 18:30 | 44115.7708 | 0 | 13.8014 | 39.95
2020-10-11 19:00 | 44115.7917 | 0 | 13.4535 | 39.95
2020-10-11 19:30 | 44115.8125 | 0 | 13.279 | 39.95
2020-10-11 20:00 | 44115.8333 | 0 | 13.0344 | 39.95
2020-10-11 20:30 | 44115.8542 | 0 | 12.5367 | 39.95
2020-10-11 21:00 | 44115.875 | 0 | 11.6242 | 39.95
2020-10-11 21:30 | 44115.8958 | 0 | 11.3003 | 39.95
2020-10-11 22:00 | 44115.9167 | 0 | 10.7649 | 39.95
2020-10-11 22:30 | 44115.9375 | 0 | 10.0678 | 39.95
2020-10-11 23:00 | 44115.9583 | 0 | 9.4297 | 39.95
2020-10-11 23:30 | 44115.9792 | 0 | 9.0433 | 39.95
2020-10-12 | 44116 | 0 | 8.6087 | 39.95
2020-10-12 00:30 | 44116.0208 | 0 | 8.1646 | 39.95
2020-10-12 01:00 | 44116.0417 | 0 | 7.8649 | 39.95
2020-10-12 01:30 | 44116.0625 | 0 | 7.8089 | 39.95
2020-10-12 02:00 | 44116.0833 | 0 | 7.4331 | 39.95
2020-10-12 02:30 | 44116.1042 | 0 | 7.7309 | 39.95
2020-10-12 03:00 | 44116.125 | 0 | 7.8012 | 39.95
2020-10-12 03:30 | 44116.1458 | 0 | 7.7905 | 39.95
2020-10-12 04:00 | 44116.1667 | 0 | 7.8612 | 39.95
2020-10-12 04:30 | 44116.1875 | 0 | 8.2432 | 39.95
2020-10-12 05:00 | 44116.2083 | 0 | 8.6981 | 39.95
2020-10-12 05:30 | 44116.2292 | 0 | 9.2647 | 39.95
2020-10-12 06:00 | 44116.25 | 0 | 9.4485 | 39.95
2020-10-12 06:30 | 44116.2708 | 0 | 10.0966 | 39.95
2020-10-12 07:00 | 44116.2917 | 0 | 10.3958 | 39.95
2020-10-12 07:30 | 44116.3125 | 0 | 10.2525 | 39.95
2020-10-12 08:00 | 44116.3333 | 0 | 10.2021 | 39.95
2020-10-12 08:30 | 44116.3542 | 0 | 10.0922 | 39.95
2020-10-12 09:00 | 44116.375 | 0 | 10.2066 | 39.95
2020-10-12 09:30 | 44116.3958 | 0 | 10.5334 | 39.95
2020-10-12 10:00 | 44116.4167 | 0 | 11.0799 | 39.95
2020-10-12 10:30 | 44116.4375 | 0 | 11.7427 | 39.95
2020-10-12 11:00 | 44116.4583 | 0 | 11.2024 | 39.95
2020-10-12 11:30 | 44116.4792 | 0 | 10.7799 | 39.95
2020-10-12 12:00 | 44116.5 | 0 | 9.8973 | 39.95
2020-10-12 12:30 | 44116.5208 | 0 | 10.1184 | 39.95
2020-10-12 13:00 | 44116.5417 | 0 | 10.8043 | 39.95
2020-10-12 13:30 | 44116.5625 | 0 | 10.9069 | 39.95
2020-10-12 14:00 | 44116.5833 | 0 | 11.9023 | 39.95
2020-10-12 14:30 | 44116.6042 | 0 | 10.9036 | 39.95
2020-10-12 15:00 | 44116.625 | 0 | 11.5541 | 39.95
2020-10-12 15:30 | 44116.6458 | 0 | 11.2034 | 39.95
2020-10-12 16:00 | 44116.6667 | 0 | 12.0004 | 39.95
2020-10-12 16:30 | 44116.6875 | 0 | 12.3476 | 39.95
2020-10-12 17:00 | 44116.7083 | 0 | 12.2388 | 39.95
2020-10-12 17:30 | 44116.7292 | 0 | 12.873 | 39.95
2020-10-12 18:00 | 44116.75 | 0 | 13.4323 | 39.95
2020-10-12 18:30 | 44116.7708 | 0 | 13.8834 | 39.95
2020-10-12 19:00 | 44116.7917 | 0 | 13.5665 | 39.95
2020-10-12 19:30 | 44116.8125 | 0 | 13.1454 | 39.95
2020-10-12 20:00 | 44116.8333 | 0 | 12.9974 | 39.95
2020-10-12 20:30 | 44116.8542 | 0 | 12.5816 | 39.95
2020-10-12 21:00 | 44116.875 | 0 | 11.8509 | 39.95
2020-10-12 21:30 | 44116.8958 | 0 | 11.3876 | 39.95
2020-10-12 22:00 | 44116.9167 | 0 | 10.9425 | 39.95
2020-10-12 22:30 | 44116.9375 | 0 | 10.1269 | 39.95
2020-10-12 23:00 | 44116.9583 | 0 | 9.4644 | 39.95
2020-10-12 23:30 | 44116.9792 | 0 | 8.9983 | 39.95
2020-10-13 | 44117 | 0 | 8.4581 | 39.95
2020-10-13 00:30 | 44117.0208 | 0 | 8.0484 | 39.95
2020-10-13 01:00 | 44117.0417 | 0 | 7.7475 | 39.95
2020-10-13 01:30 | 44117.0625 | 0 | 7.7233 | 39.95
2020-10-13 02:00 | 44117.0833 | 0 | 7.7178 | 39.95
2020-10-13 02:30 | 44117.1042 | 0 | 7.7067 | 39.95
2020-10-13 03:00 | 44117.125 | 0 | 7.6449 | 39.95
2020-10-13 03:30 | 44117.1458 | 0 | 7.7629 | 39.95
2020-10-13 04:00 | 44117.1667 | 0 | 8.0457 | 39.95
2020-10-13 04:30 | 44117.1875 | 0 | 8.2707 | 39.95
2020-10-13 05:00 | 44117.2083 | 0 | 8.7878 | 39.95
2020-10-13 05:30 | 44117.2292 | 0 | 9.0654 | 39.95
2020-10-13 06:00 | 44117.25 | 0 | 9.5077 | 39.95
2020-10-13 06:30 | 44117.2708 | 0 | 10.4957 | 39.95
2020-10-13 07:00 | 44117.2917 | 0 | 11.02 | 39.95
2020-10-13 07:30 | 44117.3125 | 0 | 10.7776 | 39.95
2020-10-13 08:00 | 44117.3333 | 0 | 11.5836 | 39.95
2020-10-13 08:30 | 44117.3542 | 0 | 11.5097 | 39.95
2020-10-13 09:00 | 44117.375 | 0 | 11.9708 | 39.95
2020-10-13 09:30 | 44117.3958 | 0 | 11.3045 | 39.95
2020-10-13 10:00 | 44117.4167 | 0 | 11.0546 | 39.95
2020-10-13 10:30 | 44117.4375 | 0 | 9.4181 | 39.95
2020-10-13 11:00 | 44117.4583 | 0 | 8.884 | 39.95
2020-10-13 11:30 | 44117.4792 | 0 | 11.0631 | 39.95
2020-10-13 12:00 | 44117.5 | 0 | 11.5715 | 39.95
2020-10-13 12:30 | 44117.5208 | 0 | 10.3345 | 39.95
2020-10-13 13:00 | 44117.5417 | 0 | 11.4981 | 39.95
2020-10-13 13:30 | 44117.5625 | 0 | 10.3057 | 39.95
2020-10-13 14:00 | 44117.5833 | 0 | 10.5411 | 39.95
2020-10-13 14:30 | 44117.6042 | 0 | 11.365 | 39.95
2020-10-13 15:00 | 44117.625 | 0 | 11.2285 | 39.95
2020-10-13 15:30 | 44117.6458 | 0 | 11.1067 | 39.95
2020-10-13 16:00 | 44117.6667 | 0 | 11.887 | 39.95
2020-10-13 16:30 | 44117.6875 | 0 | 11.9425 | 39.95
2020-10-13 17:00 | 44117.7083 | 0 | 12.1742 | 39.95
2020-10-13 17:30 | 44117.7292 | 0 | 12.5329 | 39.95
2020-10-13 18:00 | 44117.75 | 0 | 13.1338 | 39.95
2020-10-13 18:30 | 44117.7708 | 0 | 13.8088 | 39.95
2020-10-13 19:00 | 44117.7917 | 0 | 13.3114 | 39.95
2020-10-13 19:30 | 44117.8125 | 0 | 12.8298 | 39.95
2020-10-13 20:00 | 44117.8333 | 0 | 12.6327 | 39.95
2020-10-13 20:30 | 44117.8542 | 0 | 12.2491 | 39.95
2020-10-13 21:00 | 44117.875 | 0 | 11.4621 | 39.95
2020-10-13 21:30 | 44117.8958 | 0 | 11.1263 | 39.95
2020-10-13 22:00 | 44117.9167 | 0 | 10.5829 | 39.95
2020-10-13 22:30 | 44117.9375 | 0 | 9.7489 | 39.95
2020-10-13 23:00 | 44117.9583 | 0 | 9.2341 | 39.95
2020-10-13 23:30 | 44117.9792 | 0 | 8.814 | 39.95
2020-10-14 | 44118 | 0 | 8.2271 | 39.95
2020-10-14 00:30 | 44118.0208 | 0 | 7.9295 | 39.95
2020-10-14 01:00 | 44118.0417 | 0 | 7.6936 | 39.95
2020-10-14 01:30 | 44118.0625 | 0 | 7.5831 | 39.95
2020-10-14 02:00 | 44118.0833 | 0 | 7.6135 | 39.95
2020-10-14 02:30 | 44118.1042 | 0 | 7.5112 | 39.95
2020-10-14 03:00 | 44118.125 | 0 | 7.5393 | 39.95
2020-10-14 03:30 | 44118.1458 | 0 | 7.6173 | 39.95
2020-10-14 04:00 | 44118.1667 | 0 | 7.7479 | 39.95
2020-10-14 04:30 | 44118.1875 | 0 | 8.181 | 39.95
2020-10-14 05:00 | 44118.2083 | 0 | 8.6265 | 39.95
2020-10-14 05:30 | 44118.2292 | 0 | 9.0097 | 39.95
2020-10-14 06:00 | 44118.25 | 0 | 9.6493 | 39.95
2020-10-14 06:30 | 44118.2708 | 0 | 9.9715 | 39.95
2020-10-14 07:00 | 44118.2917 | 0 | 10.1461 | 39.95
2020-10-14 07:30 | 44118.3125 | 0 | 9.8566 | 39.95
2020-10-14 08:00 | 44118.3333 | 0 | 10.0633 | 39.95
2020-10-14 08:30 | 44118.3542 | 0 | 10.7319 | 39.95
2020-10-14 09:00 | 44118.375 | 0 | 6.0232 | 39.95
2020-10-14 09:30 | 44118.3958 | 0 | 0.022333 | 39.95
2020-10-14 10:00 | 44118.4167 | 0 | 0.022333 | 39.95
2020-10-14 10:30 | 44118.4375 | 0 | 0.022333 | 39.95
2020-10-14 11:00 | 44118.4583 | 0 | 0.022333 | 39.95
2020-10-14 11:30 | 44118.4792 | 0 | 0.022333 | 39.95
2020-10-14 12:00 | 44118.5 | 0 | 0.022333 | 39.95
2020-10-14 12:30 | 44118.5208 | 0 | 0.022333 | 39.95
2020-10-14 13:00 | 44118.5417 | 0 | 3.6657 | 39.95
2020-10-14 13:30 | 44118.5625 | 0 | 9.7882 | 39.95
2020-10-14 14:00 | 44118.5833 | 0 | 9.951 | 39.95
2020-10-14 14:30 | 44118.6042 | 0 | 10.2269 | 39.95
2020-10-14 15:00 | 44118.625 | 0 | 10.6857 | 39.95
2020-10-14 15:30 | 44118.6458 | 0 | 11.2646 | 39.95
2020-10-14 16:00 | 44118.6667 | 0 | 11.7755 | 39.95
2020-10-14 16:30 | 44118.6875 | 0 | 12.2665 | 39.95
2020-10-14 17:00 | 44118.7083 | 0 | 12.4782 | 39.95
2020-10-14 17:30 | 44118.7292 | 0 | 12.6975 | 39.95
2020-10-14 18:00 | 44118.75 | 0 | 13.0779 | 39.95
2020-10-14 18:30 | 44118.7708 | 0 | 13.5617 | 39.95
2020-10-14 19:00 | 44118.7917 | 0 | 13.2733 | 39.95
2020-10-14 19:30 | 44118.8125 | 0 | 12.9921 | 39.95
2020-10-14 20:00 | 44118.8333 | 0 | 12.9639 | 39.95
2020-10-14 20:30 | 44118.8542 | 0 | 12.35 | 39.95
2020-10-14 21:00 | 44118.875 | 0 | 11.6759 | 39.95
2020-10-14 21:30 | 44118.8958 | 0 | 11.3449 | 39.95
2020-10-14 22:00 | 44118.9167 | 0 | 10.9623 | 39.95
2020-10-14 22:30 | 44118.9375 | 0 | 10.1574 | 39.95
2020-10-14 23:00 | 44118.9583 | 0 | 9.6183 | 39.95
2020-10-14 23:30 | 44118.9792 | 0 | 8.9895 | 39.95
2020-10-15 | 44119 | 0 | 8.4466 | 39.95
2020-10-15 00:30 | 44119.0208 | 0 | 8.0635 | 39.95
2020-10-15 01:00 | 44119.0417 | 0 | 7.8034 | 39.95
2020-10-15 01:30 | 44119.0625 | 0 | 7.7493 | 39.95
2020-10-15 02:00 | 44119.0833 | 0 | 7.6749 | 39.95
2020-10-15 02:30 | 44119.1042 | 0 | 7.69 | 39.95
2020-10-15 03:00 | 44119.125 | 0 | 7.662 | 39.95
2020-10-15 03:30 | 44119.1458 | 0 | 7.6861 | 39.95
2020-10-15 04:00 | 44119.1667 | 0 | 7.8894 | 39.95
2020-10-15 04:30 | 44119.1875 | 0 | 8.256 | 39.95
2020-10-15 05:00 | 44119.2083 | 0 | 8.6187 | 39.95
2020-10-15 05:30 | 44119.2292 | 0 | 8.9595 | 39.95
2020-10-15 06:00 | 44119.25 | 0 | 9.5254 | 39.95
2020-10-15 06:30 | 44119.2708 | 0 | 9.7223 | 39.95
2020-10-15 07:00 | 44119.2917 | 0 | 9.9846 | 39.95
2020-10-15 07:30 | 44119.3125 | 0 | 9.9248 | 39.95
2020-10-15 08:00 | 44119.3333 | 0 | 9.6567 | 39.95
2020-10-15 08:30 | 44119.3542 | 0 | 9.5191 | 39.95
2020-10-15 09:00 | 44119.375 | 0 | 9.4169 | 39.95
2020-10-15 09:30 | 44119.3958 | 0 | 9.2678 | 39.95
2020-10-15 10:00 | 44119.4167 | 0 | 9.3838 | 39.95
2020-10-15 10:30 | 44119.4375 | 0 | 9.4653 | 39.95
2020-10-15 11:00 | 44119.4583 | 0 | 9.512 | 39.95
2020-10-15 11:30 | 44119.4792 | 0 | 9.5269 | 39.95
2020-10-15 12:00 | 44119.5 | 0 | 9.5993 | 39.95
2020-10-15 12:30 | 44119.5208 | 0 | 9.6757 | 39.95
2020-10-15 13:00 | 44119.5417 | 0 | 9.6143 | 39.95
2020-10-15 13:30 | 44119.5625 | 0 | 9.8862 | 39.95
2020-10-15 14:00 | 44119.5833 | 0 | 10.3941 | 39.95
2020-10-15 14:30 | 44119.6042 | 0 | 10.8513 | 39.95
2020-10-15 15:00 | 44119.625 | 0 | 11.0647 | 39.95
2020-10-15 15:30 | 44119.6458 | 0 | 11.6616 | 39.95
2020-10-15 16:00 | 44119.6667 | 0 | 12.2272 | 39.95
2020-10-15 16:30 | 44119.6875 | 0 | 12.7097 | 39.95
2020-10-15 17:00 | 44119.7083 | 0 | 12.8212 | 39.95
2020-10-15 17:30 | 44119.7292 | 0 | 12.7277 | 39.95
2020-10-15 18:00 | 44119.75 | 0 | 12.8341 | 39.95
2020-10-15 18:30 | 44119.7708 | 0 | 13.2342 | 39.95
2020-10-15 19:00 | 44119.7917 | 0 | 12.9842 | 39.95
2020-10-15 19:30 | 44119.8125 | 0 | 12.8451 | 39.95
2020-10-15 20:00 | 44119.8333 | 0 | 12.7461 | 39.95
2020-10-15 20:30 | 44119.8542 | 0 | 12.223 | 39.95
2020-10-15 21:00 | 44119.875 | 0 | 11.8262 | 39.95
2020-10-15 21:30 | 44119.8958 | 0 | 11.531 | 39.95
2020-10-15 22:00 | 44119.9167 | 0 | 10.8241 | 39.95
2020-10-15 22:30 | 44119.9375 | 0 | 10.1072 | 39.95
2020-10-15 23:00 | 44119.9583 | 0 | 9.6575 | 39.95
2020-10-15 23:30 | 44119.9792 | 0 | 9.294 | 39.95
2020-10-16 | 44120 | 0 | 8.631 | 39.95
2020-10-16 00:30 | 44120.0208 | 0 | 8.2223 | 39.95
2020-10-16 01:00 | 44120.0417 | 0 | 7.9184 | 39.95
2020-10-16 01:30 | 44120.0625 | 0 | 7.7997 | 39.95
2020-10-16 02:00 | 44120.0833 | 0 | 7.7549 | 39.95
2020-10-16 02:30 | 44120.1042 | 0 | 7.6881 | 39.95
2020-10-16 03:00 | 44120.125 | 0 | 7.5334 | 39.95
2020-10-16 03:30 | 44120.1458 | 0 | 7.6212 | 39.95
2020-10-16 04:00 | 44120.1667 | 0 | 7.5819 | 39.95
2020-10-16 04:30 | 44120.1875 | 0 | 7.6676 | 39.95
2020-10-16 05:00 | 44120.2083 | 0 | 7.7606 | 39.95
2020-10-16 05:30 | 44120.2292 | 0 | 7.6804 | 39.95
2020-10-16 06:00 | 44120.25 | 0 | 7.7104 | 39.95
2020-10-16 06:30 | 44120.2708 | 0 | 7.5596 | 39.95
2020-10-16 07:00 | 44120.2917 | 0 | 7.6563 | 39.95
2020-10-16 07:30 | 44120.3125 | 0 | 7.5428 | 39.95
2020-10-16 08:00 | 44120.3333 | 0 | 8.1608 | 39.95
2020-10-16 08:30 | 44120.3542 | 0 | 7.933 | 39.95
2020-10-16 09:00 | 44120.375 | 0 | 8.1353 | 39.95
2020-10-16 09:30 | 44120.3958 | 0 | 7.6861 | 39.95
2020-10-16 10:00 | 44120.4167 | 0 | 7.2615 | 39.95
2020-10-16 10:30 | 44120.4375 | 0 | 7.0944 | 39.95
2020-10-16 11:00 | 44120.4583 | 0 | 7.135 | 39.95
2020-10-16 11:30 | 44120.4792 | 0 | 7.2082 | 39.95
2020-10-16 12:00 | 44120.5 | 0 | 7.2467 | 39.95
2020-10-16 12:30 | 44120.5208 | 0 | 7.169 | 39.95
2020-10-16 13:00 | 44120.5417 | 0 | 8.2668 | 39.95
2020-10-16 13:30 | 44120.5625 | 0 | 8.5541 | 39.95
2020-10-16 14:00 | 44120.5833 | 0 | 8.123 | 39.95
2020-10-16 14:30 | 44120.6042 | 0 | 9.0214 | 39.95
2020-10-16 15:00 | 44120.625 | 0 | 8.615 | 39.95
2020-10-16 15:30 | 44120.6458 | 0 | 8.7076 | 39.95
2020-10-16 16:00 | 44120.6667 | 0 | 9.3863 | 39.95
2020-10-16 16:30 | 44120.6875 | 0 | 9.9992 | 39.95
2020-10-16 17:00 | 44120.7083 | 0 | 10.3142 | 39.95
2020-10-16 17:30 | 44120.7292 | 0 | 10.6325 | 39.95
2020-10-16 18:00 | 44120.75 | 0 | 10.9972 | 39.95
2020-10-16 18:30 | 44120.7708 | 0 | 11.3543 | 39.95
2020-10-16 19:00 | 44120.7917 | 0 | 11.1063 | 39.95
2020-10-16 19:30 | 44120.8125 | 0 | 10.8109 | 39.95
2020-10-16 20:00 | 44120.8333 | 0 | 10.6002 | 39.95
2020-10-16 20:30 | 44120.8542 | 0 | 10.1666 | 39.95
2020-10-16 21:00 | 44120.875 | 0 | 9.9238 | 39.95
2020-10-16 21:30 | 44120.8958 | 0 | 9.7016 | 39.95
2020-10-16 22:00 | 44120.9167 | 0 | 9.448 | 39.95
2020-10-16 22:30 | 44120.9375 | 0 | 8.8815 | 39.95
2020-10-16 23:00 | 44120.9583 | 0 | 8.3777 | 39.95
2020-10-16 23:30 | 44120.9792 | 0 | 8.0673 | 39.95
2020-10-17 | 44121 | 0 | 7.7436 | 39.95
2020-10-17 00:30 | 44121.0208 | 0 | 7.4328 | 39.95
2020-10-17 01:00 | 44121.0417 | 0 | 7.1909 | 39.95
2020-10-17 01:30 | 44121.0625 | 0 | 7.0159 | 39.95
2020-10-17 02:00 | 44121.0833 | 0 | 7.0033 | 39.95
2020-10-17 02:30 | 44121.1042 | 0 | 6.9936 | 39.95
2020-10-17 03:00 | 44121.125 | 0 | 6.8692 | 39.95
2020-10-17 03:30 | 44121.1458 | 0 | 6.7648 | 39.95
2020-10-17 04:00 | 44121.1667 | 0 | 6.7092 | 39.95
2020-10-17 04:30 | 44121.1875 | 0 | 6.7426 | 39.95
2020-10-17 05:00 | 44121.2083 | 0 | 6.7873 | 39.95
2020-10-17 05:30 | 44121.2292 | 0 | 6.6661 | 39.95
2020-10-17 06:00 | 44121.25 | 0 | 6.5526 | 39.95
2020-10-17 06:30 | 44121.2708 | 0 | 6.4278 | 39.95
2020-10-17 07:00 | 44121.2917 | 0 | 6.2948 | 39.95
2020-10-17 07:30 | 44121.3125 | 0 | 6.2679 | 39.95
2020-10-17 08:00 | 44121.3333 | 0 | 6.3314 | 39.95
2020-10-17 08:30 | 44121.3542 | 0 | 6.3201 | 39.95
2020-10-17 09:00 | 44121.375 | 0 | 6.2606 | 39.95
2020-10-17 09:30 | 44121.3958 | 0 | 6.2289 | 39.95
2020-10-17 10:00 | 44121.4167 | 0 | 6.2606 | 39.95
2020-10-17 10:30 | 44121.4375 | 0 | 6.2261 | 39.95
2020-10-17 11:00 | 44121.4583 | 0 | 6.3517 | 39.95
2020-10-17 11:30 | 44121.4792 | 0 | 6.3145 | 39.95
2020-10-17 12:00 | 44121.5 | 0 | 7.1462 | 39.95
2020-10-17 12:30 | 44121.5208 | 0 | 7.3091 | 39.95
2020-10-17 13:00 | 44121.5417 | 0 | 6.58 | 39.95
2020-10-17 13:30 | 44121.5625 | 0 | 6.8557 | 39.95
2020-10-17 14:00 | 44121.5833 | 0 | 7.4694 | 39.95
2020-10-17 14:30 | 44121.6042 | 0 | 8.2872 | 39.95
2020-10-17 15:00 | 44121.625 | 0 | 8.4438 | 39.95
2020-10-17 15:30 | 44121.6458 | 0 | 9.0281 | 39.95
2020-10-17 16:00 | 44121.6667 | 0 | 9.6236 | 39.95
2020-10-17 16:30 | 44121.6875 | 0 | 10.4662 | 39.95
2020-10-17 17:00 | 44121.7083 | 0 | 10.837 | 39.95
2020-10-17 17:30 | 44121.7292 | 0 | 11.3413 | 39.95
2020-10-17 18:00 | 44121.75 | 0 | 11.8767 | 39.95
2020-10-17 18:30 | 44121.7708 | 0 | 12.3444 | 39.95
2020-10-17 19:00 | 44121.7917 | 0 | 12.018 | 39.95
2020-10-17 19:30 | 44121.8125 | 0 | 11.5771 | 39.95
2020-10-17 20:00 | 44121.8333 | 0 | 11.425 | 39.95
2020-10-17 20:30 | 44121.8542 | 0 | 11.0842 | 39.95
2020-10-17 21:00 | 44121.875 | 0 | 10.588 | 39.95
2020-10-17 21:30 | 44121.8958 | 0 | 10.1815 | 39.95
2020-10-17 22:00 | 44121.9167 | 0 | 9.6765 | 39.95
2020-10-17 22:30 | 44121.9375 | 0 | 9.0853 | 39.95
2020-10-17 23:00 | 44121.9583 | 0 | 8.4108 | 39.95
2020-10-17 23:30 | 44121.9792 | 0 | 8.1361 | 39.95
2020-10-18 | 44122 | 0 | 7.8407 | 39.95
2020-10-18 00:30 | 44122.0208 | 0 | 7.6489 | 39.95
2020-10-18 01:00 | 44122.0417 | 0 | 7.3711 | 39.95
2020-10-18 01:30 | 44122.0625 | 0 | 7.3401 | 39.95
2020-10-18 02:00 | 44122.0833 | 0 | 7.3678 | 39.95
2020-10-18 02:30 | 44122.1042 | 0 | 7.3326 | 39.95
2020-10-18 03:00 | 44122.125 | 0 | 7.3495 | 39.95
2020-10-18 03:30 | 44122.1458 | 0 | 7.4349 | 39.95
2020-10-18 04:00 | 44122.1667 | 0 | 7.6177 | 39.95
2020-10-18 04:30 | 44122.1875 | 0 | 7.9696 | 39.95
2020-10-18 05:00 | 44122.2083 | 0 | 8.4641 | 39.95
2020-10-18 05:30 | 44122.2292 | 0 | 8.9488 | 39.95
2020-10-18 06:00 | 44122.25 | 0 | 9.2196 | 39.95
2020-10-18 06:30 | 44122.2708 | 0 | 9.4781 | 39.95
2020-10-18 07:00 | 44122.2917 | 0 | 10.2615 | 39.95
2020-10-18 07:30 | 44122.3125 | 0 | 9.9621 | 39.95
2020-10-18 08:00 | 44122.3333 | 0 | 9.7982 | 39.95
2020-10-18 08:30 | 44122.3542 | 0 | 9.4622 | 39.95
2020-10-18 09:00 | 44122.375 | 0 | 9.2437 | 39.95
2020-10-18 09:30 | 44122.3958 | 0 | 9.2478 | 39.95
2020-10-18 10:00 | 44122.4167 | 0 | 9.1318 | 39.95
2020-10-18 10:30 | 44122.4375 | 0 | 9.0652 | 39.95
2020-10-18 11:00 | 44122.4583 | 0 | 9.4293 | 39.95
2020-10-18 11:30 | 44122.4792 | 0 | 9.9567 | 39.95
2020-10-18 12:00 | 44122.5 | 0 | 9.9644 | 39.95
2020-10-18 12:30 | 44122.5208 | 0 | 10.018 | 39.95
2020-10-18 13:00 | 44122.5417 | 0 | 10.9302 | 39.95
2020-10-18 13:30 | 44122.5625 | 0 | 11.3368 | 39.95
2020-10-18 14:00 | 44122.5833 | 0 | 12.414 | 39.95
2020-10-18 14:30 | 44122.6042 | 0 | 13.3046 | 39.95
2020-10-18 15:00 | 44122.625 | 0 | 13.5915 | 39.95
2020-10-18 15:30 | 44122.6458 | 0 | 13.2894 | 39.95
2020-10-18 16:00 | 44122.6667 | 0 | 12.8502 | 39.95
2020-10-18 16:30 | 44122.6875 | 0 | 13.0669 | 39.95
2020-10-18 17:00 | 44122.7083 | 0 | 13.0105 | 39.95
2020-10-18 17:30 | 44122.7292 | 0 | 13.3811 | 39.95
2020-10-18 18:00 | 44122.75 | 0 | 13.6288 | 39.95
2020-10-18 18:30 | 44122.7708 | 0 | 14.0525 | 39.95
2020-10-18 19:00 | 44122.7917 | 0 | 13.7461 | 39.95
2020-10-18 19:30 | 44122.8125 | 0 | 13.347 | 39.95
2020-10-18 20:00 | 44122.8333 | 0 | 13.2771 | 39.95
2020-10-18 20:30 | 44122.8542 | 0 | 12.7032 | 39.95
2020-10-18 21:00 | 44122.875 | 0 | 12.0719 | 39.95
2020-10-18 21:30 | 44122.8958 | 0 | 11.6822 | 39.95
2020-10-18 22:00 | 44122.9167 | 0 | 11.276 | 39.95
2020-10-18 22:30 | 44122.9375 | 0 | 10.5849 | 39.95
2020-10-18 23:00 | 44122.9583 | 0 | 9.9246 | 39.95
2020-10-18 23:30 | 44122.9792 | 0 | 9.4418 | 39.95
2020-10-19 | 44123 | 0 | 8.8961 | 39.95
2020-10-19 00:30 | 44123.0208 | 0 | 8.3946 | 39.95
2020-10-19 01:00 | 44123.0417 | 0 | 8.2296 | 39.95
2020-10-19 01:30 | 44123.0625 | 0 | 8.0653 | 39.95
2020-10-19 02:00 | 44123.0833 | 0 | 8.1011 | 39.95
2020-10-19 02:30 | 44123.1042 | 0 | 8.0378 | 39.95
2020-10-19 03:00 | 44123.125 | 0 | 7.8349 | 39.95
2020-10-19 03:30 | 44123.1458 | 0 | 7.8944 | 39.95
2020-10-19 04:00 | 44123.1667 | 0 | 7.9193 | 39.95
2020-10-19 04:30 | 44123.1875 | 0 | 8.2634 | 39.95
2020-10-19 05:00 | 44123.2083 | 0 | 8.7678 | 39.95
2020-10-19 05:30 | 44123.2292 | 0 | 9.339 | 39.95
2020-10-19 06:00 | 44123.25 | 0 | 9.6057 | 39.95
2020-10-19 06:30 | 44123.2708 | 0 | 10.1244 | 39.95
2020-10-19 07:00 | 44123.2917 | 0 | 10.4206 | 39.95
2020-10-19 07:30 | 44123.3125 | 0 | 10.4697 | 39.95
2020-10-19 08:00 | 44123.3333 | 0 | 10.8626 | 39.95
2020-10-19 08:30 | 44123.3542 | 0 | 9.8443 | 39.95
2020-10-19 09:00 | 44123.375 | 0 | 10.1769 | 39.95
2020-10-19 09:30 | 44123.3958 | 0 | 10.5481 | 39.95
2020-10-19 10:00 | 44123.4167 | 0 | 10.2965 | 39.95
2020-10-19 10:30 | 44123.4375 | 0 | 11.8447 | 39.95
2020-10-19 11:00 | 44123.4583 | 0 | 11.7084 | 39.95
2020-10-19 11:30 | 44123.4792 | 0 | 11.8998 | 39.95
2020-10-19 12:00 | 44123.5 | 0 | 11.1288 | 39.95
2020-10-19 12:30 | 44123.5208 | 0 | 9.7408 | 39.95
2020-10-19 13:00 | 44123.5417 | 0 | 10.8027 | 39.95
2020-10-19 13:30 | 44123.5625 | 0 | 10.7453 | 39.95
2020-10-19 14:00 | 44123.5833 | 0 | 10.8396 | 39.95
2020-10-19 14:30 | 44123.6042 | 0 | 11.4399 | 39.95
2020-10-19 15:00 | 44123.625 | 0 | 11.7003 | 39.95
2020-10-19 15:30 | 44123.6458 | 0 | 11.4009 | 39.95
2020-10-19 16:00 | 44123.6667 | 0 | 12.2008 | 39.95
2020-10-19 16:30 | 44123.6875 | 0 | 12.2499 | 39.95
2020-10-19 17:00 | 44123.7083 | 0 | 12.5872 | 39.95
2020-10-19 17:30 | 44123.7292 | 0 | 13.0204 | 39.95
2020-10-19 18:00 | 44123.75 | 0 | 13.6615 | 39.95
2020-10-19 18:30 | 44123.7708 | 0 | 14.1831 | 39.95
2020-10-19 19:00 | 44123.7917 | 0 | 13.8084 | 39.95
2020-10-19 19:30 | 44123.8125 | 0 | 13.6435 | 39.95
2020-10-19 20:00 | 44123.8333 | 0 | 13.3055 | 39.95
2020-10-19 20:30 | 44123.8542 | 0 | 12.7472 | 39.95
2020-10-19 21:00 | 44123.875 | 0 | 12.0999 | 39.95
2020-10-19 21:30 | 44123.8958 | 0 | 11.6055 | 39.95
2020-10-19 22:00 | 44123.9167 | 0 | 10.9617 | 39.95
2020-10-19 22:30 | 44123.9375 | 0 | 10.4394 | 39.95
2020-10-19 23:00 | 44123.9583 | 0 | 9.7292 | 39.95
2020-10-19 23:30 | 44123.9792 | 0 | 9.1331 | 39.95
2020-10-20 | 44124 | 0 | 8.4785 | 39.95
2020-10-20 00:30 | 44124.0208 | 0 | 8.2524 | 39.95
2020-10-20 01:00 | 44124.0417 | 0 | 7.9279 | 39.95
2020-10-20 01:30 | 44124.0625 | 0 | 7.8705 | 39.95
2020-10-20 02:00 | 44124.0833 | 0 | 8.0231 | 39.95
2020-10-20 02:30 | 44124.1042 | 0 | 7.9057 | 39.95
2020-10-20 03:00 | 44124.125 | 0 | 7.8293 | 39.95
2020-10-20 03:30 | 44124.1458 | 0 | 7.9375 | 39.95
2020-10-20 04:00 | 44124.1667 | 0 | 7.9991 | 39.95
2020-10-20 04:30 | 44124.1875 | 0 | 8.3894 | 39.95
2020-10-20 05:00 | 44124.2083 | 0 | 8.6857 | 39.95
2020-10-20 05:30 | 44124.2292 | 0 | 9.0823 | 39.95
2020-10-20 06:00 | 44124.25 | 0 | 9.4195 | 39.95
2020-10-20 06:30 | 44124.2708 | 0 | 9.952 | 39.95
2020-10-20 07:00 | 44124.2917 | 0 | 10.3718 | 39.95
2020-10-20 07:30 | 44124.3125 | 0 | 10.0604 | 39.95
2020-10-20 08:00 | 44124.3333 | 0 | 9.9623 | 39.95
2020-10-20 08:30 | 44124.3542 | 0 | 10.2075 | 39.95
2020-10-20 09:00 | 44124.375 | 0 | 10.3579 | 39.95
2020-10-20 09:30 | 44124.3958 | 0 | 10.258 | 39.95
2020-10-20 10:00 | 44124.4167 | 0 | 9.5177 | 39.95
2020-10-20 10:30 | 44124.4375 | 0 | 9.9761 | 39.95
2020-10-20 11:00 | 44124.4583 | 0 | 9.8318 | 39.95
2020-10-20 11:30 | 44124.4792 | 0 | 9.6264 | 39.95
2020-10-20 12:00 | 44124.5 | 0 | 10.6999 | 39.95
2020-10-20 12:30 | 44124.5208 | 0 | 9.7563 | 39.95
2020-10-20 13:00 | 44124.5417 | 0 | 12.1428 | 39.95
2020-10-20 13:30 | 44124.5625 | 0 | 11.9981 | 39.95
2020-10-20 14:00 | 44124.5833 | 0 | 12.4658 | 39.95
2020-10-20 14:30 | 44124.6042 | 0 | 12.9399 | 39.95
2020-10-20 15:00 | 44124.625 | 0 | 12.7686 | 39.95
2020-10-20 15:30 | 44124.6458 | 0 | 13.0203 | 39.95
2020-10-20 16:00 | 44124.6667 | 0 | 12.7011 | 39.95
2020-10-20 16:30 | 44124.6875 | 0 | 12.7656 | 39.95
2020-10-20 17:00 | 44124.7083 | 0 | 12.7942 | 39.95
2020-10-20 17:30 | 44124.7292 | 0 | 13.0912 | 39.95
2020-10-20 18:00 | 44124.75 | 0 | 13.382 | 39.95
2020-10-20 18:30 | 44124.7708 | 0 | 13.8443 | 39.95
2020-10-20 19:00 | 44124.7917 | 0 | 13.6075 | 39.95
2020-10-20 19:30 | 44124.8125 | 0 | 13.2527 | 39.95
2020-10-20 20:00 | 44124.8333 | 0 | 12.91 | 39.95
2020-10-20 20:30 | 44124.8542 | 0 | 12.4342 | 39.95
2020-10-20 21:00 | 44124.875 | 0 | 11.8951 | 39.95
2020-10-20 21:30 | 44124.8958 | 0 | 11.4818 | 39.95
2020-10-20 22:00 | 44124.9167 | 0 | 10.8819 | 39.95
2020-10-20 22:30 | 44124.9375 | 0 | 10.0437 | 39.95
2020-10-20 23:00 | 44124.9583 | 0 | 9.4875 | 39.95
2020-10-20 23:30 | 44124.9792 | 0 | 9.1411 | 39.95
2020-10-21 | 44125 | 0 | 8.5849 | 39.95
2020-10-21 00:30 | 44125.0208 | 0 | 8.2889 | 39.95
2020-10-21 01:00 | 44125.0417 | 0 | 7.9504 | 39.95
2020-10-21 01:30 | 44125.0625 | 0 | 7.9801 | 39.95
2020-10-21 02:00 | 44125.0833 | 0 | 7.9953 | 39.95
2020-10-21 02:30 | 44125.1042 | 0 | 7.8236 | 39.95
2020-10-21 03:00 | 44125.125 | 0 | 7.8612 | 39.95
2020-10-21 03:30 | 44125.1458 | 0 | 7.8349 | 39.95
2020-10-21 04:00 | 44125.1667 | 0 | 8.0122 | 39.95
2020-10-21 04:30 | 44125.1875 | 0 | 8.4863 | 39.95
2020-10-21 05:00 | 44125.2083 | 0 | 8.9671 | 39.95
2020-10-21 05:30 | 44125.2292 | 0 | 9.3668 | 39.95
2020-10-21 06:00 | 44125.25 | 0 | 9.9768 | 39.95
2020-10-21 06:30 | 44125.2708 | 0 | 10.3736 | 39.95
2020-10-21 07:00 | 44125.2917 | 0 | 11.3031 | 39.95
2020-10-21 07:30 | 44125.3125 | 0 | 12.2031 | 39.95
2020-10-21 08:00 | 44125.3333 | 0 | 12.5513 | 39.95
2020-10-21 08:30 | 44125.3542 | 0 | 11.8402 | 39.95
2020-10-21 09:00 | 44125.375 | 0 | 11.4772 | 39.95
2020-10-21 09:30 | 44125.3958 | 0 | 11.3178 | 39.95
2020-10-21 10:00 | 44125.4167 | 0 | 11.0131 | 39.95
2020-10-21 10:30 | 44125.4375 | 0 | 12.0182 | 39.95
2020-10-21 11:00 | 44125.4583 | 0 | 12.3655 | 39.95
2020-10-21 11:30 | 44125.4792 | 0 | 12.5814 | 39.95
2020-10-21 12:00 | 44125.5 | 0 | 12.3672 | 39.95
2020-10-21 12:30 | 44125.5208 | 0 | 13.1912 | 39.95
2020-10-21 13:00 | 44125.5417 | 0 | 11.7819 | 39.95
2020-10-21 13:30 | 44125.5625 | 0 | 10.9879 | 39.95
2020-10-21 14:00 | 44125.5833 | 0 | 11.9114 | 39.95
2020-10-21 14:30 | 44125.6042 | 0 | 12.7304 | 39.95
2020-10-21 15:00 | 44125.625 | 0 | 12.5289 | 39.95
2020-10-21 15:30 | 44125.6458 | 0 | 12.7681 | 39.95
2020-10-21 16:00 | 44125.6667 | 0 | 12.3629 | 39.95
2020-10-21 16:30 | 44125.6875 | 0 | 12.4731 | 39.95
2020-10-21 17:00 | 44125.7083 | 0 | 12.7377 | 39.95
2020-10-21 17:30 | 44125.7292 | 0 | 13.1861 | 39.95
2020-10-21 18:00 | 44125.75 | 0 | 13.5776 | 39.95
2020-10-21 18:30 | 44125.7708 | 0 | 14.0472 | 39.95
2020-10-21 19:00 | 44125.7917 | 0 | 13.8591 | 39.95
2020-10-21 19:30 | 44125.8125 | 0 | 13.4478 | 39.95
2020-10-21 20:00 | 44125.8333 | 0 | 13.3279 | 39.95
2020-10-21 20:30 | 44125.8542 | 0 | 12.7887 | 39.95
2020-10-21 21:00 | 44125.875 | 0 | 12.2208 | 39.95
2020-10-21 21:30 | 44125.8958 | 0 | 11.8882 | 39.95
2020-10-21 22:00 | 44125.9167 | 0 | 11.4367 | 39.95
2020-10-21 22:30 | 44125.9375 | 0 | 10.6148 | 39.95
2020-10-21 23:00 | 44125.9583 | 0 | 9.8193 | 39.95
2020-10-21 23:30 | 44125.9792 | 0 | 9.223 | 39.95
2020-10-22 | 44126 | 0 | 8.7837 | 39.95
2020-10-22 00:30 | 44126.0208 | 0 | 8.4755 | 39.95
2020-10-22 01:00 | 44126.0417 | 0 | 8.2144 | 39.95
2020-10-22 01:30 | 44126.0625 | 0 | 8.1886 | 39.95
2020-10-22 02:00 | 44126.0833 | 0 | 8.1776 | 39.95
2020-10-22 02:30 | 44126.1042 | 0 | 8.1233 | 39.95
2020-10-22 03:00 | 44126.125 | 0 | 8.1068 | 39.95
2020-10-22 03:30 | 44126.1458 | 0 | 8.1682 | 39.95
2020-10-22 04:00 | 44126.1667 | 0 | 8.2932 | 39.95
2020-10-22 04:30 | 44126.1875 | 0 | 8.6431 | 39.95
2020-10-22 05:00 | 44126.2083 | 0 | 9.0859 | 39.95
2020-10-22 05:30 | 44126.2292 | 0 | 9.3261 | 39.95
2020-10-22 06:00 | 44126.25 | 0 | 10.2187 | 39.95
2020-10-22 06:30 | 44126.2708 | 0 | 11.0603 | 39.95
2020-10-22 07:00 | 44126.2917 | 0 | 11.9664 | 39.95
2020-10-22 07:30 | 44126.3125 | 0 | 12.0465 | 39.95
2020-10-22 08:00 | 44126.3333 | 0 | 12.2745 | 39.95
2020-10-22 08:30 | 44126.3542 | 0 | 11.9409 | 39.95
2020-10-22 09:00 | 44126.375 | 0 | 12.5664 | 39.95
2020-10-22 09:30 | 44126.3958 | 0 | 12.2575 | 39.95
2020-10-22 10:00 | 44126.4167 | 0 | 12.4269 | 39.95
2020-10-22 10:30 | 44126.4375 | 0 | 11.2785 | 39.95
2020-10-22 11:00 | 44126.4583 | 0 | 12.4848 | 39.95
2020-10-22 11:30 | 44126.4792 | 0 | 12.59 | 39.95
2020-10-22 12:00 | 44126.5 | 0 | 12.2586 | 39.95
2020-10-22 12:30 | 44126.5208 | 0 | 9.9985 | 39.95
2020-10-22 13:00 | 44126.5417 | 0 | 10.7013 | 39.95
2020-10-22 13:30 | 44126.5625 | 0 | 11.13 | 39.95
2020-10-22 14:00 | 44126.5833 | 0 | 11.0954 | 39.95
2020-10-22 14:30 | 44126.6042 | 0 | 11.3046 | 39.95
2020-10-22 15:00 | 44126.625 | 0 | 11.8166 | 39.95
2020-10-22 15:30 | 44126.6458 | 0 | 11.9549 | 39.95
2020-10-22 16:00 | 44126.6667 | 0 | 12.7611 | 39.95
2020-10-22 16:30 | 44126.6875 | 0 | 13.2806 | 39.95
2020-10-22 17:00 | 44126.7083 | 0 | 13.2207 | 39.95
2020-10-22 17:30 | 44126.7292 | 0 | 13.3703 | 39.95
2020-10-22 18:00 | 44126.75 | 0 | 13.6229 | 39.95
2020-10-22 18:30 | 44126.7708 | 0 | 13.7773 | 39.95
2020-10-22 19:00 | 44126.7917 | 0 | 13.4475 | 39.95
2020-10-22 19:30 | 44126.8125 | 0 | 13.2658 | 39.95
2020-10-22 20:00 | 44126.8333 | 0 | 13.1069 | 39.95
2020-10-22 20:30 | 44126.8542 | 0 | 12.664 | 39.95
2020-10-22 21:00 | 44126.875 | 0 | 12.0822 | 39.95
2020-10-22 21:30 | 44126.8958 | 0 | 11.9852 | 39.95
2020-10-22 22:00 | 44126.9167 | 0 | 11.5792 | 39.95
2020-10-22 22:30 | 44126.9375 | 0 | 10.6348 | 39.95
2020-10-22 23:00 | 44126.9583 | 0 | 10.1376 | 39.95
2020-10-22 23:30 | 44126.9792 | 0 | 9.7885 | 39.95
2020-10-23 | 44127 | 0 | 9.0641 | 39.95
2020-10-23 00:30 | 44127.0208 | 0 | 8.6163 | 39.95
2020-10-23 01:00 | 44127.0417 | 0 | 8.4973 | 39.95
2020-10-23 01:30 | 44127.0625 | 0 | 8.4026 | 39.95
2020-10-23 02:00 | 44127.0833 | 0 | 8.3863 | 39.95
2020-10-23 02:30 | 44127.1042 | 0 | 8.3727 | 39.95
2020-10-23 03:00 | 44127.125 | 0 | 8.3207 | 39.95
2020-10-23 03:30 | 44127.1458 | 0 | 8.3189 | 39.95
2020-10-23 04:00 | 44127.1667 | 0 | 8.3972 | 39.95
2020-10-23 04:30 | 44127.1875 | 0 | 8.343 | 39.95
2020-10-23 05:00 | 44127.2083 | 0 | 8.4697 | 39.95
2020-10-23 05:30 | 44127.2292 | 0 | 8.619 | 39.95
2020-10-23 06:00 | 44127.25 | 0 | 8.8574 | 39.95
2020-10-23 06:30 | 44127.2708 | 0 | 9.3298 | 39.95
2020-10-23 07:00 | 44127.2917 | 0 | 8.398 | 39.95
2020-10-23 07:30 | 44127.3125 | 0 | 9.1222 | 39.95
2020-10-23 08:00 | 44127.3333 | 0 | 10.1347 | 39.95
2020-10-23 08:30 | 44127.3542 | 0 | 9.9686 | 39.95
2020-10-23 09:00 | 44127.375 | 0 | 10.5971 | 39.95
2020-10-23 09:30 | 44127.3958 | 0 | 10.7544 | 39.95
2020-10-23 10:00 | 44127.4167 | 0 | 10.9724 | 39.95
2020-10-23 10:30 | 44127.4375 | 0 | 11.0452 | 39.95
2020-10-23 11:00 | 44127.4583 | 0 | 10.6172 | 39.95
2020-10-23 11:30 | 44127.4792 | 0 | 11.0787 | 39.95
2020-10-23 12:00 | 44127.5 | 0 | 10.5929 | 39.95
2020-10-23 12:30 | 44127.5208 | 0 | 10.3515 | 39.95
2020-10-23 13:00 | 44127.5417 | 0 | 11.319 | 39.95
2020-10-23 13:30 | 44127.5625 | 0 | 11.7299 | 39.95
2020-10-23 14:00 | 44127.5833 | 0 | 11.675 | 39.95
2020-10-23 14:30 | 44127.6042 | 0 | 12.041 | 39.95
2020-10-23 15:00 | 44127.625 | 0 | 11.6814 | 39.95
2020-10-23 15:30 | 44127.6458 | 0 | 11.4227 | 39.95
2020-10-23 16:00 | 44127.6667 | 0 | 11.4083 | 39.95
2020-10-23 16:30 | 44127.6875 | 0 | 11.5202 | 39.95
2020-10-23 17:00 | 44127.7083 | 0 | 11.462 | 39.95
2020-10-23 17:30 | 44127.7292 | 0 | 11.5369 | 39.95
2020-10-23 18:00 | 44127.75 | 0 | 11.7025 | 39.95
2020-10-23 18:30 | 44127.7708 | 0 | 11.7702 | 39.95
2020-10-23 19:00 | 44127.7917 | 0 | 11.3746 | 39.95
2020-10-23 19:30 | 44127.8125 | 0 | 10.9892 | 39.95
2020-10-23 20:00 | 44127.8333 | 0 | 10.8461 | 39.95
2020-10-23 20:30 | 44127.8542 | 0 | 10.5089 | 39.95
2020-10-23 21:00 | 44127.875 | 0 | 10.0311 | 39.95
2020-10-23 21:30 | 44127.8958 | 0 | 9.8022 | 39.95
2020-10-23 22:00 | 44127.9167 | 0 | 9.6962 | 39.95
2020-10-23 22:30 | 44127.9375 | 0 | 9.0219 | 39.95
2020-10-23 23:00 | 44127.9583 | 0 | 8.7271 | 39.95
2020-10-23 23:30 | 44127.9792 | 0 | 8.4375 | 39.95
2020-10-24 | 44128 | 0 | 8.0257 | 39.95
2020-10-24 00:30 | 44128.0208 | 0 | 7.7343 | 39.95
2020-10-24 01:00 | 44128.0417 | 0 | 7.4514 | 39.95
2020-10-24 01:30 | 44128.0625 | 0 | 7.2041 | 39.95
2020-10-24 02:00 | 44128.0833 | 0 | 7.2694 | 39.95
2020-10-24 02:30 | 44128.1042 | 0 | 7.1294 | 39.95
2020-10-24 03:00 | 44128.125 | 0 | 7.0534 | 39.95
2020-10-24 03:30 | 44128.1458 | 0 | 7.0272 | 39.95
2020-10-24 04:00 | 44128.1667 | 0 | 6.9621 | 39.95
2020-10-24 04:30 | 44128.1875 | 0 | 6.9232 | 39.95
2020-10-24 05:00 | 44128.2083 | 0 | 6.9081 | 39.95
2020-10-24 05:30 | 44128.2292 | 0 | 6.8395 | 39.95
2020-10-24 06:00 | 44128.25 | 0 | 6.6125 | 39.95
2020-10-24 06:30 | 44128.2708 | 0 | 6.6673 | 39.95
2020-10-24 07:00 | 44128.2917 | 0 | 6.9731 | 39.95
2020-10-24 07:30 | 44128.3125 | 0 | 8.4838 | 39.95
2020-10-24 08:00 | 44128.3333 | 0 | 7.9325 | 39.95
2020-10-24 08:30 | 44128.3542 | 0 | 6.9211 | 39.95
2020-10-24 09:00 | 44128.375 | 0 | 7.5987 | 39.95
2020-10-24 09:30 | 44128.3958 | 0 | 8.7914 | 39.95
2020-10-24 10:00 | 44128.4167 | 0 | 8.5729 | 39.95
2020-10-24 10:30 | 44128.4375 | 0 | 9.4007 | 39.95
2020-10-24 11:00 | 44128.4583 | 0 | 8.1291 | 39.95
2020-10-24 11:30 | 44128.4792 | 0 | 9.7158 | 39.95
2020-10-24 12:00 | 44128.5 | 0 | 8.498 | 39.95
2020-10-24 12:30 | 44128.5208 | 0 | 9.7312 | 39.95
2020-10-24 13:00 | 44128.5417 | 0 | 9.9714 | 39.95
2020-10-24 13:30 | 44128.5625 | 0 | 11.8218 | 39.95
2020-10-24 14:00 | 44128.5833 | 0 | 11.9975 | 39.95
2020-10-24 14:30 | 44128.6042 | 0 | 11.103 | 39.95
2020-10-24 15:00 | 44128.625 | 0 | 8.6589 | 39.95
2020-10-24 15:30 | 44128.6458 | 0 | 9.3091 | 39.95
2020-10-24 16:00 | 44128.6667 | 0 | 10.4073 | 39.95
2020-10-24 16:30 | 44128.6875 | 0 | 10.5086 | 39.95
2020-10-24 17:00 | 44128.7083 | 0 | 10.9027 | 39.95
2020-10-24 17:30 | 44128.7292 | 0 | 11.439 | 39.95
2020-10-24 18:00 | 44128.75 | 0 | 12.1225 | 39.95
2020-10-24 18:30 | 44128.7708 | 0 | 12.6737 | 39.95
2020-10-24 19:00 | 44128.7917 | 0 | 12.4649 | 39.95
2020-10-24 19:30 | 44128.8125 | 0 | 12.149 | 39.95
2020-10-24 20:00 | 44128.8333 | 0 | 11.8025 | 39.95
2020-10-24 20:30 | 44128.8542 | 0 | 11.3558 | 39.95
2020-10-24 21:00 | 44128.875 | 0 | 10.8407 | 39.95
2020-10-24 21:30 | 44128.8958 | 0 | 10.5052 | 39.95
2020-10-24 22:00 | 44128.9167 | 0 | 10.0549 | 39.95
2020-10-24 22:30 | 44128.9375 | 0 | 9.4959 | 39.95
2020-10-24 23:00 | 44128.9583 | 0 | 8.83 | 39.95
2020-10-24 23:30 | 44128.9792 | 0 | 8.6445 | 39.95
2020-10-25 | 44129 | 0 | 8.3497 | 39.95
2020-10-25 00:30 | 44129.0208 | 0 | 8.0711 | 39.95
2020-10-25 01:00 | 44129.0417 | 0 | 7.7865 | 39.95
2020-10-25 01:30 | 44129.0625 | 0 | 7.7009 | 39.95
2020-10-25 02:00 | 44129.0833 | 0 | 7.7235 | 39.95
2020-10-25 02:30 | 44129.1042 | 0 | 7.753 | 39.95
2020-10-25 03:00 | 44129.125 | 0 | 7.5805 | 39.95
2020-10-25 03:30 | 44129.1458 | 0 | 7.8188 | 39.95
2020-10-25 04:00 | 44129.1667 | 0 | 8.1678 | 39.95
2020-10-25 04:30 | 44129.1875 | 0 | 8.5993 | 39.95
2020-10-25 05:00 | 44129.2083 | 0 | 8.9962 | 39.95
2020-10-25 05:30 | 44129.2292 | 0 | 9.4356 | 39.95
2020-10-25 06:00 | 44129.25 | 0 | 10.1871 | 39.95
2020-10-25 06:30 | 44129.2708 | 0 | 11.0782 | 39.95
2020-10-25 07:00 | 44129.2917 | 0 | 11.1472 | 39.95
2020-10-25 07:30 | 44129.3125 | 0 | 11.6153 | 39.95
2020-10-25 08:00 | 44129.3333 | 0 | 12.6433 | 39.95
2020-10-25 08:30 | 44129.3542 | 0 | 12.8222 | 39.95
2020-10-25 09:00 | 44129.375 | 0 | 13.3523 | 39.95
2020-10-25 09:30 | 44129.3958 | 0 | 12.046 | 39.95
2020-10-25 10:00 | 44129.4167 | 0 | 10.5573 | 39.95
2020-10-25 10:30 | 44129.4375 | 0 | 10.6154 | 39.95
2020-10-25 11:00 | 44129.4583 | 0 | 10.8407 | 39.95
2020-10-25 11:30 | 44129.4792 | 0 | 11.3027 | 39.95
2020-10-25 12:00 | 44129.5 | 0 | 11.5423 | 39.95
2020-10-25 12:30 | 44129.5208 | 0 | 11.7628 | 39.95
2020-10-25 13:00 | 44129.5417 | 0 | 12.6175 | 39.95
2020-10-25 13:30 | 44129.5625 | 0 | 12.5057 | 39.95
2020-10-25 14:00 | 44129.5833 | 0 | 14.983 | 39.95
2020-10-25 14:30 | 44129.6042 | 0 | 13.854 | 39.95
2020-10-25 15:00 | 44129.625 | 0 | 13.0144 | 39.95
2020-10-25 15:30 | 44129.6458 | 0 | 13.4604 | 39.95
2020-10-25 16:00 | 44129.6667 | 0 | 14.1401 | 39.95
2020-10-25 16:30 | 44129.6875 | 0 | 14.3601 | 39.95
2020-10-25 17:00 | 44129.7083 | 0 | 14.3821 | 39.95
2020-10-25 17:30 | 44129.7292 | 0 | 14.8088 | 39.95
2020-10-25 18:00 | 44129.75 | 0 | 15.3479 | 39.95
2020-10-25 18:30 | 44129.7708 | 0 | 15.8858 | 39.95
2020-10-25 19:00 | 44129.7917 | 0 | 15.46 | 39.95
2020-10-25 19:30 | 44129.8125 | 0 | 14.9682 | 39.95
2020-10-25 20:00 | 44129.8333 | 0 | 14.5708 | 39.95
2020-10-25 20:30 | 44129.8542 | 0 | 13.8717 | 39.95
2020-10-25 21:00 | 44129.875 | 0 | 13.264 | 39.95
2020-10-25 21:30 | 44129.8958 | 0 | 12.7964 | 39.95
2020-10-25 22:00 | 44129.9167 | 0 | 12.2829 | 39.95
2020-10-25 22:30 | 44129.9375 | 0 | 11.5031 | 39.95
2020-10-25 23:00 | 44129.9583 | 0 | 10.8235 | 39.95
2020-10-25 23:30 | 44129.9792 | 0 | 10.255 | 39.95
2020-10-26 | 44130 | 0 | 9.6417 | 39.95
2020-10-26 00:30 | 44130.0208 | 0 | 9.1517 | 39.95
2020-10-26 01:00 | 44130.0417 | 0 | 8.8718 | 39.95
2020-10-26 01:30 | 44130.0625 | 0 | 8.7951 | 39.95
2020-10-26 02:00 | 44130.0833 | 0 | 8.6461 | 39.95
2020-10-26 02:30 | 44130.1042 | 0 | 8.4715 | 39.95
2020-10-26 03:00 | 44130.125 | 0 | 8.4716 | 39.95
2020-10-26 03:30 | 44130.1458 | 0 | 8.6337 | 39.95
2020-10-26 04:00 | 44130.1667 | 0 | 8.857 | 39.95
2020-10-26 04:30 | 44130.1875 | 0 | 9.1848 | 39.95
2020-10-26 05:00 | 44130.2083 | 0 | 9.5715 | 39.95
2020-10-26 05:30 | 44130.2292 | 0 | 10.015 | 39.95
2020-10-26 06:00 | 44130.25 | 0 | 10.3895 | 39.95
2020-10-26 06:30 | 44130.2708 | 0 | 11.7852 | 39.95
2020-10-26 07:00 | 44130.2917 | 0 | 12.2667 | 39.95
2020-10-26 07:30 | 44130.3125 | 0 | 12.8808 | 39.95
2020-10-26 08:00 | 44130.3333 | 0 | 12.081 | 39.95
2020-10-26 08:30 | 44130.3542 | 0 | 11.9955 | 39.95
2020-10-26 09:00 | 44130.375 | 0 | 12.7593 | 39.95
2020-10-26 09:30 | 44130.3958 | 0 | 12.7919 | 39.95
2020-10-26 10:00 | 44130.4167 | 0 | 12.655 | 39.95
2020-10-26 10:30 | 44130.4375 | 0 | 12.7804 | 39.95
2020-10-26 11:00 | 44130.4583 | 0 | 14.1719 | 39.95
2020-10-26 11:30 | 44130.4792 | 0 | 14.1324 | 39.95
2020-10-26 12:00 | 44130.5 | 0 | 12.9103 | 39.95
2020-10-26 12:30 | 44130.5208 | 0 | 12.6453 | 39.95
2020-10-26 13:00 | 44130.5417 | 0 | 13.2643 | 39.95
2020-10-26 13:30 | 44130.5625 | 0 | 13.5789 | 39.95
2020-10-26 14:00 | 44130.5833 | 0 | 13.8336 | 39.95
2020-10-26 14:30 | 44130.6042 | 0 | 14.0134 | 39.95
2020-10-26 15:00 | 44130.625 | 0 | 13.8872 | 39.95
2020-10-26 15:30 | 44130.6458 | 0 | 13.9895 | 39.95
2020-10-26 16:00 | 44130.6667 | 0 | 14.1556 | 39.95
2020-10-26 16:30 | 44130.6875 | 0 | 14.5008 | 39.95
2020-10-26 17:00 | 44130.7083 | 0 | 14.3092 | 39.95
2020-10-26 17:30 | 44130.7292 | 0 | 14.4085 | 39.95
2020-10-26 18:00 | 44130.75 | 0 | 14.5089 | 39.95
2020-10-26 18:30 | 44130.7708 | 0 | 14.6241 | 39.95
2020-10-26 19:00 | 44130.7917 | 0 | 14.2297 | 39.95
2020-10-26 19:30 | 44130.8125 | 0 | 13.7547 | 39.95
2020-10-26 20:00 | 44130.8333 | 0 | 13.5862 | 39.95
2020-10-26 20:30 | 44130.8542 | 0 | 12.9684 | 39.95
2020-10-26 21:00 | 44130.875 | 0 | 12.3176 | 39.95
2020-10-26 21:30 | 44130.8958 | 0 | 11.8028 | 39.95
2020-10-26 22:00 | 44130.9167 | 0 | 11.4188 | 39.95
2020-10-26 22:30 | 44130.9375 | 0 | 10.4988 | 39.95
2020-10-26 23:00 | 44130.9583 | 0 | 9.9597 | 39.95
2020-10-26 23:30 | 44130.9792 | 0 | 9.5678 | 39.95
2020-10-27 | 44131 | 0 | 8.9661 | 39.95
2020-10-27 00:30 | 44131.0208 | 0 | 8.5592 | 39.95
2020-10-27 01:00 | 44131.0417 | 0 | 8.3653 | 39.95
2020-10-27 01:30 | 44131.0625 | 0 | 8.3413 | 39.95
2020-10-27 02:00 | 44131.0833 | 0 | 8.3375 | 39.95
2020-10-27 02:30 | 44131.1042 | 0 | 8.1513 | 39.95
2020-10-27 03:00 | 44131.125 | 0 | 8.1792 | 39.95
2020-10-27 03:30 | 44131.1458 | 0 | 8.4832 | 39.95
2020-10-27 04:00 | 44131.1667 | 0 | 8.8684 | 39.95
2020-10-27 04:30 | 44131.1875 | 0 | 9.1393 | 39.95
2020-10-27 05:00 | 44131.2083 | 0 | 9.5719 | 39.95
2020-10-27 05:30 | 44131.2292 | 0 | 10.0303 | 39.95
2020-10-27 06:00 | 44131.25 | 0 | 10.6615 | 39.95
2020-10-27 06:30 | 44131.2708 | 0 | 10.8198 | 39.95
2020-10-27 07:00 | 44131.2917 | 0 | 11.3207 | 39.95
2020-10-27 07:30 | 44131.3125 | 0 | 11.3021 | 39.95
2020-10-27 08:00 | 44131.3333 | 0 | 11.1663 | 39.95
2020-10-27 08:30 | 44131.3542 | 0 | 11.8007 | 39.95
2020-10-27 09:00 | 44131.375 | 0 | 13.4788 | 39.95
2020-10-27 09:30 | 44131.3958 | 0 | 12.5209 | 39.95
2020-10-27 10:00 | 44131.4167 | 0 | 11.9227 | 39.95
2020-10-27 10:30 | 44131.4375 | 0 | 12.1998 | 39.95
2020-10-27 11:00 | 44131.4583 | 0 | 12.4732 | 39.95
2020-10-27 11:30 | 44131.4792 | 0 | 11.5537 | 39.95
2020-10-27 12:00 | 44131.5 | 0 | 12.1688 | 39.95
2020-10-27 12:30 | 44131.5208 | 0 | 12.3371 | 39.95
2020-10-27 13:00 | 44131.5417 | 0 | 11.5422 | 39.95
2020-10-27 13:30 | 44131.5625 | 0 | 13.5827 | 39.95
2020-10-27 14:00 | 44131.5833 | 0 | 15.4205 | 39.95
2020-10-27 14:30 | 44131.6042 | 0 | 15.3044 | 39.95
2020-10-27 15:00 | 44131.625 | 0 | 15.041 | 39.95
2020-10-27 15:30 | 44131.6458 | 0 | 13.0211 | 39.95
2020-10-27 16:00 | 44131.6667 | 0 | 13.1032 | 39.95
2020-10-27 16:30 | 44131.6875 | 0 | 13.9535 | 39.95
2020-10-27 17:00 | 44131.7083 | 0 | 13.7533 | 39.95
2020-10-27 17:30 | 44131.7292 | 0 | 14.1939 | 39.95
2020-10-27 18:00 | 44131.75 | 0 | 14.4793 | 39.95
2020-10-27 18:30 | 44131.7708 | 0 | 15.1507 | 39.95
2020-10-27 19:00 | 44131.7917 | 0 | 14.7456 | 39.95
2020-10-27 19:30 | 44131.8125 | 0 | 14.4141 | 39.95
2020-10-27 20:00 | 44131.8333 | 0 | 14.1675 | 39.95
2020-10-27 20:30 | 44131.8542 | 0 | 13.5447 | 39.95
2020-10-27 21:00 | 44131.875 | 0 | 12.9072 | 39.95
2020-10-27 21:30 | 44131.8958 | 0 | 12.3733 | 39.95
2020-10-27 22:00 | 44131.9167 | 0 | 11.7243 | 39.95
2020-10-27 22:30 | 44131.9375 | 0 | 10.9039 | 39.95
2020-10-27 23:00 | 44131.9583 | 0 | 10.2357 | 39.95
2020-10-27 23:30 | 44131.9792 | 0 | 9.7312 | 39.95
2020-10-28 | 44132 | 0 | 9.2007 | 39.95
2020-10-28 00:30 | 44132.0208 | 0 | 8.7645 | 39.95
2020-10-28 01:00 | 44132.0417 | 0 | 8.4678 | 39.95
2020-10-28 01:30 | 44132.0625 | 0 | 8.4154 | 39.95
2020-10-28 02:00 | 44132.0833 | 0 | 8.4007 | 39.95
2020-10-28 02:30 | 44132.1042 | 0 | 8.3486 | 39.95
2020-10-28 03:00 | 44132.125 | 0 | 8.3618 | 39.95
2020-10-28 03:30 | 44132.1458 | 0 | 8.4195 | 39.95
2020-10-28 04:00 | 44132.1667 | 0 | 8.6471 | 39.95
2020-10-28 04:30 | 44132.1875 | 0 | 9.1352 | 39.95
2020-10-28 05:00 | 44132.2083 | 0 | 9.4863 | 39.95
2020-10-28 05:30 | 44132.2292 | 0 | 9.9948 | 39.95
2020-10-28 06:00 | 44132.25 | 0 | 10.412 | 39.95
2020-10-28 06:30 | 44132.2708 | 0 | 10.8036 | 39.95
2020-10-28 07:00 | 44132.2917 | 0 | 11.1886 | 39.95
2020-10-28 07:30 | 44132.3125 | 0 | 11.2029 | 39.95
2020-10-28 08:00 | 44132.3333 | 0 | 11.1592 | 39.95
2020-10-28 08:30 | 44132.3542 | 0 | 10.8292 | 39.95
2020-10-28 09:00 | 44132.375 | 0 | 10.8202 | 39.95
2020-10-28 09:30 | 44132.3958 | 0 | 10.8963 | 39.95
2020-10-28 10:00 | 44132.4167 | 0 | 11.2854 | 39.95
2020-10-28 10:30 | 44132.4375 | 0 | 11.3905 | 39.95
2020-10-28 11:00 | 44132.4583 | 0 | 11.6777 | 39.95
2020-10-28 11:30 | 44132.4792 | 0 | 12.1267 | 39.95
2020-10-28 12:00 | 44132.5 | 0 | 11.4623 | 39.95
2020-10-28 12:30 | 44132.5208 | 0 | 12.1523 | 39.95
2020-10-28 13:00 | 44132.5417 | 0 | 12.1519 | 39.95
2020-10-28 13:30 | 44132.5625 | 0 | 12.7519 | 39.95
2020-10-28 14:00 | 44132.5833 | 0 | 12.9402 | 39.95
2020-10-28 14:30 | 44132.6042 | 0 | 12.5423 | 39.95
2020-10-28 15:00 | 44132.625 | 0 | 12.8843 | 39.95
2020-10-28 15:30 | 44132.6458 | 0 | 13.5562 | 39.95
2020-10-28 16:00 | 44132.6667 | 0 | 14.2846 | 39.95
2020-10-28 16:30 | 44132.6875 | 0 | 14.9112 | 39.95
2020-10-28 17:00 | 44132.7083 | 0 | 14.9217 | 39.95
2020-10-28 17:30 | 44132.7292 | 0 | 15.0245 | 39.95
2020-10-28 18:00 | 44132.75 | 0 | 15.2525 | 39.95
2020-10-28 18:30 | 44132.7708 | 0 | 15.9642 | 39.95
2020-10-28 19:00 | 44132.7917 | 0 | 15.8894 | 39.95
2020-10-28 19:30 | 44132.8125 | 0 | 15.4377 | 39.95
2020-10-28 20:00 | 44132.8333 | 0 | 15.0612 | 39.95
2020-10-28 20:30 | 44132.8542 | 0 | 14.5022 | 39.95
2020-10-28 21:00 | 44132.875 | 0 | 13.7742 | 39.95
2020-10-28 21:30 | 44132.8958 | 0 | 13.1313 | 39.95
2020-10-28 22:00 | 44132.9167 | 0 | 12.4545 | 39.95
2020-10-28 22:30 | 44132.9375 | 0 | 11.6563 | 39.95
2020-10-28 23:00 | 44132.9583 | 0 | 10.8575 | 39.95
2020-10-28 23:30 | 44132.9792 | 0 | 10.306 | 39.95
2020-10-29 | 44133 | 0 | 9.6293 | 39.95
2020-10-29 00:30 | 44133.0208 | 0 | 9.1448 | 39.95
2020-10-29 01:00 | 44133.0417 | 0 | 9.1435 | 39.95
2020-10-29 01:30 | 44133.0625 | 0 | 8.9635 | 39.95
2020-10-29 02:00 | 44133.0833 | 0 | 8.9369 | 39.95
2020-10-29 02:30 | 44133.1042 | 0 | 8.9257 | 39.95
2020-10-29 03:00 | 44133.125 | 0 | 9.0185 | 39.95
2020-10-29 03:30 | 44133.1458 | 0 | 8.8455 | 39.95
2020-10-29 04:00 | 44133.1667 | 0 | 8.909 | 39.95
2020-10-29 04:30 | 44133.1875 | 0 | 9.2661 | 39.95
2020-10-29 05:00 | 44133.2083 | 0 | 9.7336 | 39.95
2020-10-29 05:30 | 44133.2292 | 0 | 9.821 | 39.95
2020-10-29 06:00 | 44133.25 | 0 | 10.3741 | 39.95
2020-10-29 06:30 | 44133.2708 | 0 | 10.7805 | 39.95
2020-10-29 07:00 | 44133.2917 | 0 | 11.0569 | 39.95
2020-10-29 07:30 | 44133.3125 | 0 | 11.0827 | 39.95
2020-10-29 08:00 | 44133.3333 | 0 | 11.2369 | 39.95
2020-10-29 08:30 | 44133.3542 | 0 | 11.1797 | 39.95
2020-10-29 09:00 | 44133.375 | 0 | 11.3078 | 39.95
2020-10-29 09:30 | 44133.3958 | 0 | 11.3754 | 39.95
2020-10-29 10:00 | 44133.4167 | 0 | 11.5292 | 39.95
2020-10-29 10:30 | 44133.4375 | 0 | 11.4622 | 39.95
2020-10-29 11:00 | 44133.4583 | 0 | 11.5106 | 39.95
2020-10-29 11:30 | 44133.4792 | 0 | 11.3895 | 39.95
2020-10-29 12:00 | 44133.5 | 0 | 11.4549 | 39.95
2020-10-29 12:30 | 44133.5208 | 0 | 11.3691 | 39.95
2020-10-29 13:00 | 44133.5417 | 0 | 11.5853 | 39.95
2020-10-29 13:30 | 44133.5625 | 0 | 11.7694 | 39.95
2020-10-29 14:00 | 44133.5833 | 0 | 12.1703 | 39.95
2020-10-29 14:30 | 44133.6042 | 0 | 12.5067 | 39.95
2020-10-29 15:00 | 44133.625 | 0 | 12.8562 | 39.95
2020-10-29 15:30 | 44133.6458 | 0 | 13.567 | 39.95
2020-10-29 16:00 | 44133.6667 | 0 | 14.0031 | 39.95
2020-10-29 16:30 | 44133.6875 | 0 | 14.5818 | 39.95
2020-10-29 17:00 | 44133.7083 | 0 | 14.7247 | 39.95
2020-10-29 17:30 | 44133.7292 | 0 | 14.6669 | 39.95
2020-10-29 18:00 | 44133.75 | 0 | 14.7584 | 39.95
2020-10-29 18:30 | 44133.7708 | 0 | 15.4878 | 39.95
2020-10-29 19:00 | 44133.7917 | 0 | 15.4707 | 39.95
2020-10-29 19:30 | 44133.8125 | 0 | 15.2348 | 39.95
2020-10-29 20:00 | 44133.8333 | 0 | 15.0293 | 39.95
2020-10-29 20:30 | 44133.8542 | 0 | 14.6564 | 39.95
2020-10-29 21:00 | 44133.875 | 0 | 14.0871 | 39.95
2020-10-29 21:30 | 44133.8958 | 0 | 13.8201 | 39.95
2020-10-29 22:00 | 44133.9167 | 0 | 13.3135 | 39.95
2020-10-29 22:30 | 44133.9375 | 0 | 12.5818 | 39.95
2020-10-29 23:00 | 44133.9583 | 0 | 11.8881 | 39.95
2020-10-29 23:30 | 44133.9792 | 0 | 11.2873 | 39.95
2020-10-30 | 44134 | 0 | 10.4802 | 39.95
2020-10-30 00:30 | 44134.0208 | 0 | 9.971 | 39.95
2020-10-30 01:00 | 44134.0417 | 0 | 9.8042 | 39.95
2020-10-30 01:30 | 44134.0625 | 0 | 9.6123 | 39.95
2020-10-30 02:00 | 44134.0833 | 0 | 9.5754 | 39.95
2020-10-30 02:30 | 44134.1042 | 0 | 9.4409 | 39.95
2020-10-30 03:00 | 44134.125 | 0 | 9.3333 | 39.95
2020-10-30 03:30 | 44134.1458 | 0 | 9.3963 | 39.95
2020-10-30 04:00 | 44134.1667 | 0 | 9.3146 | 39.95
2020-10-30 04:30 | 44134.1875 | 0 | 9.4562 | 39.95
2020-10-30 05:00 | 44134.2083 | 0 | 9.4353 | 39.95
2020-10-30 05:30 | 44134.2292 | 0 | 9.1934 | 39.95
2020-10-30 06:00 | 44134.25 | 0 | 9.3076 | 39.95
2020-10-30 06:30 | 44134.2708 | 0 | 9.6775 | 39.95
2020-10-30 07:00 | 44134.2917 | 0 | 9.5415 | 39.95
2020-10-30 07:30 | 44134.3125 | 0 | 10.0328 | 39.95
2020-10-30 08:00 | 44134.3333 | 0 | 10.54 | 39.95
2020-10-30 08:30 | 44134.3542 | 0 | 10.6718 | 39.95
2020-10-30 09:00 | 44134.375 | 0 | 10.2018 | 39.95
2020-10-30 09:30 | 44134.3958 | 0 | 11.1983 | 39.95
2020-10-30 10:00 | 44134.4167 | 0 | 10.5092 | 39.95
2020-10-30 10:30 | 44134.4375 | 0 | 10.8768 | 39.95
2020-10-30 11:00 | 44134.4583 | 0 | 10.2779 | 39.95
2020-10-30 11:30 | 44134.4792 | 0 | 10.118 | 39.95
2020-10-30 12:00 | 44134.5 | 0 | 10.0587 | 39.95
2020-10-30 12:30 | 44134.5208 | 0 | 12.6562 | 39.95
2020-10-30 13:00 | 44134.5417 | 0 | 11.4998 | 39.95
2020-10-30 13:30 | 44134.5625 | 0 | 12.774 | 39.95
2020-10-30 14:00 | 44134.5833 | 0 | 13.8481 | 39.95
2020-10-30 14:30 | 44134.6042 | 0 | 14.4606 | 39.95
2020-10-30 15:00 | 44134.625 | 0 | 14.2293 | 39.95
2020-10-30 15:30 | 44134.6458 | 0 | 13.4363 | 39.95
2020-10-30 16:00 | 44134.6667 | 0 | 12.826 | 39.95
2020-10-30 16:30 | 44134.6875 | 0 | 12.3043 | 39.95
2020-10-30 17:00 | 44134.7083 | 0 | 11.8759 | 39.95
2020-10-30 17:30 | 44134.7292 | 0 | 12.164 | 39.95
2020-10-30 18:00 | 44134.75 | 0 | 12.2888 | 39.95
2020-10-30 18:30 | 44134.7708 | 0 | 12.7651 | 39.95
2020-10-30 19:00 | 44134.7917 | 0 | 12.5822 | 39.95
2020-10-30 19:30 | 44134.8125 | 0 | 12.2253 | 39.95
2020-10-30 20:00 | 44134.8333 | 0 | 12.2402 | 39.95
2020-10-30 20:30 | 44134.8542 | 0 | 11.7338 | 39.95
2020-10-30 21:00 | 44134.875 | 0 | 11.2885 | 39.95
2020-10-30 21:30 | 44134.8958 | 0 | 11.1066 | 39.95
2020-10-30 22:00 | 44134.9167 | 0 | 10.6522 | 39.95
2020-10-30 22:30 | 44134.9375 | 0 | 9.993 | 39.95
2020-10-30 23:00 | 44134.9583 | 0 | 9.5674 | 39.95
2020-10-30 23:30 | 44134.9792 | 0 | 9.0913 | 39.95
2020-10-31 | 44135 | 0 | 8.6404 | 39.95
2020-10-31 00:30 | 44135.0208 | 0 | 8.2908 | 39.95
2020-10-31 01:00 | 44135.0417 | 0 | 8.1291 | 39.95
2020-10-31 01:30 | 44135.0625 | 0 | 7.9836 | 39.95
2020-10-31 02:00 | 44135.0833 | 0 | 8.0381 | 39.95
2020-10-31 02:30 | 44135.1042 | 0 | 7.8703 | 39.95
2020-10-31 03:00 | 44135.125 | 0 | 7.6577 | 39.95
2020-10-31 03:30 | 44135.1458 | 0 | 7.6154 | 39.95
2020-10-31 04:00 | 44135.1667 | 0 | 7.5856 | 39.95
2020-10-31 04:30 | 44135.1875 | 0 | 7.5466 | 39.95
2020-10-31 05:00 | 44135.2083 | 0 | 7.4497 | 39.95
2020-10-31 05:30 | 44135.2292 | 0 | 7.2839 | 39.95
2020-10-31 06:00 | 44135.25 | 0 | 7.1191 | 39.95
2020-10-31 06:30 | 44135.2708 | 0 | 6.925 | 39.95
2020-10-31 07:00 | 44135.2917 | 0 | 6.9176 | 39.95
2020-10-31 07:30 | 44135.3125 | 0 | 6.8541 | 39.95
2020-10-31 08:00 | 44135.3333 | 0 | 6.8915 | 39.95
2020-10-31 08:30 | 44135.3542 | 0 | 6.7627 | 39.95
2020-10-31 09:00 | 44135.375 | 0 | 6.7072 | 39.95
2020-10-31 09:30 | 44135.3958 | 0 | 6.6682 | 39.95
2020-10-31 10:00 | 44135.4167 | 0 | 6.6924 | 39.95
2020-10-31 10:30 | 44135.4375 | 0 | 6.7131 | 39.95
2020-10-31 11:00 | 44135.4583 | 0 | 6.9774 | 39.95
2020-10-31 11:30 | 44135.4792 | 0 | 7.1689 | 39.95
2020-10-31 12:00 | 44135.5 | 0 | 7.1372 | 39.95
2020-10-31 12:30 | 44135.5208 | 0 | 7.4292 | 39.95
2020-10-31 13:00 | 44135.5417 | 0 | 7.774 | 39.95
2020-10-31 13:30 | 44135.5625 | 0 | 8.2967 | 39.95
2020-10-31 14:00 | 44135.5833 | 0 | 9.0698 | 39.95
2020-10-31 14:30 | 44135.6042 | 0 | 9.748 | 39.95
2020-10-31 15:00 | 44135.625 | 0 | 10.4762 | 39.95
2020-10-31 15:30 | 44135.6458 | 0 | 11.4754 | 39.95
2020-10-31 16:00 | 44135.6667 | 0 | 12.1485 | 39.95
2020-10-31 16:30 | 44135.6875 | 0 | 12.8379 | 39.95
2020-10-31 17:00 | 44135.7083 | 0 | 13.2936 | 39.95
2020-10-31 17:30 | 44135.7292 | 0 | 13.6953 | 39.95
2020-10-31 18:00 | 44135.75 | 0 | 14.0048 | 39.95
2020-10-31 18:30 | 44135.7708 | 0 | 14.82 | 39.95
2020-10-31 19:00 | 44135.7917 | 0 | 14.5562 | 39.95
2020-10-31 19:30 | 44135.8125 | 0 | 14.038 | 39.95
2020-10-31 20:00 | 44135.8333 | 0 | 13.614 | 39.95
2020-10-31 20:30 | 44135.8542 | 0 | 12.8646 | 39.95
2020-10-31 21:00 | 44135.875 | 0 | 12.2345 | 39.95
2020-10-31 21:30 | 44135.8958 | 0 | 11.6891 | 39.95
2020-10-31 22:00 | 44135.9167 | 0 | 11.1215 | 39.95
2020-10-31 22:30 | 44135.9375 | 0 | 10.278 | 39.95
2020-10-31 23:00 | 44135.9583 | 0 | 9.6872 | 39.95
2020-10-31 23:30 | 44135.9792 | 0 | 9.2281 | 39.95
2020-11-01 | 44136 | 0 | 8.7745 | 37.78
2020-11-01 00:30 | 44136.0208 | 0 | 8.61 | 37.78
2020-11-01 01:00 | 44136.0417 | 0 | 8.2928 | 37.78
2020-11-01 01:30 | 44136.0625 | 0 | 8.2573 | 37.78
2020-11-01 02:00 | 44136.0833 | 0 | 8.239 | 37.78
2020-11-01 02:30 | 44136.1042 | 0 | 8.1699 | 37.78
2020-11-01 03:00 | 44136.125 | 0 | 8.2001 | 37.78
2020-11-01 03:30 | 44136.1458 | 0 | 8.3674 | 37.78
2020-11-01 04:00 | 44136.1667 | 0 | 8.4942 | 37.78
2020-11-01 04:30 | 44136.1875 | 0 | 8.949 | 37.78
2020-11-01 05:00 | 44136.2083 | 0 | 9.3226 | 37.78
2020-11-01 05:30 | 44136.2292 | 0 | 9.7391 | 37.78
2020-11-01 06:00 | 44136.25 | 0 | 10.3326 | 37.78
2020-11-01 06:30 | 44136.2708 | 0 | 10.9321 | 37.78
2020-11-01 07:00 | 44136.2917 | 0 | 11.3916 | 37.78
2020-11-01 07:30 | 44136.3125 | 0 | 11.4363 | 37.78
2020-11-01 08:00 | 44136.3333 | 0 | 11.5222 | 37.78
2020-11-01 08:30 | 44136.3542 | 0 | 11.9933 | 37.78
2020-11-01 09:00 | 44136.375 | 0 | 12.1355 | 37.78
2020-11-01 09:30 | 44136.3958 | 0 | 12.3408 | 37.78
2020-11-01 10:00 | 44136.4167 | 0 | 12.4617 | 37.78
2020-11-01 10:30 | 44136.4375 | 0 | 12.9204 | 37.78
2020-11-01 11:00 | 44136.4583 | 0 | 12.8593 | 37.78
2020-11-01 11:30 | 44136.4792 | 0 | 13.5562 | 37.78
2020-11-01 12:00 | 44136.5 | 0 | 13.6115 | 37.78
2020-11-01 12:30 | 44136.5208 | 0 | 11.6348 | 37.78
2020-11-01 13:00 | 44136.5417 | 0 | 11.3727 | 37.78
2020-11-01 13:30 | 44136.5625 | 0 | 12.2387 | 37.78
2020-11-01 14:00 | 44136.5833 | 0 | 14.4629 | 37.78
2020-11-01 14:30 | 44136.6042 | 0 | 13.3697 | 37.78
2020-11-01 15:00 | 44136.625 | 0 | 13.3983 | 37.78
2020-11-01 15:30 | 44136.6458 | 0 | 13.314 | 37.78
2020-11-01 16:00 | 44136.6667 | 0 | 13.8434 | 37.78
2020-11-01 16:30 | 44136.6875 | 0 | 14.4589 | 37.78
2020-11-01 17:00 | 44136.7083 | 0 | 14.7333 | 37.78
2020-11-01 17:30 | 44136.7292 | 0 | 14.6131 | 37.78
2020-11-01 18:00 | 44136.75 | 0 | 14.708 | 37.78
2020-11-01 18:30 | 44136.7708 | 0 | 15.2943 | 37.78
2020-11-01 19:00 | 44136.7917 | 0 | 15.0408 | 37.78
2020-11-01 19:30 | 44136.8125 | 0 | 14.7544 | 37.78
2020-11-01 20:00 | 44136.8333 | 0 | 14.3279 | 37.78
2020-11-01 20:30 | 44136.8542 | 0 | 13.5319 | 37.78
2020-11-01 21:00 | 44136.875 | 0 | 12.9137 | 37.78
2020-11-01 21:30 | 44136.8958 | 0 | 12.4578 | 37.78
2020-11-01 22:00 | 44136.9167 | 0 | 11.8349 | 37.78
2020-11-01 22:30 | 44136.9375 | 0 | 10.9543 | 37.78
2020-11-01 23:00 | 44136.9583 | 0 | 10.2764 | 37.78
2020-11-01 23:30 | 44136.9792 | 0 | 9.6844 | 37.78
2020-11-02 | 44137 | 0 | 9.1702 | 37.78
2020-11-02 00:30 | 44137.0208 | 0 | 8.7691 | 37.78
2020-11-02 01:00 | 44137.0417 | 0 | 8.5942 | 37.78
2020-11-02 01:30 | 44137.0625 | 0 | 8.3634 | 37.78
2020-11-02 02:00 | 44137.0833 | 0 | 8.3989 | 37.78
2020-11-02 02:30 | 44137.1042 | 0 | 8.4157 | 37.78
2020-11-02 03:00 | 44137.125 | 0 | 8.3244 | 37.78
2020-11-02 03:30 | 44137.1458 | 0 | 8.3972 | 37.78
2020-11-02 04:00 | 44137.1667 | 0 | 8.4885 | 37.78
2020-11-02 04:30 | 44137.1875 | 0 | 8.7902 | 37.78
2020-11-02 05:00 | 44137.2083 | 0 | 9.4414 | 37.78
2020-11-02 05:30 | 44137.2292 | 0 | 9.7186 | 37.78
2020-11-02 06:00 | 44137.25 | 0 | 10.1545 | 37.78
2020-11-02 06:30 | 44137.2708 | 0 | 10.6695 | 37.78
2020-11-02 07:00 | 44137.2917 | 0 | 10.9524 | 37.78
2020-11-02 07:30 | 44137.3125 | 0 | 10.6467 | 37.78
2020-11-02 08:00 | 44137.3333 | 0 | 10.5019 | 37.78
2020-11-02 08:30 | 44137.3542 | 0 | 10.1862 | 37.78
2020-11-02 09:00 | 44137.375 | 0 | 10.0928 | 37.78
2020-11-02 09:30 | 44137.3958 | 0 | 10.3501 | 37.78
2020-11-02 10:00 | 44137.4167 | 0 | 10.3414 | 37.78
2020-11-02 10:30 | 44137.4375 | 0 | 10.576 | 37.78
2020-11-02 11:00 | 44137.4583 | 0 | 11.3014 | 37.78
2020-11-02 11:30 | 44137.4792 | 0 | 11.1237 | 37.78
2020-11-02 12:00 | 44137.5 | 0 | 11.33 | 37.78
2020-11-02 12:30 | 44137.5208 | 0 | 10.902 | 37.78
2020-11-02 13:00 | 44137.5417 | 0 | 11.3612 | 37.78
2020-11-02 13:30 | 44137.5625 | 0 | 11.4156 | 37.78
2020-11-02 14:00 | 44137.5833 | 0 | 11.3194 | 37.78
2020-11-02 14:30 | 44137.6042 | 0 | 11.6057 | 37.78
2020-11-02 15:00 | 44137.625 | 0 | 12.1195 | 37.78
2020-11-02 15:30 | 44137.6458 | 0 | 12.4293 | 37.78
2020-11-02 16:00 | 44137.6667 | 0 | 13.0439 | 37.78
2020-11-02 16:30 | 44137.6875 | 0 | 13.5095 | 37.78
2020-11-02 17:00 | 44137.7083 | 0 | 13.593 | 37.78
2020-11-02 17:30 | 44137.7292 | 0 | 14.0034 | 37.78
2020-11-02 18:00 | 44137.75 | 0 | 13.9878 | 37.78
2020-11-02 18:30 | 44137.7708 | 0 | 14.9652 | 37.78
2020-11-02 19:00 | 44137.7917 | 0 | 14.7252 | 37.78
2020-11-02 19:30 | 44137.8125 | 0 | 14.222 | 37.78
2020-11-02 20:00 | 44137.8333 | 0 | 13.829 | 37.78
2020-11-02 20:30 | 44137.8542 | 0 | 13.3996 | 37.78
2020-11-02 21:00 | 44137.875 | 0 | 12.6106 | 37.78
2020-11-02 21:30 | 44137.8958 | 0 | 12.1972 | 37.78
2020-11-02 22:00 | 44137.9167 | 0 | 11.7005 | 37.78
2020-11-02 22:30 | 44137.9375 | 0 | 10.6901 | 37.78
2020-11-02 23:00 | 44137.9583 | 0 | 9.9984 | 37.78
2020-11-02 23:30 | 44137.9792 | 0 | 9.6545 | 37.78
2020-11-03 | 44138 | 0 | 9.3199 | 37.78
2020-11-03 00:30 | 44138.0208 | 0 | 8.6785 | 37.78
2020-11-03 01:00 | 44138.0417 | 0 | 8.6259 | 37.78
2020-11-03 01:30 | 44138.0625 | 0 | 8.4957 | 37.78
2020-11-03 02:00 | 44138.0833 | 0 | 8.3853 | 37.78
2020-11-03 02:30 | 44138.1042 | 0 | 8.0417 | 37.78
2020-11-03 03:00 | 44138.125 | 0 | 8.2893 | 37.78
2020-11-03 03:30 | 44138.1458 | 0 | 8.254 | 37.78
2020-11-03 04:00 | 44138.1667 | 0 | 8.4989 | 37.78
2020-11-03 04:30 | 44138.1875 | 0 | 8.7829 | 37.78
2020-11-03 05:00 | 44138.2083 | 0 | 9.3356 | 37.78
2020-11-03 05:30 | 44138.2292 | 0 | 9.5346 | 37.78
2020-11-03 06:00 | 44138.25 | 0 | 10.1081 | 37.78
2020-11-03 06:30 | 44138.2708 | 0 | 10.5662 | 37.78
2020-11-03 07:00 | 44138.2917 | 0 | 10.7217 | 37.78
2020-11-03 07:30 | 44138.3125 | 0 | 10.5835 | 37.78
2020-11-03 08:00 | 44138.3333 | 0 | 10.2787 | 37.78
2020-11-03 08:30 | 44138.3542 | 0 | 10.1053 | 37.78
2020-11-03 09:00 | 44138.375 | 0 | 10.215 | 37.78
2020-11-03 09:30 | 44138.3958 | 0 | 10.4239 | 37.78
2020-11-03 10:00 | 44138.4167 | 0 | 10.0854 | 37.78
2020-11-03 10:30 | 44138.4375 | 0 | 10.6431 | 37.78
2020-11-03 11:00 | 44138.4583 | 0 | 10.5563 | 37.78
2020-11-03 11:30 | 44138.4792 | 0 | 10.8087 | 37.78
2020-11-03 12:00 | 44138.5 | 0 | 10.5837 | 37.78
2020-11-03 12:30 | 44138.5208 | 0 | 10.513 | 37.78
2020-11-03 13:00 | 44138.5417 | 0 | 10.7427 | 37.78
2020-11-03 13:30 | 44138.5625 | 0 | 11.2543 | 37.78
2020-11-03 14:00 | 44138.5833 | 0 | 11.5277 | 37.78
2020-11-03 14:30 | 44138.6042 | 0 | 11.9415 | 37.78
2020-11-03 15:00 | 44138.625 | 0 | 12.3481 | 37.78
2020-11-03 15:30 | 44138.6458 | 0 | 12.9553 | 37.78
2020-11-03 16:00 | 44138.6667 | 0 | 13.4325 | 37.78
2020-11-03 16:30 | 44138.6875 | 0 | 14.0727 | 37.78
2020-11-03 17:00 | 44138.7083 | 0 | 14.3599 | 37.78
2020-11-03 17:30 | 44138.7292 | 0 | 14.4085 | 37.78
2020-11-03 18:00 | 44138.75 | 0 | 14.555 | 37.78
2020-11-03 18:30 | 44138.7708 | 0 | 15.2057 | 37.78
2020-11-03 19:00 | 44138.7917 | 0 | 14.9687 | 37.78
2020-11-03 19:30 | 44138.8125 | 0 | 14.5125 | 37.78
2020-11-03 20:00 | 44138.8333 | 0 | 14.2889 | 37.78
2020-11-03 20:30 | 44138.8542 | 0 | 13.7974 | 37.78
2020-11-03 21:00 | 44138.875 | 0 | 12.9927 | 37.78
2020-11-03 21:30 | 44138.8958 | 0 | 12.5858 | 37.78
2020-11-03 22:00 | 44138.9167 | 0 | 12.1952 | 37.78
2020-11-03 22:30 | 44138.9375 | 0 | 11.2299 | 37.78
2020-11-03 23:00 | 44138.9583 | 0 | 10.5871 | 37.78
2020-11-03 23:30 | 44138.9792 | 0 | 10.0773 | 37.78
2020-11-04 | 44139 | 0 | 9.3864 | 37.78
2020-11-04 00:30 | 44139.0208 | 0 | 8.985 | 37.78
2020-11-04 01:00 | 44139.0417 | 0 | 9.0074 | 37.78
2020-11-04 01:30 | 44139.0625 | 0 | 8.8512 | 37.78
2020-11-04 02:00 | 44139.0833 | 0 | 8.7619 | 37.78
2020-11-04 02:30 | 44139.1042 | 0 | 8.583 | 37.78
2020-11-04 03:00 | 44139.125 | 0 | 8.6186 | 37.78
2020-11-04 03:30 | 44139.1458 | 0 | 8.639 | 37.78
2020-11-04 04:00 | 44139.1667 | 0 | 8.8032 | 37.78
2020-11-04 04:30 | 44139.1875 | 0 | 9.2628 | 37.78
2020-11-04 05:00 | 44139.2083 | 0 | 9.9002 | 37.78
2020-11-04 05:30 | 44139.2292 | 0 | 10.2509 | 37.78
2020-11-04 06:00 | 44139.25 | 0 | 10.8722 | 37.78
2020-11-04 06:30 | 44139.2708 | 0 | 11.466 | 37.78
2020-11-04 07:00 | 44139.2917 | 0 | 11.6316 | 37.78
2020-11-04 07:30 | 44139.3125 | 0 | 11.8609 | 37.78
2020-11-04 08:00 | 44139.3333 | 0 | 11.9539 | 37.78
2020-11-04 08:30 | 44139.3542 | 0 | 12.0133 | 37.78
2020-11-04 09:00 | 44139.375 | 0 | 12.1437 | 37.78
2020-11-04 09:30 | 44139.3958 | 0 | 12.3576 | 37.78
2020-11-04 10:00 | 44139.4167 | 0 | 12.5084 | 37.78
2020-11-04 10:30 | 44139.4375 | 0 | 12.6742 | 37.78
2020-11-04 11:00 | 44139.4583 | 0 | 12.7324 | 37.78
2020-11-04 11:30 | 44139.4792 | 0 | 13.9648 | 37.78
2020-11-04 12:00 | 44139.5 | 0 | 15.5068 | 37.78
2020-11-04 12:30 | 44139.5208 | 0 | 14.2419 | 37.78
2020-11-04 13:00 | 44139.5417 | 0 | 13.4565 | 37.78
2020-11-04 13:30 | 44139.5625 | 0 | 14.1571 | 37.78
2020-11-04 14:00 | 44139.5833 | 0 | 14.7904 | 37.78
2020-11-04 14:30 | 44139.6042 | 0 | 15.3202 | 37.78
2020-11-04 15:00 | 44139.625 | 0 | 16.5399 | 37.78
2020-11-04 15:30 | 44139.6458 | 0 | 17.1042 | 37.78
2020-11-04 16:00 | 44139.6667 | 0 | 15.3919 | 37.78
2020-11-04 16:30 | 44139.6875 | 0 | 16.627 | 37.78
2020-11-04 17:00 | 44139.7083 | 0 | 16.9127 | 37.78
2020-11-04 17:30 | 44139.7292 | 0 | 16.8091 | 37.78
2020-11-04 18:00 | 44139.75 | 0 | 16.7328 | 37.78
2020-11-04 18:30 | 44139.7708 | 0 | 17.5473 | 37.78
2020-11-04 19:00 | 44139.7917 | 0 | 17.5365 | 37.78
2020-11-04 19:30 | 44139.8125 | 0 | 17.003 | 37.78
2020-11-04 20:00 | 44139.8333 | 0 | 16.6196 | 37.78
2020-11-04 20:30 | 44139.8542 | 0 | 15.9717 | 37.78
2020-11-04 21:00 | 44139.875 | 0 | 15.0683 | 37.78
2020-11-04 21:30 | 44139.8958 | 0 | 14.0756 | 37.78
2020-11-04 22:00 | 44139.9167 | 0 | 13.2215 | 37.78
2020-11-04 22:30 | 44139.9375 | 0 | 12.0599 | 37.78
2020-11-04 23:00 | 44139.9583 | 0 | 11.0808 | 37.78
2020-11-04 23:30 | 44139.9792 | 0 | 10.3823 | 37.78
2020-11-05 | 44140 | 0 | 9.7452 | 37.78
2020-11-05 00:30 | 44140.0208 | 0 | 9.2803 | 37.78
2020-11-05 01:00 | 44140.0417 | 0 | 9.0072 | 37.78
2020-11-05 01:30 | 44140.0625 | 0 | 8.8883 | 37.78
2020-11-05 02:00 | 44140.0833 | 0 | 8.7841 | 37.78
2020-11-05 02:30 | 44140.1042 | 0 | 8.7095 | 37.78
2020-11-05 03:00 | 44140.125 | 0 | 8.5368 | 37.78
2020-11-05 03:30 | 44140.1458 | 0 | 8.6671 | 37.78
2020-11-05 04:00 | 44140.1667 | 0 | 8.8755 | 37.78
2020-11-05 04:30 | 44140.1875 | 0 | 9.1663 | 37.78
2020-11-05 05:00 | 44140.2083 | 0 | 9.5577 | 37.78
2020-11-05 05:30 | 44140.2292 | 0 | 9.7109 | 37.78
2020-11-05 06:00 | 44140.25 | 0 | 9.9682 | 37.78
2020-11-05 06:30 | 44140.2708 | 0 | 10.3461 | 37.78
2020-11-05 07:00 | 44140.2917 | 0 | 10.3469 | 37.78
2020-11-05 07:30 | 44140.3125 | 0 | 10.2899 | 37.78
2020-11-05 08:00 | 44140.3333 | 0 | 10.2676 | 37.78
2020-11-05 08:30 | 44140.3542 | 0 | 10.0818 | 37.78
2020-11-05 09:00 | 44140.375 | 0 | 10.216 | 37.78
2020-11-05 09:30 | 44140.3958 | 0 | 9.9896 | 37.78
2020-11-05 10:00 | 44140.4167 | 0 | 10.0628 | 37.78
2020-11-05 10:30 | 44140.4375 | 0 | 10.0758 | 37.78
2020-11-05 11:00 | 44140.4583 | 0 | 10.1109 | 37.78
2020-11-05 11:30 | 44140.4792 | 0 | 10.2377 | 37.78
2020-11-05 12:00 | 44140.5 | 0 | 10.377 | 37.78
2020-11-05 12:30 | 44140.5208 | 0 | 10.2096 | 37.78
2020-11-05 13:00 | 44140.5417 | 0 | 10.3253 | 37.78
2020-11-05 13:30 | 44140.5625 | 0 | 10.6509 | 37.78
2020-11-05 14:00 | 44140.5833 | 0 | 10.9603 | 37.78
2020-11-05 14:30 | 44140.6042 | 0 | 11.3505 | 37.78
2020-11-05 15:00 | 44140.625 | 0 | 11.9456 | 37.78
2020-11-05 15:30 | 44140.6458 | 0 | 12.6044 | 37.78
2020-11-05 16:00 | 44140.6667 | 0 | 13.2504 | 37.78
2020-11-05 16:30 | 44140.6875 | 0 | 13.8021 | 37.78
2020-11-05 17:00 | 44140.7083 | 0 | 13.7528 | 37.78
2020-11-05 17:30 | 44140.7292 | 0 | 13.716 | 37.78
2020-11-05 18:00 | 44140.75 | 0 | 13.8427 | 37.78
2020-11-05 18:30 | 44140.7708 | 0 | 14.3118 | 37.78
2020-11-05 19:00 | 44140.7917 | 0 | 13.8587 | 37.78
2020-11-05 19:30 | 44140.8125 | 0 | 13.6917 | 37.78
2020-11-05 20:00 | 44140.8333 | 0 | 13.5636 | 37.78
2020-11-05 20:30 | 44140.8542 | 0 | 13.0659 | 37.78
2020-11-05 21:00 | 44140.875 | 0 | 12.5656 | 37.78
2020-11-05 21:30 | 44140.8958 | 0 | 12.3125 | 37.78
2020-11-05 22:00 | 44140.9167 | 0 | 11.8313 | 37.78
2020-11-05 22:30 | 44140.9375 | 0 | 11.0894 | 37.78
2020-11-05 23:00 | 44140.9583 | 0 | 10.4328 | 37.78
2020-11-05 23:30 | 44140.9792 | 0 | 9.8995 | 37.78
2020-11-06 | 44141 | 0 | 9.3141 | 37.78
2020-11-06 00:30 | 44141.0208 | 0 | 8.983 | 37.78
2020-11-06 01:00 | 44141.0417 | 0 | 8.8137 | 37.78
2020-11-06 01:30 | 44141.0625 | 0 | 8.5618 | 37.78
2020-11-06 02:00 | 44141.0833 | 0 | 8.4211 | 37.78
2020-11-06 02:30 | 44141.1042 | 0 | 8.2908 | 37.78
2020-11-06 03:00 | 44141.125 | 0 | 8.2577 | 37.78
2020-11-06 03:30 | 44141.1458 | 0 | 8.3375 | 37.78
2020-11-06 04:00 | 44141.1667 | 0 | 8.358 | 37.78
2020-11-06 04:30 | 44141.1875 | 0 | 8.3747 | 37.78
2020-11-06 05:00 | 44141.2083 | 0 | 8.5982 | 37.78
2020-11-06 05:30 | 44141.2292 | 0 | 8.5684 | 37.78
2020-11-06 06:00 | 44141.25 | 0 | 8.3763 | 37.78
2020-11-06 06:30 | 44141.2708 | 0 | 8.0688 | 37.78
2020-11-06 07:00 | 44141.2917 | 0 | 7.7178 | 37.78
2020-11-06 07:30 | 44141.3125 | 0 | 7.9451 | 37.78
2020-11-06 08:00 | 44141.3333 | 0 | 8.0607 | 37.78
2020-11-06 08:30 | 44141.3542 | 0 | 8.6276 | 37.78
2020-11-06 09:00 | 44141.375 | 0 | 9.0282 | 37.78
2020-11-06 09:30 | 44141.3958 | 0 | 8.7746 | 37.78
2020-11-06 10:00 | 44141.4167 | 0 | 9.4424 | 37.78
2020-11-06 10:30 | 44141.4375 | 0 | 8.6545 | 37.78
2020-11-06 11:00 | 44141.4583 | 0 | 8.4068 | 37.78
2020-11-06 11:30 | 44141.4792 | 0 | 9.7618 | 37.78
2020-11-06 12:00 | 44141.5 | 0 | 10.5662 | 37.78
2020-11-06 12:30 | 44141.5208 | 0 | 9.9864 | 37.78
2020-11-06 13:00 | 44141.5417 | 0 | 8.3143 | 37.78
2020-11-06 13:30 | 44141.5625 | 0 | 8.8517 | 37.78
2020-11-06 14:00 | 44141.5833 | 0 | 9.4362 | 37.78
2020-11-06 14:30 | 44141.6042 | 0 | 10.9759 | 37.78
2020-11-06 15:00 | 44141.625 | 0 | 10.0686 | 37.78
2020-11-06 15:30 | 44141.6458 | 0 | 10.8674 | 37.78
2020-11-06 16:00 | 44141.6667 | 0 | 11.5945 | 37.78
2020-11-06 16:30 | 44141.6875 | 0 | 11.7698 | 37.78
2020-11-06 17:00 | 44141.7083 | 0 | 11.4951 | 37.78
2020-11-06 17:30 | 44141.7292 | 0 | 11.5185 | 37.78
2020-11-06 18:00 | 44141.75 | 0 | 11.8693 | 37.78
2020-11-06 18:30 | 44141.7708 | 0 | 12.4563 | 37.78
2020-11-06 19:00 | 44141.7917 | 0 | 12.1746 | 37.78
2020-11-06 19:30 | 44141.8125 | 0 | 11.8473 | 37.78
2020-11-06 20:00 | 44141.8333 | 0 | 11.7296 | 37.78
2020-11-06 20:30 | 44141.8542 | 0 | 11.1977 | 37.78
2020-11-06 21:00 | 44141.875 | 0 | 10.9994 | 37.78
2020-11-06 21:30 | 44141.8958 | 0 | 10.6975 | 37.78
2020-11-06 22:00 | 44141.9167 | 0 | 10.4225 | 37.78
2020-11-06 22:30 | 44141.9375 | 0 | 9.7906 | 37.78
2020-11-06 23:00 | 44141.9583 | 0 | 9.2976 | 37.78
2020-11-06 23:30 | 44141.9792 | 0 | 9.001 | 37.78
2020-11-07 | 44142 | 0 | 8.4862 | 37.78
2020-11-07 00:30 | 44142.0208 | 0 | 8.233 | 37.78
2020-11-07 01:00 | 44142.0417 | 0 | 8.088 | 37.78
2020-11-07 01:30 | 44142.0625 | 0 | 7.9858 | 37.78
2020-11-07 02:00 | 44142.0833 | 0 | 7.8499 | 37.78
2020-11-07 02:30 | 44142.1042 | 0 | 7.7624 | 37.78
2020-11-07 03:00 | 44142.125 | 0 | 7.7605 | 37.78
2020-11-07 03:30 | 44142.1458 | 0 | 7.7588 | 37.78
2020-11-07 04:00 | 44142.1667 | 0 | 7.6972 | 37.78
2020-11-07 04:30 | 44142.1875 | 0 | 7.6879 | 37.78
2020-11-07 05:00 | 44142.2083 | 0 | 7.7588 | 37.78
2020-11-07 05:30 | 44142.2292 | 0 | 7.7457 | 37.78
2020-11-07 06:00 | 44142.25 | 0 | 7.6786 | 37.78
2020-11-07 06:30 | 44142.2708 | 0 | 7.297 | 37.78
2020-11-07 07:00 | 44142.2917 | 0 | 7.6399 | 37.78
2020-11-07 07:30 | 44142.3125 | 0 | 8.0205 | 37.78
2020-11-07 08:00 | 44142.3333 | 0 | 9.0569 | 37.78
2020-11-07 08:30 | 44142.3542 | 0 | 9.3116 | 37.78
2020-11-07 09:00 | 44142.375 | 0 | 9.3495 | 37.78
2020-11-07 09:30 | 44142.3958 | 0 | 9.7266 | 37.78
2020-11-07 10:00 | 44142.4167 | 0 | 9.5408 | 37.78
2020-11-07 10:30 | 44142.4375 | 0 | 8.5606 | 37.78
2020-11-07 11:00 | 44142.4583 | 0 | 8.134 | 37.78
2020-11-07 11:30 | 44142.4792 | 0 | 8.8914 | 37.78
2020-11-07 12:00 | 44142.5 | 0 | 9.8372 | 37.78
2020-11-07 12:30 | 44142.5208 | 0 | 9.2951 | 37.78
2020-11-07 13:00 | 44142.5417 | 0 | 9.4407 | 37.78
2020-11-07 13:30 | 44142.5625 | 0 | 9.6604 | 37.78
2020-11-07 14:00 | 44142.5833 | 0 | 9.4956 | 37.78
2020-11-07 14:30 | 44142.6042 | 0 | 9.1487 | 37.78
2020-11-07 15:00 | 44142.625 | 0 | 8.8593 | 37.78
2020-11-07 15:30 | 44142.6458 | 0 | 9.4875 | 37.78
2020-11-07 16:00 | 44142.6667 | 0 | 9.7263 | 37.78
2020-11-07 16:30 | 44142.6875 | 0 | 10.245 | 37.78
2020-11-07 17:00 | 44142.7083 | 0 | 10.6435 | 37.78
2020-11-07 17:30 | 44142.7292 | 0 | 10.931 | 37.78
2020-11-07 18:00 | 44142.75 | 0 | 11.3321 | 37.78
2020-11-07 18:30 | 44142.7708 | 0 | 11.9734 | 37.78
2020-11-07 19:00 | 44142.7917 | 0 | 11.8534 | 37.78
2020-11-07 19:30 | 44142.8125 | 0 | 11.533 | 37.78
2020-11-07 20:00 | 44142.8333 | 0 | 11.4397 | 37.78
2020-11-07 20:30 | 44142.8542 | 0 | 10.9481 | 37.78
2020-11-07 21:00 | 44142.875 | 0 | 10.505 | 37.78
2020-11-07 21:30 | 44142.8958 | 0 | 10.0435 | 37.78
2020-11-07 22:00 | 44142.9167 | 0 | 9.6208 | 37.78
2020-11-07 22:30 | 44142.9375 | 0 | 8.9028 | 37.78
2020-11-07 23:00 | 44142.9583 | 0 | 8.4098 | 37.78
2020-11-07 23:30 | 44142.9792 | 0 | 8.1303 | 37.78
2020-11-08 | 44143 | 0 | 7.8664 | 37.78
2020-11-08 00:30 | 44143.0208 | 0 | 7.5856 | 37.78
2020-11-08 01:00 | 44143.0417 | 0 | 7.4521 | 37.78
2020-11-08 01:30 | 44143.0625 | 0 | 7.4017 | 37.78
2020-11-08 02:00 | 44143.0833 | 0 | 7.5299 | 37.78
2020-11-08 02:30 | 44143.1042 | 0 | 7.4142 | 37.78
2020-11-08 03:00 | 44143.125 | 0 | 7.4743 | 37.78
2020-11-08 03:30 | 44143.1458 | 0 | 7.5503 | 37.78
2020-11-08 04:00 | 44143.1667 | 0 | 7.8931 | 37.78
2020-11-08 04:30 | 44143.1875 | 0 | 8.1609 | 37.78
2020-11-08 05:00 | 44143.2083 | 0 | 8.7195 | 37.78
2020-11-08 05:30 | 44143.2292 | 0 | 9.0278 | 37.78
2020-11-08 06:00 | 44143.25 | 0 | 9.4898 | 37.78
2020-11-08 06:30 | 44143.2708 | 0 | 9.7935 | 37.78
2020-11-08 07:00 | 44143.2917 | 0 | 10.2735 | 37.78
2020-11-08 07:30 | 44143.3125 | 0 | 10.176 | 37.78
2020-11-08 08:00 | 44143.3333 | 0 | 10.1502 | 37.78
2020-11-08 08:30 | 44143.3542 | 0 | 9.6829 | 37.78
2020-11-08 09:00 | 44143.375 | 0 | 9.8887 | 37.78
2020-11-08 09:30 | 44143.3958 | 0 | 10.7339 | 37.78
2020-11-08 10:00 | 44143.4167 | 0 | 10.4666 | 37.78
2020-11-08 10:30 | 44143.4375 | 0 | 10.2878 | 37.78
2020-11-08 11:00 | 44143.4583 | 0 | 10.8286 | 37.78
2020-11-08 11:30 | 44143.4792 | 0 | 10.1095 | 37.78
2020-11-08 12:00 | 44143.5 | 0 | 10.4681 | 37.78
2020-11-08 12:30 | 44143.5208 | 0 | 9.9624 | 37.78
2020-11-08 13:00 | 44143.5417 | 0 | 9.6252 | 37.78
2020-11-08 13:30 | 44143.5625 | 0 | 10.7338 | 37.78
2020-11-08 14:00 | 44143.5833 | 0 | 12.0576 | 37.78
2020-11-08 14:30 | 44143.6042 | 0 | 11.3204 | 37.78
2020-11-08 15:00 | 44143.625 | 0 | 12.007 | 37.78
2020-11-08 15:30 | 44143.6458 | 0 | 12.2717 | 37.78
2020-11-08 16:00 | 44143.6667 | 0 | 12.4044 | 37.78
2020-11-08 16:30 | 44143.6875 | 0 | 12.9476 | 37.78
2020-11-08 17:00 | 44143.7083 | 0 | 12.824 | 37.78
2020-11-08 17:30 | 44143.7292 | 0 | 13.3024 | 37.78
2020-11-08 18:00 | 44143.75 | 0 | 13.6212 | 37.78
2020-11-08 18:30 | 44143.7708 | 0 | 14.37 | 37.78
2020-11-08 19:00 | 44143.7917 | 0 | 13.9619 | 37.78
2020-11-08 19:30 | 44143.8125 | 0 | 13.4906 | 37.78
2020-11-08 20:00 | 44143.8333 | 0 | 13.161 | 37.78
2020-11-08 20:30 | 44143.8542 | 0 | 12.5765 | 37.78
2020-11-08 21:00 | 44143.875 | 0 | 12.1113 | 37.78
2020-11-08 21:30 | 44143.8958 | 0 | 11.7184 | 37.78
2020-11-08 22:00 | 44143.9167 | 0 | 11.0692 | 37.78
2020-11-08 22:30 | 44143.9375 | 0 | 10.287 | 37.78
2020-11-08 23:00 | 44143.9583 | 0 | 9.8387 | 37.78
2020-11-08 23:30 | 44143.9792 | 0 | 9.2602 | 37.78
2020-11-09 | 44144 | 0 | 8.7503 | 37.78
2020-11-09 00:30 | 44144.0208 | 0 | 8.2803 | 37.78
2020-11-09 01:00 | 44144.0417 | 0 | 8.1494 | 37.78
2020-11-09 01:30 | 44144.0625 | 0 | 8.0787 | 37.78
2020-11-09 02:00 | 44144.0833 | 0 | 8.0491 | 37.78
2020-11-09 02:30 | 44144.1042 | 0 | 7.9503 | 37.78
2020-11-09 03:00 | 44144.125 | 0 | 7.8349 | 37.78
2020-11-09 03:30 | 44144.1458 | 0 | 7.9284 | 37.78
2020-11-09 04:00 | 44144.1667 | 0 | 8.0959 | 37.78
2020-11-09 04:30 | 44144.1875 | 0 | 8.4961 | 37.78
2020-11-09 05:00 | 44144.2083 | 0 | 8.9987 | 37.78
2020-11-09 05:30 | 44144.2292 | 0 | 9.4998 | 37.78
2020-11-09 06:00 | 44144.25 | 0 | 9.8797 | 37.78
2020-11-09 06:30 | 44144.2708 | 0 | 10.1021 | 37.78
2020-11-09 07:00 | 44144.2917 | 0 | 10.3456 | 37.78
2020-11-09 07:30 | 44144.3125 | 0 | 10.4369 | 37.78
2020-11-09 08:00 | 44144.3333 | 0 | 10.3104 | 37.78
2020-11-09 08:30 | 44144.3542 | 0 | 10.6395 | 37.78
2020-11-09 09:00 | 44144.375 | 0 | 10.657 | 37.78
2020-11-09 09:30 | 44144.3958 | 0 | 9.7543 | 37.78
2020-11-09 10:00 | 44144.4167 | 0 | 11.4253 | 37.78
2020-11-09 10:30 | 44144.4375 | 0 | 11.6293 | 37.78
2020-11-09 11:00 | 44144.4583 | 0 | 10.6085 | 37.78
2020-11-09 11:30 | 44144.4792 | 0 | 11.8914 | 37.78
2020-11-09 12:00 | 44144.5 | 0 | 11.8344 | 37.78
2020-11-09 12:30 | 44144.5208 | 0 | 11.4191 | 37.78
2020-11-09 13:00 | 44144.5417 | 0 | 11.1307 | 37.78
2020-11-09 13:30 | 44144.5625 | 0 | 11.4593 | 37.78
2020-11-09 14:00 | 44144.5833 | 0 | 11.8593 | 37.78
2020-11-09 14:30 | 44144.6042 | 0 | 12.5569 | 37.78
2020-11-09 15:00 | 44144.625 | 0 | 12.1593 | 37.78
2020-11-09 15:30 | 44144.6458 | 0 | 11.6615 | 37.78
2020-11-09 16:00 | 44144.6667 | 0 | 12.2773 | 37.78
2020-11-09 16:30 | 44144.6875 | 0 | 13.1138 | 37.78
2020-11-09 17:00 | 44144.7083 | 0 | 13.0531 | 37.78
2020-11-09 17:30 | 44144.7292 | 0 | 13.3762 | 37.78
2020-11-09 18:00 | 44144.75 | 0 | 13.7955 | 37.78
2020-11-09 18:30 | 44144.7708 | 0 | 14.5511 | 37.78
2020-11-09 19:00 | 44144.7917 | 0 | 14.27 | 37.78
2020-11-09 19:30 | 44144.8125 | 0 | 14.0136 | 37.78
2020-11-09 20:00 | 44144.8333 | 0 | 13.9503 | 37.78
2020-11-09 20:30 | 44144.8542 | 0 | 13.2858 | 37.78
2020-11-09 21:00 | 44144.875 | 0 | 12.2653 | 37.78
2020-11-09 21:30 | 44144.8958 | 0 | 11.9331 | 37.78
2020-11-09 22:00 | 44144.9167 | 0 | 11.5607 | 37.78
2020-11-09 22:30 | 44144.9375 | 0 | 10.7026 | 37.78
2020-11-09 23:00 | 44144.9583 | 0 | 10.1087 | 37.78
2020-11-09 23:30 | 44144.9792 | 0 | 9.5648 | 37.78
2020-11-10 | 44145 | 0 | 9.0525 | 37.78
2020-11-10 00:30 | 44145.0208 | 0 | 8.5604 | 37.78
2020-11-10 01:00 | 44145.0417 | 0 | 8.3958 | 37.78
2020-11-10 01:30 | 44145.0625 | 0 | 8.3616 | 37.78
2020-11-10 02:00 | 44145.0833 | 0 | 8.3189 | 37.78
2020-11-10 02:30 | 44145.1042 | 0 | 8.2782 | 37.78
2020-11-10 03:00 | 44145.125 | 0 | 8.2705 | 37.78
2020-11-10 03:30 | 44145.1458 | 0 | 8.2687 | 37.78
2020-11-10 04:00 | 44145.1667 | 0 | 8.4644 | 37.78
2020-11-10 04:30 | 44145.1875 | 0 | 8.8883 | 37.78
2020-11-10 05:00 | 44145.2083 | 0 | 9.3912 | 37.78
2020-11-10 05:30 | 44145.2292 | 0 | 9.6173 | 37.78
2020-11-10 06:00 | 44145.25 | 0 | 9.9734 | 37.78
2020-11-10 06:30 | 44145.2708 | 0 | 10.4447 | 37.78
2020-11-10 07:00 | 44145.2917 | 0 | 10.7349 | 37.78
2020-11-10 07:30 | 44145.3125 | 0 | 10.5626 | 37.78
2020-11-10 08:00 | 44145.3333 | 0 | 10.8463 | 37.78
2020-11-10 08:30 | 44145.3542 | 0 | 10.87 | 37.78
2020-11-10 09:00 | 44145.375 | 0 | 10.8821 | 37.78
2020-11-10 09:30 | 44145.3958 | 0 | 10.7762 | 37.78
2020-11-10 10:00 | 44145.4167 | 0 | 10.364 | 37.78
2020-11-10 10:30 | 44145.4375 | 0 | 10.3121 | 37.78
2020-11-10 11:00 | 44145.4583 | 0 | 10.1892 | 37.78
2020-11-10 11:30 | 44145.4792 | 0 | 10.3382 | 37.78
2020-11-10 12:00 | 44145.5 | 0 | 10.1611 | 37.78
2020-11-10 12:30 | 44145.5208 | 0 | 10.0795 | 37.78
2020-11-10 13:00 | 44145.5417 | 0 | 10.3276 | 37.78
2020-11-10 13:30 | 44145.5625 | 0 | 10.8064 | 37.78
2020-11-10 14:00 | 44145.5833 | 0 | 11.2151 | 37.78
2020-11-10 14:30 | 44145.6042 | 0 | 11.4097 | 37.78
2020-11-10 15:00 | 44145.625 | 0 | 11.9747 | 37.78
2020-11-10 15:30 | 44145.6458 | 0 | 12.6495 | 37.78
2020-11-10 16:00 | 44145.6667 | 0 | 13.3947 | 37.78
2020-11-10 16:30 | 44145.6875 | 0 | 13.8261 | 37.78
2020-11-10 17:00 | 44145.7083 | 0 | 14.1869 | 37.78
2020-11-10 17:30 | 44145.7292 | 0 | 14.3708 | 37.78
2020-11-10 18:00 | 44145.75 | 0 | 14.2891 | 37.78
2020-11-10 18:30 | 44145.7708 | 0 | 14.9532 | 37.78
2020-11-10 19:00 | 44145.7917 | 0 | 14.7303 | 37.78
2020-11-10 19:30 | 44145.8125 | 0 | 14.3671 | 37.78
2020-11-10 20:00 | 44145.8333 | 0 | 14.0036 | 37.78
2020-11-10 20:30 | 44145.8542 | 0 | 13.4515 | 37.78
2020-11-10 21:00 | 44145.875 | 0 | 12.8749 | 37.78
2020-11-10 21:30 | 44145.8958 | 0 | 12.4132 | 37.78
2020-11-10 22:00 | 44145.9167 | 0 | 11.7279 | 37.78
2020-11-10 22:30 | 44145.9375 | 0 | 10.964 | 37.78
2020-11-10 23:00 | 44145.9583 | 0 | 10.4065 | 37.78
2020-11-10 23:30 | 44145.9792 | 0 | 9.8663 | 37.78
2020-11-11 | 44146 | 0 | 9.2639 | 37.78
2020-11-11 00:30 | 44146.0208 | 0 | 8.8118 | 37.78
2020-11-11 01:00 | 44146.0417 | 0 | 8.5905 | 37.78
2020-11-11 01:30 | 44146.0625 | 0 | 8.5068 | 37.78
2020-11-11 02:00 | 44146.0833 | 0 | 8.5722 | 37.78
2020-11-11 02:30 | 44146.1042 | 0 | 8.4675 | 37.78
2020-11-11 03:00 | 44146.125 | 0 | 8.5199 | 37.78
2020-11-11 03:30 | 44146.1458 | 0 | 8.5648 | 37.78
2020-11-11 04:00 | 44146.1667 | 0 | 8.6653 | 37.78
2020-11-11 04:30 | 44146.1875 | 0 | 8.9891 | 37.78
2020-11-11 05:00 | 44146.2083 | 0 | 9.5286 | 37.78
2020-11-11 05:30 | 44146.2292 | 0 | 9.9459 | 37.78
2020-11-11 06:00 | 44146.25 | 0 | 10.8566 | 37.78
2020-11-11 06:30 | 44146.2708 | 0 | 11.1492 | 37.78
2020-11-11 07:00 | 44146.2917 | 0 | 11.9459 | 37.78
2020-11-11 07:30 | 44146.3125 | 0 | 12.5205 | 37.78
2020-11-11 08:00 | 44146.3333 | 0 | 11.7279 | 37.78
2020-11-11 08:30 | 44146.3542 | 0 | 11.797 | 37.78
2020-11-11 09:00 | 44146.375 | 0 | 12.1599 | 37.78
2020-11-11 09:30 | 44146.3958 | 0 | 11.4335 | 37.78
2020-11-11 10:00 | 44146.4167 | 0 | 11.389 | 37.78
2020-11-11 10:30 | 44146.4375 | 0 | 11.6353 | 37.78
2020-11-11 11:00 | 44146.4583 | 0 | 11.2115 | 37.78
2020-11-11 11:30 | 44146.4792 | 0 | 11.2164 | 37.78
2020-11-11 12:00 | 44146.5 | 0 | 11.7709 | 37.78
2020-11-11 12:30 | 44146.5208 | 0 | 11.0901 | 37.78
2020-11-11 13:00 | 44146.5417 | 0 | 11.9029 | 37.78
2020-11-11 13:30 | 44146.5625 | 0 | 11.1981 | 37.78
2020-11-11 14:00 | 44146.5833 | 0 | 11.5075 | 37.78
2020-11-11 14:30 | 44146.6042 | 0 | 11.7695 | 37.78
2020-11-11 15:00 | 44146.625 | 0 | 12.0842 | 37.78
2020-11-11 15:30 | 44146.6458 | 0 | 12.0373 | 37.78
2020-11-11 16:00 | 44146.6667 | 0 | 12.4782 | 37.78
2020-11-11 16:30 | 44146.6875 | 0 | 12.9826 | 37.78
2020-11-11 17:00 | 44146.7083 | 0 | 13.2916 | 37.78
2020-11-11 17:30 | 44146.7292 | 0 | 13.3955 | 37.78
2020-11-11 18:00 | 44146.75 | 0 | 13.6387 | 37.78
2020-11-11 18:30 | 44146.7708 | 0 | 14.1095 | 37.78
2020-11-11 19:00 | 44146.7917 | 0 | 13.8794 | 37.78
2020-11-11 19:30 | 44146.8125 | 0 | 13.7339 | 37.78
2020-11-11 20:00 | 44146.8333 | 0 | 13.5525 | 37.78
2020-11-11 20:30 | 44146.8542 | 0 | 13.1099 | 37.78
2020-11-11 21:00 | 44146.875 | 0 | 12.5655 | 37.78
2020-11-11 21:30 | 44146.8958 | 0 | 12.2315 | 37.78
2020-11-11 22:00 | 44146.9167 | 0 | 11.6379 | 37.78
2020-11-11 22:30 | 44146.9375 | 0 | 10.6881 | 37.78
2020-11-11 23:00 | 44146.9583 | 0 | 10.1264 | 37.78
2020-11-11 23:30 | 44146.9792 | 0 | 9.5287 | 37.78
2020-11-12 | 44147 | 0 | 8.8958 | 37.78
2020-11-12 00:30 | 44147.0208 | 0 | 8.5774 | 37.78
2020-11-12 01:00 | 44147.0417 | 0 | 8.4972 | 37.78
2020-11-12 01:30 | 44147.0625 | 0 | 8.2969 | 37.78
2020-11-12 02:00 | 44147.0833 | 0 | 8.2353 | 37.78
2020-11-12 02:30 | 44147.1042 | 0 | 8.1122 | 37.78
2020-11-12 03:00 | 44147.125 | 0 | 8.0167 | 37.78
2020-11-12 03:30 | 44147.1458 | 0 | 8.1677 | 37.78
2020-11-12 04:00 | 44147.1667 | 0 | 8.2658 | 37.78
2020-11-12 04:30 | 44147.1875 | 0 | 8.6894 | 37.78
2020-11-12 05:00 | 44147.2083 | 0 | 8.9705 | 37.78
2020-11-12 05:30 | 44147.2292 | 0 | 9.3607 | 37.78
2020-11-12 06:00 | 44147.25 | 0 | 9.8425 | 37.78
2020-11-12 06:30 | 44147.2708 | 0 | 10.3549 | 37.78
2020-11-12 07:00 | 44147.2917 | 0 | 10.7113 | 37.78
2020-11-12 07:30 | 44147.3125 | 0 | 11.429 | 37.78
2020-11-12 08:00 | 44147.3333 | 0 | 10.8595 | 37.78
2020-11-12 08:30 | 44147.3542 | 0 | 11.9096 | 37.78
2020-11-12 09:00 | 44147.375 | 0 | 10.39 | 37.78
2020-11-12 09:30 | 44147.3958 | 0 | 12.1885 | 37.78
2020-11-12 10:00 | 44147.4167 | 0 | 13.7518 | 37.78
2020-11-12 10:30 | 44147.4375 | 0 | 13.9782 | 37.78
2020-11-12 11:00 | 44147.4583 | 0 | 13.384 | 37.78
2020-11-12 11:30 | 44147.4792 | 0 | 12.9609 | 37.78
2020-11-12 12:00 | 44147.5 | 0 | 12.8112 | 37.78
2020-11-12 12:30 | 44147.5208 | 0 | 12.2959 | 37.78
2020-11-12 13:00 | 44147.5417 | 0 | 10.7147 | 37.78
2020-11-12 13:30 | 44147.5625 | 0 | 11.1615 | 37.78
2020-11-12 14:00 | 44147.5833 | 0 | 11.6133 | 37.78
2020-11-12 14:30 | 44147.6042 | 0 | 11.4032 | 37.78
2020-11-12 15:00 | 44147.625 | 0 | 11.7579 | 37.78
2020-11-12 15:30 | 44147.6458 | 0 | 12.232 | 37.78
2020-11-12 16:00 | 44147.6667 | 0 | 13.5831 | 37.78
2020-11-12 16:30 | 44147.6875 | 0 | 13.8774 | 37.78
2020-11-12 17:00 | 44147.7083 | 0 | 13.9403 | 37.78
2020-11-12 17:30 | 44147.7292 | 0 | 13.8774 | 37.78
2020-11-12 18:00 | 44147.75 | 0 | 13.7427 | 37.78
2020-11-12 18:30 | 44147.7708 | 0 | 14.0811 | 37.78
2020-11-12 19:00 | 44147.7917 | 0 | 14.0872 | 37.78
2020-11-12 19:30 | 44147.8125 | 0 | 13.7765 | 37.78
2020-11-12 20:00 | 44147.8333 | 0 | 13.6161 | 37.78
2020-11-12 20:30 | 44147.8542 | 0 | 13.3089 | 37.78
2020-11-12 21:00 | 44147.875 | 0 | 12.7302 | 37.78
2020-11-12 21:30 | 44147.8958 | 0 | 12.3706 | 37.78
2020-11-12 22:00 | 44147.9167 | 0 | 11.7251 | 37.78
2020-11-12 22:30 | 44147.9375 | 0 | 11.0884 | 37.78
2020-11-12 23:00 | 44147.9583 | 0 | 10.3515 | 37.78
2020-11-12 23:30 | 44147.9792 | 0 | 9.8138 | 37.78
2020-11-13 | 44148 | 0 | 9.2883 | 37.78
2020-11-13 00:30 | 44148.0208 | 0 | 8.9026 | 37.78
2020-11-13 01:00 | 44148.0417 | 0 | 8.66 | 37.78
2020-11-13 01:30 | 44148.0625 | 0 | 8.3754 | 37.78
2020-11-13 02:00 | 44148.0833 | 0 | 8.257 | 37.78
2020-11-13 02:30 | 44148.1042 | 0 | 8.1541 | 37.78
2020-11-13 03:00 | 44148.125 | 0 | 8.1325 | 37.78
2020-11-13 03:30 | 44148.1458 | 0 | 8.2029 | 37.78
2020-11-13 04:00 | 44148.1667 | 0 | 8.2563 | 37.78
2020-11-13 04:30 | 44148.1875 | 0 | 8.3314 | 37.78
2020-11-13 05:00 | 44148.2083 | 0 | 8.4681 | 37.78
2020-11-13 05:30 | 44148.2292 | 0 | 8.437 | 37.78
2020-11-13 06:00 | 44148.25 | 0 | 8.4512 | 37.78
2020-11-13 06:30 | 44148.2708 | 0 | 8.4898 | 37.78
2020-11-13 07:00 | 44148.2917 | 0 | 8.4722 | 37.78
2020-11-13 07:30 | 44148.3125 | 0 | 8.5805 | 37.78
2020-11-13 08:00 | 44148.3333 | 0 | 8.9733 | 37.78
2020-11-13 08:30 | 44148.3542 | 0 | 8.9094 | 37.78
2020-11-13 09:00 | 44148.375 | 0 | 9.0292 | 37.78
2020-11-13 09:30 | 44148.3958 | 0 | 9.3791 | 37.78
2020-11-13 10:00 | 44148.4167 | 0 | 9.3486 | 37.78
2020-11-13 10:30 | 44148.4375 | 0 | 9.589 | 37.78
2020-11-13 11:00 | 44148.4583 | 0 | 9.7377 | 37.78
2020-11-13 11:30 | 44148.4792 | 0 | 9.89 | 37.78
2020-11-13 12:00 | 44148.5 | 0 | 9.9096 | 37.78
2020-11-13 12:30 | 44148.5208 | 0 | 10.3325 | 37.78
2020-11-13 13:00 | 44148.5417 | 0 | 10.7787 | 37.78
2020-11-13 13:30 | 44148.5625 | 0 | 11.6171 | 37.78
2020-11-13 14:00 | 44148.5833 | 0 | 11.8763 | 37.78
2020-11-13 14:30 | 44148.6042 | 0 | 12.351 | 37.78
2020-11-13 15:00 | 44148.625 | 0 | 13.0348 | 37.78
2020-11-13 15:30 | 44148.6458 | 0 | 13.4122 | 37.78
2020-11-13 16:00 | 44148.6667 | 0 | 13.8041 | 37.78
2020-11-13 16:30 | 44148.6875 | 0 | 14.2036 | 37.78
2020-11-13 17:00 | 44148.7083 | 0 | 14.4337 | 37.78
2020-11-13 17:30 | 44148.7292 | 0 | 14.1075 | 37.78
2020-11-13 18:00 | 44148.75 | 0 | 14.121 | 37.78
2020-11-13 18:30 | 44148.7708 | 0 | 14.6419 | 37.78
2020-11-13 19:00 | 44148.7917 | 0 | 14.6207 | 37.78
2020-11-13 19:30 | 44148.8125 | 0 | 14.2963 | 37.78
2020-11-13 20:00 | 44148.8333 | 0 | 14.1189 | 37.78
2020-11-13 20:30 | 44148.8542 | 0 | 13.5026 | 37.78
2020-11-13 21:00 | 44148.875 | 0 | 12.8964 | 37.78
2020-11-13 21:30 | 44148.8958 | 0 | 12.5281 | 37.78
2020-11-13 22:00 | 44148.9167 | 0 | 11.8525 | 37.78
2020-11-13 22:30 | 44148.9375 | 0 | 11.0835 | 37.78
2020-11-13 23:00 | 44148.9583 | 0 | 10.5268 | 37.78
2020-11-13 23:30 | 44148.9792 | 0 | 9.9532 | 37.78
2020-11-14 | 44149 | 0 | 9.3485 | 37.78
2020-11-14 00:30 | 44149.0208 | 0 | 8.9892 | 37.78
2020-11-14 01:00 | 44149.0417 | 0 | 8.7153 | 37.78
2020-11-14 01:30 | 44149.0625 | 0 | 8.617 | 37.78
2020-11-14 02:00 | 44149.0833 | 0 | 8.4627 | 37.78
2020-11-14 02:30 | 44149.1042 | 0 | 8.3159 | 37.78
2020-11-14 03:00 | 44149.125 | 0 | 8.148 | 37.78
2020-11-14 03:30 | 44149.1458 | 0 | 8.0268 | 37.78
2020-11-14 04:00 | 44149.1667 | 0 | 7.9186 | 37.78
2020-11-14 04:30 | 44149.1875 | 0 | 7.9146 | 37.78
2020-11-14 05:00 | 44149.2083 | 0 | 7.8097 | 37.78
2020-11-14 05:30 | 44149.2292 | 0 | 7.7007 | 37.78
2020-11-14 06:00 | 44149.25 | 0 | 7.834 | 37.78
2020-11-14 06:30 | 44149.2708 | 0 | 8.0486 | 37.78
2020-11-14 07:00 | 44149.2917 | 0 | 7.6316 | 37.78
2020-11-14 07:30 | 44149.3125 | 0 | 8.0472 | 37.78
2020-11-14 08:00 | 44149.3333 | 0 | 8.1839 | 37.78
2020-11-14 08:30 | 44149.3542 | 0 | 8.3941 | 37.78
2020-11-14 09:00 | 44149.375 | 0 | 8.4967 | 37.78
2020-11-14 09:30 | 44149.3958 | 0 | 8.6143 | 37.78
2020-11-14 10:00 | 44149.4167 | 0 | 8.7977 | 37.78
2020-11-14 10:30 | 44149.4375 | 0 | 9.3198 | 37.78
2020-11-14 11:00 | 44149.4583 | 0 | 9.5036 | 37.78
2020-11-14 11:30 | 44149.4792 | 0 | 9.7536 | 37.78
2020-11-14 12:00 | 44149.5 | 0 | 9.8149 | 37.78
2020-11-14 12:30 | 44149.5208 | 0 | 10.133 | 37.78
2020-11-14 13:00 | 44149.5417 | 0 | 10.6963 | 37.78
2020-11-14 13:30 | 44149.5625 | 0 | 11.2157 | 37.78
2020-11-14 14:00 | 44149.5833 | 0 | 11.9093 | 37.78
2020-11-14 14:30 | 44149.6042 | 0 | 12.6017 | 37.78
2020-11-14 15:00 | 44149.625 | 0 | 13.2772 | 37.78
2020-11-14 15:30 | 44149.6458 | 0 | 13.9218 | 37.78
2020-11-14 16:00 | 44149.6667 | 0 | 14.5203 | 37.78
2020-11-14 16:30 | 44149.6875 | 0 | 14.9037 | 37.78
2020-11-14 17:00 | 44149.7083 | 0 | 14.9832 | 37.78
2020-11-14 17:30 | 44149.7292 | 0 | 15.0767 | 37.78
2020-11-14 18:00 | 44149.75 | 0 | 15.1808 | 37.78
2020-11-14 18:30 | 44149.7708 | 0 | 15.6223 | 37.78
2020-11-14 19:00 | 44149.7917 | 0 | 15.6931 | 37.78
2020-11-14 19:30 | 44149.8125 | 0 | 15.1889 | 37.78
2020-11-14 20:00 | 44149.8333 | 0 | 14.8037 | 37.78
2020-11-14 20:30 | 44149.8542 | 0 | 14.0683 | 37.78
2020-11-14 21:00 | 44149.875 | 0 | 13.3048 | 37.78
2020-11-14 21:30 | 44149.8958 | 0 | 12.6497 | 37.78
2020-11-14 22:00 | 44149.9167 | 0 | 11.903 | 37.78
2020-11-14 22:30 | 44149.9375 | 0 | 10.9963 | 37.78
2020-11-14 23:00 | 44149.9583 | 0 | 10.2705 | 37.78
2020-11-14 23:30 | 44149.9792 | 0 | 9.8082 | 37.78
2020-11-15 | 44150 | 0 | 9.5099 | 37.78
2020-11-15 00:30 | 44150.0208 | 0 | 9.2186 | 37.78
2020-11-15 01:00 | 44150.0417 | 0 | 8.9721 | 37.78
2020-11-15 01:30 | 44150.0625 | 0 | 8.8755 | 37.78
2020-11-15 02:00 | 44150.0833 | 0 | 8.8721 | 37.78
2020-11-15 02:30 | 44150.1042 | 0 | 8.7124 | 37.78
2020-11-15 03:00 | 44150.125 | 0 | 8.7233 | 37.78
2020-11-15 03:30 | 44150.1458 | 0 | 8.7043 | 37.78
2020-11-15 04:00 | 44150.1667 | 0 | 8.8701 | 37.78
2020-11-15 04:30 | 44150.1875 | 0 | 9.4387 | 37.78
2020-11-15 05:00 | 44150.2083 | 0 | 9.9572 | 37.78
2020-11-15 05:30 | 44150.2292 | 0 | 10.6969 | 37.78
2020-11-15 06:00 | 44150.25 | 0 | 11.4871 | 37.78
2020-11-15 06:30 | 44150.2708 | 0 | 12.1713 | 37.78
2020-11-15 07:00 | 44150.2917 | 0 | 13.6665 | 37.78
2020-11-15 07:30 | 44150.3125 | 0 | 14.1023 | 37.78
2020-11-15 08:00 | 44150.3333 | 0 | 14.6036 | 37.78
2020-11-15 08:30 | 44150.3542 | 0 | 14.9409 | 37.78
2020-11-15 09:00 | 44150.375 | 0 | 13.4605 | 37.78
2020-11-15 09:30 | 44150.3958 | 0 | 14.0531 | 37.78
2020-11-15 10:00 | 44150.4167 | 0 | 15.0739 | 37.78
2020-11-15 10:30 | 44150.4375 | 0 | 14.4077 | 37.78
2020-11-15 11:00 | 44150.4583 | 0 | 14.9697 | 37.78
2020-11-15 11:30 | 44150.4792 | 0 | 15.0739 | 37.78
2020-11-15 12:00 | 44150.5 | 0 | 14.6807 | 37.78
2020-11-15 12:30 | 44150.5208 | 0 | 14.7206 | 37.78
2020-11-15 13:00 | 44150.5417 | 0 | 15.2816 | 37.78
2020-11-15 13:30 | 44150.5625 | 0 | 15.7946 | 37.78
2020-11-15 14:00 | 44150.5833 | 0 | 16.2618 | 37.78
2020-11-15 14:30 | 44150.6042 | 0 | 16.5167 | 37.78
2020-11-15 15:00 | 44150.625 | 0 | 16.6345 | 37.78
2020-11-15 15:30 | 44150.6458 | 0 | 17.2774 | 37.78
2020-11-15 16:00 | 44150.6667 | 0 | 17.5578 | 37.78
2020-11-15 16:30 | 44150.6875 | 0 | 18.0895 | 37.78
2020-11-15 17:00 | 44150.7083 | 0 | 17.9277 | 37.78
2020-11-15 17:30 | 44150.7292 | 0 | 17.7978 | 37.78
2020-11-15 18:00 | 44150.75 | 0 | 17.6015 | 37.78
2020-11-15 18:30 | 44150.7708 | 0 | 18.3876 | 37.78
2020-11-15 19:00 | 44150.7917 | 0 | 17.9809 | 37.78
2020-11-15 19:30 | 44150.8125 | 0 | 17.6658 | 37.78
2020-11-15 20:00 | 44150.8333 | 0 | 17.3382 | 37.78
2020-11-15 20:30 | 44150.8542 | 0 | 16.3988 | 37.78
2020-11-15 21:00 | 44150.875 | 0 | 15.5528 | 37.78
2020-11-15 21:30 | 44150.8958 | 0 | 14.8479 | 37.78
2020-11-15 22:00 | 44150.9167 | 0 | 13.9918 | 37.78
2020-11-15 22:30 | 44150.9375 | 0 | 12.9184 | 37.78
2020-11-15 23:00 | 44150.9583 | 0 | 12.1941 | 37.78
2020-11-15 23:30 | 44150.9792 | 0 | 11.4499 | 37.78
2020-11-16 | 44151 | 0 | 10.7203 | 37.78
2020-11-16 00:30 | 44151.0208 | 0 | 10.3041 | 37.78
2020-11-16 01:00 | 44151.0417 | 0 | 9.9231 | 37.78
2020-11-16 01:30 | 44151.0625 | 0 | 9.5779 | 37.78
2020-11-16 02:00 | 44151.0833 | 0 | 9.5726 | 37.78
2020-11-16 02:30 | 44151.1042 | 0 | 9.4873 | 37.78
2020-11-16 03:00 | 44151.125 | 0 | 9.3432 | 37.78
2020-11-16 03:30 | 44151.1458 | 0 | 9.289 | 37.78
2020-11-16 04:00 | 44151.1667 | 0 | 9.4034 | 37.78
2020-11-16 04:30 | 44151.1875 | 0 | 9.9333 | 37.78
2020-11-16 05:00 | 44151.2083 | 0 | 10.3639 | 37.78
2020-11-16 05:30 | 44151.2292 | 0 | 10.5575 | 37.78
2020-11-16 06:00 | 44151.25 | 0 | 11.783 | 37.78
2020-11-16 06:30 | 44151.2708 | 0 | 12.3104 | 37.78
2020-11-16 07:00 | 44151.2917 | 0 | 12.6464 | 37.78
2020-11-16 07:30 | 44151.3125 | 0 | 13.283 | 37.78
2020-11-16 08:00 | 44151.3333 | 0 | 13.3211 | 37.78
2020-11-16 08:30 | 44151.3542 | 0 | 13.7361 | 37.78
2020-11-16 09:00 | 44151.375 | 0 | 13.8212 | 37.78
2020-11-16 09:30 | 44151.3958 | 0 | 14.2857 | 37.78
2020-11-16 10:00 | 44151.4167 | 0 | 14.6304 | 37.78
2020-11-16 10:30 | 44151.4375 | 0 | 15.2997 | 37.78
2020-11-16 11:00 | 44151.4583 | 0 | 15.0992 | 37.78
2020-11-16 11:30 | 44151.4792 | 0 | 16.3164 | 37.78
2020-11-16 12:00 | 44151.5 | 0 | 17.1515 | 37.78
2020-11-16 12:30 | 44151.5208 | 0 | 17.0175 | 37.78
2020-11-16 13:00 | 44151.5417 | 0 | 17.1222 | 37.78
2020-11-16 13:30 | 44151.5625 | 0 | 18.7099 | 37.78
2020-11-16 14:00 | 44151.5833 | 0 | 19.1025 | 37.78
2020-11-16 14:30 | 44151.6042 | 0 | 18.2221 | 37.78
2020-11-16 15:00 | 44151.625 | 0 | 17.2611 | 37.78
2020-11-16 15:30 | 44151.6458 | 0 | 17.0204 | 37.78
2020-11-16 16:00 | 44151.6667 | 0 | 17.2599 | 37.78
2020-11-16 16:30 | 44151.6875 | 0 | 17.4391 | 37.78
2020-11-16 17:00 | 44151.7083 | 0 | 17.186 | 37.78
2020-11-16 17:30 | 44151.7292 | 0 | 17.008 | 37.78
2020-11-16 18:00 | 44151.75 | 0 | 16.8646 | 37.78
2020-11-16 18:30 | 44151.7708 | 0 | 16.899 | 37.78
2020-11-16 19:00 | 44151.7917 | 0 | 16.4653 | 37.78
2020-11-16 19:30 | 44151.8125 | 0 | 16.0389 | 37.78
2020-11-16 20:00 | 44151.8333 | 0 | 15.6171 | 37.78
2020-11-16 20:30 | 44151.8542 | 0 | 14.6919 | 37.78
2020-11-16 21:00 | 44151.875 | 0 | 13.9217 | 37.78
2020-11-16 21:30 | 44151.8958 | 0 | 13.4073 | 37.78
2020-11-16 22:00 | 44151.9167 | 0 | 12.5646 | 37.78
2020-11-16 22:30 | 44151.9375 | 0 | 11.6935 | 37.78
2020-11-16 23:00 | 44151.9583 | 0 | 11.0693 | 37.78
2020-11-16 23:30 | 44151.9792 | 0 | 10.2894 | 37.78
2020-11-17 | 44152 | 0 | 9.7248 | 37.78
2020-11-17 00:30 | 44152.0208 | 0 | 9.4064 | 37.78
2020-11-17 01:00 | 44152.0417 | 0 | 9.2261 | 37.78
2020-11-17 01:30 | 44152.0625 | 0 | 9.0569 | 37.78
2020-11-17 02:00 | 44152.0833 | 0 | 8.8749 | 37.78
2020-11-17 02:30 | 44152.1042 | 0 | 8.7788 | 37.78
2020-11-17 03:00 | 44152.125 | 0 | 8.864 | 37.78
2020-11-17 03:30 | 44152.1458 | 0 | 8.862 | 37.78
2020-11-17 04:00 | 44152.1667 | 0 | 9.0935 | 37.78
2020-11-17 04:30 | 44152.1875 | 0 | 9.4433 | 37.78
2020-11-17 05:00 | 44152.2083 | 0 | 9.9155 | 37.78
2020-11-17 05:30 | 44152.2292 | 0 | 10.2581 | 37.78
2020-11-17 06:00 | 44152.25 | 0 | 10.6019 | 37.78
2020-11-17 06:30 | 44152.2708 | 0 | 11.122 | 37.78
2020-11-17 07:00 | 44152.2917 | 0 | 11.3444 | 37.78
2020-11-17 07:30 | 44152.3125 | 0 | 11.9047 | 37.78
2020-11-17 08:00 | 44152.3333 | 0 | 11.7558 | 37.78
2020-11-17 08:30 | 44152.3542 | 0 | 11.745 | 37.78
2020-11-17 09:00 | 44152.375 | 0 | 11.6705 | 37.78
2020-11-17 09:30 | 44152.3958 | 0 | 11.8908 | 37.78
2020-11-17 10:00 | 44152.4167 | 0 | 12.158 | 37.78
2020-11-17 10:30 | 44152.4375 | 0 | 12.5127 | 37.78
2020-11-17 11:00 | 44152.4583 | 0 | 12.3626 | 37.78
2020-11-17 11:30 | 44152.4792 | 0 | 12.4698 | 37.78
2020-11-17 12:00 | 44152.5 | 0 | 11.8673 | 37.78
2020-11-17 12:30 | 44152.5208 | 0 | 12.1006 | 37.78
2020-11-17 13:00 | 44152.5417 | 0 | 12.6933 | 37.78
2020-11-17 13:30 | 44152.5625 | 0 | 13.0769 | 37.78
2020-11-17 14:00 | 44152.5833 | 0 | 13.2791 | 37.78
2020-11-17 14:30 | 44152.6042 | 0 | 13.6031 | 37.78
2020-11-17 15:00 | 44152.625 | 0 | 13.6877 | 37.78
2020-11-17 15:30 | 44152.6458 | 0 | 14.3048 | 37.78
2020-11-17 16:00 | 44152.6667 | 0 | 14.7768 | 37.78
2020-11-17 16:30 | 44152.6875 | 0 | 14.8499 | 37.78
2020-11-17 17:00 | 44152.7083 | 0 | 14.411 | 37.78
2020-11-17 17:30 | 44152.7292 | 0 | 14.2726 | 37.78
2020-11-17 18:00 | 44152.75 | 0 | 14.2875 | 37.78
2020-11-17 18:30 | 44152.7708 | 0 | 14.833 | 37.78
2020-11-17 19:00 | 44152.7917 | 0 | 14.6874 | 37.78
2020-11-17 19:30 | 44152.8125 | 0 | 14.0988 | 37.78
2020-11-17 20:00 | 44152.8333 | 0 | 13.8543 | 37.78
2020-11-17 20:30 | 44152.8542 | 0 | 13.3908 | 37.78
2020-11-17 21:00 | 44152.875 | 0 | 12.7481 | 37.78
2020-11-17 21:30 | 44152.8958 | 0 | 12.4332 | 37.78
2020-11-17 22:00 | 44152.9167 | 0 | 11.9003 | 37.78
2020-11-17 22:30 | 44152.9375 | 0 | 11.148 | 37.78
2020-11-17 23:00 | 44152.9583 | 0 | 10.4952 | 37.78
2020-11-17 23:30 | 44152.9792 | 0 | 9.9127 | 37.78
2020-11-18 | 44153 | 0 | 9.3886 | 37.78
2020-11-18 00:30 | 44153.0208 | 0 | 8.8741 | 37.78
2020-11-18 01:00 | 44153.0417 | 0 | 8.7179 | 37.78
2020-11-18 01:30 | 44153.0625 | 0 | 8.638 | 37.78
2020-11-18 02:00 | 44153.0833 | 0 | 8.5642 | 37.78
2020-11-18 02:30 | 44153.1042 | 0 | 8.4817 | 37.78
2020-11-18 03:00 | 44153.125 | 0 | 8.4465 | 37.78
2020-11-18 03:30 | 44153.1458 | 0 | 8.5757 | 37.78
2020-11-18 04:00 | 44153.1667 | 0 | 8.7828 | 37.78
2020-11-18 04:30 | 44153.1875 | 0 | 8.9033 | 37.78
2020-11-18 05:00 | 44153.2083 | 0 | 9.2783 | 37.78
2020-11-18 05:30 | 44153.2292 | 0 | 9.645 | 37.78
2020-11-18 06:00 | 44153.25 | 0 | 10.1021 | 37.78
2020-11-18 06:30 | 44153.2708 | 0 | 10.5555 | 37.78
2020-11-18 07:00 | 44153.2917 | 0 | 10.8347 | 37.78
2020-11-18 07:30 | 44153.3125 | 0 | 11.0919 | 37.78
2020-11-18 08:00 | 44153.3333 | 0 | 11.6974 | 37.78
2020-11-18 08:30 | 44153.3542 | 0 | 12.0196 | 37.78
2020-11-18 09:00 | 44153.375 | 0 | 11.8991 | 37.78
2020-11-18 09:30 | 44153.3958 | 0 | 11.4275 | 37.78
2020-11-18 10:00 | 44153.4167 | 0 | 12.0126 | 37.78
2020-11-18 10:30 | 44153.4375 | 0 | 12.4482 | 37.78
2020-11-18 11:00 | 44153.4583 | 0 | 12.1408 | 37.78
2020-11-18 11:30 | 44153.4792 | 0 | 11.8763 | 37.78
2020-11-18 12:00 | 44153.5 | 0 | 11.3944 | 37.78
2020-11-18 12:30 | 44153.5208 | 0 | 11.4837 | 37.78
2020-11-18 13:00 | 44153.5417 | 0 | 11.8446 | 37.78
2020-11-18 13:30 | 44153.5625 | 0 | 11.9723 | 37.78
2020-11-18 14:00 | 44153.5833 | 0 | 12.1151 | 37.78
2020-11-18 14:30 | 44153.6042 | 0 | 12.7069 | 37.78
2020-11-18 15:00 | 44153.625 | 0 | 12.7574 | 37.78
2020-11-18 15:30 | 44153.6458 | 0 | 13.4257 | 37.78
2020-11-18 16:00 | 44153.6667 | 0 | 13.9578 | 37.78
2020-11-18 16:30 | 44153.6875 | 0 | 14.4093 | 37.78
2020-11-18 17:00 | 44153.7083 | 0 | 14.4817 | 37.78
2020-11-18 17:30 | 44153.7292 | 0 | 14.5641 | 37.78
2020-11-18 18:00 | 44153.75 | 0 | 14.3802 | 37.78
2020-11-18 18:30 | 44153.7708 | 0 | 14.8883 | 37.78
2020-11-18 19:00 | 44153.7917 | 0 | 14.7375 | 37.78
2020-11-18 19:30 | 44153.8125 | 0 | 14.4164 | 37.78
2020-11-18 20:00 | 44153.8333 | 0 | 14.213 | 37.78
2020-11-18 20:30 | 44153.8542 | 0 | 13.5819 | 37.78
2020-11-18 21:00 | 44153.875 | 0 | 12.9878 | 37.78
2020-11-18 21:30 | 44153.8958 | 0 | 12.5023 | 37.78
2020-11-18 22:00 | 44153.9167 | 0 | 11.7653 | 37.78
2020-11-18 22:30 | 44153.9375 | 0 | 10.8493 | 37.78
2020-11-18 23:00 | 44153.9583 | 0 | 10.2563 | 37.78
2020-11-18 23:30 | 44153.9792 | 0 | 9.802 | 37.78
2020-11-19 | 44154 | 0 | 9.3167 | 37.78
2020-11-19 00:30 | 44154.0208 | 0 | 8.9896 | 37.78
2020-11-19 01:00 | 44154.0417 | 0 | 8.684 | 37.78
2020-11-19 01:30 | 44154.0625 | 0 | 8.4532 | 37.78
2020-11-19 02:00 | 44154.0833 | 0 | 8.4966 | 37.78
2020-11-19 02:30 | 44154.1042 | 0 | 8.3991 | 37.78
2020-11-19 03:00 | 44154.125 | 0 | 8.2847 | 37.78
2020-11-19 03:30 | 44154.1458 | 0 | 8.3544 | 37.78
2020-11-19 04:00 | 44154.1667 | 0 | 8.5243 | 37.78
2020-11-19 04:30 | 44154.1875 | 0 | 8.8722 | 37.78
2020-11-19 05:00 | 44154.2083 | 0 | 9.3913 | 37.78
2020-11-19 05:30 | 44154.2292 | 0 | 9.4244 | 37.78
2020-11-19 06:00 | 44154.25 | 0 | 9.8696 | 37.78
2020-11-19 06:30 | 44154.2708 | 0 | 10.3425 | 37.78
2020-11-19 07:00 | 44154.2917 | 0 | 10.7955 | 37.78
2020-11-19 07:30 | 44154.3125 | 0 | 10.8909 | 37.78
2020-11-19 08:00 | 44154.3333 | 0 | 11.122 | 37.78
2020-11-19 08:30 | 44154.3542 | 0 | 11.0457 | 37.78
2020-11-19 09:00 | 44154.375 | 0 | 11.1792 | 37.78
2020-11-19 09:30 | 44154.3958 | 0 | 10.9322 | 37.78
2020-11-19 10:00 | 44154.4167 | 0 | 11.1129 | 37.78
2020-11-19 10:30 | 44154.4375 | 0 | 11.0621 | 37.78
2020-11-19 11:00 | 44154.4583 | 0 | 10.9843 | 37.78
2020-11-19 11:30 | 44154.4792 | 0 | 11.1514 | 37.78
2020-11-19 12:00 | 44154.5 | 0 | 11.3167 | 37.78
2020-11-19 12:30 | 44154.5208 | 0 | 11.4567 | 37.78
2020-11-19 13:00 | 44154.5417 | 0 | 11.9077 | 37.78
2020-11-19 13:30 | 44154.5625 | 0 | 12.2255 | 37.78
2020-11-19 14:00 | 44154.5833 | 0 | 12.7481 | 37.78
2020-11-19 14:30 | 44154.6042 | 0 | 13.3771 | 37.78
2020-11-19 15:00 | 44154.625 | 0 | 13.5079 | 37.78
2020-11-19 15:30 | 44154.6458 | 0 | 14.158 | 37.78
2020-11-19 16:00 | 44154.6667 | 0 | 14.6064 | 37.78
2020-11-19 16:30 | 44154.6875 | 0 | 15.0863 | 37.78
2020-11-19 17:00 | 44154.7083 | 0 | 15.0244 | 37.78
2020-11-19 17:30 | 44154.7292 | 0 | 14.7219 | 37.78
2020-11-19 18:00 | 44154.75 | 0 | 14.2648 | 37.78
2020-11-19 18:30 | 44154.7708 | 0 | 14.5805 | 37.78
2020-11-19 19:00 | 44154.7917 | 0 | 14.479 | 37.78
2020-11-19 19:30 | 44154.8125 | 0 | 14.3186 | 37.78
2020-11-19 20:00 | 44154.8333 | 0 | 13.9382 | 37.78
2020-11-19 20:30 | 44154.8542 | 0 | 13.3684 | 37.78
2020-11-19 21:00 | 44154.875 | 0 | 12.961 | 37.78
2020-11-19 21:30 | 44154.8958 | 0 | 12.3421 | 37.78
2020-11-19 22:00 | 44154.9167 | 0 | 11.9553 | 37.78
2020-11-19 22:30 | 44154.9375 | 0 | 11.0616 | 37.78
2020-11-19 23:00 | 44154.9583 | 0 | 10.6039 | 37.78
2020-11-19 23:30 | 44154.9792 | 0 | 10.0266 | 37.78
2020-11-20 | 44155 | 0 | 9.4761 | 37.78
2020-11-20 00:30 | 44155.0208 | 0 | 9.0908 | 37.78
2020-11-20 01:00 | 44155.0417 | 0 | 8.8079 | 37.78
2020-11-20 01:30 | 44155.0625 | 0 | 8.6028 | 37.78
2020-11-20 02:00 | 44155.0833 | 0 | 8.4803 | 37.78
2020-11-20 02:30 | 44155.1042 | 0 | 8.3531 | 37.78
2020-11-20 03:00 | 44155.125 | 0 | 8.303 | 37.78
2020-11-20 03:30 | 44155.1458 | 0 | 8.3125 | 37.78
2020-11-20 04:00 | 44155.1667 | 0 | 8.3186 | 37.78
2020-11-20 04:30 | 44155.1875 | 0 | 8.328 | 37.78
2020-11-20 05:00 | 44155.2083 | 0 | 8.3409 | 37.78
2020-11-20 05:30 | 44155.2292 | 0 | 8.3298 | 37.78
2020-11-20 06:00 | 44155.25 | 0 | 8.165 | 37.78
2020-11-20 06:30 | 44155.2708 | 0 | 8.0885 | 37.78
2020-11-20 07:00 | 44155.2917 | 0 | 8.077 | 37.78
2020-11-20 07:30 | 44155.3125 | 0 | 8.2232 | 37.78
2020-11-20 08:00 | 44155.3333 | 0 | 8.7763 | 37.78
2020-11-20 08:30 | 44155.3542 | 0 | 9.0623 | 37.78
2020-11-20 09:00 | 44155.375 | 0 | 9.4894 | 37.78
2020-11-20 09:30 | 44155.3958 | 0 | 9.3851 | 37.78
2020-11-20 10:00 | 44155.4167 | 0 | 9.3357 | 37.78
2020-11-20 10:30 | 44155.4375 | 0 | 9.3831 | 37.78
2020-11-20 11:00 | 44155.4583 | 0 | 9.4102 | 37.78
2020-11-20 11:30 | 44155.4792 | 0 | 9.5787 | 37.78
2020-11-20 12:00 | 44155.5 | 0 | 9.7025 | 37.78
2020-11-20 12:30 | 44155.5208 | 0 | 9.7351 | 37.78
2020-11-20 13:00 | 44155.5417 | 0 | 10.2426 | 37.78
2020-11-20 13:30 | 44155.5625 | 0 | 10.5274 | 37.78
2020-11-20 14:00 | 44155.5833 | 0 | 10.9092 | 37.78
2020-11-20 14:30 | 44155.6042 | 0 | 11.538 | 37.78
2020-11-20 15:00 | 44155.625 | 0 | 12.0325 | 37.78
2020-11-20 15:30 | 44155.6458 | 0 | 12.0218 | 37.78
2020-11-20 16:00 | 44155.6667 | 0 | 12.8642 | 37.78
2020-11-20 16:30 | 44155.6875 | 0 | 13.2933 | 37.78
2020-11-20 17:00 | 44155.7083 | 0 | 13.3109 | 37.78
2020-11-20 17:30 | 44155.7292 | 0 | 13.2406 | 37.78
2020-11-20 18:00 | 44155.75 | 0 | 13.3747 | 37.78
2020-11-20 18:30 | 44155.7708 | 0 | 13.6019 | 37.78
2020-11-20 19:00 | 44155.7917 | 0 | 13.3908 | 37.78
2020-11-20 19:30 | 44155.8125 | 0 | 13.0748 | 37.78
2020-11-20 20:00 | 44155.8333 | 0 | 12.9671 | 37.78
2020-11-20 20:30 | 44155.8542 | 0 | 12.2092 | 37.78
2020-11-20 21:00 | 44155.875 | 0 | 11.7446 | 37.78
2020-11-20 21:30 | 44155.8958 | 0 | 11.4939 | 37.78
2020-11-20 22:00 | 44155.9167 | 0 | 11.1238 | 37.78
2020-11-20 22:30 | 44155.9375 | 0 | 10.4571 | 37.78
2020-11-20 23:00 | 44155.9583 | 0 | 9.8812 | 37.78
2020-11-20 23:30 | 44155.9792 | 0 | 9.4932 | 37.78
2020-11-21 | 44156 | 0 | 8.8241 | 37.78
2020-11-21 00:30 | 44156.0208 | 0 | 8.5757 | 37.78
2020-11-21 01:00 | 44156.0417 | 0 | 8.3228 | 37.78
2020-11-21 01:30 | 44156.0625 | 0 | 8.098 | 37.78
2020-11-21 02:00 | 44156.0833 | 0 | 8.0316 | 37.78
2020-11-21 02:30 | 44156.1042 | 0 | 7.8651 | 37.78
2020-11-21 03:00 | 44156.125 | 0 | 7.9084 | 37.78
2020-11-21 03:30 | 44156.1458 | 0 | 7.677 | 37.78
2020-11-21 04:00 | 44156.1667 | 0 | 7.5647 | 37.78
2020-11-21 04:30 | 44156.1875 | 0 | 7.4059 | 37.78
2020-11-21 05:00 | 44156.2083 | 0 | 7.2939 | 37.78
2020-11-21 05:30 | 44156.2292 | 0 | 7.1058 | 37.78
2020-11-21 06:00 | 44156.25 | 0 | 7.1207 | 37.78
2020-11-21 06:30 | 44156.2708 | 0 | 7.3211 | 37.78
2020-11-21 07:00 | 44156.2917 | 0 | 7.9623 | 37.78
2020-11-21 07:30 | 44156.3125 | 0 | 8.0255 | 37.78
2020-11-21 08:00 | 44156.3333 | 0 | 8.0357 | 37.78
2020-11-21 08:30 | 44156.3542 | 0 | 7.4255 | 37.78
2020-11-21 09:00 | 44156.375 | 0 | 7.3251 | 37.78
2020-11-21 09:30 | 44156.3958 | 0 | 7.5701 | 37.78
2020-11-21 10:00 | 44156.4167 | 0 | 7.7643 | 37.78
2020-11-21 10:30 | 44156.4375 | 0 | 7.859 | 37.78
2020-11-21 11:00 | 44156.4583 | 0 | 7.9924 | 37.78
2020-11-21 11:30 | 44156.4792 | 0 | 8.1088 | 37.78
2020-11-21 12:00 | 44156.5 | 0 | 8.0357 | 37.78
2020-11-21 12:30 | 44156.5208 | 0 | 8.3084 | 37.78
2020-11-21 13:00 | 44156.5417 | 0 | 8.5751 | 37.78
2020-11-21 13:30 | 44156.5625 | 0 | 8.9493 | 37.78
2020-11-21 14:00 | 44156.5833 | 0 | 9.5372 | 37.78
2020-11-21 14:30 | 44156.6042 | 0 | 10.3371 | 37.78
2020-11-21 15:00 | 44156.625 | 0 | 11.0321 | 37.78
2020-11-21 15:30 | 44156.6458 | 0 | 11.8844 | 37.78
2020-11-21 16:00 | 44156.6667 | 0 | 12.8603 | 37.78
2020-11-21 16:30 | 44156.6875 | 0 | 13.4828 | 37.78
2020-11-21 17:00 | 44156.7083 | 0 | 13.2101 | 37.78
2020-11-21 17:30 | 44156.7292 | 0 | 13.5498 | 37.78
2020-11-21 18:00 | 44156.75 | 0 | 13.7461 | 37.78
2020-11-21 18:30 | 44156.7708 | 0 | 14.2278 | 37.78
2020-11-21 19:00 | 44156.7917 | 0 | 14.2645 | 37.78
2020-11-21 19:30 | 44156.8125 | 0 | 13.7129 | 37.78
2020-11-21 20:00 | 44156.8333 | 0 | 13.3082 | 37.78
2020-11-21 20:30 | 44156.8542 | 0 | 12.6551 | 37.78
2020-11-21 21:00 | 44156.875 | 0 | 11.931 | 37.78
2020-11-21 21:30 | 44156.8958 | 0 | 11.5261 | 37.78
2020-11-21 22:00 | 44156.9167 | 0 | 10.9199 | 37.78
2020-11-21 22:30 | 44156.9375 | 0 | 10.0471 | 37.78
2020-11-21 23:00 | 44156.9583 | 0 | 9.405 | 37.78
2020-11-21 23:30 | 44156.9792 | 0 | 9.0016 | 37.78
2020-11-22 | 44157 | 0 | 8.6381 | 37.78
2020-11-22 00:30 | 44157.0208 | 0 | 8.305 | 37.78
2020-11-22 01:00 | 44157.0417 | 0 | 8.2793 | 37.78
2020-11-22 01:30 | 44157.0625 | 0 | 8.1614 | 37.78
2020-11-22 02:00 | 44157.0833 | 0 | 8.0397 | 37.78
2020-11-22 02:30 | 44157.1042 | 0 | 8.0797 | 37.78
2020-11-22 03:00 | 44157.125 | 0 | 8.0404 | 37.78
2020-11-22 03:30 | 44157.1458 | 0 | 8.1149 | 37.78
2020-11-22 04:00 | 44157.1667 | 0 | 8.2868 | 37.78
2020-11-22 04:30 | 44157.1875 | 0 | 8.5418 | 37.78
2020-11-22 05:00 | 44157.2083 | 0 | 8.9473 | 37.78
2020-11-22 05:30 | 44157.2292 | 0 | 9.4076 | 37.78
2020-11-22 06:00 | 44157.25 | 0 | 10.109 | 37.78
2020-11-22 06:30 | 44157.2708 | 0 | 10.8094 | 37.78
2020-11-22 07:00 | 44157.2917 | 0 | 11.3859 | 37.78
2020-11-22 07:30 | 44157.3125 | 0 | 11.3592 | 37.78
2020-11-22 08:00 | 44157.3333 | 0 | 11.6617 | 37.78
2020-11-22 08:30 | 44157.3542 | 0 | 11.6834 | 37.78
2020-11-22 09:00 | 44157.375 | 0 | 11.6488 | 37.78
2020-11-22 09:30 | 44157.3958 | 0 | 11.7903 | 37.78
2020-11-22 10:00 | 44157.4167 | 0 | 12.0524 | 37.78
2020-11-22 10:30 | 44157.4375 | 0 | 12.3107 | 37.78
2020-11-22 11:00 | 44157.4583 | 0 | 12.8284 | 37.78
2020-11-22 11:30 | 44157.4792 | 0 | 13.0213 | 37.78
2020-11-22 12:00 | 44157.5 | 0 | 13.4838 | 37.78
2020-11-22 12:30 | 44157.5208 | 0 | 13.5455 | 37.78
2020-11-22 13:00 | 44157.5417 | 0 | 14.0297 | 37.78
2020-11-22 13:30 | 44157.5625 | 0 | 14.4504 | 37.78
2020-11-22 14:00 | 44157.5833 | 0 | 15.1247 | 37.78
2020-11-22 14:30 | 44157.6042 | 0 | 15.4168 | 37.78
2020-11-22 15:00 | 44157.625 | 0 | 15.5165 | 37.78
2020-11-22 15:30 | 44157.6458 | 0 | 16.173 | 37.78
2020-11-22 16:00 | 44157.6667 | 0 | 16.7126 | 37.78
2020-11-22 16:30 | 44157.6875 | 0 | 17.1752 | 37.78
2020-11-22 17:00 | 44157.7083 | 0 | 17.2158 | 37.78
2020-11-22 17:30 | 44157.7292 | 0 | 17.4202 | 37.78
2020-11-22 18:00 | 44157.75 | 0 | 17.2591 | 37.78
2020-11-22 18:30 | 44157.7708 | 0 | 17.6594 | 37.78
2020-11-22 19:00 | 44157.7917 | 0 | 17.6036 | 37.78
2020-11-22 19:30 | 44157.8125 | 0 | 17.0176 | 37.78
2020-11-22 20:00 | 44157.8333 | 0 | 16.2687 | 37.78
2020-11-22 20:30 | 44157.8542 | 0 | 15.5607 | 37.78
2020-11-22 21:00 | 44157.875 | 0 | 14.8575 | 37.78
2020-11-22 21:30 | 44157.8958 | 0 | 14.3147 | 37.78
2020-11-22 22:00 | 44157.9167 | 0 | 13.4891 | 37.78
2020-11-22 22:30 | 44157.9375 | 0 | 12.6247 | 37.78
2020-11-22 23:00 | 44157.9583 | 0 | 11.7639 | 37.78
2020-11-22 23:30 | 44157.9792 | 0 | 11.082 | 37.78
2020-11-23 | 44158 | 0 | 10.4285 | 37.78
2020-11-23 00:30 | 44158.0208 | 0 | 9.9414 | 37.78
2020-11-23 01:00 | 44158.0417 | 0 | 9.6609 | 37.78
2020-11-23 01:30 | 44158.0625 | 0 | 9.3174 | 37.78
2020-11-23 02:00 | 44158.0833 | 0 | 9.3202 | 37.78
2020-11-23 02:30 | 44158.1042 | 0 | 9.2416 | 37.78
2020-11-23 03:00 | 44158.125 | 0 | 9.0434 | 37.78
2020-11-23 03:30 | 44158.1458 | 0 | 9.0698 | 37.78
2020-11-23 04:00 | 44158.1667 | 0 | 9.4332 | 37.78
2020-11-23 04:30 | 44158.1875 | 0 | 9.9042 | 37.78
2020-11-23 05:00 | 44158.2083 | 0 | 10.1708 | 37.78
2020-11-23 05:30 | 44158.2292 | 0 | 10.5331 | 37.78
2020-11-23 06:00 | 44158.25 | 0 | 11.121 | 37.78
2020-11-23 06:30 | 44158.2708 | 0 | 11.6188 | 37.78
2020-11-23 07:00 | 44158.2917 | 0 | 12.4826 | 37.78
2020-11-23 07:30 | 44158.3125 | 0 | 12.1992 | 37.78
2020-11-23 08:00 | 44158.3333 | 0 | 12.2296 | 37.78
2020-11-23 08:30 | 44158.3542 | 0 | 12.7679 | 37.78
2020-11-23 09:00 | 44158.375 | 0 | 13.1324 | 37.78
2020-11-23 09:30 | 44158.3958 | 0 | 13.3031 | 37.78
2020-11-23 10:00 | 44158.4167 | 0 | 13.8165 | 37.78
2020-11-23 10:30 | 44158.4375 | 0 | 14.2308 | 37.78
2020-11-23 11:00 | 44158.4583 | 0 | 14.3179 | 37.78
2020-11-23 11:30 | 44158.4792 | 0 | 14.5128 | 37.78
2020-11-23 12:00 | 44158.5 | 0 | 15.1533 | 37.78
2020-11-23 12:30 | 44158.5208 | 0 | 15.5025 | 37.78
2020-11-23 13:00 | 44158.5417 | 0 | 15.5015 | 37.78
2020-11-23 13:30 | 44158.5625 | 0 | 16.0904 | 37.78
2020-11-23 14:00 | 44158.5833 | 0 | 16.9188 | 37.78
2020-11-23 14:30 | 44158.6042 | 0 | 17.3771 | 37.78
2020-11-23 15:00 | 44158.625 | 0 | 17.161 | 37.78
2020-11-23 15:30 | 44158.6458 | 0 | 17.5947 | 37.78
2020-11-23 16:00 | 44158.6667 | 0 | 17.2541 | 37.78
2020-11-23 16:30 | 44158.6875 | 0 | 17.1758 | 37.78
2020-11-23 17:00 | 44158.7083 | 0 | 16.6807 | 37.78
2020-11-23 17:30 | 44158.7292 | 0 | 16.2494 | 37.78
2020-11-23 18:00 | 44158.75 | 0 | 16.1313 | 37.78
2020-11-23 18:30 | 44158.7708 | 0 | 16.4483 | 37.78
2020-11-23 19:00 | 44158.7917 | 0 | 16.0374 | 37.78
2020-11-23 19:30 | 44158.8125 | 0 | 15.7256 | 37.78
2020-11-23 20:00 | 44158.8333 | 0 | 15.5997 | 37.78
2020-11-23 20:30 | 44158.8542 | 0 | 15.0482 | 37.78
2020-11-23 21:00 | 44158.875 | 0 | 14.1955 | 37.78
2020-11-23 21:30 | 44158.8958 | 0 | 13.6046 | 37.78
2020-11-23 22:00 | 44158.9167 | 0 | 12.8369 | 37.78
2020-11-23 22:30 | 44158.9375 | 0 | 11.9266 | 37.78
2020-11-23 23:00 | 44158.9583 | 0 | 11.4316 | 37.78
2020-11-23 23:30 | 44158.9792 | 0 | 10.8012 | 37.78
2020-11-24 | 44159 | 0 | 10.2108 | 37.78
2020-11-24 00:30 | 44159.0208 | 0 | 9.723 | 37.78
2020-11-24 01:00 | 44159.0417 | 0 | 9.5651 | 37.78
2020-11-24 01:30 | 44159.0625 | 0 | 9.377 | 37.78
2020-11-24 02:00 | 44159.0833 | 0 | 9.3831 | 37.78
2020-11-24 02:30 | 44159.1042 | 0 | 9.1956 | 37.78
2020-11-24 03:00 | 44159.125 | 0 | 9.1002 | 37.78
2020-11-24 03:30 | 44159.1458 | 0 | 9.1361 | 37.78
2020-11-24 04:00 | 44159.1667 | 0 | 9.3019 | 37.78
2020-11-24 04:30 | 44159.1875 | 0 | 9.8765 | 37.78
2020-11-24 05:00 | 44159.2083 | 0 | 10.294 | 37.78
2020-11-24 05:30 | 44159.2292 | 0 | 10.5934 | 37.78
2020-11-24 06:00 | 44159.25 | 0 | 11.5823 | 37.78
2020-11-24 06:30 | 44159.2708 | 0 | 12.396 | 37.78
2020-11-24 07:00 | 44159.2917 | 0 | 12.9791 | 37.78
2020-11-24 07:30 | 44159.3125 | 0 | 13.5756 | 37.78
2020-11-24 08:00 | 44159.3333 | 0 | 13.6778 | 37.78
2020-11-24 08:30 | 44159.3542 | 0 | 13.7731 | 37.78
2020-11-24 09:00 | 44159.375 | 0 | 14.3362 | 37.78
2020-11-24 09:30 | 44159.3958 | 0 | 14.1643 | 37.78
2020-11-24 10:00 | 44159.4167 | 0 | 13.9346 | 37.78
2020-11-24 10:30 | 44159.4375 | 0 | 13.8821 | 37.78
2020-11-24 11:00 | 44159.4583 | 0 | 12.8494 | 37.78
2020-11-24 11:30 | 44159.4792 | 0 | 13.167 | 37.78
2020-11-24 12:00 | 44159.5 | 0 | 13.1648 | 37.78
2020-11-24 12:30 | 44159.5208 | 0 | 13.0766 | 37.78
2020-11-24 13:00 | 44159.5417 | 0 | 12.6897 | 37.78
2020-11-24 13:30 | 44159.5625 | 0 | 12.5019 | 37.78
2020-11-24 14:00 | 44159.5833 | 0 | 13.4667 | 37.78
2020-11-24 14:30 | 44159.6042 | 0 | 13.0157 | 37.78
2020-11-24 15:00 | 44159.625 | 0 | 14.14 | 37.78
2020-11-24 15:30 | 44159.6458 | 0 | 13.631 | 37.78
2020-11-24 16:00 | 44159.6667 | 0 | 13.4409 | 37.78
2020-11-24 16:30 | 44159.6875 | 0 | 13.6351 | 37.78
2020-11-24 17:00 | 44159.7083 | 0 | 13.9985 | 37.78
2020-11-24 17:30 | 44159.7292 | 0 | 14.0378 | 37.78
2020-11-24 18:00 | 44159.75 | 0 | 14.2712 | 37.78
2020-11-24 18:30 | 44159.7708 | 0 | 14.7011 | 37.78
2020-11-24 19:00 | 44159.7917 | 0 | 14.6895 | 37.78
2020-11-24 19:30 | 44159.8125 | 0 | 14.5758 | 37.78
2020-11-24 20:00 | 44159.8333 | 0 | 14.4614 | 37.78
2020-11-24 20:30 | 44159.8542 | 0 | 13.7801 | 37.78
2020-11-24 21:00 | 44159.875 | 0 | 13.277 | 37.78
2020-11-24 21:30 | 44159.8958 | 0 | 12.7573 | 37.78
2020-11-24 22:00 | 44159.9167 | 0 | 12.2169 | 37.78
2020-11-24 22:30 | 44159.9375 | 0 | 11.0315 | 37.78
2020-11-24 23:00 | 44159.9583 | 0 | 10.4378 | 37.78
2020-11-24 23:30 | 44159.9792 | 0 | 9.8715 | 37.78
2020-11-25 | 44160 | 0 | 9.4216 | 37.78
2020-11-25 00:30 | 44160.0208 | 0 | 8.998 | 37.78
2020-11-25 01:00 | 44160.0417 | 0 | 8.7199 | 37.78
2020-11-25 01:30 | 44160.0625 | 0 | 8.5954 | 37.78
2020-11-25 02:00 | 44160.0833 | 0 | 8.546 | 37.78
2020-11-25 02:30 | 44160.1042 | 0 | 8.4708 | 37.78
2020-11-25 03:00 | 44160.125 | 0 | 8.5358 | 37.78
2020-11-25 03:30 | 44160.1458 | 0 | 8.5196 | 37.78
2020-11-25 04:00 | 44160.1667 | 0 | 8.8268 | 37.78
2020-11-25 04:30 | 44160.1875 | 0 | 9.0353 | 37.78
2020-11-25 05:00 | 44160.2083 | 0 | 9.375 | 37.78
2020-11-25 05:30 | 44160.2292 | 0 | 9.7325 | 37.78
2020-11-25 06:00 | 44160.25 | 0 | 10.4301 | 37.78
2020-11-25 06:30 | 44160.2708 | 0 | 10.9584 | 37.78
2020-11-25 07:00 | 44160.2917 | 0 | 11.4364 | 37.78
2020-11-25 07:30 | 44160.3125 | 0 | 12.671 | 37.78
2020-11-25 08:00 | 44160.3333 | 0 | 12.4752 | 37.78
2020-11-25 08:30 | 44160.3542 | 0 | 11.8093 | 37.78
2020-11-25 09:00 | 44160.375 | 0 | 12.0962 | 37.78
2020-11-25 09:30 | 44160.3958 | 0 | 12.1541 | 37.78
2020-11-25 10:00 | 44160.4167 | 0 | 12.3262 | 37.78
2020-11-25 10:30 | 44160.4375 | 0 | 12.2309 | 37.78
2020-11-25 11:00 | 44160.4583 | 0 | 12.4109 | 37.78
2020-11-25 11:30 | 44160.4792 | 0 | 12.4406 | 37.78
2020-11-25 12:00 | 44160.5 | 0 | 12.645 | 37.78
2020-11-25 12:30 | 44160.5208 | 0 | 12.798 | 37.78
2020-11-25 13:00 | 44160.5417 | 0 | 13.1892 | 37.78
2020-11-25 13:30 | 44160.5625 | 0 | 13.7404 | 37.78
2020-11-25 14:00 | 44160.5833 | 0 | 13.943 | 37.78
2020-11-25 14:30 | 44160.6042 | 0 | 14.2 | 37.78
2020-11-25 15:00 | 44160.625 | 0 | 14.5514 | 37.78
2020-11-25 15:30 | 44160.6458 | 0 | 15.2097 | 37.78
2020-11-25 16:00 | 44160.6667 | 0 | 15.8842 | 37.78
2020-11-25 16:30 | 44160.6875 | 0 | 16.1621 | 37.78
2020-11-25 17:00 | 44160.7083 | 0 | 16.0003 | 37.78
2020-11-25 17:30 | 44160.7292 | 0 | 15.9415 | 37.78
2020-11-25 18:00 | 44160.75 | 0 | 15.7465 | 37.78
2020-11-25 18:30 | 44160.7708 | 0 | 16.0464 | 37.78
2020-11-25 19:00 | 44160.7917 | 0 | 15.9929 | 37.78
2020-11-25 19:30 | 44160.8125 | 0 | 15.7066 | 37.78
2020-11-25 20:00 | 44160.8333 | 0 | 15.4735 | 37.78
2020-11-25 20:30 | 44160.8542 | 0 | 14.9141 | 37.78
2020-11-25 21:00 | 44160.875 | 0 | 14.2743 | 37.78
2020-11-25 21:30 | 44160.8958 | 0 | 13.8076 | 37.78
2020-11-25 22:00 | 44160.9167 | 0 | 13.0182 | 37.78
2020-11-25 22:30 | 44160.9375 | 0 | 12.0386 | 37.78
2020-11-25 23:00 | 44160.9583 | 0 | 11.3402 | 37.78
2020-11-25 23:30 | 44160.9792 | 0 | 10.7036 | 37.78
2020-11-26 | 44161 | 0 | 10.088 | 37.78
2020-11-26 00:30 | 44161.0208 | 0 | 9.5609 | 37.78
2020-11-26 01:00 | 44161.0417 | 0 | 9.3438 | 37.78
2020-11-26 01:30 | 44161.0625 | 0 | 9.1902 | 37.78
2020-11-26 02:00 | 44161.0833 | 0 | 9.1137 | 37.78
2020-11-26 02:30 | 44161.1042 | 0 | 8.994 | 37.78
2020-11-26 03:00 | 44161.125 | 0 | 8.887 | 37.78
2020-11-26 03:30 | 44161.1458 | 0 | 9.0711 | 37.78
2020-11-26 04:00 | 44161.1667 | 0 | 9.2247 | 37.78
2020-11-26 04:30 | 44161.1875 | 0 | 9.7055 | 37.78
2020-11-26 05:00 | 44161.2083 | 0 | 9.9895 | 37.78
2020-11-26 05:30 | 44161.2292 | 0 | 10.3259 | 37.78
2020-11-26 06:00 | 44161.25 | 0 | 11.0772 | 37.78
2020-11-26 06:30 | 44161.2708 | 0 | 11.7736 | 37.78
2020-11-26 07:00 | 44161.2917 | 0 | 12.427 | 37.78
2020-11-26 07:30 | 44161.3125 | 0 | 13.0107 | 37.78
2020-11-26 08:00 | 44161.3333 | 0 | 13.1027 | 37.78
2020-11-26 08:30 | 44161.3542 | 0 | 13.3661 | 37.78
2020-11-26 09:00 | 44161.375 | 0 | 14.0623 | 37.78
2020-11-26 09:30 | 44161.3958 | 0 | 13.582 | 37.78
2020-11-26 10:00 | 44161.4167 | 0 | 13.8449 | 37.78
2020-11-26 10:30 | 44161.4375 | 0 | 13.9346 | 37.78
2020-11-26 11:00 | 44161.4583 | 0 | 12.6186 | 37.78
2020-11-26 11:30 | 44161.4792 | 0 | 12.5665 | 37.78
2020-11-26 12:00 | 44161.5 | 0 | 12.6902 | 37.78
2020-11-26 12:30 | 44161.5208 | 0 | 13.1553 | 37.78
2020-11-26 13:00 | 44161.5417 | 0 | 13.0572 | 37.78
2020-11-26 13:30 | 44161.5625 | 0 | 13.2825 | 37.78
2020-11-26 14:00 | 44161.5833 | 0 | 13.598 | 37.78
2020-11-26 14:30 | 44161.6042 | 0 | 14.1216 | 37.78
2020-11-26 15:00 | 44161.625 | 0 | 14.2632 | 37.78
2020-11-26 15:30 | 44161.6458 | 0 | 14.7687 | 37.78
2020-11-26 16:00 | 44161.6667 | 0 | 15.2292 | 37.78
2020-11-26 16:30 | 44161.6875 | 0 | 15.4644 | 37.78
2020-11-26 17:00 | 44161.7083 | 0 | 15.419 | 37.78
2020-11-26 17:30 | 44161.7292 | 0 | 15.2979 | 37.78
2020-11-26 18:00 | 44161.75 | 0 | 14.9446 | 37.78
2020-11-26 18:30 | 44161.7708 | 0 | 15.0712 | 37.78
2020-11-26 19:00 | 44161.7917 | 0 | 14.9304 | 37.78
2020-11-26 19:30 | 44161.8125 | 0 | 14.7333 | 37.78
2020-11-26 20:00 | 44161.8333 | 0 | 14.5607 | 37.78
2020-11-26 20:30 | 44161.8542 | 0 | 13.9681 | 37.78
2020-11-26 21:00 | 44161.875 | 0 | 13.2136 | 37.78
2020-11-26 21:30 | 44161.8958 | 0 | 12.9597 | 37.78
2020-11-26 22:00 | 44161.9167 | 0 | 12.3678 | 37.78
2020-11-26 22:30 | 44161.9375 | 0 | 11.3517 | 37.78
2020-11-26 23:00 | 44161.9583 | 0 | 10.7967 | 37.78
2020-11-26 23:30 | 44161.9792 | 0 | 10.3657 | 37.78
2020-11-27 | 44162 | 0 | 9.6081 | 37.78
2020-11-27 00:30 | 44162.0208 | 0 | 9.2382 | 37.78
2020-11-27 01:00 | 44162.0417 | 0 | 9.0325 | 37.78
2020-11-27 01:30 | 44162.0625 | 0 | 8.7896 | 37.78
2020-11-27 02:00 | 44162.0833 | 0 | 8.5981 | 37.78
2020-11-27 02:30 | 44162.1042 | 0 | 8.4817 | 37.78
2020-11-27 03:00 | 44162.125 | 0 | 8.367 | 37.78
2020-11-27 03:30 | 44162.1458 | 0 | 8.3172 | 37.78
2020-11-27 04:00 | 44162.1667 | 0 | 8.2766 | 37.78
2020-11-27 04:30 | 44162.1875 | 0 | 8.3748 | 37.78
2020-11-27 05:00 | 44162.2083 | 0 | 8.4384 | 37.78
2020-11-27 05:30 | 44162.2292 | 0 | 8.3747 | 37.78
2020-11-27 06:00 | 44162.25 | 0 | 8.3774 | 37.78
2020-11-27 06:30 | 44162.2708 | 0 | 8.4688 | 37.78
2020-11-27 07:00 | 44162.2917 | 0 | 8.8483 | 37.78
2020-11-27 07:30 | 44162.3125 | 0 | 8.9953 | 37.78
2020-11-27 08:00 | 44162.3333 | 0 | 8.8735 | 37.78
2020-11-27 08:30 | 44162.3542 | 0 | 8.9501 | 37.78
2020-11-27 09:00 | 44162.375 | 0 | 9.0278 | 37.78
2020-11-27 09:30 | 44162.3958 | 0 | 8.8918 | 37.78
2020-11-27 10:00 | 44162.4167 | 0 | 8.9473 | 37.78
2020-11-27 10:30 | 44162.4375 | 0 | 8.9838 | 37.78
2020-11-27 11:00 | 44162.4583 | 0 | 8.8552 | 37.78
2020-11-27 11:30 | 44162.4792 | 0 | 8.9567 | 37.78
2020-11-27 12:00 | 44162.5 | 0 | 9.1097 | 37.78
2020-11-27 12:30 | 44162.5208 | 0 | 9.5709 | 37.78
2020-11-27 13:00 | 44162.5417 | 0 | 9.9864 | 37.78
2020-11-27 13:30 | 44162.5625 | 0 | 10.4348 | 37.78
2020-11-27 14:00 | 44162.5833 | 0 | 10.7538 | 37.78
2020-11-27 14:30 | 44162.6042 | 0 | 11.3348 | 37.78
2020-11-27 15:00 | 44162.625 | 0 | 11.7794 | 37.78
2020-11-27 15:30 | 44162.6458 | 0 | 12.3002 | 37.78
2020-11-27 16:00 | 44162.6667 | 0 | 12.5794 | 37.78
2020-11-27 16:30 | 44162.6875 | 0 | 13.2045 | 37.78
2020-11-27 17:00 | 44162.7083 | 0 | 13.2568 | 37.78
2020-11-27 17:30 | 44162.7292 | 0 | 13.271 | 37.78
2020-11-27 18:00 | 44162.75 | 0 | 13.0923 | 37.78
2020-11-27 18:30 | 44162.7708 | 0 | 13.3428 | 37.78
2020-11-27 19:00 | 44162.7917 | 0 | 13.3245 | 37.78
2020-11-27 19:30 | 44162.8125 | 0 | 13.0687 | 37.78
2020-11-27 20:00 | 44162.8333 | 0 | 12.748 | 37.78
2020-11-27 20:30 | 44162.8542 | 0 | 12.2572 | 37.78
2020-11-27 21:00 | 44162.875 | 0 | 11.8498 | 37.78
2020-11-27 21:30 | 44162.8958 | 0 | 11.615 | 37.78
2020-11-27 22:00 | 44162.9167 | 0 | 11.2747 | 37.78
2020-11-27 22:30 | 44162.9375 | 0 | 10.4887 | 37.78
2020-11-27 23:00 | 44162.9583 | 0 | 9.8797 | 37.78
2020-11-27 23:30 | 44162.9792 | 0 | 9.3508 | 37.78
2020-11-28 | 44163 | 0 | 8.8877 | 37.78
2020-11-28 00:30 | 44163.0208 | 0 | 8.4383 | 37.78
2020-11-28 01:00 | 44163.0417 | 0 | 8.3104 | 37.78
2020-11-28 01:30 | 44163.0625 | 0 | 8.1494 | 37.78
2020-11-28 02:00 | 44163.0833 | 0 | 8.1494 | 37.78
2020-11-28 02:30 | 44163.1042 | 0 | 7.9599 | 37.78
2020-11-28 03:00 | 44163.125 | 0 | 7.9238 | 37.78
2020-11-28 03:30 | 44163.1458 | 0 | 7.7562 | 37.78
2020-11-28 04:00 | 44163.1667 | 0 | 7.6114 | 37.78
2020-11-28 04:30 | 44163.1875 | 0 | 7.5254 | 37.78
2020-11-28 05:00 | 44163.2083 | 0 | 7.4544 | 37.78
2020-11-28 05:30 | 44163.2292 | 0 | 7.3853 | 37.78
2020-11-28 06:00 | 44163.25 | 0 | 7.3007 | 37.78
2020-11-28 06:30 | 44163.2708 | 0 | 7.298 | 37.78
2020-11-28 07:00 | 44163.2917 | 0 | 7.2215 | 37.78
2020-11-28 07:30 | 44163.3125 | 0 | 7.3407 | 37.78
2020-11-28 08:00 | 44163.3333 | 0 | 7.4077 | 37.78
2020-11-28 08:30 | 44163.3542 | 0 | 7.6317 | 37.78
2020-11-28 09:00 | 44163.375 | 0 | 7.9455 | 37.78
2020-11-28 09:30 | 44163.3958 | 0 | 8.3768 | 37.78
2020-11-28 10:00 | 44163.4167 | 0 | 8.5473 | 37.78
2020-11-28 10:30 | 44163.4375 | 0 | 8.802 | 37.78
2020-11-28 11:00 | 44163.4583 | 0 | 9.0062 | 37.78
2020-11-28 11:30 | 44163.4792 | 0 | 9.471 | 37.78
2020-11-28 12:00 | 44163.5 | 0 | 9.8379 | 37.78
2020-11-28 12:30 | 44163.5208 | 0 | 10.032 | 37.78
2020-11-28 13:00 | 44163.5417 | 0 | 10.7488 | 37.78
2020-11-28 13:30 | 44163.5625 | 0 | 11.3921 | 37.78
2020-11-28 14:00 | 44163.5833 | 0 | 11.6944 | 37.78
2020-11-28 14:30 | 44163.6042 | 0 | 12.2368 | 37.78
2020-11-28 15:00 | 44163.625 | 0 | 12.7378 | 37.78
2020-11-28 15:30 | 44163.6458 | 0 | 13.2849 | 37.78
2020-11-28 16:00 | 44163.6667 | 0 | 13.9269 | 37.78
2020-11-28 16:30 | 44163.6875 | 0 | 14.7743 | 37.78
2020-11-28 17:00 | 44163.7083 | 0 | 14.7808 | 37.78
2020-11-28 17:30 | 44163.7292 | 0 | 14.8796 | 37.78
2020-11-28 18:00 | 44163.75 | 0 | 14.9026 | 37.78
2020-11-28 18:30 | 44163.7708 | 0 | 15.5142 | 37.78
2020-11-28 19:00 | 44163.7917 | 0 | 15.7425 | 37.78
2020-11-28 19:30 | 44163.8125 | 0 | 15.5408 | 37.78
2020-11-28 20:00 | 44163.8333 | 0 | 15.1564 | 37.78
2020-11-28 20:30 | 44163.8542 | 0 | 14.3122 | 37.78
2020-11-28 21:00 | 44163.875 | 0 | 13.6199 | 37.78
2020-11-28 21:30 | 44163.8958 | 0 | 12.9612 | 37.78
2020-11-28 22:00 | 44163.9167 | 0 | 12.3351 | 37.78
2020-11-28 22:30 | 44163.9375 | 0 | 11.2155 | 37.78
2020-11-28 23:00 | 44163.9583 | 0 | 10.6752 | 37.78
2020-11-28 23:30 | 44163.9792 | 0 | 10.1051 | 37.78
2020-11-29 | 44164 | 0 | 9.5949 | 37.78
2020-11-29 00:30 | 44164.0208 | 0 | 9.2891 | 37.78
2020-11-29 01:00 | 44164.0417 | 0 | 9.0285 | 37.78
2020-11-29 01:30 | 44164.0625 | 0 | 8.9906 | 37.78
2020-11-29 02:00 | 44164.0833 | 0 | 8.8403 | 37.78
2020-11-29 02:30 | 44164.1042 | 0 | 8.7889 | 37.78
2020-11-29 03:00 | 44164.125 | 0 | 8.625 | 37.78
2020-11-29 03:30 | 44164.1458 | 0 | 8.6617 | 37.78
2020-11-29 04:00 | 44164.1667 | 0 | 8.8428 | 37.78
2020-11-29 04:30 | 44164.1875 | 0 | 9.1821 | 37.78
2020-11-29 05:00 | 44164.2083 | 0 | 9.6792 | 37.78
2020-11-29 05:30 | 44164.2292 | 0 | 10.2344 | 37.78
2020-11-29 06:00 | 44164.25 | 0 | 11.111 | 37.78
2020-11-29 06:30 | 44164.2708 | 0 | 11.9622 | 37.78
2020-11-29 07:00 | 44164.2917 | 0 | 12.7107 | 37.78
2020-11-29 07:30 | 44164.3125 | 0 | 13.0975 | 37.78
2020-11-29 08:00 | 44164.3333 | 0 | 13.0681 | 37.78
2020-11-29 08:30 | 44164.3542 | 0 | 13.5418 | 37.78
2020-11-29 09:00 | 44164.375 | 0 | 14.0699 | 37.78
2020-11-29 09:30 | 44164.3958 | 0 | 14.8113 | 37.78
2020-11-29 10:00 | 44164.4167 | 0 | 14.3671 | 37.78
2020-11-29 10:30 | 44164.4375 | 0 | 14.7923 | 37.78
2020-11-29 11:00 | 44164.4583 | 0 | 14.7483 | 37.78
2020-11-29 11:30 | 44164.4792 | 0 | 15.2081 | 37.78
2020-11-29 12:00 | 44164.5 | 0 | 15.486 | 37.78
2020-11-29 12:30 | 44164.5208 | 0 | 15.7943 | 37.78
2020-11-29 13:00 | 44164.5417 | 0 | 16.6076 | 37.78
2020-11-29 13:30 | 44164.5625 | 0 | 16.5659 | 37.78
2020-11-29 14:00 | 44164.5833 | 0 | 16.7004 | 37.78
2020-11-29 14:30 | 44164.6042 | 0 | 16.76 | 37.78
2020-11-29 15:00 | 44164.625 | 0 | 16.879 | 37.78
2020-11-29 15:30 | 44164.6458 | 0 | 17.4726 | 37.78
2020-11-29 16:00 | 44164.6667 | 0 | 17.749 | 37.78
2020-11-29 16:30 | 44164.6875 | 0 | 18.0373 | 37.78
2020-11-29 17:00 | 44164.7083 | 0 | 17.8661 | 37.78
2020-11-29 17:30 | 44164.7292 | 0 | 17.4763 | 37.78
2020-11-29 18:00 | 44164.75 | 0 | 17.1372 | 37.78
2020-11-29 18:30 | 44164.7708 | 0 | 17.5054 | 37.78
2020-11-29 19:00 | 44164.7917 | 0 | 17.4005 | 37.78
2020-11-29 19:30 | 44164.8125 | 0 | 17.2293 | 37.78
2020-11-29 20:00 | 44164.8333 | 0 | 16.6883 | 37.78
2020-11-29 20:30 | 44164.8542 | 0 | 15.9004 | 37.78
2020-11-29 21:00 | 44164.875 | 0 | 15.0449 | 37.78
2020-11-29 21:30 | 44164.8958 | 0 | 14.5528 | 37.78
2020-11-29 22:00 | 44164.9167 | 0 | 13.8273 | 37.78
2020-11-29 22:30 | 44164.9375 | 0 | 12.8121 | 37.78
2020-11-29 23:00 | 44164.9583 | 0 | 12.2462 | 37.78
2020-11-29 23:30 | 44164.9792 | 0 | 11.732 | 37.78
2020-11-30 | 44165 | 0 | 10.9543 | 37.78
2020-11-30 00:30 | 44165.0208 | 0 | 10.441 | 37.78
2020-11-30 01:00 | 44165.0417 | 0 | 10.1309 | 37.78
2020-11-30 01:30 | 44165.0625 | 0 | 9.7834 | 37.78
2020-11-30 02:00 | 44165.0833 | 0 | 9.7655 | 37.78
2020-11-30 02:30 | 44165.1042 | 0 | 9.7106 | 37.78
2020-11-30 03:00 | 44165.125 | 0 | 9.5919 | 37.78
2020-11-30 03:30 | 44165.1458 | 0 | 9.5665 | 37.78
2020-11-30 04:00 | 44165.1667 | 0 | 9.7785 | 37.78
2020-11-30 04:30 | 44165.1875 | 0 | 10.2514 | 37.78
2020-11-30 05:00 | 44165.2083 | 0 | 10.5634 | 37.78
2020-11-30 05:30 | 44165.2292 | 0 | 11.2335 | 37.78
2020-11-30 06:00 | 44165.25 | 0 | 11.8518 | 37.78
2020-11-30 06:30 | 44165.2708 | 0 | 12.6177 | 37.78
2020-11-30 07:00 | 44165.2917 | 0 | 13.6218 | 37.78
2020-11-30 07:30 | 44165.3125 | 0 | 13.9748 | 37.78
2020-11-30 08:00 | 44165.3333 | 0 | 13.9498 | 37.78
2020-11-30 08:30 | 44165.3542 | 0 | 13.7231 | 37.78
2020-11-30 09:00 | 44165.375 | 0 | 13.9863 | 37.78
2020-11-30 09:30 | 44165.3958 | 0 | 14.5135 | 37.78
2020-11-30 10:00 | 44165.4167 | 0 | 15.0722 | 37.78
2020-11-30 10:30 | 44165.4375 | 0 | 16.182 | 37.78
2020-11-30 11:00 | 44165.4583 | 0 | 15.872 | 37.78
2020-11-30 11:30 | 44165.4792 | 0 | 15.9094 | 37.78
2020-11-30 12:00 | 44165.5 | 0 | 16.342 | 37.78
2020-11-30 12:30 | 44165.5208 | 0 | 15.9225 | 37.78
2020-11-30 13:00 | 44165.5417 | 0 | 16.5026 | 37.78
2020-11-30 13:30 | 44165.5625 | 0 | 17.23 | 37.78
2020-11-30 14:00 | 44165.5833 | 0 | 17.6846 | 37.78
2020-11-30 14:30 | 44165.6042 | 0 | 17.8106 | 37.78
2020-11-30 15:00 | 44165.625 | 0 | 18.3766 | 37.78
2020-11-30 15:30 | 44165.6458 | 0 | 19.1749 | 37.78
2020-11-30 16:00 | 44165.6667 | 0 | 19.5519 | 37.78
2020-11-30 16:30 | 44165.6875 | 0 | 19.946 | 37.78
2020-11-30 17:00 | 44165.7083 | 0 | 20.1569 | 37.78
2020-11-30 17:30 | 44165.7292 | 0 | 20.1407 | 37.78
2020-11-30 18:00 | 44165.75 | 0 | 19.9728 | 37.78
2020-11-30 18:30 | 44165.7708 | 0 | 20.0276 | 37.78
2020-11-30 19:00 | 44165.7917 | 0 | 20.0737 | 37.78
2020-11-30 19:30 | 44165.8125 | 0 | 19.8205 | 37.78
2020-11-30 20:00 | 44165.8333 | 0 | 19.2994 | 37.78
2020-11-30 20:30 | 44165.8542 | 0 | 18.6505 | 37.78
2020-11-30 21:00 | 44165.875 | 0 | 17.5845 | 37.78
2020-11-30 21:30 | 44165.8958 | 0 | 16.5488 | 37.78
2020-11-30 22:00 | 44165.9167 | 0 | 15.6693 | 37.78
2020-11-30 22:30 | 44165.9375 | 0 | 14.511 | 37.78
2020-11-30 23:00 | 44165.9583 | 0 | 13.6694 | 37.78
2020-11-30 23:30 | 44165.9792 | 0 | 12.9614 | 37.78
2020-12-01 | 44166 | 0 | 12.1351 | 37.78
2020-12-01 00:30 | 44166.0208 | 0 | 11.4878 | 37.78
2020-12-01 01:00 | 44166.0417 | 0 | 11.0458 | 37.78
2020-12-01 01:30 | 44166.0625 | 0 | 10.9282 | 37.78
2020-12-01 02:00 | 44166.0833 | 0 | 10.8279 | 37.78
2020-12-01 02:30 | 44166.1042 | 0 | 10.6242 | 37.78
2020-12-01 03:00 | 44166.125 | 0 | 10.4013 | 37.78
2020-12-01 03:30 | 44166.1458 | 0 | 10.4219 | 37.78
2020-12-01 04:00 | 44166.1667 | 0 | 10.5613 | 37.78
2020-12-01 04:30 | 44166.1875 | 0 | 10.8973 | 37.78
2020-12-01 05:00 | 44166.2083 | 0 | 11.1352 | 37.78
2020-12-01 05:30 | 44166.2292 | 0 | 11.7355 | 37.78
2020-12-01 06:00 | 44166.25 | 0 | 12.6706 | 37.78
2020-12-01 06:30 | 44166.2708 | 0 | 13.4529 | 37.78
2020-12-01 07:00 | 44166.2917 | 0 | 14.564 | 37.78
2020-12-01 07:30 | 44166.3125 | 0 | 15.2478 | 37.78
2020-12-01 08:00 | 44166.3333 | 0 | 15.8455 | 37.78
2020-12-01 08:30 | 44166.3542 | 0 | 16.3489 | 37.78
2020-12-01 09:00 | 44166.375 | 0 | 16.7515 | 37.78
2020-12-01 09:30 | 44166.3958 | 0 | 16.9802 | 37.78
2020-12-01 10:00 | 44166.4167 | 0 | 16.9396 | 37.78
2020-12-01 10:30 | 44166.4375 | 0 | 17.0331 | 37.78
2020-12-01 11:00 | 44166.4583 | 0 | 17.3119 | 37.78
2020-12-01 11:30 | 44166.4792 | 0 | 17.6214 | 37.78
2020-12-01 12:00 | 44166.5 | 0 | 18.0265 | 37.78
2020-12-01 12:30 | 44166.5208 | 0 | 18.2235 | 37.78
2020-12-01 13:00 | 44166.5417 | 0 | 18.4973 | 37.78
2020-12-01 13:30 | 44166.5625 | 0 | 18.9738 | 37.78
2020-12-01 14:00 | 44166.5833 | 0 | 18.9612 | 37.78
2020-12-01 14:30 | 44166.6042 | 0 | 19.0385 | 37.78
2020-12-01 15:00 | 44166.625 | 0 | 19.6841 | 37.78
2020-12-01 15:30 | 44166.6458 | 0 | 20.4395 | 37.78
2020-12-01 16:00 | 44166.6667 | 0 | 20.9006 | 37.78
2020-12-01 16:30 | 44166.6875 | 0 | 20.8776 | 37.78
2020-12-01 17:00 | 44166.7083 | 0 | 20.3352 | 37.78
2020-12-01 17:30 | 44166.7292 | 0 | 20.2591 | 37.78
2020-12-01 18:00 | 44166.75 | 0 | 20.163 | 37.78
2020-12-01 18:30 | 44166.7708 | 0 | 20.5318 | 37.78
2020-12-01 19:00 | 44166.7917 | 0 | 20.0653 | 37.78
2020-12-01 19:30 | 44166.8125 | 0 | 19.4711 | 37.78
2020-12-01 20:00 | 44166.8333 | 0 | 19.4272 | 37.78
2020-12-01 20:30 | 44166.8542 | 0 | 18.8924 | 37.78
2020-12-01 21:00 | 44166.875 | 0 | 17.9451 | 37.78
2020-12-01 21:30 | 44166.8958 | 0 | 17.1419 | 37.78
2020-12-01 22:00 | 44166.9167 | 0 | 15.8125 | 37.78
2020-12-01 22:30 | 44166.9375 | 0 | 14.8998 | 37.78
2020-12-01 23:00 | 44166.9583 | 0 | 14.0123 | 37.78
2020-12-01 23:30 | 44166.9792 | 0 | 13.6483 | 37.78
2020-12-02 | 44167 | 0 | 12.8758 | 37.78
2020-12-02 00:30 | 44167.0208 | 0 | 12.4631 | 37.78
2020-12-02 01:00 | 44167.0417 | 0 | 12.0456 | 37.78
2020-12-02 01:30 | 44167.0625 | 0 | 11.6901 | 37.78
2020-12-02 02:00 | 44167.0833 | 0 | 11.421 | 37.78
2020-12-02 02:30 | 44167.1042 | 0 | 11.236 | 37.78
2020-12-02 03:00 | 44167.125 | 0 | 11.1778 | 37.78
2020-12-02 03:30 | 44167.1458 | 0 | 11.1772 | 37.78
2020-12-02 04:00 | 44167.1667 | 0 | 11.41 | 37.78
2020-12-02 04:30 | 44167.1875 | 0 | 11.8082 | 37.78
2020-12-02 05:00 | 44167.2083 | 0 | 12.235 | 37.78
2020-12-02 05:30 | 44167.2292 | 0 | 12.7841 | 37.78
2020-12-02 06:00 | 44167.25 | 0 | 13.6974 | 37.78
2020-12-02 06:30 | 44167.2708 | 0 | 14.4287 | 37.78
2020-12-02 07:00 | 44167.2917 | 0 | 15.1354 | 37.78
2020-12-02 07:30 | 44167.3125 | 0 | 15.2264 | 37.78
2020-12-02 08:00 | 44167.3333 | 0 | 16.1336 | 37.78
2020-12-02 08:30 | 44167.3542 | 0 | 15.4424 | 37.78
2020-12-02 09:00 | 44167.375 | 0 | 16.0305 | 37.78
2020-12-02 09:30 | 44167.3958 | 0 | 16.358 | 37.78
2020-12-02 10:00 | 44167.4167 | 0 | 15.9395 | 37.78
2020-12-02 10:30 | 44167.4375 | 0 | 16.6878 | 37.78
2020-12-02 11:00 | 44167.4583 | 0 | 16.1831 | 37.78
2020-12-02 11:30 | 44167.4792 | 0 | 16.1022 | 37.78
2020-12-02 12:00 | 44167.5 | 0 | 15.1893 | 37.78
2020-12-02 12:30 | 44167.5208 | 0 | 15.5956 | 37.78
2020-12-02 13:00 | 44167.5417 | 0 | 16.0094 | 37.78
2020-12-02 13:30 | 44167.5625 | 0 | 16.5918 | 37.78
2020-12-02 14:00 | 44167.5833 | 0 | 17.073 | 37.78
2020-12-02 14:30 | 44167.6042 | 0 | 17.4892 | 37.78
2020-12-02 15:00 | 44167.625 | 0 | 17.833 | 37.78
2020-12-02 15:30 | 44167.6458 | 0 | 18.322 | 37.78
2020-12-02 16:00 | 44167.6667 | 0 | 18.8262 | 37.78
2020-12-02 16:30 | 44167.6875 | 0 | 19.2095 | 37.78
2020-12-02 17:00 | 44167.7083 | 0 | 19.0003 | 37.78
2020-12-02 17:30 | 44167.7292 | 0 | 18.6721 | 37.78
2020-12-02 18:00 | 44167.75 | 0 | 18.4145 | 37.78
2020-12-02 18:30 | 44167.7708 | 0 | 18.6959 | 37.78
2020-12-02 19:00 | 44167.7917 | 0 | 19.1093 | 37.78
2020-12-02 19:30 | 44167.8125 | 0 | 18.9861 | 37.78
2020-12-02 20:00 | 44167.8333 | 0 | 18.5816 | 37.78
2020-12-02 20:30 | 44167.8542 | 0 | 17.9959 | 37.78
2020-12-02 21:00 | 44167.875 | 0 | 17.0191 | 37.78
2020-12-02 21:30 | 44167.8958 | 0 | 16.3944 | 37.78
2020-12-02 22:00 | 44167.9167 | 0 | 15.2144 | 37.78
2020-12-02 22:30 | 44167.9375 | 0 | 13.9391 | 37.78
2020-12-02 23:00 | 44167.9583 | 0 | 13.392 | 37.78
2020-12-02 23:30 | 44167.9792 | 0 | 12.7903 | 37.78
2020-12-03 | 44168 | 0 | 12.0555 | 37.78
2020-12-03 00:30 | 44168.0208 | 0 | 11.4242 | 37.78
2020-12-03 01:00 | 44168.0417 | 0 | 11.2245 | 37.78
2020-12-03 01:30 | 44168.0625 | 0 | 11.0046 | 37.78
2020-12-03 02:00 | 44168.0833 | 0 | 10.8482 | 37.78
2020-12-03 02:30 | 44168.1042 | 0 | 10.6825 | 37.78
2020-12-03 03:00 | 44168.125 | 0 | 10.5525 | 37.78
2020-12-03 03:30 | 44168.1458 | 0 | 10.6202 | 37.78
2020-12-03 04:00 | 44168.1667 | 0 | 10.7393 | 37.78
2020-12-03 04:30 | 44168.1875 | 0 | 11.2004 | 37.78
2020-12-03 05:00 | 44168.2083 | 0 | 11.5433 | 37.78
2020-12-03 05:30 | 44168.2292 | 0 | 12.0874 | 37.78
2020-12-03 06:00 | 44168.25 | 0 | 12.7901 | 37.78
2020-12-03 06:30 | 44168.2708 | 0 | 13.5487 | 37.78
2020-12-03 07:00 | 44168.2917 | 0 | 13.7517 | 37.78
2020-12-03 07:30 | 44168.3125 | 0 | 14.4491 | 37.78
2020-12-03 08:00 | 44168.3333 | 0 | 14.909 | 37.78
2020-12-03 08:30 | 44168.3542 | 0 | 15.2011 | 37.78
2020-12-03 09:00 | 44168.375 | 0 | 15.3791 | 37.78
2020-12-03 09:30 | 44168.3958 | 0 | 16.4065 | 37.78
2020-12-03 10:00 | 44168.4167 | 0 | 16.6211 | 37.78
2020-12-03 10:30 | 44168.4375 | 0 | 18.8349 | 37.78
2020-12-03 11:00 | 44168.4583 | 0 | 19.1425 | 37.78
2020-12-03 11:30 | 44168.4792 | 0 | 18.44 | 37.78
2020-12-03 12:00 | 44168.5 | 0 | 18.2351 | 37.78
2020-12-03 12:30 | 44168.5208 | 0 | 7.307 | 37.78
2020-12-03 13:00 | 44168.5417 | 0 | 9.1935 | 37.78
2020-12-03 13:30 | 44168.5625 | 0 | 18.5404 | 37.78
2020-12-03 14:00 | 44168.5833 | 0 | 18.5971 | 37.78
2020-12-03 14:30 | 44168.6042 | 0 | 19.3555 | 37.78
2020-12-03 15:00 | 44168.625 | 0 | 19.5649 | 37.78
2020-12-03 15:30 | 44168.6458 | 0 | 20.0487 | 37.78
2020-12-03 16:00 | 44168.6667 | 0 | 20.4328 | 37.78
2020-12-03 16:30 | 44168.6875 | 0 | 20.7227 | 37.78
2020-12-03 17:00 | 44168.7083 | 0 | 20.4025 | 37.78
2020-12-03 17:30 | 44168.7292 | 0 | 20.025 | 37.78
2020-12-03 18:00 | 44168.75 | 0 | 19.1631 | 37.78
2020-12-03 18:30 | 44168.7708 | 0 | 19.1567 | 37.78
2020-12-03 19:00 | 44168.7917 | 0 | 19.1451 | 37.78
2020-12-03 19:30 | 44168.8125 | 0 | 18.7495 | 37.78
2020-12-03 20:00 | 44168.8333 | 0 | 18.3689 | 37.78
2020-12-03 20:30 | 44168.8542 | 0 | 17.7158 | 37.78
2020-12-03 21:00 | 44168.875 | 0 | 16.9999 | 37.78
2020-12-03 21:30 | 44168.8958 | 0 | 16.5508 | 37.78
2020-12-03 22:00 | 44168.9167 | 0 | 15.985 | 37.78
2020-12-03 22:30 | 44168.9375 | 0 | 14.8477 | 37.78
2020-12-03 23:00 | 44168.9583 | 0 | 14.0836 | 37.78
2020-12-03 23:30 | 44168.9792 | 0 | 13.1998 | 37.78
2020-12-04 | 44169 | 0 | 12.3555 | 37.78
2020-12-04 00:30 | 44169.0208 | 0 | 11.6773 | 37.78
2020-12-04 01:00 | 44169.0417 | 0 | 11.2685 | 37.78
2020-12-04 01:30 | 44169.0625 | 0 | 11.0276 | 37.78
2020-12-04 02:00 | 44169.0833 | 0 | 10.844 | 37.78
2020-12-04 02:30 | 44169.1042 | 0 | 10.6351 | 37.78
2020-12-04 03:00 | 44169.125 | 0 | 10.4625 | 37.78
2020-12-04 03:30 | 44169.1458 | 0 | 10.3366 | 37.78
2020-12-04 04:00 | 44169.1667 | 0 | 10.1915 | 37.78
2020-12-04 04:30 | 44169.1875 | 0 | 10.1072 | 37.78
2020-12-04 05:00 | 44169.2083 | 0 | 10.2446 | 37.78
2020-12-04 05:30 | 44169.2292 | 0 | 10.2981 | 37.78
2020-12-04 06:00 | 44169.25 | 0 | 10.5018 | 37.78
2020-12-04 06:30 | 44169.2708 | 0 | 10.6052 | 37.78
2020-12-04 07:00 | 44169.2917 | 0 | 10.9545 | 37.78
2020-12-04 07:30 | 44169.3125 | 0 | 11.5545 | 37.78
2020-12-04 08:00 | 44169.3333 | 0 | 12.3574 | 37.78
2020-12-04 08:30 | 44169.3542 | 0 | 12.8905 | 37.78
2020-12-04 09:00 | 44169.375 | 0 | 13.1905 | 37.78
2020-12-04 09:30 | 44169.3958 | 0 | 13.5401 | 37.78
2020-12-04 10:00 | 44169.4167 | 0 | 13.8449 | 37.78
2020-12-04 10:30 | 44169.4375 | 0 | 14.1176 | 37.78
2020-12-04 11:00 | 44169.4583 | 0 | 14.2374 | 37.78
2020-12-04 11:30 | 44169.4792 | 0 | 14.4303 | 37.78
2020-12-04 12:00 | 44169.5 | 0 | 14.6685 | 37.78
2020-12-04 12:30 | 44169.5208 | 0 | 14.8393 | 37.78
2020-12-04 13:00 | 44169.5417 | 0 | 16.5958 | 37.78
2020-12-04 13:30 | 44169.5625 | 0 | 15.3554 | 37.78
2020-12-04 14:00 | 44169.5833 | 0 | 15.7889 | 37.78
2020-12-04 14:30 | 44169.6042 | 0 | 16.225 | 37.78
2020-12-04 15:00 | 44169.625 | 0 | 16.8139 | 37.78
2020-12-04 15:30 | 44169.6458 | 0 | 16.177 | 37.78
2020-12-04 16:00 | 44169.6667 | 0 | 16.8458 | 37.78
2020-12-04 16:30 | 44169.6875 | 0 | 16.6974 | 37.78
2020-12-04 17:00 | 44169.7083 | 0 | 16.9782 | 37.78
2020-12-04 17:30 | 44169.7292 | 0 | 16.4321 | 37.78
2020-12-04 18:00 | 44169.75 | 0 | 16.1587 | 37.78
2020-12-04 18:30 | 44169.7708 | 0 | 16.3766 | 37.78
2020-12-04 19:00 | 44169.7917 | 0 | 16.3238 | 37.78
2020-12-04 19:30 | 44169.8125 | 0 | 16.0396 | 37.78
2020-12-04 20:00 | 44169.8333 | 0 | 15.8343 | 37.78
2020-12-04 20:30 | 44169.8542 | 0 | 15.2823 | 37.78
2020-12-04 21:00 | 44169.875 | 0 | 14.7655 | 37.78
2020-12-04 21:30 | 44169.8958 | 0 | 14.2327 | 37.78
2020-12-04 22:00 | 44169.9167 | 0 | 13.7076 | 37.78
2020-12-04 22:30 | 44169.9375 | 0 | 12.7194 | 37.78
2020-12-04 23:00 | 44169.9583 | 0 | 12.1301 | 37.78
2020-12-04 23:30 | 44169.9792 | 0 | 11.6583 | 37.78
2020-12-05 | 44170 | 0 | 11.3025 | 37.78
2020-12-05 00:30 | 44170.0208 | 0 | 10.754 | 37.78
2020-12-05 01:00 | 44170.0417 | 0 | 10.3441 | 37.78
2020-12-05 01:30 | 44170.0625 | 0 | 9.9969 | 37.78
2020-12-05 02:00 | 44170.0833 | 0 | 9.9008 | 37.78
2020-12-05 02:30 | 44170.1042 | 0 | 9.7154 | 37.78
2020-12-05 03:00 | 44170.125 | 0 | 9.643 | 37.78
2020-12-05 03:30 | 44170.1458 | 0 | 9.4399 | 37.78
2020-12-05 04:00 | 44170.1667 | 0 | 9.3162 | 37.78
2020-12-05 04:30 | 44170.1875 | 0 | 9.2572 | 37.78
2020-12-05 05:00 | 44170.2083 | 0 | 9.1631 | 37.78
2020-12-05 05:30 | 44170.2292 | 0 | 8.9209 | 37.78
2020-12-05 06:00 | 44170.25 | 0 | 9.3649 | 37.78
2020-12-05 06:30 | 44170.2708 | 0 | 9.1103 | 37.78
2020-12-05 07:00 | 44170.2917 | 0 | 9.4075 | 37.78
2020-12-05 07:30 | 44170.3125 | 0 | 9.7531 | 37.78
2020-12-05 08:00 | 44170.3333 | 0 | 10.1704 | 37.78
2020-12-05 08:30 | 44170.3542 | 0 | 10.6743 | 37.78
2020-12-05 09:00 | 44170.375 | 0 | 11.6522 | 37.78
2020-12-05 09:30 | 44170.3958 | 0 | 12.7074 | 37.78
2020-12-05 10:00 | 44170.4167 | 0 | 12.2109 | 37.78
2020-12-05 10:30 | 44170.4375 | 0 | 12.1783 | 37.78
2020-12-05 11:00 | 44170.4583 | 0 | 12.9011 | 37.78
2020-12-05 11:30 | 44170.4792 | 0 | 13.5263 | 37.78
2020-12-05 12:00 | 44170.5 | 0 | 13.9963 | 37.78
2020-12-05 12:30 | 44170.5208 | 0 | 15.1748 | 37.78
2020-12-05 13:00 | 44170.5417 | 0 | 15.6039 | 37.78
2020-12-05 13:30 | 44170.5625 | 0 | 16.0808 | 37.78
2020-12-05 14:00 | 44170.5833 | 0 | 16.5201 | 37.78
2020-12-05 14:30 | 44170.6042 | 0 | 16.1622 | 37.78
2020-12-05 15:00 | 44170.625 | 0 | 16.459 | 37.78
2020-12-05 15:30 | 44170.6458 | 0 | 17.3043 | 37.78
2020-12-05 16:00 | 44170.6667 | 0 | 16.5925 | 37.78
2020-12-05 16:30 | 44170.6875 | 0 | 17.7862 | 37.78
2020-12-05 17:00 | 44170.7083 | 0 | 17.8092 | 37.78
2020-12-05 17:30 | 44170.7292 | 0 | 17.8411 | 37.78
2020-12-05 18:00 | 44170.75 | 0 | 18.6149 | 37.78
2020-12-05 18:30 | 44170.7708 | 0 | 19.6916 | 37.78
2020-12-05 19:00 | 44170.7917 | 0 | 20.2246 | 37.78
2020-12-05 19:30 | 44170.8125 | 0 | 19.943 | 37.78
2020-12-05 20:00 | 44170.8333 | 0 | 19.553 | 37.78
2020-12-05 20:30 | 44170.8542 | 0 | 18.7181 | 37.78
2020-12-05 21:00 | 44170.875 | 0 | 17.7094 | 37.78
2020-12-05 21:30 | 44170.8958 | 0 | 16.9077 | 37.78
2020-12-05 22:00 | 44170.9167 | 0 | 15.9648 | 37.78
2020-12-05 22:30 | 44170.9375 | 0 | 14.7567 | 37.78
2020-12-05 23:00 | 44170.9583 | 0 | 14.0571 | 37.78
2020-12-05 23:30 | 44170.9792 | 0 | 13.4442 | 37.78
2020-12-06 | 44171 | 0 | 13.0783 | 37.78
2020-12-06 00:30 | 44171.0208 | 0 | 12.7796 | 37.78
2020-12-06 01:00 | 44171.0417 | 0 | 12.5327 | 37.78
2020-12-06 01:30 | 44171.0625 | 0 | 12.2825 | 37.78
2020-12-06 02:00 | 44171.0833 | 0 | 12.1211 | 37.78
2020-12-06 02:30 | 44171.1042 | 0 | 11.71 | 37.78
2020-12-06 03:00 | 44171.125 | 0 | 11.7179 | 37.78
2020-12-06 03:30 | 44171.1458 | 0 | 11.3612 | 37.78
2020-12-06 04:00 | 44171.1667 | 0 | 11.3206 | 37.78
2020-12-06 04:30 | 44171.1875 | 0 | 11.634 | 37.78
2020-12-06 05:00 | 44171.2083 | 0 | 12.0623 | 37.78
2020-12-06 05:30 | 44171.2292 | 0 | 12.6915 | 37.78
2020-12-06 06:00 | 44171.25 | 0 | 13.7386 | 37.78
2020-12-06 06:30 | 44171.2708 | 0 | 14.4521 | 37.78
2020-12-06 07:00 | 44171.2917 | 0 | 16.0184 | 37.78
2020-12-06 07:30 | 44171.3125 | 0 | 16.8732 | 37.78
2020-12-06 08:00 | 44171.3333 | 0 | 17.3427 | 37.78
2020-12-06 08:30 | 44171.3542 | 0 | 17.795 | 37.78
2020-12-06 09:00 | 44171.375 | 0 | 17.8594 | 37.78
2020-12-06 09:30 | 44171.3958 | 0 | 17.6681 | 37.78
2020-12-06 10:00 | 44171.4167 | 0 | 18.5004 | 37.78
2020-12-06 10:30 | 44171.4375 | 0 | 18.8393 | 37.78
2020-12-06 11:00 | 44171.4583 | 0 | 17.8413 | 37.78
2020-12-06 11:30 | 44171.4792 | 0 | 18.5147 | 37.78
2020-12-06 12:00 | 44171.5 | 0 | 18.3867 | 37.78
2020-12-06 12:30 | 44171.5208 | 0 | 19.2175 | 37.78
2020-12-06 13:00 | 44171.5417 | 0 | 21.3037 | 37.78
2020-12-06 13:30 | 44171.5625 | 0 | 21.7867 | 37.78
2020-12-06 14:00 | 44171.5833 | 0 | 21.962 | 37.78
2020-12-06 14:30 | 44171.6042 | 0 | 20.3768 | 37.78
2020-12-06 15:00 | 44171.625 | 0 | 19.615 | 37.78
2020-12-06 15:30 | 44171.6458 | 0 | 20.0649 | 37.78
2020-12-06 16:00 | 44171.6667 | 0 | 19.274 | 37.78
2020-12-06 16:30 | 44171.6875 | 0 | 18.4934 | 37.78
2020-12-06 17:00 | 44171.7083 | 0 | 17.8607 | 37.78
2020-12-06 17:30 | 44171.7292 | 0 | 18.1761 | 37.78
2020-12-06 18:00 | 44171.75 | 0 | 17.8309 | 37.78
2020-12-06 18:30 | 44171.7708 | 0 | 18.3061 | 37.78
2020-12-06 19:00 | 44171.7917 | 0 | 17.9025 | 37.78
2020-12-06 19:30 | 44171.8125 | 0 | 17.3029 | 37.78
2020-12-06 20:00 | 44171.8333 | 0 | 16.9315 | 37.78
2020-12-06 20:30 | 44171.8542 | 0 | 16.4746 | 37.78
2020-12-06 21:00 | 44171.875 | 0 | 15.6556 | 37.78
2020-12-06 21:30 | 44171.8958 | 0 | 15.0797 | 37.78
2020-12-06 22:00 | 44171.9167 | 0 | 13.9802 | 37.78
2020-12-06 22:30 | 44171.9375 | 0 | 13.3542 | 37.78
2020-12-06 23:00 | 44171.9583 | 0 | 12.7128 | 37.78
2020-12-06 23:30 | 44171.9792 | 0 | 11.8369 | 37.78
2020-12-07 | 44172 | 0 | 11.1941 | 37.78
2020-12-07 00:30 | 44172.0208 | 0 | 10.7359 | 37.78
2020-12-07 01:00 | 44172.0417 | 0 | 10.4869 | 37.78
2020-12-07 01:30 | 44172.0625 | 0 | 10.2974 | 37.78
2020-12-07 02:00 | 44172.0833 | 0 | 10.0934 | 37.78
2020-12-07 02:30 | 44172.1042 | 0 | 9.8062 | 37.78
2020-12-07 03:00 | 44172.125 | 0 | 9.7499 | 37.78
2020-12-07 03:30 | 44172.1458 | 0 | 9.802 | 37.78
2020-12-07 04:00 | 44172.1667 | 0 | 10.0754 | 37.78
2020-12-07 04:30 | 44172.1875 | 0 | 10.3881 | 37.78
2020-12-07 05:00 | 44172.2083 | 0 | 10.8852 | 37.78
2020-12-07 05:30 | 44172.2292 | 0 | 11.5462 | 37.78
2020-12-07 06:00 | 44172.25 | 0 | 12.271 | 37.78
2020-12-07 06:30 | 44172.2708 | 0 | 13.2014 | 37.78
2020-12-07 07:00 | 44172.2917 | 0 | 13.8962 | 37.78
2020-12-07 07:30 | 44172.3125 | 0 | 14.4899 | 37.78
2020-12-07 08:00 | 44172.3333 | 0 | 14.9492 | 37.78
2020-12-07 08:30 | 44172.3542 | 0 | 14.7466 | 37.78
2020-12-07 09:00 | 44172.375 | 0 | 15.1598 | 37.78
2020-12-07 09:30 | 44172.3958 | 0 | 15.375 | 37.78
2020-12-07 10:00 | 44172.4167 | 0 | 15.5036 | 37.78
2020-12-07 10:30 | 44172.4375 | 0 | 14.6187 | 37.78
2020-12-07 11:00 | 44172.4583 | 0 | 14.8261 | 37.78
2020-12-07 11:30 | 44172.4792 | 0 | 14.9582 | 37.78
2020-12-07 12:00 | 44172.5 | 0 | 13.7361 | 37.78
2020-12-07 12:30 | 44172.5208 | 0 | 13.3841 | 37.78
2020-12-07 13:00 | 44172.5417 | 0 | 13.3995 | 37.78
2020-12-07 13:30 | 44172.5625 | 0 | 14.0191 | 37.78
2020-12-07 14:00 | 44172.5833 | 0 | 14.1877 | 37.78
2020-12-07 14:30 | 44172.6042 | 0 | 14.92 | 37.78
2020-12-07 15:00 | 44172.625 | 0 | 15.8873 | 37.78
2020-12-07 15:30 | 44172.6458 | 0 | 15.5789 | 37.78
2020-12-07 16:00 | 44172.6667 | 0 | 15.2969 | 37.78
2020-12-07 16:30 | 44172.6875 | 0 | 16.508 | 37.78
2020-12-07 17:00 | 44172.7083 | 0 | 16.4206 | 37.78
2020-12-07 17:30 | 44172.7292 | 0 | 16.131 | 37.78
2020-12-07 18:00 | 44172.75 | 0 | 16.02 | 37.78
2020-12-07 18:30 | 44172.7708 | 0 | 16.7519 | 37.78
2020-12-07 19:00 | 44172.7917 | 0 | 16.8375 | 37.78
2020-12-07 19:30 | 44172.8125 | 0 | 16.5519 | 37.78
2020-12-07 20:00 | 44172.8333 | 0 | 16.1893 | 37.78
2020-12-07 20:30 | 44172.8542 | 0 | 15.642 | 37.78
2020-12-07 21:00 | 44172.875 | 0 | 14.9265 | 37.78
2020-12-07 21:30 | 44172.8958 | 0 | 14.311 | 37.78
2020-12-07 22:00 | 44172.9167 | 0 | 13.706 | 37.78
2020-12-07 22:30 | 44172.9375 | 0 | 12.613 | 37.78
2020-12-07 23:00 | 44172.9583 | 0 | 11.7811 | 37.78
2020-12-07 23:30 | 44172.9792 | 0 | 11.1184 | 37.78
2020-12-08 | 44173 | 0 | 10.313 | 37.78
2020-12-08 00:30 | 44173.0208 | 0 | 9.7687 | 37.78
2020-12-08 01:00 | 44173.0417 | 0 | 9.712 | 37.78
2020-12-08 01:30 | 44173.0625 | 0 | 9.5083 | 37.78
2020-12-08 02:00 | 44173.0833 | 0 | 9.3032 | 37.78
2020-12-08 02:30 | 44173.1042 | 0 | 9.1597 | 37.78
2020-12-08 03:00 | 44173.125 | 0 | 9.0001 | 37.78
2020-12-08 03:30 | 44173.1458 | 0 | 9.0454 | 37.78
2020-12-08 04:00 | 44173.1667 | 0 | 9.2904 | 37.78
2020-12-08 04:30 | 44173.1875 | 0 | 9.5445 | 37.78
2020-12-08 05:00 | 44173.2083 | 0 | 9.8629 | 37.78
2020-12-08 05:30 | 44173.2292 | 0 | 10.1579 | 37.78
2020-12-08 06:00 | 44173.25 | 0 | 10.8252 | 37.78
2020-12-08 06:30 | 44173.2708 | 0 | 11.1758 | 37.78
2020-12-08 07:00 | 44173.2917 | 0 | 11.5717 | 37.78
2020-12-08 07:30 | 44173.3125 | 0 | 11.7094 | 37.78
2020-12-08 08:00 | 44173.3333 | 0 | 12.2326 | 37.78
2020-12-08 08:30 | 44173.3542 | 0 | 12.8341 | 37.78
2020-12-08 09:00 | 44173.375 | 0 | 13.3908 | 37.78
2020-12-08 09:30 | 44173.3958 | 0 | 13.0072 | 37.78
2020-12-08 10:00 | 44173.4167 | 0 | 12.4712 | 37.78
2020-12-08 10:30 | 44173.4375 | 0 | 13.8371 | 37.78
2020-12-08 11:00 | 44173.4583 | 0 | 12.802 | 37.78
2020-12-08 11:30 | 44173.4792 | 0 | 12.5957 | 37.78
2020-12-08 12:00 | 44173.5 | 0 | 12.4068 | 37.78
2020-12-08 12:30 | 44173.5208 | 0 | 12.5337 | 37.78
2020-12-08 13:00 | 44173.5417 | 0 | 12.7148 | 37.78
2020-12-08 13:30 | 44173.5625 | 0 | 13.7248 | 37.78
2020-12-08 14:00 | 44173.5833 | 0 | 13.5551 | 37.78
2020-12-08 14:30 | 44173.6042 | 0 | 14.0651 | 37.78
2020-12-08 15:00 | 44173.625 | 0 | 14.4424 | 37.78
2020-12-08 15:30 | 44173.6458 | 0 | 14.4553 | 37.78
2020-12-08 16:00 | 44173.6667 | 0 | 14.8309 | 37.78
2020-12-08 16:30 | 44173.6875 | 0 | 15.102 | 37.78
2020-12-08 17:00 | 44173.7083 | 0 | 15.2985 | 37.78
2020-12-08 17:30 | 44173.7292 | 0 | 15.3906 | 37.78
2020-12-08 18:00 | 44173.75 | 0 | 15.174 | 37.78
2020-12-08 18:30 | 44173.7708 | 0 | 15.4285 | 37.78
2020-12-08 19:00 | 44173.7917 | 0 | 15.4488 | 37.78
2020-12-08 19:30 | 44173.8125 | 0 | 15.2985 | 37.78
2020-12-08 20:00 | 44173.8333 | 0 | 14.9806 | 37.78
2020-12-08 20:30 | 44173.8542 | 0 | 14.4688 | 37.78
2020-12-08 21:00 | 44173.875 | 0 | 14.0294 | 37.78
2020-12-08 21:30 | 44173.8958 | 0 | 13.4853 | 37.78
2020-12-08 22:00 | 44173.9167 | 0 | 12.8545 | 37.78
2020-12-08 22:30 | 44173.9375 | 0 | 12.0986 | 37.78
2020-12-08 23:00 | 44173.9583 | 0 | 11.4147 | 37.78
2020-12-08 23:30 | 44173.9792 | 0 | 10.7893 | 37.78
2020-12-09 | 44174 | 0 | 10.2085 | 37.78
2020-12-09 00:30 | 44174.0208 | 0 | 9.7656 | 37.78
2020-12-09 01:00 | 44174.0417 | 0 | 9.6856 | 37.78
2020-12-09 01:30 | 44174.0625 | 0 | 9.5664 | 37.78
2020-12-09 02:00 | 44174.0833 | 0 | 9.5029 | 37.78
2020-12-09 02:30 | 44174.1042 | 0 | 9.4379 | 37.78
2020-12-09 03:00 | 44174.125 | 0 | 9.3885 | 37.78
2020-12-09 03:30 | 44174.1458 | 0 | 9.3533 | 37.78
2020-12-09 04:00 | 44174.1667 | 0 | 9.5997 | 37.78
2020-12-09 04:30 | 44174.1875 | 0 | 10.0159 | 37.78
2020-12-09 05:00 | 44174.2083 | 0 | 10.4028 | 37.78
2020-12-09 05:30 | 44174.2292 | 0 | 10.5782 | 37.78
2020-12-09 06:00 | 44174.25 | 0 | 11.2223 | 37.78
2020-12-09 06:30 | 44174.2708 | 0 | 11.8729 | 37.78
2020-12-09 07:00 | 44174.2917 | 0 | 12.452 | 37.78
2020-12-09 07:30 | 44174.3125 | 0 | 12.8333 | 37.78
2020-12-09 08:00 | 44174.3333 | 0 | 13.4443 | 37.78
2020-12-09 08:30 | 44174.3542 | 0 | 13.5393 | 37.78
2020-12-09 09:00 | 44174.375 | 0 | 12.3581 | 37.78
2020-12-09 09:30 | 44174.3958 | 0 | 12.5596 | 37.78
2020-12-09 10:00 | 44174.4167 | 0 | 12.9837 | 37.78
2020-12-09 10:30 | 44174.4375 | 0 | 13.1429 | 37.78
2020-12-09 11:00 | 44174.4583 | 0 | 12.9736 | 37.78
2020-12-09 11:30 | 44174.4792 | 0 | 13.4233 | 37.78
2020-12-09 12:00 | 44174.5 | 0 | 13.001 | 37.78
2020-12-09 12:30 | 44174.5208 | 0 | 13.0978 | 37.78
2020-12-09 13:00 | 44174.5417 | 0 | 13.4818 | 37.78
2020-12-09 13:30 | 44174.5625 | 0 | 14.0865 | 37.78
2020-12-09 14:00 | 44174.5833 | 0 | 14.4925 | 37.78
2020-12-09 14:30 | 44174.6042 | 0 | 14.6238 | 37.78
2020-12-09 15:00 | 44174.625 | 0 | 15.0482 | 37.78
2020-12-09 15:30 | 44174.6458 | 0 | 15.4319 | 37.78
2020-12-09 16:00 | 44174.6667 | 0 | 15.9132 | 37.78
2020-12-09 16:30 | 44174.6875 | 0 | 16.091 | 37.78
2020-12-09 17:00 | 44174.7083 | 0 | 16.3258 | 37.78
2020-12-09 17:30 | 44174.7292 | 0 | 16.1492 | 37.78
2020-12-09 18:00 | 44174.75 | 0 | 15.8102 | 37.78
2020-12-09 18:30 | 44174.7708 | 0 | 16.179 | 37.78
2020-12-09 19:00 | 44174.7917 | 0 | 16.1133 | 37.78
2020-12-09 19:30 | 44174.8125 | 0 | 15.8136 | 37.78
2020-12-09 20:00 | 44174.8333 | 0 | 15.5021 | 37.78
2020-12-09 20:30 | 44174.8542 | 0 | 15.1679 | 37.78
2020-12-09 21:00 | 44174.875 | 0 | 14.5707 | 37.78
2020-12-09 21:30 | 44174.8958 | 0 | 14.12 | 37.78
2020-12-09 22:00 | 44174.9167 | 0 | 13.3138 | 37.78
2020-12-09 22:30 | 44174.9375 | 0 | 12.5758 | 37.78
2020-12-09 23:00 | 44174.9583 | 0 | 11.8242 | 37.78
2020-12-09 23:30 | 44174.9792 | 0 | 11.1837 | 37.78
2020-12-10 | 44175 | 0 | 10.5517 | 37.78
2020-12-10 00:30 | 44175.0208 | 0 | 10.0994 | 37.78
2020-12-10 01:00 | 44175.0417 | 0 | 9.8683 | 37.78
2020-12-10 01:30 | 44175.0625 | 0 | 9.8616 | 37.78
2020-12-10 02:00 | 44175.0833 | 0 | 9.7871 | 37.78
2020-12-10 02:30 | 44175.1042 | 0 | 9.5793 | 37.78
2020-12-10 03:00 | 44175.125 | 0 | 9.4284 | 37.78
2020-12-10 03:30 | 44175.1458 | 0 | 9.3919 | 37.78
2020-12-10 04:00 | 44175.1667 | 0 | 9.6572 | 37.78
2020-12-10 04:30 | 44175.1875 | 0 | 9.892 | 37.78
2020-12-10 05:00 | 44175.2083 | 0 | 10.3753 | 37.78
2020-12-10 05:30 | 44175.2292 | 0 | 10.7217 | 37.78
2020-12-10 06:00 | 44175.25 | 0 | 10.9275 | 37.78
2020-12-10 06:30 | 44175.2708 | 0 | 11.5508 | 37.78
2020-12-10 07:00 | 44175.2917 | 0 | 11.6835 | 37.78
2020-12-10 07:30 | 44175.3125 | 0 | 13.1456 | 37.78
2020-12-10 08:00 | 44175.3333 | 0 | 12.6708 | 37.78
2020-12-10 08:30 | 44175.3542 | 0 | 12.4438 | 37.78
2020-12-10 09:00 | 44175.375 | 0 | 14.0342 | 37.78
2020-12-10 09:30 | 44175.3958 | 0 | 13.5964 | 37.78
2020-12-10 10:00 | 44175.4167 | 0 | 13.5952 | 37.78
2020-12-10 10:30 | 44175.4375 | 0 | 13.6575 | 37.78
2020-12-10 11:00 | 44175.4583 | 0 | 13.9338 | 37.78
2020-12-10 11:30 | 44175.4792 | 0 | 14.0005 | 37.78
2020-12-10 12:00 | 44175.5 | 0 | 13.6953 | 37.78
2020-12-10 12:30 | 44175.5208 | 0 | 13.456 | 37.78
2020-12-10 13:00 | 44175.5417 | 0 | 13.3576 | 37.78
2020-12-10 13:30 | 44175.5625 | 0 | 12.9736 | 37.78
2020-12-10 14:00 | 44175.5833 | 0 | 12.8207 | 37.78
2020-12-10 14:30 | 44175.6042 | 0 | 12.9339 | 37.78
2020-12-10 15:00 | 44175.625 | 0 | 13.4488 | 37.78
2020-12-10 15:30 | 44175.6458 | 0 | 13.1796 | 37.78
2020-12-10 16:00 | 44175.6667 | 0 | 13.0416 | 37.78
2020-12-10 16:30 | 44175.6875 | 0 | 13.0571 | 37.78
2020-12-10 17:00 | 44175.7083 | 0 | 12.8995 | 37.78
2020-12-10 17:30 | 44175.7292 | 0 | 12.5637 | 37.78
2020-12-10 18:00 | 44175.75 | 0 | 12.4887 | 37.78
2020-12-10 18:30 | 44175.7708 | 0 | 12.8663 | 37.78
2020-12-10 19:00 | 44175.7917 | 0 | 12.9922 | 37.78
2020-12-10 19:30 | 44175.8125 | 0 | 12.8 | 37.78
2020-12-10 20:00 | 44175.8333 | 0 | 12.6883 | 37.78
2020-12-10 20:30 | 44175.8542 | 0 | 12.141 | 37.78
2020-12-10 21:00 | 44175.875 | 0 | 11.7436 | 37.78
2020-12-10 21:30 | 44175.8958 | 0 | 11.4087 | 37.78
2020-12-10 22:00 | 44175.9167 | 0 | 11.215 | 37.78
2020-12-10 22:30 | 44175.9375 | 0 | 10.441 | 37.78
2020-12-10 23:00 | 44175.9583 | 0 | 10.0298 | 37.78
2020-12-10 23:30 | 44175.9792 | 0 | 9.5753 | 37.78
2020-12-11 | 44176 | 0 | 9.1862 | 37.78
2020-12-11 00:30 | 44176.0208 | 0 | 8.7862 | 37.78
2020-12-11 01:00 | 44176.0417 | 0 | 8.5425 | 37.78
2020-12-11 01:30 | 44176.0625 | 0 | 8.4661 | 37.78
2020-12-11 02:00 | 44176.0833 | 0 | 8.3984 | 37.78
2020-12-11 02:30 | 44176.1042 | 0 | 8.3456 | 37.78
2020-12-11 03:00 | 44176.125 | 0 | 8.2949 | 37.78
2020-12-11 03:30 | 44176.1458 | 0 | 8.2827 | 37.78
2020-12-11 04:00 | 44176.1667 | 0 | 8.349 | 37.78
2020-12-11 04:30 | 44176.1875 | 0 | 8.4519 | 37.78
2020-12-11 05:00 | 44176.2083 | 0 | 8.5215 | 37.78
2020-12-11 05:30 | 44176.2292 | 0 | 8.4688 | 37.78
2020-12-11 06:00 | 44176.25 | 0 | 8.5203 | 37.78
2020-12-11 06:30 | 44176.2708 | 0 | 8.8695 | 37.78
2020-12-11 07:00 | 44176.2917 | 0 | 9.2918 | 37.78
2020-12-11 07:30 | 44176.3125 | 0 | 9.2261 | 37.78
2020-12-11 08:00 | 44176.3333 | 0 | 9.7258 | 37.78
2020-12-11 08:30 | 44176.3542 | 0 | 10.4498 | 37.78
2020-12-11 09:00 | 44176.375 | 0 | 9.7767 | 37.78
2020-12-11 09:30 | 44176.3958 | 0 | 10.0226 | 37.78
2020-12-11 10:00 | 44176.4167 | 0 | 10.1982 | 37.78
2020-12-11 10:30 | 44176.4375 | 0 | 9.9055 | 37.78
2020-12-11 11:00 | 44176.4583 | 0 | 9.5408 | 37.78
2020-12-11 11:30 | 44176.4792 | 0 | 9.0312 | 37.78
2020-12-11 12:00 | 44176.5 | 0 | 9.3748 | 37.78
2020-12-11 12:30 | 44176.5208 | 0 | 9.4555 | 37.78
2020-12-11 13:00 | 44176.5417 | 0 | 7.3678 | 37.78
2020-12-11 13:30 | 44176.5625 | 0 | 6.5129 | 37.78
2020-12-11 14:00 | 44176.5833 | 0 | 6.8006 | 37.78
2020-12-11 14:30 | 44176.6042 | 0 | 7.5676 | 37.78
2020-12-11 15:00 | 44176.625 | 0 | 8.7599 | 37.78
2020-12-11 15:30 | 44176.6458 | 0 | 8.7688 | 37.78
2020-12-11 16:00 | 44176.6667 | 0 | 9.1578 | 37.78
2020-12-11 16:30 | 44176.6875 | 0 | 9.8125 | 37.78
2020-12-11 17:00 | 44176.7083 | 0 | 10.5224 | 37.78
2020-12-11 17:30 | 44176.7292 | 0 | 10.9924 | 37.78
2020-12-11 18:00 | 44176.75 | 0 | 10.8794 | 37.78
2020-12-11 18:30 | 44176.7708 | 0 | 11.2817 | 37.78
2020-12-11 19:00 | 44176.7917 | 0 | 11.2144 | 37.78
2020-12-11 19:30 | 44176.8125 | 0 | 11.01 | 37.78
2020-12-11 20:00 | 44176.8333 | 0 | 10.8441 | 37.78
2020-12-11 20:30 | 44176.8542 | 0 | 10.3075 | 37.78
2020-12-11 21:00 | 44176.875 | 0 | 10.0195 | 37.78
2020-12-11 21:30 | 44176.8958 | 0 | 9.7966 | 37.78
2020-12-11 22:00 | 44176.9167 | 0 | 9.4385 | 37.78
2020-12-11 22:30 | 44176.9375 | 0 | 9.0513 | 37.78
2020-12-11 23:00 | 44176.9583 | 0 | 8.5744 | 37.78
2020-12-11 23:30 | 44176.9792 | 0 | 8.1558 | 37.78
2020-12-12 | 44177 | 0 | 7.832 | 37.78
2020-12-12 00:30 | 44177.0208 | 0 | 7.6669 | 37.78
2020-12-12 01:00 | 44177.0417 | 0 | 7.5674 | 37.78
2020-12-12 01:30 | 44177.0625 | 0 | 7.388 | 37.78
2020-12-12 02:00 | 44177.0833 | 0 | 7.3481 | 37.78
2020-12-12 02:30 | 44177.1042 | 0 | 7.0957 | 37.78
2020-12-12 03:00 | 44177.125 | 0 | 7.0761 | 37.78
2020-12-12 03:30 | 44177.1458 | 0 | 7.0747 | 37.78
2020-12-12 04:00 | 44177.1667 | 0 | 7.0883 | 37.78
2020-12-12 04:30 | 44177.1875 | 0 | 7.137 | 37.78
2020-12-12 05:00 | 44177.2083 | 0 | 7.1363 | 37.78
2020-12-12 05:30 | 44177.2292 | 0 | 7.1025 | 37.78
2020-12-12 06:00 | 44177.25 | 0 | 7.5125 | 37.78
2020-12-12 06:30 | 44177.2708 | 0 | 7.7359 | 37.78
2020-12-12 07:00 | 44177.2917 | 0 | 8.4681 | 37.78
2020-12-12 07:30 | 44177.3125 | 0 | 8.0972 | 37.78
2020-12-12 08:00 | 44177.3333 | 0 | 9.0767 | 37.78
2020-12-12 08:30 | 44177.3542 | 0 | 9.3364 | 37.78
2020-12-12 09:00 | 44177.375 | 0 | 9.4744 | 37.78
2020-12-12 09:30 | 44177.3958 | 0 | 10.2319 | 37.78
2020-12-12 10:00 | 44177.4167 | 0 | 10.422 | 37.78
2020-12-12 10:30 | 44177.4375 | 0 | 10.5085 | 37.78
2020-12-12 11:00 | 44177.4583 | 0 | 9.9587 | 37.78
2020-12-12 11:30 | 44177.4792 | 0 | 10.0484 | 37.78
2020-12-12 12:00 | 44177.5 | 0 | 10.319 | 37.78
2020-12-12 12:30 | 44177.5208 | 0 | 10.1498 | 37.78
2020-12-12 13:00 | 44177.5417 | 0 | 10.0754 | 37.78
2020-12-12 13:30 | 44177.5625 | 0 | 9.5064 | 37.78
2020-12-12 14:00 | 44177.5833 | 0 | 9.1309 | 37.78
2020-12-12 14:30 | 44177.6042 | 0 | 9.2836 | 37.78
2020-12-12 15:00 | 44177.625 | 0 | 9.5279 | 37.78
2020-12-12 15:30 | 44177.6458 | 0 | 9.8023 | 37.78
2020-12-12 16:00 | 44177.6667 | 0 | 9.9665 | 37.78
2020-12-12 16:30 | 44177.6875 | 0 | 10.454 | 37.78
2020-12-12 17:00 | 44177.7083 | 0 | 10.5735 | 37.78
2020-12-12 17:30 | 44177.7292 | 0 | 10.7258 | 37.78
2020-12-12 18:00 | 44177.75 | 0 | 10.8009 | 37.78
2020-12-12 18:30 | 44177.7708 | 0 | 11.2788 | 37.78
2020-12-12 19:00 | 44177.7917 | 0 | 11.3809 | 37.78
2020-12-12 19:30 | 44177.8125 | 0 | 10.897 | 37.78
2020-12-12 20:00 | 44177.8333 | 0 | 10.8691 | 37.78
2020-12-12 20:30 | 44177.8542 | 0 | 10.4882 | 37.78
2020-12-12 21:00 | 44177.875 | 0 | 10.2696 | 37.78
2020-12-12 21:30 | 44177.8958 | 0 | 9.9847 | 37.78
2020-12-12 22:00 | 44177.9167 | 0 | 9.6903 | 37.78
2020-12-12 22:30 | 44177.9375 | 0 | 9.3822 | 37.78
2020-12-12 23:00 | 44177.9583 | 0 | 9.0217 | 37.78
2020-12-12 23:30 | 44177.9792 | 0 | 8.5577 | 37.78
2020-12-13 | 44178 | 0 | 8.3483 | 37.78
2020-12-13 00:30 | 44178.0208 | 0 | 8.1886 | 37.78
2020-12-13 01:00 | 44178.0417 | 0 | 8.0688 | 37.78
2020-12-13 01:30 | 44178.0625 | 0 | 8.084 | 37.78
2020-12-13 02:00 | 44178.0833 | 0 | 8.2238 | 37.78
2020-12-13 02:30 | 44178.1042 | 0 | 8.0431 | 37.78
2020-12-13 03:00 | 44178.125 | 0 | 7.7636 | 37.78
2020-12-13 03:30 | 44178.1458 | 0 | 7.8171 | 37.78
2020-12-13 04:00 | 44178.1667 | 0 | 8.1081 | 37.78
2020-12-13 04:30 | 44178.1875 | 0 | 8.6488 | 37.78
2020-12-13 05:00 | 44178.2083 | 0 | 9.1056 | 37.78
2020-12-13 05:30 | 44178.2292 | 0 | 9.7379 | 37.78
2020-12-13 06:00 | 44178.25 | 0 | 10.3149 | 37.78
2020-12-13 06:30 | 44178.2708 | 0 | 11.1852 | 37.78
2020-12-13 07:00 | 44178.2917 | 0 | 12.2346 | 37.78
2020-12-13 07:30 | 44178.3125 | 0 | 12.6775 | 37.78
2020-12-13 08:00 | 44178.3333 | 0 | 12.997 | 37.78
2020-12-13 08:30 | 44178.3542 | 0 | 13.1224 | 37.78
2020-12-13 09:00 | 44178.375 | 0 | 13.2063 | 37.78
2020-12-13 09:30 | 44178.3958 | 0 | 12.1712 | 37.78
2020-12-13 10:00 | 44178.4167 | 0 | 12.267 | 37.78
2020-12-13 10:30 | 44178.4375 | 0 | 13.1298 | 37.78
2020-12-13 11:00 | 44178.4583 | 0 | 13.7055 | 37.78
2020-12-13 11:30 | 44178.4792 | 0 | 13.6087 | 37.78
2020-12-13 12:00 | 44178.5 | 0 | 10.3933 | 37.78
2020-12-13 12:30 | 44178.5208 | 0 | 11.7943 | 37.78
2020-12-13 13:00 | 44178.5417 | 0 | 12.9103 | 37.78
2020-12-13 13:30 | 44178.5625 | 0 | 12.478 | 37.78
2020-12-13 14:00 | 44178.5833 | 0 | 11.7973 | 37.78
2020-12-13 14:30 | 44178.6042 | 0 | 12.7058 | 37.78
2020-12-13 15:00 | 44178.625 | 0 | 12.7443 | 37.78
2020-12-13 15:30 | 44178.6458 | 0 | 12.6919 | 37.78
2020-12-13 16:00 | 44178.6667 | 0 | 12.5615 | 37.78
2020-12-13 16:30 | 44178.6875 | 0 | 13.2463 | 37.78
2020-12-13 17:00 | 44178.7083 | 0 | 13.5302 | 37.78
2020-12-13 17:30 | 44178.7292 | 0 | 13.7373 | 37.78
2020-12-13 18:00 | 44178.75 | 0 | 13.9877 | 37.78
2020-12-13 18:30 | 44178.7708 | 0 | 14.5849 | 37.78
2020-12-13 19:00 | 44178.7917 | 0 | 14.6035 | 37.78
2020-12-13 19:30 | 44178.8125 | 0 | 13.9984 | 37.78
2020-12-13 20:00 | 44178.8333 | 0 | 13.8259 | 37.78
2020-12-13 20:30 | 44178.8542 | 0 | 13.2952 | 37.78
2020-12-13 21:00 | 44178.875 | 0 | 13.0104 | 37.78
2020-12-13 21:30 | 44178.8958 | 0 | 12.5013 | 37.78
2020-12-13 22:00 | 44178.9167 | 0 | 11.9255 | 37.78
2020-12-13 22:30 | 44178.9375 | 0 | 11.2607 | 37.78
2020-12-13 23:00 | 44178.9583 | 0 | 10.4332 | 37.78
2020-12-13 23:30 | 44178.9792 | 0 | 10.2101 | 37.78
2020-12-14 | 44179 | 0 | 9.6152 | 37.78
2020-12-14 00:30 | 44179.0208 | 0 | 9.1342 | 37.78
2020-12-14 01:00 | 44179.0417 | 0 | 9.1185 | 37.78
2020-12-14 01:30 | 44179.0625 | 0 | 8.818 | 37.78
2020-12-14 02:00 | 44179.0833 | 0 | 8.8965 | 37.78
2020-12-14 02:30 | 44179.1042 | 0 | 8.6779 | 37.78
2020-12-14 03:00 | 44179.125 | 0 | 8.5534 | 37.78
2020-12-14 03:30 | 44179.1458 | 0 | 8.7707 | 37.78
2020-12-14 04:00 | 44179.1667 | 0 | 8.883 | 37.78
2020-12-14 04:30 | 44179.1875 | 0 | 9.2721 | 37.78
2020-12-14 05:00 | 44179.2083 | 0 | 9.6051 | 37.78
2020-12-14 05:30 | 44179.2292 | 0 | 10.0029 | 37.78
2020-12-14 06:00 | 44179.25 | 0 | 10.5503 | 37.78
2020-12-14 06:30 | 44179.2708 | 0 | 11.2511 | 37.78
2020-12-14 07:00 | 44179.2917 | 0 | 11.8792 | 37.78
2020-12-14 07:30 | 44179.3125 | 0 | 12.2627 | 37.78
2020-12-14 08:00 | 44179.3333 | 0 | 12.9822 | 37.78
2020-12-14 08:30 | 44179.3542 | 0 | 13.8759 | 37.78
2020-12-14 09:00 | 44179.375 | 0 | 13.4384 | 37.78
2020-12-14 09:30 | 44179.3958 | 0 | 13.9652 | 37.78
2020-12-14 10:00 | 44179.4167 | 0 | 15.1214 | 37.78
2020-12-14 10:30 | 44179.4375 | 0 | 14.4909 | 37.78
2020-12-14 11:00 | 44179.4583 | 0 | 13.3072 | 37.78
2020-12-14 11:30 | 44179.4792 | 0 | 13.8184 | 37.78
2020-12-14 12:00 | 44179.5 | 0 | 13.8531 | 37.78
2020-12-14 12:30 | 44179.5208 | 0 | 13.593 | 37.78
2020-12-14 13:00 | 44179.5417 | 0 | 14.2463 | 37.78
2020-12-14 13:30 | 44179.5625 | 0 | 14.1594 | 37.78
2020-12-14 14:00 | 44179.5833 | 0 | 14.9599 | 37.78
2020-12-14 14:30 | 44179.6042 | 0 | 15.3391 | 37.78
2020-12-14 15:00 | 44179.625 | 0 | 16.1073 | 37.78
2020-12-14 15:30 | 44179.6458 | 0 | 16.2934 | 37.78
2020-12-14 16:00 | 44179.6667 | 0 | 16.5792 | 37.78
2020-12-14 16:30 | 44179.6875 | 0 | 16.9193 | 37.78
2020-12-14 17:00 | 44179.7083 | 0 | 17.0087 | 37.78
2020-12-14 17:30 | 44179.7292 | 0 | 17.0351 | 37.78
2020-12-14 18:00 | 44179.75 | 0 | 17.0127 | 37.78
2020-12-14 18:30 | 44179.7708 | 0 | 17.4736 | 37.78
2020-12-14 19:00 | 44179.7917 | 0 | 17.5156 | 37.78
2020-12-14 19:30 | 44179.8125 | 0 | 17.4174 | 37.78
2020-12-14 20:00 | 44179.8333 | 0 | 17.1474 | 37.78
2020-12-14 20:30 | 44179.8542 | 0 | 16.6108 | 37.78
2020-12-14 21:00 | 44179.875 | 0 | 15.5585 | 37.78
2020-12-14 21:30 | 44179.8958 | 0 | 15.0361 | 37.78
2020-12-14 22:00 | 44179.9167 | 0 | 14.2655 | 37.78
2020-12-14 22:30 | 44179.9375 | 0 | 13.2323 | 37.78
2020-12-14 23:00 | 44179.9583 | 0 | 12.4327 | 37.78
2020-12-14 23:30 | 44179.9792 | 0 | 11.7545 | 37.78
2020-12-15 | 44180 | 0 | 10.9212 | 37.78
2020-12-15 00:30 | 44180.0208 | 0 | 10.4002 | 37.78
2020-12-15 01:00 | 44180.0417 | 0 | 10.1846 | 37.78
2020-12-15 01:30 | 44180.0625 | 0 | 10.1065 | 37.78
2020-12-15 02:00 | 44180.0833 | 0 | 10.047 | 37.78
2020-12-15 02:30 | 44180.1042 | 0 | 9.9258 | 37.78
2020-12-15 03:00 | 44180.125 | 0 | 9.8487 | 37.78
2020-12-15 03:30 | 44180.1458 | 0 | 10.0314 | 37.78
2020-12-15 04:00 | 44180.1667 | 0 | 10.2575 | 37.78
2020-12-15 04:30 | 44180.1875 | 0 | 10.5713 | 37.78
2020-12-15 05:00 | 44180.2083 | 0 | 10.9457 | 37.78
2020-12-15 05:30 | 44180.2292 | 0 | 11.105 | 37.78
2020-12-15 06:00 | 44180.25 | 0 | 12.3296 | 37.78
2020-12-15 06:30 | 44180.2708 | 0 | 13.0438 | 37.78
2020-12-15 07:00 | 44180.2917 | 0 | 14.3286 | 37.78
2020-12-15 07:30 | 44180.3125 | 0 | 14.8979 | 37.78
2020-12-15 08:00 | 44180.3333 | 0 | 14.3702 | 37.78
2020-12-15 08:30 | 44180.3542 | 0 | 14.7017 | 37.78
2020-12-15 09:00 | 44180.375 | 0 | 15.1549 | 37.78
2020-12-15 09:30 | 44180.3958 | 0 | 15.6465 | 37.78
2020-12-15 10:00 | 44180.4167 | 0 | 15.2837 | 37.78
2020-12-15 10:30 | 44180.4375 | 0 | 14.9121 | 37.78
2020-12-15 11:00 | 44180.4583 | 0 | 15.2635 | 37.78
2020-12-15 11:30 | 44180.4792 | 0 | 15.6084 | 37.78
2020-12-15 12:00 | 44180.5 | 0 | 17.0213 | 37.78
2020-12-15 12:30 | 44180.5208 | 0 | 15.1609 | 37.78
2020-12-15 13:00 | 44180.5417 | 0 | 15.759 | 37.78
2020-12-15 13:30 | 44180.5625 | 0 | 16.1686 | 37.78
2020-12-15 14:00 | 44180.5833 | 0 | 16.8289 | 37.78
2020-12-15 14:30 | 44180.6042 | 0 | 18.0176 | 37.78
2020-12-15 15:00 | 44180.625 | 0 | 18.423 | 37.78
2020-12-15 15:30 | 44180.6458 | 0 | 17.9311 | 37.78
2020-12-15 16:00 | 44180.6667 | 0 | 17.8096 | 37.78
2020-12-15 16:30 | 44180.6875 | 0 | 17.8673 | 37.78
2020-12-15 17:00 | 44180.7083 | 0 | 17.263 | 37.78
2020-12-15 17:30 | 44180.7292 | 0 | 17.1771 | 37.78
2020-12-15 18:00 | 44180.75 | 0 | 17.1037 | 37.78
2020-12-15 18:30 | 44180.7708 | 0 | 17.4217 | 37.78
2020-12-15 19:00 | 44180.7917 | 0 | 16.9379 | 37.78
2020-12-15 19:30 | 44180.8125 | 0 | 16.8909 | 37.78
2020-12-15 20:00 | 44180.8333 | 0 | 16.3745 | 37.78
2020-12-15 20:30 | 44180.8542 | 0 | 15.821 | 37.78
2020-12-15 21:00 | 44180.875 | 0 | 15.2659 | 37.78
2020-12-15 21:30 | 44180.8958 | 0 | 14.781 | 37.78
2020-12-15 22:00 | 44180.9167 | 0 | 14.2167 | 37.78
2020-12-15 22:30 | 44180.9375 | 0 | 13.4394 | 37.78
2020-12-15 23:00 | 44180.9583 | 0 | 12.8441 | 37.78
2020-12-15 23:30 | 44180.9792 | 0 | 12.3757 | 37.78
2020-12-16 | 44181 | 0 | 11.498 | 37.78
2020-12-16 00:30 | 44181.0208 | 0 | 11.0447 | 37.78
2020-12-16 01:00 | 44181.0417 | 0 | 10.6419 | 37.78
2020-12-16 01:30 | 44181.0625 | 0 | 10.395 | 37.78
2020-12-16 02:00 | 44181.0833 | 0 | 10.339 | 37.78
2020-12-16 02:30 | 44181.1042 | 0 | 10.0077 | 37.78
2020-12-16 03:00 | 44181.125 | 0 | 9.9262 | 37.78
2020-12-16 03:30 | 44181.1458 | 0 | 10.1706 | 37.78
2020-12-16 04:00 | 44181.1667 | 0 | 10.3894 | 37.78
2020-12-16 04:30 | 44181.1875 | 0 | 10.78 | 37.78
2020-12-16 05:00 | 44181.2083 | 0 | 11.1461 | 37.78
2020-12-16 05:30 | 44181.2292 | 0 | 11.5462 | 37.78
2020-12-16 06:00 | 44181.25 | 0 | 12.3121 | 37.78
2020-12-16 06:30 | 44181.2708 | 0 | 13.1828 | 37.78
2020-12-16 07:00 | 44181.2917 | 0 | 14.3359 | 37.78
2020-12-16 07:30 | 44181.3125 | 0 | 14.4161 | 37.78
2020-12-16 08:00 | 44181.3333 | 0 | 14.9666 | 37.78
2020-12-16 08:30 | 44181.3542 | 0 | 14.2237 | 37.78
2020-12-16 09:00 | 44181.375 | 0 | 14.4129 | 37.78
2020-12-16 09:30 | 44181.3958 | 0 | 16.4768 | 37.78
2020-12-16 10:00 | 44181.4167 | 0 | 14.9159 | 37.78
2020-12-16 10:30 | 44181.4375 | 0 | 14.0367 | 37.78
2020-12-16 11:00 | 44181.4583 | 0 | 13.6559 | 37.78
2020-12-16 11:30 | 44181.4792 | 0 | 16.3979 | 37.78
2020-12-16 12:00 | 44181.5 | 0 | 15.3146 | 37.78
2020-12-16 12:30 | 44181.5208 | 0 | 13.9559 | 37.78
2020-12-16 13:00 | 44181.5417 | 0 | 14.8585 | 37.78
2020-12-16 13:30 | 44181.5625 | 0 | 15.7665 | 37.78
2020-12-16 14:00 | 44181.5833 | 0 | 15.3102 | 37.78
2020-12-16 14:30 | 44181.6042 | 0 | 15.6965 | 37.78
2020-12-16 15:00 | 44181.625 | 0 | 15.7533 | 37.78
2020-12-16 15:30 | 44181.6458 | 0 | 16.1707 | 37.78
2020-12-16 16:00 | 44181.6667 | 0 | 16.5101 | 37.78
2020-12-16 16:30 | 44181.6875 | 0 | 16.5651 | 37.78
2020-12-16 17:00 | 44181.7083 | 0 | 16.8134 | 37.78
2020-12-16 17:30 | 44181.7292 | 0 | 16.7256 | 37.78
2020-12-16 18:00 | 44181.75 | 0 | 16.3413 | 37.78
2020-12-16 18:30 | 44181.7708 | 0 | 16.5666 | 37.78
2020-12-16 19:00 | 44181.7917 | 0 | 16.7155 | 37.78
2020-12-16 19:30 | 44181.8125 | 0 | 16.9767 | 37.78
2020-12-16 20:00 | 44181.8333 | 0 | 16.6887 | 37.78
2020-12-16 20:30 | 44181.8542 | 0 | 16.1865 | 37.78
2020-12-16 21:00 | 44181.875 | 0 | 15.6639 | 37.78
2020-12-16 21:30 | 44181.8958 | 0 | 15.4873 | 37.78
2020-12-16 22:00 | 44181.9167 | 0 | 14.7874 | 37.78
2020-12-16 22:30 | 44181.9375 | 0 | 13.6986 | 37.78
2020-12-16 23:00 | 44181.9583 | 0 | 12.961 | 37.78
2020-12-16 23:30 | 44181.9792 | 0 | 12.1277 | 37.78
2020-12-17 | 44182 | 0 | 11.4243 | 37.78
2020-12-17 00:30 | 44182.0208 | 0 | 10.9606 | 37.78
2020-12-17 01:00 | 44182.0417 | 0 | 10.5631 | 37.78
2020-12-17 01:30 | 44182.0625 | 0 | 10.5618 | 37.78
2020-12-17 02:00 | 44182.0833 | 0 | 10.4623 | 37.78
2020-12-17 02:30 | 44182.1042 | 0 | 10.4396 | 37.78
2020-12-17 03:00 | 44182.125 | 0 | 10.4739 | 37.78
2020-12-17 03:30 | 44182.1458 | 0 | 10.4043 | 37.78
2020-12-17 04:00 | 44182.1667 | 0 | 10.4756 | 37.78
2020-12-17 04:30 | 44182.1875 | 0 | 10.6683 | 37.78
2020-12-17 05:00 | 44182.2083 | 0 | 11.052 | 37.78
2020-12-17 05:30 | 44182.2292 | 0 | 11.6247 | 37.78
2020-12-17 06:00 | 44182.25 | 0 | 12.2513 | 37.78
2020-12-17 06:30 | 44182.2708 | 0 | 12.9191 | 37.78
2020-12-17 07:00 | 44182.2917 | 0 | 14.0143 | 37.78
2020-12-17 07:30 | 44182.3125 | 0 | 14.7722 | 37.78
2020-12-17 08:00 | 44182.3333 | 0 | 15.186 | 37.78
2020-12-17 08:30 | 44182.3542 | 0 | 14.7327 | 37.78
2020-12-17 09:00 | 44182.375 | 0 | 15.0645 | 37.78
2020-12-17 09:30 | 44182.3958 | 0 | 14.5659 | 37.78
2020-12-17 10:00 | 44182.4167 | 0 | 14.338 | 37.78
2020-12-17 10:30 | 44182.4375 | 0 | 15.0381 | 37.78
2020-12-17 11:00 | 44182.4583 | 0 | 15.081 | 37.78
2020-12-17 11:30 | 44182.4792 | 0 | 14.9663 | 37.78
2020-12-17 12:00 | 44182.5 | 0 | 15.5983 | 37.78
2020-12-17 12:30 | 44182.5208 | 0 | 15.5226 | 37.78
2020-12-17 13:00 | 44182.5417 | 0 | 16.3015 | 37.78
2020-12-17 13:30 | 44182.5625 | 0 | 16.5727 | 37.78
2020-12-17 14:00 | 44182.5833 | 0 | 16.7002 | 37.78
2020-12-17 14:30 | 44182.6042 | 0 | 16.739 | 37.78
2020-12-17 15:00 | 44182.625 | 0 | 17.1843 | 37.78
2020-12-17 15:30 | 44182.6458 | 0 | 17.9432 | 37.78
2020-12-17 16:00 | 44182.6667 | 0 | 18.2966 | 37.78
2020-12-17 16:30 | 44182.6875 | 0 | 18.6154 | 37.78
2020-12-17 17:00 | 44182.7083 | 0 | 18.5206 | 37.78
2020-12-17 17:30 | 44182.7292 | 0 | 18.2128 | 37.78
2020-12-17 18:00 | 44182.75 | 0 | 17.7674 | 37.78
2020-12-17 18:30 | 44182.7708 | 0 | 18.0237 | 37.78
2020-12-17 19:00 | 44182.7917 | 0 | 17.8708 | 37.78
2020-12-17 19:30 | 44182.8125 | 0 | 17.8882 | 37.78
2020-12-17 20:00 | 44182.8333 | 0 | 17.6305 | 37.78
2020-12-17 20:30 | 44182.8542 | 0 | 17.1544 | 37.78
2020-12-17 21:00 | 44182.875 | 0 | 16.4818 | 37.78
2020-12-17 21:30 | 44182.8958 | 0 | 15.951 | 37.78
2020-12-17 22:00 | 44182.9167 | 0 | 15.3861 | 37.78
2020-12-17 22:30 | 44182.9375 | 0 | 14.5506 | 37.78
2020-12-17 23:00 | 44182.9583 | 0 | 13.6957 | 37.78
2020-12-17 23:30 | 44182.9792 | 0 | 13.0604 | 37.78
2020-12-18 | 44183 | 0 | 12.2294 | 37.78
2020-12-18 00:30 | 44183.0208 | 0 | 11.6922 | 37.78
2020-12-18 01:00 | 44183.0417 | 0 | 11.4003 | 37.78
2020-12-18 01:30 | 44183.0625 | 0 | 11.2345 | 37.78
2020-12-18 02:00 | 44183.0833 | 0 | 11.1498 | 37.78
2020-12-18 02:30 | 44183.1042 | 0 | 10.9113 | 37.78
2020-12-18 03:00 | 44183.125 | 0 | 10.6113 | 37.78
2020-12-18 03:30 | 44183.1458 | 0 | 10.6318 | 37.78
2020-12-18 04:00 | 44183.1667 | 0 | 10.8004 | 37.78
2020-12-18 04:30 | 44183.1875 | 0 | 10.7242 | 37.78
2020-12-18 05:00 | 44183.2083 | 0 | 10.7792 | 37.78
2020-12-18 05:30 | 44183.2292 | 0 | 10.8344 | 37.78
2020-12-18 06:00 | 44183.25 | 0 | 11.1718 | 37.78
2020-12-18 06:30 | 44183.2708 | 0 | 11.1305 | 37.78
2020-12-18 07:00 | 44183.2917 | 0 | 11.912 | 37.78
2020-12-18 07:30 | 44183.3125 | 0 | 12.0865 | 37.78
2020-12-18 08:00 | 44183.3333 | 0 | 12.9143 | 37.78
2020-12-18 08:30 | 44183.3542 | 0 | 12.2597 | 37.78
2020-12-18 09:00 | 44183.375 | 0 | 11.7801 | 37.78
2020-12-18 09:30 | 44183.3958 | 0 | 14.2009 | 37.78
2020-12-18 10:00 | 44183.4167 | 0 | 14.9643 | 37.78
2020-12-18 10:30 | 44183.4375 | 0 | 15.2354 | 37.78
2020-12-18 11:00 | 44183.4583 | 0 | 14.3962 | 37.78
2020-12-18 11:30 | 44183.4792 | 0 | 13.7644 | 37.78
2020-12-18 12:00 | 44183.5 | 0 | 11.9945 | 37.78
2020-12-18 12:30 | 44183.5208 | 0 | 12.7688 | 37.78
2020-12-18 13:00 | 44183.5417 | 0 | 13.4625 | 37.78
2020-12-18 13:30 | 44183.5625 | 0 | 13.6371 | 37.78
2020-12-18 14:00 | 44183.5833 | 0 | 14.1356 | 37.78
2020-12-18 14:30 | 44183.6042 | 0 | 14.6592 | 37.78
2020-12-18 15:00 | 44183.625 | 0 | 15.163 | 37.78
2020-12-18 15:30 | 44183.6458 | 0 | 15.645 | 37.78
2020-12-18 16:00 | 44183.6667 | 0 | 16.1403 | 37.78
2020-12-18 16:30 | 44183.6875 | 0 | 16.5318 | 37.78
2020-12-18 17:00 | 44183.7083 | 0 | 16.8001 | 37.78
2020-12-18 17:30 | 44183.7292 | 0 | 16.62 | 37.78
2020-12-18 18:00 | 44183.75 | 0 | 16.356 | 37.78
2020-12-18 18:30 | 44183.7708 | 0 | 16.3415 | 37.78
2020-12-18 19:00 | 44183.7917 | 0 | 16.2207 | 37.78
2020-12-18 19:30 | 44183.8125 | 0 | 16.0961 | 37.78
2020-12-18 20:00 | 44183.8333 | 0 | 15.8276 | 37.78
2020-12-18 20:30 | 44183.8542 | 0 | 15.2387 | 37.78
2020-12-18 21:00 | 44183.875 | 0 | 14.6334 | 37.78
2020-12-18 21:30 | 44183.8958 | 0 | 14.0039 | 37.78
2020-12-18 22:00 | 44183.9167 | 0 | 13.5588 | 37.78
2020-12-18 22:30 | 44183.9375 | 0 | 12.8927 | 37.78
2020-12-18 23:00 | 44183.9583 | 0 | 12.1573 | 37.78
2020-12-18 23:30 | 44183.9792 | 0 | 11.6609 | 37.78
2020-12-19 | 44184 | 0 | 11.1287 | 37.78
2020-12-19 00:30 | 44184.0208 | 0 | 10.7456 | 37.78
2020-12-19 01:00 | 44184.0417 | 0 | 10.5184 | 37.78
2020-12-19 01:30 | 44184.0625 | 0 | 10.1683 | 37.78
2020-12-19 02:00 | 44184.0833 | 0 | 10.0361 | 37.78
2020-12-19 02:30 | 44184.1042 | 0 | 9.7281 | 37.78
2020-12-19 03:00 | 44184.125 | 0 | 9.6312 | 37.78
2020-12-19 03:30 | 44184.1458 | 0 | 9.4927 | 37.78
2020-12-19 04:00 | 44184.1667 | 0 | 9.4394 | 37.78
2020-12-19 04:30 | 44184.1875 | 0 | 9.317 | 37.78
2020-12-19 05:00 | 44184.2083 | 0 | 9.2425 | 37.78
2020-12-19 05:30 | 44184.2292 | 0 | 9.0103 | 37.78
2020-12-19 06:00 | 44184.25 | 0 | 9.2831 | 37.78
2020-12-19 06:30 | 44184.2708 | 0 | 9.1016 | 37.78
2020-12-19 07:00 | 44184.2917 | 0 | 9.2862 | 37.78
2020-12-19 07:30 | 44184.3125 | 0 | 9.8183 | 37.78
2020-12-19 08:00 | 44184.3333 | 0 | 10.1096 | 37.78
2020-12-19 08:30 | 44184.3542 | 0 | 10.5703 | 37.78
2020-12-19 09:00 | 44184.375 | 0 | 11.7992 | 37.78
2020-12-19 09:30 | 44184.3958 | 0 | 11.6749 | 37.78
2020-12-19 10:00 | 44184.4167 | 0 | 11.3964 | 37.78
2020-12-19 10:30 | 44184.4375 | 0 | 11.2953 | 37.78
2020-12-19 11:00 | 44184.4583 | 0 | 11.3614 | 37.78
2020-12-19 11:30 | 44184.4792 | 0 | 11.6221 | 37.78
2020-12-19 12:00 | 44184.5 | 0 | 11.9156 | 37.78
2020-12-19 12:30 | 44184.5208 | 0 | 12.1196 | 37.78
2020-12-19 13:00 | 44184.5417 | 0 | 12.508 | 37.78
2020-12-19 13:30 | 44184.5625 | 0 | 12.9267 | 37.78
2020-12-19 14:00 | 44184.5833 | 0 | 13.5414 | 37.78
2020-12-19 14:30 | 44184.6042 | 0 | 13.8607 | 37.78
2020-12-19 15:00 | 44184.625 | 0 | 14.3112 | 37.78
2020-12-19 15:30 | 44184.6458 | 0 | 15.0326 | 37.78
2020-12-19 16:00 | 44184.6667 | 0 | 16.0251 | 37.78
2020-12-19 16:30 | 44184.6875 | 0 | 16.3219 | 37.78
2020-12-19 17:00 | 44184.7083 | 0 | 16.2605 | 37.78
2020-12-19 17:30 | 44184.7292 | 0 | 16.1809 | 37.78
2020-12-19 18:00 | 44184.75 | 0 | 15.987 | 37.78
2020-12-19 18:30 | 44184.7708 | 0 | 16.16 | 37.78
2020-12-19 19:00 | 44184.7917 | 0 | 16.1718 | 37.78
2020-12-19 19:30 | 44184.8125 | 0 | 16.0735 | 37.78
2020-12-19 20:00 | 44184.8333 | 0 | 15.9571 | 37.78
2020-12-19 20:30 | 44184.8542 | 0 | 15.3081 | 37.78
2020-12-19 21:00 | 44184.875 | 0 | 14.4562 | 37.78
2020-12-19 21:30 | 44184.8958 | 0 | 13.9813 | 37.78
2020-12-19 22:00 | 44184.9167 | 0 | 13.328 | 37.78
2020-12-19 22:30 | 44184.9375 | 0 | 12.5484 | 37.78
2020-12-19 23:00 | 44184.9583 | 0 | 12.0413 | 37.78
2020-12-19 23:30 | 44184.9792 | 0 | 11.4008 | 37.78
2020-12-20 | 44185 | 0 | 11.059 | 37.78
2020-12-20 00:30 | 44185.0208 | 0 | 10.7587 | 37.78
2020-12-20 01:00 | 44185.0417 | 0 | 10.5468 | 37.78
2020-12-20 01:30 | 44185.0625 | 0 | 10.4399 | 37.78
2020-12-20 02:00 | 44185.0833 | 0 | 10.441 | 37.78
2020-12-20 02:30 | 44185.1042 | 0 | 10.1743 | 37.78
2020-12-20 03:00 | 44185.125 | 0 | 10.0333 | 37.78
2020-12-20 03:30 | 44185.1458 | 0 | 10.0483 | 37.78
2020-12-20 04:00 | 44185.1667 | 0 | 10.2642 | 37.78
2020-12-20 04:30 | 44185.1875 | 0 | 10.6188 | 37.78
2020-12-20 05:00 | 44185.2083 | 0 | 10.9681 | 37.78
2020-12-20 05:30 | 44185.2292 | 0 | 11.3361 | 37.78
2020-12-20 06:00 | 44185.25 | 0 | 12.094 | 37.78
2020-12-20 06:30 | 44185.2708 | 0 | 12.7738 | 37.78
2020-12-20 07:00 | 44185.2917 | 0 | 13.3515 | 37.78
2020-12-20 07:30 | 44185.3125 | 0 | 13.5631 | 37.78
2020-12-20 08:00 | 44185.3333 | 0 | 14.2795 | 37.78
2020-12-20 08:30 | 44185.3542 | 0 | 16.087 | 37.78
2020-12-20 09:00 | 44185.375 | 0 | 16.2652 | 37.78
2020-12-20 09:30 | 44185.3958 | 0 | 16.3483 | 37.78
2020-12-20 10:00 | 44185.4167 | 0 | 16.5811 | 37.78
2020-12-20 10:30 | 44185.4375 | 0 | 15.0202 | 37.78
2020-12-20 11:00 | 44185.4583 | 0 | 15.9389 | 37.78
2020-12-20 11:30 | 44185.4792 | 0 | 16.6565 | 37.78
2020-12-20 12:00 | 44185.5 | 0 | 15.9739 | 37.78
2020-12-20 12:30 | 44185.5208 | 0 | 16.1366 | 37.78
2020-12-20 13:00 | 44185.5417 | 0 | 16.5053 | 37.78
2020-12-20 13:30 | 44185.5625 | 0 | 17.5348 | 37.78
2020-12-20 14:00 | 44185.5833 | 0 | 17.3019 | 37.78
2020-12-20 14:30 | 44185.6042 | 0 | 17.8919 | 37.78
2020-12-20 15:00 | 44185.625 | 0 | 18.3677 | 37.78
2020-12-20 15:30 | 44185.6458 | 0 | 19.3155 | 37.78
2020-12-20 16:00 | 44185.6667 | 0 | 18.5666 | 37.78
2020-12-20 16:30 | 44185.6875 | 0 | 19.5058 | 37.78
2020-12-20 17:00 | 44185.7083 | 0 | 18.7751 | 37.78
2020-12-20 17:30 | 44185.7292 | 0 | 18.5112 | 37.78
2020-12-20 18:00 | 44185.75 | 0 | 18.3809 | 37.78
2020-12-20 18:30 | 44185.7708 | 0 | 18.3917 | 37.78
2020-12-20 19:00 | 44185.7917 | 0 | 18.4318 | 37.78
2020-12-20 19:30 | 44185.8125 | 0 | 18.295 | 37.78
2020-12-20 20:00 | 44185.8333 | 0 | 18.1394 | 37.78
2020-12-20 20:30 | 44185.8542 | 0 | 17.3343 | 37.78
2020-12-20 21:00 | 44185.875 | 0 | 17.0274 | 37.78
2020-12-20 21:30 | 44185.8958 | 0 | 16.2609 | 37.78
2020-12-20 22:00 | 44185.9167 | 0 | 15.4797 | 37.78
2020-12-20 22:30 | 44185.9375 | 0 | 14.7049 | 37.78
2020-12-20 23:00 | 44185.9583 | 0 | 13.82 | 37.78
2020-12-20 23:30 | 44185.9792 | 0 | 13.3261 | 37.78
2020-12-21 | 44186 | 0 | 12.3956 | 37.78
2020-12-21 00:30 | 44186.0208 | 0 | 11.6851 | 37.78
2020-12-21 01:00 | 44186.0417 | 0 | 11.2685 | 37.78
2020-12-21 01:30 | 44186.0625 | 0 | 11.0485 | 37.78
2020-12-21 02:00 | 44186.0833 | 0 | 10.7493 | 37.78
2020-12-21 02:30 | 44186.1042 | 0 | 10.4172 | 37.78
2020-12-21 03:00 | 44186.125 | 0 | 10.2834 | 37.78
2020-12-21 03:30 | 44186.1458 | 0 | 10.2093 | 37.78
2020-12-21 04:00 | 44186.1667 | 0 | 10.696 | 37.78
2020-12-21 04:30 | 44186.1875 | 0 | 10.9774 | 37.78
2020-12-21 05:00 | 44186.2083 | 0 | 11.2353 | 37.78
2020-12-21 05:30 | 44186.2292 | 0 | 11.5462 | 37.78
2020-12-21 06:00 | 44186.25 | 0 | 12.1213 | 37.78
2020-12-21 06:30 | 44186.2708 | 0 | 12.9365 | 37.78
2020-12-21 07:00 | 44186.2917 | 0 | 13.5517 | 37.78
2020-12-21 07:30 | 44186.3125 | 0 | 13.2869 | 37.78
2020-12-21 08:00 | 44186.3333 | 0 | 12.9414 | 37.78
2020-12-21 08:30 | 44186.3542 | 0 | 13.7995 | 37.78
2020-12-21 09:00 | 44186.375 | 0 | 15.0545 | 37.78
2020-12-21 09:30 | 44186.3958 | 0 | 14.9101 | 37.78
2020-12-21 10:00 | 44186.4167 | 0 | 16.293 | 37.78
2020-12-21 10:30 | 44186.4375 | 0 | 17.3438 | 37.78
2020-12-21 11:00 | 44186.4583 | 0 | 17.4945 | 37.78
2020-12-21 11:30 | 44186.4792 | 0 | 17.9502 | 37.78
2020-12-21 12:00 | 44186.5 | 0 | 17.1316 | 37.78
2020-12-21 12:30 | 44186.5208 | 0 | 16.7909 | 37.78
2020-12-21 13:00 | 44186.5417 | 0 | 17.9522 | 37.78
2020-12-21 13:30 | 44186.5625 | 0 | 18.1173 | 37.78
2020-12-21 14:00 | 44186.5833 | 0 | 19.2088 | 37.78
2020-12-21 14:30 | 44186.6042 | 0 | 19.911 | 37.78
2020-12-21 15:00 | 44186.625 | 0 | 21.0166 | 37.78
2020-12-21 15:30 | 44186.6458 | 0 | 21.2671 | 37.78
2020-12-21 16:00 | 44186.6667 | 0 | 20.5392 | 37.78
2020-12-21 16:30 | 44186.6875 | 0 | 20.7728 | 37.78
2020-12-21 17:00 | 44186.7083 | 0 | 20.8077 | 37.78
2020-12-21 17:30 | 44186.7292 | 0 | 20.481 | 37.78
2020-12-21 18:00 | 44186.75 | 0 | 19.8789 | 37.78
2020-12-21 18:30 | 44186.7708 | 0 | 19.8179 | 37.78
2020-12-21 19:00 | 44186.7917 | 0 | 19.6748 | 37.78
2020-12-21 19:30 | 44186.8125 | 0 | 19.5797 | 37.78
2020-12-21 20:00 | 44186.8333 | 0 | 19.0756 | 37.78
2020-12-21 20:30 | 44186.8542 | 0 | 17.8371 | 37.78
2020-12-21 21:00 | 44186.875 | 0 | 17.151 | 37.78
2020-12-21 21:30 | 44186.8958 | 0 | 16.4129 | 37.78
2020-12-21 22:00 | 44186.9167 | 0 | 15.4085 | 37.78
2020-12-21 22:30 | 44186.9375 | 0 | 14.5274 | 37.78
2020-12-21 23:00 | 44186.9583 | 0 | 13.3638 | 37.78
2020-12-21 23:30 | 44186.9792 | 0 | 12.947 | 37.78
2020-12-22 | 44187 | 0 | 12.0499 | 37.78
2020-12-22 00:30 | 44187.0208 | 0 | 11.6528 | 37.78
2020-12-22 01:00 | 44187.0417 | 0 | 11.264 | 37.78
2020-12-22 01:30 | 44187.0625 | 0 | 10.8758 | 37.78
2020-12-22 02:00 | 44187.0833 | 0 | 10.6687 | 37.78
2020-12-22 02:30 | 44187.1042 | 0 | 10.5351 | 37.78
2020-12-22 03:00 | 44187.125 | 0 | 10.4218 | 37.78
2020-12-22 03:30 | 44187.1458 | 0 | 10.4459 | 37.78
2020-12-22 04:00 | 44187.1667 | 0 | 10.7559 | 37.78
2020-12-22 04:30 | 44187.1875 | 0 | 10.8567 | 37.78
2020-12-22 05:00 | 44187.2083 | 0 | 10.992 | 37.78
2020-12-22 05:30 | 44187.2292 | 0 | 11.0977 | 37.78
2020-12-22 06:00 | 44187.25 | 0 | 11.64 | 37.78
2020-12-22 06:30 | 44187.2708 | 0 | 11.7263 | 37.78
2020-12-22 07:00 | 44187.2917 | 0 | 12.2285 | 37.78
2020-12-22 07:30 | 44187.3125 | 0 | 12.5131 | 37.78
2020-12-22 08:00 | 44187.3333 | 0 | 12.3057 | 37.78
2020-12-22 08:30 | 44187.3542 | 0 | 12.6063 | 37.78
2020-12-22 09:00 | 44187.375 | 0 | 12.8689 | 37.78
2020-12-22 09:30 | 44187.3958 | 0 | 12.9813 | 37.78
2020-12-22 10:00 | 44187.4167 | 0 | 13.2205 | 37.78
2020-12-22 10:30 | 44187.4375 | 0 | 13.7448 | 37.78
2020-12-22 11:00 | 44187.4583 | 0 | 13.8924 | 37.78
2020-12-22 11:30 | 44187.4792 | 0 | 14.2792 | 37.78
2020-12-22 12:00 | 44187.5 | 0 | 14.6591 | 37.78
2020-12-22 12:30 | 44187.5208 | 0 | 15.2155 | 37.78
2020-12-22 13:00 | 44187.5417 | 0 | 15.3199 | 37.78
2020-12-22 13:30 | 44187.5625 | 0 | 15.9881 | 37.78
2020-12-22 14:00 | 44187.5833 | 0 | 16.2409 | 37.78
2020-12-22 14:30 | 44187.6042 | 0 | 16.8697 | 37.78
2020-12-22 15:00 | 44187.625 | 0 | 17.4224 | 37.78
2020-12-22 15:30 | 44187.6458 | 0 | 17.3911 | 37.78
2020-12-22 16:00 | 44187.6667 | 0 | 17.4852 | 37.78
2020-12-22 16:30 | 44187.6875 | 0 | 17.3045 | 37.78
2020-12-22 17:00 | 44187.7083 | 0 | 16.4513 | 37.78
2020-12-22 17:30 | 44187.7292 | 0 | 15.9794 | 37.78
2020-12-22 18:00 | 44187.75 | 0 | 15.5283 | 37.78
2020-12-22 18:30 | 44187.7708 | 0 | 15.7104 | 37.78
2020-12-22 19:00 | 44187.7917 | 0 | 15.4731 | 37.78
2020-12-22 19:30 | 44187.8125 | 0 | 15.0342 | 37.78
2020-12-22 20:00 | 44187.8333 | 0 | 14.59 | 37.78
2020-12-22 20:30 | 44187.8542 | 0 | 14.0016 | 37.78
2020-12-22 21:00 | 44187.875 | 0 | 13.5423 | 37.78
2020-12-22 21:30 | 44187.8958 | 0 | 13.2611 | 37.78
2020-12-22 22:00 | 44187.9167 | 0 | 12.9184 | 37.78
2020-12-22 22:30 | 44187.9375 | 0 | 12.3313 | 37.78
2020-12-22 23:00 | 44187.9583 | 0 | 11.4857 | 37.78
2020-12-22 23:30 | 44187.9792 | 0 | 11.0464 | 37.78
2020-12-23 | 44188 | 0 | 10.2537 | 37.78
2020-12-23 00:30 | 44188.0208 | 0 | 9.6128 | 37.78
2020-12-23 01:00 | 44188.0417 | 0 | 9.3272 | 37.78
2020-12-23 01:30 | 44188.0625 | 0 | 9.1099 | 37.78
2020-12-23 02:00 | 44188.0833 | 0 | 8.8525 | 37.78
2020-12-23 02:30 | 44188.1042 | 0 | 8.7938 | 37.78
2020-12-23 03:00 | 44188.125 | 0 | 8.6054 | 37.78
2020-12-23 03:30 | 44188.1458 | 0 | 8.792 | 37.78
2020-12-23 04:00 | 44188.1667 | 0 | 9.0412 | 37.78
2020-12-23 04:30 | 44188.1875 | 0 | 9.252 | 37.78
2020-12-23 05:00 | 44188.2083 | 0 | 9.5867 | 37.78
2020-12-23 05:30 | 44188.2292 | 0 | 9.9078 | 37.78
2020-12-23 06:00 | 44188.25 | 0 | 10.1199 | 37.78
2020-12-23 06:30 | 44188.2708 | 0 | 10.3405 | 37.78
2020-12-23 07:00 | 44188.2917 | 0 | 10.6493 | 37.78
2020-12-23 07:30 | 44188.3125 | 0 | 11.2822 | 37.78
2020-12-23 08:00 | 44188.3333 | 0 | 11.1128 | 37.78
2020-12-23 08:30 | 44188.3542 | 0 | 11.7802 | 37.78
2020-12-23 09:00 | 44188.375 | 0 | 13.0604 | 37.78
2020-12-23 09:30 | 44188.3958 | 0 | 12.8821 | 37.78
2020-12-23 10:00 | 44188.4167 | 0 | 13.2215 | 37.78
2020-12-23 10:30 | 44188.4375 | 0 | 12.7265 | 37.78
2020-12-23 11:00 | 44188.4583 | 0 | 12.3484 | 37.78
2020-12-23 11:30 | 44188.4792 | 0 | 11.7666 | 37.78
2020-12-23 12:00 | 44188.5 | 0 | 13.0019 | 37.78
2020-12-23 12:30 | 44188.5208 | 0 | 12.234 | 37.78
2020-12-23 13:00 | 44188.5417 | 0 | 13.2657 | 37.78
2020-12-23 13:30 | 44188.5625 | 0 | 14.0682 | 37.78
2020-12-23 14:00 | 44188.5833 | 0 | 12.878 | 37.78
2020-12-23 14:30 | 44188.6042 | 0 | 13.4145 | 37.78
2020-12-23 15:00 | 44188.625 | 0 | 13.8205 | 37.78
2020-12-23 15:30 | 44188.6458 | 0 | 13.7447 | 37.78
2020-12-23 16:00 | 44188.6667 | 0 | 13.722 | 37.78
2020-12-23 16:30 | 44188.6875 | 0 | 14.0818 | 37.78
2020-12-23 17:00 | 44188.7083 | 0 | 13.5227 | 37.78
2020-12-23 17:30 | 44188.7292 | 0 | 13.315 | 37.78
2020-12-23 18:00 | 44188.75 | 0 | 13.2354 | 37.78
2020-12-23 18:30 | 44188.7708 | 0 | 13.3747 | 37.78
2020-12-23 19:00 | 44188.7917 | 0 | 13.4156 | 37.78
2020-12-23 19:30 | 44188.8125 | 0 | 13.2135 | 37.78
2020-12-23 20:00 | 44188.8333 | 0 | 12.9234 | 37.78
2020-12-23 20:30 | 44188.8542 | 0 | 12.5343 | 37.78
2020-12-23 21:00 | 44188.875 | 0 | 12.1511 | 37.78
2020-12-23 21:30 | 44188.8958 | 0 | 12.021 | 37.78
2020-12-23 22:00 | 44188.9167 | 0 | 11.7233 | 37.78
2020-12-23 22:30 | 44188.9375 | 0 | 11.2332 | 37.78
2020-12-23 23:00 | 44188.9583 | 0 | 10.5942 | 37.78
2020-12-23 23:30 | 44188.9792 | 0 | 10.0501 | 37.78
2020-12-24 | 44189 | 0 | 9.3811 | 37.78
2020-12-24 00:30 | 44189.0208 | 0 | 8.9791 | 37.78
2020-12-24 01:00 | 44189.0417 | 0 | 8.8265 | 37.78
2020-12-24 01:30 | 44189.0625 | 0 | 8.7082 | 37.78
2020-12-24 02:00 | 44189.0833 | 0 | 8.6441 | 37.78
2020-12-24 02:30 | 44189.1042 | 0 | 8.5473 | 37.78
2020-12-24 03:00 | 44189.125 | 0 | 8.3047 | 37.78
2020-12-24 03:30 | 44189.1458 | 0 | 8.2451 | 37.78
2020-12-24 04:00 | 44189.1667 | 0 | 8.3375 | 37.78
2020-12-24 04:30 | 44189.1875 | 0 | 8.3229 | 37.78
2020-12-24 05:00 | 44189.2083 | 0 | 8.3017 | 37.78
2020-12-24 05:30 | 44189.2292 | 0 | 8.3438 | 37.78
2020-12-24 06:00 | 44189.25 | 0 | 8.6775 | 37.78
2020-12-24 06:30 | 44189.2708 | 0 | 8.6634 | 37.78
2020-12-24 07:00 | 44189.2917 | 0 | 9.3099 | 37.78
2020-12-24 07:30 | 44189.3125 | 0 | 8.8163 | 37.78
2020-12-24 08:00 | 44189.3333 | 0 | 8.455 | 37.78
2020-12-24 08:30 | 44189.3542 | 0 | 9.6369 | 37.78
2020-12-24 09:00 | 44189.375 | 0 | 8.8558 | 37.78
2020-12-24 09:30 | 44189.3958 | 0 | 10.3872 | 37.78
2020-12-24 10:00 | 44189.4167 | 0 | 11.0125 | 37.78
2020-12-24 10:30 | 44189.4375 | 0 | 10.4392 | 37.78
2020-12-24 11:00 | 44189.4583 | 0 | 12.0588 | 37.78
2020-12-24 11:30 | 44189.4792 | 0 | 11.6273 | 37.78
2020-12-24 12:00 | 44189.5 | 0 | 9.4115 | 37.78
2020-12-24 12:30 | 44189.5208 | 0 | 8.7559 | 37.78
2020-12-24 13:00 | 44189.5417 | 0 | 10.6808 | 37.78
2020-12-24 13:30 | 44189.5625 | 0 | 11.1801 | 37.78
2020-12-24 14:00 | 44189.5833 | 0 | 9.1872 | 37.78
2020-12-24 14:30 | 44189.6042 | 0 | 9.7706 | 37.78
2020-12-24 15:00 | 44189.625 | 0 | 9.9386 | 37.78
2020-12-24 15:30 | 44189.6458 | 0 | 10.5944 | 37.78
2020-12-24 16:00 | 44189.6667 | 0 | 11.0475 | 37.78
2020-12-24 16:30 | 44189.6875 | 0 | 11.3744 | 37.78
2020-12-24 17:00 | 44189.7083 | 0 | 11.5643 | 37.78
2020-12-24 17:30 | 44189.7292 | 0 | 11.3627 | 37.78
2020-12-24 18:00 | 44189.75 | 0 | 11.3223 | 37.78
2020-12-24 18:30 | 44189.7708 | 0 | 11.4034 | 37.78
2020-12-24 19:00 | 44189.7917 | 0 | 11.5399 | 37.78
2020-12-24 19:30 | 44189.8125 | 0 | 11.561 | 37.78
2020-12-24 20:00 | 44189.8333 | 0 | 11.4995 | 37.78
2020-12-24 20:30 | 44189.8542 | 0 | 11.1065 | 37.78
2020-12-24 21:00 | 44189.875 | 0 | 10.8417 | 37.78
2020-12-24 21:30 | 44189.8958 | 0 | 10.5599 | 37.78
2020-12-24 22:00 | 44189.9167 | 0 | 10.2178 | 37.78
2020-12-24 22:30 | 44189.9375 | 0 | 9.7094 | 37.78
2020-12-24 23:00 | 44189.9583 | 0 | 9.1931 | 37.78
2020-12-24 23:30 | 44189.9792 | 0 | 8.8312 | 37.78
2020-12-25 | 44190 | 0 | 8.5262 | 37.78
2020-12-25 00:30 | 44190.0208 | 0 | 8.2672 | 37.78
2020-12-25 01:00 | 44190.0417 | 0 | 8.1083 | 37.78
2020-12-25 01:30 | 44190.0625 | 0 | 8.0128 | 37.78
2020-12-25 02:00 | 44190.0833 | 0 | 8.0127 | 37.78
2020-12-25 02:30 | 44190.1042 | 0 | 7.8418 | 37.78
2020-12-25 03:00 | 44190.125 | 0 | 7.7403 | 37.78
2020-12-25 03:30 | 44190.1458 | 0 | 7.6763 | 37.78
2020-12-25 04:00 | 44190.1667 | 0 | 7.5012 | 37.78
2020-12-25 04:30 | 44190.1875 | 0 | 7.4771 | 37.78
2020-12-25 05:00 | 44190.2083 | 0 | 7.4248 | 37.78
2020-12-25 05:30 | 44190.2292 | 0 | 7.3756 | 37.78
2020-12-25 06:00 | 44190.25 | 0 | 7.6232 | 37.78
2020-12-25 06:30 | 44190.2708 | 0 | 8.1705 | 37.78
2020-12-25 07:00 | 44190.2917 | 0 | 7.3525 | 37.78
2020-12-25 07:30 | 44190.3125 | 0 | 6.8498 | 37.78
2020-12-25 08:00 | 44190.3333 | 0 | 8.5872 | 37.78
2020-12-25 08:30 | 44190.3542 | 0 | 8.375 | 37.78
2020-12-25 09:00 | 44190.375 | 0 | 7.3876 | 37.78
2020-12-25 09:30 | 44190.3958 | 0 | 8.9583 | 37.78
2020-12-25 10:00 | 44190.4167 | 0 | 8.7989 | 37.78
2020-12-25 10:30 | 44190.4375 | 0 | 7.2717 | 37.78
2020-12-25 11:00 | 44190.4583 | 0 | 7.6854 | 37.78
2020-12-25 11:30 | 44190.4792 | 0 | 8.9891 | 37.78
2020-12-25 12:00 | 44190.5 | 0 | 8.434 | 37.78
2020-12-25 12:30 | 44190.5208 | 0 | 8.2439 | 37.78
2020-12-25 13:00 | 44190.5417 | 0 | 7.6207 | 37.78
2020-12-25 13:30 | 44190.5625 | 0 | 8.2788 | 37.78
2020-12-25 14:00 | 44190.5833 | 0 | 8.228 | 37.78
2020-12-25 14:30 | 44190.6042 | 0 | 9.2282 | 37.78
2020-12-25 15:00 | 44190.625 | 0 | 9.703 | 37.78
2020-12-25 15:30 | 44190.6458 | 0 | 9.9467 | 37.78
2020-12-25 16:00 | 44190.6667 | 0 | 10.1812 | 37.78
2020-12-25 16:30 | 44190.6875 | 0 | 10.7192 | 37.78
2020-12-25 17:00 | 44190.7083 | 0 | 11.0593 | 37.78
2020-12-25 17:30 | 44190.7292 | 0 | 11.396 | 37.78
2020-12-25 18:00 | 44190.75 | 0 | 11.6665 | 37.78
2020-12-25 18:30 | 44190.7708 | 0 | 11.7726 | 37.78
2020-12-25 19:00 | 44190.7917 | 0 | 11.9405 | 37.78
2020-12-25 19:30 | 44190.8125 | 0 | 11.9451 | 37.78
2020-12-25 20:00 | 44190.8333 | 0 | 11.7136 | 37.78
2020-12-25 20:30 | 44190.8542 | 0 | 11.191 | 37.78
2020-12-25 21:00 | 44190.875 | 0 | 10.831 | 37.78
2020-12-25 21:30 | 44190.8958 | 0 | 10.5513 | 37.78
2020-12-25 22:00 | 44190.9167 | 0 | 10.1211 | 37.78
2020-12-25 22:30 | 44190.9375 | 0 | 9.5336 | 37.78
2020-12-25 23:00 | 44190.9583 | 0 | 9.1858 | 37.78
2020-12-25 23:30 | 44190.9792 | 0 | 8.7042 | 37.78
2020-12-26 | 44191 | 0 | 8.2657 | 37.78
2020-12-26 00:30 | 44191.0208 | 0 | 8.0398 | 37.78
2020-12-26 01:00 | 44191.0417 | 0 | 7.8535 | 37.78
2020-12-26 01:30 | 44191.0625 | 0 | 7.6569 | 37.78
2020-12-26 02:00 | 44191.0833 | 0 | 7.5801 | 37.78
2020-12-26 02:30 | 44191.1042 | 0 | 7.5065 | 37.78
2020-12-26 03:00 | 44191.125 | 0 | 7.3668 | 37.78
2020-12-26 03:30 | 44191.1458 | 0 | 7.3236 | 37.78
2020-12-26 04:00 | 44191.1667 | 0 | 7.3088 | 37.78
2020-12-26 04:30 | 44191.1875 | 0 | 7.2029 | 37.78
2020-12-26 05:00 | 44191.2083 | 0 | 7.1508 | 37.78
2020-12-26 05:30 | 44191.2292 | 0 | 7.0599 | 37.78
2020-12-26 06:00 | 44191.25 | 0 | 6.9362 | 37.78
2020-12-26 06:30 | 44191.2708 | 0 | 6.7912 | 37.78
2020-12-26 07:00 | 44191.2917 | 0 | 6.8131 | 37.78
2020-12-26 07:30 | 44191.3125 | 0 | 6.8672 | 37.78
2020-12-26 08:00 | 44191.3333 | 0 | 7.6417 | 37.78
2020-12-26 08:30 | 44191.3542 | 0 | 7.1582 | 37.78
2020-12-26 09:00 | 44191.375 | 0 | 8.1174 | 37.78
2020-12-26 09:30 | 44191.3958 | 0 | 7.9925 | 37.78
2020-12-26 10:00 | 44191.4167 | 0 | 7.7887 | 37.78
2020-12-26 10:30 | 44191.4375 | 0 | 8.3758 | 37.78
2020-12-26 11:00 | 44191.4583 | 0 | 8.8389 | 37.78
2020-12-26 11:30 | 44191.4792 | 0 | 8.622 | 37.78
2020-12-26 12:00 | 44191.5 | 0 | 8.5704 | 37.78
2020-12-26 12:30 | 44191.5208 | 0 | 8.1616 | 37.78
2020-12-26 13:00 | 44191.5417 | 0 | 8.0474 | 37.78
2020-12-26 13:30 | 44191.5625 | 0 | 8.9304 | 37.78
2020-12-26 14:00 | 44191.5833 | 0 | 9.2832 | 37.78
2020-12-26 14:30 | 44191.6042 | 0 | 9.6763 | 37.78
2020-12-26 15:00 | 44191.625 | 0 | 10.4075 | 37.78
2020-12-26 15:30 | 44191.6458 | 0 | 10.8834 | 37.78
2020-12-26 16:00 | 44191.6667 | 0 | 11.2725 | 37.78
2020-12-26 16:30 | 44191.6875 | 0 | 11.768 | 37.78
2020-12-26 17:00 | 44191.7083 | 0 | 12.2009 | 37.78
2020-12-26 17:30 | 44191.7292 | 0 | 12.1922 | 37.78
2020-12-26 18:00 | 44191.75 | 0 | 12.2696 | 37.78
2020-12-26 18:30 | 44191.7708 | 0 | 12.4932 | 37.78
2020-12-26 19:00 | 44191.7917 | 0 | 12.5539 | 37.78
2020-12-26 19:30 | 44191.8125 | 0 | 12.4838 | 37.78
2020-12-26 20:00 | 44191.8333 | 0 | 12.3944 | 37.78
2020-12-26 20:30 | 44191.8542 | 0 | 11.7374 | 37.78
2020-12-26 21:00 | 44191.875 | 0 | 11.4799 | 37.78
2020-12-26 21:30 | 44191.8958 | 0 | 11.1349 | 37.78
2020-12-26 22:00 | 44191.9167 | 0 | 10.7324 | 37.78
2020-12-26 22:30 | 44191.9375 | 0 | 10.264 | 37.78
2020-12-26 23:00 | 44191.9583 | 0 | 9.79 | 37.78
2020-12-26 23:30 | 44191.9792 | 0 | 9.208 | 37.78
2020-12-27 | 44192 | 0 | 8.8042 | 37.78
2020-12-27 00:30 | 44192.0208 | 0 | 8.522 | 37.78
2020-12-27 01:00 | 44192.0417 | 0 | 8.2025 | 37.78
2020-12-27 01:30 | 44192.0625 | 0 | 8.1781 | 37.78
2020-12-27 02:00 | 44192.0833 | 0 | 8.2081 | 37.78
2020-12-27 02:30 | 44192.1042 | 0 | 8.0499 | 37.78
2020-12-27 03:00 | 44192.125 | 0 | 7.9013 | 37.78
2020-12-27 03:30 | 44192.1458 | 0 | 7.9117 | 37.78
2020-12-27 04:00 | 44192.1667 | 0 | 7.888 | 37.78
2020-12-27 04:30 | 44192.1875 | 0 | 7.934 | 37.78
2020-12-27 05:00 | 44192.2083 | 0 | 7.9503 | 37.78
2020-12-27 05:30 | 44192.2292 | 0 | 7.8584 | 37.78
2020-12-27 06:00 | 44192.25 | 0 | 8.0753 | 37.78
2020-12-27 06:30 | 44192.2708 | 0 | 8.0591 | 37.78
2020-12-27 07:00 | 44192.2917 | 0 | 8.2368 | 37.78
2020-12-27 07:30 | 44192.3125 | 0 | 8.5229 | 37.78
2020-12-27 08:00 | 44192.3333 | 0 | 8.6706 | 37.78
2020-12-27 08:30 | 44192.3542 | 0 | 8.8591 | 37.78
2020-12-27 09:00 | 44192.375 | 0 | 8.7499 | 37.78
2020-12-27 09:30 | 44192.3958 | 0 | 8.8078 | 37.78
2020-12-27 10:00 | 44192.4167 | 0 | 8.6844 | 37.78
2020-12-27 10:30 | 44192.4375 | 0 | 8.8201 | 37.78
2020-12-27 11:00 | 44192.4583 | 0 | 8.7783 | 37.78
2020-12-27 11:30 | 44192.4792 | 0 | 9.0224 | 37.78
2020-12-27 12:00 | 44192.5 | 0 | 9.0701 | 37.78
2020-12-27 12:30 | 44192.5208 | 0 | 9.6562 | 37.78
2020-12-27 13:00 | 44192.5417 | 0 | 9.8037 | 37.78
2020-12-27 13:30 | 44192.5625 | 0 | 9.8461 | 37.78
2020-12-27 14:00 | 44192.5833 | 0 | 10.5102 | 37.78
2020-12-27 14:30 | 44192.6042 | 0 | 10.7287 | 37.78
2020-12-27 15:00 | 44192.625 | 0 | 11.1161 | 37.78
2020-12-27 15:30 | 44192.6458 | 0 | 11.7399 | 37.78
2020-12-27 16:00 | 44192.6667 | 0 | 12.7133 | 37.78
2020-12-27 16:30 | 44192.6875 | 0 | 12.6732 | 37.78
2020-12-27 17:00 | 44192.7083 | 0 | 12.9971 | 37.78
2020-12-27 17:30 | 44192.7292 | 0 | 13.1733 | 37.78
2020-12-27 18:00 | 44192.75 | 0 | 13.2031 | 37.78
2020-12-27 18:30 | 44192.7708 | 0 | 13.6723 | 37.78
2020-12-27 19:00 | 44192.7917 | 0 | 13.8493 | 37.78
2020-12-27 19:30 | 44192.8125 | 0 | 13.6403 | 37.78
2020-12-27 20:00 | 44192.8333 | 0 | 13.3223 | 37.78
2020-12-27 20:30 | 44192.8542 | 0 | 12.8695 | 37.78
2020-12-27 21:00 | 44192.875 | 0 | 12.3693 | 37.78
2020-12-27 21:30 | 44192.8958 | 0 | 12.1307 | 37.78
2020-12-27 22:00 | 44192.9167 | 0 | 11.7279 | 37.78
2020-12-27 22:30 | 44192.9375 | 0 | 11.072 | 37.78
2020-12-27 23:00 | 44192.9583 | 0 | 10.4964 | 37.78
2020-12-27 23:30 | 44192.9792 | 0 | 10.0389 | 37.78
2020-12-28 | 44193 | 0 | 9.4688 | 37.78
2020-12-28 00:30 | 44193.0208 | 0 | 9.171 | 37.78
2020-12-28 01:00 | 44193.0417 | 0 | 8.8627 | 37.78
2020-12-28 01:30 | 44193.0625 | 0 | 8.778 | 37.78
2020-12-28 02:00 | 44193.0833 | 0 | 8.6199 | 37.78
2020-12-28 02:30 | 44193.1042 | 0 | 8.6678 | 37.78
2020-12-28 03:00 | 44193.125 | 0 | 8.6399 | 37.78
2020-12-28 03:30 | 44193.1458 | 0 | 8.7059 | 37.78
2020-12-28 04:00 | 44193.1667 | 0 | 8.6802 | 37.78
2020-12-28 04:30 | 44193.1875 | 0 | 8.9795 | 37.78
2020-12-28 05:00 | 44193.2083 | 0 | 9.0105 | 37.78
2020-12-28 05:30 | 44193.2292 | 0 | 9.2253 | 37.78
2020-12-28 06:00 | 44193.25 | 0 | 9.7565 | 37.78
2020-12-28 06:30 | 44193.2708 | 0 | 9.9769 | 37.78
2020-12-28 07:00 | 44193.2917 | 0 | 10.5849 | 37.78
2020-12-28 07:30 | 44193.3125 | 0 | 11.1626 | 37.78
2020-12-28 08:00 | 44193.3333 | 0 | 12.0046 | 37.78
2020-12-28 08:30 | 44193.3542 | 0 | 12.4446 | 37.78
2020-12-28 09:00 | 44193.375 | 0 | 11.8369 | 37.78
2020-12-28 09:30 | 44193.3958 | 0 | 12.8677 | 37.78
2020-12-28 10:00 | 44193.4167 | 0 | 13.4147 | 37.78
2020-12-28 10:30 | 44193.4375 | 0 | 12.9591 | 37.78
2020-12-28 11:00 | 44193.4583 | 0 | 12.6544 | 37.78
2020-12-28 11:30 | 44193.4792 | 0 | 12.3905 | 37.78
2020-12-28 12:00 | 44193.5 | 0 | 12.5928 | 37.78
2020-12-28 12:30 | 44193.5208 | 0 | 13.0331 | 37.78
2020-12-28 13:00 | 44193.5417 | 0 | 13.1123 | 37.78
2020-12-28 13:30 | 44193.5625 | 0 | 13.4684 | 37.78
2020-12-28 14:00 | 44193.5833 | 0 | 14.2938 | 37.78
2020-12-28 14:30 | 44193.6042 | 0 | 15.0141 | 37.78
2020-12-28 15:00 | 44193.625 | 0 | 15.352 | 37.78
2020-12-28 15:30 | 44193.6458 | 0 | 15.5096 | 37.78
2020-12-28 16:00 | 44193.6667 | 0 | 15.7802 | 37.78
2020-12-28 16:30 | 44193.6875 | 0 | 15.8219 | 37.78
2020-12-28 17:00 | 44193.7083 | 0 | 15.5985 | 37.78
2020-12-28 17:30 | 44193.7292 | 0 | 15.6866 | 37.78
2020-12-28 18:00 | 44193.75 | 0 | 15.6196 | 37.78
2020-12-28 18:30 | 44193.7708 | 0 | 16.1433 | 37.78
2020-12-28 19:00 | 44193.7917 | 0 | 16.093 | 37.78
2020-12-28 19:30 | 44193.8125 | 0 | 16.1079 | 37.78
2020-12-28 20:00 | 44193.8333 | 0 | 15.7802 | 37.78
2020-12-28 20:30 | 44193.8542 | 0 | 15.2156 | 37.78
2020-12-28 21:00 | 44193.875 | 0 | 14.9017 | 37.78
2020-12-28 21:30 | 44193.8958 | 0 | 14.2992 | 37.78
2020-12-28 22:00 | 44193.9167 | 0 | 13.9054 | 37.78
2020-12-28 22:30 | 44193.9375 | 0 | 12.967 | 37.78
2020-12-28 23:00 | 44193.9583 | 0 | 12.3797 | 37.78
2020-12-28 23:30 | 44193.9792 | 0 | 11.9175 | 37.78
2020-12-29 | 44194 | 0 | 11.0886 | 37.78
2020-12-29 00:30 | 44194.0208 | 0 | 10.7148 | 37.78
2020-12-29 01:00 | 44194.0417 | 0 | 10.4037 | 37.78
2020-12-29 01:30 | 44194.0625 | 0 | 10.2774 | 37.78
2020-12-29 02:00 | 44194.0833 | 0 | 10.2044 | 37.78
2020-12-29 02:30 | 44194.1042 | 0 | 10.1103 | 37.78
2020-12-29 03:00 | 44194.125 | 0 | 10.0005 | 37.78
2020-12-29 03:30 | 44194.1458 | 0 | 9.9396 | 37.78
2020-12-29 04:00 | 44194.1667 | 0 | 10.1362 | 37.78
2020-12-29 04:30 | 44194.1875 | 0 | 10.3238 | 37.78
2020-12-29 05:00 | 44194.2083 | 0 | 10.501 | 37.78
2020-12-29 05:30 | 44194.2292 | 0 | 10.7381 | 37.78
2020-12-29 06:00 | 44194.25 | 0 | 11.1712 | 37.78
2020-12-29 06:30 | 44194.2708 | 0 | 11.3543 | 37.78
2020-12-29 07:00 | 44194.2917 | 0 | 11.8224 | 37.78
2020-12-29 07:30 | 44194.3125 | 0 | 12.2197 | 37.78
2020-12-29 08:00 | 44194.3333 | 0 | 13.0259 | 37.78
2020-12-29 08:30 | 44194.3542 | 0 | 13.3382 | 37.78
2020-12-29 09:00 | 44194.375 | 0 | 13.2404 | 37.78
2020-12-29 09:30 | 44194.3958 | 0 | 13.3518 | 37.78
2020-12-29 10:00 | 44194.4167 | 0 | 13.5206 | 37.78
2020-12-29 10:30 | 44194.4375 | 0 | 13.623 | 37.78
2020-12-29 11:00 | 44194.4583 | 0 | 13.561 | 37.78
2020-12-29 11:30 | 44194.4792 | 0 | 12.892 | 37.78
2020-12-29 12:00 | 44194.5 | 0 | 12.8163 | 37.78
2020-12-29 12:30 | 44194.5208 | 0 | 12.615 | 37.78
2020-12-29 13:00 | 44194.5417 | 0 | 12.6419 | 37.78
2020-12-29 13:30 | 44194.5625 | 0 | 13.1157 | 37.78
2020-12-29 14:00 | 44194.5833 | 0 | 13.1652 | 37.78
2020-12-29 14:30 | 44194.6042 | 0 | 13.0049 | 37.78
2020-12-29 15:00 | 44194.625 | 0 | 13.1659 | 37.78
2020-12-29 15:30 | 44194.6458 | 0 | 13.1632 | 37.78
2020-12-29 16:00 | 44194.6667 | 0 | 13.4383 | 37.78
2020-12-29 16:30 | 44194.6875 | 0 | 13.6277 | 37.78
2020-12-29 17:00 | 44194.7083 | 0 | 13.8966 | 37.78
2020-12-29 17:30 | 44194.7292 | 0 | 13.7211 | 37.78
2020-12-29 18:00 | 44194.75 | 0 | 13.5171 | 37.78
2020-12-29 18:30 | 44194.7708 | 0 | 13.8408 | 37.78
2020-12-29 19:00 | 44194.7917 | 0 | 13.7672 | 37.78
2020-12-29 19:30 | 44194.8125 | 0 | 13.7375 | 37.78
2020-12-29 20:00 | 44194.8333 | 0 | 13.56 | 37.78
2020-12-29 20:30 | 44194.8542 | 0 | 13.1955 | 37.78
2020-12-29 21:00 | 44194.875 | 0 | 12.8417 | 37.78
2020-12-29 21:30 | 44194.8958 | 0 | 12.454 | 37.78
2020-12-29 22:00 | 44194.9167 | 0 | 11.9313 | 37.78
2020-12-29 22:30 | 44194.9375 | 0 | 11.4876 | 37.78
2020-12-29 23:00 | 44194.9583 | 0 | 11.2027 | 37.78
2020-12-29 23:30 | 44194.9792 | 0 | 10.547 | 37.78
2020-12-30 | 44195 | 0 | 9.9032 | 37.78
2020-12-30 00:30 | 44195.0208 | 0 | 9.5955 | 37.78
2020-12-30 01:00 | 44195.0417 | 0 | 9.2474 | 37.78
2020-12-30 01:30 | 44195.0625 | 0 | 9.0936 | 37.78
2020-12-30 02:00 | 44195.0833 | 0 | 9.0538 | 37.78
2020-12-30 02:30 | 44195.1042 | 0 | 8.8552 | 37.78
2020-12-30 03:00 | 44195.125 | 0 | 8.808 | 37.78
2020-12-30 03:30 | 44195.1458 | 0 | 8.7546 | 37.78
2020-12-30 04:00 | 44195.1667 | 0 | 9.033 | 37.78
2020-12-30 04:30 | 44195.1875 | 0 | 9.3397 | 37.78
2020-12-30 05:00 | 44195.2083 | 0 | 9.4946 | 37.78
2020-12-30 05:30 | 44195.2292 | 0 | 9.6392 | 37.78
2020-12-30 06:00 | 44195.25 | 0 | 10.032 | 37.78
2020-12-30 06:30 | 44195.2708 | 0 | 10.4915 | 37.78
2020-12-30 07:00 | 44195.2917 | 0 | 10.2189 | 37.78
2020-12-30 07:30 | 44195.3125 | 0 | 10.3127 | 37.78
2020-12-30 08:00 | 44195.3333 | 0 | 11.4939 | 37.78
2020-12-30 08:30 | 44195.3542 | 0 | 11.8595 | 37.78
2020-12-30 09:00 | 44195.375 | 0 | 12.1836 | 37.78
2020-12-30 09:30 | 44195.3958 | 0 | 10.8837 | 37.78
2020-12-30 10:00 | 44195.4167 | 0 | 11.9606 | 37.78
2020-12-30 10:30 | 44195.4375 | 0 | 11.9089 | 37.78
2020-12-30 11:00 | 44195.4583 | 0 | 12.5507 | 37.78
2020-12-30 11:30 | 44195.4792 | 0 | 12.2934 | 37.78
2020-12-30 12:00 | 44195.5 | 0 | 12.3313 | 37.78
2020-12-30 12:30 | 44195.5208 | 0 | 13.5794 | 37.78
2020-12-30 13:00 | 44195.5417 | 0 | 11.9393 | 37.78
2020-12-30 13:30 | 44195.5625 | 0 | 12.5662 | 37.78
2020-12-30 14:00 | 44195.5833 | 0 | 13.4071 | 37.78
2020-12-30 14:30 | 44195.6042 | 0 | 13.5647 | 37.78
2020-12-30 15:00 | 44195.625 | 0 | 13.8507 | 37.78
2020-12-30 15:30 | 44195.6458 | 0 | 14.0256 | 37.78
2020-12-30 16:00 | 44195.6667 | 0 | 14.1937 | 37.78
2020-12-30 16:30 | 44195.6875 | 0 | 14.8481 | 37.78
2020-12-30 17:00 | 44195.7083 | 0 | 15.0227 | 37.78
2020-12-30 17:30 | 44195.7292 | 0 | 15.0161 | 37.78
2020-12-30 18:00 | 44195.75 | 0 | 14.5466 | 37.78
2020-12-30 18:30 | 44195.7708 | 0 | 14.5223 | 37.78
2020-12-30 19:00 | 44195.7917 | 0 | 14.4014 | 37.78
2020-12-30 19:30 | 44195.8125 | 0 | 14.1186 | 37.78
2020-12-30 20:00 | 44195.8333 | 0 | 13.8367 | 37.78
2020-12-30 20:30 | 44195.8542 | 0 | 13.4661 | 37.78
2020-12-30 21:00 | 44195.875 | 0 | 12.9462 | 37.78
2020-12-30 21:30 | 44195.8958 | 0 | 12.5001 | 37.78
2020-12-30 22:00 | 44195.9167 | 0 | 12.3244 | 37.78
2020-12-30 22:30 | 44195.9375 | 0 | 11.7862 | 37.78
2020-12-30 23:00 | 44195.9583 | 0 | 11.2567 | 37.78
2020-12-30 23:30 | 44195.9792 | 0 | 10.9278 | 37.78
2020-12-31 | 44196 | 0 | 10.1809 | 37.78
2020-12-31 00:30 | 44196.0208 | 0 | 9.9348 | 37.78
2020-12-31 01:00 | 44196.0417 | 0 | 9.8653 | 37.78
2020-12-31 01:30 | 44196.0625 | 0 | 9.6671 | 37.78
2020-12-31 02:00 | 44196.0833 | 0 | 9.5404 | 37.78
2020-12-31 02:30 | 44196.1042 | 0 | 9.3008 | 37.78
2020-12-31 03:00 | 44196.125 | 0 | 9.1605 | 37.78
2020-12-31 03:30 | 44196.1458 | 0 | 8.9188 | 37.78
2020-12-31 04:00 | 44196.1667 | 0 | 9.0194 | 37.78
2020-12-31 04:30 | 44196.1875 | 0 | 8.7811 | 37.78
2020-12-31 05:00 | 44196.2083 | 0 | 8.7544 | 37.78
2020-12-31 05:30 | 44196.2292 | 0 | 8.323 | 37.78
2020-12-31 06:00 | 44196.25 | 0 | 8.4031 | 37.78
2020-12-31 06:30 | 44196.2708 | 0 | 8.1953 | 37.78
2020-12-31 07:00 | 44196.2917 | 0 | 9.2446 | 37.78
2020-12-31 07:30 | 44196.3125 | 0 | 8.7369 | 37.78
2020-12-31 08:00 | 44196.3333 | 0 | 9.5857 | 37.78
2020-12-31 08:30 | 44196.3542 | 0 | 9.8828 | 37.78
2020-12-31 09:00 | 44196.375 | 0 | 9.0091 | 37.78
2020-12-31 09:30 | 44196.3958 | 0 | 8.4402 | 37.78
2020-12-31 10:00 | 44196.4167 | 0 | 8.4904 | 37.78
2020-12-31 10:30 | 44196.4375 | 0 | 8.6451 | 37.78
2020-12-31 11:00 | 44196.4583 | 0 | 10.2886 | 37.78
2020-12-31 11:30 | 44196.4792 | 0 | 9.3571 | 37.78
2020-12-31 12:00 | 44196.5 | 0 | 10.9794 | 37.78
2020-12-31 12:30 | 44196.5208 | 0 | 11.0129 | 37.78
2020-12-31 13:00 | 44196.5417 | 0 | 10.8278 | 37.78
2020-12-31 13:30 | 44196.5625 | 0 | 11.2086 | 37.78
2020-12-31 14:00 | 44196.5833 | 0 | 12.1865 | 37.78
2020-12-31 14:30 | 44196.6042 | 0 | 11.8854 | 37.78
2020-12-31 15:00 | 44196.625 | 0 | 11.2813 | 37.78
2020-12-31 15:30 | 44196.6458 | 0 | 11.6602 | 37.78
2020-12-31 16:00 | 44196.6667 | 0 | 11.2292 | 37.78
2020-12-31 16:30 | 44196.6875 | 0 | 12.1074 | 37.78
2020-12-31 17:00 | 44196.7083 | 0 | 12.1233 | 37.78
2020-12-31 17:30 | 44196.7292 | 0 | 12.271 | 37.78
2020-12-31 18:00 | 44196.75 | 0 | 12.4646 | 37.78
2020-12-31 18:30 | 44196.7708 | 0 | 12.9539 | 37.78
2020-12-31 19:00 | 44196.7917 | 0 | 13.0094 | 37.78
2020-12-31 19:30 | 44196.8125 | 0 | 13.0629 | 37.78
2020-12-31 20:00 | 44196.8333 | 0 | 12.6717 | 37.78
2020-12-31 20:30 | 44196.8542 | 0 | 12.1472 | 37.78
2020-12-31 21:00 | 44196.875 | 0 | 11.6235 | 37.78
2020-12-31 21:30 | 44196.8958 | 0 | 11.3551 | 37.78
2020-12-31 22:00 | 44196.9167 | 0 | 10.9252 | 37.78
2020-12-31 22:30 | 44196.9375 | 0 | 10.2481 | 37.78
2020-12-31 23:00 | 44196.9583 | 0 | 9.7561 | 37.78
2020-12-31 23:30 | 44196.9792 | 0 | 9.3243 | 37.78
2021-01-01 | 44197 | 0 | 8.8379 | 37.78
2021-01-01 00:30 | 44197.0208 | 0 | 8.5411 | 37.78
2021-01-01 01:00 | 44197.0417 | 0 | 8.3494 | 37.78
2021-01-01 01:30 | 44197.0625 | 0 | 8.1884 | 37.78
2021-01-01 02:00 | 44197.0833 | 0 | 8.2605 | 37.78
2021-01-01 02:30 | 44197.1042 | 0 | 8.2407 | 37.78
2021-01-01 03:00 | 44197.125 | 0 | 8.1734 | 37.78
2021-01-01 03:30 | 44197.1458 | 0 | 8.0768 | 37.78
2021-01-01 04:00 | 44197.1667 | 0 | 8.1189 | 37.78
2021-01-01 04:30 | 44197.1875 | 0 | 8.3094 | 37.78
2021-01-01 05:00 | 44197.2083 | 0 | 8.4045 | 37.78
2021-01-01 05:30 | 44197.2292 | 0 | 8.3052 | 37.78
2021-01-01 06:00 | 44197.25 | 0 | 8.6234 | 37.78
2021-01-01 06:30 | 44197.2708 | 0 | 8.4165 | 37.78
2021-01-01 07:00 | 44197.2917 | 0 | 7.9088 | 37.78
2021-01-01 07:30 | 44197.3125 | 0 | 8.6188 | 37.78
2021-01-01 08:00 | 44197.3333 | 0 | 9.5006 | 37.78
2021-01-01 08:30 | 44197.3542 | 0 | 10.7363 | 37.78
2021-01-01 09:00 | 44197.375 | 0 | 10.6144 | 37.78
2021-01-01 09:30 | 44197.3958 | 0 | 9.3773 | 37.78
2021-01-01 10:00 | 44197.4167 | 0 | 9.8262 | 37.78
2021-01-01 10:30 | 44197.4375 | 0 | 9.8619 | 37.78
2021-01-01 11:00 | 44197.4583 | 0 | 10.6419 | 37.78
2021-01-01 11:30 | 44197.4792 | 0 | 11.0924 | 37.78
2021-01-01 12:00 | 44197.5 | 0 | 10.4106 | 37.78
2021-01-01 12:30 | 44197.5208 | 0 | 8.6049 | 37.78
2021-01-01 13:00 | 44197.5417 | 0 | 9.3373 | 37.78
2021-01-01 13:30 | 44197.5625 | 0 | 9.7099 | 37.78
2021-01-01 14:00 | 44197.5833 | 0 | 10.3711 | 37.78
2021-01-01 14:30 | 44197.6042 | 0 | 10.6515 | 37.78
2021-01-01 15:00 | 44197.625 | 0 | 11.3019 | 37.78
2021-01-01 15:30 | 44197.6458 | 0 | 11.9242 | 37.78
2021-01-01 16:00 | 44197.6667 | 0 | 12.6589 | 37.78
2021-01-01 16:30 | 44197.6875 | 0 | 12.9528 | 37.78
2021-01-01 17:00 | 44197.7083 | 0 | 12.299 | 37.78
2021-01-01 17:30 | 44197.7292 | 0 | 12.0687 | 37.78
2021-01-01 18:00 | 44197.75 | 0 | 12.4117 | 37.78
2021-01-01 18:30 | 44197.7708 | 0 | 13.8398 | 37.78
2021-01-01 19:00 | 44197.7917 | 0 | 13.885 | 37.78
2021-01-01 19:30 | 44197.8125 | 0 | 13.4487 | 37.78
2021-01-01 20:00 | 44197.8333 | 0 | 13.2325 | 37.78
2021-01-01 20:30 | 44197.8542 | 0 | 12.7668 | 37.78
2021-01-01 21:00 | 44197.875 | 0 | 12.2615 | 37.78
2021-01-01 21:30 | 44197.8958 | 0 | 12.014 | 37.78
2021-01-01 22:00 | 44197.9167 | 0 | 11.6869 | 37.78
2021-01-01 22:30 | 44197.9375 | 0 | 10.8917 | 37.78
2021-01-01 23:00 | 44197.9583 | 0 | 10.3396 | 37.78
2021-01-01 23:30 | 44197.9792 | 0 | 9.9198 | 37.78
2021-01-02 | 44198 | 0 | 9.4095 | 37.78
2021-01-02 00:30 | 44198.0208 | 0 | 8.8431 | 37.78
2021-01-02 01:00 | 44198.0417 | 0 | 8.5745 | 37.78
2021-01-02 01:30 | 44198.0625 | 0 | 8.4355 | 37.78
2021-01-02 02:00 | 44198.0833 | 0 | 8.4672 | 37.78
2021-01-02 02:30 | 44198.1042 | 0 | 8.3852 | 37.78
2021-01-02 03:00 | 44198.125 | 0 | 8.1929 | 37.78
2021-01-02 03:30 | 44198.1458 | 0 | 8.1634 | 37.78
2021-01-02 04:00 | 44198.1667 | 0 | 8.1976 | 37.78
2021-01-02 04:30 | 44198.1875 | 0 | 8.2511 | 37.78
2021-01-02 05:00 | 44198.2083 | 0 | 8.0588 | 37.78
2021-01-02 05:30 | 44198.2292 | 0 | 7.7374 | 37.78
2021-01-02 06:00 | 44198.25 | 0 | 7.9077 | 37.78
2021-01-02 06:30 | 44198.2708 | 0 | 8.1527 | 37.78
2021-01-02 07:00 | 44198.2917 | 0 | 8.0657 | 37.78
2021-01-02 07:30 | 44198.3125 | 0 | 8.0865 | 37.78
2021-01-02 08:00 | 44198.3333 | 0 | 8.9778 | 37.78
2021-01-02 08:30 | 44198.3542 | 0 | 9.5739 | 37.78
2021-01-02 09:00 | 44198.375 | 0 | 9.8006 | 37.78
2021-01-02 09:30 | 44198.3958 | 0 | 10.5434 | 37.78
2021-01-02 10:00 | 44198.4167 | 0 | 11.3913 | 37.78
2021-01-02 10:30 | 44198.4375 | 0 | 9.6627 | 37.78
2021-01-02 11:00 | 44198.4583 | 0 | 8.8829 | 37.78
2021-01-02 11:30 | 44198.4792 | 0 | 9.1152 | 37.78
2021-01-02 12:00 | 44198.5 | 0 | 9.8207 | 37.78
2021-01-02 12:30 | 44198.5208 | 0 | 9.9199 | 37.78
2021-01-02 13:00 | 44198.5417 | 0 | 10.2511 | 37.78
2021-01-02 13:30 | 44198.5625 | 0 | 10.5859 | 37.78
2021-01-02 14:00 | 44198.5833 | 0 | 10.9883 | 37.78
2021-01-02 14:30 | 44198.6042 | 0 | 11.7591 | 37.78
2021-01-02 15:00 | 44198.625 | 0 | 11.9886 | 37.78
2021-01-02 15:30 | 44198.6458 | 0 | 12.9841 | 37.78
2021-01-02 16:00 | 44198.6667 | 0 | 13.5001 | 37.78
2021-01-02 16:30 | 44198.6875 | 0 | 13.3509 | 37.78
2021-01-02 17:00 | 44198.7083 | 0 | 13.604 | 37.78
2021-01-02 17:30 | 44198.7292 | 0 | 14.0331 | 37.78
2021-01-02 18:00 | 44198.75 | 0 | 14.2719 | 37.78
2021-01-02 18:30 | 44198.7708 | 0 | 14.806 | 37.78
2021-01-02 19:00 | 44198.7917 | 0 | 14.7738 | 37.78
2021-01-02 19:30 | 44198.8125 | 0 | 14.662 | 37.78
2021-01-02 20:00 | 44198.8333 | 0 | 14.4992 | 37.78
2021-01-02 20:30 | 44198.8542 | 0 | 13.9547 | 37.78
2021-01-02 21:00 | 44198.875 | 0 | 13.4603 | 37.78
2021-01-02 21:30 | 44198.8958 | 0 | 13.0854 | 37.78
2021-01-02 22:00 | 44198.9167 | 0 | 12.4041 | 37.78
2021-01-02 22:30 | 44198.9375 | 0 | 11.5371 | 37.78
2021-01-02 23:00 | 44198.9583 | 0 | 11.0512 | 37.78
2021-01-02 23:30 | 44198.9792 | 0 | 10.4867 | 37.78
2021-01-03 | 44199 | 0 | 10.08 | 37.78
2021-01-03 00:30 | 44199.0208 | 0 | 9.8409 | 37.78
2021-01-03 01:00 | 44199.0417 | 0 | 9.5778 | 37.78
2021-01-03 01:30 | 44199.0625 | 0 | 9.3049 | 37.78
2021-01-03 02:00 | 44199.0833 | 0 | 9.3067 | 37.78
2021-01-03 02:30 | 44199.1042 | 0 | 9.1383 | 37.78
2021-01-03 03:00 | 44199.125 | 0 | 9.1953 | 37.78
2021-01-03 03:30 | 44199.1458 | 0 | 9.2236 | 37.78
2021-01-03 04:00 | 44199.1667 | 0 | 9.4769 | 37.78
2021-01-03 04:30 | 44199.1875 | 0 | 9.8544 | 37.78
2021-01-03 05:00 | 44199.2083 | 0 | 10.3296 | 37.78
2021-01-03 05:30 | 44199.2292 | 0 | 10.5843 | 37.78
2021-01-03 06:00 | 44199.25 | 0 | 11.1967 | 37.78
2021-01-03 06:30 | 44199.2708 | 0 | 11.9806 | 37.78
2021-01-03 07:00 | 44199.2917 | 0 | 12.6723 | 37.78
2021-01-03 07:30 | 44199.3125 | 0 | 13.277 | 37.78
2021-01-03 08:00 | 44199.3333 | 0 | 13.5693 | 37.78
2021-01-03 08:30 | 44199.3542 | 0 | 13.3293 | 37.78
2021-01-03 09:00 | 44199.375 | 0 | 13.9826 | 37.78
2021-01-03 09:30 | 44199.3958 | 0 | 12.5536 | 37.78
2021-01-03 10:00 | 44199.4167 | 0 | 12.7258 | 37.78
2021-01-03 10:30 | 44199.4375 | 0 | 12.6693 | 37.78
2021-01-03 11:00 | 44199.4583 | 0 | 13.5295 | 37.78
2021-01-03 11:30 | 44199.4792 | 0 | 14.6122 | 37.78
2021-01-03 12:00 | 44199.5 | 0 | 13.2019 | 37.78
2021-01-03 12:30 | 44199.5208 | 0 | 14.2812 | 37.78
2021-01-03 13:00 | 44199.5417 | 0 | 13.9871 | 37.78
2021-01-03 13:30 | 44199.5625 | 0 | 14.6129 | 37.78
2021-01-03 14:00 | 44199.5833 | 0 | 14.9822 | 37.78
2021-01-03 14:30 | 44199.6042 | 0 | 16.0332 | 37.78
2021-01-03 15:00 | 44199.625 | 0 | 17.0525 | 37.78
2021-01-03 15:30 | 44199.6458 | 0 | 16.4777 | 37.78
2021-01-03 16:00 | 44199.6667 | 0 | 17.3335 | 37.78
2021-01-03 16:30 | 44199.6875 | 0 | 16.7006 | 37.78
2021-01-03 17:00 | 44199.7083 | 0 | 16.7681 | 37.78
2021-01-03 17:30 | 44199.7292 | 0 | 16.765 | 37.78
2021-01-03 18:00 | 44199.75 | 0 | 16.9604 | 37.78
2021-01-03 18:30 | 44199.7708 | 0 | 16.8835 | 37.78
2021-01-03 19:00 | 44199.7917 | 0 | 16.9909 | 37.78
2021-01-03 19:30 | 44199.8125 | 0 | 17.11 | 37.78
2021-01-03 20:00 | 44199.8333 | 0 | 16.7128 | 37.78
2021-01-03 20:30 | 44199.8542 | 0 | 16.0671 | 37.78
2021-01-03 21:00 | 44199.875 | 0 | 15.4045 | 37.78
2021-01-03 21:30 | 44199.8958 | 0 | 14.8299 | 37.78
2021-01-03 22:00 | 44199.9167 | 0 | 14.16 | 37.78
2021-01-03 22:30 | 44199.9375 | 0 | 13.2992 | 37.78
2021-01-03 23:00 | 44199.9583 | 0 | 12.595 | 37.78
2021-01-03 23:30 | 44199.9792 | 0 | 12.1007 | 37.78
2021-01-04 | 44200 | 0 | 11.3204 | 37.78
2021-01-04 00:30 | 44200.0208 | 0 | 10.7859 | 37.78
2021-01-04 01:00 | 44200.0417 | 0 | 10.2028 | 37.78
2021-01-04 01:30 | 44200.0625 | 0 | 10.0361 | 37.78
2021-01-04 02:00 | 44200.0833 | 0 | 10.0126 | 37.78
2021-01-04 02:30 | 44200.1042 | 0 | 9.9543 | 37.78
2021-01-04 03:00 | 44200.125 | 0 | 9.8546 | 37.78
2021-01-04 03:30 | 44200.1458 | 0 | 9.8817 | 37.78
2021-01-04 04:00 | 44200.1667 | 0 | 10.2106 | 37.78
2021-01-04 04:30 | 44200.1875 | 0 | 10.4934 | 37.78
2021-01-04 05:00 | 44200.2083 | 0 | 10.8479 | 37.78
2021-01-04 05:30 | 44200.2292 | 0 | 11.0788 | 37.78
2021-01-04 06:00 | 44200.25 | 0 | 11.5057 | 37.78
2021-01-04 06:30 | 44200.2708 | 0 | 11.9247 | 37.78
2021-01-04 07:00 | 44200.2917 | 0 | 12.7831 | 37.78
2021-01-04 07:30 | 44200.3125 | 0 | 13.0009 | 37.78
2021-01-04 08:00 | 44200.3333 | 0 | 13.6253 | 37.78
2021-01-04 08:30 | 44200.3542 | 0 | 13.7461 | 37.78
2021-01-04 09:00 | 44200.375 | 0 | 14.3449 | 37.78
2021-01-04 09:30 | 44200.3958 | 0 | 14.5496 | 37.78
2021-01-04 10:00 | 44200.4167 | 0 | 15.069 | 37.78
2021-01-04 10:30 | 44200.4375 | 0 | 15.2445 | 37.78
2021-01-04 11:00 | 44200.4583 | 0 | 15.5977 | 37.78
2021-01-04 11:30 | 44200.4792 | 0 | 16.1094 | 37.78
2021-01-04 12:00 | 44200.5 | 0 | 16.2789 | 37.78
2021-01-04 12:30 | 44200.5208 | 0 | 16.65 | 37.78
2021-01-04 13:00 | 44200.5417 | 0 | 17.2368 | 37.78
2021-01-04 13:30 | 44200.5625 | 0 | 18.1185 | 37.78
2021-01-04 14:00 | 44200.5833 | 0 | 18.0303 | 37.78
2021-01-04 14:30 | 44200.6042 | 0 | 19.2794 | 37.78
2021-01-04 15:00 | 44200.625 | 0 | 21.3704 | 37.78
2021-01-04 15:30 | 44200.6458 | 0 | 20.9088 | 37.78
2021-01-04 16:00 | 44200.6667 | 0 | 20.047 | 37.78
2021-01-04 16:30 | 44200.6875 | 0 | 18.9852 | 37.78
2021-01-04 17:00 | 44200.7083 | 0 | 18.7145 | 37.78
2021-01-04 17:30 | 44200.7292 | 0 | 18.6836 | 37.78
2021-01-04 18:00 | 44200.75 | 0 | 18.6048 | 37.78
2021-01-04 18:30 | 44200.7708 | 0 | 19.1062 | 37.78
2021-01-04 19:00 | 44200.7917 | 0 | 19.3163 | 37.78
2021-01-04 19:30 | 44200.8125 | 0 | 19.2536 | 37.78
2021-01-04 20:00 | 44200.8333 | 0 | 18.6464 | 37.78
2021-01-04 20:30 | 44200.8542 | 0 | 17.7291 | 37.78
2021-01-04 21:00 | 44200.875 | 0 | 17.0556 | 37.78
2021-01-04 21:30 | 44200.8958 | 0 | 16.2754 | 37.78
2021-01-04 22:00 | 44200.9167 | 0 | 15.6184 | 37.78
2021-01-04 22:30 | 44200.9375 | 0 | 14.6589 | 37.78
2021-01-04 23:00 | 44200.9583 | 0 | 13.8529 | 37.78
2021-01-04 23:30 | 44200.9792 | 0 | 12.9208 | 37.78
2021-01-05 | 44201 | 0 | 12.1119 | 37.78
2021-01-05 00:30 | 44201.0208 | 0 | 11.3108 | 37.78
2021-01-05 01:00 | 44201.0417 | 0 | 10.9593 | 37.78
2021-01-05 01:30 | 44201.0625 | 0 | 10.6596 | 37.78
2021-01-05 02:00 | 44201.0833 | 0 | 10.3374 | 37.78
2021-01-05 02:30 | 44201.1042 | 0 | 10.2001 | 37.78
2021-01-05 03:00 | 44201.125 | 0 | 10.0806 | 37.78
2021-01-05 03:30 | 44201.1458 | 0 | 10.1706 | 37.78
2021-01-05 04:00 | 44201.1667 | 0 | 10.3016 | 37.78
2021-01-05 04:30 | 44201.1875 | 0 | 10.4919 | 37.78
2021-01-05 05:00 | 44201.2083 | 0 | 10.9426 | 37.78
2021-01-05 05:30 | 44201.2292 | 0 | 10.9698 | 37.78
2021-01-05 06:00 | 44201.25 | 0 | 11.9362 | 37.78
2021-01-05 06:30 | 44201.2708 | 0 | 12.8233 | 37.78
2021-01-05 07:00 | 44201.2917 | 0 | 13.4287 | 37.78
2021-01-05 07:30 | 44201.3125 | 0 | 14.0222 | 37.78
2021-01-05 08:00 | 44201.3333 | 0 | 15.1685 | 37.78
2021-01-05 08:30 | 44201.3542 | 0 | 14.7337 | 37.78
2021-01-05 09:00 | 44201.375 | 0 | 15.281 | 37.78
2021-01-05 09:30 | 44201.3958 | 0 | 14.8615 | 37.78
2021-01-05 10:00 | 44201.4167 | 0 | 15.2487 | 37.78
2021-01-05 10:30 | 44201.4375 | 0 | 15.7688 | 37.78
2021-01-05 11:00 | 44201.4583 | 0 | 16.0948 | 37.78
2021-01-05 11:30 | 44201.4792 | 0 | 16.4264 | 37.78
2021-01-05 12:00 | 44201.5 | 0 | 16.6934 | 37.78
2021-01-05 12:30 | 44201.5208 | 0 | 17.1506 | 37.78
2021-01-05 13:00 | 44201.5417 | 0 | 17.6611 | 37.78
2021-01-05 13:30 | 44201.5625 | 0 | 18.2278 | 37.78
2021-01-05 14:00 | 44201.5833 | 0 | 18.7674 | 37.78
2021-01-05 14:30 | 44201.6042 | 0 | 19.1684 | 37.78
2021-01-05 15:00 | 44201.625 | 0 | 19.9653 | 37.78
2021-01-05 15:30 | 44201.6458 | 0 | 20.7178 | 37.78
2021-01-05 16:00 | 44201.6667 | 0 | 20.5043 | 37.78
2021-01-05 16:30 | 44201.6875 | 0 | 22.2137 | 37.78
2021-01-05 17:00 | 44201.7083 | 0 | 21.6353 | 37.78
2021-01-05 17:30 | 44201.7292 | 0 | 21.5437 | 37.78
2021-01-05 18:00 | 44201.75 | 0 | 21.3096 | 37.78
2021-01-05 18:30 | 44201.7708 | 0 | 21.4406 | 37.78
2021-01-05 19:00 | 44201.7917 | 0 | 20.8615 | 37.78
2021-01-05 19:30 | 44201.8125 | 0 | 19.9132 | 37.78
2021-01-05 20:00 | 44201.8333 | 0 | 18.6471 | 37.78
2021-01-05 20:30 | 44201.8542 | 0 | 17.4383 | 37.78
2021-01-05 21:00 | 44201.875 | 0 | 16.4264 | 37.78
2021-01-05 21:30 | 44201.8958 | 0 | 15.5382 | 37.78
2021-01-05 22:00 | 44201.9167 | 0 | 14.7319 | 37.78
2021-01-05 22:30 | 44201.9375 | 0 | 13.6469 | 37.78
2021-01-05 23:00 | 44201.9583 | 0 | 12.8666 | 37.78
2021-01-05 23:30 | 44201.9792 | 0 | 12.1493 | 37.78
2021-01-06 | 44202 | 0 | 11.5218 | 37.78
2021-01-06 00:30 | 44202.0208 | 0 | 10.8904 | 37.78
2021-01-06 01:00 | 44202.0417 | 0 | 10.5542 | 37.78
2021-01-06 01:30 | 44202.0625 | 0 | 10.3432 | 37.78
2021-01-06 02:00 | 44202.0833 | 0 | 10.4025 | 37.78
2021-01-06 02:30 | 44202.1042 | 0 | 10.234 | 37.78
2021-01-06 03:00 | 44202.125 | 0 | 10.1809 | 37.78
2021-01-06 03:30 | 44202.1458 | 0 | 10.1762 | 37.78
2021-01-06 04:00 | 44202.1667 | 0 | 10.5923 | 37.78
2021-01-06 04:30 | 44202.1875 | 0 | 11.1158 | 37.78
2021-01-06 05:00 | 44202.2083 | 0 | 11.4658 | 37.78
2021-01-06 05:30 | 44202.2292 | 0 | 11.7228 | 37.78
2021-01-06 06:00 | 44202.25 | 0 | 12.3698 | 37.78
2021-01-06 06:30 | 44202.2708 | 0 | 13.1208 | 37.78
2021-01-06 07:00 | 44202.2917 | 0 | 13.3796 | 37.78
2021-01-06 07:30 | 44202.3125 | 0 | 13.6536 | 37.78
2021-01-06 08:00 | 44202.3333 | 0 | 13.7263 | 37.78
2021-01-06 08:30 | 44202.3542 | 0 | 14.2544 | 37.78
2021-01-06 09:00 | 44202.375 | 0 | 14.1498 | 37.78
2021-01-06 09:30 | 44202.3958 | 0 | 13.648 | 37.78
2021-01-06 10:00 | 44202.4167 | 0 | 15.2706 | 37.78
2021-01-06 10:30 | 44202.4375 | 0 | 14.6967 | 37.78
2021-01-06 11:00 | 44202.4583 | 0 | 15.2993 | 37.78
2021-01-06 11:30 | 44202.4792 | 0 | 15.3645 | 37.78
2021-01-06 12:00 | 44202.5 | 0 | 15.4591 | 37.78
2021-01-06 12:30 | 44202.5208 | 0 | 14.5603 | 37.78
2021-01-06 13:00 | 44202.5417 | 0 | 14.8108 | 37.78
2021-01-06 13:30 | 44202.5625 | 0 | 14.2934 | 37.78
2021-01-06 14:00 | 44202.5833 | 0 | 14.0415 | 37.78
2021-01-06 14:30 | 44202.6042 | 0 | 14.8221 | 37.78
2021-01-06 15:00 | 44202.625 | 0 | 14.9492 | 37.78
2021-01-06 15:30 | 44202.6458 | 0 | 14.9744 | 37.78
2021-01-06 16:00 | 44202.6667 | 0 | 15.0854 | 37.78
2021-01-06 16:30 | 44202.6875 | 0 | 15.2771 | 37.78
2021-01-06 17:00 | 44202.7083 | 0 | 15.0948 | 37.78
2021-01-06 17:30 | 44202.7292 | 0 | 15.2714 | 37.78
2021-01-06 18:00 | 44202.75 | 0 | 15.076 | 37.78
2021-01-06 18:30 | 44202.7708 | 0 | 15.1889 | 37.78
2021-01-06 19:00 | 44202.7917 | 0 | 15.1848 | 37.78
2021-01-06 19:30 | 44202.8125 | 0 | 14.9657 | 37.78
2021-01-06 20:00 | 44202.8333 | 0 | 14.5543 | 37.78
2021-01-06 20:30 | 44202.8542 | 0 | 13.9982 | 37.78
2021-01-06 21:00 | 44202.875 | 0 | 13.5629 | 37.78
2021-01-06 21:30 | 44202.8958 | 0 | 13.3275 | 37.78
2021-01-06 22:00 | 44202.9167 | 0 | 12.5997 | 37.78
2021-01-06 22:30 | 44202.9375 | 0 | 11.7954 | 37.78
2021-01-06 23:00 | 44202.9583 | 0 | 11.2493 | 37.78
2021-01-06 23:30 | 44202.9792 | 0 | 10.5652 | 37.78
2021-01-07 | 44203 | 0 | 10.0343 | 37.78
2021-01-07 00:30 | 44203.0208 | 0 | 9.7088 | 37.78
2021-01-07 01:00 | 44203.0417 | 0 | 9.4331 | 37.78
2021-01-07 01:30 | 44203.0625 | 0 | 9.3885 | 37.78
2021-01-07 02:00 | 44203.0833 | 0 | 9.2203 | 37.78
2021-01-07 02:30 | 44203.1042 | 0 | 9.1415 | 37.78
2021-01-07 03:00 | 44203.125 | 0 | 9.1086 | 37.78
2021-01-07 03:30 | 44203.1458 | 0 | 9.1088 | 37.78
2021-01-07 04:00 | 44203.1667 | 0 | 9.4681 | 37.78
2021-01-07 04:30 | 44203.1875 | 0 | 9.7022 | 37.78
2021-01-07 05:00 | 44203.2083 | 0 | 10.081 | 37.78
2021-01-07 05:30 | 44203.2292 | 0 | 10.3833 | 37.78
2021-01-07 06:00 | 44203.25 | 0 | 10.8529 | 37.78
2021-01-07 06:30 | 44203.2708 | 0 | 11.5468 | 37.78
2021-01-07 07:00 | 44203.2917 | 0 | 12.2514 | 37.78
2021-01-07 07:30 | 44203.3125 | 0 | 12.581 | 37.78
2021-01-07 08:00 | 44203.3333 | 0 | 13.3141 | 37.78
2021-01-07 08:30 | 44203.3542 | 0 | 13.1865 | 37.78
2021-01-07 09:00 | 44203.375 | 0 | 12.8692 | 37.78
2021-01-07 09:30 | 44203.3958 | 0 | 13.2862 | 37.78
2021-01-07 10:00 | 44203.4167 | 0 | 13.2235 | 37.78
2021-01-07 10:30 | 44203.4375 | 0 | 12.77 | 37.78
2021-01-07 11:00 | 44203.4583 | 0 | 12.4194 | 37.78
2021-01-07 11:30 | 44203.4792 | 0 | 12.566 | 37.78
2021-01-07 12:00 | 44203.5 | 0 | 12.2431 | 37.78
2021-01-07 12:30 | 44203.5208 | 0 | 12.591 | 37.78
2021-01-07 13:00 | 44203.5417 | 0 | 12.0635 | 37.78
2021-01-07 13:30 | 44203.5625 | 0 | 11.9187 | 37.78
2021-01-07 14:00 | 44203.5833 | 0 | 12.2436 | 37.78
2021-01-07 14:30 | 44203.6042 | 0 | 12.3289 | 37.78
2021-01-07 15:00 | 44203.625 | 0 | 12.3651 | 37.78
2021-01-07 15:30 | 44203.6458 | 0 | 12.4238 | 37.78
2021-01-07 16:00 | 44203.6667 | 0 | 12.4411 | 37.78
2021-01-07 16:30 | 44203.6875 | 0 | 12.8269 | 37.78
2021-01-07 17:00 | 44203.7083 | 0 | 12.923 | 37.78
2021-01-07 17:30 | 44203.7292 | 0 | 12.9215 | 37.78
2021-01-07 18:00 | 44203.75 | 0 | 12.8189 | 37.78
2021-01-07 18:30 | 44203.7708 | 0 | 13.498 | 37.78
2021-01-07 19:00 | 44203.7917 | 0 | 13.3814 | 37.78
2021-01-07 19:30 | 44203.8125 | 0 | 13.0573 | 37.78
2021-01-07 20:00 | 44203.8333 | 0 | 12.8869 | 37.78
2021-01-07 20:30 | 44203.8542 | 0 | 12.1085 | 37.78
2021-01-07 21:00 | 44203.875 | 0 | 11.6007 | 37.78
2021-01-07 21:30 | 44203.8958 | 0 | 11.2702 | 37.78
2021-01-07 22:00 | 44203.9167 | 0 | 11.0493 | 37.78
2021-01-07 22:30 | 44203.9375 | 0 | 10.2516 | 37.78
2021-01-07 23:00 | 44203.9583 | 0 | 9.8064 | 37.78
2021-01-07 23:30 | 44203.9792 | 0 | 9.4418 | 37.78
2021-01-08 | 44204 | 0 | 9.0399 | 37.78
2021-01-08 00:30 | 44204.0208 | 0 | 8.6919 | 37.78
2021-01-08 01:00 | 44204.0417 | 0 | 8.4421 | 37.78
2021-01-08 01:30 | 44204.0625 | 0 | 8.3239 | 37.78
2021-01-08 02:00 | 44204.0833 | 0 | 8.1572 | 37.78
2021-01-08 02:30 | 44204.1042 | 0 | 8.0889 | 37.78
2021-01-08 03:00 | 44204.125 | 0 | 8.1097 | 37.78
2021-01-08 03:30 | 44204.1458 | 0 | 8.0128 | 37.78
2021-01-08 04:00 | 44204.1667 | 0 | 8.1144 | 37.78
2021-01-08 04:30 | 44204.1875 | 0 | 8.0247 | 37.78
2021-01-08 05:00 | 44204.2083 | 0 | 7.9966 | 37.78
2021-01-08 05:30 | 44204.2292 | 0 | 8.1948 | 37.78
2021-01-08 06:00 | 44204.25 | 0 | 8.0961 | 37.78
2021-01-08 06:30 | 44204.2708 | 0 | 8.1503 | 37.78
2021-01-08 07:00 | 44204.2917 | 0 | 8.1971 | 37.78
2021-01-08 07:30 | 44204.3125 | 0 | 8.9225 | 37.78
2021-01-08 08:00 | 44204.3333 | 0 | 9.4595 | 37.78
2021-01-08 08:30 | 44204.3542 | 0 | 9.7896 | 37.78
2021-01-08 09:00 | 44204.375 | 0 | 9.981 | 37.78
2021-01-08 09:30 | 44204.3958 | 0 | 9.7855 | 37.78
2021-01-08 10:00 | 44204.4167 | 0 | 8.5581 | 37.78
2021-01-08 10:30 | 44204.4375 | 0 | 8.1963 | 37.78
2021-01-08 11:00 | 44204.4583 | 0 | 10.1539 | 37.78
2021-01-08 11:30 | 44204.4792 | 0 | 9.664 | 37.78
2021-01-08 12:00 | 44204.5 | 0 | 10.1162 | 37.78
2021-01-08 12:30 | 44204.5208 | 0 | 9.9172 | 37.78
2021-01-08 13:00 | 44204.5417 | 0 | 8.9631 | 37.78
2021-01-08 13:30 | 44204.5625 | 0 | 9.5793 | 37.78
2021-01-08 14:00 | 44204.5833 | 0 | 10.3136 | 37.78
2021-01-08 14:30 | 44204.6042 | 0 | 10.265 | 37.78
2021-01-08 15:00 | 44204.625 | 0 | 9.8408 | 37.78
2021-01-08 15:30 | 44204.6458 | 0 | 10.1801 | 37.78
2021-01-08 16:00 | 44204.6667 | 0 | 10.3203 | 37.78
2021-01-08 16:30 | 44204.6875 | 0 | 10.5816 | 37.78
2021-01-08 17:00 | 44204.7083 | 0 | 10.7677 | 37.78
2021-01-08 17:30 | 44204.7292 | 0 | 11.2079 | 37.78
2021-01-08 18:00 | 44204.75 | 0 | 11.33 | 37.78
2021-01-08 18:30 | 44204.7708 | 0 | 11.719 | 37.78
2021-01-08 19:00 | 44204.7917 | 0 | 11.5995 | 37.78
2021-01-08 19:30 | 44204.8125 | 0 | 11.5577 | 37.78
2021-01-08 20:00 | 44204.8333 | 0 | 11.2148 | 37.78
2021-01-08 20:30 | 44204.8542 | 0 | 10.7059 | 37.78
2021-01-08 21:00 | 44204.875 | 0 | 10.1648 | 37.78
2021-01-08 21:30 | 44204.8958 | 0 | 9.9858 | 37.78
2021-01-08 22:00 | 44204.9167 | 0 | 9.8051 | 37.78
2021-01-08 22:30 | 44204.9375 | 0 | 9.2439 | 37.78
2021-01-08 23:00 | 44204.9583 | 0 | 8.8443 | 37.78
2021-01-08 23:30 | 44204.9792 | 0 | 8.5054 | 37.78
2021-01-09 | 44205 | 0 | 8.2551 | 37.78
2021-01-09 00:30 | 44205.0208 | 0 | 7.8653 | 37.78
2021-01-09 01:00 | 44205.0417 | 0 | 7.7194 | 37.78
2021-01-09 01:30 | 44205.0625 | 0 | 7.608 | 37.78
2021-01-09 02:00 | 44205.0833 | 0 | 7.5633 | 37.78
2021-01-09 02:30 | 44205.1042 | 0 | 7.4604 | 37.78
2021-01-09 03:00 | 44205.125 | 0 | 7.3983 | 37.78
2021-01-09 03:30 | 44205.1458 | 0 | 7.3391 | 37.78
2021-01-09 04:00 | 44205.1667 | 0 | 7.3309 | 37.78
2021-01-09 04:30 | 44205.1875 | 0 | 7.1806 | 37.78
2021-01-09 05:00 | 44205.2083 | 0 | 7.2418 | 37.78
2021-01-09 05:30 | 44205.2292 | 0 | 7.0985 | 37.78
2021-01-09 06:00 | 44205.25 | 0 | 7.157 | 37.78
2021-01-09 06:30 | 44205.2708 | 0 | 7.0425 | 37.78
2021-01-09 07:00 | 44205.2917 | 0 | 7.3881 | 37.78
2021-01-09 07:30 | 44205.3125 | 0 | 7.325 | 37.78
2021-01-09 08:00 | 44205.3333 | 0 | 7.1184 | 37.78
2021-01-09 08:30 | 44205.3542 | 0 | 7.2884 | 37.78
2021-01-09 09:00 | 44205.375 | 0 | 8.2703 | 37.78
2021-01-09 09:30 | 44205.3958 | 0 | 8.1567 | 37.78
2021-01-09 10:00 | 44205.4167 | 0 | 7.7762 | 37.78
2021-01-09 10:30 | 44205.4375 | 0 | 8.1549 | 37.78
2021-01-09 11:00 | 44205.4583 | 0 | 7.3627 | 37.78
2021-01-09 11:30 | 44205.4792 | 0 | 8.9935 | 37.78
2021-01-09 12:00 | 44205.5 | 0 | 8.9718 | 37.78
2021-01-09 12:30 | 44205.5208 | 0 | 9.9037 | 37.78
2021-01-09 13:00 | 44205.5417 | 0 | 9.824 | 37.78
2021-01-09 13:30 | 44205.5625 | 0 | 9.1007 | 37.78
2021-01-09 14:00 | 44205.5833 | 0 | 8.8337 | 37.78
2021-01-09 14:30 | 44205.6042 | 0 | 8.7253 | 37.78
2021-01-09 15:00 | 44205.625 | 0 | 8.8561 | 37.78
2021-01-09 15:30 | 44205.6458 | 0 | 10.049 | 37.78
2021-01-09 16:00 | 44205.6667 | 0 | 9.9902 | 37.78
2021-01-09 16:30 | 44205.6875 | 0 | 10.3673 | 37.78
2021-01-09 17:00 | 44205.7083 | 0 | 10.7082 | 37.78
2021-01-09 17:30 | 44205.7292 | 0 | 11.5798 | 37.78
2021-01-09 18:00 | 44205.75 | 0 | 11.7923 | 37.78
2021-01-09 18:30 | 44205.7708 | 0 | 12.097 | 37.78
2021-01-09 19:00 | 44205.7917 | 0 | 12.2668 | 37.78
2021-01-09 19:30 | 44205.8125 | 0 | 12.2948 | 37.78
2021-01-09 20:00 | 44205.8333 | 0 | 12.1247 | 37.78
2021-01-09 20:30 | 44205.8542 | 0 | 11.4594 | 37.78
2021-01-09 21:00 | 44205.875 | 0 | 10.8833 | 37.78
2021-01-09 21:30 | 44205.8958 | 0 | 10.5617 | 37.78
2021-01-09 22:00 | 44205.9167 | 0 | 10.1513 | 37.78
2021-01-09 22:30 | 44205.9375 | 0 | 9.4971 | 37.78
2021-01-09 23:00 | 44205.9583 | 0 | 8.9742 | 37.78
2021-01-09 23:30 | 44205.9792 | 0 | 8.5537 | 37.78
2021-01-10 | 44206 | 0 | 8.2449 | 37.78
2021-01-10 00:30 | 44206.0208 | 0 | 7.8944 | 37.78
2021-01-10 01:00 | 44206.0417 | 0 | 7.7911 | 37.78
2021-01-10 01:30 | 44206.0625 | 0 | 7.7209 | 37.78
2021-01-10 02:00 | 44206.0833 | 0 | 7.7315 | 37.78
2021-01-10 02:30 | 44206.1042 | 0 | 7.6588 | 37.78
2021-01-10 03:00 | 44206.125 | 0 | 7.6718 | 37.78
2021-01-10 03:30 | 44206.1458 | 0 | 7.8348 | 37.78
2021-01-10 04:00 | 44206.1667 | 0 | 8.0861 | 37.78
2021-01-10 04:30 | 44206.1875 | 0 | 8.2392 | 37.78
2021-01-10 05:00 | 44206.2083 | 0 | 8.4604 | 37.78
2021-01-10 05:30 | 44206.2292 | 0 | 8.78 | 37.78
2021-01-10 06:00 | 44206.25 | 0 | 9.3139 | 37.78
2021-01-10 06:30 | 44206.2708 | 0 | 9.6274 | 37.78
2021-01-10 07:00 | 44206.2917 | 0 | 9.9244 | 37.78
2021-01-10 07:30 | 44206.3125 | 0 | 10.2839 | 37.78
2021-01-10 08:00 | 44206.3333 | 0 | 10.2947 | 37.78
2021-01-10 08:30 | 44206.3542 | 0 | 10.5825 | 37.78
2021-01-10 09:00 | 44206.375 | 0 | 10.2868 | 37.78
2021-01-10 09:30 | 44206.3958 | 0 | 10.3989 | 37.78
2021-01-10 10:00 | 44206.4167 | 0 | 10.887 | 37.78
2021-01-10 10:30 | 44206.4375 | 0 | 10.6484 | 37.78
2021-01-10 11:00 | 44206.4583 | 0 | 11.9916 | 37.78
2021-01-10 11:30 | 44206.4792 | 0 | 11.2698 | 37.78
2021-01-10 12:00 | 44206.5 | 0 | 11.1971 | 37.78
2021-01-10 12:30 | 44206.5208 | 0 | 11.9781 | 37.78
2021-01-10 13:00 | 44206.5417 | 0 | 12.6777 | 37.78
2021-01-10 13:30 | 44206.5625 | 0 | 12.0259 | 37.78
2021-01-10 14:00 | 44206.5833 | 0 | 11.995 | 37.78
2021-01-10 14:30 | 44206.6042 | 0 | 12.7104 | 37.78
2021-01-10 15:00 | 44206.625 | 0 | 12.8834 | 37.78
2021-01-10 15:30 | 44206.6458 | 0 | 13.2132 | 37.78
2021-01-10 16:00 | 44206.6667 | 0 | 13.2624 | 37.78
2021-01-10 16:30 | 44206.6875 | 0 | 13.5844 | 37.78
2021-01-10 17:00 | 44206.7083 | 0 | 13.8596 | 37.78
2021-01-10 17:30 | 44206.7292 | 0 | 13.8525 | 37.78
2021-01-10 18:00 | 44206.75 | 0 | 13.943 | 37.78
2021-01-10 18:30 | 44206.7708 | 0 | 14.1801 | 37.78
2021-01-10 19:00 | 44206.7917 | 0 | 14.2575 | 37.78
2021-01-10 19:30 | 44206.8125 | 0 | 14.2034 | 37.78
2021-01-10 20:00 | 44206.8333 | 0 | 13.9377 | 37.78
2021-01-10 20:30 | 44206.8542 | 0 | 13.3747 | 37.78
2021-01-10 21:00 | 44206.875 | 0 | 12.8557 | 37.78
2021-01-10 21:30 | 44206.8958 | 0 | 12.3995 | 37.78
2021-01-10 22:00 | 44206.9167 | 0 | 11.8683 | 37.78
2021-01-10 22:30 | 44206.9375 | 0 | 11.1375 | 37.78
2021-01-10 23:00 | 44206.9583 | 0 | 10.4181 | 37.78
2021-01-10 23:30 | 44206.9792 | 0 | 10.0225 | 37.78
2021-01-11 | 44207 | 0 | 9.3152 | 37.78
2021-01-11 00:30 | 44207.0208 | 0 | 8.9674 | 37.78
2021-01-11 01:00 | 44207.0417 | 0 | 8.6929 | 37.78
2021-01-11 01:30 | 44207.0625 | 0 | 8.5204 | 37.78
2021-01-11 02:00 | 44207.0833 | 0 | 8.4537 | 37.78
2021-01-11 02:30 | 44207.1042 | 0 | 8.3565 | 37.78
2021-01-11 03:00 | 44207.125 | 0 | 8.2735 | 37.78
2021-01-11 03:30 | 44207.1458 | 0 | 8.3167 | 37.78
2021-01-11 04:00 | 44207.1667 | 0 | 8.5062 | 37.78
2021-01-11 04:30 | 44207.1875 | 0 | 8.6963 | 37.78
2021-01-11 05:00 | 44207.2083 | 0 | 9.0218 | 37.78
2021-01-11 05:30 | 44207.2292 | 0 | 9.4456 | 37.78
2021-01-11 06:00 | 44207.25 | 0 | 9.6884 | 37.78
2021-01-11 06:30 | 44207.2708 | 0 | 10.0502 | 37.78
2021-01-11 07:00 | 44207.2917 | 0 | 10.5015 | 37.78
2021-01-11 07:30 | 44207.3125 | 0 | 11.0602 | 37.78
2021-01-11 08:00 | 44207.3333 | 0 | 10.9507 | 37.78
2021-01-11 08:30 | 44207.3542 | 0 | 11.1337 | 37.78
2021-01-11 09:00 | 44207.375 | 0 | 11.9791 | 37.78
2021-01-11 09:30 | 44207.3958 | 0 | 12.293 | 37.78
2021-01-11 10:00 | 44207.4167 | 0 | 12.0723 | 37.78
2021-01-11 10:30 | 44207.4375 | 0 | 11.9993 | 37.78
2021-01-11 11:00 | 44207.4583 | 0 | 12.4642 | 37.78
2021-01-11 11:30 | 44207.4792 | 0 | 12.792 | 37.78
2021-01-11 12:00 | 44207.5 | 0 | 13.6415 | 37.78
2021-01-11 12:30 | 44207.5208 | 0 | 12.1861 | 37.78
2021-01-11 13:00 | 44207.5417 | 0 | 12.5483 | 37.78
2021-01-11 13:30 | 44207.5625 | 0 | 13.9764 | 37.78
2021-01-11 14:00 | 44207.5833 | 0 | 14.4658 | 37.78
2021-01-11 14:30 | 44207.6042 | 0 | 14.3596 | 37.78
2021-01-11 15:00 | 44207.625 | 0 | 14.8952 | 37.78
2021-01-11 15:30 | 44207.6458 | 0 | 14.0154 | 37.78
2021-01-11 16:00 | 44207.6667 | 0 | 14.6986 | 37.78
2021-01-11 16:30 | 44207.6875 | 0 | 14.9171 | 37.78
2021-01-11 17:00 | 44207.7083 | 0 | 15.0565 | 37.78
2021-01-11 17:30 | 44207.7292 | 0 | 15.277 | 37.78
2021-01-11 18:00 | 44207.75 | 0 | 15.2831 | 37.78
2021-01-11 18:30 | 44207.7708 | 0 | 15.6706 | 37.78
2021-01-11 19:00 | 44207.7917 | 0 | 15.825 | 37.78
2021-01-11 19:30 | 44207.8125 | 0 | 15.695 | 37.78
2021-01-11 20:00 | 44207.8333 | 0 | 15.2824 | 37.78
2021-01-11 20:30 | 44207.8542 | 0 | 14.5635 | 37.78
2021-01-11 21:00 | 44207.875 | 0 | 13.9306 | 37.78
2021-01-11 21:30 | 44207.8958 | 0 | 13.4933 | 37.78
2021-01-11 22:00 | 44207.9167 | 0 | 12.8819 | 37.78
2021-01-11 22:30 | 44207.9375 | 0 | 11.892 | 37.78
2021-01-11 23:00 | 44207.9583 | 0 | 11.1285 | 37.78
2021-01-11 23:30 | 44207.9792 | 0 | 10.6577 | 37.78
2021-01-12 | 44208 | 0 | 9.994 | 37.78
2021-01-12 00:30 | 44208.0208 | 0 | 9.6681 | 37.78
2021-01-12 01:00 | 44208.0417 | 0 | 9.256 | 37.78
2021-01-12 01:30 | 44208.0625 | 0 | 9.1339 | 37.78
2021-01-12 02:00 | 44208.0833 | 0 | 9.0848 | 37.78
2021-01-12 02:30 | 44208.1042 | 0 | 8.8674 | 37.78
2021-01-12 03:00 | 44208.125 | 0 | 8.7781 | 37.78
2021-01-12 03:30 | 44208.1458 | 0 | 8.7305 | 37.78
2021-01-12 04:00 | 44208.1667 | 0 | 8.8798 | 37.78
2021-01-12 04:30 | 44208.1875 | 0 | 9.1954 | 37.78
2021-01-12 05:00 | 44208.2083 | 0 | 9.5424 | 37.78
2021-01-12 05:30 | 44208.2292 | 0 | 9.9532 | 37.78
2021-01-12 06:00 | 44208.25 | 0 | 10.4371 | 37.78
2021-01-12 06:30 | 44208.2708 | 0 | 10.8149 | 37.78
2021-01-12 07:00 | 44208.2917 | 0 | 11.5419 | 37.78
2021-01-12 07:30 | 44208.3125 | 0 | 11.7621 | 37.78
2021-01-12 08:00 | 44208.3333 | 0 | 12.097 | 37.78
2021-01-12 08:30 | 44208.3542 | 0 | 12.1982 | 37.78
2021-01-12 09:00 | 44208.375 | 0 | 12.227 | 37.78
2021-01-12 09:30 | 44208.3958 | 0 | 12.9642 | 37.78
2021-01-12 10:00 | 44208.4167 | 0 | 13.1327 | 37.78
2021-01-12 10:30 | 44208.4375 | 0 | 14.2765 | 37.78
2021-01-12 11:00 | 44208.4583 | 0 | 13.4052 | 37.78
2021-01-12 11:30 | 44208.4792 | 0 | 13.2893 | 37.78
2021-01-12 12:00 | 44208.5 | 0 | 13.5659 | 37.78
2021-01-12 12:30 | 44208.5208 | 0 | 13.1715 | 37.78
2021-01-12 13:00 | 44208.5417 | 0 | 13.6456 | 37.78
2021-01-12 13:30 | 44208.5625 | 0 | 13.8583 | 37.78
2021-01-12 14:00 | 44208.5833 | 0 | 14.0921 | 37.78
2021-01-12 14:30 | 44208.6042 | 0 | 14.4362 | 37.78
2021-01-12 15:00 | 44208.625 | 0 | 15.071 | 37.78
2021-01-12 15:30 | 44208.6458 | 0 | 15.5467 | 37.78
2021-01-12 16:00 | 44208.6667 | 0 | 16.0291 | 37.78
2021-01-12 16:30 | 44208.6875 | 0 | 16.3666 | 37.78
2021-01-12 17:00 | 44208.7083 | 0 | 16.376 | 37.78
2021-01-12 17:30 | 44208.7292 | 0 | 16.0841 | 37.78
2021-01-12 18:00 | 44208.75 | 0 | 16.1482 | 37.78
2021-01-12 18:30 | 44208.7708 | 0 | 16.5507 | 37.78
2021-01-12 19:00 | 44208.7917 | 0 | 16.4013 | 37.78
2021-01-12 19:30 | 44208.8125 | 0 | 16.3608 | 37.78
2021-01-12 20:00 | 44208.8333 | 0 | 16.0064 | 37.78
2021-01-12 20:30 | 44208.8542 | 0 | 15.3423 | 37.78
2021-01-12 21:00 | 44208.875 | 0 | 14.8035 | 37.78
2021-01-12 21:30 | 44208.8958 | 0 | 14.3223 | 37.78
2021-01-12 22:00 | 44208.9167 | 0 | 13.554 | 37.78
2021-01-12 22:30 | 44208.9375 | 0 | 12.6923 | 37.78
2021-01-12 23:00 | 44208.9583 | 0 | 12.1066 | 37.78
2021-01-12 23:30 | 44208.9792 | 0 | 11.542 | 37.78
2021-01-13 | 44209 | 0 | 10.7252 | 37.78
2021-01-13 00:30 | 44209.0208 | 0 | 10.1757 | 37.78
2021-01-13 01:00 | 44209.0417 | 0 | 9.9007 | 37.78
2021-01-13 01:30 | 44209.0625 | 0 | 9.7247 | 37.78
2021-01-13 02:00 | 44209.0833 | 0 | 9.6222 | 37.78
2021-01-13 02:30 | 44209.1042 | 0 | 9.5525 | 37.78
2021-01-13 03:00 | 44209.125 | 0 | 9.4258 | 37.78
2021-01-13 03:30 | 44209.1458 | 0 | 9.4884 | 37.78
2021-01-13 04:00 | 44209.1667 | 0 | 9.6839 | 37.78
2021-01-13 04:30 | 44209.1875 | 0 | 9.874 | 37.78
2021-01-13 05:00 | 44209.2083 | 0 | 10.2624 | 37.78
2021-01-13 05:30 | 44209.2292 | 0 | 10.5964 | 37.78
2021-01-13 06:00 | 44209.25 | 0 | 11.3725 | 37.78
2021-01-13 06:30 | 44209.2708 | 0 | 11.6932 | 37.78
2021-01-13 07:00 | 44209.2917 | 0 | 12.2432 | 37.78
2021-01-13 07:30 | 44209.3125 | 0 | 12.5527 | 37.78
2021-01-13 08:00 | 44209.3333 | 0 | 13.3778 | 37.78
2021-01-13 08:30 | 44209.3542 | 0 | 13.3444 | 37.78
2021-01-13 09:00 | 44209.375 | 0 | 14.2641 | 37.78
2021-01-13 09:30 | 44209.3958 | 0 | 14.4164 | 37.78
2021-01-13 10:00 | 44209.4167 | 0 | 14.7956 | 37.78
2021-01-13 10:30 | 44209.4375 | 0 | 14.3981 | 37.78
2021-01-13 11:00 | 44209.4583 | 0 | 15.5569 | 37.78
2021-01-13 11:30 | 44209.4792 | 0 | 14.3916 | 37.78
2021-01-13 12:00 | 44209.5 | 0 | 13.9596 | 37.78
2021-01-13 12:30 | 44209.5208 | 0 | 14.8162 | 37.78
2021-01-13 13:00 | 44209.5417 | 0 | 14.8763 | 37.78
2021-01-13 13:30 | 44209.5625 | 0 | 15.7002 | 37.78
2021-01-13 14:00 | 44209.5833 | 0 | 15.5793 | 37.78
2021-01-13 14:30 | 44209.6042 | 0 | 15.7765 | 37.78
2021-01-13 15:00 | 44209.625 | 0 | 16.1631 | 37.78
2021-01-13 15:30 | 44209.6458 | 0 | 16.4227 | 37.78
2021-01-13 16:00 | 44209.6667 | 0 | 16.7003 | 37.78
2021-01-13 16:30 | 44209.6875 | 0 | 17.1376 | 37.78
2021-01-13 17:00 | 44209.7083 | 0 | 17.1289 | 37.78
2021-01-13 17:30 | 44209.7292 | 0 | 17.2812 | 37.78
2021-01-13 18:00 | 44209.75 | 0 | 17.0157 | 37.78
2021-01-13 18:30 | 44209.7708 | 0 | 17.0577 | 37.78
2021-01-13 19:00 | 44209.7917 | 0 | 17.0876 | 37.78
2021-01-13 19:30 | 44209.8125 | 0 | 17.0816 | 37.78
2021-01-13 20:00 | 44209.8333 | 0 | 16.7929 | 37.78
2021-01-13 20:30 | 44209.8542 | 0 | 16.0001 | 37.78
2021-01-13 21:00 | 44209.875 | 0 | 15.2767 | 37.78
2021-01-13 21:30 | 44209.8958 | 0 | 14.9217 | 37.78
2021-01-13 22:00 | 44209.9167 | 0 | 14.2299 | 37.78
2021-01-13 22:30 | 44209.9375 | 0 | 12.9548 | 37.78
2021-01-13 23:00 | 44209.9583 | 0 | 12.0945 | 37.78
2021-01-13 23:30 | 44209.9792 | 0 | 11.5649 | 37.78
2021-01-14 | 44210 | 0 | 10.8196 | 37.78
2021-01-14 00:30 | 44210.0208 | 0 | 10.3884 | 37.78
2021-01-14 01:00 | 44210.0417 | 0 | 10.1001 | 37.78
2021-01-14 01:30 | 44210.0625 | 0 | 9.8173 | 37.78
2021-01-14 02:00 | 44210.0833 | 0 | 9.7668 | 37.78
2021-01-14 02:30 | 44210.1042 | 0 | 9.5834 | 37.78
2021-01-14 03:00 | 44210.125 | 0 | 9.3391 | 37.78
2021-01-14 03:30 | 44210.1458 | 0 | 9.4811 | 37.78
2021-01-14 04:00 | 44210.1667 | 0 | 9.7194 | 37.78
2021-01-14 04:30 | 44210.1875 | 0 | 9.9496 | 37.78
2021-01-14 05:00 | 44210.2083 | 0 | 10.1987 | 37.78
2021-01-14 05:30 | 44210.2292 | 0 | 10.6533 | 37.78
2021-01-14 06:00 | 44210.25 | 0 | 10.9859 | 37.78
2021-01-14 06:30 | 44210.2708 | 0 | 11.5271 | 37.78
2021-01-14 07:00 | 44210.2917 | 0 | 12.1836 | 37.78
2021-01-14 07:30 | 44210.3125 | 0 | 12.597 | 37.78
2021-01-14 08:00 | 44210.3333 | 0 | 12.8341 | 37.78
2021-01-14 08:30 | 44210.3542 | 0 | 13.2595 | 37.78
2021-01-14 09:00 | 44210.375 | 0 | 13.6384 | 37.78
2021-01-14 09:30 | 44210.3958 | 0 | 13.9277 | 37.78
2021-01-14 10:00 | 44210.4167 | 0 | 13.8836 | 37.78
2021-01-14 10:30 | 44210.4375 | 0 | 14.6241 | 37.78
2021-01-14 11:00 | 44210.4583 | 0 | 14.5267 | 37.78
2021-01-14 11:30 | 44210.4792 | 0 | 14.6538 | 37.78
2021-01-14 12:00 | 44210.5 | 0 | 15.0911 | 37.78
2021-01-14 12:30 | 44210.5208 | 0 | 15.0955 | 37.78
2021-01-14 13:00 | 44210.5417 | 0 | 15.4361 | 37.78
2021-01-14 13:30 | 44210.5625 | 0 | 15.5882 | 37.78
2021-01-14 14:00 | 44210.5833 | 0 | 16.3396 | 37.78
2021-01-14 14:30 | 44210.6042 | 0 | 16.5905 | 37.78
2021-01-14 15:00 | 44210.625 | 0 | 16.946 | 37.78
2021-01-14 15:30 | 44210.6458 | 0 | 17.2857 | 37.78
2021-01-14 16:00 | 44210.6667 | 0 | 17.618 | 37.78
2021-01-14 16:30 | 44210.6875 | 0 | 18.0185 | 37.78
2021-01-14 17:00 | 44210.7083 | 0 | 18.1356 | 37.78
2021-01-14 17:30 | 44210.7292 | 0 | 18.2175 | 37.78
2021-01-14 18:00 | 44210.75 | 0 | 17.6021 | 37.78
2021-01-14 18:30 | 44210.7708 | 0 | 17.5787 | 37.78
2021-01-14 19:00 | 44210.7917 | 0 | 17.5357 | 37.78
2021-01-14 19:30 | 44210.8125 | 0 | 17.5716 | 37.78
2021-01-14 20:00 | 44210.8333 | 0 | 17.1704 | 37.78
2021-01-14 20:30 | 44210.8542 | 0 | 16.6865 | 37.78
2021-01-14 21:00 | 44210.875 | 0 | 16.1218 | 37.78
2021-01-14 21:30 | 44210.8958 | 0 | 15.6388 | 37.78
2021-01-14 22:00 | 44210.9167 | 0 | 14.9539 | 37.78
2021-01-14 22:30 | 44210.9375 | 0 | 13.914 | 37.78
2021-01-14 23:00 | 44210.9583 | 0 | 13.1336 | 37.78
2021-01-14 23:30 | 44210.9792 | 0 | 12.4947 | 37.78
2021-01-15 | 44211 | 0 | 11.6624 | 37.78
2021-01-15 00:30 | 44211.0208 | 0 | 11.2644 | 37.78
2021-01-15 01:00 | 44211.0417 | 0 | 10.9013 | 37.78
2021-01-15 01:30 | 44211.0625 | 0 | 10.5333 | 37.78
2021-01-15 02:00 | 44211.0833 | 0 | 10.4518 | 37.78
2021-01-15 02:30 | 44211.1042 | 0 | 10.3353 | 37.78
2021-01-15 03:00 | 44211.125 | 0 | 10.156 | 37.78
2021-01-15 03:30 | 44211.1458 | 0 | 10.157 | 37.78
2021-01-15 04:00 | 44211.1667 | 0 | 10.2224 | 37.78
2021-01-15 04:30 | 44211.1875 | 0 | 10.2418 | 37.78
2021-01-15 05:00 | 44211.2083 | 0 | 10.1911 | 37.78
2021-01-15 05:30 | 44211.2292 | 0 | 10.1806 | 37.78
2021-01-15 06:00 | 44211.25 | 0 | 10.2254 | 37.78
2021-01-15 06:30 | 44211.2708 | 0 | 10.2936 | 37.78
2021-01-15 07:00 | 44211.2917 | 0 | 10.3626 | 37.78
2021-01-15 07:30 | 44211.3125 | 0 | 10.5044 | 37.78
2021-01-15 08:00 | 44211.3333 | 0 | 11.0419 | 37.78
2021-01-15 08:30 | 44211.3542 | 0 | 11.5881 | 37.78
2021-01-15 09:00 | 44211.375 | 0 | 11.7307 | 37.78
2021-01-15 09:30 | 44211.3958 | 0 | 12.6289 | 37.78
2021-01-15 10:00 | 44211.4167 | 0 | 12.6416 | 37.78
2021-01-15 10:30 | 44211.4375 | 0 | 13.164 | 37.78
2021-01-15 11:00 | 44211.4583 | 0 | 13.9218 | 37.78
2021-01-15 11:30 | 44211.4792 | 0 | 14.3422 | 37.78
2021-01-15 12:00 | 44211.5 | 0 | 16.0763 | 37.78
2021-01-15 12:30 | 44211.5208 | 0 | 17.7096 | 37.78
2021-01-15 13:00 | 44211.5417 | 0 | 17.5516 | 37.78
2021-01-15 13:30 | 44211.5625 | 0 | 17.9038 | 37.78
2021-01-15 14:00 | 44211.5833 | 0 | 16.1044 | 37.78
2021-01-15 14:30 | 44211.6042 | 0 | 18.1088 | 37.78
2021-01-15 15:00 | 44211.625 | 0 | 17.7911 | 37.78
2021-01-15 15:30 | 44211.6458 | 0 | 14.424 | 37.78
2021-01-15 16:00 | 44211.6667 | 0 | 14.6461 | 37.78
2021-01-15 16:30 | 44211.6875 | 0 | 14.7817 | 37.78
2021-01-15 17:00 | 44211.7083 | 0 | 14.7534 | 37.78
2021-01-15 17:30 | 44211.7292 | 0 | 14.7134 | 37.78
2021-01-15 18:00 | 44211.75 | 0 | 15.11 | 37.78
2021-01-15 18:30 | 44211.7708 | 0 | 15.1909 | 37.78
2021-01-15 19:00 | 44211.7917 | 0 | 15.2718 | 37.78
2021-01-15 19:30 | 44211.8125 | 0 | 14.8988 | 37.78
2021-01-15 20:00 | 44211.8333 | 0 | 14.6167 | 37.78
2021-01-15 20:30 | 44211.8542 | 0 | 13.956 | 37.78
2021-01-15 21:00 | 44211.875 | 0 | 13.4902 | 37.78
2021-01-15 21:30 | 44211.8958 | 0 | 12.9516 | 37.78
2021-01-15 22:00 | 44211.9167 | 0 | 12.3276 | 37.78
2021-01-15 22:30 | 44211.9375 | 0 | 11.6603 | 37.78
2021-01-15 23:00 | 44211.9583 | 0 | 10.9893 | 37.78
2021-01-15 23:30 | 44211.9792 | 0 | 10.5987 | 37.78
2021-01-16 | 44212 | 0 | 9.961 | 37.78
2021-01-16 00:30 | 44212.0208 | 0 | 9.6994 | 37.78
2021-01-16 01:00 | 44212.0417 | 0 | 9.2814 | 37.78
2021-01-16 01:30 | 44212.0625 | 0 | 9.2218 | 37.78
2021-01-16 02:00 | 44212.0833 | 0 | 9.198 | 37.78
2021-01-16 02:30 | 44212.1042 | 0 | 8.9209 | 37.78
2021-01-16 03:00 | 44212.125 | 0 | 8.7608 | 37.78
2021-01-16 03:30 | 44212.1458 | 0 | 8.656 | 37.78
2021-01-16 04:00 | 44212.1667 | 0 | 8.4328 | 37.78
2021-01-16 04:30 | 44212.1875 | 0 | 8.5148 | 37.78
2021-01-16 05:00 | 44212.2083 | 0 | 8.4729 | 37.78
2021-01-16 05:30 | 44212.2292 | 0 | 8.5103 | 37.78
2021-01-16 06:00 | 44212.25 | 0 | 8.7353 | 37.78
2021-01-16 06:30 | 44212.2708 | 0 | 8.7694 | 37.78
2021-01-16 07:00 | 44212.2917 | 0 | 9.105 | 37.78
2021-01-16 07:30 | 44212.3125 | 0 | 9.2413 | 37.78
2021-01-16 08:00 | 44212.3333 | 0 | 9.2433 | 37.78
2021-01-16 08:30 | 44212.3542 | 0 | 9.3754 | 37.78
2021-01-16 09:00 | 44212.375 | 0 | 9.5348 | 37.78
2021-01-16 09:30 | 44212.3958 | 0 | 9.4965 | 37.78
2021-01-16 10:00 | 44212.4167 | 0 | 9.0827 | 37.78
2021-01-16 10:30 | 44212.4375 | 0 | 9.1143 | 37.78
2021-01-16 11:00 | 44212.4583 | 0 | 9.4648 | 37.78
2021-01-16 11:30 | 44212.4792 | 0 | 9.6188 | 37.78
2021-01-16 12:00 | 44212.5 | 0 | 9.7625 | 37.78
2021-01-16 12:30 | 44212.5208 | 0 | 10.5057 | 37.78
2021-01-16 13:00 | 44212.5417 | 0 | 9.6695 | 37.78
2021-01-16 13:30 | 44212.5625 | 0 | 10.798 | 37.78
2021-01-16 14:00 | 44212.5833 | 0 | 11.2026 | 37.78
2021-01-16 14:30 | 44212.6042 | 0 | 11.6738 | 37.78
2021-01-16 15:00 | 44212.625 | 0 | 12.2906 | 37.78
2021-01-16 15:30 | 44212.6458 | 0 | 11.98 | 37.78
2021-01-16 16:00 | 44212.6667 | 0 | 12.3873 | 37.78
2021-01-16 16:30 | 44212.6875 | 0 | 13.2412 | 37.78
2021-01-16 17:00 | 44212.7083 | 0 | 14 | 37.78
2021-01-16 17:30 | 44212.7292 | 0 | 14.5171 | 37.78
2021-01-16 18:00 | 44212.75 | 0 | 14.7487 | 37.78
2021-01-16 18:30 | 44212.7708 | 0 | 15.1964 | 37.78
2021-01-16 19:00 | 44212.7917 | 0 | 15.4992 | 37.78
2021-01-16 19:30 | 44212.8125 | 0 | 15.4602 | 37.78
2021-01-16 20:00 | 44212.8333 | 0 | 15.4284 | 37.78
2021-01-16 20:30 | 44212.8542 | 0 | 14.8898 | 37.78
2021-01-16 21:00 | 44212.875 | 0 | 14.3815 | 37.78
2021-01-16 21:30 | 44212.8958 | 0 | 13.9754 | 37.78
2021-01-16 22:00 | 44212.9167 | 0 | 13.3373 | 37.78
2021-01-16 22:30 | 44212.9375 | 0 | 12.4369 | 37.78
2021-01-16 23:00 | 44212.9583 | 0 | 11.7837 | 37.78
2021-01-16 23:30 | 44212.9792 | 0 | 11.112 | 37.78
2021-01-17 | 44213 | 0 | 10.6943 | 37.78
2021-01-17 00:30 | 44213.0208 | 0 | 10.4009 | 37.78
2021-01-17 01:00 | 44213.0417 | 0 | 10.1972 | 37.78
2021-01-17 01:30 | 44213.0625 | 0 | 10.138 | 37.78
2021-01-17 02:00 | 44213.0833 | 0 | 10.09 | 37.78
2021-01-17 02:30 | 44213.1042 | 0 | 9.8798 | 37.78
2021-01-17 03:00 | 44213.125 | 0 | 9.8546 | 37.78
2021-01-17 03:30 | 44213.1458 | 0 | 10.0592 | 37.78
2021-01-17 04:00 | 44213.1667 | 0 | 10.2 | 37.78
2021-01-17 04:30 | 44213.1875 | 0 | 10.5196 | 37.78
2021-01-17 05:00 | 44213.2083 | 0 | 11.1313 | 37.78
2021-01-17 05:30 | 44213.2292 | 0 | 11.7666 | 37.78
2021-01-17 06:00 | 44213.25 | 0 | 12.2435 | 37.78
2021-01-17 06:30 | 44213.2708 | 0 | 12.9529 | 37.78
2021-01-17 07:00 | 44213.2917 | 0 | 14.3722 | 37.78
2021-01-17 07:30 | 44213.3125 | 0 | 13.8108 | 37.78
2021-01-17 08:00 | 44213.3333 | 0 | 15.4705 | 37.78
2021-01-17 08:30 | 44213.3542 | 0 | 15.5963 | 37.78
2021-01-17 09:00 | 44213.375 | 0 | 15.2764 | 37.78
2021-01-17 09:30 | 44213.3958 | 0 | 15.6727 | 37.78
2021-01-17 10:00 | 44213.4167 | 0 | 15.0936 | 37.78
2021-01-17 10:30 | 44213.4375 | 0 | 16.6358 | 37.78
2021-01-17 11:00 | 44213.4583 | 0 | 15.1832 | 37.78
2021-01-17 11:30 | 44213.4792 | 0 | 16.474 | 37.78
2021-01-17 12:00 | 44213.5 | 0 | 15.1367 | 37.78
2021-01-17 12:30 | 44213.5208 | 0 | 15.5257 | 37.78
2021-01-17 13:00 | 44213.5417 | 0 | 16.6005 | 37.78
2021-01-17 13:30 | 44213.5625 | 0 | 17.5665 | 37.78
2021-01-17 14:00 | 44213.5833 | 0 | 19.7129 | 37.78
2021-01-17 14:30 | 44213.6042 | 0 | 19.4414 | 37.78
2021-01-17 15:00 | 44213.625 | 0 | 18.684 | 37.78
2021-01-17 15:30 | 44213.6458 | 0 | 17.9996 | 37.78
2021-01-17 16:00 | 44213.6667 | 0 | 18.0277 | 37.78
2021-01-17 16:30 | 44213.6875 | 0 | 18.4392 | 37.78
2021-01-17 17:00 | 44213.7083 | 0 | 18.0606 | 37.78
2021-01-17 17:30 | 44213.7292 | 0 | 17.6999 | 37.78
2021-01-17 18:00 | 44213.75 | 0 | 17.4364 | 37.78
2021-01-17 18:30 | 44213.7708 | 0 | 16.7314 | 37.78
2021-01-17 19:00 | 44213.7917 | 0 | 16.0956 | 37.78
2021-01-17 19:30 | 44213.8125 | 0 | 15.7081 | 37.78
2021-01-17 20:00 | 44213.8333 | 0 | 15.4166 | 37.78
2021-01-17 20:30 | 44213.8542 | 0 | 14.503 | 37.78
2021-01-17 21:00 | 44213.875 | 0 | 13.7892 | 37.78
2021-01-17 21:30 | 44213.8958 | 0 | 13.1108 | 37.78
2021-01-17 22:00 | 44213.9167 | 0 | 12.5478 | 37.78
2021-01-17 22:30 | 44213.9375 | 0 | 11.5094 | 37.78
2021-01-17 23:00 | 44213.9583 | 0 | 11.0338 | 37.78
2021-01-17 23:30 | 44213.9792 | 0 | 10.3922 | 37.78
2021-01-18 | 44214 | 0 | 9.8349 | 37.78
2021-01-18 00:30 | 44214.0208 | 0 | 9.3773 | 37.78
2021-01-18 01:00 | 44214.0417 | 0 | 9.2041 | 37.78
2021-01-18 01:30 | 44214.0625 | 0 | 9.0668 | 37.78
2021-01-18 02:00 | 44214.0833 | 0 | 8.9657 | 37.78
2021-01-18 02:30 | 44214.1042 | 0 | 8.9494 | 37.78
2021-01-18 03:00 | 44214.125 | 0 | 8.8229 | 37.78
2021-01-18 03:30 | 44214.1458 | 0 | 8.8988 | 37.78
2021-01-18 04:00 | 44214.1667 | 0 | 9.0258 | 37.78
2021-01-18 04:30 | 44214.1875 | 0 | 9.474 | 37.78
2021-01-18 05:00 | 44214.2083 | 0 | 9.9722 | 37.78
2021-01-18 05:30 | 44214.2292 | 0 | 10.5603 | 37.78
2021-01-18 06:00 | 44214.25 | 0 | 11.0982 | 37.78
2021-01-18 06:30 | 44214.2708 | 0 | 11.8676 | 37.78
2021-01-18 07:00 | 44214.2917 | 0 | 12.4718 | 37.78
2021-01-18 07:30 | 44214.3125 | 0 | 12.4125 | 37.78
2021-01-18 08:00 | 44214.3333 | 0 | 12.8607 | 37.78
2021-01-18 08:30 | 44214.3542 | 0 | 11.8553 | 37.78
2021-01-18 09:00 | 44214.375 | 0 | 12.8442 | 37.78
2021-01-18 09:30 | 44214.3958 | 0 | 12.7242 | 37.78
2021-01-18 10:00 | 44214.4167 | 0 | 12.5539 | 37.78
2021-01-18 10:30 | 44214.4375 | 0 | 12.6895 | 37.78
2021-01-18 11:00 | 44214.4583 | 0 | 11.3962 | 37.78
2021-01-18 11:30 | 44214.4792 | 0 | 11.3079 | 37.78
2021-01-18 12:00 | 44214.5 | 0 | 12.7603 | 37.78
2021-01-18 12:30 | 44214.5208 | 0 | 13.0357 | 37.78
2021-01-18 13:00 | 44214.5417 | 0 | 13.394 | 37.78
2021-01-18 13:30 | 44214.5625 | 0 | 14.2756 | 37.78
2021-01-18 14:00 | 44214.5833 | 0 | 15.6034 | 37.78
2021-01-18 14:30 | 44214.6042 | 0 | 16.5215 | 37.78
2021-01-18 15:00 | 44214.625 | 0 | 17.5772 | 37.78
2021-01-18 15:30 | 44214.6458 | 0 | 16.9486 | 37.78
2021-01-18 16:00 | 44214.6667 | 0 | 17.2381 | 37.78
2021-01-18 16:30 | 44214.6875 | 0 | 17.3673 | 37.78
2021-01-18 17:00 | 44214.7083 | 0 | 17.6459 | 37.78
2021-01-18 17:30 | 44214.7292 | 0 | 17.9006 | 37.78
2021-01-18 18:00 | 44214.75 | 0 | 17.8717 | 37.78
2021-01-18 18:30 | 44214.7708 | 0 | 17.8244 | 37.78
2021-01-18 19:00 | 44214.7917 | 0 | 17.7247 | 37.78
2021-01-18 19:30 | 44214.8125 | 0 | 17.4951 | 37.78
2021-01-18 20:00 | 44214.8333 | 0 | 16.8598 | 37.78
2021-01-18 20:30 | 44214.8542 | 0 | 16.0162 | 37.78
2021-01-18 21:00 | 44214.875 | 0 | 15.4258 | 37.78
2021-01-18 21:30 | 44214.8958 | 0 | 14.7867 | 37.78
2021-01-18 22:00 | 44214.9167 | 0 | 14.0444 | 37.78
2021-01-18 22:30 | 44214.9375 | 0 | 12.9226 | 37.78
2021-01-18 23:00 | 44214.9583 | 0 | 12.1073 | 37.78
2021-01-18 23:30 | 44214.9792 | 0 | 11.2731 | 37.78
2021-01-19 | 44215 | 0 | 10.6686 | 37.78
2021-01-19 00:30 | 44215.0208 | 0 | 10.3684 | 37.78
2021-01-19 01:00 | 44215.0417 | 0 | 10.2076 | 37.78
2021-01-19 01:30 | 44215.0625 | 0 | 9.933 | 37.78
2021-01-19 02:00 | 44215.0833 | 0 | 9.7189 | 37.78
2021-01-19 02:30 | 44215.1042 | 0 | 9.6416 | 37.78
2021-01-19 03:00 | 44215.125 | 0 | 9.615 | 37.78
2021-01-19 03:30 | 44215.1458 | 0 | 9.5464 | 37.78
2021-01-19 04:00 | 44215.1667 | 0 | 9.7345 | 37.78
2021-01-19 04:30 | 44215.1875 | 0 | 9.993 | 37.78
2021-01-19 05:00 | 44215.2083 | 0 | 10.3553 | 37.78
2021-01-19 05:30 | 44215.2292 | 0 | 10.9343 | 37.78
2021-01-19 06:00 | 44215.25 | 0 | 11.7659 | 37.78
2021-01-19 06:30 | 44215.2708 | 0 | 12.0281 | 37.78
2021-01-19 07:00 | 44215.2917 | 0 | 12.606 | 37.78
2021-01-19 07:30 | 44215.3125 | 0 | 13.1469 | 37.78
2021-01-19 08:00 | 44215.3333 | 0 | 14.3565 | 37.78
2021-01-19 08:30 | 44215.3542 | 0 | 14.1873 | 37.78
2021-01-19 09:00 | 44215.375 | 0 | 14.4508 | 37.78
2021-01-19 09:30 | 44215.3958 | 0 | 14.6054 | 37.78
2021-01-19 10:00 | 44215.4167 | 0 | 13.9345 | 37.78
2021-01-19 10:30 | 44215.4375 | 0 | 13.5722 | 37.78
2021-01-19 11:00 | 44215.4583 | 0 | 15.1604 | 37.78
2021-01-19 11:30 | 44215.4792 | 0 | 13.5743 | 37.78
2021-01-19 12:00 | 44215.5 | 0 | 13.8167 | 37.78
2021-01-19 12:30 | 44215.5208 | 0 | 15.097 | 37.78
2021-01-19 13:00 | 44215.5417 | 0 | 13.8524 | 37.78
2021-01-19 13:30 | 44215.5625 | 0 | 14.7468 | 37.78
2021-01-19 14:00 | 44215.5833 | 0 | 13.1455 | 37.78
2021-01-19 14:30 | 44215.6042 | 0 | 14.3104 | 37.78
2021-01-19 15:00 | 44215.625 | 0 | 14.3382 | 37.78
2021-01-19 15:30 | 44215.6458 | 0 | 14.2157 | 37.78
2021-01-19 16:00 | 44215.6667 | 0 | 13.8441 | 37.78
2021-01-19 16:30 | 44215.6875 | 0 | 13.8185 | 37.78
2021-01-19 17:00 | 44215.7083 | 0 | 14.275 | 37.78
2021-01-19 17:30 | 44215.7292 | 0 | 14.3912 | 37.78
2021-01-19 18:00 | 44215.75 | 0 | 14.6861 | 37.78
2021-01-19 18:30 | 44215.7708 | 0 | 14.9555 | 37.78
2021-01-19 19:00 | 44215.7917 | 0 | 15.0628 | 37.78
2021-01-19 19:30 | 44215.8125 | 0 | 14.9389 | 37.78
2021-01-19 20:00 | 44215.8333 | 0 | 14.6571 | 37.78
2021-01-19 20:30 | 44215.8542 | 0 | 14.0767 | 37.78
2021-01-19 21:00 | 44215.875 | 0 | 13.6358 | 37.78
2021-01-19 21:30 | 44215.8958 | 0 | 13.1309 | 37.78
2021-01-19 22:00 | 44215.9167 | 0 | 12.518 | 37.78
2021-01-19 22:30 | 44215.9375 | 0 | 11.6042 | 37.78
2021-01-19 23:00 | 44215.9583 | 0 | 11.0734 | 37.78
2021-01-19 23:30 | 44215.9792 | 0 | 10.497 | 37.78
2021-01-20 | 44216 | 0 | 9.9197 | 37.78
2021-01-20 00:30 | 44216.0208 | 0 | 9.4438 | 37.78
2021-01-20 01:00 | 44216.0417 | 0 | 9.2308 | 37.78
2021-01-20 01:30 | 44216.0625 | 0 | 9.1115 | 37.78
2021-01-20 02:00 | 44216.0833 | 0 | 9.0181 | 37.78
2021-01-20 02:30 | 44216.1042 | 0 | 8.7409 | 37.78
2021-01-20 03:00 | 44216.125 | 0 | 8.7737 | 37.78
2021-01-20 03:30 | 44216.1458 | 0 | 8.8486 | 37.78
2021-01-20 04:00 | 44216.1667 | 0 | 9.1389 | 37.78
2021-01-20 04:30 | 44216.1875 | 0 | 9.3877 | 37.78
2021-01-20 05:00 | 44216.2083 | 0 | 9.8581 | 37.78
2021-01-20 05:30 | 44216.2292 | 0 | 10.2739 | 37.78
2021-01-20 06:00 | 44216.25 | 0 | 10.8868 | 37.78
2021-01-20 06:30 | 44216.2708 | 0 | 11.5679 | 37.78
2021-01-20 07:00 | 44216.2917 | 0 | 12.1621 | 37.78
2021-01-20 07:30 | 44216.3125 | 0 | 12.2924 | 37.78
2021-01-20 08:00 | 44216.3333 | 0 | 12.4998 | 37.78
2021-01-20 08:30 | 44216.3542 | 0 | 12.8626 | 37.78
2021-01-20 09:00 | 44216.375 | 0 | 13.1903 | 37.78
2021-01-20 09:30 | 44216.3958 | 0 | 12.8907 | 37.78
2021-01-20 10:00 | 44216.4167 | 0 | 13.8335 | 37.78
2021-01-20 10:30 | 44216.4375 | 0 | 13.1351 | 37.78
2021-01-20 11:00 | 44216.4583 | 0 | 13.3213 | 37.78
2021-01-20 11:30 | 44216.4792 | 0 | 12.9367 | 37.78
2021-01-20 12:00 | 44216.5 | 0 | 12.3964 | 37.78
2021-01-20 12:30 | 44216.5208 | 0 | 13.2022 | 37.78
2021-01-20 13:00 | 44216.5417 | 0 | 13.3274 | 37.78
2021-01-20 13:30 | 44216.5625 | 0 | 13.8728 | 37.78
2021-01-20 14:00 | 44216.5833 | 0 | 13.8448 | 37.78
2021-01-20 14:30 | 44216.6042 | 0 | 12.4472 | 37.78
2021-01-20 15:00 | 44216.625 | 0 | 13.3286 | 37.78
2021-01-20 15:30 | 44216.6458 | 0 | 13.9273 | 37.78
2021-01-20 16:00 | 44216.6667 | 0 | 13.612 | 37.78
2021-01-20 16:30 | 44216.6875 | 0 | 13.8509 | 37.78
2021-01-20 17:00 | 44216.7083 | 0 | 13.7152 | 37.78
2021-01-20 17:30 | 44216.7292 | 0 | 13.6627 | 37.78
2021-01-20 18:00 | 44216.75 | 0 | 13.7262 | 37.78
2021-01-20 18:30 | 44216.7708 | 0 | 14.3252 | 37.78
2021-01-20 19:00 | 44216.7917 | 0 | 14.3197 | 37.78
2021-01-20 19:30 | 44216.8125 | 0 | 14.2603 | 37.78
2021-01-20 20:00 | 44216.8333 | 0 | 14.1987 | 37.78
2021-01-20 20:30 | 44216.8542 | 0 | 13.7434 | 37.78
2021-01-20 21:00 | 44216.875 | 0 | 13.2128 | 37.78
2021-01-20 21:30 | 44216.8958 | 0 | 12.8351 | 37.78
2021-01-20 22:00 | 44216.9167 | 0 | 12.4119 | 37.78
2021-01-20 22:30 | 44216.9375 | 0 | 11.6069 | 37.78
2021-01-20 23:00 | 44216.9583 | 0 | 10.9043 | 37.78
2021-01-20 23:30 | 44216.9792 | 0 | 10.3487 | 37.78
2021-01-21 | 44217 | 0 | 9.4647 | 37.78
2021-01-21 00:30 | 44217.0208 | 0 | 9.2202 | 37.78
2021-01-21 01:00 | 44217.0417 | 0 | 8.9717 | 37.78
2021-01-21 01:30 | 44217.0625 | 0 | 8.7825 | 37.78
2021-01-21 02:00 | 44217.0833 | 0 | 8.6277 | 37.78
2021-01-21 02:30 | 44217.1042 | 0 | 8.5607 | 37.78
2021-01-21 03:00 | 44217.125 | 0 | 8.5058 | 37.78
2021-01-21 03:30 | 44217.1458 | 0 | 8.5938 | 37.78
2021-01-21 04:00 | 44217.1667 | 0 | 8.8768 | 37.78
2021-01-21 04:30 | 44217.1875 | 0 | 9.2745 | 37.78
2021-01-21 05:00 | 44217.2083 | 0 | 9.618 | 37.78
2021-01-21 05:30 | 44217.2292 | 0 | 9.8216 | 37.78
2021-01-21 06:00 | 44217.25 | 0 | 10.459 | 37.78
2021-01-21 06:30 | 44217.2708 | 0 | 10.9298 | 37.78
2021-01-21 07:00 | 44217.2917 | 0 | 11.688 | 37.78
2021-01-21 07:30 | 44217.3125 | 0 | 11.8901 | 37.78
2021-01-21 08:00 | 44217.3333 | 0 | 11.6522 | 37.78
2021-01-21 08:30 | 44217.3542 | 0 | 11.9572 | 37.78
2021-01-21 09:00 | 44217.375 | 0 | 12.3337 | 37.78
2021-01-21 09:30 | 44217.3958 | 0 | 13.2587 | 37.78
2021-01-21 10:00 | 44217.4167 | 0 | 13.4715 | 37.78
2021-01-21 10:30 | 44217.4375 | 0 | 12.2376 | 37.78
2021-01-21 11:00 | 44217.4583 | 0 | 11.6979 | 37.78
2021-01-21 11:30 | 44217.4792 | 0 | 12.0677 | 37.78
2021-01-21 12:00 | 44217.5 | 0 | 11.8342 | 37.78
2021-01-21 12:30 | 44217.5208 | 0 | 12.1129 | 37.78
2021-01-21 13:00 | 44217.5417 | 0 | 12.1791 | 37.78
2021-01-21 13:30 | 44217.5625 | 0 | 12.6599 | 37.78
2021-01-21 14:00 | 44217.5833 | 0 | 13.0138 | 37.78
2021-01-21 14:30 | 44217.6042 | 0 | 13.8414 | 37.78
2021-01-21 15:00 | 44217.625 | 0 | 14.1602 | 37.78
2021-01-21 15:30 | 44217.6458 | 0 | 14.8118 | 37.78
2021-01-21 16:00 | 44217.6667 | 0 | 14.9177 | 37.78
2021-01-21 16:30 | 44217.6875 | 0 | 14.4651 | 37.78
2021-01-21 17:00 | 44217.7083 | 0 | 14.5403 | 37.78
2021-01-21 17:30 | 44217.7292 | 0 | 14.7444 | 37.78
2021-01-21 18:00 | 44217.75 | 0 | 14.8809 | 37.78
2021-01-21 18:30 | 44217.7708 | 0 | 14.9657 | 37.78
2021-01-21 19:00 | 44217.7917 | 0 | 14.9512 | 37.78
2021-01-21 19:30 | 44217.8125 | 0 | 15.0136 | 37.78
2021-01-21 20:00 | 44217.8333 | 0 | 14.7138 | 37.78
2021-01-21 20:30 | 44217.8542 | 0 | 14.1854 | 37.78
2021-01-21 21:00 | 44217.875 | 0 | 13.7482 | 37.78
2021-01-21 21:30 | 44217.8958 | 0 | 13.3325 | 37.78
2021-01-21 22:00 | 44217.9167 | 0 | 12.8726 | 37.78
2021-01-21 22:30 | 44217.9375 | 0 | 11.863 | 37.78
2021-01-21 23:00 | 44217.9583 | 0 | 11.2313 | 37.78
2021-01-21 23:30 | 44217.9792 | 0 | 10.6266 | 37.78
2021-01-22 | 44218 | 0 | 10.0258 | 37.78
2021-01-22 00:30 | 44218.0208 | 0 | 9.817 | 37.78
2021-01-22 01:00 | 44218.0417 | 0 | 9.4407 | 37.78
2021-01-22 01:30 | 44218.0625 | 0 | 9.0605 | 37.78
2021-01-22 02:00 | 44218.0833 | 0 | 8.9346 | 37.78
2021-01-22 02:30 | 44218.1042 | 0 | 8.738 | 37.78
2021-01-22 03:00 | 44218.125 | 0 | 8.4894 | 37.78
2021-01-22 03:30 | 44218.1458 | 0 | 8.5191 | 37.78
2021-01-22 04:00 | 44218.1667 | 0 | 8.5848 | 37.78
2021-01-22 04:30 | 44218.1875 | 0 | 8.5071 | 37.78
2021-01-22 05:00 | 44218.2083 | 0 | 8.5148 | 37.78
2021-01-22 05:30 | 44218.2292 | 0 | 8.5026 | 37.78
2021-01-22 06:00 | 44218.25 | 0 | 8.4657 | 37.78
2021-01-22 06:30 | 44218.2708 | 0 | 8.6071 | 37.78
2021-01-22 07:00 | 44218.2917 | 0 | 8.5924 | 37.78
2021-01-22 07:30 | 44218.3125 | 0 | 8.9337 | 37.78
2021-01-22 08:00 | 44218.3333 | 0 | 9.1919 | 37.78
2021-01-22 08:30 | 44218.3542 | 0 | 9.7056 | 37.78
2021-01-22 09:00 | 44218.375 | 0 | 10.9465 | 37.78
2021-01-22 09:30 | 44218.3958 | 0 | 10.7294 | 37.78
2021-01-22 10:00 | 44218.4167 | 0 | 11.3446 | 37.78
2021-01-22 10:30 | 44218.4375 | 0 | 10.4717 | 37.78
2021-01-22 11:00 | 44218.4583 | 0 | 9.0563 | 37.78
2021-01-22 11:30 | 44218.4792 | 0 | 8.7431 | 37.78
2021-01-22 12:00 | 44218.5 | 0 | 8.784 | 37.78
2021-01-22 12:30 | 44218.5208 | 0 | 8.7395 | 37.78
2021-01-22 13:00 | 44218.5417 | 0 | 9.0983 | 37.78
2021-01-22 13:30 | 44218.5625 | 0 | 9.3592 | 37.78
2021-01-22 14:00 | 44218.5833 | 0 | 9.7321 | 37.78
2021-01-22 14:30 | 44218.6042 | 0 | 10.1332 | 37.78
2021-01-22 15:00 | 44218.625 | 0 | 10.5255 | 37.78
2021-01-22 15:30 | 44218.6458 | 0 | 11.1016 | 37.78
2021-01-22 16:00 | 44218.6667 | 0 | 11.6605 | 37.78
2021-01-22 16:30 | 44218.6875 | 0 | 12.2284 | 37.78
2021-01-22 17:00 | 44218.7083 | 0 | 12.6761 | 37.78
2021-01-22 17:30 | 44218.7292 | 0 | 13.1104 | 37.78
2021-01-22 18:00 | 44218.75 | 0 | 13.1939 | 37.78
2021-01-22 18:30 | 44218.7708 | 0 | 13.273 | 37.78
2021-01-22 19:00 | 44218.7917 | 0 | 13.3059 | 37.78
2021-01-22 19:30 | 44218.8125 | 0 | 13.2104 | 37.78
2021-01-22 20:00 | 44218.8333 | 0 | 12.9915 | 37.78
2021-01-22 20:30 | 44218.8542 | 0 | 12.4224 | 37.78
2021-01-22 21:00 | 44218.875 | 0 | 11.9536 | 37.78
2021-01-22 21:30 | 44218.8958 | 0 | 11.6381 | 37.78
2021-01-22 22:00 | 44218.9167 | 0 | 11.1731 | 37.78
2021-01-22 22:30 | 44218.9375 | 0 | 10.4842 | 37.78
2021-01-22 23:00 | 44218.9583 | 0 | 10.0229 | 37.78
2021-01-22 23:30 | 44218.9792 | 0 | 9.5879 | 37.78
2021-01-23 | 44219 | 0 | 9.0011 | 37.78
2021-01-23 00:30 | 44219.0208 | 0 | 8.6293 | 37.78
2021-01-23 01:00 | 44219.0417 | 0 | 8.4237 | 37.78
2021-01-23 01:30 | 44219.0625 | 0 | 8.1987 | 37.78
2021-01-23 02:00 | 44219.0833 | 0 | 8.1248 | 37.78
2021-01-23 02:30 | 44219.1042 | 0 | 7.8867 | 37.78
2021-01-23 03:00 | 44219.125 | 0 | 7.7686 | 37.78
2021-01-23 03:30 | 44219.1458 | 0 | 7.76 | 37.78
2021-01-23 04:00 | 44219.1667 | 0 | 7.6705 | 37.78
2021-01-23 04:30 | 44219.1875 | 0 | 7.7869 | 37.78
2021-01-23 05:00 | 44219.2083 | 0 | 7.861 | 37.78
2021-01-23 05:30 | 44219.2292 | 0 | 7.8655 | 37.78
2021-01-23 06:00 | 44219.25 | 0 | 7.7449 | 37.78
2021-01-23 06:30 | 44219.2708 | 0 | 7.6986 | 37.78
2021-01-23 07:00 | 44219.2917 | 0 | 7.1649 | 37.78
2021-01-23 07:30 | 44219.3125 | 0 | 7.6811 | 37.78
2021-01-23 08:00 | 44219.3333 | 0 | 7.168 | 37.78
2021-01-23 08:30 | 44219.3542 | 0 | 7.9554 | 37.78
2021-01-23 09:00 | 44219.375 | 0 | 7.915 | 37.78
2021-01-23 09:30 | 44219.3958 | 0 | 7.9614 | 37.78
2021-01-23 10:00 | 44219.4167 | 0 | 8.5476 | 37.78
2021-01-23 10:30 | 44219.4375 | 0 | 8.2509 | 37.78
2021-01-23 11:00 | 44219.4583 | 0 | 8.1907 | 37.78
2021-01-23 11:30 | 44219.4792 | 0 | 8.1066 | 37.78
2021-01-23 12:00 | 44219.5 | 0 | 8.3196 | 37.78
2021-01-23 12:30 | 44219.5208 | 0 | 8.5952 | 37.78
2021-01-23 13:00 | 44219.5417 | 0 | 10.1751 | 37.78
2021-01-23 13:30 | 44219.5625 | 0 | 9.6878 | 37.78
2021-01-23 14:00 | 44219.5833 | 0 | 10.0567 | 37.78
2021-01-23 14:30 | 44219.6042 | 0 | 10.4826 | 37.78
2021-01-23 15:00 | 44219.625 | 0 | 11.2152 | 37.78
2021-01-23 15:30 | 44219.6458 | 0 | 11.6245 | 37.78
2021-01-23 16:00 | 44219.6667 | 0 | 13.0464 | 37.78
2021-01-23 16:30 | 44219.6875 | 0 | 13.6696 | 37.78
2021-01-23 17:00 | 44219.7083 | 0 | 13.7388 | 37.78
2021-01-23 17:30 | 44219.7292 | 0 | 13.7527 | 37.78
2021-01-23 18:00 | 44219.75 | 0 | 13.8 | 37.78
2021-01-23 18:30 | 44219.7708 | 0 | 14.0129 | 37.78
2021-01-23 19:00 | 44219.7917 | 0 | 14.1036 | 37.78
2021-01-23 19:30 | 44219.8125 | 0 | 13.8291 | 37.78
2021-01-23 20:00 | 44219.8333 | 0 | 13.4258 | 37.78
2021-01-23 20:30 | 44219.8542 | 0 | 12.9411 | 37.78
2021-01-23 21:00 | 44219.875 | 0 | 12.5669 | 37.78
2021-01-23 21:30 | 44219.8958 | 0 | 12.2077 | 37.78
2021-01-23 22:00 | 44219.9167 | 0 | 11.7769 | 37.78
2021-01-23 22:30 | 44219.9375 | 0 | 10.8806 | 37.78
2021-01-23 23:00 | 44219.9583 | 0 | 10.4303 | 37.78
2021-01-23 23:30 | 44219.9792 | 0 | 9.9102 | 37.78
2021-01-24 | 44220 | 0 | 9.5182 | 37.78
2021-01-24 00:30 | 44220.0208 | 0 | 9.229 | 37.78
2021-01-24 01:00 | 44220.0417 | 0 | 9.1043 | 37.78
2021-01-24 01:30 | 44220.0625 | 0 | 8.9998 | 37.78
2021-01-24 02:00 | 44220.0833 | 0 | 8.9673 | 37.78
2021-01-24 02:30 | 44220.1042 | 0 | 8.8209 | 37.78
2021-01-24 03:00 | 44220.125 | 0 | 8.7349 | 37.78
2021-01-24 03:30 | 44220.1458 | 0 | 8.9348 | 37.78
2021-01-24 04:00 | 44220.1667 | 0 | 9.1549 | 37.78
2021-01-24 04:30 | 44220.1875 | 0 | 9.5394 | 37.78
2021-01-24 05:00 | 44220.2083 | 0 | 10.0068 | 37.78
2021-01-24 05:30 | 44220.2292 | 0 | 10.6374 | 37.78
2021-01-24 06:00 | 44220.25 | 0 | 11.2785 | 37.78
2021-01-24 06:30 | 44220.2708 | 0 | 11.7146 | 37.78
2021-01-24 07:00 | 44220.2917 | 0 | 12.4384 | 37.78
2021-01-24 07:30 | 44220.3125 | 0 | 12.5579 | 37.78
2021-01-24 08:00 | 44220.3333 | 0 | 13.137 | 37.78
2021-01-24 08:30 | 44220.3542 | 0 | 13.4958 | 37.78
2021-01-24 09:00 | 44220.375 | 0 | 14.0908 | 37.78
2021-01-24 09:30 | 44220.3958 | 0 | 13.5423 | 37.78
2021-01-24 10:00 | 44220.4167 | 0 | 12.6501 | 37.78
2021-01-24 10:30 | 44220.4375 | 0 | 13.7957 | 37.78
2021-01-24 11:00 | 44220.4583 | 0 | 14.3131 | 37.78
2021-01-24 11:30 | 44220.4792 | 0 | 13.0362 | 37.78
2021-01-24 12:00 | 44220.5 | 0 | 13.362 | 37.78
2021-01-24 12:30 | 44220.5208 | 0 | 12.45 | 37.78
2021-01-24 13:00 | 44220.5417 | 0 | 13.1726 | 37.78
2021-01-24 13:30 | 44220.5625 | 0 | 13.7895 | 37.78
2021-01-24 14:00 | 44220.5833 | 0 | 14.6137 | 37.78
2021-01-24 14:30 | 44220.6042 | 0 | 14.8381 | 37.78
2021-01-24 15:00 | 44220.625 | 0 | 15.3573 | 37.78
2021-01-24 15:30 | 44220.6458 | 0 | 15.6842 | 37.78
2021-01-24 16:00 | 44220.6667 | 0 | 16.3549 | 37.78
2021-01-24 16:30 | 44220.6875 | 0 | 15.8898 | 37.78
2021-01-24 17:00 | 44220.7083 | 0 | 15.4773 | 37.78
2021-01-24 17:30 | 44220.7292 | 0 | 15.7456 | 37.78
2021-01-24 18:00 | 44220.75 | 0 | 15.3613 | 37.78
2021-01-24 18:30 | 44220.7708 | 0 | 15.5645 | 37.78
2021-01-24 19:00 | 44220.7917 | 0 | 15.7861 | 37.78
2021-01-24 19:30 | 44220.8125 | 0 | 15.591 | 37.78
2021-01-24 20:00 | 44220.8333 | 0 | 15.2273 | 37.78
2021-01-24 20:30 | 44220.8542 | 0 | 14.5843 | 37.78
2021-01-24 21:00 | 44220.875 | 0 | 13.8985 | 37.78
2021-01-24 21:30 | 44220.8958 | 0 | 13.6123 | 37.78
2021-01-24 22:00 | 44220.9167 | 0 | 13.0973 | 37.78
2021-01-24 22:30 | 44220.9375 | 0 | 12.2763 | 37.78
2021-01-24 23:00 | 44220.9583 | 0 | 11.5529 | 37.78
2021-01-24 23:30 | 44220.9792 | 0 | 11.0453 | 37.78
2021-01-25 | 44221 | 0 | 10.2924 | 37.78
2021-01-25 00:30 | 44221.0208 | 0 | 9.7334 | 37.78
2021-01-25 01:00 | 44221.0417 | 0 | 9.4196 | 37.78
2021-01-25 01:30 | 44221.0625 | 0 | 9.1478 | 37.78
2021-01-25 02:00 | 44221.0833 | 0 | 8.8315 | 37.78
2021-01-25 02:30 | 44221.1042 | 0 | 8.6873 | 37.78
2021-01-25 03:00 | 44221.125 | 0 | 8.5937 | 37.78
2021-01-25 03:30 | 44221.1458 | 0 | 8.5547 | 37.78
2021-01-25 04:00 | 44221.1667 | 0 | 8.4863 | 37.78
2021-01-25 04:30 | 44221.1875 | 0 | 8.4226 | 37.78
2021-01-25 05:00 | 44221.2083 | 0 | 8.4703 | 37.78
2021-01-25 05:30 | 44221.2292 | 0 | 8.6444 | 37.78
2021-01-25 06:00 | 44221.25 | 0 | 8.6278 | 37.78
2021-01-25 06:30 | 44221.2708 | 0 | 8.3686 | 37.78
2021-01-25 07:00 | 44221.2917 | 0 | 8.6296 | 37.78
2021-01-25 07:30 | 44221.3125 | 0 | 8.8475 | 37.78
2021-01-25 08:00 | 44221.3333 | 0 | 9.0718 | 37.78
2021-01-25 08:30 | 44221.3542 | 0 | 9.2193 | 37.78
2021-01-25 09:00 | 44221.375 | 0 | 9.756 | 37.78
2021-01-25 09:30 | 44221.3958 | 0 | 10.0433 | 37.78
2021-01-25 10:00 | 44221.4167 | 0 | 9.9392 | 37.78
2021-01-25 10:30 | 44221.4375 | 0 | 9.986 | 37.78
2021-01-25 11:00 | 44221.4583 | 0 | 10.0923 | 37.78
2021-01-25 11:30 | 44221.4792 | 0 | 10.3866 | 37.78
2021-01-25 12:00 | 44221.5 | 0 | 10.5238 | 37.78
2021-01-25 12:30 | 44221.5208 | 0 | 10.7704 | 37.78
2021-01-25 13:00 | 44221.5417 | 0 | 11.0311 | 37.78
2021-01-25 13:30 | 44221.5625 | 0 | 11.3945 | 37.78
2021-01-25 14:00 | 44221.5833 | 0 | 12.1359 | 37.78
2021-01-25 14:30 | 44221.6042 | 0 | 12.5881 | 37.78
2021-01-25 15:00 | 44221.625 | 0 | 13.1972 | 37.78
2021-01-25 15:30 | 44221.6458 | 0 | 13.8196 | 37.78
2021-01-25 16:00 | 44221.6667 | 0 | 14.537 | 37.78
2021-01-25 16:30 | 44221.6875 | 0 | 15.4487 | 37.78
2021-01-25 17:00 | 44221.7083 | 0 | 16.0313 | 37.78
2021-01-25 17:30 | 44221.7292 | 0 | 16.4653 | 37.78
2021-01-25 18:00 | 44221.75 | 0 | 16.3682 | 37.78
2021-01-25 18:30 | 44221.7708 | 0 | 16.5087 | 37.78
2021-01-25 19:00 | 44221.7917 | 0 | 16.7332 | 37.78
2021-01-25 19:30 | 44221.8125 | 0 | 16.578 | 37.78
2021-01-25 20:00 | 44221.8333 | 0 | 16.2258 | 37.78
2021-01-25 20:30 | 44221.8542 | 0 | 15.4777 | 37.78
2021-01-25 21:00 | 44221.875 | 0 | 14.844 | 37.78
2021-01-25 21:30 | 44221.8958 | 0 | 14.2064 | 37.78
2021-01-25 22:00 | 44221.9167 | 0 | 13.2469 | 37.78
2021-01-25 22:30 | 44221.9375 | 0 | 12.2121 | 37.78
2021-01-25 23:00 | 44221.9583 | 0 | 11.4565 | 37.78
2021-01-25 23:30 | 44221.9792 | 0 | 10.9873 | 37.78
2021-01-26 | 44222 | 0 | 10.5061 | 37.78
2021-01-26 00:30 | 44222.0208 | 0 | 10.1091 | 37.78
2021-01-26 01:00 | 44222.0417 | 0 | 9.8838 | 37.78
2021-01-26 01:30 | 44222.0625 | 0 | 9.7576 | 37.78
2021-01-26 02:00 | 44222.0833 | 0 | 9.6462 | 37.78
2021-01-26 02:30 | 44222.1042 | 0 | 9.6014 | 37.78
2021-01-26 03:00 | 44222.125 | 0 | 9.4273 | 37.78
2021-01-26 03:30 | 44222.1458 | 0 | 9.4526 | 37.78
2021-01-26 04:00 | 44222.1667 | 0 | 9.5885 | 37.78
2021-01-26 04:30 | 44222.1875 | 0 | 10.0561 | 37.78
2021-01-26 05:00 | 44222.2083 | 0 | 10.3452 | 37.78
2021-01-26 05:30 | 44222.2292 | 0 | 10.9312 | 37.78
2021-01-26 06:00 | 44222.25 | 0 | 11.8413 | 37.78
2021-01-26 06:30 | 44222.2708 | 0 | 12.5607 | 37.78
2021-01-26 07:00 | 44222.2917 | 0 | 13.2829 | 37.78
2021-01-26 07:30 | 44222.3125 | 0 | 13.8805 | 37.78
2021-01-26 08:00 | 44222.3333 | 0 | 14.3273 | 37.78
2021-01-26 08:30 | 44222.3542 | 0 | 14.5814 | 37.78
2021-01-26 09:00 | 44222.375 | 0 | 14.9853 | 37.78
2021-01-26 09:30 | 44222.3958 | 0 | 15.8025 | 37.78
2021-01-26 10:00 | 44222.4167 | 0 | 16.6819 | 37.78
2021-01-26 10:30 | 44222.4375 | 0 | 15.8321 | 37.78
2021-01-26 11:00 | 44222.4583 | 0 | 16.1368 | 37.78
2021-01-26 11:30 | 44222.4792 | 0 | 16.1503 | 37.78
2021-01-26 12:00 | 44222.5 | 0 | 16.855 | 37.78
2021-01-26 12:30 | 44222.5208 | 0 | 16.8178 | 37.78
2021-01-26 13:00 | 44222.5417 | 0 | 17.6759 | 37.78
2021-01-26 13:30 | 44222.5625 | 0 | 17.7428 | 37.78
2021-01-26 14:00 | 44222.5833 | 0 | 18.5025 | 37.78
2021-01-26 14:30 | 44222.6042 | 0 | 18.9645 | 37.78
2021-01-26 15:00 | 44222.625 | 0 | 19.046 | 37.78
2021-01-26 15:30 | 44222.6458 | 0 | 19.8532 | 37.78
2021-01-26 16:00 | 44222.6667 | 0 | 20.363 | 37.78
2021-01-26 16:30 | 44222.6875 | 0 | 20.7069 | 37.78
2021-01-26 17:00 | 44222.7083 | 0 | 20.7391 | 37.78
2021-01-26 17:30 | 44222.7292 | 0 | 20.8381 | 37.78
2021-01-26 18:00 | 44222.75 | 0 | 20.629 | 37.78
2021-01-26 18:30 | 44222.7708 | 0 | 20.8119 | 37.78
2021-01-26 19:00 | 44222.7917 | 0 | 20.5612 | 37.78
2021-01-26 19:30 | 44222.8125 | 0 | 20.4476 | 37.78
2021-01-26 20:00 | 44222.8333 | 0 | 20.0431 | 37.78
2021-01-26 20:30 | 44222.8542 | 0 | 18.7605 | 37.78
2021-01-26 21:00 | 44222.875 | 0 | 17.6687 | 37.78
2021-01-26 21:30 | 44222.8958 | 0 | 16.8223 | 37.78
2021-01-26 22:00 | 44222.9167 | 0 | 15.8801 | 37.78
2021-01-26 22:30 | 44222.9375 | 0 | 14.7031 | 37.78
2021-01-26 23:00 | 44222.9583 | 0 | 13.8323 | 37.78
2021-01-26 23:30 | 44222.9792 | 0 | 13.2081 | 37.78
2021-01-27 | 44223 | 0 | 12.3605 | 37.78
2021-01-27 00:30 | 44223.0208 | 0 | 11.6616 | 37.78
2021-01-27 01:00 | 44223.0417 | 0 | 11.2588 | 37.78
2021-01-27 01:30 | 44223.0625 | 0 | 11.0291 | 37.78
2021-01-27 02:00 | 44223.0833 | 0 | 10.823 | 37.78
2021-01-27 02:30 | 44223.1042 | 0 | 10.6169 | 37.78
2021-01-27 03:00 | 44223.125 | 0 | 10.5811 | 37.78
2021-01-27 03:30 | 44223.1458 | 0 | 10.5441 | 37.78
2021-01-27 04:00 | 44223.1667 | 0 | 10.7736 | 37.78
2021-01-27 04:30 | 44223.1875 | 0 | 11.1346 | 37.78
2021-01-27 05:00 | 44223.2083 | 0 | 11.5525 | 37.78
2021-01-27 05:30 | 44223.2292 | 0 | 11.9472 | 37.78
2021-01-27 06:00 | 44223.25 | 0 | 12.8714 | 37.78
2021-01-27 06:30 | 44223.2708 | 0 | 13.5366 | 37.78
2021-01-27 07:00 | 44223.2917 | 0 | 15.1946 | 37.78
2021-01-27 07:30 | 44223.3125 | 0 | 14.8016 | 37.78
2021-01-27 08:00 | 44223.3333 | 0 | 14.5881 | 37.78
2021-01-27 08:30 | 44223.3542 | 0 | 14.3591 | 37.78
2021-01-27 09:00 | 44223.375 | 0 | 14.6265 | 37.78
2021-01-27 09:30 | 44223.3958 | 0 | 15.2191 | 37.78
2021-01-27 10:00 | 44223.4167 | 0 | 14.8632 | 37.78
2021-01-27 10:30 | 44223.4375 | 0 | 15.4671 | 37.78
2021-01-27 11:00 | 44223.4583 | 0 | 16.0027 | 37.78
2021-01-27 11:30 | 44223.4792 | 0 | 15.0222 | 37.78
2021-01-27 12:00 | 44223.5 | 0 | 14.5917 | 37.78
2021-01-27 12:30 | 44223.5208 | 0 | 15.2996 | 37.78
2021-01-27 13:00 | 44223.5417 | 0 | 15.3908 | 37.78
2021-01-27 13:30 | 44223.5625 | 0 | 16.0403 | 37.78
2021-01-27 14:00 | 44223.5833 | 0 | 16.7615 | 37.78
2021-01-27 14:30 | 44223.6042 | 0 | 16.5397 | 37.78
2021-01-27 15:00 | 44223.625 | 0 | 17.8236 | 37.78
2021-01-27 15:30 | 44223.6458 | 0 | 16.9399 | 37.78
2021-01-27 16:00 | 44223.6667 | 0 | 17.4713 | 37.78
2021-01-27 16:30 | 44223.6875 | 0 | 17.7078 | 37.78
2021-01-27 17:00 | 44223.7083 | 0 | 17.594 | 37.78
2021-01-27 17:30 | 44223.7292 | 0 | 17.9928 | 37.78
2021-01-27 18:00 | 44223.75 | 0 | 17.6333 | 37.78
2021-01-27 18:30 | 44223.7708 | 0 | 17.9291 | 37.78
2021-01-27 19:00 | 44223.7917 | 0 | 18.2779 | 37.78
2021-01-27 19:30 | 44223.8125 | 0 | 17.9794 | 37.78
2021-01-27 20:00 | 44223.8333 | 0 | 17.6168 | 37.78
2021-01-27 20:30 | 44223.8542 | 0 | 16.8077 | 37.78
2021-01-27 21:00 | 44223.875 | 0 | 15.9629 | 37.78
2021-01-27 21:30 | 44223.8958 | 0 | 15.3163 | 37.78
2021-01-27 22:00 | 44223.9167 | 0 | 14.5117 | 37.78
2021-01-27 22:30 | 44223.9375 | 0 | 13.4794 | 37.78
2021-01-27 23:00 | 44223.9583 | 0 | 12.8097 | 37.78
2021-01-27 23:30 | 44223.9792 | 0 | 12.0856 | 37.78
2021-01-28 | 44224 | 0 | 11.3462 | 37.78
2021-01-28 00:30 | 44224.0208 | 0 | 10.918 | 37.78
2021-01-28 01:00 | 44224.0417 | 0 | 10.4272 | 37.78
2021-01-28 01:30 | 44224.0625 | 0 | 10.1842 | 37.78
2021-01-28 02:00 | 44224.0833 | 0 | 10.1092 | 37.78
2021-01-28 02:30 | 44224.1042 | 0 | 10.0421 | 37.78
2021-01-28 03:00 | 44224.125 | 0 | 10.0496 | 37.78
2021-01-28 03:30 | 44224.1458 | 0 | 10.0828 | 37.78
2021-01-28 04:00 | 44224.1667 | 0 | 10.1957 | 37.78
2021-01-28 04:30 | 44224.1875 | 0 | 10.6055 | 37.78
2021-01-28 05:00 | 44224.2083 | 0 | 10.9657 | 37.78
2021-01-28 05:30 | 44224.2292 | 0 | 11.4538 | 37.78
2021-01-28 06:00 | 44224.25 | 0 | 12.2571 | 37.78
2021-01-28 06:30 | 44224.2708 | 0 | 12.95 | 37.78
2021-01-28 07:00 | 44224.2917 | 0 | 13.2177 | 37.78
2021-01-28 07:30 | 44224.3125 | 0 | 14.1754 | 37.78
2021-01-28 08:00 | 44224.3333 | 0 | 13.7847 | 37.78
2021-01-28 08:30 | 44224.3542 | 0 | 14.4881 | 37.78
2021-01-28 09:00 | 44224.375 | 0 | 14.3314 | 37.78
2021-01-28 09:30 | 44224.3958 | 0 | 14.6693 | 37.78
2021-01-28 10:00 | 44224.4167 | 0 | 15.3909 | 37.78
2021-01-28 10:30 | 44224.4375 | 0 | 15.0336 | 37.78
2021-01-28 11:00 | 44224.4583 | 0 | 14.3605 | 37.78
2021-01-28 11:30 | 44224.4792 | 0 | 14.9662 | 37.78
2021-01-28 12:00 | 44224.5 | 0 | 14.5818 | 37.78
2021-01-28 12:30 | 44224.5208 | 0 | 14.8306 | 37.78
2021-01-28 13:00 | 44224.5417 | 0 | 15.137 | 37.78
2021-01-28 13:30 | 44224.5625 | 0 | 15.9381 | 37.78
2021-01-28 14:00 | 44224.5833 | 0 | 15.8847 | 37.78
2021-01-28 14:30 | 44224.6042 | 0 | 16.5645 | 37.78
2021-01-28 15:00 | 44224.625 | 0 | 16.0106 | 37.78
2021-01-28 15:30 | 44224.6458 | 0 | 16.3522 | 37.78
2021-01-28 16:00 | 44224.6667 | 0 | 16.746 | 37.78
2021-01-28 16:30 | 44224.6875 | 0 | 17.0774 | 37.78
2021-01-28 17:00 | 44224.7083 | 0 | 17.1777 | 37.78
2021-01-28 17:30 | 44224.7292 | 0 | 16.9834 | 37.78
2021-01-28 18:00 | 44224.75 | 0 | 16.5425 | 37.78
2021-01-28 18:30 | 44224.7708 | 0 | 16.5133 | 37.78
2021-01-28 19:00 | 44224.7917 | 0 | 16.6028 | 37.78
2021-01-28 19:30 | 44224.8125 | 0 | 16.6248 | 37.78
2021-01-28 20:00 | 44224.8333 | 0 | 16.2705 | 37.78
2021-01-28 20:30 | 44224.8542 | 0 | 15.6098 | 37.78
2021-01-28 21:00 | 44224.875 | 0 | 15.1221 | 37.78
2021-01-28 21:30 | 44224.8958 | 0 | 14.4483 | 37.78
2021-01-28 22:00 | 44224.9167 | 0 | 14.0542 | 37.78
2021-01-28 22:30 | 44224.9375 | 0 | 13.0723 | 37.78
2021-01-28 23:00 | 44224.9583 | 0 | 12.3982 | 37.78
2021-01-28 23:30 | 44224.9792 | 0 | 11.7238 | 37.78
2021-01-29 | 44225 | 0 | 11.0365 | 37.78
2021-01-29 00:30 | 44225.0208 | 0 | 10.468 | 37.78
2021-01-29 01:00 | 44225.0417 | 0 | 10.1966 | 37.78
2021-01-29 01:30 | 44225.0625 | 0 | 9.9025 | 37.78
2021-01-29 02:00 | 44225.0833 | 0 | 9.8317 | 37.78
2021-01-29 02:30 | 44225.1042 | 0 | 9.6384 | 37.78
2021-01-29 03:00 | 44225.125 | 0 | 9.5371 | 37.78
2021-01-29 03:30 | 44225.1458 | 0 | 9.6837 | 37.78
2021-01-29 04:00 | 44225.1667 | 0 | 9.6691 | 37.78
2021-01-29 04:30 | 44225.1875 | 0 | 9.5106 | 37.78
2021-01-29 05:00 | 44225.2083 | 0 | 9.416 | 37.78
2021-01-29 05:30 | 44225.2292 | 0 | 9.2884 | 37.78
2021-01-29 06:00 | 44225.25 | 0 | 9.1594 | 37.78
2021-01-29 06:30 | 44225.2708 | 0 | 9.3426 | 37.78
2021-01-29 07:00 | 44225.2917 | 0 | 9.8485 | 37.78
2021-01-29 07:30 | 44225.3125 | 0 | 10.2123 | 37.78
2021-01-29 08:00 | 44225.3333 | 0 | 10.3335 | 37.78
2021-01-29 08:30 | 44225.3542 | 0 | 10.8655 | 37.78
2021-01-29 09:00 | 44225.375 | 0 | 11.0323 | 37.78
2021-01-29 09:30 | 44225.3958 | 0 | 11.0212 | 37.78
2021-01-29 10:00 | 44225.4167 | 0 | 11.3403 | 37.78
2021-01-29 10:30 | 44225.4375 | 0 | 11.056 | 37.78
2021-01-29 11:00 | 44225.4583 | 0 | 11.5926 | 37.78
2021-01-29 11:30 | 44225.4792 | 0 | 11.8058 | 37.78
2021-01-29 12:00 | 44225.5 | 0 | 12.3826 | 37.78
2021-01-29 12:30 | 44225.5208 | 0 | 12.4016 | 37.78
2021-01-29 13:00 | 44225.5417 | 0 | 12.8115 | 37.78
2021-01-29 13:30 | 44225.5625 | 0 | 12.8735 | 37.78
2021-01-29 14:00 | 44225.5833 | 0 | 13.8047 | 37.78
2021-01-29 14:30 | 44225.6042 | 0 | 13.9156 | 37.78
2021-01-29 15:00 | 44225.625 | 0 | 13.9777 | 37.78
2021-01-29 15:30 | 44225.6458 | 0 | 14.5571 | 37.78
2021-01-29 16:00 | 44225.6667 | 0 | 14.7155 | 37.78
2021-01-29 16:30 | 44225.6875 | 0 | 15.766 | 37.78
2021-01-29 17:00 | 44225.7083 | 0 | 15.4271 | 37.78
2021-01-29 17:30 | 44225.7292 | 0 | 15.6456 | 37.78
2021-01-29 18:00 | 44225.75 | 0 | 15.4649 | 37.78
2021-01-29 18:30 | 44225.7708 | 0 | 15.6284 | 37.78
2021-01-29 19:00 | 44225.7917 | 0 | 15.4597 | 37.78
2021-01-29 19:30 | 44225.8125 | 0 | 15.2108 | 37.78
2021-01-29 20:00 | 44225.8333 | 0 | 15.0954 | 37.78
2021-01-29 20:30 | 44225.8542 | 0 | 14.8916 | 37.78
2021-01-29 21:00 | 44225.875 | 0 | 14.3191 | 37.78
2021-01-29 21:30 | 44225.8958 | 0 | 13.7917 | 37.78
2021-01-29 22:00 | 44225.9167 | 0 | 13.2772 | 37.78
2021-01-29 22:30 | 44225.9375 | 0 | 12.1903 | 37.78
2021-01-29 23:00 | 44225.9583 | 0 | 11.6324 | 37.78
2021-01-29 23:30 | 44225.9792 | 0 | 11.1831 | 37.78
2021-01-30 | 44226 | 0 | 10.5627 | 37.78
2021-01-30 00:30 | 44226.0208 | 0 | 10.1596 | 37.78
2021-01-30 01:00 | 44226.0417 | 0 | 9.905 | 37.78
2021-01-30 01:30 | 44226.0625 | 0 | 9.638 | 37.78
2021-01-30 02:00 | 44226.0833 | 0 | 9.5052 | 37.78
2021-01-30 02:30 | 44226.1042 | 0 | 9.1956 | 37.78
2021-01-30 03:00 | 44226.125 | 0 | 9.1631 | 37.78
2021-01-30 03:30 | 44226.1458 | 0 | 9.1188 | 37.78
2021-01-30 04:00 | 44226.1667 | 0 | 9.0437 | 37.78
2021-01-30 04:30 | 44226.1875 | 0 | 8.9644 | 37.78
2021-01-30 05:00 | 44226.2083 | 0 | 8.9749 | 37.78
2021-01-30 05:30 | 44226.2292 | 0 | 8.8297 | 37.78
2021-01-30 06:00 | 44226.25 | 0 | 8.5919 | 37.78
2021-01-30 06:30 | 44226.2708 | 0 | 8.7483 | 37.78
2021-01-30 07:00 | 44226.2917 | 0 | 9.1571 | 37.78
2021-01-30 07:30 | 44226.3125 | 0 | 9.4032 | 37.78
2021-01-30 08:00 | 44226.3333 | 0 | 10.0458 | 37.78
2021-01-30 08:30 | 44226.3542 | 0 | 9.4601 | 37.78
2021-01-30 09:00 | 44226.375 | 0 | 10.8398 | 37.78
2021-01-30 09:30 | 44226.3958 | 0 | 11.2635 | 37.78
2021-01-30 10:00 | 44226.4167 | 0 | 11.0216 | 37.78
2021-01-30 10:30 | 44226.4375 | 0 | 11.687 | 37.78
2021-01-30 11:00 | 44226.4583 | 0 | 11.1343 | 37.78
2021-01-30 11:30 | 44226.4792 | 0 | 11.1389 | 37.78
2021-01-30 12:00 | 44226.5 | 0 | 11.0109 | 37.78
2021-01-30 12:30 | 44226.5208 | 0 | 11.3014 | 37.78
2021-01-30 13:00 | 44226.5417 | 0 | 11.8586 | 37.78
2021-01-30 13:30 | 44226.5625 | 0 | 12.276 | 37.78
2021-01-30 14:00 | 44226.5833 | 0 | 12.8968 | 37.78
2021-01-30 14:30 | 44226.6042 | 0 | 14.3735 | 37.78
2021-01-30 15:00 | 44226.625 | 0 | 14.2064 | 37.78
2021-01-30 15:30 | 44226.6458 | 0 | 14.691 | 37.78
2021-01-30 16:00 | 44226.6667 | 0 | 15.5526 | 37.78
2021-01-30 16:30 | 44226.6875 | 0 | 15.7331 | 37.78
2021-01-30 17:00 | 44226.7083 | 0 | 15.9157 | 37.78
2021-01-30 17:30 | 44226.7292 | 0 | 15.953 | 37.78
2021-01-30 18:00 | 44226.75 | 0 | 15.9159 | 37.78
2021-01-30 18:30 | 44226.7708 | 0 | 16.2067 | 37.78
2021-01-30 19:00 | 44226.7917 | 0 | 16.3158 | 37.78
2021-01-30 19:30 | 44226.8125 | 0 | 16.0475 | 37.78
2021-01-30 20:00 | 44226.8333 | 0 | 15.7894 | 37.78
2021-01-30 20:30 | 44226.8542 | 0 | 14.8941 | 37.78
2021-01-30 21:00 | 44226.875 | 0 | 14.3613 | 37.78
2021-01-30 21:30 | 44226.8958 | 0 | 13.436 | 37.78
2021-01-30 22:00 | 44226.9167 | 0 | 12.624 | 37.78
2021-01-30 22:30 | 44226.9375 | 0 | 11.7719 | 37.78
2021-01-30 23:00 | 44226.9583 | 0 | 10.9589 | 37.78
2021-01-30 23:30 | 44226.9792 | 0 | 10.3078 | 37.78
2021-01-31 | 44227 | 0 | 9.9132 | 37.78
2021-01-31 00:30 | 44227.0208 | 0 | 9.7064 | 37.78
2021-01-31 01:00 | 44227.0417 | 0 | 9.579 | 37.78
2021-01-31 01:30 | 44227.0625 | 0 | 9.3509 | 37.78
2021-01-31 02:00 | 44227.0833 | 0 | 9.4008 | 37.78
2021-01-31 02:30 | 44227.1042 | 0 | 9.1346 | 37.78
2021-01-31 03:00 | 44227.125 | 0 | 9.1782 | 37.78
2021-01-31 03:30 | 44227.1458 | 0 | 9.2094 | 37.78
2021-01-31 04:00 | 44227.1667 | 0 | 9.4787 | 37.78
2021-01-31 04:30 | 44227.1875 | 0 | 9.9461 | 37.78
2021-01-31 05:00 | 44227.2083 | 0 | 10.4021 | 37.78
2021-01-31 05:30 | 44227.2292 | 0 | 10.7305 | 37.78
2021-01-31 06:00 | 44227.25 | 0 | 11.5621 | 37.78
2021-01-31 06:30 | 44227.2708 | 0 | 12.0526 | 37.78
2021-01-31 07:00 | 44227.2917 | 0 | 12.9117 | 37.78
2021-01-31 07:30 | 44227.3125 | 0 | 13.7403 | 37.78
2021-01-31 08:00 | 44227.3333 | 0 | 13.4816 | 37.78
2021-01-31 08:30 | 44227.3542 | 0 | 14.9219 | 37.78
2021-01-31 09:00 | 44227.375 | 0 | 14.3579 | 37.78
2021-01-31 09:30 | 44227.3958 | 0 | 12.7305 | 37.78
2021-01-31 10:00 | 44227.4167 | 0 | 14.9854 | 37.78
2021-01-31 10:30 | 44227.4375 | 0 | 13.4788 | 37.78
2021-01-31 11:00 | 44227.4583 | 0 | 13.3581 | 37.78
2021-01-31 11:30 | 44227.4792 | 0 | 14.1772 | 37.78
2021-01-31 12:00 | 44227.5 | 0 | 13.7508 | 37.78
2021-01-31 12:30 | 44227.5208 | 0 | 14.4779 | 37.78
2021-01-31 13:00 | 44227.5417 | 0 | 14.1537 | 37.78
2021-01-31 13:30 | 44227.5625 | 0 | 15.2163 | 37.78
2021-01-31 14:00 | 44227.5833 | 0 | 15.3693 | 37.78
2021-01-31 14:30 | 44227.6042 | 0 | 15.0786 | 37.78
2021-01-31 15:00 | 44227.625 | 0 | 15.2245 | 37.78
2021-01-31 15:30 | 44227.6458 | 0 | 15.279 | 37.78
2021-01-31 16:00 | 44227.6667 | 0 | 16.0855 | 37.78
2021-01-31 16:30 | 44227.6875 | 0 | 16.5274 | 37.78
2021-01-31 17:00 | 44227.7083 | 0 | 16.3693 | 37.78
2021-01-31 17:30 | 44227.7292 | 0 | 16.6981 | 37.78
2021-01-31 18:00 | 44227.75 | 0 | 16.5847 | 37.78
2021-01-31 18:30 | 44227.7708 | 0 | 17.0848 | 37.78
2021-01-31 19:00 | 44227.7917 | 0 | 16.9354 | 37.78
2021-01-31 19:30 | 44227.8125 | 0 | 16.8382 | 37.78
2021-01-31 20:00 | 44227.8333 | 0 | 16.4289 | 37.78
2021-01-31 20:30 | 44227.8542 | 0 | 15.7518 | 37.78
2021-01-31 21:00 | 44227.875 | 0 | 14.9992 | 37.78
2021-01-31 21:30 | 44227.8958 | 0 | 14.4185 | 37.78
2021-01-31 22:00 | 44227.9167 | 0 | 13.8047 | 37.78
2021-01-31 22:30 | 44227.9375 | 0 | 12.9451 | 37.78
2021-01-31 23:00 | 44227.9583 | 0 | 12.183 | 37.78
2021-01-31 23:30 | 44227.9792 | 0 | 11.5932 | 37.78
2021-02-01 | 44228 | 0 | 10.8479 | 37.78
2021-02-01 00:30 | 44228.0208 | 0 | 10.2517 | 37.78
2021-02-01 01:00 | 44228.0417 | 0 | 9.96 | 37.78
2021-02-01 01:30 | 44228.0625 | 0 | 9.8606 | 37.78
2021-02-01 02:00 | 44228.0833 | 0 | 9.6858 | 37.78
2021-02-01 02:30 | 44228.1042 | 0 | 9.6468 | 37.78
2021-02-01 03:00 | 44228.125 | 0 | 9.5954 | 37.78
2021-02-01 03:30 | 44228.1458 | 0 | 9.6865 | 37.78
2021-02-01 04:00 | 44228.1667 | 0 | 9.9173 | 37.78
2021-02-01 04:30 | 44228.1875 | 0 | 10.1219 | 37.78
2021-02-01 05:00 | 44228.2083 | 0 | 10.8314 | 37.78
2021-02-01 05:30 | 44228.2292 | 0 | 11.4217 | 37.78
2021-02-01 06:00 | 44228.25 | 0 | 11.9326 | 37.78
2021-02-01 06:30 | 44228.2708 | 0 | 13.0621 | 37.78
2021-02-01 07:00 | 44228.2917 | 0 | 13.595 | 37.78
2021-02-01 07:30 | 44228.3125 | 0 | 13.719 | 37.78
2021-02-01 08:00 | 44228.3333 | 0 | 14.5753 | 37.78
2021-02-01 08:30 | 44228.3542 | 0 | 15.0394 | 37.78
2021-02-01 09:00 | 44228.375 | 0 | 15.2904 | 37.78
2021-02-01 09:30 | 44228.3958 | 0 | 15.2599 | 37.78
2021-02-01 10:00 | 44228.4167 | 0 | 15.0581 | 37.78
2021-02-01 10:30 | 44228.4375 | 0 | 14.6136 | 37.78
2021-02-01 11:00 | 44228.4583 | 0 | 14.2083 | 37.78
2021-02-01 11:30 | 44228.4792 | 0 | 14.6203 | 37.78
2021-02-01 12:00 | 44228.5 | 0 | 14.3694 | 37.78
2021-02-01 12:30 | 44228.5208 | 0 | 13.7237 | 37.78
2021-02-01 13:00 | 44228.5417 | 0 | 14.3663 | 37.78
2021-02-01 13:30 | 44228.5625 | 0 | 14.6189 | 37.78
2021-02-01 14:00 | 44228.5833 | 0 | 14.4246 | 37.78
2021-02-01 14:30 | 44228.6042 | 0 | 14.0742 | 37.78
2021-02-01 15:00 | 44228.625 | 0 | 13.6389 | 37.78
2021-02-01 15:30 | 44228.6458 | 0 | 13.8265 | 37.78
2021-02-01 16:00 | 44228.6667 | 0 | 14.0512 | 37.78
2021-02-01 16:30 | 44228.6875 | 0 | 13.8655 | 37.78
2021-02-01 17:00 | 44228.7083 | 0 | 14.2145 | 37.78
2021-02-01 17:30 | 44228.7292 | 0 | 14.3916 | 37.78
2021-02-01 18:00 | 44228.75 | 0 | 14.4524 | 37.78
2021-02-01 18:30 | 44228.7708 | 0 | 14.9783 | 37.78
2021-02-01 19:00 | 44228.7917 | 0 | 15.1256 | 37.78
2021-02-01 19:30 | 44228.8125 | 0 | 15.052 | 37.78
2021-02-01 20:00 | 44228.8333 | 0 | 14.6507 | 37.78
2021-02-01 20:30 | 44228.8542 | 0 | 14.1102 | 37.78
2021-02-01 21:00 | 44228.875 | 0 | 13.5998 | 37.78
2021-02-01 21:30 | 44228.8958 | 0 | 13.1806 | 37.78
2021-02-01 22:00 | 44228.9167 | 0 | 12.5383 | 37.78
2021-02-01 22:30 | 44228.9375 | 0 | 11.854 | 37.78
2021-02-01 23:00 | 44228.9583 | 0 | 11.1102 | 37.78
2021-02-01 23:30 | 44228.9792 | 0 | 10.6178 | 37.78
2021-02-02 | 44229 | 0 | 9.9257 | 37.78
2021-02-02 00:30 | 44229.0208 | 0 | 9.4924 | 37.78
2021-02-02 01:00 | 44229.0417 | 0 | 9.1633 | 37.78
2021-02-02 01:30 | 44229.0625 | 0 | 9.0901 | 37.78
2021-02-02 02:00 | 44229.0833 | 0 | 9.0871 | 37.78
2021-02-02 02:30 | 44229.1042 | 0 | 8.9479 | 37.78
2021-02-02 03:00 | 44229.125 | 0 | 8.8067 | 37.78
2021-02-02 03:30 | 44229.1458 | 0 | 8.9185 | 37.78
2021-02-02 04:00 | 44229.1667 | 0 | 9.1243 | 37.78
2021-02-02 04:30 | 44229.1875 | 0 | 9.5257 | 37.78
2021-02-02 05:00 | 44229.2083 | 0 | 10.063 | 37.78
2021-02-02 05:30 | 44229.2292 | 0 | 10.3191 | 37.78
2021-02-02 06:00 | 44229.25 | 0 | 11.01 | 37.78
2021-02-02 06:30 | 44229.2708 | 0 | 11.5392 | 37.78
2021-02-02 07:00 | 44229.2917 | 0 | 11.8813 | 37.78
2021-02-02 07:30 | 44229.3125 | 0 | 12.1882 | 37.78
2021-02-02 08:00 | 44229.3333 | 0 | 12.5644 | 37.78
2021-02-02 08:30 | 44229.3542 | 0 | 12.5549 | 37.78
2021-02-02 09:00 | 44229.375 | 0 | 12.5945 | 37.78
2021-02-02 09:30 | 44229.3958 | 0 | 12.6441 | 37.78
2021-02-02 10:00 | 44229.4167 | 0 | 13.1484 | 37.78
2021-02-02 10:30 | 44229.4375 | 0 | 13.5848 | 37.78
2021-02-02 11:00 | 44229.4583 | 0 | 14.0701 | 37.78
2021-02-02 11:30 | 44229.4792 | 0 | 13.5401 | 37.78
2021-02-02 12:00 | 44229.5 | 0 | 14.6915 | 37.78
2021-02-02 12:30 | 44229.5208 | 0 | 12.8494 | 37.78
2021-02-02 13:00 | 44229.5417 | 0 | 13.5828 | 37.78
2021-02-02 13:30 | 44229.5625 | 0 | 13.13 | 37.78
2021-02-02 14:00 | 44229.5833 | 0 | 12.3087 | 37.78
2021-02-02 14:30 | 44229.6042 | 0 | 12.8576 | 37.78
2021-02-02 15:00 | 44229.625 | 0 | 13.5376 | 37.78
2021-02-02 15:30 | 44229.6458 | 0 | 14.1098 | 37.78
2021-02-02 16:00 | 44229.6667 | 0 | 14.5557 | 37.78
2021-02-02 16:30 | 44229.6875 | 0 | 14.9822 | 37.78
2021-02-02 17:00 | 44229.7083 | 0 | 15.2719 | 37.78
2021-02-02 17:30 | 44229.7292 | 0 | 15.5797 | 37.78
2021-02-02 18:00 | 44229.75 | 0 | 15.5917 | 37.78
2021-02-02 18:30 | 44229.7708 | 0 | 16.0078 | 37.78
2021-02-02 19:00 | 44229.7917 | 0 | 16.1639 | 37.78
2021-02-02 19:30 | 44229.8125 | 0 | 15.834 | 37.78
2021-02-02 20:00 | 44229.8333 | 0 | 15.3863 | 37.78
2021-02-02 20:30 | 44229.8542 | 0 | 14.7198 | 37.78
2021-02-02 21:00 | 44229.875 | 0 | 14.0368 | 37.78
2021-02-02 21:30 | 44229.8958 | 0 | 13.4638 | 37.78
2021-02-02 22:00 | 44229.9167 | 0 | 12.6813 | 37.78
2021-02-02 22:30 | 44229.9375 | 0 | 11.8561 | 37.78
2021-02-02 23:00 | 44229.9583 | 0 | 10.8639 | 37.78
2021-02-02 23:30 | 44229.9792 | 0 | 10.6269 | 37.78
2021-02-03 | 44230 | 0 | 10.0076 | 37.78
2021-02-03 00:30 | 44230.0208 | 0 | 9.6179 | 37.78
2021-02-03 01:00 | 44230.0417 | 0 | 9.3705 | 37.78
2021-02-03 01:30 | 44230.0625 | 0 | 9.1192 | 37.78
2021-02-03 02:00 | 44230.0833 | 0 | 9.1701 | 37.78
2021-02-03 02:30 | 44230.1042 | 0 | 8.876 | 37.78
2021-02-03 03:00 | 44230.125 | 0 | 8.8197 | 37.78
2021-02-03 03:30 | 44230.1458 | 0 | 8.7873 | 37.78
2021-02-03 04:00 | 44230.1667 | 0 | 9.0388 | 37.78
2021-02-03 04:30 | 44230.1875 | 0 | 9.3482 | 37.78
2021-02-03 05:00 | 44230.2083 | 0 | 9.794 | 37.78
2021-02-03 05:30 | 44230.2292 | 0 | 10.1359 | 37.78
2021-02-03 06:00 | 44230.25 | 0 | 10.8175 | 37.78
2021-02-03 06:30 | 44230.2708 | 0 | 11.2717 | 37.78
2021-02-03 07:00 | 44230.2917 | 0 | 11.6757 | 37.78
2021-02-03 07:30 | 44230.3125 | 0 | 12.0993 | 37.78
2021-02-03 08:00 | 44230.3333 | 0 | 11.9857 | 37.78
2021-02-03 08:30 | 44230.3542 | 0 | 12.213 | 37.78
2021-02-03 09:00 | 44230.375 | 0 | 12.8194 | 37.78
2021-02-03 09:30 | 44230.3958 | 0 | 13.039 | 37.78
2021-02-03 10:00 | 44230.4167 | 0 | 13.2678 | 37.78
2021-02-03 10:30 | 44230.4375 | 0 | 13.7062 | 37.78
2021-02-03 11:00 | 44230.4583 | 0 | 14.1742 | 37.78
2021-02-03 11:30 | 44230.4792 | 0 | 14.8212 | 37.78
2021-02-03 12:00 | 44230.5 | 0 | 14.5051 | 37.78
2021-02-03 12:30 | 44230.5208 | 0 | 14.4811 | 37.78
2021-02-03 13:00 | 44230.5417 | 0 | 14.9993 | 37.78
2021-02-03 13:30 | 44230.5625 | 0 | 15.1532 | 37.78
2021-02-03 14:00 | 44230.5833 | 0 | 15.1466 | 37.78
2021-02-03 14:30 | 44230.6042 | 0 | 15.5041 | 37.78
2021-02-03 15:00 | 44230.625 | 0 | 15.0328 | 37.78
2021-02-03 15:30 | 44230.6458 | 0 | 15.6825 | 37.78
2021-02-03 16:00 | 44230.6667 | 0 | 16.692 | 37.78
2021-02-03 16:30 | 44230.6875 | 0 | 16.8794 | 37.78
2021-02-03 17:00 | 44230.7083 | 0 | 17.2262 | 37.78
2021-02-03 17:30 | 44230.7292 | 0 | 17.4652 | 37.78
2021-02-03 18:00 | 44230.75 | 0 | 17.2039 | 37.78
2021-02-03 18:30 | 44230.7708 | 0 | 17.4205 | 37.78
2021-02-03 19:00 | 44230.7917 | 0 | 17.3414 | 37.78
2021-02-03 19:30 | 44230.8125 | 0 | 17.1072 | 37.78
2021-02-03 20:00 | 44230.8333 | 0 | 16.7946 | 37.78
2021-02-03 20:30 | 44230.8542 | 0 | 15.9271 | 37.78
2021-02-03 21:00 | 44230.875 | 0 | 15.2389 | 37.78
2021-02-03 21:30 | 44230.8958 | 0 | 14.5829 | 37.78
2021-02-03 22:00 | 44230.9167 | 0 | 13.6651 | 37.78
2021-02-03 22:30 | 44230.9375 | 0 | 12.5888 | 37.78
2021-02-03 23:00 | 44230.9583 | 0 | 11.8541 | 37.78
2021-02-03 23:30 | 44230.9792 | 0 | 11.2001 | 37.78
2021-02-04 | 44231 | 0 | 10.4176 | 37.78
2021-02-04 00:30 | 44231.0208 | 0 | 9.9659 | 37.78
2021-02-04 01:00 | 44231.0417 | 0 | 9.6377 | 37.78
2021-02-04 01:30 | 44231.0625 | 0 | 9.6685 | 37.78
2021-02-04 02:00 | 44231.0833 | 0 | 9.469 | 37.78
2021-02-04 02:30 | 44231.1042 | 0 | 9.4092 | 37.78
2021-02-04 03:00 | 44231.125 | 0 | 9.4237 | 37.78
2021-02-04 03:30 | 44231.1458 | 0 | 9.4988 | 37.78
2021-02-04 04:00 | 44231.1667 | 0 | 9.5605 | 37.78
2021-02-04 04:30 | 44231.1875 | 0 | 9.7973 | 37.78
2021-02-04 05:00 | 44231.2083 | 0 | 10.3437 | 37.78
2021-02-04 05:30 | 44231.2292 | 0 | 10.79 | 37.78
2021-02-04 06:00 | 44231.25 | 0 | 11.3616 | 37.78
2021-02-04 06:30 | 44231.2708 | 0 | 12.1359 | 37.78
2021-02-04 07:00 | 44231.2917 | 0 | 12.3351 | 37.78
2021-02-04 07:30 | 44231.3125 | 0 | 12.7888 | 37.78
2021-02-04 08:00 | 44231.3333 | 0 | 12.9959 | 37.78
2021-02-04 08:30 | 44231.3542 | 0 | 13.3439 | 37.78
2021-02-04 09:00 | 44231.375 | 0 | 14.2512 | 37.78
2021-02-04 09:30 | 44231.3958 | 0 | 14.5602 | 37.78
2021-02-04 10:00 | 44231.4167 | 0 | 14.1001 | 37.78
2021-02-04 10:30 | 44231.4375 | 0 | 14.1264 | 37.78
2021-02-04 11:00 | 44231.4583 | 0 | 14.5329 | 37.78
2021-02-04 11:30 | 44231.4792 | 0 | 15.3098 | 37.78
2021-02-04 12:00 | 44231.5 | 0 | 14.7251 | 37.78
2021-02-04 12:30 | 44231.5208 | 0 | 14.4678 | 37.78
2021-02-04 13:00 | 44231.5417 | 0 | 14.9163 | 37.78
2021-02-04 13:30 | 44231.5625 | 0 | 15.61 | 37.78
2021-02-04 14:00 | 44231.5833 | 0 | 16.2637 | 37.78
2021-02-04 14:30 | 44231.6042 | 0 | 15.0989 | 37.78
2021-02-04 15:00 | 44231.625 | 0 | 16.3388 | 37.78
2021-02-04 15:30 | 44231.6458 | 0 | 16.5117 | 37.78
2021-02-04 16:00 | 44231.6667 | 0 | 17.4599 | 37.78
2021-02-04 16:30 | 44231.6875 | 0 | 16.6342 | 37.78
2021-02-04 17:00 | 44231.7083 | 0 | 16.4676 | 37.78
2021-02-04 17:30 | 44231.7292 | 0 | 16.468 | 37.78
2021-02-04 18:00 | 44231.75 | 0 | 16.3217 | 37.78
2021-02-04 18:30 | 44231.7708 | 0 | 16.155 | 37.78
2021-02-04 19:00 | 44231.7917 | 0 | 16.182 | 37.78
2021-02-04 19:30 | 44231.8125 | 0 | 15.8396 | 37.78
2021-02-04 20:00 | 44231.8333 | 0 | 15.8643 | 37.78
2021-02-04 20:30 | 44231.8542 | 0 | 15.4678 | 37.78
2021-02-04 21:00 | 44231.875 | 0 | 14.6722 | 37.78
2021-02-04 21:30 | 44231.8958 | 0 | 14.1263 | 37.78
2021-02-04 22:00 | 44231.9167 | 0 | 13.4397 | 37.78
2021-02-04 22:30 | 44231.9375 | 0 | 12.4745 | 37.78
2021-02-04 23:00 | 44231.9583 | 0 | 11.7756 | 37.78
2021-02-04 23:30 | 44231.9792 | 0 | 11.1894 | 37.78
2021-02-05 | 44232 | 0 | 10.454 | 37.78
2021-02-05 00:30 | 44232.0208 | 0 | 10.1224 | 37.78
2021-02-05 01:00 | 44232.0417 | 0 | 9.8998 | 37.78
2021-02-05 01:30 | 44232.0625 | 0 | 9.7426 | 37.78
2021-02-05 02:00 | 44232.0833 | 0 | 9.5015 | 37.78
2021-02-05 02:30 | 44232.1042 | 0 | 9.4152 | 37.78
2021-02-05 03:00 | 44232.125 | 0 | 9.259 | 37.78
2021-02-05 03:30 | 44232.1458 | 0 | 9.2031 | 37.78
2021-02-05 04:00 | 44232.1667 | 0 | 9.2826 | 37.78
2021-02-05 04:30 | 44232.1875 | 0 | 9.2833 | 37.78
2021-02-05 05:00 | 44232.2083 | 0 | 9.4242 | 37.78
2021-02-05 05:30 | 44232.2292 | 0 | 9.4088 | 37.78
2021-02-05 06:00 | 44232.25 | 0 | 9.3131 | 37.78
2021-02-05 06:30 | 44232.2708 | 0 | 9.4187 | 37.78
2021-02-05 07:00 | 44232.2917 | 0 | 9.4751 | 37.78
2021-02-05 07:30 | 44232.3125 | 0 | 9.5861 | 37.78
2021-02-05 08:00 | 44232.3333 | 0 | 10.1563 | 37.78
2021-02-05 08:30 | 44232.3542 | 0 | 10.5414 | 37.78
2021-02-05 09:00 | 44232.375 | 0 | 11.0348 | 37.78
2021-02-05 09:30 | 44232.3958 | 0 | 10.8149 | 37.78
2021-02-05 10:00 | 44232.4167 | 0 | 11.2359 | 37.78
2021-02-05 10:30 | 44232.4375 | 0 | 11.3838 | 37.78
2021-02-05 11:00 | 44232.4583 | 0 | 11.6073 | 37.78
2021-02-05 11:30 | 44232.4792 | 0 | 12.7644 | 37.78
2021-02-05 12:00 | 44232.5 | 0 | 13.2945 | 37.78
2021-02-05 12:30 | 44232.5208 | 0 | 13.1449 | 37.78
2021-02-05 13:00 | 44232.5417 | 0 | 12.8499 | 37.78
2021-02-05 13:30 | 44232.5625 | 0 | 13.1206 | 37.78
2021-02-05 14:00 | 44232.5833 | 0 | 13.5408 | 37.78
2021-02-05 14:30 | 44232.6042 | 0 | 13.9043 | 37.78
2021-02-05 15:00 | 44232.625 | 0 | 14.6384 | 37.78
2021-02-05 15:30 | 44232.6458 | 0 | 15.0815 | 37.78
2021-02-05 16:00 | 44232.6667 | 0 | 15.0372 | 37.78
2021-02-05 16:30 | 44232.6875 | 0 | 15.8648 | 37.78
2021-02-05 17:00 | 44232.7083 | 0 | 16.2608 | 37.78
2021-02-05 17:30 | 44232.7292 | 0 | 16.6527 | 37.78
2021-02-05 18:00 | 44232.75 | 0 | 16.2798 | 37.78
2021-02-05 18:30 | 44232.7708 | 0 | 16.4817 | 37.78
2021-02-05 19:00 | 44232.7917 | 0 | 16.1542 | 37.78
2021-02-05 19:30 | 44232.8125 | 0 | 16.0634 | 37.78
2021-02-05 20:00 | 44232.8333 | 0 | 15.6448 | 37.78
2021-02-05 20:30 | 44232.8542 | 0 | 15.0413 | 37.78
2021-02-05 21:00 | 44232.875 | 0 | 14.5767 | 37.78
2021-02-05 21:30 | 44232.8958 | 0 | 14.034 | 37.78
2021-02-05 22:00 | 44232.9167 | 0 | 13.5638 | 37.78
2021-02-05 22:30 | 44232.9375 | 0 | 12.5065 | 37.78
2021-02-05 23:00 | 44232.9583 | 0 | 11.9035 | 37.78
2021-02-05 23:30 | 44232.9792 | 0 | 11.4096 | 37.78
2021-02-06 | 44233 | 0 | 10.7225 | 37.78
2021-02-06 00:30 | 44233.0208 | 0 | 10.3312 | 37.78
2021-02-06 01:00 | 44233.0417 | 0 | 10.0852 | 37.78
2021-02-06 01:30 | 44233.0625 | 0 | 9.8924 | 37.78
2021-02-06 02:00 | 44233.0833 | 0 | 9.7316 | 37.78
2021-02-06 02:30 | 44233.1042 | 0 | 9.5031 | 37.78
2021-02-06 03:00 | 44233.125 | 0 | 9.289 | 37.78
2021-02-06 03:30 | 44233.1458 | 0 | 9.1704 | 37.78
2021-02-06 04:00 | 44233.1667 | 0 | 8.9527 | 37.78
2021-02-06 04:30 | 44233.1875 | 0 | 8.9625 | 37.78
2021-02-06 05:00 | 44233.2083 | 0 | 9.06 | 37.78
2021-02-06 05:30 | 44233.2292 | 0 | 9.0974 | 37.78
2021-02-06 06:00 | 44233.25 | 0 | 9.1275 | 37.78
2021-02-06 06:30 | 44233.2708 | 0 | 9.1737 | 37.78
2021-02-06 07:00 | 44233.2917 | 0 | 9.6309 | 37.78
2021-02-06 07:30 | 44233.3125 | 0 | 9.3687 | 37.78
2021-02-06 08:00 | 44233.3333 | 0 | 10.2404 | 37.78
2021-02-06 08:30 | 44233.3542 | 0 | 10.4687 | 37.78
2021-02-06 09:00 | 44233.375 | 0 | 10.5609 | 37.78
2021-02-06 09:30 | 44233.3958 | 0 | 10.3708 | 37.78
2021-02-06 10:00 | 44233.4167 | 0 | 10.6826 | 37.78
2021-02-06 10:30 | 44233.4375 | 0 | 11.0707 | 37.78
2021-02-06 11:00 | 44233.4583 | 0 | 11.5317 | 37.78
2021-02-06 11:30 | 44233.4792 | 0 | 12.5808 | 37.78
2021-02-06 12:00 | 44233.5 | 0 | 13.5206 | 37.78
2021-02-06 12:30 | 44233.5208 | 0 | 14.2566 | 37.78
2021-02-06 13:00 | 44233.5417 | 0 | 15.7121 | 37.78
2021-02-06 13:30 | 44233.5625 | 0 | 15.8359 | 37.78
2021-02-06 14:00 | 44233.5833 | 0 | 17.8691 | 37.78
2021-02-06 14:30 | 44233.6042 | 0 | 16.7635 | 37.78
2021-02-06 15:00 | 44233.625 | 0 | 18.4677 | 37.78
2021-02-06 15:30 | 44233.6458 | 0 | 18.7765 | 37.78
2021-02-06 16:00 | 44233.6667 | 0 | 18.1285 | 37.78
2021-02-06 16:30 | 44233.6875 | 0 | 19.4298 | 37.78
2021-02-06 17:00 | 44233.7083 | 0 | 19.9587 | 37.78
2021-02-06 17:30 | 44233.7292 | 0 | 20.4012 | 37.78
2021-02-06 18:00 | 44233.75 | 0 | 20.2986 | 37.78
2021-02-06 18:30 | 44233.7708 | 0 | 20.4365 | 37.78
2021-02-06 19:00 | 44233.7917 | 0 | 20.551 | 37.78
2021-02-06 19:30 | 44233.8125 | 0 | 20.3284 | 37.78
2021-02-06 20:00 | 44233.8333 | 0 | 19.7016 | 37.78
2021-02-06 20:30 | 44233.8542 | 0 | 18.4206 | 37.78
2021-02-06 21:00 | 44233.875 | 0 | 17.3658 | 37.78
2021-02-06 21:30 | 44233.8958 | 0 | 15.9804 | 37.78
2021-02-06 22:00 | 44233.9167 | 0 | 14.8266 | 37.78
2021-02-06 22:30 | 44233.9375 | 0 | 14.0814 | 37.78
2021-02-06 23:00 | 44233.9583 | 0 | 13.5781 | 37.78
2021-02-06 23:30 | 44233.9792 | 0 | 13.1061 | 37.78
2021-02-07 | 44234 | 0 | 12.4134 | 37.78
2021-02-07 00:30 | 44234.0208 | 0 | 11.9595 | 37.78
2021-02-07 01:00 | 44234.0417 | 0 | 11.5402 | 37.78
2021-02-07 01:30 | 44234.0625 | 0 | 11.3505 | 37.78
2021-02-07 02:00 | 44234.0833 | 0 | 11.0661 | 37.78
2021-02-07 02:30 | 44234.1042 | 0 | 10.8203 | 37.78
2021-02-07 03:00 | 44234.125 | 0 | 10.5334 | 37.78
2021-02-07 03:30 | 44234.1458 | 0 | 10.453 | 37.78
2021-02-07 04:00 | 44234.1667 | 0 | 10.5083 | 37.78
2021-02-07 04:30 | 44234.1875 | 0 | 10.7097 | 37.78
2021-02-07 05:00 | 44234.2083 | 0 | 11.2299 | 37.78
2021-02-07 05:30 | 44234.2292 | 0 | 11.766 | 37.78
2021-02-07 06:00 | 44234.25 | 0 | 12.5575 | 37.78
2021-02-07 06:30 | 44234.2708 | 0 | 13.3754 | 37.78
2021-02-07 07:00 | 44234.2917 | 0 | 13.4493 | 37.78
2021-02-07 07:30 | 44234.3125 | 0 | 14.4806 | 37.78
2021-02-07 08:00 | 44234.3333 | 0 | 15.1243 | 37.78
2021-02-07 08:30 | 44234.3542 | 0 | 14.8263 | 37.78
2021-02-07 09:00 | 44234.375 | 0 | 14.0823 | 37.78
2021-02-07 09:30 | 44234.3958 | 0 | 14.633 | 37.78
2021-02-07 10:00 | 44234.4167 | 0 | 14.6392 | 37.78
2021-02-07 10:30 | 44234.4375 | 0 | 15.0539 | 37.78
2021-02-07 11:00 | 44234.4583 | 0 | 17.153 | 37.78
2021-02-07 11:30 | 44234.4792 | 0 | 17.5159 | 37.78
2021-02-07 12:00 | 44234.5 | 0 | 16.6927 | 37.78
2021-02-07 12:30 | 44234.5208 | 0 | 16.3955 | 37.78
2021-02-07 13:00 | 44234.5417 | 0 | 16.5357 | 37.78
2021-02-07 13:30 | 44234.5625 | 0 | 15.7971 | 37.78
2021-02-07 14:00 | 44234.5833 | 0 | 15.0271 | 37.78
2021-02-07 14:30 | 44234.6042 | 0 | 16.1565 | 37.78
2021-02-07 15:00 | 44234.625 | 0 | 15.4309 | 37.78
2021-02-07 15:30 | 44234.6458 | 0 | 16.0519 | 37.78
2021-02-07 16:00 | 44234.6667 | 0 | 15.8148 | 37.78
2021-02-07 16:30 | 44234.6875 | 0 | 15.5845 | 37.78
2021-02-07 17:00 | 44234.7083 | 0 | 16.0788 | 37.78
2021-02-07 17:30 | 44234.7292 | 0 | 16.3621 | 37.78
2021-02-07 18:00 | 44234.75 | 0 | 16.428 | 37.78
2021-02-07 18:30 | 44234.7708 | 0 | 16.8059 | 37.78
2021-02-07 19:00 | 44234.7917 | 0 | 16.7525 | 37.78
2021-02-07 19:30 | 44234.8125 | 0 | 16.4705 | 37.78
2021-02-07 20:00 | 44234.8333 | 0 | 16.16 | 37.78
2021-02-07 20:30 | 44234.8542 | 0 | 15.6699 | 37.78
2021-02-07 21:00 | 44234.875 | 0 | 14.7337 | 37.78
2021-02-07 21:30 | 44234.8958 | 0 | 14.0916 | 37.78
2021-02-07 22:00 | 44234.9167 | 0 | 13.5628 | 37.78
2021-02-07 22:30 | 44234.9375 | 0 | 12.4937 | 37.78
2021-02-07 23:00 | 44234.9583 | 0 | 11.9501 | 37.78
2021-02-07 23:30 | 44234.9792 | 0 | 11.4009 | 37.78
2021-02-08 | 44235 | 0 | 10.8997 | 37.78
2021-02-08 00:30 | 44235.0208 | 0 | 10.3838 | 37.78
2021-02-08 01:00 | 44235.0417 | 0 | 9.8334 | 37.78
2021-02-08 01:30 | 44235.0625 | 0 | 9.8381 | 37.78
2021-02-08 02:00 | 44235.0833 | 0 | 9.7059 | 37.78
2021-02-08 02:30 | 44235.1042 | 0 | 9.5785 | 37.78
2021-02-08 03:00 | 44235.125 | 0 | 9.472 | 37.78
2021-02-08 03:30 | 44235.1458 | 0 | 9.5085 | 37.78
2021-02-08 04:00 | 44235.1667 | 0 | 9.5563 | 37.78
2021-02-08 04:30 | 44235.1875 | 0 | 9.7902 | 37.78
2021-02-08 05:00 | 44235.2083 | 0 | 10.3659 | 37.78
2021-02-08 05:30 | 44235.2292 | 0 | 10.7417 | 37.78
2021-02-08 06:00 | 44235.25 | 0 | 11.4819 | 37.78
2021-02-08 06:30 | 44235.2708 | 0 | 12.0457 | 37.78
2021-02-08 07:00 | 44235.2917 | 0 | 12.7744 | 37.78
2021-02-08 07:30 | 44235.3125 | 0 | 13.012 | 37.78
2021-02-08 08:00 | 44235.3333 | 0 | 12.8319 | 37.78
2021-02-08 08:30 | 44235.3542 | 0 | 12.7336 | 37.78
2021-02-08 09:00 | 44235.375 | 0 | 12.8116 | 37.78
2021-02-08 09:30 | 44235.3958 | 0 | 13.4926 | 37.78
2021-02-08 10:00 | 44235.4167 | 0 | 13.7953 | 37.78
2021-02-08 10:30 | 44235.4375 | 0 | 14.1682 | 37.78
2021-02-08 11:00 | 44235.4583 | 0 | 13.8577 | 37.78
2021-02-08 11:30 | 44235.4792 | 0 | 14.1853 | 37.78
2021-02-08 12:00 | 44235.5 | 0 | 14.0493 | 37.78
2021-02-08 12:30 | 44235.5208 | 0 | 14.5613 | 37.78
2021-02-08 13:00 | 44235.5417 | 0 | 14.1246 | 37.78
2021-02-08 13:30 | 44235.5625 | 0 | 14.9917 | 37.78
2021-02-08 14:00 | 44235.5833 | 0 | 14.6957 | 37.78
2021-02-08 14:30 | 44235.6042 | 0 | 13.7742 | 37.78
2021-02-08 15:00 | 44235.625 | 0 | 14.3607 | 37.78
2021-02-08 15:30 | 44235.6458 | 0 | 15.0052 | 37.78
2021-02-08 16:00 | 44235.6667 | 0 | 15.2222 | 37.78
2021-02-08 16:30 | 44235.6875 | 0 | 15.4753 | 37.78
2021-02-08 17:00 | 44235.7083 | 0 | 16.0467 | 37.78
2021-02-08 17:30 | 44235.7292 | 0 | 15.7684 | 37.78
2021-02-08 18:00 | 44235.75 | 0 | 15.3574 | 37.78
2021-02-08 18:30 | 44235.7708 | 0 | 15.4871 | 37.78
2021-02-08 19:00 | 44235.7917 | 0 | 15.5557 | 37.78
2021-02-08 19:30 | 44235.8125 | 0 | 15.5539 | 37.78
2021-02-08 20:00 | 44235.8333 | 0 | 15.1151 | 37.78
2021-02-08 20:30 | 44235.8542 | 0 | 14.4935 | 37.78
2021-02-08 21:00 | 44235.875 | 0 | 13.7284 | 37.78
2021-02-08 21:30 | 44235.8958 | 0 | 13.1678 | 37.78
2021-02-08 22:00 | 44235.9167 | 0 | 12.4164 | 37.78
2021-02-08 22:30 | 44235.9375 | 0 | 11.3927 | 37.78
2021-02-08 23:00 | 44235.9583 | 0 | 10.7205 | 37.78
2021-02-08 23:30 | 44235.9792 | 0 | 10.2977 | 37.78
2021-02-09 | 44236 | 0 | 9.6716 | 37.78
2021-02-09 00:30 | 44236.0208 | 0 | 9.4681 | 37.78
2021-02-09 01:00 | 44236.0417 | 0 | 9.3074 | 37.78
2021-02-09 01:30 | 44236.0625 | 0 | 9.0556 | 37.78
2021-02-09 02:00 | 44236.0833 | 0 | 8.9563 | 37.78
2021-02-09 02:30 | 44236.1042 | 0 | 8.8293 | 37.78
2021-02-09 03:00 | 44236.125 | 0 | 8.6633 | 37.78
2021-02-09 03:30 | 44236.1458 | 0 | 8.6538 | 37.78
2021-02-09 04:00 | 44236.1667 | 0 | 8.8232 | 37.78
2021-02-09 04:30 | 44236.1875 | 0 | 9.0458 | 37.78
2021-02-09 05:00 | 44236.2083 | 0 | 9.5214 | 37.78
2021-02-09 05:30 | 44236.2292 | 0 | 10.1904 | 37.78
2021-02-09 06:00 | 44236.25 | 0 | 10.6357 | 37.78
2021-02-09 06:30 | 44236.2708 | 0 | 11.185 | 37.78
2021-02-09 07:00 | 44236.2917 | 0 | 11.5324 | 37.78
2021-02-09 07:30 | 44236.3125 | 0 | 11.6606 | 37.78
2021-02-09 08:00 | 44236.3333 | 0 | 11.4284 | 37.78
2021-02-09 08:30 | 44236.3542 | 0 | 12.4057 | 37.78
2021-02-09 09:00 | 44236.375 | 0 | 12.2721 | 37.78
2021-02-09 09:30 | 44236.3958 | 0 | 13.3086 | 37.78
2021-02-09 10:00 | 44236.4167 | 0 | 13.8727 | 37.78
2021-02-09 10:30 | 44236.4375 | 0 | 13.6941 | 37.78
2021-02-09 11:00 | 44236.4583 | 0 | 14.1437 | 37.78
2021-02-09 11:30 | 44236.4792 | 0 | 14.0387 | 37.78
2021-02-09 12:00 | 44236.5 | 0 | 13.1114 | 37.78
2021-02-09 12:30 | 44236.5208 | 0 | 11.7739 | 37.78
2021-02-09 13:00 | 44236.5417 | 0 | 12.5295 | 37.78
2021-02-09 13:30 | 44236.5625 | 0 | 12.7633 | 37.78
2021-02-09 14:00 | 44236.5833 | 0 | 13.6372 | 37.78
2021-02-09 14:30 | 44236.6042 | 0 | 12.9537 | 37.78
2021-02-09 15:00 | 44236.625 | 0 | 14.0473 | 37.78
2021-02-09 15:30 | 44236.6458 | 0 | 14.1736 | 37.78
2021-02-09 16:00 | 44236.6667 | 0 | 15.0066 | 37.78
2021-02-09 16:30 | 44236.6875 | 0 | 15.4529 | 37.78
2021-02-09 17:00 | 44236.7083 | 0 | 15.418 | 37.78
2021-02-09 17:30 | 44236.7292 | 0 | 14.9871 | 37.78
2021-02-09 18:00 | 44236.75 | 0 | 15.2155 | 37.78
2021-02-09 18:30 | 44236.7708 | 0 | 15.4661 | 37.78
2021-02-09 19:00 | 44236.7917 | 0 | 15.5727 | 37.78
2021-02-09 19:30 | 44236.8125 | 0 | 15.1642 | 37.78
2021-02-09 20:00 | 44236.8333 | 0 | 14.92 | 37.78
2021-02-09 20:30 | 44236.8542 | 0 | 14.3541 | 37.78
2021-02-09 21:00 | 44236.875 | 0 | 13.7108 | 37.78
2021-02-09 21:30 | 44236.8958 | 0 | 13.3519 | 37.78
2021-02-09 22:00 | 44236.9167 | 0 | 12.7212 | 37.78
2021-02-09 22:30 | 44236.9375 | 0 | 11.7722 | 37.78
2021-02-09 23:00 | 44236.9583 | 0 | 11.1504 | 37.78
2021-02-09 23:30 | 44236.9792 | 0 | 10.423 | 37.78
2021-02-10 | 44237 | 0 | 9.7238 | 37.78
2021-02-10 00:30 | 44237.0208 | 0 | 9.3245 | 37.78
2021-02-10 01:00 | 44237.0417 | 0 | 9.1506 | 37.78
2021-02-10 01:30 | 44237.0625 | 0 | 8.9536 | 37.78
2021-02-10 02:00 | 44237.0833 | 0 | 9.0478 | 37.78
2021-02-10 02:30 | 44237.1042 | 0 | 9.0319 | 37.78
2021-02-10 03:00 | 44237.125 | 0 | 8.9173 | 37.78
2021-02-10 03:30 | 44237.1458 | 0 | 8.9165 | 37.78
2021-02-10 04:00 | 44237.1667 | 0 | 9.2115 | 37.78
2021-02-10 04:30 | 44237.1875 | 0 | 9.4681 | 37.78
2021-02-10 05:00 | 44237.2083 | 0 | 9.8822 | 37.78
2021-02-10 05:30 | 44237.2292 | 0 | 10.4047 | 37.78
2021-02-10 06:00 | 44237.25 | 0 | 10.8843 | 37.78
2021-02-10 06:30 | 44237.2708 | 0 | 11.6866 | 37.78
2021-02-10 07:00 | 44237.2917 | 0 | 12.0776 | 37.78
2021-02-10 07:30 | 44237.3125 | 0 | 12.0172 | 37.78
2021-02-10 08:00 | 44237.3333 | 0 | 11.9523 | 37.78
2021-02-10 08:30 | 44237.3542 | 0 | 12.1872 | 37.78
2021-02-10 09:00 | 44237.375 | 0 | 12.6599 | 37.78
2021-02-10 09:30 | 44237.3958 | 0 | 12.6443 | 37.78
2021-02-10 10:00 | 44237.4167 | 0 | 13.2338 | 37.78
2021-02-10 10:30 | 44237.4375 | 0 | 13.6078 | 37.78
2021-02-10 11:00 | 44237.4583 | 0 | 14.4677 | 37.78
2021-02-10 11:30 | 44237.4792 | 0 | 14.5462 | 37.78
2021-02-10 12:00 | 44237.5 | 0 | 13.9907 | 37.78
2021-02-10 12:30 | 44237.5208 | 0 | 14.406 | 37.78
2021-02-10 13:00 | 44237.5417 | 0 | 13.15 | 37.78
2021-02-10 13:30 | 44237.5625 | 0 | 13.4374 | 37.78
2021-02-10 14:00 | 44237.5833 | 0 | 14.2919 | 37.78
2021-02-10 14:30 | 44237.6042 | 0 | 14.6901 | 37.78
2021-02-10 15:00 | 44237.625 | 0 | 14.2742 | 37.78
2021-02-10 15:30 | 44237.6458 | 0 | 14.3011 | 37.78
2021-02-10 16:00 | 44237.6667 | 0 | 14.254 | 37.78
2021-02-10 16:30 | 44237.6875 | 0 | 14.522 | 37.78
2021-02-10 17:00 | 44237.7083 | 0 | 14.7044 | 37.78
2021-02-10 17:30 | 44237.7292 | 0 | 14.6429 | 37.78
2021-02-10 18:00 | 44237.75 | 0 | 14.7526 | 37.78
2021-02-10 18:30 | 44237.7708 | 0 | 15.1315 | 37.78
2021-02-10 19:00 | 44237.7917 | 0 | 15.2711 | 37.78
2021-02-10 19:30 | 44237.8125 | 0 | 15.1625 | 37.78
2021-02-10 20:00 | 44237.8333 | 0 | 14.8878 | 37.78
2021-02-10 20:30 | 44237.8542 | 0 | 14.355 | 37.78
2021-02-10 21:00 | 44237.875 | 0 | 13.9072 | 37.78
2021-02-10 21:30 | 44237.8958 | 0 | 13.3572 | 37.78
2021-02-10 22:00 | 44237.9167 | 0 | 12.6036 | 37.78
2021-02-10 22:30 | 44237.9375 | 0 | 11.5962 | 37.78
2021-02-10 23:00 | 44237.9583 | 0 | 11.1234 | 37.78
2021-02-10 23:30 | 44237.9792 | 0 | 10.6017 | 37.78
2021-02-11 | 44238 | 0 | 10.067 | 37.78
2021-02-11 00:30 | 44238.0208 | 0 | 9.6812 | 37.78
2021-02-11 01:00 | 44238.0417 | 0 | 9.4914 | 37.78
2021-02-11 01:30 | 44238.0625 | 0 | 9.4813 | 37.78
2021-02-11 02:00 | 44238.0833 | 0 | 9.4125 | 37.78
2021-02-11 02:30 | 44238.1042 | 0 | 9.0433 | 37.78
2021-02-11 03:00 | 44238.125 | 0 | 9.0333 | 37.78
2021-02-11 03:30 | 44238.1458 | 0 | 9.0803 | 37.78
2021-02-11 04:00 | 44238.1667 | 0 | 9.2287 | 37.78
2021-02-11 04:30 | 44238.1875 | 0 | 9.5592 | 37.78
2021-02-11 05:00 | 44238.2083 | 0 | 9.9874 | 37.78
2021-02-11 05:30 | 44238.2292 | 0 | 10.4974 | 37.78
2021-02-11 06:00 | 44238.25 | 0 | 11.1391 | 37.78
2021-02-11 06:30 | 44238.2708 | 0 | 12.167 | 37.78
2021-02-11 07:00 | 44238.2917 | 0 | 13.0548 | 37.78
2021-02-11 07:30 | 44238.3125 | 0 | 13.4307 | 37.78
2021-02-11 08:00 | 44238.3333 | 0 | 13.0671 | 37.78
2021-02-11 08:30 | 44238.3542 | 0 | 13.0428 | 37.78
2021-02-11 09:00 | 44238.375 | 0 | 13.9835 | 37.78
2021-02-11 09:30 | 44238.3958 | 0 | 14.5156 | 37.78
2021-02-11 10:00 | 44238.4167 | 0 | 13.1421 | 37.78
2021-02-11 10:30 | 44238.4375 | 0 | 13.0111 | 37.78
2021-02-11 11:00 | 44238.4583 | 0 | 13.2583 | 37.78
2021-02-11 11:30 | 44238.4792 | 0 | 13.2545 | 37.78
2021-02-11 12:00 | 44238.5 | 0 | 14.1856 | 37.78
2021-02-11 12:30 | 44238.5208 | 0 | 13.7359 | 37.78
2021-02-11 13:00 | 44238.5417 | 0 | 14.4012 | 37.78
2021-02-11 13:30 | 44238.5625 | 0 | 13.7448 | 37.78
2021-02-11 14:00 | 44238.5833 | 0 | 14.1515 | 37.78
2021-02-11 14:30 | 44238.6042 | 0 | 14.2669 | 37.78
2021-02-11 15:00 | 44238.625 | 0 | 14.9337 | 37.78
2021-02-11 15:30 | 44238.6458 | 0 | 15.4111 | 37.78
2021-02-11 16:00 | 44238.6667 | 0 | 15.9083 | 37.78
2021-02-11 16:30 | 44238.6875 | 0 | 16.3883 | 37.78
2021-02-11 17:00 | 44238.7083 | 0 | 16.4813 | 37.78
2021-02-11 17:30 | 44238.7292 | 0 | 16.269 | 37.78
2021-02-11 18:00 | 44238.75 | 0 | 15.9498 | 37.78
2021-02-11 18:30 | 44238.7708 | 0 | 16.1129 | 37.78
2021-02-11 19:00 | 44238.7917 | 0 | 16.2957 | 37.78
2021-02-11 19:30 | 44238.8125 | 0 | 15.8736 | 37.78
2021-02-11 20:00 | 44238.8333 | 0 | 15.4846 | 37.78
2021-02-11 20:30 | 44238.8542 | 0 | 14.9545 | 37.78
2021-02-11 21:00 | 44238.875 | 0 | 14.5287 | 37.78
2021-02-11 21:30 | 44238.8958 | 0 | 13.7847 | 37.78
2021-02-11 22:00 | 44238.9167 | 0 | 13.0753 | 37.78
2021-02-11 22:30 | 44238.9375 | 0 | 12.3858 | 37.78
2021-02-11 23:00 | 44238.9583 | 0 | 12.0779 | 37.78
2021-02-11 23:30 | 44238.9792 | 0 | 11.55 | 37.78
2021-02-12 | 44239 | 0 | 10.7149 | 37.78
2021-02-12 00:30 | 44239.0208 | 0 | 10.4576 | 37.78
2021-02-12 01:00 | 44239.0417 | 0 | 10.1083 | 37.78
2021-02-12 01:30 | 44239.0625 | 0 | 9.7316 | 37.78
2021-02-12 02:00 | 44239.0833 | 0 | 9.5338 | 37.78
2021-02-12 02:30 | 44239.1042 | 0 | 9.1962 | 37.78
2021-02-12 03:00 | 44239.125 | 0 | 8.9049 | 37.78
2021-02-12 03:30 | 44239.1458 | 0 | 8.8141 | 37.78
2021-02-12 04:00 | 44239.1667 | 0 | 8.9509 | 37.78
2021-02-12 04:30 | 44239.1875 | 0 | 8.8635 | 37.78
2021-02-12 05:00 | 44239.2083 | 0 | 9.052 | 37.78
2021-02-12 05:30 | 44239.2292 | 0 | 9.0228 | 37.78
2021-02-12 06:00 | 44239.25 | 0 | 9.1731 | 37.78
2021-02-12 06:30 | 44239.2708 | 0 | 9.3002 | 37.78
2021-02-12 07:00 | 44239.2917 | 0 | 9.3514 | 37.78
2021-02-12 07:30 | 44239.3125 | 0 | 8.9898 | 37.78
2021-02-12 08:00 | 44239.3333 | 0 | 10.1133 | 37.78
2021-02-12 08:30 | 44239.3542 | 0 | 10.169 | 37.78
2021-02-12 09:00 | 44239.375 | 0 | 10.0547 | 37.78
2021-02-12 09:30 | 44239.3958 | 0 | 9.7831 | 37.78
2021-02-12 10:00 | 44239.4167 | 0 | 10.2124 | 37.78
2021-02-12 10:30 | 44239.4375 | 0 | 9.8054 | 37.78
2021-02-12 11:00 | 44239.4583 | 0 | 10.3609 | 37.78
2021-02-12 11:30 | 44239.4792 | 0 | 10.5106 | 37.78
2021-02-12 12:00 | 44239.5 | 0 | 10.8205 | 37.78
2021-02-12 12:30 | 44239.5208 | 0 | 11.2647 | 37.78
2021-02-12 13:00 | 44239.5417 | 0 | 12.2692 | 37.78
2021-02-12 13:30 | 44239.5625 | 0 | 13.0771 | 37.78
2021-02-12 14:00 | 44239.5833 | 0 | 13.4121 | 37.78
2021-02-12 14:30 | 44239.6042 | 0 | 14.7747 | 37.78
2021-02-12 15:00 | 44239.625 | 0 | 14.4399 | 37.78
2021-02-12 15:30 | 44239.6458 | 0 | 15.0415 | 37.78
2021-02-12 16:00 | 44239.6667 | 0 | 14.6046 | 37.78
2021-02-12 16:30 | 44239.6875 | 0 | 15.054 | 37.78
2021-02-12 17:00 | 44239.7083 | 0 | 15.4951 | 37.78
2021-02-12 17:30 | 44239.7292 | 0 | 15.7134 | 37.78
2021-02-12 18:00 | 44239.75 | 0 | 15.4256 | 37.78
2021-02-12 18:30 | 44239.7708 | 0 | 15.5349 | 37.78
2021-02-12 19:00 | 44239.7917 | 0 | 15.6573 | 37.78
2021-02-12 19:30 | 44239.8125 | 0 | 15.5176 | 37.78
2021-02-12 20:00 | 44239.8333 | 0 | 15.1486 | 37.78
2021-02-12 20:30 | 44239.8542 | 0 | 14.5646 | 37.78
2021-02-12 21:00 | 44239.875 | 0 | 14.3155 | 37.78
2021-02-12 21:30 | 44239.8958 | 0 | 13.9467 | 37.78
2021-02-12 22:00 | 44239.9167 | 0 | 13.3919 | 37.78
2021-02-12 22:30 | 44239.9375 | 0 | 12.6431 | 37.78
2021-02-12 23:00 | 44239.9583 | 0 | 11.9379 | 37.78
2021-02-12 23:30 | 44239.9792 | 0 | 11.4293 | 37.78
2021-02-13 | 44240 | 0 | 10.855 | 37.78
2021-02-13 00:30 | 44240.0208 | 0 | 10.4844 | 37.78
2021-02-13 01:00 | 44240.0417 | 0 | 10.2662 | 37.78
2021-02-13 01:30 | 44240.0625 | 0 | 10.0592 | 37.78
2021-02-13 02:00 | 44240.0833 | 0 | 9.924 | 37.78
2021-02-13 02:30 | 44240.1042 | 0 | 9.7838 | 37.78
2021-02-13 03:00 | 44240.125 | 0 | 9.5355 | 37.78
2021-02-13 03:30 | 44240.1458 | 0 | 9.5934 | 37.78
2021-02-13 04:00 | 44240.1667 | 0 | 9.4427 | 37.78
2021-02-13 04:30 | 44240.1875 | 0 | 9.3285 | 37.78
2021-02-13 05:00 | 44240.2083 | 0 | 9.229 | 37.78
2021-02-13 05:30 | 44240.2292 | 0 | 9.2619 | 37.78
2021-02-13 06:00 | 44240.25 | 0 | 9.3193 | 37.78
2021-02-13 06:30 | 44240.2708 | 0 | 9.3496 | 37.78
2021-02-13 07:00 | 44240.2917 | 0 | 9.5773 | 37.78
2021-02-13 07:30 | 44240.3125 | 0 | 10.0224 | 37.78
2021-02-13 08:00 | 44240.3333 | 0 | 9.8034 | 37.78
2021-02-13 08:30 | 44240.3542 | 0 | 9.8399 | 37.78
2021-02-13 09:00 | 44240.375 | 0 | 10.1145 | 37.78
2021-02-13 09:30 | 44240.3958 | 0 | 9.8056 | 37.78
2021-02-13 10:00 | 44240.4167 | 0 | 9.8442 | 37.78
2021-02-13 10:30 | 44240.4375 | 0 | 10.646 | 37.78
2021-02-13 11:00 | 44240.4583 | 0 | 11.3358 | 37.78
2021-02-13 11:30 | 44240.4792 | 0 | 11.504 | 37.78
2021-02-13 12:00 | 44240.5 | 0 | 10.5467 | 37.78
2021-02-13 12:30 | 44240.5208 | 0 | 12.5855 | 37.78
2021-02-13 13:00 | 44240.5417 | 0 | 12.711 | 37.78
2021-02-13 13:30 | 44240.5625 | 0 | 12.0409 | 37.78
2021-02-13 14:00 | 44240.5833 | 0 | 14.5218 | 37.78
2021-02-13 14:30 | 44240.6042 | 0 | 12.9919 | 37.78
2021-02-13 15:00 | 44240.625 | 0 | 13.1219 | 37.78
2021-02-13 15:30 | 44240.6458 | 0 | 14.2409 | 37.78
2021-02-13 16:00 | 44240.6667 | 0 | 13.9164 | 37.78
2021-02-13 16:30 | 44240.6875 | 0 | 14.1753 | 37.78
2021-02-13 17:00 | 44240.7083 | 0 | 14.2923 | 37.78
2021-02-13 17:30 | 44240.7292 | 0 | 14.0551 | 37.78
2021-02-13 18:00 | 44240.75 | 0 | 13.7499 | 37.78
2021-02-13 18:30 | 44240.7708 | 0 | 13.7754 | 37.78
2021-02-13 19:00 | 44240.7917 | 0 | 13.7015 | 37.78
2021-02-13 19:30 | 44240.8125 | 0 | 13.2713 | 37.78
2021-02-13 20:00 | 44240.8333 | 0 | 12.9659 | 37.78
2021-02-13 20:30 | 44240.8542 | 0 | 12.3992 | 37.78
2021-02-13 21:00 | 44240.875 | 0 | 11.7582 | 37.78
2021-02-13 21:30 | 44240.8958 | 0 | 11.415 | 37.78
2021-02-13 22:00 | 44240.9167 | 0 | 10.9045 | 37.78
2021-02-13 22:30 | 44240.9375 | 0 | 10.0905 | 37.78
2021-02-13 23:00 | 44240.9583 | 0 | 9.7527 | 37.78
2021-02-13 23:30 | 44240.9792 | 0 | 9.2844 | 37.78
2021-02-14 | 44241 | 0 | 9.037 | 37.78
2021-02-14 00:30 | 44241.0208 | 0 | 8.7641 | 37.78
2021-02-14 01:00 | 44241.0417 | 0 | 8.6979 | 37.78
2021-02-14 01:30 | 44241.0625 | 0 | 8.5254 | 37.78
2021-02-14 02:00 | 44241.0833 | 0 | 8.6015 | 37.78
2021-02-14 02:30 | 44241.1042 | 0 | 8.3055 | 37.78
2021-02-14 03:00 | 44241.125 | 0 | 8.3375 | 37.78
2021-02-14 03:30 | 44241.1458 | 0 | 8.4392 | 37.78
2021-02-14 04:00 | 44241.1667 | 0 | 8.6989 | 37.78
2021-02-14 04:30 | 44241.1875 | 0 | 9.0024 | 37.78
2021-02-14 05:00 | 44241.2083 | 0 | 9.5624 | 37.78
2021-02-14 05:30 | 44241.2292 | 0 | 10.215 | 37.78
2021-02-14 06:00 | 44241.25 | 0 | 10.9889 | 37.78
2021-02-14 06:30 | 44241.2708 | 0 | 11.6718 | 37.78
2021-02-14 07:00 | 44241.2917 | 0 | 12.128 | 37.78
2021-02-14 07:30 | 44241.3125 | 0 | 12.1713 | 37.78
2021-02-14 08:00 | 44241.3333 | 0 | 12.1507 | 37.78
2021-02-14 08:30 | 44241.3542 | 0 | 12.2463 | 37.78
2021-02-14 09:00 | 44241.375 | 0 | 13.1878 | 37.78
2021-02-14 09:30 | 44241.3958 | 0 | 12.6974 | 37.78
2021-02-14 10:00 | 44241.4167 | 0 | 12.984 | 37.78
2021-02-14 10:30 | 44241.4375 | 0 | 13.4081 | 37.78
2021-02-14 11:00 | 44241.4583 | 0 | 13.9623 | 37.78
2021-02-14 11:30 | 44241.4792 | 0 | 13.9903 | 37.78
2021-02-14 12:00 | 44241.5 | 0 | 14.0796 | 37.78
2021-02-14 12:30 | 44241.5208 | 0 | 13.7668 | 37.78
2021-02-14 13:00 | 44241.5417 | 0 | 15.2125 | 37.78
2021-02-14 13:30 | 44241.5625 | 0 | 14.4243 | 37.78
2021-02-14 14:00 | 44241.5833 | 0 | 14.0561 | 37.78
2021-02-14 14:30 | 44241.6042 | 0 | 13.6639 | 37.78
2021-02-14 15:00 | 44241.625 | 0 | 13.8788 | 37.78
2021-02-14 15:30 | 44241.6458 | 0 | 14.5873 | 37.78
2021-02-14 16:00 | 44241.6667 | 0 | 15.2154 | 37.78
2021-02-14 16:30 | 44241.6875 | 0 | 15.7063 | 37.78
2021-02-14 17:00 | 44241.7083 | 0 | 16.0536 | 37.78
2021-02-14 17:30 | 44241.7292 | 0 | 16.0971 | 37.78
2021-02-14 18:00 | 44241.75 | 0 | 16.2565 | 37.78
2021-02-14 18:30 | 44241.7708 | 0 | 16.7384 | 37.78
2021-02-14 19:00 | 44241.7917 | 0 | 16.5007 | 37.78
2021-02-14 19:30 | 44241.8125 | 0 | 15.9932 | 37.78
2021-02-14 20:00 | 44241.8333 | 0 | 15.6133 | 37.78
2021-02-14 20:30 | 44241.8542 | 0 | 14.6859 | 37.78
2021-02-14 21:00 | 44241.875 | 0 | 14.3524 | 37.78
2021-02-14 21:30 | 44241.8958 | 0 | 13.6479 | 37.78
2021-02-14 22:00 | 44241.9167 | 0 | 12.8785 | 37.78
2021-02-14 22:30 | 44241.9375 | 0 | 11.9644 | 37.78
2021-02-14 23:00 | 44241.9583 | 0 | 11.3196 | 37.78
2021-02-14 23:30 | 44241.9792 | 0 | 10.8401 | 37.78
2021-02-15 | 44242 | 0 | 10.1784 | 37.78
2021-02-15 00:30 | 44242.0208 | 0 | 9.6915 | 37.78
2021-02-15 01:00 | 44242.0417 | 0 | 9.5867 | 37.78
2021-02-15 01:30 | 44242.0625 | 0 | 9.2024 | 37.78
2021-02-15 02:00 | 44242.0833 | 0 | 9.1918 | 37.78
2021-02-15 02:30 | 44242.1042 | 0 | 9.0438 | 37.78
2021-02-15 03:00 | 44242.125 | 0 | 8.9176 | 37.78
2021-02-15 03:30 | 44242.1458 | 0 | 8.8728 | 37.78
2021-02-15 04:00 | 44242.1667 | 0 | 9.079 | 37.78
2021-02-15 04:30 | 44242.1875 | 0 | 9.3492 | 37.78
2021-02-15 05:00 | 44242.2083 | 0 | 10.09 | 37.78
2021-02-15 05:30 | 44242.2292 | 0 | 10.5109 | 37.78
2021-02-15 06:00 | 44242.25 | 0 | 11.2478 | 37.78
2021-02-15 06:30 | 44242.2708 | 0 | 11.9826 | 37.78
2021-02-15 07:00 | 44242.2917 | 0 | 12.4722 | 37.78
2021-02-15 07:30 | 44242.3125 | 0 | 12.9672 | 37.78
2021-02-15 08:00 | 44242.3333 | 0 | 12.9375 | 37.78
2021-02-15 08:30 | 44242.3542 | 0 | 13.5837 | 37.78
2021-02-15 09:00 | 44242.375 | 0 | 14.5719 | 37.78
2021-02-15 09:30 | 44242.3958 | 0 | 13.9183 | 37.78
2021-02-15 10:00 | 44242.4167 | 0 | 14.327 | 37.78
2021-02-15 10:30 | 44242.4375 | 0 | 13.4463 | 37.78
2021-02-15 11:00 | 44242.4583 | 0 | 14.3984 | 37.78
2021-02-15 11:30 | 44242.4792 | 0 | 14.7937 | 37.78
2021-02-15 12:00 | 44242.5 | 0 | 14.9327 | 37.78
2021-02-15 12:30 | 44242.5208 | 0 | 13.8401 | 37.78
2021-02-15 13:00 | 44242.5417 | 0 | 16.3763 | 37.78
2021-02-15 13:30 | 44242.5625 | 0 | 13.2334 | 37.78
2021-02-15 14:00 | 44242.5833 | 0 | 14.0606 | 37.78
2021-02-15 14:30 | 44242.6042 | 0 | 14.4398 | 37.78
2021-02-15 15:00 | 44242.625 | 0 | 15.6906 | 37.78
2021-02-15 15:30 | 44242.6458 | 0 | 14.8604 | 37.78
2021-02-15 16:00 | 44242.6667 | 0 | 14.2902 | 37.78
2021-02-15 16:30 | 44242.6875 | 0 | 13.6691 | 37.78
2021-02-15 17:00 | 44242.7083 | 0 | 14.8072 | 37.78
2021-02-15 17:30 | 44242.7292 | 0 | 15.1392 | 37.78
2021-02-15 18:00 | 44242.75 | 0 | 14.7436 | 37.78
2021-02-15 18:30 | 44242.7708 | 0 | 15.2865 | 37.78
2021-02-15 19:00 | 44242.7917 | 0 | 15.3114 | 37.78
2021-02-15 19:30 | 44242.8125 | 0 | 14.937 | 37.78
2021-02-15 20:00 | 44242.8333 | 0 | 14.4644 | 37.78
2021-02-15 20:30 | 44242.8542 | 0 | 13.9726 | 37.78
2021-02-15 21:00 | 44242.875 | 0 | 13.4446 | 37.78
2021-02-15 21:30 | 44242.8958 | 0 | 12.7826 | 37.78
2021-02-15 22:00 | 44242.9167 | 0 | 12.1992 | 37.78
2021-02-15 22:30 | 44242.9375 | 0 | 11.2437 | 37.78
2021-02-15 23:00 | 44242.9583 | 0 | 10.5739 | 37.78
2021-02-15 23:30 | 44242.9792 | 0 | 9.986 | 37.78
2021-02-16 | 44243 | 0 | 9.2055 | 37.78
2021-02-16 00:30 | 44243.0208 | 0 | 8.9619 | 37.78
2021-02-16 01:00 | 44243.0417 | 0 | 8.8661 | 37.78
2021-02-16 01:30 | 44243.0625 | 0 | 8.7065 | 37.78
2021-02-16 02:00 | 44243.0833 | 0 | 8.5556 | 37.78
2021-02-16 02:30 | 44243.1042 | 0 | 8.3676 | 37.78
2021-02-16 03:00 | 44243.125 | 0 | 8.3174 | 37.78
2021-02-16 03:30 | 44243.1458 | 0 | 8.5632 | 37.78
2021-02-16 04:00 | 44243.1667 | 0 | 8.8897 | 37.78
2021-02-16 04:30 | 44243.1875 | 0 | 9.1206 | 37.78
2021-02-16 05:00 | 44243.2083 | 0 | 9.5362 | 37.78
2021-02-16 05:30 | 44243.2292 | 0 | 10.251 | 37.78
2021-02-16 06:00 | 44243.25 | 0 | 10.6866 | 37.78
2021-02-16 06:30 | 44243.2708 | 0 | 11.3325 | 37.78
2021-02-16 07:00 | 44243.2917 | 0 | 11.9019 | 37.78
2021-02-16 07:30 | 44243.3125 | 0 | 12.0111 | 37.78
2021-02-16 08:00 | 44243.3333 | 0 | 12.1169 | 37.78
2021-02-16 08:30 | 44243.3542 | 0 | 11.9422 | 37.78
2021-02-16 09:00 | 44243.375 | 0 | 14.0592 | 37.78
2021-02-16 09:30 | 44243.3958 | 0 | 13.3462 | 37.78
2021-02-16 10:00 | 44243.4167 | 0 | 13.4159 | 37.78
2021-02-16 10:30 | 44243.4375 | 0 | 13.0641 | 37.78
2021-02-16 11:00 | 44243.4583 | 0 | 12.9523 | 37.78
2021-02-16 11:30 | 44243.4792 | 0 | 11.6722 | 37.78
2021-02-16 12:00 | 44243.5 | 0 | 12.6289 | 37.78
2021-02-16 12:30 | 44243.5208 | 0 | 12.6203 | 37.78
2021-02-16 13:00 | 44243.5417 | 0 | 13.6768 | 37.78
2021-02-16 13:30 | 44243.5625 | 0 | 12.4398 | 37.78
2021-02-16 14:00 | 44243.5833 | 0 | 13.6829 | 37.78
2021-02-16 14:30 | 44243.6042 | 0 | 13.4006 | 37.78
2021-02-16 15:00 | 44243.625 | 0 | 13.5716 | 37.78
2021-02-16 15:30 | 44243.6458 | 0 | 13.7473 | 37.78
2021-02-16 16:00 | 44243.6667 | 0 | 13.5933 | 37.78
2021-02-16 16:30 | 44243.6875 | 0 | 14.0254 | 37.78
2021-02-16 17:00 | 44243.7083 | 0 | 14.4923 | 37.78
2021-02-16 17:30 | 44243.7292 | 0 | 14.5793 | 37.78
2021-02-16 18:00 | 44243.75 | 0 | 14.6039 | 37.78
2021-02-16 18:30 | 44243.7708 | 0 | 15.0887 | 37.78
2021-02-16 19:00 | 44243.7917 | 0 | 15.0351 | 37.78
2021-02-16 19:30 | 44243.8125 | 0 | 14.6638 | 37.78
2021-02-16 20:00 | 44243.8333 | 0 | 14.4675 | 37.78
2021-02-16 20:30 | 44243.8542 | 0 | 13.8482 | 37.78
2021-02-16 21:00 | 44243.875 | 0 | 13.4197 | 37.78
2021-02-16 21:30 | 44243.8958 | 0 | 12.85 | 37.78
2021-02-16 22:00 | 44243.9167 | 0 | 12.1818 | 37.78
2021-02-16 22:30 | 44243.9375 | 0 | 11.1349 | 37.78
2021-02-16 23:00 | 44243.9583 | 0 | 10.6201 | 37.78
2021-02-16 23:30 | 44243.9792 | 0 | 10.0565 | 37.78
2021-02-17 | 44244 | 0 | 9.5399 | 37.78
2021-02-17 00:30 | 44244.0208 | 0 | 9.1212 | 37.78
2021-02-17 01:00 | 44244.0417 | 0 | 8.9348 | 37.78
2021-02-17 01:30 | 44244.0625 | 0 | 8.9631 | 37.78
2021-02-17 02:00 | 44244.0833 | 0 | 8.599 | 37.78
2021-02-17 02:30 | 44244.1042 | 0 | 8.5399 | 37.78
2021-02-17 03:00 | 44244.125 | 0 | 8.5993 | 37.78
2021-02-17 03:30 | 44244.1458 | 0 | 8.5513 | 37.78
2021-02-17 04:00 | 44244.1667 | 0 | 8.8424 | 37.78
2021-02-17 04:30 | 44244.1875 | 0 | 9.2612 | 37.78
2021-02-17 05:00 | 44244.2083 | 0 | 9.841 | 37.78
2021-02-17 05:30 | 44244.2292 | 0 | 10.2966 | 37.78
2021-02-17 06:00 | 44244.25 | 0 | 11.0788 | 37.78
2021-02-17 06:30 | 44244.2708 | 0 | 12.0919 | 37.78
2021-02-17 07:00 | 44244.2917 | 0 | 12.7273 | 37.78
2021-02-17 07:30 | 44244.3125 | 0 | 13.1772 | 37.78
2021-02-17 08:00 | 44244.3333 | 0 | 12.4669 | 37.78
2021-02-17 08:30 | 44244.3542 | 0 | 14.1894 | 37.78
2021-02-17 09:00 | 44244.375 | 0 | 14.2146 | 37.78
2021-02-17 09:30 | 44244.3958 | 0 | 14.4752 | 37.78
2021-02-17 10:00 | 44244.4167 | 0 | 13.8069 | 37.78
2021-02-17 10:30 | 44244.4375 | 0 | 13.0282 | 37.78
2021-02-17 11:00 | 44244.4583 | 0 | 12.9711 | 37.78
2021-02-17 11:30 | 44244.4792 | 0 | 12.9787 | 37.78
2021-02-17 12:00 | 44244.5 | 0 | 13.9759 | 37.78
2021-02-17 12:30 | 44244.5208 | 0 | 13.5517 | 37.78
2021-02-17 13:00 | 44244.5417 | 0 | 13.8239 | 37.78
2021-02-17 13:30 | 44244.5625 | 0 | 12.9699 | 37.78
2021-02-17 14:00 | 44244.5833 | 0 | 12.072 | 37.78
2021-02-17 14:30 | 44244.6042 | 0 | 12.4451 | 37.78
2021-02-17 15:00 | 44244.625 | 0 | 12.8404 | 37.78
2021-02-17 15:30 | 44244.6458 | 0 | 14.2213 | 37.78
2021-02-17 16:00 | 44244.6667 | 0 | 13.6271 | 37.78
2021-02-17 16:30 | 44244.6875 | 0 | 14.593 | 37.78
2021-02-17 17:00 | 44244.7083 | 0 | 14.7741 | 37.78
2021-02-17 17:30 | 44244.7292 | 0 | 15.0348 | 37.78
2021-02-17 18:00 | 44244.75 | 0 | 14.9209 | 37.78
2021-02-17 18:30 | 44244.7708 | 0 | 15.5847 | 37.78
2021-02-17 19:00 | 44244.7917 | 0 | 15.4077 | 37.78
2021-02-17 19:30 | 44244.8125 | 0 | 15.2965 | 37.78
2021-02-17 20:00 | 44244.8333 | 0 | 14.8501 | 37.78
2021-02-17 20:30 | 44244.8542 | 0 | 14.3024 | 37.78
2021-02-17 21:00 | 44244.875 | 0 | 13.6937 | 37.78
2021-02-17 21:30 | 44244.8958 | 0 | 13.1984 | 37.78
2021-02-17 22:00 | 44244.9167 | 0 | 12.62 | 37.78
2021-02-17 22:30 | 44244.9375 | 0 | 11.6702 | 37.78
2021-02-17 23:00 | 44244.9583 | 0 | 11.0711 | 37.78
2021-02-17 23:30 | 44244.9792 | 0 | 10.5657 | 37.78
2021-02-18 | 44245 | 0 | 9.98 | 37.78
2021-02-18 00:30 | 44245.0208 | 0 | 9.493 | 37.78
2021-02-18 01:00 | 44245.0417 | 0 | 9.1576 | 37.78
2021-02-18 01:30 | 44245.0625 | 0 | 9.0334 | 37.78
2021-02-18 02:00 | 44245.0833 | 0 | 9.0625 | 37.78
2021-02-18 02:30 | 44245.1042 | 0 | 8.8061 | 37.78
2021-02-18 03:00 | 44245.125 | 0 | 8.7469 | 37.78
2021-02-18 03:30 | 44245.1458 | 0 | 8.8854 | 37.78
2021-02-18 04:00 | 44245.1667 | 0 | 9.0566 | 37.78
2021-02-18 04:30 | 44245.1875 | 0 | 9.465 | 37.78
2021-02-18 05:00 | 44245.2083 | 0 | 10.0614 | 37.78
2021-02-18 05:30 | 44245.2292 | 0 | 10.5587 | 37.78
2021-02-18 06:00 | 44245.25 | 0 | 11.0639 | 37.78
2021-02-18 06:30 | 44245.2708 | 0 | 11.7388 | 37.78
2021-02-18 07:00 | 44245.2917 | 0 | 12.4304 | 37.78
2021-02-18 07:30 | 44245.3125 | 0 | 13.2121 | 37.78
2021-02-18 08:00 | 44245.3333 | 0 | 13.4709 | 37.78
2021-02-18 08:30 | 44245.3542 | 0 | 13.7915 | 37.78
2021-02-18 09:00 | 44245.375 | 0 | 13.6619 | 37.78
2021-02-18 09:30 | 44245.3958 | 0 | 13.26 | 37.78
2021-02-18 10:00 | 44245.4167 | 0 | 13.4404 | 37.78
2021-02-18 10:30 | 44245.4375 | 0 | 13.5206 | 37.78
2021-02-18 11:00 | 44245.4583 | 0 | 13.2783 | 37.78
2021-02-18 11:30 | 44245.4792 | 0 | 14.5254 | 37.78
2021-02-18 12:00 | 44245.5 | 0 | 14.207 | 37.78
2021-02-18 12:30 | 44245.5208 | 0 | 14.2076 | 37.78
2021-02-18 13:00 | 44245.5417 | 0 | 15.0293 | 37.78
2021-02-18 13:30 | 44245.5625 | 0 | 15.5373 | 37.78
2021-02-18 14:00 | 44245.5833 | 0 | 15.6948 | 37.78
2021-02-18 14:30 | 44245.6042 | 0 | 15.7389 | 37.78
2021-02-18 15:00 | 44245.625 | 0 | 15.2236 | 37.78
2021-02-18 15:30 | 44245.6458 | 0 | 15.7662 | 37.78
2021-02-18 16:00 | 44245.6667 | 0 | 15.3111 | 37.78
2021-02-18 16:30 | 44245.6875 | 0 | 15.3748 | 37.78
2021-02-18 17:00 | 44245.7083 | 0 | 15.036 | 37.78
2021-02-18 17:30 | 44245.7292 | 0 | 15.2207 | 37.78
2021-02-18 18:00 | 44245.75 | 0 | 14.9895 | 37.78
2021-02-18 18:30 | 44245.7708 | 0 | 15.3375 | 37.78
2021-02-18 19:00 | 44245.7917 | 0 | 15.424 | 37.78
2021-02-18 19:30 | 44245.8125 | 0 | 15.2903 | 37.78
2021-02-18 20:00 | 44245.8333 | 0 | 14.9316 | 37.78
2021-02-18 20:30 | 44245.8542 | 0 | 14.4387 | 37.78
2021-02-18 21:00 | 44245.875 | 0 | 14.0597 | 37.78
2021-02-18 21:30 | 44245.8958 | 0 | 13.8028 | 37.78
2021-02-18 22:00 | 44245.9167 | 0 | 13.0215 | 37.78
2021-02-18 22:30 | 44245.9375 | 0 | 12.065 | 37.78
2021-02-18 23:00 | 44245.9583 | 0 | 11.3773 | 37.78
2021-02-18 23:30 | 44245.9792 | 0 | 11.0253 | 37.78
2021-02-19 | 44246 | 0 | 10.4204 | 37.78
2021-02-19 00:30 | 44246.0208 | 0 | 9.851 | 37.78
2021-02-19 01:00 | 44246.0417 | 0 | 9.5947 | 37.78
2021-02-19 01:30 | 44246.0625 | 0 | 9.4659 | 37.78
2021-02-19 02:00 | 44246.0833 | 0 | 9.4431 | 37.78
2021-02-19 02:30 | 44246.1042 | 0 | 9.2024 | 37.78
2021-02-19 03:00 | 44246.125 | 0 | 9.1411 | 37.78
2021-02-19 03:30 | 44246.1458 | 0 | 9.1338 | 37.78
2021-02-19 04:00 | 44246.1667 | 0 | 9.2584 | 37.78
2021-02-19 04:30 | 44246.1875 | 0 | 9.2204 | 37.78
2021-02-19 05:00 | 44246.2083 | 0 | 9.402 | 37.78
2021-02-19 05:30 | 44246.2292 | 0 | 9.4567 | 37.78
2021-02-19 06:00 | 44246.25 | 0 | 9.3749 | 37.78
2021-02-19 06:30 | 44246.2708 | 0 | 9.5069 | 37.78
2021-02-19 07:00 | 44246.2917 | 0 | 9.8167 | 37.78
2021-02-19 07:30 | 44246.3125 | 0 | 10.0912 | 37.78
2021-02-19 08:00 | 44246.3333 | 0 | 10.1621 | 37.78
2021-02-19 08:30 | 44246.3542 | 0 | 10.8713 | 37.78
2021-02-19 09:00 | 44246.375 | 0 | 10.6327 | 37.78
2021-02-19 09:30 | 44246.3958 | 0 | 10.6554 | 37.78
2021-02-19 10:00 | 44246.4167 | 0 | 10.3467 | 37.78
2021-02-19 10:30 | 44246.4375 | 0 | 9.9041 | 37.78
2021-02-19 11:00 | 44246.4583 | 0 | 10.7859 | 37.78
2021-02-19 11:30 | 44246.4792 | 0 | 12.3771 | 37.78
2021-02-19 12:00 | 44246.5 | 0 | 12.467 | 37.78
2021-02-19 12:30 | 44246.5208 | 0 | 12.448 | 37.78
2021-02-19 13:00 | 44246.5417 | 0 | 12.1888 | 37.78
2021-02-19 13:30 | 44246.5625 | 0 | 12.2982 | 37.78
2021-02-19 14:00 | 44246.5833 | 0 | 12.7293 | 37.78
2021-02-19 14:30 | 44246.6042 | 0 | 12.8721 | 37.78
2021-02-19 15:00 | 44246.625 | 0 | 12.8506 | 37.78
2021-02-19 15:30 | 44246.6458 | 0 | 12.4874 | 37.78
2021-02-19 16:00 | 44246.6667 | 0 | 12.6648 | 37.78
2021-02-19 16:30 | 44246.6875 | 0 | 13.5612 | 37.78
2021-02-19 17:00 | 44246.7083 | 0 | 14.1463 | 37.78
2021-02-19 17:30 | 44246.7292 | 0 | 14.9944 | 37.78
2021-02-19 18:00 | 44246.75 | 0 | 14.8167 | 37.78
2021-02-19 18:30 | 44246.7708 | 0 | 15.251 | 37.78
2021-02-19 19:00 | 44246.7917 | 0 | 14.8377 | 37.78
2021-02-19 19:30 | 44246.8125 | 0 | 14.6992 | 37.78
2021-02-19 20:00 | 44246.8333 | 0 | 14.342 | 37.78
2021-02-19 20:30 | 44246.8542 | 0 | 13.8601 | 37.78
2021-02-19 21:00 | 44246.875 | 0 | 13.3306 | 37.78
2021-02-19 21:30 | 44246.8958 | 0 | 12.971 | 37.78
2021-02-19 22:00 | 44246.9167 | 0 | 12.5073 | 37.78
2021-02-19 22:30 | 44246.9375 | 0 | 11.6539 | 37.78
2021-02-19 23:00 | 44246.9583 | 0 | 11.1089 | 37.78
2021-02-19 23:30 | 44246.9792 | 0 | 10.5827 | 37.78
2021-02-20 | 44247 | 0 | 9.9477 | 37.78
2021-02-20 00:30 | 44247.0208 | 0 | 9.6755 | 37.78
2021-02-20 01:00 | 44247.0417 | 0 | 9.1617 | 37.78
2021-02-20 01:30 | 44247.0625 | 0 | 9.0784 | 37.78
2021-02-20 02:00 | 44247.0833 | 0 | 8.9999 | 37.78
2021-02-20 02:30 | 44247.1042 | 0 | 8.7097 | 37.78
2021-02-20 03:00 | 44247.125 | 0 | 8.6768 | 37.78
2021-02-20 03:30 | 44247.1458 | 0 | 8.6217 | 37.78
2021-02-20 04:00 | 44247.1667 | 0 | 8.5821 | 37.78
2021-02-20 04:30 | 44247.1875 | 0 | 8.6432 | 37.78
2021-02-20 05:00 | 44247.2083 | 0 | 8.5381 | 37.78
2021-02-20 05:30 | 44247.2292 | 0 | 8.4228 | 37.78
2021-02-20 06:00 | 44247.25 | 0 | 8.398 | 37.78
2021-02-20 06:30 | 44247.2708 | 0 | 8.6 | 37.78
2021-02-20 07:00 | 44247.2917 | 0 | 8.9566 | 37.78
2021-02-20 07:30 | 44247.3125 | 0 | 8.8911 | 37.78
2021-02-20 08:00 | 44247.3333 | 0 | 9.0751 | 37.78
2021-02-20 08:30 | 44247.3542 | 0 | 9.3109 | 37.78
2021-02-20 09:00 | 44247.375 | 0 | 9.5404 | 37.78
2021-02-20 09:30 | 44247.3958 | 0 | 9.8553 | 37.78
2021-02-20 10:00 | 44247.4167 | 0 | 10.3542 | 37.78
2021-02-20 10:30 | 44247.4375 | 0 | 11.3217 | 37.78
2021-02-20 11:00 | 44247.4583 | 0 | 11.1599 | 37.78
2021-02-20 11:30 | 44247.4792 | 0 | 12.6623 | 37.78
2021-02-20 12:00 | 44247.5 | 0 | 12.7788 | 37.78
2021-02-20 12:30 | 44247.5208 | 0 | 13.2037 | 37.78
2021-02-20 13:00 | 44247.5417 | 0 | 13.5396 | 37.78
2021-02-20 13:30 | 44247.5625 | 0 | 14.0471 | 37.78
2021-02-20 14:00 | 44247.5833 | 0 | 15.4774 | 37.78
2021-02-20 14:30 | 44247.6042 | 0 | 15.0928 | 37.78
2021-02-20 15:00 | 44247.625 | 0 | 15.6755 | 37.78
2021-02-20 15:30 | 44247.6458 | 0 | 16.6243 | 37.78
2021-02-20 16:00 | 44247.6667 | 0 | 18.4674 | 37.78
2021-02-20 16:30 | 44247.6875 | 0 | 18.9103 | 37.78
2021-02-20 17:00 | 44247.7083 | 0 | 18.4527 | 37.78
2021-02-20 17:30 | 44247.7292 | 0 | 18.7467 | 37.78
2021-02-20 18:00 | 44247.75 | 0 | 18.5218 | 37.78
2021-02-20 18:30 | 44247.7708 | 0 | 18.8162 | 37.78
2021-02-20 19:00 | 44247.7917 | 0 | 18.4435 | 37.78
2021-02-20 19:30 | 44247.8125 | 0 | 18.1427 | 37.78
2021-02-20 20:00 | 44247.8333 | 0 | 17.7353 | 37.78
2021-02-20 20:30 | 44247.8542 | 0 | 16.6974 | 37.78
2021-02-20 21:00 | 44247.875 | 0 | 15.7471 | 37.78
2021-02-20 21:30 | 44247.8958 | 0 | 14.7871 | 37.78
2021-02-20 22:00 | 44247.9167 | 0 | 13.7312 | 37.78
2021-02-20 22:30 | 44247.9375 | 0 | 12.5792 | 37.78
2021-02-20 23:00 | 44247.9583 | 0 | 11.761 | 37.78
2021-02-20 23:30 | 44247.9792 | 0 | 11.3452 | 37.78
2021-02-21 | 44248 | 0 | 10.9841 | 37.78
2021-02-21 00:30 | 44248.0208 | 0 | 10.4555 | 37.78
2021-02-21 01:00 | 44248.0417 | 0 | 10.2379 | 37.78
2021-02-21 01:30 | 44248.0625 | 0 | 10.0758 | 37.78
2021-02-21 02:00 | 44248.0833 | 0 | 9.9918 | 37.78
2021-02-21 02:30 | 44248.1042 | 0 | 9.5059 | 37.78
2021-02-21 03:00 | 44248.125 | 0 | 9.3928 | 37.78
2021-02-21 03:30 | 44248.1458 | 0 | 9.4403 | 37.78
2021-02-21 04:00 | 44248.1667 | 0 | 9.6888 | 37.78
2021-02-21 04:30 | 44248.1875 | 0 | 10.0796 | 37.78
2021-02-21 05:00 | 44248.2083 | 0 | 10.6252 | 37.78
2021-02-21 05:30 | 44248.2292 | 0 | 11.3321 | 37.78
2021-02-21 06:00 | 44248.25 | 0 | 12.3148 | 37.78
2021-02-21 06:30 | 44248.2708 | 0 | 13.0719 | 37.78
2021-02-21 07:00 | 44248.2917 | 0 | 13.8325 | 37.78
2021-02-21 07:30 | 44248.3125 | 0 | 14.4174 | 37.78
2021-02-21 08:00 | 44248.3333 | 0 | 14.5661 | 37.78
2021-02-21 08:30 | 44248.3542 | 0 | 15.212 | 37.78
2021-02-21 09:00 | 44248.375 | 0 | 15.5743 | 37.78
2021-02-21 09:30 | 44248.3958 | 0 | 15.992 | 37.78
2021-02-21 10:00 | 44248.4167 | 0 | 16.0055 | 37.78
2021-02-21 10:30 | 44248.4375 | 0 | 16.4229 | 37.78
2021-02-21 11:00 | 44248.4583 | 0 | 17.0246 | 37.78
2021-02-21 11:30 | 44248.4792 | 0 | 17.3955 | 37.78
2021-02-21 12:00 | 44248.5 | 0 | 17.6148 | 37.78
2021-02-21 12:30 | 44248.5208 | 0 | 17.9702 | 37.78
2021-02-21 13:00 | 44248.5417 | 0 | 18.6202 | 37.78
2021-02-21 13:30 | 44248.5625 | 0 | 19.2865 | 37.78
2021-02-21 14:00 | 44248.5833 | 0 | 20.0425 | 37.78
2021-02-21 14:30 | 44248.6042 | 0 | 20.1947 | 37.78
2021-02-21 15:00 | 44248.625 | 0 | 20.6651 | 37.78
2021-02-21 15:30 | 44248.6458 | 0 | 20.7723 | 37.78
2021-02-21 16:00 | 44248.6667 | 0 | 21.7257 | 37.78
2021-02-21 16:30 | 44248.6875 | 0 | 22.0201 | 37.78
2021-02-21 17:00 | 44248.7083 | 0 | 22.1409 | 37.78
2021-02-21 17:30 | 44248.7292 | 0 | 22.4439 | 37.78
2021-02-21 18:00 | 44248.75 | 0 | 21.9372 | 37.78
2021-02-21 18:30 | 44248.7708 | 0 | 22.2316 | 37.78
2021-02-21 19:00 | 44248.7917 | 0 | 22.312 | 37.78
2021-02-21 19:30 | 44248.8125 | 0 | 21.7399 | 37.78
2021-02-21 20:00 | 44248.8333 | 0 | 21.5961 | 37.78
2021-02-21 20:30 | 44248.8542 | 0 | 20.6924 | 37.78
2021-02-21 21:00 | 44248.875 | 0 | 18.0992 | 37.78
2021-02-21 21:30 | 44248.8958 | 0 | 17.6999 | 37.78
2021-02-21 22:00 | 44248.9167 | 0 | 16.3146 | 37.78
2021-02-21 22:30 | 44248.9375 | 0 | 15.2182 | 37.78
2021-02-21 23:00 | 44248.9583 | 0 | 14.0491 | 37.78
2021-02-21 23:30 | 44248.9792 | 0 | 13.4837 | 37.78
2021-02-22 | 44249 | 0 | 12.8483 | 37.78
2021-02-22 00:30 | 44249.0208 | 0 | 12.1842 | 37.78
2021-02-22 01:00 | 44249.0417 | 0 | 11.7356 | 37.78
2021-02-22 01:30 | 44249.0625 | 0 | 11.3926 | 37.78
2021-02-22 02:00 | 44249.0833 | 0 | 11.2386 | 37.78
2021-02-22 02:30 | 44249.1042 | 0 | 10.9189 | 37.78
2021-02-22 03:00 | 44249.125 | 0 | 10.8593 | 37.78
2021-02-22 03:30 | 44249.1458 | 0 | 10.9037 | 37.78
2021-02-22 04:00 | 44249.1667 | 0 | 11.2996 | 37.78
2021-02-22 04:30 | 44249.1875 | 0 | 11.5195 | 37.78
2021-02-22 05:00 | 44249.2083 | 0 | 11.875 | 37.78
2021-02-22 05:30 | 44249.2292 | 0 | 12.3671 | 37.78
2021-02-22 06:00 | 44249.25 | 0 | 13.1839 | 37.78
2021-02-22 06:30 | 44249.2708 | 0 | 13.9925 | 37.78
2021-02-22 07:00 | 44249.2917 | 0 | 15.0212 | 37.78
2021-02-22 07:30 | 44249.3125 | 0 | 15.4659 | 37.78
2021-02-22 08:00 | 44249.3333 | 0 | 15.9314 | 37.78
2021-02-22 08:30 | 44249.3542 | 0 | 16.423 | 37.78
2021-02-22 09:00 | 44249.375 | 0 | 17.1173 | 37.78
2021-02-22 09:30 | 44249.3958 | 0 | 16.5275 | 37.78
2021-02-22 10:00 | 44249.4167 | 0 | 16.2282 | 37.78
2021-02-22 10:30 | 44249.4375 | 0 | 16.4121 | 37.78
2021-02-22 11:00 | 44249.4583 | 0 | 16.7863 | 37.78
2021-02-22 11:30 | 44249.4792 | 0 | 17.1222 | 37.78
2021-02-22 12:00 | 44249.5 | 0 | 17.3757 | 37.78
2021-02-22 12:30 | 44249.5208 | 0 | 17.5672 | 37.78
2021-02-22 13:00 | 44249.5417 | 0 | 18.0236 | 37.78
2021-02-22 13:30 | 44249.5625 | 0 | 18.4812 | 37.78
2021-02-22 14:00 | 44249.5833 | 0 | 18.8979 | 37.78
2021-02-22 14:30 | 44249.6042 | 0 | 19.7506 | 37.78
2021-02-22 15:00 | 44249.625 | 0 | 20.0777 | 37.78
2021-02-22 15:30 | 44249.6458 | 0 | 20.3581 | 37.78
2021-02-22 16:00 | 44249.6667 | 0 | 20.8224 | 37.78
2021-02-22 16:30 | 44249.6875 | 0 | 21.5226 | 37.78
2021-02-22 17:00 | 44249.7083 | 0 | 21.54 | 37.78
2021-02-22 17:30 | 44249.7292 | 0 | 21.1332 | 37.78
2021-02-22 18:00 | 44249.75 | 0 | 21.0326 | 37.78
2021-02-22 18:30 | 44249.7708 | 0 | 20.5941 | 37.78
2021-02-22 19:00 | 44249.7917 | 0 | 19.0908 | 37.78
2021-02-22 19:30 | 44249.8125 | 0 | 18.1204 | 37.78
2021-02-22 20:00 | 44249.8333 | 0 | 17.3498 | 37.78
2021-02-22 20:30 | 44249.8542 | 0 | 16.277 | 37.78
2021-02-22 21:00 | 44249.875 | 0 | 15.3307 | 37.78
2021-02-22 21:30 | 44249.8958 | 0 | 14.6511 | 37.78
2021-02-22 22:00 | 44249.9167 | 0 | 13.8021 | 37.78
2021-02-22 22:30 | 44249.9375 | 0 | 12.816 | 37.78
2021-02-22 23:00 | 44249.9583 | 0 | 12.1305 | 37.78
2021-02-22 23:30 | 44249.9792 | 0 | 11.5914 | 37.78
2021-02-23 | 44250 | 0 | 11.119 | 37.78
2021-02-23 00:30 | 44250.0208 | 0 | 10.6227 | 37.78
2021-02-23 01:00 | 44250.0417 | 0 | 10.2159 | 37.78
2021-02-23 01:30 | 44250.0625 | 0 | 9.9187 | 37.78
2021-02-23 02:00 | 44250.0833 | 0 | 9.8386 | 37.78
2021-02-23 02:30 | 44250.1042 | 0 | 9.6428 | 37.78
2021-02-23 03:00 | 44250.125 | 0 | 9.3659 | 37.78
2021-02-23 03:30 | 44250.1458 | 0 | 9.5006 | 37.78
2021-02-23 04:00 | 44250.1667 | 0 | 9.8215 | 37.78
2021-02-23 04:30 | 44250.1875 | 0 | 10.2019 | 37.78
2021-02-23 05:00 | 44250.2083 | 0 | 10.7172 | 37.78
2021-02-23 05:30 | 44250.2292 | 0 | 11.2014 | 37.78
2021-02-23 06:00 | 44250.25 | 0 | 11.9503 | 37.78
2021-02-23 06:30 | 44250.2708 | 0 | 12.5914 | 37.78
2021-02-23 07:00 | 44250.2917 | 0 | 12.9424 | 37.78
2021-02-23 07:30 | 44250.3125 | 0 | 13.4821 | 37.78
2021-02-23 08:00 | 44250.3333 | 0 | 14.412 | 37.78
2021-02-23 08:30 | 44250.3542 | 0 | 13.9342 | 37.78
2021-02-23 09:00 | 44250.375 | 0 | 14.5902 | 37.78
2021-02-23 09:30 | 44250.3958 | 0 | 13.5378 | 37.78
2021-02-23 10:00 | 44250.4167 | 0 | 14.9203 | 37.78
2021-02-23 10:30 | 44250.4375 | 0 | 14.3416 | 37.78
2021-02-23 11:00 | 44250.4583 | 0 | 14.4235 | 37.78
2021-02-23 11:30 | 44250.4792 | 0 | 14.9185 | 37.78
2021-02-23 12:00 | 44250.5 | 0 | 14.3419 | 37.78
2021-02-23 12:30 | 44250.5208 | 0 | 14.4148 | 37.78
2021-02-23 13:00 | 44250.5417 | 0 | 15.0928 | 37.78
2021-02-23 13:30 | 44250.5625 | 0 | 15.2417 | 37.78
2021-02-23 14:00 | 44250.5833 | 0 | 15.7556 | 37.78
2021-02-23 14:30 | 44250.6042 | 0 | 16.3196 | 37.78
2021-02-23 15:00 | 44250.625 | 0 | 17.0837 | 37.78
2021-02-23 15:30 | 44250.6458 | 0 | 17.4658 | 37.78
2021-02-23 16:00 | 44250.6667 | 0 | 18.814 | 37.78
2021-02-23 16:30 | 44250.6875 | 0 | 18.9985 | 37.78
2021-02-23 17:00 | 44250.7083 | 0 | 18.9594 | 37.78
2021-02-23 17:30 | 44250.7292 | 0 | 18.7098 | 37.78
2021-02-23 18:00 | 44250.75 | 0 | 18.3658 | 37.78
2021-02-23 18:30 | 44250.7708 | 0 | 18.9532 | 37.78
2021-02-23 19:00 | 44250.7917 | 0 | 18.8093 | 37.78
2021-02-23 19:30 | 44250.8125 | 0 | 18.6256 | 37.78
2021-02-23 20:00 | 44250.8333 | 0 | 17.8782 | 37.78
2021-02-23 20:30 | 44250.8542 | 0 | 17.4435 | 37.78
2021-02-23 21:00 | 44250.875 | 0 | 16.66 | 37.78
2021-02-23 21:30 | 44250.8958 | 0 | 16.0916 | 37.78
2021-02-23 22:00 | 44250.9167 | 0 | 15.0885 | 37.78
2021-02-23 22:30 | 44250.9375 | 0 | 14.057 | 37.78
2021-02-23 23:00 | 44250.9583 | 0 | 13.2802 | 37.78
2021-02-23 23:30 | 44250.9792 | 0 | 12.8333 | 37.78
2021-02-24 | 44251 | 0 | 11.8251 | 37.78
2021-02-24 00:30 | 44251.0208 | 0 | 11.3597 | 37.78
2021-02-24 01:00 | 44251.0417 | 0 | 10.8242 | 37.78
2021-02-24 01:30 | 44251.0625 | 0 | 10.5151 | 37.78
2021-02-24 02:00 | 44251.0833 | 0 | 10.3058 | 37.78
2021-02-24 02:30 | 44251.1042 | 0 | 10.1666 | 37.78
2021-02-24 03:00 | 44251.125 | 0 | 10.1153 | 37.78
2021-02-24 03:30 | 44251.1458 | 0 | 10.1946 | 37.78
2021-02-24 04:00 | 44251.1667 | 0 | 10.2791 | 37.78
2021-02-24 04:30 | 44251.1875 | 0 | 10.7031 | 37.78
2021-02-24 05:00 | 44251.2083 | 0 | 11.2937 | 37.78
2021-02-24 05:30 | 44251.2292 | 0 | 11.6537 | 37.78
2021-02-24 06:00 | 44251.25 | 0 | 12.764 | 37.78
2021-02-24 06:30 | 44251.2708 | 0 | 13.4311 | 37.78
2021-02-24 07:00 | 44251.2917 | 0 | 14.1622 | 37.78
2021-02-24 07:30 | 44251.3125 | 0 | 14.4584 | 37.78
2021-02-24 08:00 | 44251.3333 | 0 | 15.5209 | 37.78
2021-02-24 08:30 | 44251.3542 | 0 | 15.0044 | 37.78
2021-02-24 09:00 | 44251.375 | 0 | 14.6292 | 37.78
2021-02-24 09:30 | 44251.3958 | 0 | 14.1047 | 37.78
2021-02-24 10:00 | 44251.4167 | 0 | 14.3941 | 37.78
2021-02-24 10:30 | 44251.4375 | 0 | 14.3258 | 37.78
2021-02-24 11:00 | 44251.4583 | 0 | 16.153 | 37.78
2021-02-24 11:30 | 44251.4792 | 0 | 15.8381 | 37.78
2021-02-24 12:00 | 44251.5 | 0 | 16.2267 | 37.78
2021-02-24 12:30 | 44251.5208 | 0 | 15.7545 | 37.78
2021-02-24 13:00 | 44251.5417 | 0 | 15.0061 | 37.78
2021-02-24 13:30 | 44251.5625 | 0 | 14.9025 | 37.78
2021-02-24 14:00 | 44251.5833 | 0 | 15.641 | 37.78
2021-02-24 14:30 | 44251.6042 | 0 | 15.7779 | 37.78
2021-02-24 15:00 | 44251.625 | 0 | 15.6744 | 37.78
2021-02-24 15:30 | 44251.6458 | 0 | 16.4758 | 37.78
2021-02-24 16:00 | 44251.6667 | 0 | 16.9594 | 37.78
2021-02-24 16:30 | 44251.6875 | 0 | 17.8053 | 37.78
2021-02-24 17:00 | 44251.7083 | 0 | 17.966 | 37.78
2021-02-24 17:30 | 44251.7292 | 0 | 18.1328 | 37.78
2021-02-24 18:00 | 44251.75 | 0 | 17.976 | 37.78
2021-02-24 18:30 | 44251.7708 | 0 | 18.3555 | 37.78
2021-02-24 19:00 | 44251.7917 | 0 | 18.3228 | 37.78
2021-02-24 19:30 | 44251.8125 | 0 | 18.0635 | 37.78
2021-02-24 20:00 | 44251.8333 | 0 | 17.5927 | 37.78
2021-02-24 20:30 | 44251.8542 | 0 | 17.0131 | 37.78
2021-02-24 21:00 | 44251.875 | 0 | 16.3491 | 37.78
2021-02-24 21:30 | 44251.8958 | 0 | 15.4988 | 37.78
2021-02-24 22:00 | 44251.9167 | 0 | 14.391 | 37.78
2021-02-24 22:30 | 44251.9375 | 0 | 13.0947 | 37.78
2021-02-24 23:00 | 44251.9583 | 0 | 12.3928 | 37.78
2021-02-24 23:30 | 44251.9792 | 0 | 11.7802 | 37.78
2021-02-25 | 44252 | 0 | 10.1615 | 37.78
2021-02-25 00:30 | 44252.0208 | 0 | 9.9359 | 37.78
2021-02-25 01:00 | 44252.0417 | 0 | 10.2056 | 37.78
2021-02-25 01:30 | 44252.0625 | 0 | 10.1474 | 37.78
2021-02-25 02:00 | 44252.0833 | 0 | 10.0172 | 37.78
2021-02-25 02:30 | 44252.1042 | 0 | 9.9476 | 37.78
2021-02-25 03:00 | 44252.125 | 0 | 9.9639 | 37.78
2021-02-25 03:30 | 44252.1458 | 0 | 9.9718 | 37.78
2021-02-25 04:00 | 44252.1667 | 0 | 10.2896 | 37.78
2021-02-25 04:30 | 44252.1875 | 0 | 10.7408 | 37.78
2021-02-25 05:00 | 44252.2083 | 0 | 11.0329 | 37.78
2021-02-25 05:30 | 44252.2292 | 0 | 11.5151 | 37.78
2021-02-25 06:00 | 44252.25 | 0 | 12.4554 | 37.78
2021-02-25 06:30 | 44252.2708 | 0 | 13.341 | 37.78
2021-02-25 07:00 | 44252.2917 | 0 | 14.2829 | 37.78
2021-02-25 07:30 | 44252.3125 | 0 | 14.5991 | 37.78
2021-02-25 08:00 | 44252.3333 | 0 | 15.1088 | 37.78
2021-02-25 08:30 | 44252.3542 | 0 | 15.7907 | 37.78
2021-02-25 09:00 | 44252.375 | 0 | 15.696 | 37.78
2021-02-25 09:30 | 44252.3958 | 0 | 16.8369 | 37.78
2021-02-25 10:00 | 44252.4167 | 0 | 16.3168 | 37.78
2021-02-25 10:30 | 44252.4375 | 0 | 16.8847 | 37.78
2021-02-25 11:00 | 44252.4583 | 0 | 17.2513 | 37.78
2021-02-25 11:30 | 44252.4792 | 0 | 17.544 | 37.78
2021-02-25 12:00 | 44252.5 | 0 | 16.1936 | 37.78
2021-02-25 12:30 | 44252.5208 | 0 | 16.7354 | 37.78
2021-02-25 13:00 | 44252.5417 | 0 | 17.3358 | 37.78
2021-02-25 13:30 | 44252.5625 | 0 | 17.5299 | 37.78
2021-02-25 14:00 | 44252.5833 | 0 | 18.0313 | 37.78
2021-02-25 14:30 | 44252.6042 | 0 | 18.492 | 37.78
2021-02-25 15:00 | 44252.625 | 0 | 18.6317 | 37.78
2021-02-25 15:30 | 44252.6458 | 0 | 19.1731 | 37.78
2021-02-25 16:00 | 44252.6667 | 0 | 19.8685 | 37.78
2021-02-25 16:30 | 44252.6875 | 0 | 20.2396 | 37.78
2021-02-25 17:00 | 44252.7083 | 0 | 20.0269 | 37.78
2021-02-25 17:30 | 44252.7292 | 0 | 19.7574 | 37.78
2021-02-25 18:00 | 44252.75 | 0 | 19.2358 | 37.78
2021-02-25 18:30 | 44252.7708 | 0 | 19.2911 | 37.78
2021-02-25 19:00 | 44252.7917 | 0 | 19.0436 | 37.78
2021-02-25 19:30 | 44252.8125 | 0 | 18.6632 | 37.78
2021-02-25 20:00 | 44252.8333 | 0 | 17.9983 | 37.78
2021-02-25 20:30 | 44252.8542 | 0 | 17.4337 | 37.78
2021-02-25 21:00 | 44252.875 | 0 | 16.8253 | 37.78
2021-02-25 21:30 | 44252.8958 | 0 | 16.1819 | 37.78
2021-02-25 22:00 | 44252.9167 | 0 | 15.4662 | 37.78
2021-02-25 22:30 | 44252.9375 | 0 | 14.1943 | 37.78
2021-02-25 23:00 | 44252.9583 | 0 | 13.6303 | 37.78
2021-02-25 23:30 | 44252.9792 | 0 | 12.9087 | 37.78
2021-02-26 | 44253 | 0 | 11.9818 | 37.78
2021-02-26 00:30 | 44253.0208 | 0 | 11.3479 | 37.78
2021-02-26 01:00 | 44253.0417 | 0 | 11.0419 | 37.78
2021-02-26 01:30 | 44253.0625 | 0 | 10.7646 | 37.78
2021-02-26 02:00 | 44253.0833 | 0 | 10.5261 | 37.78
2021-02-26 02:30 | 44253.1042 | 0 | 10.4762 | 37.78
2021-02-26 03:00 | 44253.125 | 0 | 10.3155 | 37.78
2021-02-26 03:30 | 44253.1458 | 0 | 10.2472 | 37.78
2021-02-26 04:00 | 44253.1667 | 0 | 10.3802 | 37.78
2021-02-26 04:30 | 44253.1875 | 0 | 10.224 | 37.78
2021-02-26 05:00 | 44253.2083 | 0 | 10.4228 | 37.78
2021-02-26 05:30 | 44253.2292 | 0 | 10.3856 | 37.78
2021-02-26 06:00 | 44253.25 | 0 | 10.4228 | 37.78
2021-02-26 06:30 | 44253.2708 | 0 | 10.515 | 37.78
2021-02-26 07:00 | 44253.2917 | 0 | 9.9163 | 37.78
2021-02-26 07:30 | 44253.3125 | 0 | 10.5455 | 37.78
2021-02-26 08:00 | 44253.3333 | 0 | 11.6745 | 37.78
2021-02-26 08:30 | 44253.3542 | 0 | 11.4347 | 37.78
2021-02-26 09:00 | 44253.375 | 0 | 12.2967 | 37.78
2021-02-26 09:30 | 44253.3958 | 0 | 12.4622 | 37.78
2021-02-26 10:00 | 44253.4167 | 0 | 11.7647 | 37.78
2021-02-26 10:30 | 44253.4375 | 0 | 11.9002 | 37.78
2021-02-26 11:00 | 44253.4583 | 0 | 13.2819 | 37.78
2021-02-26 11:30 | 44253.4792 | 0 | 13.1559 | 37.78
2021-02-26 12:00 | 44253.5 | 0 | 12.3095 | 37.78
2021-02-26 12:30 | 44253.5208 | 0 | 12.958 | 37.78
2021-02-26 13:00 | 44253.5417 | 0 | 14.7376 | 37.78
2021-02-26 13:30 | 44253.5625 | 0 | 15.6227 | 37.78
2021-02-26 14:00 | 44253.5833 | 0 | 16.922 | 37.78
2021-02-26 14:30 | 44253.6042 | 0 | 16.7038 | 37.78
2021-02-26 15:00 | 44253.625 | 0 | 16.7739 | 37.78
2021-02-26 15:30 | 44253.6458 | 0 | 17.1062 | 37.78
2021-02-26 16:00 | 44253.6667 | 0 | 16.5303 | 37.78
2021-02-26 16:30 | 44253.6875 | 0 | 15.854 | 37.78
2021-02-26 17:00 | 44253.7083 | 0 | 16.3551 | 37.78
2021-02-26 17:30 | 44253.7292 | 0 | 16.3622 | 37.78
2021-02-26 18:00 | 44253.75 | 0 | 16.487 | 37.78
2021-02-26 18:30 | 44253.7708 | 0 | 16.8717 | 37.78
2021-02-26 19:00 | 44253.7917 | 0 | 16.6925 | 37.78
2021-02-26 19:30 | 44253.8125 | 0 | 16.6659 | 37.78
2021-02-26 20:00 | 44253.8333 | 0 | 15.9757 | 37.78
2021-02-26 20:30 | 44253.8542 | 0 | 15.6319 | 37.78
2021-02-26 21:00 | 44253.875 | 0 | 15.1247 | 37.78
2021-02-26 21:30 | 44253.8958 | 0 | 14.7095 | 37.78
2021-02-26 22:00 | 44253.9167 | 0 | 13.8735 | 37.78
2021-02-26 22:30 | 44253.9375 | 0 | 13.0232 | 37.78
2021-02-26 23:00 | 44253.9583 | 0 | 12.4773 | 37.78
2021-02-26 23:30 | 44253.9792 | 0 | 11.9576 | 37.78
2021-02-27 | 44254 | 0 | 11.1906 | 37.78
2021-02-27 00:30 | 44254.0208 | 0 | 10.9534 | 37.78
2021-02-27 01:00 | 44254.0417 | 0 | 10.6179 | 37.78
2021-02-27 01:30 | 44254.0625 | 0 | 10.4905 | 37.78
2021-02-27 02:00 | 44254.0833 | 0 | 10.3693 | 37.78
2021-02-27 02:30 | 44254.1042 | 0 | 10.2135 | 37.78
2021-02-27 03:00 | 44254.125 | 0 | 10.0518 | 37.78
2021-02-27 03:30 | 44254.1458 | 0 | 9.984 | 37.78
2021-02-27 04:00 | 44254.1667 | 0 | 9.9914 | 37.78
2021-02-27 04:30 | 44254.1875 | 0 | 9.903 | 37.78
2021-02-27 05:00 | 44254.2083 | 0 | 9.9126 | 37.78
2021-02-27 05:30 | 44254.2292 | 0 | 9.9105 | 37.78
2021-02-27 06:00 | 44254.25 | 0 | 9.9218 | 37.78
2021-02-27 06:30 | 44254.2708 | 0 | 10.0472 | 37.78
2021-02-27 07:00 | 44254.2917 | 0 | 10.2686 | 37.78
2021-02-27 07:30 | 44254.3125 | 0 | 10.5151 | 37.78
2021-02-27 08:00 | 44254.3333 | 0 | 10.6223 | 37.78
2021-02-27 08:30 | 44254.3542 | 0 | 11.2715 | 37.78
2021-02-27 09:00 | 44254.375 | 0 | 11.3237 | 37.78
2021-02-27 09:30 | 44254.3958 | 0 | 11.2212 | 37.78
2021-02-27 10:00 | 44254.4167 | 0 | 12.2033 | 37.78
2021-02-27 10:30 | 44254.4375 | 0 | 12.8632 | 37.78
2021-02-27 11:00 | 44254.4583 | 0 | 13.5173 | 37.78
2021-02-27 11:30 | 44254.4792 | 0 | 12.9438 | 37.78
2021-02-27 12:00 | 44254.5 | 0 | 12.8774 | 37.78
2021-02-27 12:30 | 44254.5208 | 0 | 13.9589 | 37.78
2021-02-27 13:00 | 44254.5417 | 0 | 14.4532 | 37.78
2021-02-27 13:30 | 44254.5625 | 0 | 14.3467 | 37.78
2021-02-27 14:00 | 44254.5833 | 0 | 14.6739 | 37.78
2021-02-27 14:30 | 44254.6042 | 0 | 15.4728 | 37.78
2021-02-27 15:00 | 44254.625 | 0 | 16.6008 | 37.78
2021-02-27 15:30 | 44254.6458 | 0 | 17.0267 | 37.78
2021-02-27 16:00 | 44254.6667 | 0 | 17.0744 | 37.78
2021-02-27 16:30 | 44254.6875 | 0 | 17.1638 | 37.78
2021-02-27 17:00 | 44254.7083 | 0 | 17.3358 | 37.78
2021-02-27 17:30 | 44254.7292 | 0 | 17.3854 | 37.78
2021-02-27 18:00 | 44254.75 | 0 | 17.5369 | 37.78
2021-02-27 18:30 | 44254.7708 | 0 | 17.9808 | 37.78
2021-02-27 19:00 | 44254.7917 | 0 | 17.8809 | 37.78
2021-02-27 19:30 | 44254.8125 | 0 | 17.397 | 37.78
2021-02-27 20:00 | 44254.8333 | 0 | 16.8885 | 37.78
2021-02-27 20:30 | 44254.8542 | 0 | 16.0945 | 37.78
2021-02-27 21:00 | 44254.875 | 0 | 15.2174 | 37.78
2021-02-27 21:30 | 44254.8958 | 0 | 14.4547 | 37.78
2021-02-27 22:00 | 44254.9167 | 0 | 13.5632 | 37.78
2021-02-27 22:30 | 44254.9375 | 0 | 12.3761 | 37.78
2021-02-27 23:00 | 44254.9583 | 0 | 11.8033 | 37.78
2021-02-27 23:30 | 44254.9792 | 0 | 11.2819 | 37.78
2021-02-28 | 44255 | 0 | 10.8741 | 37.78
2021-02-28 00:30 | 44255.0208 | 0 | 10.5279 | 37.78
2021-02-28 01:00 | 44255.0417 | 0 | 10.364 | 37.78
2021-02-28 01:30 | 44255.0625 | 0 | 10.1983 | 37.78
2021-02-28 02:00 | 44255.0833 | 0 | 10.1758 | 37.78
2021-02-28 02:30 | 44255.1042 | 0 | 10.1307 | 37.78
2021-02-28 03:00 | 44255.125 | 0 | 9.9144 | 37.78
2021-02-28 03:30 | 44255.1458 | 0 | 10.0495 | 37.78
2021-02-28 04:00 | 44255.1667 | 0 | 10.4575 | 37.78
2021-02-28 04:30 | 44255.1875 | 0 | 10.8399 | 37.78
2021-02-28 05:00 | 44255.2083 | 0 | 11.41 | 37.78
2021-02-28 05:30 | 44255.2292 | 0 | 12.0836 | 37.78
2021-02-28 06:00 | 44255.25 | 0 | 12.9571 | 37.78
2021-02-28 06:30 | 44255.2708 | 0 | 13.8433 | 37.78
2021-02-28 07:00 | 44255.2917 | 0 | 14.9197 | 37.78
2021-02-28 07:30 | 44255.3125 | 0 | 15.7357 | 37.78
2021-02-28 08:00 | 44255.3333 | 0 | 15.6005 | 37.78
2021-02-28 08:30 | 44255.3542 | 0 | 16.1256 | 37.78
2021-02-28 09:00 | 44255.375 | 0 | 16.3253 | 37.78
2021-02-28 09:30 | 44255.3958 | 0 | 16.429 | 37.78
2021-02-28 10:00 | 44255.4167 | 0 | 16.6594 | 37.78
2021-02-28 10:30 | 44255.4375 | 0 | 16.6863 | 37.78
2021-02-28 11:00 | 44255.4583 | 0 | 17.1253 | 37.78
2021-02-28 11:30 | 44255.4792 | 0 | 17.3063 | 37.78
2021-02-28 12:00 | 44255.5 | 0 | 16.8989 | 37.78
2021-02-28 12:30 | 44255.5208 | 0 | 16.9884 | 37.78
2021-02-28 13:00 | 44255.5417 | 0 | 16.5918 | 37.78
2021-02-28 13:30 | 44255.5625 | 0 | 17.0027 | 37.78
2021-02-28 14:00 | 44255.5833 | 0 | 16.5122 | 37.78
2021-02-28 14:30 | 44255.6042 | 0 | 17.0912 | 37.78
2021-02-28 15:00 | 44255.625 | 0 | 17.816 | 37.78
2021-02-28 15:30 | 44255.6458 | 0 | 18.471 | 37.78
2021-02-28 16:00 | 44255.6667 | 0 | 18.5851 | 37.78
2021-02-28 16:30 | 44255.6875 | 0 | 18.7369 | 37.78
2021-02-28 17:00 | 44255.7083 | 0 | 18.5023 | 37.78
2021-02-28 17:30 | 44255.7292 | 0 | 18.5489 | 37.78
2021-02-28 18:00 | 44255.75 | 0 | 18.7506 | 37.78
2021-02-28 18:30 | 44255.7708 | 0 | 19.5725 | 37.78
2021-02-28 19:00 | 44255.7917 | 0 | 19.2388 | 37.78
2021-02-28 19:30 | 44255.8125 | 0 | 19.0378 | 37.78
2021-02-28 20:00 | 44255.8333 | 0 | 18.5605 | 37.78
2021-02-28 20:30 | 44255.8542 | 0 | 17.7399 | 37.78
2021-02-28 21:00 | 44255.875 | 0 | 16.7336 | 37.78
2021-02-28 21:30 | 44255.8958 | 0 | 16.047 | 37.78
2021-02-28 22:00 | 44255.9167 | 0 | 15.0733 | 37.78
2021-02-28 22:30 | 44255.9375 | 0 | 13.8293 | 37.78
2021-02-28 23:00 | 44255.9583 | 0 | 13.0225 | 37.78
2021-02-28 23:30 | 44255.9792 | 0 | 12.6608 | 37.78
2021-03-01 | 44256 | 0 | 11.9512 | 37.78
2021-03-01 00:30 | 44256.0208 | 0 | 11.3448 | 37.78
2021-03-01 01:00 | 44256.0417 | 0 | 11.0584 | 37.78
2021-03-01 01:30 | 44256.0625 | 0 | 10.7036 | 37.78
2021-03-01 02:00 | 44256.0833 | 0 | 10.6 | 37.78
2021-03-01 02:30 | 44256.1042 | 0 | 10.3891 | 37.78
2021-03-01 03:00 | 44256.125 | 0 | 10.1692 | 37.78
2021-03-01 03:30 | 44256.1458 | 0 | 10.2362 | 37.78
2021-03-01 04:00 | 44256.1667 | 0 | 10.4972 | 37.78
2021-03-01 04:30 | 44256.1875 | 0 | 10.7487 | 37.78
2021-03-01 05:00 | 44256.2083 | 0 | 11.3083 | 37.78
2021-03-01 05:30 | 44256.2292 | 0 | 11.9071 | 37.78
2021-03-01 06:00 | 44256.25 | 0 | 12.3568 | 37.78
2021-03-01 06:30 | 44256.2708 | 0 | 13.0156 | 37.78
2021-03-01 07:00 | 44256.2917 | 0 | 13.7277 | 37.78
2021-03-01 07:30 | 44256.3125 | 0 | 13.9697 | 37.78
2021-03-01 08:00 | 44256.3333 | 0 | 14.3145 | 37.78
2021-03-01 08:30 | 44256.3542 | 0 | 14.6507 | 37.78
2021-03-01 09:00 | 44256.375 | 0 | 14.8232 | 37.78
2021-03-01 09:30 | 44256.3958 | 0 | 15.1374 | 37.78
2021-03-01 10:00 | 44256.4167 | 0 | 15.5864 | 37.78
2021-03-01 10:30 | 44256.4375 | 0 | 15.89 | 37.78
2021-03-01 11:00 | 44256.4583 | 0 | 16.412 | 37.78
2021-03-01 11:30 | 44256.4792 | 0 | 17.3516 | 37.78
2021-03-01 12:00 | 44256.5 | 0 | 17.3504 | 37.78
2021-03-01 12:30 | 44256.5208 | 0 | 17.8192 | 37.78
2021-03-01 13:00 | 44256.5417 | 0 | 18.2809 | 37.78
2021-03-01 13:30 | 44256.5625 | 0 | 19.0464 | 37.78
2021-03-01 14:00 | 44256.5833 | 0 | 19.6622 | 37.78
2021-03-01 14:30 | 44256.6042 | 0 | 19.9331 | 37.78
2021-03-01 15:00 | 44256.625 | 0 | 20.1214 | 37.78
2021-03-01 15:30 | 44256.6458 | 0 | 21.0004 | 37.78
2021-03-01 16:00 | 44256.6667 | 0 | 21.8136 | 37.78
2021-03-01 16:30 | 44256.6875 | 0 | 23.0719 | 37.78
2021-03-01 17:00 | 44256.7083 | 0 | 22.7645 | 37.78
2021-03-01 17:30 | 44256.7292 | 0 | 21.3661 | 37.78
2021-03-01 18:00 | 44256.75 | 0 | 20.7635 | 37.78
2021-03-01 18:30 | 44256.7708 | 0 | 20.5806 | 37.78
2021-03-01 19:00 | 44256.7917 | 0 | 20.3261 | 37.78
2021-03-01 19:30 | 44256.8125 | 0 | 20.0808 | 37.78
2021-03-01 20:00 | 44256.8333 | 0 | 19.3751 | 37.78
2021-03-01 20:30 | 44256.8542 | 0 | 18.4985 | 37.78
2021-03-01 21:00 | 44256.875 | 0 | 17.2337 | 37.78
2021-03-01 21:30 | 44256.8958 | 0 | 16.3116 | 37.78
2021-03-01 22:00 | 44256.9167 | 0 | 15.4389 | 37.78
2021-03-01 22:30 | 44256.9375 | 0 | 13.9517 | 37.78
2021-03-01 23:00 | 44256.9583 | 0 | 13.3406 | 37.78
2021-03-01 23:30 | 44256.9792 | 0 | 12.7798 | 37.78
2021-03-02 | 44257 | 0 | 11.9469 | 37.78
2021-03-02 00:30 | 44257.0208 | 0 | 11.3203 | 37.78
2021-03-02 01:00 | 44257.0417 | 0 | 11.0021 | 37.78
2021-03-02 01:30 | 44257.0625 | 0 | 10.9832 | 37.78
2021-03-02 02:00 | 44257.0833 | 0 | 10.691 | 37.78
2021-03-02 02:30 | 44257.1042 | 0 | 10.5221 | 37.78
2021-03-02 03:00 | 44257.125 | 0 | 10.2884 | 37.78
2021-03-02 03:30 | 44257.1458 | 0 | 10.3734 | 37.78
2021-03-02 04:00 | 44257.1667 | 0 | 10.6993 | 37.78
2021-03-02 04:30 | 44257.1875 | 0 | 11.1367 | 37.78
2021-03-02 05:00 | 44257.2083 | 0 | 11.5978 | 37.78
2021-03-02 05:30 | 44257.2292 | 0 | 12.043 | 37.78
2021-03-02 06:00 | 44257.25 | 0 | 12.9283 | 37.78
2021-03-02 06:30 | 44257.2708 | 0 | 13.482 | 37.78
2021-03-02 07:00 | 44257.2917 | 0 | 14.1903 | 37.78
2021-03-02 07:30 | 44257.3125 | 0 | 14.0393 | 37.78
2021-03-02 08:00 | 44257.3333 | 0 | 14.7373 | 37.78
2021-03-02 08:30 | 44257.3542 | 0 | 14.7936 | 37.78
2021-03-02 09:00 | 44257.375 | 0 | 15.9809 | 37.78
2021-03-02 09:30 | 44257.3958 | 0 | 16.0712 | 37.78
2021-03-02 10:00 | 44257.4167 | 0 | 15.1025 | 37.78
2021-03-02 10:30 | 44257.4375 | 0 | 14.7646 | 37.78
2021-03-02 11:00 | 44257.4583 | 0 | 14.9578 | 37.78
2021-03-02 11:30 | 44257.4792 | 0 | 15.2203 | 37.78
2021-03-02 12:00 | 44257.5 | 0 | 14.3722 | 37.78
2021-03-02 12:30 | 44257.5208 | 0 | 13.1652 | 37.78
2021-03-02 13:00 | 44257.5417 | 0 | 12.9024 | 37.78
2021-03-02 13:30 | 44257.5625 | 0 | 14.9612 | 37.78
2021-03-02 14:00 | 44257.5833 | 0 | 14.292 | 37.78
2021-03-02 14:30 | 44257.6042 | 0 | 14.1165 | 37.78
2021-03-02 15:00 | 44257.625 | 0 | 15.2356 | 37.78
2021-03-02 15:30 | 44257.6458 | 0 | 14.6729 | 37.78
2021-03-02 16:00 | 44257.6667 | 0 | 14.8097 | 37.78
2021-03-02 16:30 | 44257.6875 | 0 | 15.0412 | 37.78
2021-03-02 17:00 | 44257.7083 | 0 | 14.9804 | 37.78
2021-03-02 17:30 | 44257.7292 | 0 | 15.1473 | 37.78
2021-03-02 18:00 | 44257.75 | 0 | 15.2833 | 37.78
2021-03-02 18:30 | 44257.7708 | 0 | 15.8041 | 37.78
2021-03-02 19:00 | 44257.7917 | 0 | 15.5203 | 37.78
2021-03-02 19:30 | 44257.8125 | 0 | 15.6026 | 37.78
2021-03-02 20:00 | 44257.8333 | 0 | 15.2417 | 37.78
2021-03-02 20:30 | 44257.8542 | 0 | 14.7802 | 37.78
2021-03-02 21:00 | 44257.875 | 0 | 14.3353 | 37.78
2021-03-02 21:30 | 44257.8958 | 0 | 13.69 | 37.78
2021-03-02 22:00 | 44257.9167 | 0 | 13.197 | 37.78
2021-03-02 22:30 | 44257.9375 | 0 | 12.2477 | 37.78
2021-03-02 23:00 | 44257.9583 | 0 | 11.42 | 37.78
2021-03-02 23:30 | 44257.9792 | 0 | 10.9823 | 37.78
2021-03-03 | 44258 | 0 | 10.1213 | 37.78
2021-03-03 00:30 | 44258.0208 | 0 | 9.6155 | 37.78
2021-03-03 01:00 | 44258.0417 | 0 | 9.3818 | 37.78
2021-03-03 01:30 | 44258.0625 | 0 | 9.1144 | 37.78
2021-03-03 02:00 | 44258.0833 | 0 | 9.1524 | 37.78
2021-03-03 02:30 | 44258.1042 | 0 | 8.9416 | 37.78
2021-03-03 03:00 | 44258.125 | 0 | 8.8108 | 37.78
2021-03-03 03:30 | 44258.1458 | 0 | 8.7435 | 37.78
2021-03-03 04:00 | 44258.1667 | 0 | 9.0881 | 37.78
2021-03-03 04:30 | 44258.1875 | 0 | 9.5652 | 37.78
2021-03-03 05:00 | 44258.2083 | 0 | 10.2571 | 37.78
2021-03-03 05:30 | 44258.2292 | 0 | 10.8339 | 37.78
2021-03-03 06:00 | 44258.25 | 0 | 11.8937 | 37.78
2021-03-03 06:30 | 44258.2708 | 0 | 12.4212 | 37.78
2021-03-03 07:00 | 44258.2917 | 0 | 13.0383 | 37.78
2021-03-03 07:30 | 44258.3125 | 0 | 13.1155 | 37.78
2021-03-03 08:00 | 44258.3333 | 0 | 13.6167 | 37.78
2021-03-03 08:30 | 44258.3542 | 0 | 13.8515 | 37.78
2021-03-03 09:00 | 44258.375 | 0 | 12.6357 | 37.78
2021-03-03 09:30 | 44258.3958 | 0 | 13.5022 | 37.78
2021-03-03 10:00 | 44258.4167 | 0 | 13.3865 | 37.78
2021-03-03 10:30 | 44258.4375 | 0 | 12.3449 | 37.78
2021-03-03 11:00 | 44258.4583 | 0 | 11.833 | 37.78
2021-03-03 11:30 | 44258.4792 | 0 | 12.9278 | 37.78
2021-03-03 12:00 | 44258.5 | 0 | 12.419 | 37.78
2021-03-03 12:30 | 44258.5208 | 0 | 12.5145 | 37.78
2021-03-03 13:00 | 44258.5417 | 0 | 12.6585 | 37.78
2021-03-03 13:30 | 44258.5625 | 0 | 13.0454 | 37.78
2021-03-03 14:00 | 44258.5833 | 0 | 12.8004 | 37.78
2021-03-03 14:30 | 44258.6042 | 0 | 13.3818 | 37.78
2021-03-03 15:00 | 44258.625 | 0 | 13.3062 | 37.78
2021-03-03 15:30 | 44258.6458 | 0 | 12.9464 | 37.78
2021-03-03 16:00 | 44258.6667 | 0 | 13.1349 | 37.78
2021-03-03 16:30 | 44258.6875 | 0 | 13.7923 | 37.78
2021-03-03 17:00 | 44258.7083 | 0 | 14.3892 | 37.78
2021-03-03 17:30 | 44258.7292 | 0 | 14.7571 | 37.78
2021-03-03 18:00 | 44258.75 | 0 | 14.5951 | 37.78
2021-03-03 18:30 | 44258.7708 | 0 | 15.0348 | 37.78
2021-03-03 19:00 | 44258.7917 | 0 | 15.032 | 37.78
2021-03-03 19:30 | 44258.8125 | 0 | 14.792 | 37.78
2021-03-03 20:00 | 44258.8333 | 0 | 14.3628 | 37.78
2021-03-03 20:30 | 44258.8542 | 0 | 13.7869 | 37.78
2021-03-03 21:00 | 44258.875 | 0 | 13.0898 | 37.78
2021-03-03 21:30 | 44258.8958 | 0 | 12.606 | 37.78
2021-03-03 22:00 | 44258.9167 | 0 | 11.8762 | 37.78
2021-03-03 22:30 | 44258.9375 | 0 | 11.0248 | 37.78
2021-03-03 23:00 | 44258.9583 | 0 | 10.2655 | 37.78
2021-03-03 23:30 | 44258.9792 | 0 | 9.8393 | 37.78
2021-03-04 | 44259 | 0 | 9.3122 | 37.78
2021-03-04 00:30 | 44259.0208 | 0 | 9.0551 | 37.78
2021-03-04 01:00 | 44259.0417 | 0 | 8.7447 | 37.78
2021-03-04 01:30 | 44259.0625 | 0 | 8.5916 | 37.78
2021-03-04 02:00 | 44259.0833 | 0 | 8.5446 | 37.78
2021-03-04 02:30 | 44259.1042 | 0 | 8.3746 | 37.78
2021-03-04 03:00 | 44259.125 | 0 | 8.2885 | 37.78
2021-03-04 03:30 | 44259.1458 | 0 | 8.395 | 37.78
2021-03-04 04:00 | 44259.1667 | 0 | 8.6889 | 37.78
2021-03-04 04:30 | 44259.1875 | 0 | 9.1897 | 37.78
2021-03-04 05:00 | 44259.2083 | 0 | 9.5812 | 37.78
2021-03-04 05:30 | 44259.2292 | 0 | 10.2127 | 37.78
2021-03-04 06:00 | 44259.25 | 0 | 10.5915 | 37.78
2021-03-04 06:30 | 44259.2708 | 0 | 11.0626 | 37.78
2021-03-04 07:00 | 44259.2917 | 0 | 11.338 | 37.78
2021-03-04 07:30 | 44259.3125 | 0 | 11.3477 | 37.78
2021-03-04 08:00 | 44259.3333 | 0 | 11.401 | 37.78
2021-03-04 08:30 | 44259.3542 | 0 | 11.2083 | 37.78
2021-03-04 09:00 | 44259.375 | 0 | 11.148 | 37.78
2021-03-04 09:30 | 44259.3958 | 0 | 11.095 | 37.78
2021-03-04 10:00 | 44259.4167 | 0 | 10.8523 | 37.78
2021-03-04 10:30 | 44259.4375 | 0 | 11.2732 | 37.78
2021-03-04 11:00 | 44259.4583 | 0 | 11.7293 | 37.78
2021-03-04 11:30 | 44259.4792 | 0 | 12.6346 | 37.78
2021-03-04 12:00 | 44259.5 | 0 | 12.8003 | 37.78
2021-03-04 12:30 | 44259.5208 | 0 | 12.811 | 37.78
2021-03-04 13:00 | 44259.5417 | 0 | 12.6193 | 37.78
2021-03-04 13:30 | 44259.5625 | 0 | 13.6336 | 37.78
2021-03-04 14:00 | 44259.5833 | 0 | 14.4164 | 37.78
2021-03-04 14:30 | 44259.6042 | 0 | 15.5129 | 37.78
2021-03-04 15:00 | 44259.625 | 0 | 14.6784 | 37.78
2021-03-04 15:30 | 44259.6458 | 0 | 15.6689 | 37.78
2021-03-04 16:00 | 44259.6667 | 0 | 16.2488 | 37.78
2021-03-04 16:30 | 44259.6875 | 0 | 16.61 | 37.78
2021-03-04 17:00 | 44259.7083 | 0 | 16.8028 | 37.78
2021-03-04 17:30 | 44259.7292 | 0 | 16.622 | 37.78
2021-03-04 18:00 | 44259.75 | 0 | 16.4596 | 37.78
2021-03-04 18:30 | 44259.7708 | 0 | 16.7184 | 37.78
2021-03-04 19:00 | 44259.7917 | 0 | 16.4998 | 37.78
2021-03-04 19:30 | 44259.8125 | 0 | 16.4114 | 37.78
2021-03-04 20:00 | 44259.8333 | 0 | 15.9838 | 37.78
2021-03-04 20:30 | 44259.8542 | 0 | 15.3165 | 37.78
2021-03-04 21:00 | 44259.875 | 0 | 14.7445 | 37.78
2021-03-04 21:30 | 44259.8958 | 0 | 14.2345 | 37.78
2021-03-04 22:00 | 44259.9167 | 0 | 13.6037 | 37.78
2021-03-04 22:30 | 44259.9375 | 0 | 12.5631 | 37.78
2021-03-04 23:00 | 44259.9583 | 0 | 11.7475 | 37.78
2021-03-04 23:30 | 44259.9792 | 0 | 11.417 | 37.78
2021-03-05 | 44260 | 0 | 10.7061 | 37.78
2021-03-05 00:30 | 44260.0208 | 0 | 10.1974 | 37.78
2021-03-05 01:00 | 44260.0417 | 0 | 9.8622 | 37.78
2021-03-05 01:30 | 44260.0625 | 0 | 9.6719 | 37.78
2021-03-05 02:00 | 44260.0833 | 0 | 9.4944 | 37.78
2021-03-05 02:30 | 44260.1042 | 0 | 9.2987 | 37.78
2021-03-05 03:00 | 44260.125 | 0 | 9.1129 | 37.78
2021-03-05 03:30 | 44260.1458 | 0 | 9.0842 | 37.78
2021-03-05 04:00 | 44260.1667 | 0 | 9.0964 | 37.78
2021-03-05 04:30 | 44260.1875 | 0 | 9.2362 | 37.78
2021-03-05 05:00 | 44260.2083 | 0 | 9.3644 | 37.78
2021-03-05 05:30 | 44260.2292 | 0 | 9.3934 | 37.78
2021-03-05 06:00 | 44260.25 | 0 | 9.5241 | 37.78
2021-03-05 06:30 | 44260.2708 | 0 | 9.4128 | 37.78
2021-03-05 07:00 | 44260.2917 | 0 | 10.1745 | 37.78
2021-03-05 07:30 | 44260.3125 | 0 | 9.5322 | 37.78
2021-03-05 08:00 | 44260.3333 | 0 | 9.7683 | 37.78
2021-03-05 08:30 | 44260.3542 | 0 | 10.0612 | 37.78
2021-03-05 09:00 | 44260.375 | 0 | 10.6499 | 37.78
2021-03-05 09:30 | 44260.3958 | 0 | 10.7793 | 37.78
2021-03-05 10:00 | 44260.4167 | 0 | 10.7955 | 37.78
2021-03-05 10:30 | 44260.4375 | 0 | 11.1843 | 37.78
2021-03-05 11:00 | 44260.4583 | 0 | 10.5249 | 37.78
2021-03-05 11:30 | 44260.4792 | 0 | 9.6021 | 37.78
2021-03-05 12:00 | 44260.5 | 0 | 10.5017 | 37.78
2021-03-05 12:30 | 44260.5208 | 0 | 11.2033 | 37.78
2021-03-05 13:00 | 44260.5417 | 0 | 12.1204 | 37.78
2021-03-05 13:30 | 44260.5625 | 0 | 11.7367 | 37.78
2021-03-05 14:00 | 44260.5833 | 0 | 11.2049 | 37.78
2021-03-05 14:30 | 44260.6042 | 0 | 12.2382 | 37.78
2021-03-05 15:00 | 44260.625 | 0 | 12.5475 | 37.78
2021-03-05 15:30 | 44260.6458 | 0 | 11.2536 | 37.78
2021-03-05 16:00 | 44260.6667 | 0 | 11.6501 | 37.78
2021-03-05 16:30 | 44260.6875 | 0 | 12.4164 | 37.78
2021-03-05 17:00 | 44260.7083 | 0 | 12.4597 | 37.78
2021-03-05 17:30 | 44260.7292 | 0 | 12.4653 | 37.78
2021-03-05 18:00 | 44260.75 | 0 | 12.7441 | 37.78
2021-03-05 18:30 | 44260.7708 | 0 | 13.054 | 37.78
2021-03-05 19:00 | 44260.7917 | 0 | 12.87 | 37.78
2021-03-05 19:30 | 44260.8125 | 0 | 12.6394 | 37.78
2021-03-05 20:00 | 44260.8333 | 0 | 12.4753 | 37.78
2021-03-05 20:30 | 44260.8542 | 0 | 11.9812 | 37.78
2021-03-05 21:00 | 44260.875 | 0 | 11.6062 | 37.78
2021-03-05 21:30 | 44260.8958 | 0 | 11.2929 | 37.78
2021-03-05 22:00 | 44260.9167 | 0 | 10.9317 | 37.78
2021-03-05 22:30 | 44260.9375 | 0 | 10.4178 | 37.78
2021-03-05 23:00 | 44260.9583 | 0 | 10.0832 | 37.78
2021-03-05 23:30 | 44260.9792 | 0 | 9.5879 | 37.78
2021-03-06 | 44261 | 0 | 9.2032 | 37.78
2021-03-06 00:30 | 44261.0208 | 0 | 8.8848 | 37.78
2021-03-06 01:00 | 44261.0417 | 0 | 8.7425 | 37.78
2021-03-06 01:30 | 44261.0625 | 0 | 8.5113 | 37.78
2021-03-06 02:00 | 44261.0833 | 0 | 8.4821 | 37.78
2021-03-06 02:30 | 44261.1042 | 0 | 8.4113 | 37.78
2021-03-06 03:00 | 44261.125 | 0 | 8.2841 | 37.78
2021-03-06 03:30 | 44261.1458 | 0 | 8.1895 | 37.78
2021-03-06 04:00 | 44261.1667 | 0 | 8.2105 | 37.78
2021-03-06 04:30 | 44261.1875 | 0 | 8.1931 | 37.78
2021-03-06 05:00 | 44261.2083 | 0 | 8.2419 | 37.78
2021-03-06 05:30 | 44261.2292 | 0 | 8.1528 | 37.78
2021-03-06 06:00 | 44261.25 | 0 | 8.2193 | 37.78
2021-03-06 06:30 | 44261.2708 | 0 | 8.3849 | 37.78
2021-03-06 07:00 | 44261.2917 | 0 | 8.6634 | 37.78
2021-03-06 07:30 | 44261.3125 | 0 | 9.3032 | 37.78
2021-03-06 08:00 | 44261.3333 | 0 | 9.4416 | 37.78
2021-03-06 08:30 | 44261.3542 | 0 | 8.7402 | 37.78
2021-03-06 09:00 | 44261.375 | 0 | 8.1668 | 37.78
2021-03-06 09:30 | 44261.3958 | 0 | 9.3702 | 37.78
2021-03-06 10:00 | 44261.4167 | 0 | 8.6806 | 37.78
2021-03-06 10:30 | 44261.4375 | 0 | 9.5029 | 37.78
2021-03-06 11:00 | 44261.4583 | 0 | 10.8849 | 37.78
2021-03-06 11:30 | 44261.4792 | 0 | 10.4342 | 37.78
2021-03-06 12:00 | 44261.5 | 0 | 8.7328 | 37.78
2021-03-06 12:30 | 44261.5208 | 0 | 8.9713 | 37.78
2021-03-06 13:00 | 44261.5417 | 0 | 9.13 | 37.78
2021-03-06 13:30 | 44261.5625 | 0 | 9.5556 | 37.78
2021-03-06 14:00 | 44261.5833 | 0 | 10.1019 | 37.78
2021-03-06 14:30 | 44261.6042 | 0 | 11.0617 | 37.78
2021-03-06 15:00 | 44261.625 | 0 | 11.6123 | 37.78
2021-03-06 15:30 | 44261.6458 | 0 | 12.4761 | 37.78
2021-03-06 16:00 | 44261.6667 | 0 | 12.6018 | 37.78
2021-03-06 16:30 | 44261.6875 | 0 | 13.3533 | 37.78
2021-03-06 17:00 | 44261.7083 | 0 | 13.6342 | 37.78
2021-03-06 17:30 | 44261.7292 | 0 | 13.7521 | 37.78
2021-03-06 18:00 | 44261.75 | 0 | 13.7495 | 37.78
2021-03-06 18:30 | 44261.7708 | 0 | 14.0276 | 37.78
2021-03-06 19:00 | 44261.7917 | 0 | 13.9451 | 37.78
2021-03-06 19:30 | 44261.8125 | 0 | 13.7368 | 37.78
2021-03-06 20:00 | 44261.8333 | 0 | 13.3788 | 37.78
2021-03-06 20:30 | 44261.8542 | 0 | 12.744 | 37.78
2021-03-06 21:00 | 44261.875 | 0 | 12.3165 | 37.78
2021-03-06 21:30 | 44261.8958 | 0 | 11.8849 | 37.78
2021-03-06 22:00 | 44261.9167 | 0 | 11.461 | 37.78
2021-03-06 22:30 | 44261.9375 | 0 | 10.5987 | 37.78
2021-03-06 23:00 | 44261.9583 | 0 | 10.057 | 37.78
2021-03-06 23:30 | 44261.9792 | 0 | 9.6353 | 37.78
2021-03-07 | 44262 | 0 | 9.3753 | 37.78
2021-03-07 00:30 | 44262.0208 | 0 | 9.1743 | 37.78
2021-03-07 01:00 | 44262.0417 | 0 | 9.0485 | 37.78
2021-03-07 01:30 | 44262.0625 | 0 | 8.9326 | 37.78
2021-03-07 02:00 | 44262.0833 | 0 | 8.8402 | 37.78
2021-03-07 02:30 | 44262.1042 | 0 | 8.6392 | 37.78
2021-03-07 03:00 | 44262.125 | 0 | 8.5288 | 37.78
2021-03-07 03:30 | 44262.1458 | 0 | 8.6314 | 37.78
2021-03-07 04:00 | 44262.1667 | 0 | 8.9456 | 37.78
2021-03-07 04:30 | 44262.1875 | 0 | 9.5584 | 37.78
2021-03-07 05:00 | 44262.2083 | 0 | 10.1381 | 37.78
2021-03-07 05:30 | 44262.2292 | 0 | 10.7289 | 37.78
2021-03-07 06:00 | 44262.25 | 0 | 11.5615 | 37.78
2021-03-07 06:30 | 44262.2708 | 0 | 12.4218 | 37.78
2021-03-07 07:00 | 44262.2917 | 0 | 12.8606 | 37.78
2021-03-07 07:30 | 44262.3125 | 0 | 12.9215 | 37.78
2021-03-07 08:00 | 44262.3333 | 0 | 13.2529 | 37.78
2021-03-07 08:30 | 44262.3542 | 0 | 13.0371 | 37.78
2021-03-07 09:00 | 44262.375 | 0 | 13.3943 | 37.78
2021-03-07 09:30 | 44262.3958 | 0 | 13.6237 | 37.78
2021-03-07 10:00 | 44262.4167 | 0 | 13.5686 | 37.78
2021-03-07 10:30 | 44262.4375 | 0 | 13.87 | 37.78
2021-03-07 11:00 | 44262.4583 | 0 | 13.6259 | 37.78
2021-03-07 11:30 | 44262.4792 | 0 | 13.7431 | 37.78
2021-03-07 12:00 | 44262.5 | 0 | 13.8992 | 37.78
2021-03-07 12:30 | 44262.5208 | 0 | 14.2536 | 37.78
2021-03-07 13:00 | 44262.5417 | 0 | 15.9658 | 37.78
2021-03-07 13:30 | 44262.5625 | 0 | 14.7228 | 37.78
2021-03-07 14:00 | 44262.5833 | 0 | 16.0848 | 37.78
2021-03-07 14:30 | 44262.6042 | 0 | 15.3718 | 37.78
2021-03-07 15:00 | 44262.625 | 0 | 16.4659 | 37.78
2021-03-07 15:30 | 44262.6458 | 0 | 16.8652 | 37.78
2021-03-07 16:00 | 44262.6667 | 0 | 16.9909 | 37.78
2021-03-07 16:30 | 44262.6875 | 0 | 16.713 | 37.78
2021-03-07 17:00 | 44262.7083 | 0 | 16.6232 | 37.78
2021-03-07 17:30 | 44262.7292 | 0 | 16.7054 | 37.78
2021-03-07 18:00 | 44262.75 | 0 | 16.8857 | 37.78
2021-03-07 18:30 | 44262.7708 | 0 | 17.2355 | 37.78
2021-03-07 19:00 | 44262.7917 | 0 | 16.9359 | 37.78
2021-03-07 19:30 | 44262.8125 | 0 | 16.7182 | 37.78
2021-03-07 20:00 | 44262.8333 | 0 | 16.1915 | 37.78
2021-03-07 20:30 | 44262.8542 | 0 | 15.5449 | 37.78
2021-03-07 21:00 | 44262.875 | 0 | 14.8656 | 37.78
2021-03-07 21:30 | 44262.8958 | 0 | 14.3396 | 37.78
2021-03-07 22:00 | 44262.9167 | 0 | 13.6609 | 37.78
2021-03-07 22:30 | 44262.9375 | 0 | 12.6065 | 37.78
2021-03-07 23:00 | 44262.9583 | 0 | 11.8674 | 37.78
2021-03-07 23:30 | 44262.9792 | 0 | 11.552 | 37.78
2021-03-08 | 44263 | 0 | 10.7809 | 37.78
2021-03-08 00:30 | 44263.0208 | 0 | 10.3119 | 37.78
2021-03-08 01:00 | 44263.0417 | 0 | 9.8907 | 37.78
2021-03-08 01:30 | 44263.0625 | 0 | 9.8557 | 37.78
2021-03-08 02:00 | 44263.0833 | 0 | 9.7069 | 37.78
2021-03-08 02:30 | 44263.1042 | 0 | 9.5022 | 37.78
2021-03-08 03:00 | 44263.125 | 0 | 9.4187 | 37.78
2021-03-08 03:30 | 44263.1458 | 0 | 9.3821 | 37.78
2021-03-08 04:00 | 44263.1667 | 0 | 9.7604 | 37.78
2021-03-08 04:30 | 44263.1875 | 0 | 10.2022 | 37.78
2021-03-08 05:00 | 44263.2083 | 0 | 10.856 | 37.78
2021-03-08 05:30 | 44263.2292 | 0 | 11.5154 | 37.78
2021-03-08 06:00 | 44263.25 | 0 | 12.1735 | 37.78
2021-03-08 06:30 | 44263.2708 | 0 | 12.676 | 37.78
2021-03-08 07:00 | 44263.2917 | 0 | 13.3176 | 37.78
2021-03-08 07:30 | 44263.3125 | 0 | 13.6361 | 37.78
2021-03-08 08:00 | 44263.3333 | 0 | 13.5157 | 37.78
2021-03-08 08:30 | 44263.3542 | 0 | 14.12 | 37.78
2021-03-08 09:00 | 44263.375 | 0 | 14.1364 | 37.78
2021-03-08 09:30 | 44263.3958 | 0 | 13.3155 | 37.78
2021-03-08 10:00 | 44263.4167 | 0 | 13.1524 | 37.78
2021-03-08 10:30 | 44263.4375 | 0 | 14.1822 | 37.78
2021-03-08 11:00 | 44263.4583 | 0 | 16.1531 | 37.78
2021-03-08 11:30 | 44263.4792 | 0 | 15.7226 | 37.78
2021-03-08 12:00 | 44263.5 | 0 | 15.6595 | 37.78
2021-03-08 12:30 | 44263.5208 | 0 | 14.9107 | 37.78
2021-03-08 13:00 | 44263.5417 | 0 | 15.2887 | 37.78
2021-03-08 13:30 | 44263.5625 | 0 | 15.7091 | 37.78
2021-03-08 14:00 | 44263.5833 | 0 | 15.3778 | 37.78
2021-03-08 14:30 | 44263.6042 | 0 | 15.8711 | 37.78
2021-03-08 15:00 | 44263.625 | 0 | 16.2537 | 37.78
2021-03-08 15:30 | 44263.6458 | 0 | 17.1335 | 37.78
2021-03-08 16:00 | 44263.6667 | 0 | 17.5838 | 37.78
2021-03-08 16:30 | 44263.6875 | 0 | 18.1737 | 37.78
2021-03-08 17:00 | 44263.7083 | 0 | 18.3574 | 37.78
2021-03-08 17:30 | 44263.7292 | 0 | 18.6389 | 37.78
2021-03-08 18:00 | 44263.75 | 0 | 18.498 | 37.78
2021-03-08 18:30 | 44263.7708 | 0 | 18.9656 | 37.78
2021-03-08 19:00 | 44263.7917 | 0 | 18.5802 | 37.78
2021-03-08 19:30 | 44263.8125 | 0 | 18.0751 | 37.78
2021-03-08 20:00 | 44263.8333 | 0 | 17.4102 | 37.78
2021-03-08 20:30 | 44263.8542 | 0 | 16.6835 | 37.78
2021-03-08 21:00 | 44263.875 | 0 | 15.9241 | 37.78
2021-03-08 21:30 | 44263.8958 | 0 | 15.175 | 37.78
2021-03-08 22:00 | 44263.9167 | 0 | 14.1495 | 37.78
2021-03-08 22:30 | 44263.9375 | 0 | 13.1143 | 37.78
2021-03-08 23:00 | 44263.9583 | 0 | 12.5176 | 37.78
2021-03-08 23:30 | 44263.9792 | 0 | 11.9552 | 37.78
2021-03-09 | 44264 | 0 | 11.2249 | 37.78
2021-03-09 00:30 | 44264.0208 | 0 | 10.7481 | 37.78
2021-03-09 01:00 | 44264.0417 | 0 | 10.4937 | 37.78
2021-03-09 01:30 | 44264.0625 | 0 | 10.2094 | 37.78
2021-03-09 02:00 | 44264.0833 | 0 | 10.0168 | 37.78
2021-03-09 02:30 | 44264.1042 | 0 | 9.8325 | 37.78
2021-03-09 03:00 | 44264.125 | 0 | 9.6752 | 37.78
2021-03-09 03:30 | 44264.1458 | 0 | 9.5816 | 37.78
2021-03-09 04:00 | 44264.1667 | 0 | 9.8488 | 37.78
2021-03-09 04:30 | 44264.1875 | 0 | 10.0537 | 37.78
2021-03-09 05:00 | 44264.2083 | 0 | 10.5633 | 37.78
2021-03-09 05:30 | 44264.2292 | 0 | 11.217 | 37.78
2021-03-09 06:00 | 44264.25 | 0 | 11.8471 | 37.78
2021-03-09 06:30 | 44264.2708 | 0 | 12.4279 | 37.78
2021-03-09 07:00 | 44264.2917 | 0 | 12.7306 | 37.78
2021-03-09 07:30 | 44264.3125 | 0 | 13.5018 | 37.78
2021-03-09 08:00 | 44264.3333 | 0 | 13.6421 | 37.78
2021-03-09 08:30 | 44264.3542 | 0 | 13.2912 | 37.78
2021-03-09 09:00 | 44264.375 | 0 | 13.7033 | 37.78
2021-03-09 09:30 | 44264.3958 | 0 | 14.2046 | 37.78
2021-03-09 10:00 | 44264.4167 | 0 | 15.0321 | 37.78
2021-03-09 10:30 | 44264.4375 | 0 | 14.6141 | 37.78
2021-03-09 11:00 | 44264.4583 | 0 | 14.902 | 37.78
2021-03-09 11:30 | 44264.4792 | 0 | 16.6394 | 37.78
2021-03-09 12:00 | 44264.5 | 0 | 15.2041 | 37.78
2021-03-09 12:30 | 44264.5208 | 0 | 15.3165 | 37.78
2021-03-09 13:00 | 44264.5417 | 0 | 15.9178 | 37.78
2021-03-09 13:30 | 44264.5625 | 0 | 16.7311 | 37.78
2021-03-09 14:00 | 44264.5833 | 0 | 17.1301 | 37.78
2021-03-09 14:30 | 44264.6042 | 0 | 16.7779 | 37.78
2021-03-09 15:00 | 44264.625 | 0 | 17.2866 | 37.78
2021-03-09 15:30 | 44264.6458 | 0 | 18.0091 | 37.78
2021-03-09 16:00 | 44264.6667 | 0 | 18.3106 | 37.78
2021-03-09 16:30 | 44264.6875 | 0 | 19.0142 | 37.78
2021-03-09 17:00 | 44264.7083 | 0 | 18.12 | 37.78
2021-03-09 17:30 | 44264.7292 | 0 | 18.2674 | 37.78
2021-03-09 18:00 | 44264.75 | 0 | 18.361 | 37.78
2021-03-09 18:30 | 44264.7708 | 0 | 19.0988 | 37.78
2021-03-09 19:00 | 44264.7917 | 0 | 18.9763 | 37.78
2021-03-09 19:30 | 44264.8125 | 0 | 18.384 | 37.78
2021-03-09 20:00 | 44264.8333 | 0 | 17.9726 | 37.78
2021-03-09 20:30 | 44264.8542 | 0 | 17.2829 | 37.78
2021-03-09 21:00 | 44264.875 | 0 | 16.4093 | 37.78
2021-03-09 21:30 | 44264.8958 | 0 | 15.5487 | 37.78
2021-03-09 22:00 | 44264.9167 | 0 | 14.4587 | 37.78
2021-03-09 22:30 | 44264.9375 | 0 | 12.9747 | 37.78
2021-03-09 23:00 | 44264.9583 | 0 | 12.4503 | 37.78
2021-03-09 23:30 | 44264.9792 | 0 | 11.6823 | 37.78
2021-03-10 | 44265 | 0 | 10.9383 | 37.78
2021-03-10 00:30 | 44265.0208 | 0 | 10.5654 | 37.78
2021-03-10 01:00 | 44265.0417 | 0 | 10.3495 | 37.78
2021-03-10 01:30 | 44265.0625 | 0 | 10.2314 | 37.78
2021-03-10 02:00 | 44265.0833 | 0 | 9.9595 | 37.78
2021-03-10 02:30 | 44265.1042 | 0 | 9.8521 | 37.78
2021-03-10 03:00 | 44265.125 | 0 | 9.7125 | 37.78
2021-03-10 03:30 | 44265.1458 | 0 | 9.8225 | 37.78
2021-03-10 04:00 | 44265.1667 | 0 | 10.0029 | 37.78
2021-03-10 04:30 | 44265.1875 | 0 | 10.4086 | 37.78
2021-03-10 05:00 | 44265.2083 | 0 | 10.8783 | 37.78
2021-03-10 05:30 | 44265.2292 | 0 | 11.5694 | 37.78
2021-03-10 06:00 | 44265.25 | 0 | 12.3672 | 37.78
2021-03-10 06:30 | 44265.2708 | 0 | 12.9766 | 37.78
2021-03-10 07:00 | 44265.2917 | 0 | 13.7763 | 37.78
2021-03-10 07:30 | 44265.3125 | 0 | 14.423 | 37.78
2021-03-10 08:00 | 44265.3333 | 0 | 14.2744 | 37.78
2021-03-10 08:30 | 44265.3542 | 0 | 14.2703 | 37.78
2021-03-10 09:00 | 44265.375 | 0 | 14.0791 | 37.78
2021-03-10 09:30 | 44265.3958 | 0 | 15.3828 | 37.78
2021-03-10 10:00 | 44265.4167 | 0 | 14.233 | 37.78
2021-03-10 10:30 | 44265.4375 | 0 | 15.3971 | 37.78
2021-03-10 11:00 | 44265.4583 | 0 | 15.907 | 37.78
2021-03-10 11:30 | 44265.4792 | 0 | 15.1767 | 37.78
2021-03-10 12:00 | 44265.5 | 0 | 15.1986 | 37.78
2021-03-10 12:30 | 44265.5208 | 0 | 15.6885 | 37.78
2021-03-10 13:00 | 44265.5417 | 0 | 15.5294 | 37.78
2021-03-10 13:30 | 44265.5625 | 0 | 15.4335 | 37.78
2021-03-10 14:00 | 44265.5833 | 0 | 14.9492 | 37.78
2021-03-10 14:30 | 44265.6042 | 0 | 14.5244 | 37.78
2021-03-10 15:00 | 44265.625 | 0 | 14.211 | 37.78
2021-03-10 15:30 | 44265.6458 | 0 | 14.3856 | 37.78
2021-03-10 16:00 | 44265.6667 | 0 | 14.2829 | 37.78
2021-03-10 16:30 | 44265.6875 | 0 | 14.5953 | 37.78
2021-03-10 17:00 | 44265.7083 | 0 | 14.9283 | 37.78
2021-03-10 17:30 | 44265.7292 | 0 | 15.157 | 37.78
2021-03-10 18:00 | 44265.75 | 0 | 15.3273 | 37.78
2021-03-10 18:30 | 44265.7708 | 0 | 15.7668 | 37.78
2021-03-10 19:00 | 44265.7917 | 0 | 15.5982 | 37.78
2021-03-10 19:30 | 44265.8125 | 0 | 15.4269 | 37.78
2021-03-10 20:00 | 44265.8333 | 0 | 14.9443 | 37.78
2021-03-10 20:30 | 44265.8542 | 0 | 14.5788 | 37.78
2021-03-10 21:00 | 44265.875 | 0 | 14.0441 | 37.78
2021-03-10 21:30 | 44265.8958 | 0 | 13.4884 | 37.78
2021-03-10 22:00 | 44265.9167 | 0 | 12.6794 | 37.78
2021-03-10 22:30 | 44265.9375 | 0 | 11.7096 | 37.78
2021-03-10 23:00 | 44265.9583 | 0 | 11.1565 | 37.78
2021-03-10 23:30 | 44265.9792 | 0 | 10.4997 | 37.78
2021-03-11 | 44266 | 0 | 9.7804 | 37.78
2021-03-11 00:30 | 44266.0208 | 0 | 9.4048 | 37.78
2021-03-11 01:00 | 44266.0417 | 0 | 9.2606 | 37.78
2021-03-11 01:30 | 44266.0625 | 0 | 9.1909 | 37.78
2021-03-11 02:00 | 44266.0833 | 0 | 9.1318 | 37.78
2021-03-11 02:30 | 44266.1042 | 0 | 9.0543 | 37.78
2021-03-11 03:00 | 44266.125 | 0 | 8.7343 | 37.78
2021-03-11 03:30 | 44266.1458 | 0 | 8.9506 | 37.78
2021-03-11 04:00 | 44266.1667 | 0 | 9.2323 | 37.78
2021-03-11 04:30 | 44266.1875 | 0 | 9.6963 | 37.78
2021-03-11 05:00 | 44266.2083 | 0 | 10.2117 | 37.78
2021-03-11 05:30 | 44266.2292 | 0 | 10.9199 | 37.78
2021-03-11 06:00 | 44266.25 | 0 | 11.5288 | 37.78
2021-03-11 06:30 | 44266.2708 | 0 | 12.2078 | 37.78
2021-03-11 07:00 | 44266.2917 | 0 | 12.2629 | 37.78
2021-03-11 07:30 | 44266.3125 | 0 | 12.3139 | 37.78
2021-03-11 08:00 | 44266.3333 | 0 | 12.6353 | 37.78
2021-03-11 08:30 | 44266.3542 | 0 | 12.6489 | 37.78
2021-03-11 09:00 | 44266.375 | 0 | 12.6681 | 37.78
2021-03-11 09:30 | 44266.3958 | 0 | 13.1764 | 37.78
2021-03-11 10:00 | 44266.4167 | 0 | 14.181 | 37.78
2021-03-11 10:30 | 44266.4375 | 0 | 15.3324 | 37.78
2021-03-11 11:00 | 44266.4583 | 0 | 14.6719 | 37.78
2021-03-11 11:30 | 44266.4792 | 0 | 15.7806 | 37.78
2021-03-11 12:00 | 44266.5 | 0 | 14.2738 | 37.78
2021-03-11 12:30 | 44266.5208 | 0 | 13.982 | 37.78
2021-03-11 13:00 | 44266.5417 | 0 | 12.5888 | 37.78
2021-03-11 13:30 | 44266.5625 | 0 | 15.0226 | 37.78
2021-03-11 14:00 | 44266.5833 | 0 | 14.9168 | 37.78
2021-03-11 14:30 | 44266.6042 | 0 | 14.491 | 37.78
2021-03-11 15:00 | 44266.625 | 0 | 14.4247 | 37.78
2021-03-11 15:30 | 44266.6458 | 0 | 13.548 | 37.78
2021-03-11 16:00 | 44266.6667 | 0 | 14.8763 | 37.78
2021-03-11 16:30 | 44266.6875 | 0 | 15.534 | 37.78
2021-03-11 17:00 | 44266.7083 | 0 | 15.7204 | 37.78
2021-03-11 17:30 | 44266.7292 | 0 | 15.4222 | 37.78
2021-03-11 18:00 | 44266.75 | 0 | 15.3128 | 37.78
2021-03-11 18:30 | 44266.7708 | 0 | 15.6245 | 37.78
2021-03-11 19:00 | 44266.7917 | 0 | 15.4791 | 37.78
2021-03-11 19:30 | 44266.8125 | 0 | 15.3259 | 37.78
2021-03-11 20:00 | 44266.8333 | 0 | 14.8502 | 37.78
2021-03-11 20:30 | 44266.8542 | 0 | 13.98 | 37.78
2021-03-11 21:00 | 44266.875 | 0 | 13.6139 | 37.78
2021-03-11 21:30 | 44266.8958 | 0 | 13.2769 | 37.78
2021-03-11 22:00 | 44266.9167 | 0 | 12.7354 | 37.78
2021-03-11 22:30 | 44266.9375 | 0 | 11.776 | 37.78
2021-03-11 23:00 | 44266.9583 | 0 | 11.1542 | 37.78
2021-03-11 23:30 | 44266.9792 | 0 | 10.7051 | 37.78
2021-03-12 | 44267 | 0 | 10.0249 | 37.78
2021-03-12 00:30 | 44267.0208 | 0 | 9.6245 | 37.78
2021-03-12 01:00 | 44267.0417 | 0 | 9.4634 | 37.78
2021-03-12 01:30 | 44267.0625 | 0 | 9.3629 | 37.78
2021-03-12 02:00 | 44267.0833 | 0 | 9.144 | 37.78
2021-03-12 02:30 | 44267.1042 | 0 | 9.0163 | 37.78
2021-03-12 03:00 | 44267.125 | 0 | 8.9177 | 37.78
2021-03-12 03:30 | 44267.1458 | 0 | 8.9322 | 37.78
2021-03-12 04:00 | 44267.1667 | 0 | 9.0063 | 37.78
2021-03-12 04:30 | 44267.1875 | 0 | 9.2177 | 37.78
2021-03-12 05:00 | 44267.2083 | 0 | 9.4493 | 37.78
2021-03-12 05:30 | 44267.2292 | 0 | 9.4681 | 37.78
2021-03-12 06:00 | 44267.25 | 0 | 9.5268 | 37.78
2021-03-12 06:30 | 44267.2708 | 0 | 9.7171 | 37.78
2021-03-12 07:00 | 44267.2917 | 0 | 9.9288 | 37.78
2021-03-12 07:30 | 44267.3125 | 0 | 9.9587 | 37.78
2021-03-12 08:00 | 44267.3333 | 0 | 11.2624 | 37.78
2021-03-12 08:30 | 44267.3542 | 0 | 11.7007 | 37.78
2021-03-12 09:00 | 44267.375 | 0 | 11.2484 | 37.78
2021-03-12 09:30 | 44267.3958 | 0 | 11.523 | 37.78
2021-03-12 10:00 | 44267.4167 | 0 | 11.2326 | 37.78
2021-03-12 10:30 | 44267.4375 | 0 | 10.5318 | 37.78
2021-03-12 11:00 | 44267.4583 | 0 | 9.4354 | 37.78
2021-03-12 11:30 | 44267.4792 | 0 | 10.5448 | 37.78
2021-03-12 12:00 | 44267.5 | 0 | 11.1843 | 37.78
2021-03-12 12:30 | 44267.5208 | 0 | 11.4709 | 37.78
2021-03-12 13:00 | 44267.5417 | 0 | 10.9582 | 37.78
2021-03-12 13:30 | 44267.5625 | 0 | 11.3082 | 37.78
2021-03-12 14:00 | 44267.5833 | 0 | 12.0207 | 37.78
2021-03-12 14:30 | 44267.6042 | 0 | 13.4215 | 37.78
2021-03-12 15:00 | 44267.625 | 0 | 12.8635 | 37.78
2021-03-12 15:30 | 44267.6458 | 0 | 12.975 | 37.78
2021-03-12 16:00 | 44267.6667 | 0 | 13.36 | 37.78
2021-03-12 16:30 | 44267.6875 | 0 | 13.9821 | 37.78
2021-03-12 17:00 | 44267.7083 | 0 | 14.2715 | 37.78
2021-03-12 17:30 | 44267.7292 | 0 | 14.3012 | 37.78
2021-03-12 18:00 | 44267.75 | 0 | 14.2482 | 37.78
2021-03-12 18:30 | 44267.7708 | 0 | 14.6353 | 37.78
2021-03-12 19:00 | 44267.7917 | 0 | 14.2908 | 37.78
2021-03-12 19:30 | 44267.8125 | 0 | 14.0644 | 37.78
2021-03-12 20:00 | 44267.8333 | 0 | 13.6643 | 37.78
2021-03-12 20:30 | 44267.8542 | 0 | 13.1914 | 37.78
2021-03-12 21:00 | 44267.875 | 0 | 12.7451 | 37.78
2021-03-12 21:30 | 44267.8958 | 0 | 12.4844 | 37.78
2021-03-12 22:00 | 44267.9167 | 0 | 12.0156 | 37.78
2021-03-12 22:30 | 44267.9375 | 0 | 11.1384 | 37.78
2021-03-12 23:00 | 44267.9583 | 0 | 10.6606 | 37.78
2021-03-12 23:30 | 44267.9792 | 0 | 10.1331 | 37.78
2021-03-13 | 44268 | 0 | 9.7198 | 37.78
2021-03-13 00:30 | 44268.0208 | 0 | 9.3455 | 37.78
2021-03-13 01:00 | 44268.0417 | 0 | 9.1007 | 37.78
2021-03-13 01:30 | 44268.0625 | 0 | 9.0114 | 37.78
2021-03-13 02:00 | 44268.0833 | 0 | 8.8695 | 37.78
2021-03-13 02:30 | 44268.1042 | 0 | 8.6777 | 37.78
2021-03-13 03:00 | 44268.125 | 0 | 8.4956 | 37.78
2021-03-13 03:30 | 44268.1458 | 0 | 8.4842 | 37.78
2021-03-13 04:00 | 44268.1667 | 0 | 8.373 | 37.78
2021-03-13 04:30 | 44268.1875 | 0 | 8.3524 | 37.78
2021-03-13 05:00 | 44268.2083 | 0 | 8.3747 | 37.78
2021-03-13 05:30 | 44268.2292 | 0 | 8.3716 | 37.78
2021-03-13 06:00 | 44268.25 | 0 | 8.3551 | 37.78
2021-03-13 06:30 | 44268.2708 | 0 | 8.4173 | 37.78
2021-03-13 07:00 | 44268.2917 | 0 | 8.5705 | 37.78
2021-03-13 07:30 | 44268.3125 | 0 | 8.6664 | 37.78
2021-03-13 08:00 | 44268.3333 | 0 | 8.8017 | 37.78
2021-03-13 08:30 | 44268.3542 | 0 | 9.2333 | 37.78
2021-03-13 09:00 | 44268.375 | 0 | 9.8645 | 37.78
2021-03-13 09:30 | 44268.3958 | 0 | 9.9261 | 37.78
2021-03-13 10:00 | 44268.4167 | 0 | 9.6793 | 37.78
2021-03-13 10:30 | 44268.4375 | 0 | 10.5381 | 37.78
2021-03-13 11:00 | 44268.4583 | 0 | 10.4116 | 37.78
2021-03-13 11:30 | 44268.4792 | 0 | 10.1602 | 37.78
2021-03-13 12:00 | 44268.5 | 0 | 10.4478 | 37.78
2021-03-13 12:30 | 44268.5208 | 0 | 10.6607 | 37.78
2021-03-13 13:00 | 44268.5417 | 0 | 11.1771 | 37.78
2021-03-13 13:30 | 44268.5625 | 0 | 11.7898 | 37.78
2021-03-13 14:00 | 44268.5833 | 0 | 12.3328 | 37.78
2021-03-13 14:30 | 44268.6042 | 0 | 13.0305 | 37.78
2021-03-13 15:00 | 44268.625 | 0 | 13.5653 | 37.78
2021-03-13 15:30 | 44268.6458 | 0 | 14.1393 | 37.78
2021-03-13 16:00 | 44268.6667 | 0 | 14.7205 | 37.78
2021-03-13 16:30 | 44268.6875 | 0 | 15.4922 | 37.78
2021-03-13 17:00 | 44268.7083 | 0 | 16.1392 | 37.78
2021-03-13 17:30 | 44268.7292 | 0 | 16.4108 | 37.78
2021-03-13 18:00 | 44268.75 | 0 | 16.7578 | 37.78
2021-03-13 18:30 | 44268.7708 | 0 | 17.0595 | 37.78
2021-03-13 19:00 | 44268.7917 | 0 | 16.8664 | 37.78
2021-03-13 19:30 | 44268.8125 | 0 | 16.6433 | 37.78
2021-03-13 20:00 | 44268.8333 | 0 | 16.0465 | 37.78
2021-03-13 20:30 | 44268.8542 | 0 | 15.4461 | 37.78
2021-03-13 21:00 | 44268.875 | 0 | 14.6798 | 37.78
2021-03-13 21:30 | 44268.8958 | 0 | 14.0721 | 37.78
2021-03-13 22:00 | 44268.9167 | 0 | 13.3573 | 37.78
2021-03-13 22:30 | 44268.9375 | 0 | 12.2749 | 37.78
2021-03-13 23:00 | 44268.9583 | 0 | 11.3867 | 37.78
2021-03-13 23:30 | 44268.9792 | 0 | 10.9271 | 37.78
2021-03-14 | 44269 | 0 | 10.4427 | 37.78
2021-03-14 00:30 | 44269.0208 | 0 | 9.9723 | 37.78
2021-03-14 01:00 | 44269.0417 | 0 | 9.7878 | 37.78
2021-03-14 01:30 | 44269.0625 | 0 | 9.6538 | 37.78
2021-03-14 02:00 | 44269.0833 | 0 | 9.6529 | 37.78
2021-03-14 02:30 | 44269.1042 | 0 | 9.5943 | 37.78
2021-03-14 03:00 | 44269.125 | 0 | 9.4169 | 37.78
2021-03-14 03:30 | 44269.1458 | 0 | 9.5809 | 37.78
2021-03-14 04:00 | 44269.1667 | 0 | 9.947 | 37.78
2021-03-14 04:30 | 44269.1875 | 0 | 10.4308 | 37.78
2021-03-14 05:00 | 44269.2083 | 0 | 10.8656 | 37.78
2021-03-14 05:30 | 44269.2292 | 0 | 11.634 | 37.78
2021-03-14 06:00 | 44269.25 | 0 | 12.5068 | 37.78
2021-03-14 06:30 | 44269.2708 | 0 | 13.5315 | 37.78
2021-03-14 07:00 | 44269.2917 | 0 | 14.2857 | 37.78
2021-03-14 07:30 | 44269.3125 | 0 | 14.9245 | 37.78
2021-03-14 08:00 | 44269.3333 | 0 | 14.9148 | 37.78
2021-03-14 08:30 | 44269.3542 | 0 | 14.9322 | 37.78
2021-03-14 09:00 | 44269.375 | 0 | 14.9821 | 37.78
2021-03-14 09:30 | 44269.3958 | 0 | 15.0264 | 37.78
2021-03-14 10:00 | 44269.4167 | 0 | 14.7333 | 37.78
2021-03-14 10:30 | 44269.4375 | 0 | 14.3052 | 37.78
2021-03-14 11:00 | 44269.4583 | 0 | 13.5267 | 37.78
2021-03-14 11:30 | 44269.4792 | 0 | 14.0813 | 37.78
2021-03-14 12:00 | 44269.5 | 0 | 14.0967 | 37.78
2021-03-14 12:30 | 44269.5208 | 0 | 13.2794 | 37.78
2021-03-14 13:00 | 44269.5417 | 0 | 13.4557 | 37.78
2021-03-14 13:30 | 44269.5625 | 0 | 13.5041 | 37.78
2021-03-14 14:00 | 44269.5833 | 0 | 14.1238 | 37.78
2021-03-14 14:30 | 44269.6042 | 0 | 13.8236 | 37.78
2021-03-14 15:00 | 44269.625 | 0 | 13.4438 | 37.78
2021-03-14 15:30 | 44269.6458 | 0 | 13.545 | 37.78
2021-03-14 16:00 | 44269.6667 | 0 | 13.7149 | 37.78
2021-03-14 16:30 | 44269.6875 | 0 | 14.0288 | 37.78
2021-03-14 17:00 | 44269.7083 | 0 | 14.126 | 37.78
2021-03-14 17:30 | 44269.7292 | 0 | 14.1748 | 37.78
2021-03-14 18:00 | 44269.75 | 0 | 14.525 | 37.78
2021-03-14 18:30 | 44269.7708 | 0 | 14.8411 | 37.78
2021-03-14 19:00 | 44269.7917 | 0 | 14.2699 | 37.78
2021-03-14 19:30 | 44269.8125 | 0 | 14.0563 | 37.78
2021-03-14 20:00 | 44269.8333 | 0 | 13.6429 | 37.78
2021-03-14 20:30 | 44269.8542 | 0 | 13.1065 | 37.78
2021-03-14 21:00 | 44269.875 | 0 | 12.5014 | 37.78
2021-03-14 21:30 | 44269.8958 | 0 | 12.2126 | 37.78
2021-03-14 22:00 | 44269.9167 | 0 | 11.5982 | 37.78
2021-03-14 22:30 | 44269.9375 | 0 | 10.8477 | 37.78
2021-03-14 23:00 | 44269.9583 | 0 | 10.2731 | 37.78
2021-03-14 23:30 | 44269.9792 | 0 | 9.7856 | 37.78
2021-03-15 | 44270 | 0 | 9.2689 | 37.78
2021-03-15 00:30 | 44270.0208 | 0 | 8.8354 | 37.78
2021-03-15 01:00 | 44270.0417 | 0 | 8.7749 | 37.78
2021-03-15 01:30 | 44270.0625 | 0 | 8.7335 | 37.78
2021-03-15 02:00 | 44270.0833 | 0 | 8.5701 | 37.78
2021-03-15 02:30 | 44270.1042 | 0 | 8.5135 | 37.78
2021-03-15 03:00 | 44270.125 | 0 | 8.5245 | 37.78
2021-03-15 03:30 | 44270.1458 | 0 | 8.5714 | 37.78
2021-03-15 04:00 | 44270.1667 | 0 | 8.7983 | 37.78
2021-03-15 04:30 | 44270.1875 | 0 | 9.1096 | 37.78
2021-03-15 05:00 | 44270.2083 | 0 | 9.8198 | 37.78
2021-03-15 05:30 | 44270.2292 | 0 | 10.4919 | 37.78
2021-03-15 06:00 | 44270.25 | 0 | 11.2101 | 37.78
2021-03-15 06:30 | 44270.2708 | 0 | 12.0182 | 37.78
2021-03-15 07:00 | 44270.2917 | 0 | 12.5673 | 37.78
2021-03-15 07:30 | 44270.3125 | 0 | 12.844 | 37.78
2021-03-15 08:00 | 44270.3333 | 0 | 12.8663 | 37.78
2021-03-15 08:30 | 44270.3542 | 0 | 12.9662 | 37.78
2021-03-15 09:00 | 44270.375 | 0 | 12.5526 | 37.78
2021-03-15 09:30 | 44270.3958 | 0 | 12.0688 | 37.78
2021-03-15 10:00 | 44270.4167 | 0 | 11.7626 | 37.78
2021-03-15 10:30 | 44270.4375 | 0 | 12.6834 | 37.78
2021-03-15 11:00 | 44270.4583 | 0 | 12.5145 | 37.78
2021-03-15 11:30 | 44270.4792 | 0 | 13.2545 | 37.78
2021-03-15 12:00 | 44270.5 | 0 | 13.7279 | 37.78
2021-03-15 12:30 | 44270.5208 | 0 | 13.7402 | 37.78
2021-03-15 13:00 | 44270.5417 | 0 | 13.3129 | 37.78
2021-03-15 13:30 | 44270.5625 | 0 | 13.4127 | 37.78
2021-03-15 14:00 | 44270.5833 | 0 | 13.5681 | 37.78
2021-03-15 14:30 | 44270.6042 | 0 | 13.0809 | 37.78
2021-03-15 15:00 | 44270.625 | 0 | 12.9998 | 37.78
2021-03-15 15:30 | 44270.6458 | 0 | 13.1417 | 37.78
2021-03-15 16:00 | 44270.6667 | 0 | 13.2628 | 37.78
2021-03-15 16:30 | 44270.6875 | 0 | 13.5288 | 37.78
2021-03-15 17:00 | 44270.7083 | 0 | 13.5774 | 37.78
2021-03-15 17:30 | 44270.7292 | 0 | 13.91 | 37.78
2021-03-15 18:00 | 44270.75 | 0 | 14.1041 | 37.78
2021-03-15 18:30 | 44270.7708 | 0 | 14.2324 | 37.78
2021-03-15 19:00 | 44270.7917 | 0 | 13.9397 | 37.78
2021-03-15 19:30 | 44270.8125 | 0 | 13.6277 | 37.78
2021-03-15 20:00 | 44270.8333 | 0 | 13.2443 | 37.78
2021-03-15 20:30 | 44270.8542 | 0 | 12.7575 | 37.78
2021-03-15 21:00 | 44270.875 | 0 | 12.2746 | 37.78
2021-03-15 21:30 | 44270.8958 | 0 | 11.9404 | 37.78
2021-03-15 22:00 | 44270.9167 | 0 | 11.3235 | 37.78
2021-03-15 22:30 | 44270.9375 | 0 | 10.5636 | 37.78
2021-03-15 23:00 | 44270.9583 | 0 | 10.0732 | 37.78
2021-03-15 23:30 | 44270.9792 | 0 | 9.546 | 37.78
2021-03-16 | 44271 | 0 | 9.0822 | 37.78
2021-03-16 00:30 | 44271.0208 | 0 | 8.7816 | 37.78
2021-03-16 01:00 | 44271.0417 | 0 | 8.6703 | 37.78
2021-03-16 01:30 | 44271.0625 | 0 | 8.5437 | 37.78
2021-03-16 02:00 | 44271.0833 | 0 | 8.4763 | 37.78
2021-03-16 02:30 | 44271.1042 | 0 | 8.2863 | 37.78
2021-03-16 03:00 | 44271.125 | 0 | 8.3594 | 37.78
2021-03-16 03:30 | 44271.1458 | 0 | 8.3862 | 37.78
2021-03-16 04:00 | 44271.1667 | 0 | 8.67 | 37.78
2021-03-16 04:30 | 44271.1875 | 0 | 9.0177 | 37.78
2021-03-16 05:00 | 44271.2083 | 0 | 9.4894 | 37.78
2021-03-16 05:30 | 44271.2292 | 0 | 10.2475 | 37.78
2021-03-16 06:00 | 44271.25 | 0 | 11.0213 | 37.78
2021-03-16 06:30 | 44271.2708 | 0 | 11.9235 | 37.78
2021-03-16 07:00 | 44271.2917 | 0 | 12.8449 | 37.78
2021-03-16 07:30 | 44271.3125 | 0 | 13.1603 | 37.78
2021-03-16 08:00 | 44271.3333 | 0 | 13.5069 | 37.78
2021-03-16 08:30 | 44271.3542 | 0 | 13.6045 | 37.78
2021-03-16 09:00 | 44271.375 | 0 | 13.5687 | 37.78
2021-03-16 09:30 | 44271.3958 | 0 | 13.3255 | 37.78
2021-03-16 10:00 | 44271.4167 | 0 | 12.9785 | 37.78
2021-03-16 10:30 | 44271.4375 | 0 | 13.4981 | 37.78
2021-03-16 11:00 | 44271.4583 | 0 | 13.7826 | 37.78
2021-03-16 11:30 | 44271.4792 | 0 | 13.7384 | 37.78
2021-03-16 12:00 | 44271.5 | 0 | 13.4222 | 37.78
2021-03-16 12:30 | 44271.5208 | 0 | 13.2272 | 37.78
2021-03-16 13:00 | 44271.5417 | 0 | 13.1471 | 37.78
2021-03-16 13:30 | 44271.5625 | 0 | 13.285 | 37.78
2021-03-16 14:00 | 44271.5833 | 0 | 13.1001 | 37.78
2021-03-16 14:30 | 44271.6042 | 0 | 12.7226 | 37.78
2021-03-16 15:00 | 44271.625 | 0 | 12.504 | 37.78
2021-03-16 15:30 | 44271.6458 | 0 | 13.0664 | 37.78
2021-03-16 16:00 | 44271.6667 | 0 | 13.1313 | 37.78
2021-03-16 16:30 | 44271.6875 | 0 | 13.6085 | 37.78
2021-03-16 17:00 | 44271.7083 | 0 | 13.7818 | 37.78
2021-03-16 17:30 | 44271.7292 | 0 | 13.6783 | 37.78
2021-03-16 18:00 | 44271.75 | 0 | 13.8852 | 37.78
2021-03-16 18:30 | 44271.7708 | 0 | 14.1654 | 37.78
2021-03-16 19:00 | 44271.7917 | 0 | 13.9452 | 37.78
2021-03-16 19:30 | 44271.8125 | 0 | 13.4937 | 37.78
2021-03-16 20:00 | 44271.8333 | 0 | 13.3513 | 37.78
2021-03-16 20:30 | 44271.8542 | 0 | 12.8072 | 37.78
2021-03-16 21:00 | 44271.875 | 0 | 12.2039 | 37.78
2021-03-16 21:30 | 44271.8958 | 0 | 11.8131 | 37.78
2021-03-16 22:00 | 44271.9167 | 0 | 11.2625 | 37.78
2021-03-16 22:30 | 44271.9375 | 0 | 10.3966 | 37.78
2021-03-16 23:00 | 44271.9583 | 0 | 9.7067 | 37.78
2021-03-16 23:30 | 44271.9792 | 0 | 9.3401 | 37.78
2021-03-17 | 44272 | 0 | 8.8473 | 37.78
2021-03-17 00:30 | 44272.0208 | 0 | 8.4566 | 37.78
2021-03-17 01:00 | 44272.0417 | 0 | 8.4587 | 37.78
2021-03-17 01:30 | 44272.0625 | 0 | 8.2604 | 37.78
2021-03-17 02:00 | 44272.0833 | 0 | 8.155 | 37.78
2021-03-17 02:30 | 44272.1042 | 0 | 8.1338 | 37.78
2021-03-17 03:00 | 44272.125 | 0 | 8.0165 | 37.78
2021-03-17 03:30 | 44272.1458 | 0 | 8.1761 | 37.78
2021-03-17 04:00 | 44272.1667 | 0 | 8.4873 | 37.78
2021-03-17 04:30 | 44272.1875 | 0 | 8.8492 | 37.78
2021-03-17 05:00 | 44272.2083 | 0 | 9.4291 | 37.78
2021-03-17 05:30 | 44272.2292 | 0 | 9.9836 | 37.78
2021-03-17 06:00 | 44272.25 | 0 | 10.6776 | 37.78
2021-03-17 06:30 | 44272.2708 | 0 | 11.6472 | 37.78
2021-03-17 07:00 | 44272.2917 | 0 | 12.4771 | 37.78
2021-03-17 07:30 | 44272.3125 | 0 | 12.8137 | 37.78
2021-03-17 08:00 | 44272.3333 | 0 | 12.8719 | 37.78
2021-03-17 08:30 | 44272.3542 | 0 | 12.2416 | 37.78
2021-03-17 09:00 | 44272.375 | 0 | 11.8638 | 37.78
2021-03-17 09:30 | 44272.3958 | 0 | 12.2583 | 37.78
2021-03-17 10:00 | 44272.4167 | 0 | 10.8282 | 37.78
2021-03-17 10:30 | 44272.4375 | 0 | 11.4599 | 37.78
2021-03-17 11:00 | 44272.4583 | 0 | 12.2678 | 37.78
2021-03-17 11:30 | 44272.4792 | 0 | 13.1489 | 37.78
2021-03-17 12:00 | 44272.5 | 0 | 13.5698 | 37.78
2021-03-17 12:30 | 44272.5208 | 0 | 13.9256 | 37.78
2021-03-17 13:00 | 44272.5417 | 0 | 14.0414 | 37.78
2021-03-17 13:30 | 44272.5625 | 0 | 13.7138 | 37.78
2021-03-17 14:00 | 44272.5833 | 0 | 13.1322 | 37.78
2021-03-17 14:30 | 44272.6042 | 0 | 13.9406 | 37.78
2021-03-17 15:00 | 44272.625 | 0 | 13.9469 | 37.78
2021-03-17 15:30 | 44272.6458 | 0 | 14.5049 | 37.78
2021-03-17 16:00 | 44272.6667 | 0 | 14.2375 | 37.78
2021-03-17 16:30 | 44272.6875 | 0 | 14.0219 | 37.78
2021-03-17 17:00 | 44272.7083 | 0 | 14.1914 | 37.78
2021-03-17 17:30 | 44272.7292 | 0 | 14.4665 | 37.78
2021-03-17 18:00 | 44272.75 | 0 | 14.9505 | 37.78
2021-03-17 18:30 | 44272.7708 | 0 | 15.4409 | 37.78
2021-03-17 19:00 | 44272.7917 | 0 | 15.0714 | 37.78
2021-03-17 19:30 | 44272.8125 | 0 | 14.8301 | 37.78
2021-03-17 20:00 | 44272.8333 | 0 | 14.3027 | 37.78
2021-03-17 20:30 | 44272.8542 | 0 | 13.7033 | 37.78
2021-03-17 21:00 | 44272.875 | 0 | 13.1151 | 37.78
2021-03-17 21:30 | 44272.8958 | 0 | 12.6599 | 37.78
2021-03-17 22:00 | 44272.9167 | 0 | 12.0242 | 37.78
2021-03-17 22:30 | 44272.9375 | 0 | 11.0881 | 37.78
2021-03-17 23:00 | 44272.9583 | 0 | 10.3132 | 37.78
2021-03-17 23:30 | 44272.9792 | 0 | 9.9099 | 37.78
2021-03-18 | 44273 | 0 | 9.4457 | 37.78
2021-03-18 00:30 | 44273.0208 | 0 | 9.0747 | 37.78
2021-03-18 01:00 | 44273.0417 | 0 | 8.9374 | 37.78
2021-03-18 01:30 | 44273.0625 | 0 | 8.7407 | 37.78
2021-03-18 02:00 | 44273.0833 | 0 | 8.62 | 37.78
2021-03-18 02:30 | 44273.1042 | 0 | 8.5227 | 37.78
2021-03-18 03:00 | 44273.125 | 0 | 8.511 | 37.78
2021-03-18 03:30 | 44273.1458 | 0 | 8.6853 | 37.78
2021-03-18 04:00 | 44273.1667 | 0 | 8.8906 | 37.78
2021-03-18 04:30 | 44273.1875 | 0 | 9.0514 | 37.78
2021-03-18 05:00 | 44273.2083 | 0 | 9.7377 | 37.78
2021-03-18 05:30 | 44273.2292 | 0 | 10.4446 | 37.78
2021-03-18 06:00 | 44273.25 | 0 | 10.8338 | 37.78
2021-03-18 06:30 | 44273.2708 | 0 | 11.3975 | 37.78
2021-03-18 07:00 | 44273.2917 | 0 | 11.7809 | 37.78
2021-03-18 07:30 | 44273.3125 | 0 | 12.5166 | 37.78
2021-03-18 08:00 | 44273.3333 | 0 | 12.941 | 37.78
2021-03-18 08:30 | 44273.3542 | 0 | 12.0241 | 37.78
2021-03-18 09:00 | 44273.375 | 0 | 12.5389 | 37.78
2021-03-18 09:30 | 44273.3958 | 0 | 12.6726 | 37.78
2021-03-18 10:00 | 44273.4167 | 0 | 11.5534 | 37.78
2021-03-18 10:30 | 44273.4375 | 0 | 12.2279 | 37.78
2021-03-18 11:00 | 44273.4583 | 0 | 12.6644 | 37.78
2021-03-18 11:30 | 44273.4792 | 0 | 13.11 | 37.78
2021-03-18 12:00 | 44273.5 | 0 | 13.0869 | 37.78
2021-03-18 12:30 | 44273.5208 | 0 | 14.5933 | 37.78
2021-03-18 13:00 | 44273.5417 | 0 | 15.7587 | 37.78
2021-03-18 13:30 | 44273.5625 | 0 | 14.8115 | 37.78
2021-03-18 14:00 | 44273.5833 | 0 | 15.4204 | 37.78
2021-03-18 14:30 | 44273.6042 | 0 | 14.9236 | 37.78
2021-03-18 15:00 | 44273.625 | 0 | 15.0672 | 37.78
2021-03-18 15:30 | 44273.6458 | 0 | 15.1109 | 37.78
2021-03-18 16:00 | 44273.6667 | 0 | 15.8577 | 37.78
2021-03-18 16:30 | 44273.6875 | 0 | 16.2471 | 37.78
2021-03-18 17:00 | 44273.7083 | 0 | 15.7979 | 37.78
2021-03-18 17:30 | 44273.7292 | 0 | 15.4735 | 37.78
2021-03-18 18:00 | 44273.75 | 0 | 15.6676 | 37.78
2021-03-18 18:30 | 44273.7708 | 0 | 15.8941 | 37.78
2021-03-18 19:00 | 44273.7917 | 0 | 15.4208 | 37.78
2021-03-18 19:30 | 44273.8125 | 0 | 15.2629 | 37.78
2021-03-18 20:00 | 44273.8333 | 0 | 14.8951 | 37.78
2021-03-18 20:30 | 44273.8542 | 0 | 14.2801 | 37.78
2021-03-18 21:00 | 44273.875 | 0 | 13.6955 | 37.78
2021-03-18 21:30 | 44273.8958 | 0 | 13.2581 | 37.78
2021-03-18 22:00 | 44273.9167 | 0 | 12.7361 | 37.78
2021-03-18 22:30 | 44273.9375 | 0 | 11.7753 | 37.78
2021-03-18 23:00 | 44273.9583 | 0 | 11.263 | 37.78
2021-03-18 23:30 | 44273.9792 | 0 | 10.5936 | 37.78
2021-03-19 | 44274 | 0 | 10.2697 | 37.78
2021-03-19 00:30 | 44274.0208 | 0 | 9.6897 | 37.78
2021-03-19 01:00 | 44274.0417 | 0 | 9.4882 | 37.78
2021-03-19 01:30 | 44274.0625 | 0 | 9.2748 | 37.78
2021-03-19 02:00 | 44274.0833 | 0 | 9.063 | 37.78
2021-03-19 02:30 | 44274.1042 | 0 | 8.9509 | 37.78
2021-03-19 03:00 | 44274.125 | 0 | 8.73 | 37.78
2021-03-19 03:30 | 44274.1458 | 0 | 8.9331 | 37.78
2021-03-19 04:00 | 44274.1667 | 0 | 8.8616 | 37.78
2021-03-19 04:30 | 44274.1875 | 0 | 8.8385 | 37.78
2021-03-19 05:00 | 44274.2083 | 0 | 8.9664 | 37.78
2021-03-19 05:30 | 44274.2292 | 0 | 9.0837 | 37.78
2021-03-19 06:00 | 44274.25 | 0 | 9.3238 | 37.78
2021-03-19 06:30 | 44274.2708 | 0 | 9.5496 | 37.78
2021-03-19 07:00 | 44274.2917 | 0 | 9.8731 | 37.78
2021-03-19 07:30 | 44274.3125 | 0 | 10.6884 | 37.78
2021-03-19 08:00 | 44274.3333 | 0 | 10.5936 | 37.78
2021-03-19 08:30 | 44274.3542 | 0 | 10.7624 | 37.78
2021-03-19 09:00 | 44274.375 | 0 | 10.5302 | 37.78
2021-03-19 09:30 | 44274.3958 | 0 | 10.8869 | 37.78
2021-03-19 10:00 | 44274.4167 | 0 | 9.8436 | 37.78
2021-03-19 10:30 | 44274.4375 | 0 | 9.7387 | 37.78
2021-03-19 11:00 | 44274.4583 | 0 | 10.6728 | 37.78
2021-03-19 11:30 | 44274.4792 | 0 | 10.6037 | 37.78
2021-03-19 12:00 | 44274.5 | 0 | 9.8626 | 37.78
2021-03-19 12:30 | 44274.5208 | 0 | 9.7599 | 37.78
2021-03-19 13:00 | 44274.5417 | 0 | 11.0175 | 37.78
2021-03-19 13:30 | 44274.5625 | 0 | 11.8425 | 37.78
2021-03-19 14:00 | 44274.5833 | 0 | 12.1418 | 37.78
2021-03-19 14:30 | 44274.6042 | 0 | 12.6174 | 37.78
2021-03-19 15:00 | 44274.625 | 0 | 12.4003 | 37.78
2021-03-19 15:30 | 44274.6458 | 0 | 12.4496 | 37.78
2021-03-19 16:00 | 44274.6667 | 0 | 13.0791 | 37.78
2021-03-19 16:30 | 44274.6875 | 0 | 13.6015 | 37.78
2021-03-19 17:00 | 44274.7083 | 0 | 13.6525 | 37.78
2021-03-19 17:30 | 44274.7292 | 0 | 13.5741 | 37.78
2021-03-19 18:00 | 44274.75 | 0 | 13.8467 | 37.78
2021-03-19 18:30 | 44274.7708 | 0 | 14.0121 | 37.78
2021-03-19 19:00 | 44274.7917 | 0 | 13.4079 | 37.78
2021-03-19 19:30 | 44274.8125 | 0 | 13.1454 | 37.78
2021-03-19 20:00 | 44274.8333 | 0 | 12.7445 | 37.78
2021-03-19 20:30 | 44274.8542 | 0 | 12.5264 | 37.78
2021-03-19 21:00 | 44274.875 | 0 | 12.0353 | 37.78
2021-03-19 21:30 | 44274.8958 | 0 | 11.7263 | 37.78
2021-03-19 22:00 | 44274.9167 | 0 | 11.2874 | 37.78
2021-03-19 22:30 | 44274.9375 | 0 | 10.7826 | 37.78
2021-03-19 23:00 | 44274.9583 | 0 | 10.2086 | 37.78
2021-03-19 23:30 | 44274.9792 | 0 | 9.863 | 37.78
2021-03-20 | 44275 | 0 | 9.3498 | 37.78
2021-03-20 00:30 | 44275.0208 | 0 | 8.9885 | 37.78
2021-03-20 01:00 | 44275.0417 | 0 | 8.8293 | 37.78
2021-03-20 01:30 | 44275.0625 | 0 | 8.7242 | 37.78
2021-03-20 02:00 | 44275.0833 | 0 | 8.76 | 37.78
2021-03-20 02:30 | 44275.1042 | 0 | 8.6444 | 37.78
2021-03-20 03:00 | 44275.125 | 0 | 8.3283 | 37.78
2021-03-20 03:30 | 44275.1458 | 0 | 8.3624 | 37.78
2021-03-20 04:00 | 44275.1667 | 0 | 8.2285 | 37.78
2021-03-20 04:30 | 44275.1875 | 0 | 8.313 | 37.78
2021-03-20 05:00 | 44275.2083 | 0 | 8.3262 | 37.78
2021-03-20 05:30 | 44275.2292 | 0 | 8.4018 | 37.78
2021-03-20 06:00 | 44275.25 | 0 | 8.4225 | 37.78
2021-03-20 06:30 | 44275.2708 | 0 | 8.4146 | 37.78
2021-03-20 07:00 | 44275.2917 | 0 | 8.7427 | 37.78
2021-03-20 07:30 | 44275.3125 | 0 | 8.9524 | 37.78
2021-03-20 08:00 | 44275.3333 | 0 | 9.6786 | 37.78
2021-03-20 08:30 | 44275.3542 | 0 | 10.3647 | 37.78
2021-03-20 09:00 | 44275.375 | 0 | 10.1895 | 37.78
2021-03-20 09:30 | 44275.3958 | 0 | 10.392 | 37.78
2021-03-20 10:00 | 44275.4167 | 0 | 11.3106 | 37.78
2021-03-20 10:30 | 44275.4375 | 0 | 10.9273 | 37.78
2021-03-20 11:00 | 44275.4583 | 0 | 9.6648 | 37.78
2021-03-20 11:30 | 44275.4792 | 0 | 10.8357 | 37.78
2021-03-20 12:00 | 44275.5 | 0 | 11.323 | 37.78
2021-03-20 12:30 | 44275.5208 | 0 | 9.0735 | 37.78
2021-03-20 13:00 | 44275.5417 | 0 | 12.1273 | 37.78
2021-03-20 13:30 | 44275.5625 | 0 | 13.0313 | 37.78
2021-03-20 14:00 | 44275.5833 | 0 | 12.8084 | 37.78
2021-03-20 14:30 | 44275.6042 | 0 | 12.8686 | 37.78
2021-03-20 15:00 | 44275.625 | 0 | 13.061 | 37.78
2021-03-20 15:30 | 44275.6458 | 0 | 12.6251 | 37.78
2021-03-20 16:00 | 44275.6667 | 0 | 12.6989 | 37.78
2021-03-20 16:30 | 44275.6875 | 0 | 12.8378 | 37.78
2021-03-20 17:00 | 44275.7083 | 0 | 12.9367 | 37.78
2021-03-20 17:30 | 44275.7292 | 0 | 13.1861 | 37.78
2021-03-20 18:00 | 44275.75 | 0 | 13.4298 | 37.78
2021-03-20 18:30 | 44275.7708 | 0 | 13.7529 | 37.78
2021-03-20 19:00 | 44275.7917 | 0 | 13.1034 | 37.78
2021-03-20 19:30 | 44275.8125 | 0 | 12.705 | 37.78
2021-03-20 20:00 | 44275.8333 | 0 | 12.507 | 37.78
2021-03-20 20:30 | 44275.8542 | 0 | 11.9278 | 37.78
2021-03-20 21:00 | 44275.875 | 0 | 11.3172 | 37.78
2021-03-20 21:30 | 44275.8958 | 0 | 11.0734 | 37.78
2021-03-20 22:00 | 44275.9167 | 0 | 10.4976 | 37.78
2021-03-20 22:30 | 44275.9375 | 0 | 9.7708 | 37.78
2021-03-20 23:00 | 44275.9583 | 0 | 9.2645 | 37.78
2021-03-20 23:30 | 44275.9792 | 0 | 9.0003 | 37.78
2021-03-21 | 44276 | 0 | 8.8738 | 37.78
2021-03-21 00:30 | 44276.0208 | 0 | 8.6033 | 37.78
2021-03-21 01:00 | 44276.0417 | 0 | 8.4623 | 37.78
2021-03-21 01:30 | 44276.0625 | 0 | 8.3592 | 37.78
2021-03-21 02:00 | 44276.0833 | 0 | 8.3804 | 37.78
2021-03-21 02:30 | 44276.1042 | 0 | 8.3497 | 37.78
2021-03-21 03:00 | 44276.125 | 0 | 8.2075 | 37.78
2021-03-21 03:30 | 44276.1458 | 0 | 8.4063 | 37.78
2021-03-21 04:00 | 44276.1667 | 0 | 8.6748 | 37.78
2021-03-21 04:30 | 44276.1875 | 0 | 9.143 | 37.78
2021-03-21 05:00 | 44276.2083 | 0 | 9.6788 | 37.78
2021-03-21 05:30 | 44276.2292 | 0 | 10.4317 | 37.78
2021-03-21 06:00 | 44276.25 | 0 | 11.3006 | 37.78
2021-03-21 06:30 | 44276.2708 | 0 | 12.3161 | 37.78
2021-03-21 07:00 | 44276.2917 | 0 | 13.3273 | 37.78
2021-03-21 07:30 | 44276.3125 | 0 | 13.7454 | 37.78
2021-03-21 08:00 | 44276.3333 | 0 | 13.7313 | 37.78
2021-03-21 08:30 | 44276.3542 | 0 | 13.964 | 37.78
2021-03-21 09:00 | 44276.375 | 0 | 13.9651 | 37.78
2021-03-21 09:30 | 44276.3958 | 0 | 13.945 | 37.78
2021-03-21 10:00 | 44276.4167 | 0 | 13.6503 | 37.78
2021-03-21 10:30 | 44276.4375 | 0 | 13.9253 | 37.78
2021-03-21 11:00 | 44276.4583 | 0 | 13.5514 | 37.78
2021-03-21 11:30 | 44276.4792 | 0 | 13.8642 | 37.78
2021-03-21 12:00 | 44276.5 | 0 | 13.7684 | 37.78
2021-03-21 12:30 | 44276.5208 | 0 | 13.6589 | 37.78
2021-03-21 13:00 | 44276.5417 | 0 | 13.7254 | 37.78
2021-03-21 13:30 | 44276.5625 | 0 | 13.589 | 37.78
2021-03-21 14:00 | 44276.5833 | 0 | 14.2228 | 37.78
2021-03-21 14:30 | 44276.6042 | 0 | 14.263 | 37.78
2021-03-21 15:00 | 44276.625 | 0 | 13.7069 | 37.78
2021-03-21 15:30 | 44276.6458 | 0 | 14.0075 | 37.78
2021-03-21 16:00 | 44276.6667 | 0 | 13.7539 | 37.78
2021-03-21 16:30 | 44276.6875 | 0 | 14.2991 | 37.78
2021-03-21 17:00 | 44276.7083 | 0 | 14.2807 | 37.78
2021-03-21 17:30 | 44276.7292 | 0 | 14.4986 | 37.78
2021-03-21 18:00 | 44276.75 | 0 | 14.7702 | 37.78
2021-03-21 18:30 | 44276.7708 | 0 | 14.8824 | 37.78
2021-03-21 19:00 | 44276.7917 | 0 | 14.4754 | 37.78
2021-03-21 19:30 | 44276.8125 | 0 | 14.2333 | 37.78
2021-03-21 20:00 | 44276.8333 | 0 | 14.0164 | 37.78
2021-03-21 20:30 | 44276.8542 | 0 | 13.3274 | 37.78
2021-03-21 21:00 | 44276.875 | 0 | 12.927 | 37.78
2021-03-21 21:30 | 44276.8958 | 0 | 12.6065 | 37.78
2021-03-21 22:00 | 44276.9167 | 0 | 12.0628 | 37.78
2021-03-21 22:30 | 44276.9375 | 0 | 11.1575 | 37.78
2021-03-21 23:00 | 44276.9583 | 0 | 10.6752 | 37.78
2021-03-21 23:30 | 44276.9792 | 0 | 10.2436 | 37.78
2021-03-22 | 44277 | 0 | 9.7275 | 37.78
2021-03-22 00:30 | 44277.0208 | 0 | 9.2303 | 37.78
2021-03-22 01:00 | 44277.0417 | 0 | 8.9454 | 37.78
2021-03-22 01:30 | 44277.0625 | 0 | 9.0215 | 37.78
2021-03-22 02:00 | 44277.0833 | 0 | 9.0127 | 37.78
2021-03-22 02:30 | 44277.1042 | 0 | 8.8528 | 37.78
2021-03-22 03:00 | 44277.125 | 0 | 8.7273 | 37.78
2021-03-22 03:30 | 44277.1458 | 0 | 8.9576 | 37.78
2021-03-22 04:00 | 44277.1667 | 0 | 9.1163 | 37.78
2021-03-22 04:30 | 44277.1875 | 0 | 9.7327 | 37.78
2021-03-22 05:00 | 44277.2083 | 0 | 10.5967 | 37.78
2021-03-22 05:30 | 44277.2292 | 0 | 11.2782 | 37.78
2021-03-22 06:00 | 44277.25 | 0 | 12.2967 | 37.78
2021-03-22 06:30 | 44277.2708 | 0 | 12.877 | 37.78
2021-03-22 07:00 | 44277.2917 | 0 | 13.6135 | 37.78
2021-03-22 07:30 | 44277.3125 | 0 | 14.4057 | 37.78
2021-03-22 08:00 | 44277.3333 | 0 | 14.7817 | 37.78
2021-03-22 08:30 | 44277.3542 | 0 | 14.7439 | 37.78
2021-03-22 09:00 | 44277.375 | 0 | 14.9364 | 37.78
2021-03-22 09:30 | 44277.3958 | 0 | 15.2334 | 37.78
2021-03-22 10:00 | 44277.4167 | 0 | 15.204 | 37.78
2021-03-22 10:30 | 44277.4375 | 0 | 14.8966 | 37.78
2021-03-22 11:00 | 44277.4583 | 0 | 14.278 | 37.78
2021-03-22 11:30 | 44277.4792 | 0 | 14.2586 | 37.78
2021-03-22 12:00 | 44277.5 | 0 | 14.7267 | 37.78
2021-03-22 12:30 | 44277.5208 | 0 | 14.0187 | 37.78
2021-03-22 13:00 | 44277.5417 | 0 | 14.0164 | 37.78
2021-03-22 13:30 | 44277.5625 | 0 | 14.2986 | 37.78
2021-03-22 14:00 | 44277.5833 | 0 | 14.0495 | 37.78
2021-03-22 14:30 | 44277.6042 | 0 | 14.2668 | 37.78
2021-03-22 15:00 | 44277.625 | 0 | 14.6505 | 37.78
2021-03-22 15:30 | 44277.6458 | 0 | 14.6634 | 37.78
2021-03-22 16:00 | 44277.6667 | 0 | 14.3711 | 37.78
2021-03-22 16:30 | 44277.6875 | 0 | 14.5132 | 37.78
2021-03-22 17:00 | 44277.7083 | 0 | 14.7719 | 37.78
2021-03-22 17:30 | 44277.7292 | 0 | 15.2047 | 37.78
2021-03-22 18:00 | 44277.75 | 0 | 15.735 | 37.78
2021-03-22 18:30 | 44277.7708 | 0 | 16.0488 | 37.78
2021-03-22 19:00 | 44277.7917 | 0 | 15.8001 | 37.78
2021-03-22 19:30 | 44277.8125 | 0 | 15.6061 | 37.78
2021-03-22 20:00 | 44277.8333 | 0 | 15.2296 | 37.78
2021-03-22 20:30 | 44277.8542 | 0 | 14.6842 | 37.78
2021-03-22 21:00 | 44277.875 | 0 | 14.1439 | 37.78
2021-03-22 21:30 | 44277.8958 | 0 | 13.6567 | 37.78
2021-03-22 22:00 | 44277.9167 | 0 | 12.945 | 37.78
2021-03-22 22:30 | 44277.9375 | 0 | 11.9927 | 37.78
2021-03-22 23:00 | 44277.9583 | 0 | 11.4703 | 37.78
2021-03-22 23:30 | 44277.9792 | 0 | 10.9832 | 37.78
2021-03-23 | 44278 | 0 | 10.3878 | 37.78
2021-03-23 00:30 | 44278.0208 | 0 | 9.8459 | 37.78
2021-03-23 01:00 | 44278.0417 | 0 | 9.545 | 37.78
2021-03-23 01:30 | 44278.0625 | 0 | 9.4213 | 37.78
2021-03-23 02:00 | 44278.0833 | 0 | 9.3263 | 37.78
2021-03-23 02:30 | 44278.1042 | 0 | 9.1134 | 37.78
2021-03-23 03:00 | 44278.125 | 0 | 8.9698 | 37.78
2021-03-23 03:30 | 44278.1458 | 0 | 9.1399 | 37.78
2021-03-23 04:00 | 44278.1667 | 0 | 9.404 | 37.78
2021-03-23 04:30 | 44278.1875 | 0 | 9.6727 | 37.78
2021-03-23 05:00 | 44278.2083 | 0 | 10.2364 | 37.78
2021-03-23 05:30 | 44278.2292 | 0 | 10.7942 | 37.78
2021-03-23 06:00 | 44278.25 | 0 | 11.7715 | 37.78
2021-03-23 06:30 | 44278.2708 | 0 | 12.612 | 37.78
2021-03-23 07:00 | 44278.2917 | 0 | 12.7607 | 37.78
2021-03-23 07:30 | 44278.3125 | 0 | 13.9016 | 37.78
2021-03-23 08:00 | 44278.3333 | 0 | 13.6853 | 37.78
2021-03-23 08:30 | 44278.3542 | 0 | 13.6882 | 37.78
2021-03-23 09:00 | 44278.375 | 0 | 13.7536 | 37.78
2021-03-23 09:30 | 44278.3958 | 0 | 14.6518 | 37.78
2021-03-23 10:00 | 44278.4167 | 0 | 14.168 | 37.78
2021-03-23 10:30 | 44278.4375 | 0 | 15.4815 | 37.78
2021-03-23 11:00 | 44278.4583 | 0 | 15.8248 | 37.78
2021-03-23 11:30 | 44278.4792 | 0 | 13.8069 | 37.78
2021-03-23 12:00 | 44278.5 | 0 | 14.5314 | 37.78
2021-03-23 12:30 | 44278.5208 | 0 | 15.2871 | 37.78
2021-03-23 13:00 | 44278.5417 | 0 | 15.5338 | 37.78
2021-03-23 13:30 | 44278.5625 | 0 | 16.3739 | 37.78
2021-03-23 14:00 | 44278.5833 | 0 | 15.62 | 37.78
2021-03-23 14:30 | 44278.6042 | 0 | 15.2904 | 37.78
2021-03-23 15:00 | 44278.625 | 0 | 15.3347 | 37.78
2021-03-23 15:30 | 44278.6458 | 0 | 16.0344 | 37.78
2021-03-23 16:00 | 44278.6667 | 0 | 16.1559 | 37.78
2021-03-23 16:30 | 44278.6875 | 0 | 16.5806 | 37.78
2021-03-23 17:00 | 44278.7083 | 0 | 16.784 | 37.78
2021-03-23 17:30 | 44278.7292 | 0 | 16.7276 | 37.78
2021-03-23 18:00 | 44278.75 | 0 | 16.7237 | 37.78
2021-03-23 18:30 | 44278.7708 | 0 | 16.9512 | 37.78
2021-03-23 19:00 | 44278.7917 | 0 | 16.528 | 37.78
2021-03-23 19:30 | 44278.8125 | 0 | 16.0137 | 37.78
2021-03-23 20:00 | 44278.8333 | 0 | 15.4773 | 37.78
2021-03-23 20:30 | 44278.8542 | 0 | 14.9096 | 37.78
2021-03-23 21:00 | 44278.875 | 0 | 14.2355 | 37.78
2021-03-23 21:30 | 44278.8958 | 0 | 13.5228 | 37.78
2021-03-23 22:00 | 44278.9167 | 0 | 12.8442 | 37.78
2021-03-23 22:30 | 44278.9375 | 0 | 11.7384 | 37.78
2021-03-23 23:00 | 44278.9583 | 0 | 10.9296 | 37.78
2021-03-23 23:30 | 44278.9792 | 0 | 10.4553 | 37.78
2021-03-24 | 44279 | 0 | 9.7626 | 37.78
2021-03-24 00:30 | 44279.0208 | 0 | 9.2688 | 37.78
2021-03-24 01:00 | 44279.0417 | 0 | 9.0928 | 37.78
2021-03-24 01:30 | 44279.0625 | 0 | 8.8169 | 37.78
2021-03-24 02:00 | 44279.0833 | 0 | 8.7316 | 37.78
2021-03-24 02:30 | 44279.1042 | 0 | 8.599 | 37.78
2021-03-24 03:00 | 44279.125 | 0 | 8.4548 | 37.78
2021-03-24 03:30 | 44279.1458 | 0 | 8.592 | 37.78
2021-03-24 04:00 | 44279.1667 | 0 | 8.7331 | 37.78
2021-03-24 04:30 | 44279.1875 | 0 | 9.1522 | 37.78
2021-03-24 05:00 | 44279.2083 | 0 | 9.652 | 37.78
2021-03-24 05:30 | 44279.2292 | 0 | 10.2091 | 37.78
2021-03-24 06:00 | 44279.25 | 0 | 10.967 | 37.78
2021-03-24 06:30 | 44279.2708 | 0 | 11.4322 | 37.78
2021-03-24 07:00 | 44279.2917 | 0 | 11.8347 | 37.78
2021-03-24 07:30 | 44279.3125 | 0 | 11.9099 | 37.78
2021-03-24 08:00 | 44279.3333 | 0 | 11.8916 | 37.78
2021-03-24 08:30 | 44279.3542 | 0 | 11.7522 | 37.78
2021-03-24 09:00 | 44279.375 | 0 | 11.694 | 37.78
2021-03-24 09:30 | 44279.3958 | 0 | 11.9514 | 37.78
2021-03-24 10:00 | 44279.4167 | 0 | 11.4368 | 37.78
2021-03-24 10:30 | 44279.4375 | 0 | 11.5557 | 37.78
2021-03-24 11:00 | 44279.4583 | 0 | 11.5525 | 37.78
2021-03-24 11:30 | 44279.4792 | 0 | 11.6761 | 37.78
2021-03-24 12:00 | 44279.5 | 0 | 11.8165 | 37.78
2021-03-24 12:30 | 44279.5208 | 0 | 12.019 | 37.78
2021-03-24 13:00 | 44279.5417 | 0 | 12.2113 | 37.78
2021-03-24 13:30 | 44279.5625 | 0 | 12.9876 | 37.78
2021-03-24 14:00 | 44279.5833 | 0 | 13.4571 | 37.78
2021-03-24 14:30 | 44279.6042 | 0 | 13.8412 | 37.78
2021-03-24 15:00 | 44279.625 | 0 | 14.3752 | 37.78
2021-03-24 15:30 | 44279.6458 | 0 | 15.1475 | 37.78
2021-03-24 16:00 | 44279.6667 | 0 | 15.6352 | 37.78
2021-03-24 16:30 | 44279.6875 | 0 | 16.2616 | 37.78
2021-03-24 17:00 | 44279.7083 | 0 | 16.3281 | 37.78
2021-03-24 17:30 | 44279.7292 | 0 | 16.1588 | 37.78
2021-03-24 18:00 | 44279.75 | 0 | 16.2355 | 37.78
2021-03-24 18:30 | 44279.7708 | 0 | 16.5454 | 37.78
2021-03-24 19:00 | 44279.7917 | 0 | 16.012 | 37.78
2021-03-24 19:30 | 44279.8125 | 0 | 15.579 | 37.78
2021-03-24 20:00 | 44279.8333 | 0 | 15.2135 | 37.78
2021-03-24 20:30 | 44279.8542 | 0 | 14.4382 | 37.78
2021-03-24 21:00 | 44279.875 | 0 | 13.9171 | 37.78
2021-03-24 21:30 | 44279.8958 | 0 | 13.2774 | 37.78
2021-03-24 22:00 | 44279.9167 | 0 | 12.7106 | 37.78
2021-03-24 22:30 | 44279.9375 | 0 | 11.642 | 37.78
2021-03-24 23:00 | 44279.9583 | 0 | 10.7985 | 37.78
2021-03-24 23:30 | 44279.9792 | 0 | 10.2961 | 37.78
2021-03-25 | 44280 | 0 | 9.5037 | 37.78
2021-03-25 00:30 | 44280.0208 | 0 | 9.1117 | 37.78
2021-03-25 01:00 | 44280.0417 | 0 | 9.0017 | 37.78
2021-03-25 01:30 | 44280.0625 | 0 | 8.7607 | 37.78
2021-03-25 02:00 | 44280.0833 | 0 | 8.687 | 37.78
2021-03-25 02:30 | 44280.1042 | 0 | 8.5507 | 37.78
2021-03-25 03:00 | 44280.125 | 0 | 8.4413 | 37.78
2021-03-25 03:30 | 44280.1458 | 0 | 8.4979 | 37.78
2021-03-25 04:00 | 44280.1667 | 0 | 8.811 | 37.78
2021-03-25 04:30 | 44280.1875 | 0 | 9.1624 | 37.78
2021-03-25 05:00 | 44280.2083 | 0 | 9.6263 | 37.78
2021-03-25 05:30 | 44280.2292 | 0 | 10.2666 | 37.78
2021-03-25 06:00 | 44280.25 | 0 | 10.8932 | 37.78
2021-03-25 06:30 | 44280.2708 | 0 | 11.3034 | 37.78
2021-03-25 07:00 | 44280.2917 | 0 | 11.6709 | 37.78
2021-03-25 07:30 | 44280.3125 | 0 | 11.7136 | 37.78
2021-03-25 08:00 | 44280.3333 | 0 | 11.7138 | 37.78
2021-03-25 08:30 | 44280.3542 | 0 | 11.6514 | 37.78
2021-03-25 09:00 | 44280.375 | 0 | 11.4172 | 37.78
2021-03-25 09:30 | 44280.3958 | 0 | 11.3633 | 37.78
2021-03-25 10:00 | 44280.4167 | 0 | 11.1974 | 37.78
2021-03-25 10:30 | 44280.4375 | 0 | 11.3057 | 37.78
2021-03-25 11:00 | 44280.4583 | 0 | 11.4983 | 37.78
2021-03-25 11:30 | 44280.4792 | 0 | 11.8106 | 37.78
2021-03-25 12:00 | 44280.5 | 0 | 12.0034 | 37.78
2021-03-25 12:30 | 44280.5208 | 0 | 13.2628 | 37.78
2021-03-25 13:00 | 44280.5417 | 0 | 12.9325 | 37.78
2021-03-25 13:30 | 44280.5625 | 0 | 13.788 | 37.78
2021-03-25 14:00 | 44280.5833 | 0 | 13.0994 | 37.78
2021-03-25 14:30 | 44280.6042 | 0 | 13.4307 | 37.78
2021-03-25 15:00 | 44280.625 | 0 | 13.5872 | 37.78
2021-03-25 15:30 | 44280.6458 | 0 | 14.8599 | 37.78
2021-03-25 16:00 | 44280.6667 | 0 | 15.4288 | 37.78
2021-03-25 16:30 | 44280.6875 | 0 | 15.3631 | 37.78
2021-03-25 17:00 | 44280.7083 | 0 | 15.6223 | 37.78
2021-03-25 17:30 | 44280.7292 | 0 | 15.4905 | 37.78
2021-03-25 18:00 | 44280.75 | 0 | 15.3881 | 37.78
2021-03-25 18:30 | 44280.7708 | 0 | 15.6674 | 37.78
2021-03-25 19:00 | 44280.7917 | 0 | 15.3966 | 37.78
2021-03-25 19:30 | 44280.8125 | 0 | 15.0744 | 37.78
2021-03-25 20:00 | 44280.8333 | 0 | 14.7139 | 37.78
2021-03-25 20:30 | 44280.8542 | 0 | 14.1372 | 37.78
2021-03-25 21:00 | 44280.875 | 0 | 13.5046 | 37.78
2021-03-25 21:30 | 44280.8958 | 0 | 13.1496 | 37.78
2021-03-25 22:00 | 44280.9167 | 0 | 12.4327 | 37.78
2021-03-25 22:30 | 44280.9375 | 0 | 11.6594 | 37.78
2021-03-25 23:00 | 44280.9583 | 0 | 11.0575 | 37.78
2021-03-25 23:30 | 44280.9792 | 0 | 10.5544 | 37.78
2021-03-26 | 44281 | 0 | 9.8318 | 37.78
2021-03-26 00:30 | 44281.0208 | 0 | 9.2067 | 37.78
2021-03-26 01:00 | 44281.0417 | 0 | 9.1808 | 37.78
2021-03-26 01:30 | 44281.0625 | 0 | 8.9795 | 37.78
2021-03-26 02:00 | 44281.0833 | 0 | 9.0652 | 37.78
2021-03-26 02:30 | 44281.1042 | 0 | 8.7522 | 37.78
2021-03-26 03:00 | 44281.125 | 0 | 8.7437 | 37.78
2021-03-26 03:30 | 44281.1458 | 0 | 8.8994 | 37.78
2021-03-26 04:00 | 44281.1667 | 0 | 8.9811 | 37.78
2021-03-26 04:30 | 44281.1875 | 0 | 8.9966 | 37.78
2021-03-26 05:00 | 44281.2083 | 0 | 9.0968 | 37.78
2021-03-26 05:30 | 44281.2292 | 0 | 9.1678 | 37.78
2021-03-26 06:00 | 44281.25 | 0 | 9.3327 | 37.78
2021-03-26 06:30 | 44281.2708 | 0 | 9.4836 | 37.78
2021-03-26 07:00 | 44281.2917 | 0 | 9.596 | 37.78
2021-03-26 07:30 | 44281.3125 | 0 | 9.3756 | 37.78
2021-03-26 08:00 | 44281.3333 | 0 | 9.4293 | 37.78
2021-03-26 08:30 | 44281.3542 | 0 | 9.4454 | 37.78
2021-03-26 09:00 | 44281.375 | 0 | 9.5411 | 37.78
2021-03-26 09:30 | 44281.3958 | 0 | 10.0125 | 37.78
2021-03-26 10:00 | 44281.4167 | 0 | 10.3134 | 37.78
2021-03-26 10:30 | 44281.4375 | 0 | 10.3354 | 37.78
2021-03-26 11:00 | 44281.4583 | 0 | 11.6238 | 37.78
2021-03-26 11:30 | 44281.4792 | 0 | 10.5698 | 37.78
2021-03-26 12:00 | 44281.5 | 0 | 11.8548 | 37.78
2021-03-26 12:30 | 44281.5208 | 0 | 10.5086 | 37.78
2021-03-26 13:00 | 44281.5417 | 0 | 11.775 | 37.78
2021-03-26 13:30 | 44281.5625 | 0 | 11.0227 | 37.78
2021-03-26 14:00 | 44281.5833 | 0 | 11.7084 | 37.78
2021-03-26 14:30 | 44281.6042 | 0 | 13.3369 | 37.78
2021-03-26 15:00 | 44281.625 | 0 | 13.0655 | 37.78
2021-03-26 15:30 | 44281.6458 | 0 | 12.3124 | 37.78
2021-03-26 16:00 | 44281.6667 | 0 | 13.0964 | 37.78
2021-03-26 16:30 | 44281.6875 | 0 | 13.4456 | 37.78
2021-03-26 17:00 | 44281.7083 | 0 | 13.5681 | 37.78
2021-03-26 17:30 | 44281.7292 | 0 | 13.6542 | 37.78
2021-03-26 18:00 | 44281.75 | 0 | 14.0216 | 37.78
2021-03-26 18:30 | 44281.7708 | 0 | 13.9947 | 37.78
2021-03-26 19:00 | 44281.7917 | 0 | 13.7542 | 37.78
2021-03-26 19:30 | 44281.8125 | 0 | 13.5643 | 37.78
2021-03-26 20:00 | 44281.8333 | 0 | 13.2131 | 37.78
2021-03-26 20:30 | 44281.8542 | 0 | 12.6812 | 37.78
2021-03-26 21:00 | 44281.875 | 0 | 11.9653 | 37.78
2021-03-26 21:30 | 44281.8958 | 0 | 11.6831 | 37.78
2021-03-26 22:00 | 44281.9167 | 0 | 11.4948 | 37.78
2021-03-26 22:30 | 44281.9375 | 0 | 10.6276 | 37.78
2021-03-26 23:00 | 44281.9583 | 0 | 10.0547 | 37.78
2021-03-26 23:30 | 44281.9792 | 0 | 9.492 | 37.78
2021-03-27 | 44282 | 0 | 9.077 | 37.78
2021-03-27 00:30 | 44282.0208 | 0 | 8.786 | 37.78
2021-03-27 01:00 | 44282.0417 | 0 | 8.4959 | 37.78
2021-03-27 01:30 | 44282.0625 | 0 | 8.2385 | 37.78
2021-03-27 02:00 | 44282.0833 | 0 | 8.2276 | 37.78
2021-03-27 02:30 | 44282.1042 | 0 | 8.1027 | 37.78
2021-03-27 03:00 | 44282.125 | 0 | 7.8571 | 37.78
2021-03-27 03:30 | 44282.1458 | 0 | 7.8033 | 37.78
2021-03-27 04:00 | 44282.1667 | 0 | 7.7765 | 37.78
2021-03-27 04:30 | 44282.1875 | 0 | 7.7275 | 37.78
2021-03-27 05:00 | 44282.2083 | 0 | 7.7345 | 37.78
2021-03-27 05:30 | 44282.2292 | 0 | 7.8598 | 37.78
2021-03-27 06:00 | 44282.25 | 0 | 7.781 | 37.78
2021-03-27 06:30 | 44282.2708 | 0 | 7.8435 | 37.78
2021-03-27 07:00 | 44282.2917 | 0 | 7.6461 | 37.78
2021-03-27 07:30 | 44282.3125 | 0 | 7.6929 | 37.78
2021-03-27 08:00 | 44282.3333 | 0 | 7.7566 | 37.78
2021-03-27 08:30 | 44282.3542 | 0 | 7.8738 | 37.78
2021-03-27 09:00 | 44282.375 | 0 | 7.7472 | 37.78
2021-03-27 09:30 | 44282.3958 | 0 | 7.7718 | 37.78
2021-03-27 10:00 | 44282.4167 | 0 | 7.5836 | 37.78
2021-03-27 10:30 | 44282.4375 | 0 | 7.6978 | 37.78
2021-03-27 11:00 | 44282.4583 | 0 | 7.936 | 37.78
2021-03-27 11:30 | 44282.4792 | 0 | 8.9479 | 37.78
2021-03-27 12:00 | 44282.5 | 0 | 8.4828 | 37.78
2021-03-27 12:30 | 44282.5208 | 0 | 8.2635 | 37.78
2021-03-27 13:00 | 44282.5417 | 0 | 8.8186 | 37.78
2021-03-27 13:30 | 44282.5625 | 0 | 9.5362 | 37.78
2021-03-27 14:00 | 44282.5833 | 0 | 10.4957 | 37.78
2021-03-27 14:30 | 44282.6042 | 0 | 12.2492 | 37.78
2021-03-27 15:00 | 44282.625 | 0 | 11.7479 | 37.78
2021-03-27 15:30 | 44282.6458 | 0 | 12.2738 | 37.78
2021-03-27 16:00 | 44282.6667 | 0 | 12.6948 | 37.78
2021-03-27 16:30 | 44282.6875 | 0 | 13.4342 | 37.78
2021-03-27 17:00 | 44282.7083 | 0 | 13.7337 | 37.78
2021-03-27 17:30 | 44282.7292 | 0 | 14.078 | 37.78
2021-03-27 18:00 | 44282.75 | 0 | 14.5421 | 37.78
2021-03-27 18:30 | 44282.7708 | 0 | 14.6094 | 37.78
2021-03-27 19:00 | 44282.7917 | 0 | 14.302 | 37.78
2021-03-27 19:30 | 44282.8125 | 0 | 13.9709 | 37.78
2021-03-27 20:00 | 44282.8333 | 0 | 13.5054 | 37.78
2021-03-27 20:30 | 44282.8542 | 0 | 12.993 | 37.78
2021-03-27 21:00 | 44282.875 | 0 | 12.5262 | 37.78
2021-03-27 21:30 | 44282.8958 | 0 | 11.9999 | 37.78
2021-03-27 22:00 | 44282.9167 | 0 | 11.3981 | 37.78
2021-03-27 22:30 | 44282.9375 | 0 | 10.3871 | 37.78
2021-03-27 23:00 | 44282.9583 | 0 | 9.8639 | 37.78
2021-03-27 23:30 | 44282.9792 | 0 | 9.5464 | 37.78
2021-03-28 | 44283 | 0 | 9.2299 | 37.78
2021-03-28 00:30 | 44283.0208 | 0 | 9.0254 | 37.78
2021-03-28 01:00 | 44283.0417 | 0 | 8.7901 | 37.78
2021-03-28 01:30 | 44283.0625 | 0 | 8.5809 | 37.78
2021-03-28 02:00 | 44283.0833 | 0 | 8.4711 | 37.78
2021-03-28 02:30 | 44283.1042 | 0 | 8.3852 | 37.78
2021-03-28 03:00 | 44283.125 | 0 | 8.204 | 37.78
2021-03-28 03:30 | 44283.1458 | 0 | 8.3704 | 37.78
2021-03-28 04:00 | 44283.1667 | 0 | 8.4291 | 37.78
2021-03-28 04:30 | 44283.1875 | 0 | 8.8046 | 37.78
2021-03-28 05:00 | 44283.2083 | 0 | 9.2734 | 37.78
2021-03-28 05:30 | 44283.2292 | 0 | 9.8809 | 37.78
2021-03-28 06:00 | 44283.25 | 0 | 10.6515 | 37.78
2021-03-28 06:30 | 44283.2708 | 0 | 11.4546 | 37.78
2021-03-28 07:00 | 44283.2917 | 0 | 11.8845 | 37.78
2021-03-28 07:30 | 44283.3125 | 0 | 12.0245 | 37.78
2021-03-28 08:00 | 44283.3333 | 0 | 11.9568 | 37.78
2021-03-28 08:30 | 44283.3542 | 0 | 11.7666 | 37.78
2021-03-28 09:00 | 44283.375 | 0 | 11.854 | 37.78
2021-03-28 09:30 | 44283.3958 | 0 | 12.0842 | 37.78
2021-03-28 10:00 | 44283.4167 | 0 | 12.3395 | 37.78
2021-03-28 10:30 | 44283.4375 | 0 | 12.9818 | 37.78
2021-03-28 11:00 | 44283.4583 | 0 | 13.0391 | 37.78
2021-03-28 11:30 | 44283.4792 | 0 | 12.8387 | 37.78
2021-03-28 12:00 | 44283.5 | 0 | 13.503 | 37.78
2021-03-28 12:30 | 44283.5208 | 0 | 14.2453 | 37.78
2021-03-28 13:00 | 44283.5417 | 0 | 14.5546 | 37.78
2021-03-28 13:30 | 44283.5625 | 0 | 13.4453 | 37.78
2021-03-28 14:00 | 44283.5833 | 0 | 14.7246 | 37.78
2021-03-28 14:30 | 44283.6042 | 0 | 15.2936 | 37.78
2021-03-28 15:00 | 44283.625 | 0 | 16.4811 | 37.78
2021-03-28 15:30 | 44283.6458 | 0 | 14.8438 | 37.78
2021-03-28 16:00 | 44283.6667 | 0 | 15.4141 | 37.78
2021-03-28 16:30 | 44283.6875 | 0 | 15.7719 | 37.78
2021-03-28 17:00 | 44283.7083 | 0 | 15.9236 | 37.78
2021-03-28 17:30 | 44283.7292 | 0 | 15.6597 | 37.78
2021-03-28 18:00 | 44283.75 | 0 | 15.8282 | 37.78
2021-03-28 18:30 | 44283.7708 | 0 | 16.0009 | 37.78
2021-03-28 19:00 | 44283.7917 | 0 | 15.3231 | 37.78
2021-03-28 19:30 | 44283.8125 | 0 | 15.0043 | 37.78
2021-03-28 20:00 | 44283.8333 | 0 | 14.3181 | 37.78
2021-03-28 20:30 | 44283.8542 | 0 | 13.8558 | 37.78
2021-03-28 21:00 | 44283.875 | 0 | 13.1129 | 37.78
2021-03-28 21:30 | 44283.8958 | 0 | 12.8035 | 37.78
2021-03-28 22:00 | 44283.9167 | 0 | 12.2603 | 37.78
2021-03-28 22:30 | 44283.9375 | 0 | 11.3405 | 37.78
2021-03-28 23:00 | 44283.9583 | 0 | 10.6604 | 37.78
2021-03-28 23:30 | 44283.9792 | 0 | 10.3345 | 37.78
2021-03-29 | 44284 | 0 | 9.821 | 37.78
2021-03-29 00:30 | 44284.0208 | 0 | 9.3595 | 37.78
2021-03-29 01:00 | 44284.0417 | 0 | 9.0552 | 37.78
2021-03-29 01:30 | 44284.0625 | 0 | 8.9759 | 37.78
2021-03-29 02:00 | 44284.0833 | 0 | 8.8483 | 37.78
2021-03-29 02:30 | 44284.1042 | 0 | 8.7675 | 37.78
2021-03-29 03:00 | 44284.125 | 0 | 8.6725 | 37.78
2021-03-29 03:30 | 44284.1458 | 0 | 8.8384 | 37.78
2021-03-29 04:00 | 44284.1667 | 0 | 8.8982 | 37.78
2021-03-29 04:30 | 44284.1875 | 0 | 9.5056 | 37.78
2021-03-29 05:00 | 44284.2083 | 0 | 9.8717 | 37.78
2021-03-29 05:30 | 44284.2292 | 0 | 10.2705 | 37.78
2021-03-29 06:00 | 44284.25 | 0 | 10.8062 | 37.78
2021-03-29 06:30 | 44284.2708 | 0 | 11.2076 | 37.78
2021-03-29 07:00 | 44284.2917 | 0 | 11.3533 | 37.78
2021-03-29 07:30 | 44284.3125 | 0 | 11.974 | 37.78
2021-03-29 08:00 | 44284.3333 | 0 | 11.429 | 37.78
2021-03-29 08:30 | 44284.3542 | 0 | 13.151 | 37.78
2021-03-29 09:00 | 44284.375 | 0 | 13.0773 | 37.78
2021-03-29 09:30 | 44284.3958 | 0 | 12.3045 | 37.78
2021-03-29 10:00 | 44284.4167 | 0 | 12.5285 | 37.78
2021-03-29 10:30 | 44284.4375 | 0 | 11.7212 | 37.78
2021-03-29 11:00 | 44284.4583 | 0 | 11.4078 | 37.78
2021-03-29 11:30 | 44284.4792 | 0 | 10.7341 | 37.78
2021-03-29 12:00 | 44284.5 | 0 | 11.6936 | 37.78
2021-03-29 12:30 | 44284.5208 | 0 | 12.8372 | 37.78
2021-03-29 13:00 | 44284.5417 | 0 | 12.8868 | 37.78
2021-03-29 13:30 | 44284.5625 | 0 | 13.0367 | 37.78
2021-03-29 14:00 | 44284.5833 | 0 | 12.7094 | 37.78
2021-03-29 14:30 | 44284.6042 | 0 | 11.8907 | 37.78
2021-03-29 15:00 | 44284.625 | 0 | 12.1384 | 37.78
2021-03-29 15:30 | 44284.6458 | 0 | 13.4554 | 37.78
2021-03-29 16:00 | 44284.6667 | 0 | 13.1346 | 37.78
2021-03-29 16:30 | 44284.6875 | 0 | 13.1598 | 37.78
2021-03-29 17:00 | 44284.7083 | 0 | 13.7389 | 37.78
2021-03-29 17:30 | 44284.7292 | 0 | 13.7807 | 37.78
2021-03-29 18:00 | 44284.75 | 0 | 14.2551 | 37.78
2021-03-29 18:30 | 44284.7708 | 0 | 14.5134 | 37.78
2021-03-29 19:00 | 44284.7917 | 0 | 13.9331 | 37.78
2021-03-29 19:30 | 44284.8125 | 0 | 13.5245 | 37.78
2021-03-29 20:00 | 44284.8333 | 0 | 13.0304 | 37.78
2021-03-29 20:30 | 44284.8542 | 0 | 12.4971 | 37.78
2021-03-29 21:00 | 44284.875 | 0 | 12.058 | 37.78
2021-03-29 21:30 | 44284.8958 | 0 | 11.5311 | 37.78
2021-03-29 22:00 | 44284.9167 | 0 | 11.2067 | 37.78
2021-03-29 22:30 | 44284.9375 | 0 | 10.3309 | 37.78
2021-03-29 23:00 | 44284.9583 | 0 | 9.8215 | 37.78
2021-03-29 23:30 | 44284.9792 | 0 | 9.5573 | 37.78
2021-03-30 | 44285 | 0 | 8.8347 | 37.78
2021-03-30 00:30 | 44285.0208 | 0 | 8.6357 | 37.78
2021-03-30 01:00 | 44285.0417 | 0 | 8.4224 | 37.78
2021-03-30 01:30 | 44285.0625 | 0 | 8.1705 | 37.78
2021-03-30 02:00 | 44285.0833 | 0 | 8.0709 | 37.78
2021-03-30 02:30 | 44285.1042 | 0 | 8.1142 | 37.78
2021-03-30 03:00 | 44285.125 | 0 | 8.0305 | 37.78
2021-03-30 03:30 | 44285.1458 | 0 | 8.0932 | 37.78
2021-03-30 04:00 | 44285.1667 | 0 | 8.2163 | 37.78
2021-03-30 04:30 | 44285.1875 | 0 | 8.5845 | 37.78
2021-03-30 05:00 | 44285.2083 | 0 | 9.0494 | 37.78
2021-03-30 05:30 | 44285.2292 | 0 | 9.4382 | 37.78
2021-03-30 06:00 | 44285.25 | 0 | 10.0625 | 37.78
2021-03-30 06:30 | 44285.2708 | 0 | 10.2583 | 37.78
2021-03-30 07:00 | 44285.2917 | 0 | 10.6358 | 37.78
2021-03-30 07:30 | 44285.3125 | 0 | 10.4995 | 37.78
2021-03-30 08:00 | 44285.3333 | 0 | 10.6597 | 37.78
2021-03-30 08:30 | 44285.3542 | 0 | 10.484 | 37.78
2021-03-30 09:00 | 44285.375 | 0 | 10.0125 | 37.78
2021-03-30 09:30 | 44285.3958 | 0 | 10.261 | 37.78
2021-03-30 10:00 | 44285.4167 | 0 | 10.6639 | 37.78
2021-03-30 10:30 | 44285.4375 | 0 | 10.8204 | 37.78
2021-03-30 11:00 | 44285.4583 | 0 | 11.3737 | 37.78
2021-03-30 11:30 | 44285.4792 | 0 | 10.7904 | 37.78
2021-03-30 12:00 | 44285.5 | 0 | 11.5482 | 37.78
2021-03-30 12:30 | 44285.5208 | 0 | 12.5634 | 37.78
2021-03-30 13:00 | 44285.5417 | 0 | 12.7462 | 37.78
2021-03-30 13:30 | 44285.5625 | 0 | 10.2634 | 37.78
2021-03-30 14:00 | 44285.5833 | 0 | 11.6266 | 37.78
2021-03-30 14:30 | 44285.6042 | 0 | 11.8516 | 37.78
2021-03-30 15:00 | 44285.625 | 0 | 12.5894 | 37.78
2021-03-30 15:30 | 44285.6458 | 0 | 11.9051 | 37.78
2021-03-30 16:00 | 44285.6667 | 0 | 12.7378 | 37.78
2021-03-30 16:30 | 44285.6875 | 0 | 12.8871 | 37.78
2021-03-30 17:00 | 44285.7083 | 0 | 13.443 | 37.78
2021-03-30 17:30 | 44285.7292 | 0 | 13.7647 | 37.78
2021-03-30 18:00 | 44285.75 | 0 | 14.0179 | 37.78
2021-03-30 18:30 | 44285.7708 | 0 | 14.2064 | 37.78
2021-03-30 19:00 | 44285.7917 | 0 | 13.636 | 37.78
2021-03-30 19:30 | 44285.8125 | 0 | 13.2368 | 37.78
2021-03-30 20:00 | 44285.8333 | 0 | 12.7549 | 37.78
2021-03-30 20:30 | 44285.8542 | 0 | 12.0292 | 37.78
2021-03-30 21:00 | 44285.875 | 0 | 11.7363 | 37.78
2021-03-30 21:30 | 44285.8958 | 0 | 11.5813 | 37.78
2021-03-30 22:00 | 44285.9167 | 0 | 11.1512 | 37.78
2021-03-30 22:30 | 44285.9375 | 0 | 10.2975 | 37.78
2021-03-30 23:00 | 44285.9583 | 0 | 9.7456 | 37.78
2021-03-30 23:30 | 44285.9792 | 0 | 9.2928 | 37.78
2021-03-31 | 44286 | 0 | 8.9576 | 37.78
2021-03-31 00:30 | 44286.0208 | 0 | 8.7301 | 37.78
2021-03-31 01:00 | 44286.0417 | 0 | 8.5194 | 37.78
2021-03-31 01:30 | 44286.0625 | 0 | 8.2615 | 37.78
2021-03-31 02:00 | 44286.0833 | 0 | 8.2008 | 37.78
2021-03-31 02:30 | 44286.1042 | 0 | 8.1102 | 37.78
2021-03-31 03:00 | 44286.125 | 0 | 8.0566 | 37.78
2021-03-31 03:30 | 44286.1458 | 0 | 8.1726 | 37.78
2021-03-31 04:00 | 44286.1667 | 0 | 8.2219 | 37.78
2021-03-31 04:30 | 44286.1875 | 0 | 8.6019 | 37.78
2021-03-31 05:00 | 44286.2083 | 0 | 9.163 | 37.78
2021-03-31 05:30 | 44286.2292 | 0 | 9.4943 | 37.78
2021-03-31 06:00 | 44286.25 | 0 | 10.1952 | 37.78
2021-03-31 06:30 | 44286.2708 | 0 | 10.6737 | 37.78
2021-03-31 07:00 | 44286.2917 | 0 | 10.5511 | 37.78
2021-03-31 07:30 | 44286.3125 | 0 | 10.8619 | 37.78
2021-03-31 08:00 | 44286.3333 | 0 | 10.4705 | 37.78
2021-03-31 08:30 | 44286.3542 | 0 | 10.9592 | 37.78
2021-03-31 09:00 | 44286.375 | 0 | 10.3775 | 37.78
2021-03-31 09:30 | 44286.3958 | 0 | 11.8 | 37.78
2021-03-31 10:00 | 44286.4167 | 0 | 10.8251 | 37.78
2021-03-31 10:30 | 44286.4375 | 0 | 11.8561 | 37.78
2021-03-31 11:00 | 44286.4583 | 0 | 12.1176 | 37.78
2021-03-31 11:30 | 44286.4792 | 0 | 12.1372 | 37.78
2021-03-31 12:00 | 44286.5 | 0 | 11.0258 | 37.78
2021-03-31 12:30 | 44286.5208 | 0 | 11.9314 | 37.78
2021-03-31 13:00 | 44286.5417 | 0 | 12.5407 | 37.78
2021-03-31 13:30 | 44286.5625 | 0 | 11.5973 | 37.78
2021-03-31 14:00 | 44286.5833 | 0 | 11.4064 | 37.78
2021-03-31 14:30 | 44286.6042 | 0 | 11.9312 | 37.78
2021-03-31 15:00 | 44286.625 | 0 | 12.798 | 37.78
2021-03-31 15:30 | 44286.6458 | 0 | 11.5481 | 37.78
2021-03-31 16:00 | 44286.6667 | 0 | 12.1703 | 37.78
2021-03-31 16:30 | 44286.6875 | 0 | 12.4349 | 37.78
2021-03-31 17:00 | 44286.7083 | 0 | 13.0913 | 37.78
2021-03-31 17:30 | 44286.7292 | 0 | 13.0778 | 37.78
2021-03-31 18:00 | 44286.75 | 0 | 13.3976 | 37.78
2021-03-31 18:30 | 44286.7708 | 0 | 13.567 | 37.78
2021-03-31 19:00 | 44286.7917 | 0 | 13.0825 | 37.78
2021-03-31 19:30 | 44286.8125 | 0 | 12.9777 | 37.78
2021-03-31 20:00 | 44286.8333 | 0 | 12.5947 | 37.78
2021-03-31 20:30 | 44286.8542 | 0 | 12.0492 | 37.78
2021-03-31 21:00 | 44286.875 | 0 | 11.4419 | 37.78
2021-03-31 21:30 | 44286.8958 | 0 | 11.0993 | 37.78
2021-03-31 22:00 | 44286.9167 | 0 | 10.7461 | 37.78
2021-03-31 22:30 | 44286.9375 | 0 | 9.9653 | 37.78
2021-03-31 23:00 | 44286.9583 | 0 | 9.5464 | 37.78
2021-03-31 23:30 | 44286.9792 | 0 | 9.2426 | 37.78
2021-04-01 | 44287 | 0 | 8.7563 | 37.78
2021-04-01 00:30 | 44287.0208 | 0 | 8.3024 | 37.78
2021-04-01 01:00 | 44287.0417 | 0 | 8.0811 | 37.78
2021-04-01 01:30 | 44287.0625 | 0 | 7.8329 | 37.78
2021-04-01 02:00 | 44287.0833 | 0 | 8.0018 | 37.78
2021-04-01 02:30 | 44287.1042 | 0 | 7.7832 | 37.78
2021-04-01 03:00 | 44287.125 | 0 | 7.6538 | 37.78
2021-04-01 03:30 | 44287.1458 | 0 | 7.7819 | 37.78
2021-04-01 04:00 | 44287.1667 | 0 | 7.9817 | 37.78
2021-04-01 04:30 | 44287.1875 | 0 | 7.959 | 37.78
2021-04-01 05:00 | 44287.2083 | 0 | 8.0308 | 37.78
2021-04-01 05:30 | 44287.2292 | 0 | 8.0934 | 37.78
2021-04-01 06:00 | 44287.25 | 0 | 8.1396 | 37.78
2021-04-01 06:30 | 44287.2708 | 0 | 7.9654 | 37.78
2021-04-01 07:00 | 44287.2917 | 0 | 8.0464 | 37.78
2021-04-01 07:30 | 44287.3125 | 0 | 7.7274 | 37.78
2021-04-01 08:00 | 44287.3333 | 0 | 8.4579 | 37.78
2021-04-01 08:30 | 44287.3542 | 0 | 7.7453 | 37.78
2021-04-01 09:00 | 44287.375 | 0 | 8.0396 | 37.78
2021-04-01 09:30 | 44287.3958 | 0 | 8.219 | 37.78
2021-04-01 10:00 | 44287.4167 | 0 | 6.9888 | 37.78
2021-04-01 10:30 | 44287.4375 | 0 | 7.5889 | 37.78
2021-04-01 11:00 | 44287.4583 | 0 | 7.3332 | 37.78
2021-04-01 11:30 | 44287.4792 | 0 | 7.5441 | 37.78
2021-04-01 12:00 | 44287.5 | 0 | 7.8779 | 37.78
2021-04-01 12:30 | 44287.5208 | 0 | 7.0317 | 37.78
2021-04-01 13:00 | 44287.5417 | 0 | 7.5109 | 37.78
2021-04-01 13:30 | 44287.5625 | 0 | 8.2754 | 37.78
2021-04-01 14:00 | 44287.5833 | 0 | 7.8956 | 37.78
2021-04-01 14:30 | 44287.6042 | 0 | 9.9691 | 37.78
2021-04-01 15:00 | 44287.625 | 0 | 9.3793 | 37.78
2021-04-01 15:30 | 44287.6458 | 0 | 9.2208 | 37.78
2021-04-01 16:00 | 44287.6667 | 0 | 9.4095 | 37.78
2021-04-01 16:30 | 44287.6875 | 0 | 10.021 | 37.78
2021-04-01 17:00 | 44287.7083 | 0 | 10.3954 | 37.78
2021-04-01 17:30 | 44287.7292 | 0 | 10.7974 | 37.78
2021-04-01 18:00 | 44287.75 | 0 | 11.1513 | 37.78
2021-04-01 18:30 | 44287.7708 | 0 | 11.2654 | 37.78
2021-04-01 19:00 | 44287.7917 | 0 | 11.09 | 37.78
2021-04-01 19:30 | 44287.8125 | 0 | 10.8186 | 37.78
2021-04-01 20:00 | 44287.8333 | 0 | 10.6234 | 37.78
2021-04-01 20:30 | 44287.8542 | 0 | 10.1097 | 37.78
2021-04-01 21:00 | 44287.875 | 0 | 9.8288 | 37.78
2021-04-01 21:30 | 44287.8958 | 0 | 9.6422 | 37.78
2021-04-01 22:00 | 44287.9167 | 0 | 9.4653 | 37.78
2021-04-01 22:30 | 44287.9375 | 0 | 8.8416 | 37.78
2021-04-01 23:00 | 44287.9583 | 0 | 8.3948 | 37.78
2021-04-01 23:30 | 44287.9792 | 0 | 8.1378 | 37.78
2021-04-02 | 44288 | 0 | 7.7644 | 37.78
2021-04-02 00:30 | 44288.0208 | 0 | 7.5599 | 37.78
2021-04-02 01:00 | 44288.0417 | 0 | 7.3988 | 37.78
2021-04-02 01:30 | 44288.0625 | 0 | 7.2504 | 37.78
2021-04-02 02:00 | 44288.0833 | 0 | 7.2425 | 37.78
2021-04-02 02:30 | 44288.1042 | 0 | 7.1695 | 37.78
2021-04-02 03:00 | 44288.125 | 0 | 7.2879 | 37.78
2021-04-02 03:30 | 44288.1458 | 0 | 7.2942 | 37.78
2021-04-02 04:00 | 44288.1667 | 0 | 7.3055 | 37.78
2021-04-02 04:30 | 44288.1875 | 0 | 7.4089 | 37.78
2021-04-02 05:00 | 44288.2083 | 0 | 7.4845 | 37.78
2021-04-02 05:30 | 44288.2292 | 0 | 7.7432 | 37.78
2021-04-02 06:00 | 44288.25 | 0 | 7.6584 | 37.78
2021-04-02 06:30 | 44288.2708 | 0 | 8.0499 | 37.78
2021-04-02 07:00 | 44288.2917 | 0 | 8.3314 | 37.78
2021-04-02 07:30 | 44288.3125 | 0 | 8.5259 | 37.78
2021-04-02 08:00 | 44288.3333 | 0 | 8.5257 | 37.78
2021-04-02 08:30 | 44288.3542 | 0 | 8.9286 | 37.78
2021-04-02 09:00 | 44288.375 | 0 | 9.0385 | 37.78
2021-04-02 09:30 | 44288.3958 | 0 | 9.8086 | 37.78
2021-04-02 10:00 | 44288.4167 | 0 | 9.1611 | 37.78
2021-04-02 10:30 | 44288.4375 | 0 | 8.7368 | 37.78
2021-04-02 11:00 | 44288.4583 | 0 | 9.1283 | 37.78
2021-04-02 11:30 | 44288.4792 | 0 | 8.7803 | 37.78
2021-04-02 12:00 | 44288.5 | 0 | 9.3224 | 37.78
2021-04-02 12:30 | 44288.5208 | 0 | 8.9033 | 37.78
2021-04-02 13:00 | 44288.5417 | 0 | 8.3812 | 37.78
2021-04-02 13:30 | 44288.5625 | 0 | 8.5233 | 37.78
2021-04-02 14:00 | 44288.5833 | 0 | 9.3691 | 37.78
2021-04-02 14:30 | 44288.6042 | 0 | 9.6236 | 37.78
2021-04-02 15:00 | 44288.625 | 0 | 8.9721 | 37.78
2021-04-02 15:30 | 44288.6458 | 0 | 8.8375 | 37.78
2021-04-02 16:00 | 44288.6667 | 0 | 9.128 | 37.78
2021-04-02 16:30 | 44288.6875 | 0 | 9.8698 | 37.78
2021-04-02 17:00 | 44288.7083 | 0 | 10.0159 | 37.78
2021-04-02 17:30 | 44288.7292 | 0 | 10.7029 | 37.78
2021-04-02 18:00 | 44288.75 | 0 | 11.1518 | 37.78
2021-04-02 18:30 | 44288.7708 | 0 | 11.2812 | 37.78
2021-04-02 19:00 | 44288.7917 | 0 | 10.8937 | 37.78
2021-04-02 19:30 | 44288.8125 | 0 | 10.5892 | 37.78
2021-04-02 20:00 | 44288.8333 | 0 | 10.5106 | 37.78
2021-04-02 20:30 | 44288.8542 | 0 | 10.0756 | 37.78
2021-04-02 21:00 | 44288.875 | 0 | 9.7536 | 37.78
2021-04-02 21:30 | 44288.8958 | 0 | 9.5941 | 37.78
2021-04-02 22:00 | 44288.9167 | 0 | 9.2674 | 37.78
2021-04-02 22:30 | 44288.9375 | 0 | 8.7543 | 37.78
2021-04-02 23:00 | 44288.9583 | 0 | 8.3486 | 37.78
2021-04-02 23:30 | 44288.9792 | 0 | 8.1539 | 37.78
2021-04-03 | 44289 | 0 | 7.8058 | 37.78
2021-04-03 00:30 | 44289.0208 | 0 | 7.5635 | 37.78
2021-04-03 01:00 | 44289.0417 | 0 | 7.411 | 37.78
2021-04-03 01:30 | 44289.0625 | 0 | 7.2888 | 37.78
2021-04-03 02:00 | 44289.0833 | 0 | 7.2715 | 37.78
2021-04-03 02:30 | 44289.1042 | 0 | 7.1386 | 37.78
2021-04-03 03:00 | 44289.125 | 0 | 7.1167 | 37.78
2021-04-03 03:30 | 44289.1458 | 0 | 7.1069 | 37.78
2021-04-03 04:00 | 44289.1667 | 0 | 7.1558 | 37.78
2021-04-03 04:30 | 44289.1875 | 0 | 7.2146 | 37.78
2021-04-03 05:00 | 44289.2083 | 0 | 7.2001 | 37.78
2021-04-03 05:30 | 44289.2292 | 0 | 7.3423 | 37.78
2021-04-03 06:00 | 44289.25 | 0 | 7.4365 | 37.78
2021-04-03 06:30 | 44289.2708 | 0 | 7.7556 | 37.78
2021-04-03 07:00 | 44289.2917 | 0 | 8.2717 | 37.78
2021-04-03 07:30 | 44289.3125 | 0 | 8.6732 | 37.78
2021-04-03 08:00 | 44289.3333 | 0 | 9.0922 | 37.78
2021-04-03 08:30 | 44289.3542 | 0 | 9.1523 | 37.78
2021-04-03 09:00 | 44289.375 | 0 | 9.7357 | 37.78
2021-04-03 09:30 | 44289.3958 | 0 | 9.5098 | 37.78
2021-04-03 10:00 | 44289.4167 | 0 | 8.9813 | 37.78
2021-04-03 10:30 | 44289.4375 | 0 | 9.7783 | 37.78
2021-04-03 11:00 | 44289.4583 | 0 | 9.6954 | 37.78
2021-04-03 11:30 | 44289.4792 | 0 | 10.1765 | 37.78
2021-04-03 12:00 | 44289.5 | 0 | 9.8225 | 37.78
2021-04-03 12:30 | 44289.5208 | 0 | 9.2147 | 37.78
2021-04-03 13:00 | 44289.5417 | 0 | 9.7103 | 37.78
2021-04-03 13:30 | 44289.5625 | 0 | 9.9271 | 37.78
2021-04-03 14:00 | 44289.5833 | 0 | 9.6634 | 37.78
2021-04-03 14:30 | 44289.6042 | 0 | 9.7546 | 37.78
2021-04-03 15:00 | 44289.625 | 0 | 9.8158 | 37.78
2021-04-03 15:30 | 44289.6458 | 0 | 9.8071 | 37.78
2021-04-03 16:00 | 44289.6667 | 0 | 10.0238 | 37.78
2021-04-03 16:30 | 44289.6875 | 0 | 10.1452 | 37.78
2021-04-03 17:00 | 44289.7083 | 0 | 10.4916 | 37.78
2021-04-03 17:30 | 44289.7292 | 0 | 10.6319 | 37.78
2021-04-03 18:00 | 44289.75 | 0 | 10.8161 | 37.78
2021-04-03 18:30 | 44289.7708 | 0 | 10.9833 | 37.78
2021-04-03 19:00 | 44289.7917 | 0 | 10.7003 | 37.78
2021-04-03 19:30 | 44289.8125 | 0 | 10.424 | 37.78
2021-04-03 20:00 | 44289.8333 | 0 | 9.921 | 37.78
2021-04-03 20:30 | 44289.8542 | 0 | 9.7658 | 37.78
2021-04-03 21:00 | 44289.875 | 0 | 9.2875 | 37.78
2021-04-03 21:30 | 44289.8958 | 0 | 9.2037 | 37.78
2021-04-03 22:00 | 44289.9167 | 0 | 9.1656 | 37.78
2021-04-03 22:30 | 44289.9375 | 0 | 8.5471 | 37.78
2021-04-03 23:00 | 44289.9583 | 0 | 8.1762 | 37.78
2021-04-03 23:30 | 44289.9792 | 0 | 7.8646 | 37.78
2021-04-04 | 44290 | 0 | 7.666 | 37.78
2021-04-04 00:30 | 44290.0208 | 0 | 7.4098 | 37.78
2021-04-04 01:00 | 44290.0417 | 0 | 7.2026 | 37.78
2021-04-04 01:30 | 44290.0625 | 0 | 7.1594 | 37.78
2021-04-04 02:00 | 44290.0833 | 0 | 7.1468 | 37.78
2021-04-04 02:30 | 44290.1042 | 0 | 7.1085 | 37.78
2021-04-04 03:00 | 44290.125 | 0 | 7.0426 | 37.78
2021-04-04 03:30 | 44290.1458 | 0 | 7.3106 | 37.78
2021-04-04 04:00 | 44290.1667 | 0 | 7.2075 | 37.78
2021-04-04 04:30 | 44290.1875 | 0 | 7.3274 | 37.78
2021-04-04 05:00 | 44290.2083 | 0 | 7.423 | 37.78
2021-04-04 05:30 | 44290.2292 | 0 | 7.5498 | 37.78
2021-04-04 06:00 | 44290.25 | 0 | 7.7098 | 37.78
2021-04-04 06:30 | 44290.2708 | 0 | 8.0971 | 37.78
2021-04-04 07:00 | 44290.2917 | 0 | 8.5611 | 37.78
2021-04-04 07:30 | 44290.3125 | 0 | 8.8389 | 37.78
2021-04-04 08:00 | 44290.3333 | 0 | 9.2315 | 37.78
2021-04-04 08:30 | 44290.3542 | 0 | 9.5347 | 37.78
2021-04-04 09:00 | 44290.375 | 0 | 9.675 | 37.78
2021-04-04 09:30 | 44290.3958 | 0 | 10.0743 | 37.78
2021-04-04 10:00 | 44290.4167 | 0 | 9.7983 | 37.78
2021-04-04 10:30 | 44290.4375 | 0 | 9.8584 | 37.78
2021-04-04 11:00 | 44290.4583 | 0 | 9.813 | 37.78
2021-04-04 11:30 | 44290.4792 | 0 | 10.0133 | 37.78
2021-04-04 12:00 | 44290.5 | 0 | 10.1029 | 37.78
2021-04-04 12:30 | 44290.5208 | 0 | 9.7934 | 37.78
2021-04-04 13:00 | 44290.5417 | 0 | 10.1706 | 37.78
2021-04-04 13:30 | 44290.5625 | 0 | 10.3373 | 37.78
2021-04-04 14:00 | 44290.5833 | 0 | 10.3921 | 37.78
2021-04-04 14:30 | 44290.6042 | 0 | 10.6912 | 37.78
2021-04-04 15:00 | 44290.625 | 0 | 10.4695 | 37.78
2021-04-04 15:30 | 44290.6458 | 0 | 10.9854 | 37.78
2021-04-04 16:00 | 44290.6667 | 0 | 10.8915 | 37.78
2021-04-04 16:30 | 44290.6875 | 0 | 11.5653 | 37.78
2021-04-04 17:00 | 44290.7083 | 0 | 11.8747 | 37.78
2021-04-04 17:30 | 44290.7292 | 0 | 12.2975 | 37.78
2021-04-04 18:00 | 44290.75 | 0 | 12.319 | 37.78
2021-04-04 18:30 | 44290.7708 | 0 | 12.3033 | 37.78
2021-04-04 19:00 | 44290.7917 | 0 | 11.9081 | 37.78
2021-04-04 19:30 | 44290.8125 | 0 | 11.6846 | 37.78
2021-04-04 20:00 | 44290.8333 | 0 | 11.206 | 37.78
2021-04-04 20:30 | 44290.8542 | 0 | 10.761 | 37.78
2021-04-04 21:00 | 44290.875 | 0 | 10.4165 | 37.78
2021-04-04 21:30 | 44290.8958 | 0 | 10.2421 | 37.78
2021-04-04 22:00 | 44290.9167 | 0 | 9.8504 | 37.78
2021-04-04 22:30 | 44290.9375 | 0 | 9.3736 | 37.78
2021-04-04 23:00 | 44290.9583 | 0 | 8.9861 | 37.78
2021-04-04 23:30 | 44290.9792 | 0 | 8.6178 | 37.78
2021-04-05 | 44291 | 0 | 8.1374 | 37.78
2021-04-05 00:30 | 44291.0208 | 0 | 7.9567 | 37.78
2021-04-05 01:00 | 44291.0417 | 0 | 7.8101 | 37.78
2021-04-05 01:30 | 44291.0625 | 0 | 7.6916 | 37.78
2021-04-05 02:00 | 44291.0833 | 0 | 7.5891 | 37.78
2021-04-05 02:30 | 44291.1042 | 0 | 7.7431 | 37.78
2021-04-05 03:00 | 44291.125 | 0 | 7.6444 | 37.78
2021-04-05 03:30 | 44291.1458 | 0 | 7.7051 | 37.78
2021-04-05 04:00 | 44291.1667 | 0 | 8.0114 | 37.78
2021-04-05 04:30 | 44291.1875 | 0 | 8.576 | 37.78
2021-04-05 05:00 | 44291.2083 | 0 | 9.2199 | 37.78
2021-04-05 05:30 | 44291.2292 | 0 | 9.9356 | 37.78
2021-04-05 06:00 | 44291.25 | 0 | 10.68 | 37.78
2021-04-05 06:30 | 44291.2708 | 0 | 11.5268 | 37.78
2021-04-05 07:00 | 44291.2917 | 0 | 12.1649 | 37.78
2021-04-05 07:30 | 44291.3125 | 0 | 12.5551 | 37.78
2021-04-05 08:00 | 44291.3333 | 0 | 12.8406 | 37.78
2021-04-05 08:30 | 44291.3542 | 0 | 12.1814 | 37.78
2021-04-05 09:00 | 44291.375 | 0 | 13.2151 | 37.78
2021-04-05 09:30 | 44291.3958 | 0 | 13.3649 | 37.78
2021-04-05 10:00 | 44291.4167 | 0 | 12.9492 | 37.78
2021-04-05 10:30 | 44291.4375 | 0 | 12.5418 | 37.78
2021-04-05 11:00 | 44291.4583 | 0 | 12.4189 | 37.78
2021-04-05 11:30 | 44291.4792 | 0 | 12.7252 | 37.78
2021-04-05 12:00 | 44291.5 | 0 | 12.2387 | 37.78
2021-04-05 12:30 | 44291.5208 | 0 | 11.6069 | 37.78
2021-04-05 13:00 | 44291.5417 | 0 | 12.7014 | 37.78
2021-04-05 13:30 | 44291.5625 | 0 | 12.5957 | 37.78
2021-04-05 14:00 | 44291.5833 | 0 | 12.0022 | 37.78
2021-04-05 14:30 | 44291.6042 | 0 | 13.414 | 37.78
2021-04-05 15:00 | 44291.625 | 0 | 12.95 | 37.78
2021-04-05 15:30 | 44291.6458 | 0 | 13.2473 | 37.78
2021-04-05 16:00 | 44291.6667 | 0 | 13.3187 | 37.78
2021-04-05 16:30 | 44291.6875 | 0 | 13.2869 | 37.78
2021-04-05 17:00 | 44291.7083 | 0 | 13.5414 | 37.78
2021-04-05 17:30 | 44291.7292 | 0 | 13.8394 | 37.78
2021-04-05 18:00 | 44291.75 | 0 | 14.1384 | 37.78
2021-04-05 18:30 | 44291.7708 | 0 | 14.0273 | 37.78
2021-04-05 19:00 | 44291.7917 | 0 | 13.6642 | 37.78
2021-04-05 19:30 | 44291.8125 | 0 | 13.3746 | 37.78
2021-04-05 20:00 | 44291.8333 | 0 | 12.9042 | 37.78
2021-04-05 20:30 | 44291.8542 | 0 | 12.5467 | 37.78
2021-04-05 21:00 | 44291.875 | 0 | 12.0449 | 37.78
2021-04-05 21:30 | 44291.8958 | 0 | 11.7212 | 37.78
2021-04-05 22:00 | 44291.9167 | 0 | 11.0553 | 37.78
2021-04-05 22:30 | 44291.9375 | 0 | 10.5001 | 37.78
2021-04-05 23:00 | 44291.9583 | 0 | 9.9633 | 37.78
2021-04-05 23:30 | 44291.9792 | 0 | 9.5734 | 37.78
2021-04-06 | 44292 | 0 | 9.2941 | 37.78
2021-04-06 00:30 | 44292.0208 | 0 | 8.6608 | 37.78
2021-04-06 01:00 | 44292.0417 | 0 | 8.6036 | 37.78
2021-04-06 01:30 | 44292.0625 | 0 | 8.4379 | 37.78
2021-04-06 02:00 | 44292.0833 | 0 | 8.2823 | 37.78
2021-04-06 02:30 | 44292.1042 | 0 | 8.0844 | 37.78
2021-04-06 03:00 | 44292.125 | 0 | 8.1005 | 37.78
2021-04-06 03:30 | 44292.1458 | 0 | 8.3034 | 37.78
2021-04-06 04:00 | 44292.1667 | 0 | 8.7115 | 37.78
2021-04-06 04:30 | 44292.1875 | 0 | 8.8875 | 37.78
2021-04-06 05:00 | 44292.2083 | 0 | 9.631 | 37.78
2021-04-06 05:30 | 44292.2292 | 0 | 10.0515 | 37.78
2021-04-06 06:00 | 44292.25 | 0 | 10.8404 | 37.78
2021-04-06 06:30 | 44292.2708 | 0 | 11.2646 | 37.78
2021-04-06 07:00 | 44292.2917 | 0 | 11.9253 | 37.78
2021-04-06 07:30 | 44292.3125 | 0 | 12.3 | 37.78
2021-04-06 08:00 | 44292.3333 | 0 | 11.8305 | 37.78
2021-04-06 08:30 | 44292.3542 | 0 | 11.8803 | 37.78
2021-04-06 09:00 | 44292.375 | 0 | 12.1426 | 37.78
2021-04-06 09:30 | 44292.3958 | 0 | 12.0902 | 37.78
2021-04-06 10:00 | 44292.4167 | 0 | 11.764 | 37.78
2021-04-06 10:30 | 44292.4375 | 0 | 11.7614 | 37.78
2021-04-06 11:00 | 44292.4583 | 0 | 10.9774 | 37.78
2021-04-06 11:30 | 44292.4792 | 0 | 12.4188 | 37.78
2021-04-06 12:00 | 44292.5 | 0 | 11.6292 | 37.78
2021-04-06 12:30 | 44292.5208 | 0 | 12.444 | 37.78
2021-04-06 13:00 | 44292.5417 | 0 | 11.2419 | 37.78
2021-04-06 13:30 | 44292.5625 | 0 | 11.7323 | 37.78
2021-04-06 14:00 | 44292.5833 | 0 | 13.2693 | 37.78
2021-04-06 14:30 | 44292.6042 | 0 | 11.6703 | 37.78
2021-04-06 15:00 | 44292.625 | 0 | 13.3606 | 37.78
2021-04-06 15:30 | 44292.6458 | 0 | 13.7036 | 37.78
2021-04-06 16:00 | 44292.6667 | 0 | 13.767 | 37.78
2021-04-06 16:30 | 44292.6875 | 0 | 13.6977 | 37.78
2021-04-06 17:00 | 44292.7083 | 0 | 13.7206 | 37.78
2021-04-06 17:30 | 44292.7292 | 0 | 14.0509 | 37.78
2021-04-06 18:00 | 44292.75 | 0 | 14.4402 | 37.78
2021-04-06 18:30 | 44292.7708 | 0 | 14.6615 | 37.78
2021-04-06 19:00 | 44292.7917 | 0 | 14.1485 | 37.78
2021-04-06 19:30 | 44292.8125 | 0 | 13.862 | 37.78
2021-04-06 20:00 | 44292.8333 | 0 | 13.4058 | 37.78
2021-04-06 20:30 | 44292.8542 | 0 | 12.8837 | 37.78
2021-04-06 21:00 | 44292.875 | 0 | 12.3081 | 37.78
2021-04-06 21:30 | 44292.8958 | 0 | 11.9523 | 37.78
2021-04-06 22:00 | 44292.9167 | 0 | 11.4949 | 37.78
2021-04-06 22:30 | 44292.9375 | 0 | 10.6578 | 37.78
2021-04-06 23:00 | 44292.9583 | 0 | 10.2117 | 37.78
2021-04-06 23:30 | 44292.9792 | 0 | 9.8637 | 37.78
2021-04-07 | 44293 | 0 | 9.1904 | 37.78
2021-04-07 00:30 | 44293.0208 | 0 | 8.8183 | 37.78
2021-04-07 01:00 | 44293.0417 | 0 | 8.504 | 37.78
2021-04-07 01:30 | 44293.0625 | 0 | 8.4266 | 37.78
2021-04-07 02:00 | 44293.0833 | 0 | 8.1992 | 37.78
2021-04-07 02:30 | 44293.1042 | 0 | 8.2365 | 37.78
2021-04-07 03:00 | 44293.125 | 0 | 8.1329 | 37.78
2021-04-07 03:30 | 44293.1458 | 0 | 8.3171 | 37.78
2021-04-07 04:00 | 44293.1667 | 0 | 8.5741 | 37.78
2021-04-07 04:30 | 44293.1875 | 0 | 8.8539 | 37.78
2021-04-07 05:00 | 44293.2083 | 0 | 9.2386 | 37.78
2021-04-07 05:30 | 44293.2292 | 0 | 9.7341 | 37.78
2021-04-07 06:00 | 44293.25 | 0 | 10.2934 | 37.78
2021-04-07 06:30 | 44293.2708 | 0 | 10.8923 | 37.78
2021-04-07 07:00 | 44293.2917 | 0 | 11.1835 | 37.78
2021-04-07 07:30 | 44293.3125 | 0 | 11.3078 | 37.78
2021-04-07 08:00 | 44293.3333 | 0 | 11.2616 | 37.78
2021-04-07 08:30 | 44293.3542 | 0 | 11.3451 | 37.78
2021-04-07 09:00 | 44293.375 | 0 | 11.1931 | 37.78
2021-04-07 09:30 | 44293.3958 | 0 | 11.2308 | 37.78
2021-04-07 10:00 | 44293.4167 | 0 | 10.6244 | 37.78
2021-04-07 10:30 | 44293.4375 | 0 | 10.7384 | 37.78
2021-04-07 11:00 | 44293.4583 | 0 | 11.2196 | 37.78
2021-04-07 11:30 | 44293.4792 | 0 | 11.5729 | 37.78
2021-04-07 12:00 | 44293.5 | 0 | 11.5133 | 37.78
2021-04-07 12:30 | 44293.5208 | 0 | 11.6865 | 37.78
2021-04-07 13:00 | 44293.5417 | 0 | 13.1488 | 37.78
2021-04-07 13:30 | 44293.5625 | 0 | 12.8021 | 37.78
2021-04-07 14:00 | 44293.5833 | 0 | 12.9244 | 37.78
2021-04-07 14:30 | 44293.6042 | 0 | 12.1399 | 37.78
2021-04-07 15:00 | 44293.625 | 0 | 13.1609 | 37.78
2021-04-07 15:30 | 44293.6458 | 0 | 13.2221 | 37.78
2021-04-07 16:00 | 44293.6667 | 0 | 13.6503 | 37.78
2021-04-07 16:30 | 44293.6875 | 0 | 14.3046 | 37.78
2021-04-07 17:00 | 44293.7083 | 0 | 14.3036 | 37.78
2021-04-07 17:30 | 44293.7292 | 0 | 14.2559 | 37.78
2021-04-07 18:00 | 44293.75 | 0 | 14.6087 | 37.78
2021-04-07 18:30 | 44293.7708 | 0 | 14.6651 | 37.78
2021-04-07 19:00 | 44293.7917 | 0 | 14.3522 | 37.78
2021-04-07 19:30 | 44293.8125 | 0 | 14.1398 | 37.78
2021-04-07 20:00 | 44293.8333 | 0 | 13.6843 | 37.78
2021-04-07 20:30 | 44293.8542 | 0 | 13.3778 | 37.78
2021-04-07 21:00 | 44293.875 | 0 | 12.8756 | 37.78
2021-04-07 21:30 | 44293.8958 | 0 | 12.3272 | 37.78
2021-04-07 22:00 | 44293.9167 | 0 | 11.8198 | 37.78
2021-04-07 22:30 | 44293.9375 | 0 | 10.9913 | 37.78
2021-04-07 23:00 | 44293.9583 | 0 | 10.2348 | 37.78
2021-04-07 23:30 | 44293.9792 | 0 | 9.6953 | 37.78
2021-04-08 | 44294 | 0 | 8.8998 | 37.78
2021-04-08 00:30 | 44294.0208 | 0 | 8.7458 | 37.78
2021-04-08 01:00 | 44294.0417 | 0 | 8.5668 | 37.78
2021-04-08 01:30 | 44294.0625 | 0 | 8.3655 | 37.78
2021-04-08 02:00 | 44294.0833 | 0 | 8.2787 | 37.78
2021-04-08 02:30 | 44294.1042 | 0 | 8.2929 | 37.78
2021-04-08 03:00 | 44294.125 | 0 | 8.1741 | 37.78
2021-04-08 03:30 | 44294.1458 | 0 | 8.4005 | 37.78
2021-04-08 04:00 | 44294.1667 | 0 | 8.5032 | 37.78
2021-04-08 04:30 | 44294.1875 | 0 | 8.8696 | 37.78
2021-04-08 05:00 | 44294.2083 | 0 | 9.132 | 37.78
2021-04-08 05:30 | 44294.2292 | 0 | 9.714 | 37.78
2021-04-08 06:00 | 44294.25 | 0 | 10.2944 | 37.78
2021-04-08 06:30 | 44294.2708 | 0 | 10.7991 | 37.78
2021-04-08 07:00 | 44294.2917 | 0 | 10.9613 | 37.78
2021-04-08 07:30 | 44294.3125 | 0 | 11.0844 | 37.78
2021-04-08 08:00 | 44294.3333 | 0 | 11.1448 | 37.78
2021-04-08 08:30 | 44294.3542 | 0 | 11.034 | 37.78
2021-04-08 09:00 | 44294.375 | 0 | 10.796 | 37.78
2021-04-08 09:30 | 44294.3958 | 0 | 10.8256 | 37.78
2021-04-08 10:00 | 44294.4167 | 0 | 10.483 | 37.78
2021-04-08 10:30 | 44294.4375 | 0 | 10.6013 | 37.78
2021-04-08 11:00 | 44294.4583 | 0 | 10.7732 | 37.78
2021-04-08 11:30 | 44294.4792 | 0 | 10.956 | 37.78
2021-04-08 12:00 | 44294.5 | 0 | 11.2266 | 37.78
2021-04-08 12:30 | 44294.5208 | 0 | 11.2721 | 37.78
2021-04-08 13:00 | 44294.5417 | 0 | 11.4752 | 37.78
2021-04-08 13:30 | 44294.5625 | 0 | 12.2506 | 37.78
2021-04-08 14:00 | 44294.5833 | 0 | 13.1688 | 37.78
2021-04-08 14:30 | 44294.6042 | 0 | 13.6925 | 37.78
2021-04-08 15:00 | 44294.625 | 0 | 14.1831 | 37.78
2021-04-08 15:30 | 44294.6458 | 0 | 15.2128 | 37.78
2021-04-08 16:00 | 44294.6667 | 0 | 15.5997 | 37.78
2021-04-08 16:30 | 44294.6875 | 0 | 15.2504 | 37.78
2021-04-08 17:00 | 44294.7083 | 0 | 15.253 | 37.78
2021-04-08 17:30 | 44294.7292 | 0 | 14.8029 | 37.78
2021-04-08 18:00 | 44294.75 | 0 | 14.9073 | 37.78
2021-04-08 18:30 | 44294.7708 | 0 | 14.9382 | 37.78
2021-04-08 19:00 | 44294.7917 | 0 | 14.5505 | 37.78
2021-04-08 19:30 | 44294.8125 | 0 | 14.2416 | 37.78
2021-04-08 20:00 | 44294.8333 | 0 | 13.8296 | 37.78
2021-04-08 20:30 | 44294.8542 | 0 | 13.4742 | 37.78
2021-04-08 21:00 | 44294.875 | 0 | 13.0029 | 37.78
2021-04-08 21:30 | 44294.8958 | 0 | 12.4936 | 37.78
2021-04-08 22:00 | 44294.9167 | 0 | 12.143 | 37.78
2021-04-08 22:30 | 44294.9375 | 0 | 11.2264 | 37.78
2021-04-08 23:00 | 44294.9583 | 0 | 10.5104 | 37.78
2021-04-08 23:30 | 44294.9792 | 0 | 10.1682 | 37.78
2021-04-09 | 44295 | 0 | 9.5025 | 37.78
2021-04-09 00:30 | 44295.0208 | 0 | 9.0609 | 37.78
2021-04-09 01:00 | 44295.0417 | 0 | 8.5875 | 37.78
2021-04-09 01:30 | 44295.0625 | 0 | 8.3846 | 37.78
2021-04-09 02:00 | 44295.0833 | 0 | 8.2968 | 37.78
2021-04-09 02:30 | 44295.1042 | 0 | 8.1487 | 37.78
2021-04-09 03:00 | 44295.125 | 0 | 7.9453 | 37.78
2021-04-09 03:30 | 44295.1458 | 0 | 8.1429 | 37.78
2021-04-09 04:00 | 44295.1667 | 0 | 8.0946 | 37.78
2021-04-09 04:30 | 44295.1875 | 0 | 8.1068 | 37.78
2021-04-09 05:00 | 44295.2083 | 0 | 8.2509 | 37.78
2021-04-09 05:30 | 44295.2292 | 0 | 8.4543 | 37.78
2021-04-09 06:00 | 44295.25 | 0 | 8.4048 | 37.78
2021-04-09 06:30 | 44295.2708 | 0 | 8.7097 | 37.78
2021-04-09 07:00 | 44295.2917 | 0 | 8.6861 | 37.78
2021-04-09 07:30 | 44295.3125 | 0 | 8.6063 | 37.78
2021-04-09 08:00 | 44295.3333 | 0 | 8.6427 | 37.78
2021-04-09 08:30 | 44295.3542 | 0 | 8.5679 | 37.78
2021-04-09 09:00 | 44295.375 | 0 | 8.6411 | 37.78
2021-04-09 09:30 | 44295.3958 | 0 | 8.8078 | 37.78
2021-04-09 10:00 | 44295.4167 | 0 | 8.7849 | 37.78
2021-04-09 10:30 | 44295.4375 | 0 | 8.6525 | 37.78
2021-04-09 11:00 | 44295.4583 | 0 | 8.8037 | 37.78
2021-04-09 11:30 | 44295.4792 | 0 | 8.9997 | 37.78
2021-04-09 12:00 | 44295.5 | 0 | 9.1562 | 37.78
2021-04-09 12:30 | 44295.5208 | 0 | 9.5679 | 37.78
2021-04-09 13:00 | 44295.5417 | 0 | 10.0355 | 37.78
2021-04-09 13:30 | 44295.5625 | 0 | 10.6348 | 37.78
2021-04-09 14:00 | 44295.5833 | 0 | 11.2936 | 37.78
2021-04-09 14:30 | 44295.6042 | 0 | 11.949 | 37.78
2021-04-09 15:00 | 44295.625 | 0 | 12.8629 | 37.78
2021-04-09 15:30 | 44295.6458 | 0 | 12.9062 | 37.78
2021-04-09 16:00 | 44295.6667 | 0 | 13.3924 | 37.78
2021-04-09 16:30 | 44295.6875 | 0 | 13.6848 | 37.78
2021-04-09 17:00 | 44295.7083 | 0 | 13.7538 | 37.78
2021-04-09 17:30 | 44295.7292 | 0 | 13.7377 | 37.78
2021-04-09 18:00 | 44295.75 | 0 | 13.7542 | 37.78
2021-04-09 18:30 | 44295.7708 | 0 | 13.7061 | 37.78
2021-04-09 19:00 | 44295.7917 | 0 | 13.141 | 37.78
2021-04-09 19:30 | 44295.8125 | 0 | 12.6163 | 37.78
2021-04-09 20:00 | 44295.8333 | 0 | 12.2109 | 37.78
2021-04-09 20:30 | 44295.8542 | 0 | 11.6233 | 37.78
2021-04-09 21:00 | 44295.875 | 0 | 11.3111 | 37.78
2021-04-09 21:30 | 44295.8958 | 0 | 10.887 | 37.78
2021-04-09 22:00 | 44295.9167 | 0 | 10.3802 | 37.78
2021-04-09 22:30 | 44295.9375 | 0 | 9.6564 | 37.78
2021-04-09 23:00 | 44295.9583 | 0 | 9.3501 | 37.78
2021-04-09 23:30 | 44295.9792 | 0 | 8.9501 | 37.78
2021-04-10 | 44296 | 0 | 8.4667 | 37.78
2021-04-10 00:30 | 44296.0208 | 0 | 8.079 | 37.78
2021-04-10 01:00 | 44296.0417 | 0 | 7.7929 | 37.78
2021-04-10 01:30 | 44296.0625 | 0 | 7.7807 | 37.78
2021-04-10 02:00 | 44296.0833 | 0 | 7.8212 | 37.78
2021-04-10 02:30 | 44296.1042 | 0 | 7.5603 | 37.78
2021-04-10 03:00 | 44296.125 | 0 | 7.4862 | 37.78
2021-04-10 03:30 | 44296.1458 | 0 | 7.4313 | 37.78
2021-04-10 04:00 | 44296.1667 | 0 | 7.4807 | 37.78
2021-04-10 04:30 | 44296.1875 | 0 | 7.5072 | 37.78
2021-04-10 05:00 | 44296.2083 | 0 | 7.6441 | 37.78
2021-04-10 05:30 | 44296.2292 | 0 | 7.6616 | 37.78
2021-04-10 06:00 | 44296.25 | 0 | 7.7157 | 37.78
2021-04-10 06:30 | 44296.2708 | 0 | 8.0445 | 37.78
2021-04-10 07:00 | 44296.2917 | 0 | 8.2282 | 37.78
2021-04-10 07:30 | 44296.3125 | 0 | 8.292 | 37.78
2021-04-10 08:00 | 44296.3333 | 0 | 9.0732 | 37.78
2021-04-10 08:30 | 44296.3542 | 0 | 9.4394 | 37.78
2021-04-10 09:00 | 44296.375 | 0 | 8.8442 | 37.78
2021-04-10 09:30 | 44296.3958 | 0 | 9.4282 | 37.78
2021-04-10 10:00 | 44296.4167 | 0 | 8.3108 | 37.78
2021-04-10 10:30 | 44296.4375 | 0 | 7.2332 | 37.78
2021-04-10 11:00 | 44296.4583 | 0 | 7.2782 | 37.78
2021-04-10 11:30 | 44296.4792 | 0 | 7.0866 | 37.78
2021-04-10 12:00 | 44296.5 | 0 | 6.3031 | 37.78
2021-04-10 12:30 | 44296.5208 | 0 | 6.8304 | 37.78
2021-04-10 13:00 | 44296.5417 | 0 | 7.2375 | 37.78
2021-04-10 13:30 | 44296.5625 | 0 | 7.6075 | 37.78
2021-04-10 14:00 | 44296.5833 | 0 | 8.0065 | 37.78
2021-04-10 14:30 | 44296.6042 | 0 | 8.8083 | 37.78
2021-04-10 15:00 | 44296.625 | 0 | 9.5121 | 37.78
2021-04-10 15:30 | 44296.6458 | 0 | 10.1582 | 37.78
2021-04-10 16:00 | 44296.6667 | 0 | 10.7384 | 37.78
2021-04-10 16:30 | 44296.6875 | 0 | 11.3813 | 37.78
2021-04-10 17:00 | 44296.7083 | 0 | 11.8042 | 37.78
2021-04-10 17:30 | 44296.7292 | 0 | 11.8894 | 37.78
2021-04-10 18:00 | 44296.75 | 0 | 12.3496 | 37.78
2021-04-10 18:30 | 44296.7708 | 0 | 12.3234 | 37.78
2021-04-10 19:00 | 44296.7917 | 0 | 11.8521 | 37.78
2021-04-10 19:30 | 44296.8125 | 0 | 11.4152 | 37.78
2021-04-10 20:00 | 44296.8333 | 0 | 11.0603 | 37.78
2021-04-10 20:30 | 44296.8542 | 0 | 10.4595 | 37.78
2021-04-10 21:00 | 44296.875 | 0 | 10.1216 | 37.78
2021-04-10 21:30 | 44296.8958 | 0 | 9.7255 | 37.78
2021-04-10 22:00 | 44296.9167 | 0 | 9.5178 | 37.78
2021-04-10 22:30 | 44296.9375 | 0 | 8.6978 | 37.78
2021-04-10 23:00 | 44296.9583 | 0 | 8.2267 | 37.78
2021-04-10 23:30 | 44296.9792 | 0 | 7.9008 | 37.78
2021-04-11 | 44297 | 0 | 7.664 | 37.78
2021-04-11 00:30 | 44297.0208 | 0 | 7.4184 | 37.78
2021-04-11 01:00 | 44297.0417 | 0 | 7.2812 | 37.78
2021-04-11 01:30 | 44297.0625 | 0 | 7.1214 | 37.78
2021-04-11 02:00 | 44297.0833 | 0 | 7.0493 | 37.78
2021-04-11 02:30 | 44297.1042 | 0 | 6.8957 | 37.78
2021-04-11 03:00 | 44297.125 | 0 | 6.8842 | 37.78
2021-04-11 03:30 | 44297.1458 | 0 | 7.171 | 37.78
2021-04-11 04:00 | 44297.1667 | 0 | 7.4184 | 37.78
2021-04-11 04:30 | 44297.1875 | 0 | 7.7863 | 37.78
2021-04-11 05:00 | 44297.2083 | 0 | 8.337 | 37.78
2021-04-11 05:30 | 44297.2292 | 0 | 8.8894 | 37.78
2021-04-11 06:00 | 44297.25 | 0 | 9.5218 | 37.78
2021-04-11 06:30 | 44297.2708 | 0 | 10.2052 | 37.78
2021-04-11 07:00 | 44297.2917 | 0 | 10.1624 | 37.78
2021-04-11 07:30 | 44297.3125 | 0 | 10.1191 | 37.78
2021-04-11 08:00 | 44297.3333 | 0 | 9.8272 | 37.78
2021-04-11 08:30 | 44297.3542 | 0 | 9.352 | 37.78
2021-04-11 09:00 | 44297.375 | 0 | 9.0343 | 37.78
2021-04-11 09:30 | 44297.3958 | 0 | 8.749 | 37.78
2021-04-11 10:00 | 44297.4167 | 0 | 8.5515 | 37.78
2021-04-11 10:30 | 44297.4375 | 0 | 8.5001 | 37.78
2021-04-11 11:00 | 44297.4583 | 0 | 8.2442 | 37.78
2021-04-11 11:30 | 44297.4792 | 0 | 8.5746 | 37.78
2021-04-11 12:00 | 44297.5 | 0 | 8.8823 | 37.78
2021-04-11 12:30 | 44297.5208 | 0 | 9.3963 | 37.78
2021-04-11 13:00 | 44297.5417 | 0 | 9.2601 | 37.78
2021-04-11 13:30 | 44297.5625 | 0 | 10.3184 | 37.78
2021-04-11 14:00 | 44297.5833 | 0 | 10.6076 | 37.78
2021-04-11 14:30 | 44297.6042 | 0 | 10.5529 | 37.78
2021-04-11 15:00 | 44297.625 | 0 | 10.8157 | 37.78
2021-04-11 15:30 | 44297.6458 | 0 | 11.5843 | 37.78
2021-04-11 16:00 | 44297.6667 | 0 | 11.9091 | 37.78
2021-04-11 16:30 | 44297.6875 | 0 | 12.2435 | 37.78
2021-04-11 17:00 | 44297.7083 | 0 | 12.6892 | 37.78
2021-04-11 17:30 | 44297.7292 | 0 | 13.1589 | 37.78
2021-04-11 18:00 | 44297.75 | 0 | 12.3735 | 37.78
2021-04-11 18:30 | 44297.7708 | 0 | 12.5149 | 37.78
2021-04-11 19:00 | 44297.7917 | 0 | 12.8984 | 37.78
2021-04-11 19:30 | 44297.8125 | 0 | 12.4832 | 37.78
2021-04-11 20:00 | 44297.8333 | 0 | 12.1909 | 37.78
2021-04-11 20:30 | 44297.8542 | 0 | 11.8248 | 37.78
2021-04-11 21:00 | 44297.875 | 0 | 11.1563 | 37.78
2021-04-11 21:30 | 44297.8958 | 0 | 10.7981 | 37.78
2021-04-11 22:00 | 44297.9167 | 0 | 10.2978 | 37.78
2021-04-11 22:30 | 44297.9375 | 0 | 9.6855 | 37.78
2021-04-11 23:00 | 44297.9583 | 0 | 9.1351 | 37.78
2021-04-11 23:30 | 44297.9792 | 0 | 8.7703 | 37.78
2021-04-12 | 44298 | 0 | 8.3419 | 37.78
2021-04-12 00:30 | 44298.0208 | 0 | 7.9124 | 37.78
2021-04-12 01:00 | 44298.0417 | 0 | 7.7303 | 37.78
2021-04-12 01:30 | 44298.0625 | 0 | 7.6742 | 37.78
2021-04-12 02:00 | 44298.0833 | 0 | 7.6891 | 37.78
2021-04-12 02:30 | 44298.1042 | 0 | 7.5696 | 37.78
2021-04-12 03:00 | 44298.125 | 0 | 7.4935 | 37.78
2021-04-12 03:30 | 44298.1458 | 0 | 7.7122 | 37.78
2021-04-12 04:00 | 44298.1667 | 0 | 7.8837 | 37.78
2021-04-12 04:30 | 44298.1875 | 0 | 8.2631 | 37.78
2021-04-12 05:00 | 44298.2083 | 0 | 8.4917 | 37.78
2021-04-12 05:30 | 44298.2292 | 0 | 9.271 | 37.78
2021-04-12 06:00 | 44298.25 | 0 | 9.8594 | 37.78
2021-04-12 06:30 | 44298.2708 | 0 | 10.4209 | 37.78
2021-04-12 07:00 | 44298.2917 | 0 | 10.4618 | 37.78
2021-04-12 07:30 | 44298.3125 | 0 | 10.1897 | 37.78
2021-04-12 08:00 | 44298.3333 | 0 | 9.855 | 37.78
2021-04-12 08:30 | 44298.3542 | 0 | 9.5951 | 37.78
2021-04-12 09:00 | 44298.375 | 0 | 9.2662 | 37.78
2021-04-12 09:30 | 44298.3958 | 0 | 9.1242 | 37.78
2021-04-12 10:00 | 44298.4167 | 0 | 8.7395 | 37.78
2021-04-12 10:30 | 44298.4375 | 0 | 9.0317 | 37.78
2021-04-12 11:00 | 44298.4583 | 0 | 9.193 | 37.78
2021-04-12 11:30 | 44298.4792 | 0 | 10.8068 | 37.78
2021-04-12 12:00 | 44298.5 | 0 | 8.7998 | 37.78
2021-04-12 12:30 | 44298.5208 | 0 | 9.2163 | 37.78
2021-04-12 13:00 | 44298.5417 | 0 | 9.4209 | 37.78
2021-04-12 13:30 | 44298.5625 | 0 | 10.2881 | 37.78
2021-04-12 14:00 | 44298.5833 | 0 | 10.9819 | 37.78
2021-04-12 14:30 | 44298.6042 | 0 | 10.5772 | 37.78
2021-04-12 15:00 | 44298.625 | 0 | 11.4283 | 37.78
2021-04-12 15:30 | 44298.6458 | 0 | 11.397 | 37.78
2021-04-12 16:00 | 44298.6667 | 0 | 12.0175 | 37.78
2021-04-12 16:30 | 44298.6875 | 0 | 12.5975 | 37.78
2021-04-12 17:00 | 44298.7083 | 0 | 12.5443 | 37.78
2021-04-12 17:30 | 44298.7292 | 0 | 12.8495 | 37.78
2021-04-12 18:00 | 44298.75 | 0 | 13.2139 | 37.78
2021-04-12 18:30 | 44298.7708 | 0 | 13.2502 | 37.78
2021-04-12 19:00 | 44298.7917 | 0 | 12.835 | 37.78
2021-04-12 19:30 | 44298.8125 | 0 | 12.6609 | 37.78
2021-04-12 20:00 | 44298.8333 | 0 | 12.2728 | 37.78
2021-04-12 20:30 | 44298.8542 | 0 | 11.8349 | 37.78
2021-04-12 21:00 | 44298.875 | 0 | 11.2309 | 37.78
2021-04-12 21:30 | 44298.8958 | 0 | 10.954 | 37.78
2021-04-12 22:00 | 44298.9167 | 0 | 10.4384 | 37.78
2021-04-12 22:30 | 44298.9375 | 0 | 9.6971 | 37.78
2021-04-12 23:00 | 44298.9583 | 0 | 8.9165 | 37.78
2021-04-12 23:30 | 44298.9792 | 0 | 8.5234 | 37.78
2021-04-13 | 44299 | 0 | 8.0512 | 37.78
2021-04-13 00:30 | 44299.0208 | 0 | 7.9552 | 37.78
2021-04-13 01:00 | 44299.0417 | 0 | 7.7494 | 37.78
2021-04-13 01:30 | 44299.0625 | 0 | 7.6054 | 37.78
2021-04-13 02:00 | 44299.0833 | 0 | 7.6484 | 37.78
2021-04-13 02:30 | 44299.1042 | 0 | 7.4151 | 37.78
2021-04-13 03:00 | 44299.125 | 0 | 7.4309 | 37.78
2021-04-13 03:30 | 44299.1458 | 0 | 7.5824 | 37.78
2021-04-13 04:00 | 44299.1667 | 0 | 7.8984 | 37.78
2021-04-13 04:30 | 44299.1875 | 0 | 8.2473 | 37.78
2021-04-13 05:00 | 44299.2083 | 0 | 8.6924 | 37.78
2021-04-13 05:30 | 44299.2292 | 0 | 9.3423 | 37.78
2021-04-13 06:00 | 44299.25 | 0 | 9.8394 | 37.78
2021-04-13 06:30 | 44299.2708 | 0 | 10.4696 | 37.78
2021-04-13 07:00 | 44299.2917 | 0 | 10.8101 | 37.78
2021-04-13 07:30 | 44299.3125 | 0 | 10.4227 | 37.78
2021-04-13 08:00 | 44299.3333 | 0 | 10.2453 | 37.78
2021-04-13 08:30 | 44299.3542 | 0 | 9.7517 | 37.78
2021-04-13 09:00 | 44299.375 | 0 | 9.402 | 37.78
2021-04-13 09:30 | 44299.3958 | 0 | 9.1686 | 37.78
2021-04-13 10:00 | 44299.4167 | 0 | 8.9281 | 37.78
2021-04-13 10:30 | 44299.4375 | 0 | 9.1536 | 37.78
2021-04-13 11:00 | 44299.4583 | 0 | 8.9777 | 37.78
2021-04-13 11:30 | 44299.4792 | 0 | 9.2148 | 37.78
2021-04-13 12:00 | 44299.5 | 0 | 9.5202 | 37.78
2021-04-13 12:30 | 44299.5208 | 0 | 9.8504 | 37.78
2021-04-13 13:00 | 44299.5417 | 0 | 9.6924 | 37.78
2021-04-13 13:30 | 44299.5625 | 0 | 9.8756 | 37.78
2021-04-13 14:00 | 44299.5833 | 0 | 10.7129 | 37.78
2021-04-13 14:30 | 44299.6042 | 0 | 11.4483 | 37.78
2021-04-13 15:00 | 44299.625 | 0 | 11.4287 | 37.78
2021-04-13 15:30 | 44299.6458 | 0 | 11.5978 | 37.78
2021-04-13 16:00 | 44299.6667 | 0 | 12.1757 | 37.78
2021-04-13 16:30 | 44299.6875 | 0 | 12.7906 | 37.78
2021-04-13 17:00 | 44299.7083 | 0 | 12.9455 | 37.78
2021-04-13 17:30 | 44299.7292 | 0 | 13.3431 | 37.78
2021-04-13 18:00 | 44299.75 | 0 | 13.5199 | 37.78
2021-04-13 18:30 | 44299.7708 | 0 | 13.8073 | 37.78
2021-04-13 19:00 | 44299.7917 | 0 | 13.4439 | 37.78
2021-04-13 19:30 | 44299.8125 | 0 | 13.1251 | 37.78
2021-04-13 20:00 | 44299.8333 | 0 | 12.6636 | 37.78
2021-04-13 20:30 | 44299.8542 | 0 | 12.0549 | 37.78
2021-04-13 21:00 | 44299.875 | 0 | 11.6253 | 37.78
2021-04-13 21:30 | 44299.8958 | 0 | 11.3818 | 37.78
2021-04-13 22:00 | 44299.9167 | 0 | 10.8454 | 37.78
2021-04-13 22:30 | 44299.9375 | 0 | 10.0095 | 37.78
2021-04-13 23:00 | 44299.9583 | 0 | 9.4495 | 37.78
2021-04-13 23:30 | 44299.9792 | 0 | 8.9834 | 37.78
2021-04-14 | 44300 | 0 | 8.5202 | 37.78
2021-04-14 00:30 | 44300.0208 | 0 | 8.1852 | 37.78
2021-04-14 01:00 | 44300.0417 | 0 | 7.9083 | 37.78
2021-04-14 01:30 | 44300.0625 | 0 | 7.7197 | 37.78
2021-04-14 02:00 | 44300.0833 | 0 | 7.7945 | 37.78
2021-04-14 02:30 | 44300.1042 | 0 | 7.7502 | 37.78
2021-04-14 03:00 | 44300.125 | 0 | 7.6992 | 37.78
2021-04-14 03:30 | 44300.1458 | 0 | 7.9151 | 37.78
2021-04-14 04:00 | 44300.1667 | 0 | 8.0209 | 37.78
2021-04-14 04:30 | 44300.1875 | 0 | 8.3618 | 37.78
2021-04-14 05:00 | 44300.2083 | 0 | 8.8202 | 37.78
2021-04-14 05:30 | 44300.2292 | 0 | 9.3071 | 37.78
2021-04-14 06:00 | 44300.25 | 0 | 10.0906 | 37.78
2021-04-14 06:30 | 44300.2708 | 0 | 10.5233 | 37.78
2021-04-14 07:00 | 44300.2917 | 0 | 10.6296 | 37.78
2021-04-14 07:30 | 44300.3125 | 0 | 10.5431 | 37.78
2021-04-14 08:00 | 44300.3333 | 0 | 10.3036 | 37.78
2021-04-14 08:30 | 44300.3542 | 0 | 10.1884 | 37.78
2021-04-14 09:00 | 44300.375 | 0 | 9.6931 | 37.78
2021-04-14 09:30 | 44300.3958 | 0 | 9.6322 | 37.78
2021-04-14 10:00 | 44300.4167 | 0 | 9.2977 | 37.78
2021-04-14 10:30 | 44300.4375 | 0 | 9.7311 | 37.78
2021-04-14 11:00 | 44300.4583 | 0 | 9.616 | 37.78
2021-04-14 11:30 | 44300.4792 | 0 | 9.8366 | 37.78
2021-04-14 12:00 | 44300.5 | 0 | 9.5777 | 37.78
2021-04-14 12:30 | 44300.5208 | 0 | 10.4317 | 37.78
2021-04-14 13:00 | 44300.5417 | 0 | 10.4716 | 37.78
2021-04-14 13:30 | 44300.5625 | 0 | 10.6918 | 37.78
2021-04-14 14:00 | 44300.5833 | 0 | 10.9962 | 37.78
2021-04-14 14:30 | 44300.6042 | 0 | 11.6652 | 37.78
2021-04-14 15:00 | 44300.625 | 0 | 12.0133 | 37.78
2021-04-14 15:30 | 44300.6458 | 0 | 12.5227 | 37.78
2021-04-14 16:00 | 44300.6667 | 0 | 13.1314 | 37.78
2021-04-14 16:30 | 44300.6875 | 0 | 13.3907 | 37.78
2021-04-14 17:00 | 44300.7083 | 0 | 13.6632 | 37.78
2021-04-14 17:30 | 44300.7292 | 0 | 13.9595 | 37.78
2021-04-14 18:00 | 44300.75 | 0 | 13.9505 | 37.78
2021-04-14 18:30 | 44300.7708 | 0 | 14.0974 | 37.78
2021-04-14 19:00 | 44300.7917 | 0 | 13.8296 | 37.78
2021-04-14 19:30 | 44300.8125 | 0 | 13.4187 | 37.78
2021-04-14 20:00 | 44300.8333 | 0 | 13.0526 | 37.78
2021-04-14 20:30 | 44300.8542 | 0 | 12.6584 | 37.78
2021-04-14 21:00 | 44300.875 | 0 | 12.114 | 37.78
2021-04-14 21:30 | 44300.8958 | 0 | 11.6189 | 37.78
2021-04-14 22:00 | 44300.9167 | 0 | 11.1321 | 37.78
2021-04-14 22:30 | 44300.9375 | 0 | 10.255 | 37.78
2021-04-14 23:00 | 44300.9583 | 0 | 9.6219 | 37.78
2021-04-14 23:30 | 44300.9792 | 0 | 9.3147 | 37.78
2021-04-15 | 44301 | 0 | 8.8231 | 37.78
2021-04-15 00:30 | 44301.0208 | 0 | 8.453 | 37.78
2021-04-15 01:00 | 44301.0417 | 0 | 8.3618 | 37.78
2021-04-15 01:30 | 44301.0625 | 0 | 8.2365 | 37.78
2021-04-15 02:00 | 44301.0833 | 0 | 8.1392 | 37.78
2021-04-15 02:30 | 44301.1042 | 0 | 8.0218 | 37.78
2021-04-15 03:00 | 44301.125 | 0 | 8.0186 | 37.78
2021-04-15 03:30 | 44301.1458 | 0 | 8.0911 | 37.78
2021-04-15 04:00 | 44301.1667 | 0 | 8.1681 | 37.78
2021-04-15 04:30 | 44301.1875 | 0 | 8.6403 | 37.78
2021-04-15 05:00 | 44301.2083 | 0 | 9.1984 | 37.78
2021-04-15 05:30 | 44301.2292 | 0 | 9.5885 | 37.78
2021-04-15 06:00 | 44301.25 | 0 | 10.0909 | 37.78
2021-04-15 06:30 | 44301.2708 | 0 | 10.568 | 37.78
2021-04-15 07:00 | 44301.2917 | 0 | 10.9437 | 37.78
2021-04-15 07:30 | 44301.3125 | 0 | 10.9407 | 37.78
2021-04-15 08:00 | 44301.3333 | 0 | 10.8756 | 37.78
2021-04-15 08:30 | 44301.3542 | 0 | 10.6526 | 37.78
2021-04-15 09:00 | 44301.375 | 0 | 10.6276 | 37.78
2021-04-15 09:30 | 44301.3958 | 0 | 10.3585 | 37.78
2021-04-15 10:00 | 44301.4167 | 0 | 10.3165 | 37.78
2021-04-15 10:30 | 44301.4375 | 0 | 10.3549 | 37.78
2021-04-15 11:00 | 44301.4583 | 0 | 10.2425 | 37.78
2021-04-15 11:30 | 44301.4792 | 0 | 10.3122 | 37.78
2021-04-15 12:00 | 44301.5 | 0 | 10.441 | 37.78
2021-04-15 12:30 | 44301.5208 | 0 | 10.7894 | 37.78
2021-04-15 13:00 | 44301.5417 | 0 | 10.9017 | 37.78
2021-04-15 13:30 | 44301.5625 | 0 | 11.547 | 37.78
2021-04-15 14:00 | 44301.5833 | 0 | 12.2206 | 37.78
2021-04-15 14:30 | 44301.6042 | 0 | 13.6468 | 37.78
2021-04-15 15:00 | 44301.625 | 0 | 12.6768 | 37.78
2021-04-15 15:30 | 44301.6458 | 0 | 14.0261 | 37.78
2021-04-15 16:00 | 44301.6667 | 0 | 13.9725 | 37.78
2021-04-15 16:30 | 44301.6875 | 0 | 13.9112 | 37.78
2021-04-15 17:00 | 44301.7083 | 0 | 13.8723 | 37.78
2021-04-15 17:30 | 44301.7292 | 0 | 14.011 | 37.78
2021-04-15 18:00 | 44301.75 | 0 | 14.1218 | 37.78
2021-04-15 18:30 | 44301.7708 | 0 | 13.7991 | 37.78
2021-04-15 19:00 | 44301.7917 | 0 | 13.5622 | 37.78
2021-04-15 19:30 | 44301.8125 | 0 | 13.3738 | 37.78
2021-04-15 20:00 | 44301.8333 | 0 | 13.1466 | 37.78
2021-04-15 20:30 | 44301.8542 | 0 | 12.5658 | 37.78
2021-04-15 21:00 | 44301.875 | 0 | 12.0523 | 37.78
2021-04-15 21:30 | 44301.8958 | 0 | 11.8563 | 37.78
2021-04-15 22:00 | 44301.9167 | 0 | 11.2187 | 37.78
2021-04-15 22:30 | 44301.9375 | 0 | 10.4031 | 37.78
2021-04-15 23:00 | 44301.9583 | 0 | 9.8746 | 37.78
2021-04-15 23:30 | 44301.9792 | 0 | 9.6543 | 37.78
2021-04-16 | 44302 | 0 | 9.0664 | 37.78
2021-04-16 00:30 | 44302.0208 | 0 | 8.609 | 37.78
2021-04-16 01:00 | 44302.0417 | 0 | 8.2749 | 37.78
2021-04-16 01:30 | 44302.0625 | 0 | 8.1542 | 37.78
2021-04-16 02:00 | 44302.0833 | 0 | 8.0789 | 37.78
2021-04-16 02:30 | 44302.1042 | 0 | 8.0147 | 37.78
2021-04-16 03:00 | 44302.125 | 0 | 7.8467 | 37.78
2021-04-16 03:30 | 44302.1458 | 0 | 7.9739 | 37.78
2021-04-16 04:00 | 44302.1667 | 0 | 7.9806 | 37.78
2021-04-16 04:30 | 44302.1875 | 0 | 8.0744 | 37.78
2021-04-16 05:00 | 44302.2083 | 0 | 8.2929 | 37.78
2021-04-16 05:30 | 44302.2292 | 0 | 8.4386 | 37.78
2021-04-16 06:00 | 44302.25 | 0 | 8.5427 | 37.78
2021-04-16 06:30 | 44302.2708 | 0 | 9.0191 | 37.78
2021-04-16 07:00 | 44302.2917 | 0 | 9.4313 | 37.78
2021-04-16 07:30 | 44302.3125 | 0 | 9.8515 | 37.78
2021-04-16 08:00 | 44302.3333 | 0 | 9.9023 | 37.78
2021-04-16 08:30 | 44302.3542 | 0 | 10.1885 | 37.78
2021-04-16 09:00 | 44302.375 | 0 | 10.6056 | 37.78
2021-04-16 09:30 | 44302.3958 | 0 | 10.6151 | 37.78
2021-04-16 10:00 | 44302.4167 | 0 | 10.7177 | 37.78
2021-04-16 10:30 | 44302.4375 | 0 | 9.8932 | 37.78
2021-04-16 11:00 | 44302.4583 | 0 | 9.3661 | 37.78
2021-04-16 11:30 | 44302.4792 | 0 | 10.4951 | 37.78
2021-04-16 12:00 | 44302.5 | 0 | 9.4801 | 37.78
2021-04-16 12:30 | 44302.5208 | 0 | 8.3962 | 37.78
2021-04-16 13:00 | 44302.5417 | 0 | 9.606 | 37.78
2021-04-16 13:30 | 44302.5625 | 0 | 9.7798 | 37.78
2021-04-16 14:00 | 44302.5833 | 0 | 9.7105 | 37.78
2021-04-16 14:30 | 44302.6042 | 0 | 9.9298 | 37.78
2021-04-16 15:00 | 44302.625 | 0 | 9.7789 | 37.78
2021-04-16 15:30 | 44302.6458 | 0 | 10.0171 | 37.78
2021-04-16 16:00 | 44302.6667 | 0 | 10.4703 | 37.78
2021-04-16 16:30 | 44302.6875 | 0 | 11.2698 | 37.78
2021-04-16 17:00 | 44302.7083 | 0 | 11.5374 | 37.78
2021-04-16 17:30 | 44302.7292 | 0 | 11.6556 | 37.78
2021-04-16 18:00 | 44302.75 | 0 | 11.691 | 37.78
2021-04-16 18:30 | 44302.7708 | 0 | 11.6162 | 37.78
2021-04-16 19:00 | 44302.7917 | 0 | 11.1867 | 37.78
2021-04-16 19:30 | 44302.8125 | 0 | 11.1438 | 37.78
2021-04-16 20:00 | 44302.8333 | 0 | 10.7013 | 37.78
2021-04-16 20:30 | 44302.8542 | 0 | 10.2527 | 37.78
2021-04-16 21:00 | 44302.875 | 0 | 9.8143 | 37.78
2021-04-16 21:30 | 44302.8958 | 0 | 9.7386 | 37.78
2021-04-16 22:00 | 44302.9167 | 0 | 9.438 | 37.78
2021-04-16 22:30 | 44302.9375 | 0 | 8.8387 | 37.78
2021-04-16 23:00 | 44302.9583 | 0 | 8.3991 | 37.78
2021-04-16 23:30 | 44302.9792 | 0 | 7.9991 | 37.78
2021-04-17 | 44303 | 0 | 7.6332 | 37.78
2021-04-17 00:30 | 44303.0208 | 0 | 7.4369 | 37.78
2021-04-17 01:00 | 44303.0417 | 0 | 7.1237 | 37.78
2021-04-17 01:30 | 44303.0625 | 0 | 7.043 | 37.78
2021-04-17 02:00 | 44303.0833 | 0 | 7.1524 | 37.78
2021-04-17 02:30 | 44303.1042 | 0 | 7.0619 | 37.78
2021-04-17 03:00 | 44303.125 | 0 | 7.0031 | 37.78
2021-04-17 03:30 | 44303.1458 | 0 | 6.8949 | 37.78
2021-04-17 04:00 | 44303.1667 | 0 | 6.9138 | 37.78
2021-04-17 04:30 | 44303.1875 | 0 | 6.8886 | 37.78
2021-04-17 05:00 | 44303.2083 | 0 | 6.976 | 37.78
2021-04-17 05:30 | 44303.2292 | 0 | 7.1312 | 37.78
2021-04-17 06:00 | 44303.25 | 0 | 7.1522 | 37.78
2021-04-17 06:30 | 44303.2708 | 0 | 7.3447 | 37.78
2021-04-17 07:00 | 44303.2917 | 0 | 7.0626 | 37.78
2021-04-17 07:30 | 44303.3125 | 0 | 6.9294 | 37.78
2021-04-17 08:00 | 44303.3333 | 0 | 7.0567 | 37.78
2021-04-17 08:30 | 44303.3542 | 0 | 6.7934 | 37.78
2021-04-17 09:00 | 44303.375 | 0 | 6.5835 | 37.78
2021-04-17 09:30 | 44303.3958 | 0 | 6.3218 | 37.78
2021-04-17 10:00 | 44303.4167 | 0 | 5.9501 | 37.78
2021-04-17 10:30 | 44303.4375 | 0 | 5.9668 | 37.78
2021-04-17 11:00 | 44303.4583 | 0 | 5.7857 | 37.78
2021-04-17 11:30 | 44303.4792 | 0 | 5.8953 | 37.78
2021-04-17 12:00 | 44303.5 | 0 | 6.3783 | 37.78
2021-04-17 12:30 | 44303.5208 | 0 | 6.3633 | 37.78
2021-04-17 13:00 | 44303.5417 | 0 | 6.3667 | 37.78
2021-04-17 13:30 | 44303.5625 | 0 | 7.3888 | 37.78
2021-04-17 14:00 | 44303.5833 | 0 | 7.3519 | 37.78
2021-04-17 14:30 | 44303.6042 | 0 | 8.331 | 37.78
2021-04-17 15:00 | 44303.625 | 0 | 9.3914 | 37.78
2021-04-17 15:30 | 44303.6458 | 0 | 9.869 | 37.78
2021-04-17 16:00 | 44303.6667 | 0 | 9.9126 | 37.78
2021-04-17 16:30 | 44303.6875 | 0 | 10.2725 | 37.78
2021-04-17 17:00 | 44303.7083 | 0 | 10.8591 | 37.78
2021-04-17 17:30 | 44303.7292 | 0 | 11.4953 | 37.78
2021-04-17 18:00 | 44303.75 | 0 | 12.0378 | 37.78
2021-04-17 18:30 | 44303.7708 | 0 | 11.9443 | 37.78
2021-04-17 19:00 | 44303.7917 | 0 | 11.4133 | 37.78
2021-04-17 19:30 | 44303.8125 | 0 | 11.0828 | 37.78
2021-04-17 20:00 | 44303.8333 | 0 | 10.7118 | 37.78
2021-04-17 20:30 | 44303.8542 | 0 | 10.3784 | 37.78
2021-04-17 21:00 | 44303.875 | 0 | 9.7572 | 37.78
2021-04-17 21:30 | 44303.8958 | 0 | 9.4918 | 37.78
2021-04-17 22:00 | 44303.9167 | 0 | 9.1111 | 37.78
2021-04-17 22:30 | 44303.9375 | 0 | 8.4252 | 37.78
2021-04-17 23:00 | 44303.9583 | 0 | 7.913 | 37.78
2021-04-17 23:30 | 44303.9792 | 0 | 7.6809 | 37.78
2021-04-18 | 44304 | 0 | 7.4571 | 37.78
2021-04-18 00:30 | 44304.0208 | 0 | 7.2487 | 37.78
2021-04-18 01:00 | 44304.0417 | 0 | 7.0411 | 37.78
2021-04-18 01:30 | 44304.0625 | 0 | 7.1096 | 37.78
2021-04-18 02:00 | 44304.0833 | 0 | 7.0642 | 37.78
2021-04-18 02:30 | 44304.1042 | 0 | 7.0501 | 37.78
2021-04-18 03:00 | 44304.125 | 0 | 7.0222 | 37.78
2021-04-18 03:30 | 44304.1458 | 0 | 7.193 | 37.78
2021-04-18 04:00 | 44304.1667 | 0 | 7.3975 | 37.78
2021-04-18 04:30 | 44304.1875 | 0 | 7.7853 | 37.78
2021-04-18 05:00 | 44304.2083 | 0 | 8.4117 | 37.78
2021-04-18 05:30 | 44304.2292 | 0 | 9.1245 | 37.78
2021-04-18 06:00 | 44304.25 | 0 | 9.9054 | 37.78
2021-04-18 06:30 | 44304.2708 | 0 | 10.7448 | 37.78
2021-04-18 07:00 | 44304.2917 | 0 | 11.0037 | 37.78
2021-04-18 07:30 | 44304.3125 | 0 | 10.7041 | 37.78
2021-04-18 08:00 | 44304.3333 | 0 | 10.1768 | 37.78
2021-04-18 08:30 | 44304.3542 | 0 | 9.8832 | 37.78
2021-04-18 09:00 | 44304.375 | 0 | 9.6418 | 37.78
2021-04-18 09:30 | 44304.3958 | 0 | 9.369 | 37.78
2021-04-18 10:00 | 44304.4167 | 0 | 9.1495 | 37.78
2021-04-18 10:30 | 44304.4375 | 0 | 8.9311 | 37.78
2021-04-18 11:00 | 44304.4583 | 0 | 8.9793 | 37.78
2021-04-18 11:30 | 44304.4792 | 0 | 8.9533 | 37.78
2021-04-18 12:00 | 44304.5 | 0 | 9.1823 | 37.78
2021-04-18 12:30 | 44304.5208 | 0 | 9.0362 | 37.78
2021-04-18 13:00 | 44304.5417 | 0 | 9.6537 | 37.78
2021-04-18 13:30 | 44304.5625 | 0 | 9.7314 | 37.78
2021-04-18 14:00 | 44304.5833 | 0 | 10.3145 | 37.78
2021-04-18 14:30 | 44304.6042 | 0 | 11.5862 | 37.78
2021-04-18 15:00 | 44304.625 | 0 | 12.2408 | 37.78
2021-04-18 15:30 | 44304.6458 | 0 | 12.0103 | 37.78
2021-04-18 16:00 | 44304.6667 | 0 | 12.0425 | 37.78
2021-04-18 16:30 | 44304.6875 | 0 | 12.876 | 37.78
2021-04-18 17:00 | 44304.7083 | 0 | 13.0226 | 37.78
2021-04-18 17:30 | 44304.7292 | 0 | 13.6828 | 37.78
2021-04-18 18:00 | 44304.75 | 0 | 13.9333 | 37.78
2021-04-18 18:30 | 44304.7708 | 0 | 13.8642 | 37.78
2021-04-18 19:00 | 44304.7917 | 0 | 13.3703 | 37.78
2021-04-18 19:30 | 44304.8125 | 0 | 13.1634 | 37.78
2021-04-18 20:00 | 44304.8333 | 0 | 12.7748 | 37.78
2021-04-18 20:30 | 44304.8542 | 0 | 12.2989 | 37.78
2021-04-18 21:00 | 44304.875 | 0 | 11.6157 | 37.78
2021-04-18 21:30 | 44304.8958 | 0 | 11.3318 | 37.78
2021-04-18 22:00 | 44304.9167 | 0 | 10.7982 | 37.78
2021-04-18 22:30 | 44304.9375 | 0 | 9.8899 | 37.78
2021-04-18 23:00 | 44304.9583 | 0 | 9.2048 | 37.78
2021-04-18 23:30 | 44304.9792 | 0 | 9.0571 | 37.78
2021-04-19 | 44305 | 0 | 8.6005 | 37.78
2021-04-19 00:30 | 44305.0208 | 0 | 8.1822 | 37.78
2021-04-19 01:00 | 44305.0417 | 0 | 8.0268 | 37.78
2021-04-19 01:30 | 44305.0625 | 0 | 7.8933 | 37.78
2021-04-19 02:00 | 44305.0833 | 0 | 7.8086 | 37.78
2021-04-19 02:30 | 44305.1042 | 0 | 7.6335 | 37.78
2021-04-19 03:00 | 44305.125 | 0 | 7.5515 | 37.78
2021-04-19 03:30 | 44305.1458 | 0 | 7.7811 | 37.78
2021-04-19 04:00 | 44305.1667 | 0 | 8.0694 | 37.78
2021-04-19 04:30 | 44305.1875 | 0 | 8.4547 | 37.78
2021-04-19 05:00 | 44305.2083 | 0 | 8.8925 | 37.78
2021-04-19 05:30 | 44305.2292 | 0 | 9.6158 | 37.78
2021-04-19 06:00 | 44305.25 | 0 | 10.4136 | 37.78
2021-04-19 06:30 | 44305.2708 | 0 | 10.9821 | 37.78
2021-04-19 07:00 | 44305.2917 | 0 | 11.3642 | 37.78
2021-04-19 07:30 | 44305.3125 | 0 | 11.0145 | 37.78
2021-04-19 08:00 | 44305.3333 | 0 | 10.5807 | 37.78
2021-04-19 08:30 | 44305.3542 | 0 | 10.0361 | 37.78
2021-04-19 09:00 | 44305.375 | 0 | 9.7076 | 37.78
2021-04-19 09:30 | 44305.3958 | 0 | 9.5983 | 37.78
2021-04-19 10:00 | 44305.4167 | 0 | 9.7374 | 37.78
2021-04-19 10:30 | 44305.4375 | 0 | 9.6192 | 37.78
2021-04-19 11:00 | 44305.4583 | 0 | 9.535 | 37.78
2021-04-19 11:30 | 44305.4792 | 0 | 10.6068 | 37.78
2021-04-19 12:00 | 44305.5 | 0 | 11.6155 | 37.78
2021-04-19 12:30 | 44305.5208 | 0 | 10.947 | 37.78
2021-04-19 13:00 | 44305.5417 | 0 | 10.4022 | 37.78
2021-04-19 13:30 | 44305.5625 | 0 | 10.207 | 37.78
2021-04-19 14:00 | 44305.5833 | 0 | 10.6236 | 37.78
2021-04-19 14:30 | 44305.6042 | 0 | 11.0946 | 37.78
2021-04-19 15:00 | 44305.625 | 0 | 11.6452 | 37.78
2021-04-19 15:30 | 44305.6458 | 0 | 12.4658 | 37.78
2021-04-19 16:00 | 44305.6667 | 0 | 12.9207 | 37.78
2021-04-19 16:30 | 44305.6875 | 0 | 13.3942 | 37.78
2021-04-19 17:00 | 44305.7083 | 0 | 13.6836 | 37.78
2021-04-19 17:30 | 44305.7292 | 0 | 14.1757 | 37.78
2021-04-19 18:00 | 44305.75 | 0 | 14.3446 | 37.78
2021-04-19 18:30 | 44305.7708 | 0 | 14.3028 | 37.78
2021-04-19 19:00 | 44305.7917 | 0 | 13.9001 | 37.78
2021-04-19 19:30 | 44305.8125 | 0 | 13.5853 | 37.78
2021-04-19 20:00 | 44305.8333 | 0 | 13.2039 | 37.78
2021-04-19 20:30 | 44305.8542 | 0 | 12.6914 | 37.78
2021-04-19 21:00 | 44305.875 | 0 | 11.9358 | 37.78
2021-04-19 21:30 | 44305.8958 | 0 | 11.6013 | 37.78
2021-04-19 22:00 | 44305.9167 | 0 | 11.0253 | 37.78
2021-04-19 22:30 | 44305.9375 | 0 | 10.263 | 37.78
2021-04-19 23:00 | 44305.9583 | 0 | 9.6881 | 37.78
2021-04-19 23:30 | 44305.9792 | 0 | 9.4528 | 37.78
2021-04-20 | 44306 | 0 | 8.8042 | 37.78
2021-04-20 00:30 | 44306.0208 | 0 | 8.3501 | 37.78
2021-04-20 01:00 | 44306.0417 | 0 | 8.1663 | 37.78
2021-04-20 01:30 | 44306.0625 | 0 | 7.9756 | 37.78
2021-04-20 02:00 | 44306.0833 | 0 | 7.8947 | 37.78
2021-04-20 02:30 | 44306.1042 | 0 | 7.9266 | 37.78
2021-04-20 03:00 | 44306.125 | 0 | 7.8752 | 37.78
2021-04-20 03:30 | 44306.1458 | 0 | 8.0127 | 37.78
2021-04-20 04:00 | 44306.1667 | 0 | 8.3072 | 37.78
2021-04-20 04:30 | 44306.1875 | 0 | 8.5006 | 37.78
2021-04-20 05:00 | 44306.2083 | 0 | 8.9999 | 37.78
2021-04-20 05:30 | 44306.2292 | 0 | 9.6383 | 37.78
2021-04-20 06:00 | 44306.25 | 0 | 10.5773 | 37.78
2021-04-20 06:30 | 44306.2708 | 0 | 11.349 | 37.78
2021-04-20 07:00 | 44306.2917 | 0 | 11.5072 | 37.78
2021-04-20 07:30 | 44306.3125 | 0 | 11.1487 | 37.78
2021-04-20 08:00 | 44306.3333 | 0 | 10.8738 | 37.78
2021-04-20 08:30 | 44306.3542 | 0 | 10.6958 | 37.78
2021-04-20 09:00 | 44306.375 | 0 | 10.4889 | 37.78
2021-04-20 09:30 | 44306.3958 | 0 | 10.4026 | 37.78
2021-04-20 10:00 | 44306.4167 | 0 | 10.4799 | 37.78
2021-04-20 10:30 | 44306.4375 | 0 | 10.1911 | 37.78
2021-04-20 11:00 | 44306.4583 | 0 | 10.21 | 37.78
2021-04-20 11:30 | 44306.4792 | 0 | 10.345 | 37.78
2021-04-20 12:00 | 44306.5 | 0 | 10.518 | 37.78
2021-04-20 12:30 | 44306.5208 | 0 | 10.8552 | 37.78
2021-04-20 13:00 | 44306.5417 | 0 | 11.0769 | 37.78
2021-04-20 13:30 | 44306.5625 | 0 | 11.4868 | 37.78
2021-04-20 14:00 | 44306.5833 | 0 | 12.0735 | 37.78
2021-04-20 14:30 | 44306.6042 | 0 | 12.2962 | 37.78
2021-04-20 15:00 | 44306.625 | 0 | 12.7144 | 37.78
2021-04-20 15:30 | 44306.6458 | 0 | 13.2097 | 37.78
2021-04-20 16:00 | 44306.6667 | 0 | 13.7749 | 37.78
2021-04-20 16:30 | 44306.6875 | 0 | 13.8274 | 37.78
2021-04-20 17:00 | 44306.7083 | 0 | 13.7917 | 37.78
2021-04-20 17:30 | 44306.7292 | 0 | 14.2239 | 37.78
2021-04-20 18:00 | 44306.75 | 0 | 14.4826 | 37.78
2021-04-20 18:30 | 44306.7708 | 0 | 14.3843 | 37.78
2021-04-20 19:00 | 44306.7917 | 0 | 13.8394 | 37.78
2021-04-20 19:30 | 44306.8125 | 0 | 13.5066 | 37.78
2021-04-20 20:00 | 44306.8333 | 0 | 13.1227 | 37.78
2021-04-20 20:30 | 44306.8542 | 0 | 12.5258 | 37.78
2021-04-20 21:00 | 44306.875 | 0 | 12.0963 | 37.78
2021-04-20 21:30 | 44306.8958 | 0 | 11.6931 | 37.78
2021-04-20 22:00 | 44306.9167 | 0 | 11.0023 | 37.78
2021-04-20 22:30 | 44306.9375 | 0 | 10.1865 | 37.78
2021-04-20 23:00 | 44306.9583 | 0 | 9.5608 | 37.78
2021-04-20 23:30 | 44306.9792 | 0 | 9.1898 | 37.78
2021-04-21 | 44307 | 0 | 8.6358 | 37.78
2021-04-21 00:30 | 44307.0208 | 0 | 8.3146 | 37.78
2021-04-21 01:00 | 44307.0417 | 0 | 8.0575 | 37.78
2021-04-21 01:30 | 44307.0625 | 0 | 7.9191 | 37.78
2021-04-21 02:00 | 44307.0833 | 0 | 7.892 | 37.78
2021-04-21 02:30 | 44307.1042 | 0 | 7.7773 | 37.78
2021-04-21 03:00 | 44307.125 | 0 | 7.6665 | 37.78
2021-04-21 03:30 | 44307.1458 | 0 | 7.8768 | 37.78
2021-04-21 04:00 | 44307.1667 | 0 | 8.062 | 37.78
2021-04-21 04:30 | 44307.1875 | 0 | 8.3769 | 37.78
2021-04-21 05:00 | 44307.2083 | 0 | 8.9651 | 37.78
2021-04-21 05:30 | 44307.2292 | 0 | 9.5399 | 37.78
2021-04-21 06:00 | 44307.25 | 0 | 10.1452 | 37.78
2021-04-21 06:30 | 44307.2708 | 0 | 10.9464 | 37.78
2021-04-21 07:00 | 44307.2917 | 0 | 11.9686 | 37.78
2021-04-21 07:30 | 44307.3125 | 0 | 12.4444 | 37.78
2021-04-21 08:00 | 44307.3333 | 0 | 12.1228 | 37.78
2021-04-21 08:30 | 44307.3542 | 0 | 11.9023 | 37.78
2021-04-21 09:00 | 44307.375 | 0 | 12.1373 | 37.78
2021-04-21 09:30 | 44307.3958 | 0 | 11.4144 | 37.78
2021-04-21 10:00 | 44307.4167 | 0 | 11.395 | 37.78
2021-04-21 10:30 | 44307.4375 | 0 | 11.5118 | 37.78
2021-04-21 11:00 | 44307.4583 | 0 | 11.5905 | 37.78
2021-04-21 11:30 | 44307.4792 | 0 | 11.5516 | 37.78
2021-04-21 12:00 | 44307.5 | 0 | 10.9956 | 37.78
2021-04-21 12:30 | 44307.5208 | 0 | 11.3267 | 37.78
2021-04-21 13:00 | 44307.5417 | 0 | 12.1979 | 37.78
2021-04-21 13:30 | 44307.5625 | 0 | 11.7071 | 37.78
2021-04-21 14:00 | 44307.5833 | 0 | 11.7289 | 37.78
2021-04-21 14:30 | 44307.6042 | 0 | 12.3429 | 37.78
2021-04-21 15:00 | 44307.625 | 0 | 12.3879 | 37.78
2021-04-21 15:30 | 44307.6458 | 0 | 12.3561 | 37.78
2021-04-21 16:00 | 44307.6667 | 0 | 12.7187 | 37.78
2021-04-21 16:30 | 44307.6875 | 0 | 12.9759 | 37.78
2021-04-21 17:00 | 44307.7083 | 0 | 13.1749 | 37.78
2021-04-21 17:30 | 44307.7292 | 0 | 13.084 | 37.78
2021-04-21 18:00 | 44307.75 | 0 | 13.4063 | 37.78
2021-04-21 18:30 | 44307.7708 | 0 | 13.6247 | 37.78
2021-04-21 19:00 | 44307.7917 | 0 | 13.0928 | 37.78
2021-04-21 19:30 | 44307.8125 | 0 | 12.9565 | 37.78
2021-04-21 20:00 | 44307.8333 | 0 | 12.6186 | 37.78
2021-04-21 20:30 | 44307.8542 | 0 | 12.1644 | 37.78
2021-04-21 21:00 | 44307.875 | 0 | 11.6707 | 37.78
2021-04-21 21:30 | 44307.8958 | 0 | 11.2631 | 37.78
2021-04-21 22:00 | 44307.9167 | 0 | 10.6617 | 37.78
2021-04-21 22:30 | 44307.9375 | 0 | 9.7625 | 37.78
2021-04-21 23:00 | 44307.9583 | 0 | 9.1214 | 37.78
2021-04-21 23:30 | 44307.9792 | 0 | 8.7612 | 37.78
2021-04-22 | 44308 | 0 | 8.2148 | 37.78
2021-04-22 00:30 | 44308.0208 | 0 | 8.1189 | 37.78
2021-04-22 01:00 | 44308.0417 | 0 | 7.7649 | 37.78
2021-04-22 01:30 | 44308.0625 | 0 | 7.6582 | 37.78
2021-04-22 02:00 | 44308.0833 | 0 | 7.6809 | 37.78
2021-04-22 02:30 | 44308.1042 | 0 | 7.5128 | 37.78
2021-04-22 03:00 | 44308.125 | 0 | 7.4681 | 37.78
2021-04-22 03:30 | 44308.1458 | 0 | 7.6922 | 37.78
2021-04-22 04:00 | 44308.1667 | 0 | 7.9968 | 37.78
2021-04-22 04:30 | 44308.1875 | 0 | 8.2801 | 37.78
2021-04-22 05:00 | 44308.2083 | 0 | 8.8433 | 37.78
2021-04-22 05:30 | 44308.2292 | 0 | 9.5151 | 37.78
2021-04-22 06:00 | 44308.25 | 0 | 10.4824 | 37.78
2021-04-22 06:30 | 44308.2708 | 0 | 11.4569 | 37.78
2021-04-22 07:00 | 44308.2917 | 0 | 11.7321 | 37.78
2021-04-22 07:30 | 44308.3125 | 0 | 11.3852 | 37.78
2021-04-22 08:00 | 44308.3333 | 0 | 10.8252 | 37.78
2021-04-22 08:30 | 44308.3542 | 0 | 10.285 | 37.78
2021-04-22 09:00 | 44308.375 | 0 | 9.6317 | 37.78
2021-04-22 09:30 | 44308.3958 | 0 | 9.2766 | 37.78
2021-04-22 10:00 | 44308.4167 | 0 | 8.7987 | 37.78
2021-04-22 10:30 | 44308.4375 | 0 | 8.7353 | 37.78
2021-04-22 11:00 | 44308.4583 | 0 | 8.6174 | 37.78
2021-04-22 11:30 | 44308.4792 | 0 | 8.4398 | 37.78
2021-04-22 12:00 | 44308.5 | 0 | 8.3728 | 37.78
2021-04-22 12:30 | 44308.5208 | 0 | 8.4727 | 37.78
2021-04-22 13:00 | 44308.5417 | 0 | 8.5451 | 37.78
2021-04-22 13:30 | 44308.5625 | 0 | 8.8906 | 37.78
2021-04-22 14:00 | 44308.5833 | 0 | 9.5372 | 37.78
2021-04-22 14:30 | 44308.6042 | 0 | 9.978 | 37.78
2021-04-22 15:00 | 44308.625 | 0 | 10.3942 | 37.78
2021-04-22 15:30 | 44308.6458 | 0 | 11.0292 | 37.78
2021-04-22 16:00 | 44308.6667 | 0 | 11.5947 | 37.78
2021-04-22 16:30 | 44308.6875 | 0 | 11.9616 | 37.78
2021-04-22 17:00 | 44308.7083 | 0 | 12.165 | 37.78
2021-04-22 17:30 | 44308.7292 | 0 | 12.5073 | 37.78
2021-04-22 18:00 | 44308.75 | 0 | 12.7939 | 37.78
2021-04-22 18:30 | 44308.7708 | 0 | 12.7647 | 37.78
2021-04-22 19:00 | 44308.7917 | 0 | 12.3181 | 37.78
2021-04-22 19:30 | 44308.8125 | 0 | 12.0459 | 37.78
2021-04-22 20:00 | 44308.8333 | 0 | 11.9475 | 37.78
2021-04-22 20:30 | 44308.8542 | 0 | 11.4932 | 37.78
2021-04-22 21:00 | 44308.875 | 0 | 11.0851 | 37.78
2021-04-22 21:30 | 44308.8958 | 0 | 10.8867 | 37.78
2021-04-22 22:00 | 44308.9167 | 0 | 10.3426 | 37.78
2021-04-22 22:30 | 44308.9375 | 0 | 9.6753 | 37.78
2021-04-22 23:00 | 44308.9583 | 0 | 9.2035 | 37.78
2021-04-22 23:30 | 44308.9792 | 0 | 8.8177 | 37.78
2021-04-23 | 44309 | 0 | 8.2318 | 37.78
2021-04-23 00:30 | 44309.0208 | 0 | 7.9674 | 37.78
2021-04-23 01:00 | 44309.0417 | 0 | 7.6292 | 37.78
2021-04-23 01:30 | 44309.0625 | 0 | 7.4927 | 37.78
2021-04-23 02:00 | 44309.0833 | 0 | 7.4784 | 37.78
2021-04-23 02:30 | 44309.1042 | 0 | 7.2417 | 37.78
2021-04-23 03:00 | 44309.125 | 0 | 7.1727 | 37.78
2021-04-23 03:30 | 44309.1458 | 0 | 7.378 | 37.78
2021-04-23 04:00 | 44309.1667 | 0 | 7.4536 | 37.78
2021-04-23 04:30 | 44309.1875 | 0 | 7.6925 | 37.78
2021-04-23 05:00 | 44309.2083 | 0 | 7.8012 | 37.78
2021-04-23 05:30 | 44309.2292 | 0 | 7.9436 | 37.78
2021-04-23 06:00 | 44309.25 | 0 | 8.3194 | 37.78
2021-04-23 06:30 | 44309.2708 | 0 | 8.5773 | 37.78
2021-04-23 07:00 | 44309.2917 | 0 | 8.5236 | 37.78
2021-04-23 07:30 | 44309.3125 | 0 | 8.3721 | 37.78
2021-04-23 08:00 | 44309.3333 | 0 | 8.3377 | 37.78
2021-04-23 08:30 | 44309.3542 | 0 | 7.8549 | 37.78
2021-04-23 09:00 | 44309.375 | 0 | 7.5494 | 37.78
2021-04-23 09:30 | 44309.3958 | 0 | 7.2262 | 37.78
2021-04-23 10:00 | 44309.4167 | 0 | 6.8434 | 37.78
2021-04-23 10:30 | 44309.4375 | 0 | 6.5858 | 37.78
2021-04-23 11:00 | 44309.4583 | 0 | 6.2142 | 37.78
2021-04-23 11:30 | 44309.4792 | 0 | 6.665 | 37.78
2021-04-23 12:00 | 44309.5 | 0 | 7.0684 | 37.78
2021-04-23 12:30 | 44309.5208 | 0 | 7.4094 | 37.78
2021-04-23 13:00 | 44309.5417 | 0 | 6.4313 | 37.78
2021-04-23 13:30 | 44309.5625 | 0 | 6.8015 | 37.78
2021-04-23 14:00 | 44309.5833 | 0 | 7.586 | 37.78
2021-04-23 14:30 | 44309.6042 | 0 | 7.8929 | 37.78
2021-04-23 15:00 | 44309.625 | 0 | 8.7017 | 37.78
2021-04-23 15:30 | 44309.6458 | 0 | 8.9083 | 37.78
2021-04-23 16:00 | 44309.6667 | 0 | 9.4898 | 37.78
2021-04-23 16:30 | 44309.6875 | 0 | 10.1547 | 37.78
2021-04-23 17:00 | 44309.7083 | 0 | 10.5132 | 37.78
2021-04-23 17:30 | 44309.7292 | 0 | 10.8527 | 37.78
2021-04-23 18:00 | 44309.75 | 0 | 11.0508 | 37.78
2021-04-23 18:30 | 44309.7708 | 0 | 11.0567 | 37.78
2021-04-23 19:00 | 44309.7917 | 0 | 10.7166 | 37.78
2021-04-23 19:30 | 44309.8125 | 0 | 10.452 | 37.78
2021-04-23 20:00 | 44309.8333 | 0 | 10.2703 | 37.78
2021-04-23 20:30 | 44309.8542 | 0 | 9.9174 | 37.78
2021-04-23 21:00 | 44309.875 | 0 | 9.6373 | 37.78
2021-04-23 21:30 | 44309.8958 | 0 | 9.3347 | 37.78
2021-04-23 22:00 | 44309.9167 | 0 | 9.0027 | 37.78
2021-04-23 22:30 | 44309.9375 | 0 | 8.5092 | 37.78
2021-04-23 23:00 | 44309.9583 | 0 | 8.0735 | 37.78
2021-04-23 23:30 | 44309.9792 | 0 | 7.7894 | 37.78
2021-04-24 | 44310 | 0 | 7.4615 | 37.78
2021-04-24 00:30 | 44310.0208 | 0 | 7.1825 | 37.78
2021-04-24 01:00 | 44310.0417 | 0 | 7.1375 | 37.78
2021-04-24 01:30 | 44310.0625 | 0 | 6.8666 | 37.78
2021-04-24 02:00 | 44310.0833 | 0 | 6.8788 | 37.78
2021-04-24 02:30 | 44310.1042 | 0 | 6.8523 | 37.78
2021-04-24 03:00 | 44310.125 | 0 | 6.7405 | 37.78
2021-04-24 03:30 | 44310.1458 | 0 | 6.7943 | 37.78
2021-04-24 04:00 | 44310.1667 | 0 | 6.7723 | 37.78
2021-04-24 04:30 | 44310.1875 | 0 | 6.7092 | 37.78
2021-04-24 05:00 | 44310.2083 | 0 | 6.7851 | 37.78
2021-04-24 05:30 | 44310.2292 | 0 | 7.0234 | 37.78
2021-04-24 06:00 | 44310.25 | 0 | 7.2146 | 37.78
2021-04-24 06:30 | 44310.2708 | 0 | 7.1355 | 37.78
2021-04-24 07:00 | 44310.2917 | 0 | 7.2415 | 37.78
2021-04-24 07:30 | 44310.3125 | 0 | 6.8142 | 37.78
2021-04-24 08:00 | 44310.3333 | 0 | 6.4036 | 37.78
2021-04-24 08:30 | 44310.3542 | 0 | 6.3699 | 37.78
2021-04-24 09:00 | 44310.375 | 0 | 6.1244 | 37.78
2021-04-24 09:30 | 44310.3958 | 0 | 5.9158 | 37.78
2021-04-24 10:00 | 44310.4167 | 0 | 5.5709 | 37.78
2021-04-24 10:30 | 44310.4375 | 0 | 5.4798 | 37.78
2021-04-24 11:00 | 44310.4583 | 0 | 5.2783 | 37.78
2021-04-24 11:30 | 44310.4792 | 0 | 5.2333 | 37.78
2021-04-24 12:00 | 44310.5 | 0 | 5.2724 | 37.78
2021-04-24 12:30 | 44310.5208 | 0 | 5.4938 | 37.78
2021-04-24 13:00 | 44310.5417 | 0 | 5.5729 | 37.78
2021-04-24 13:30 | 44310.5625 | 0 | 5.9031 | 37.78
2021-04-24 14:00 | 44310.5833 | 0 | 6.2843 | 37.78
2021-04-24 14:30 | 44310.6042 | 0 | 7.5106 | 37.78
2021-04-24 15:00 | 44310.625 | 0 | 8.1577 | 37.78
2021-04-24 15:30 | 44310.6458 | 0 | 8.1532 | 37.78
2021-04-24 16:00 | 44310.6667 | 0 | 8.9036 | 37.78
2021-04-24 16:30 | 44310.6875 | 0 | 9.5035 | 37.78
2021-04-24 17:00 | 44310.7083 | 0 | 10.1148 | 37.78
2021-04-24 17:30 | 44310.7292 | 0 | 10.3516 | 37.78
2021-04-24 18:00 | 44310.75 | 0 | 10.5736 | 37.78
2021-04-24 18:30 | 44310.7708 | 0 | 10.5011 | 37.78
2021-04-24 19:00 | 44310.7917 | 0 | 10.2058 | 37.78
2021-04-24 19:30 | 44310.8125 | 0 | 9.9768 | 37.78
2021-04-24 20:00 | 44310.8333 | 0 | 9.7499 | 37.78
2021-04-24 20:30 | 44310.8542 | 0 | 9.5005 | 37.78
2021-04-24 21:00 | 44310.875 | 0 | 9.1294 | 37.78
2021-04-24 21:30 | 44310.8958 | 0 | 8.8655 | 37.78
2021-04-24 22:00 | 44310.9167 | 0 | 8.6444 | 37.78
2021-04-24 22:30 | 44310.9375 | 0 | 8.0141 | 37.78
2021-04-24 23:00 | 44310.9583 | 0 | 7.717 | 37.78
2021-04-24 23:30 | 44310.9792 | 0 | 7.4488 | 37.78
2021-04-25 | 44311 | 0 | 7.2606 | 37.78
2021-04-25 00:30 | 44311.0208 | 0 | 7.016 | 37.78
2021-04-25 01:00 | 44311.0417 | 0 | 6.8141 | 37.78
2021-04-25 01:30 | 44311.0625 | 0 | 6.7664 | 37.78
2021-04-25 02:00 | 44311.0833 | 0 | 6.7131 | 37.78
2021-04-25 02:30 | 44311.1042 | 0 | 6.6814 | 37.78
2021-04-25 03:00 | 44311.125 | 0 | 6.5904 | 37.78
2021-04-25 03:30 | 44311.1458 | 0 | 6.6097 | 37.78
2021-04-25 04:00 | 44311.1667 | 0 | 6.6582 | 37.78
2021-04-25 04:30 | 44311.1875 | 0 | 6.8651 | 37.78
2021-04-25 05:00 | 44311.2083 | 0 | 6.9943 | 37.78
2021-04-25 05:30 | 44311.2292 | 0 | 7.1911 | 37.78
2021-04-25 06:00 | 44311.25 | 0 | 7.4135 | 37.78
2021-04-25 06:30 | 44311.2708 | 0 | 7.5853 | 37.78
2021-04-25 07:00 | 44311.2917 | 0 | 7.5359 | 37.78
2021-04-25 07:30 | 44311.3125 | 0 | 7.5011 | 37.78
2021-04-25 08:00 | 44311.3333 | 0 | 7.427 | 37.78
2021-04-25 08:30 | 44311.3542 | 0 | 7.3745 | 37.78
2021-04-25 09:00 | 44311.375 | 0 | 7.201 | 37.78
2021-04-25 09:30 | 44311.3958 | 0 | 6.9728 | 37.78
2021-04-25 10:00 | 44311.4167 | 0 | 6.847 | 37.78
2021-04-25 10:30 | 44311.4375 | 0 | 7.8472 | 37.78
2021-04-25 11:00 | 44311.4583 | 0 | 6.9531 | 37.78
2021-04-25 11:30 | 44311.4792 | 0 | 8.6464 | 37.78
2021-04-25 12:00 | 44311.5 | 0 | 7.7679 | 37.78
2021-04-25 12:30 | 44311.5208 | 0 | 7.766 | 37.78
2021-04-25 13:00 | 44311.5417 | 0 | 8.503 | 37.78
2021-04-25 13:30 | 44311.5625 | 0 | 7.9114 | 37.78
2021-04-25 14:00 | 44311.5833 | 0 | 8.0515 | 37.78
2021-04-25 14:30 | 44311.6042 | 0 | 9.2304 | 37.78
2021-04-25 15:00 | 44311.625 | 0 | 8.8648 | 37.78
2021-04-25 15:30 | 44311.6458 | 0 | 9.1581 | 37.78
2021-04-25 16:00 | 44311.6667 | 0 | 10.2263 | 37.78
2021-04-25 16:30 | 44311.6875 | 0 | 10.6226 | 37.78
2021-04-25 17:00 | 44311.7083 | 0 | 11.3868 | 37.78
2021-04-25 17:30 | 44311.7292 | 0 | 11.9208 | 37.78
2021-04-25 18:00 | 44311.75 | 0 | 12.1499 | 37.78
2021-04-25 18:30 | 44311.7708 | 0 | 11.8842 | 37.78
2021-04-25 19:00 | 44311.7917 | 0 | 11.4469 | 37.78
2021-04-25 19:30 | 44311.8125 | 0 | 11.2377 | 37.78
2021-04-25 20:00 | 44311.8333 | 0 | 10.9945 | 37.78
2021-04-25 20:30 | 44311.8542 | 0 | 10.4057 | 37.78
2021-04-25 21:00 | 44311.875 | 0 | 9.9357 | 37.78
2021-04-25 21:30 | 44311.8958 | 0 | 9.5698 | 37.78
2021-04-25 22:00 | 44311.9167 | 0 | 9.0916 | 37.78
2021-04-25 22:30 | 44311.9375 | 0 | 8.437 | 37.78
2021-04-25 23:00 | 44311.9583 | 0 | 7.9991 | 37.78
2021-04-25 23:30 | 44311.9792 | 0 | 7.7379 | 37.78
2021-04-26 | 44312 | 0 | 7.3396 | 37.78
2021-04-26 00:30 | 44312.0208 | 0 | 7.2911 | 37.78
2021-04-26 01:00 | 44312.0417 | 0 | 7.1268 | 37.78
2021-04-26 01:30 | 44312.0625 | 0 | 7.0932 | 37.78
2021-04-26 02:00 | 44312.0833 | 0 | 7.1848 | 37.78
2021-04-26 02:30 | 44312.1042 | 0 | 7.0756 | 37.78
2021-04-26 03:00 | 44312.125 | 0 | 6.9512 | 37.78
2021-04-26 03:30 | 44312.1458 | 0 | 7.2369 | 37.78
2021-04-26 04:00 | 44312.1667 | 0 | 7.5403 | 37.78
2021-04-26 04:30 | 44312.1875 | 0 | 8.0524 | 37.78
2021-04-26 05:00 | 44312.2083 | 0 | 8.2845 | 37.78
2021-04-26 05:30 | 44312.2292 | 0 | 9.0445 | 37.78
2021-04-26 06:00 | 44312.25 | 0 | 10.1012 | 37.78
2021-04-26 06:30 | 44312.2708 | 0 | 10.9108 | 37.78
2021-04-26 07:00 | 44312.2917 | 0 | 11.421 | 37.78
2021-04-26 07:30 | 44312.3125 | 0 | 11.0696 | 37.78
2021-04-26 08:00 | 44312.3333 | 0 | 10.8929 | 37.78
2021-04-26 08:30 | 44312.3542 | 0 | 10.3028 | 37.78
2021-04-26 09:00 | 44312.375 | 0 | 9.8896 | 37.78
2021-04-26 09:30 | 44312.3958 | 0 | 9.5671 | 37.78
2021-04-26 10:00 | 44312.4167 | 0 | 9.3198 | 37.78
2021-04-26 10:30 | 44312.4375 | 0 | 9.4419 | 37.78
2021-04-26 11:00 | 44312.4583 | 0 | 10.2984 | 37.78
2021-04-26 11:30 | 44312.4792 | 0 | 10.7456 | 37.78
2021-04-26 12:00 | 44312.5 | 0 | 11.062 | 37.78
2021-04-26 12:30 | 44312.5208 | 0 | 10.274 | 37.78
2021-04-26 13:00 | 44312.5417 | 0 | 10.4647 | 37.78
2021-04-26 13:30 | 44312.5625 | 0 | 10.3155 | 37.78
2021-04-26 14:00 | 44312.5833 | 0 | 11.9601 | 37.78
2021-04-26 14:30 | 44312.6042 | 0 | 11.122 | 37.78
2021-04-26 15:00 | 44312.625 | 0 | 12.0504 | 37.78
2021-04-26 15:30 | 44312.6458 | 0 | 11.9789 | 37.78
2021-04-26 16:00 | 44312.6667 | 0 | 12.3764 | 37.78
2021-04-26 16:30 | 44312.6875 | 0 | 13.0283 | 37.78
2021-04-26 17:00 | 44312.7083 | 0 | 13.266 | 37.78
2021-04-26 17:30 | 44312.7292 | 0 | 13.6463 | 37.78
2021-04-26 18:00 | 44312.75 | 0 | 13.645 | 37.78
2021-04-26 18:30 | 44312.7708 | 0 | 13.7233 | 37.78
2021-04-26 19:00 | 44312.7917 | 0 | 13.3761 | 37.78
2021-04-26 19:30 | 44312.8125 | 0 | 13.1089 | 37.78
2021-04-26 20:00 | 44312.8333 | 0 | 12.824 | 37.78
2021-04-26 20:30 | 44312.8542 | 0 | 12.3178 | 37.78
2021-04-26 21:00 | 44312.875 | 0 | 11.6899 | 37.78
2021-04-26 21:30 | 44312.8958 | 0 | 11.3094 | 37.78
2021-04-26 22:00 | 44312.9167 | 0 | 10.8414 | 37.78
2021-04-26 22:30 | 44312.9375 | 0 | 9.9873 | 37.78
2021-04-26 23:00 | 44312.9583 | 0 | 9.3818 | 37.78
2021-04-26 23:30 | 44312.9792 | 0 | 9.05 | 37.78
2021-04-27 | 44313 | 0 | 8.4534 | 37.78
2021-04-27 00:30 | 44313.0208 | 0 | 8.1644 | 37.78
2021-04-27 01:00 | 44313.0417 | 0 | 7.9407 | 37.78
2021-04-27 01:30 | 44313.0625 | 0 | 7.7323 | 37.78
2021-04-27 02:00 | 44313.0833 | 0 | 7.599 | 37.78
2021-04-27 02:30 | 44313.1042 | 0 | 7.5265 | 37.78
2021-04-27 03:00 | 44313.125 | 0 | 7.5676 | 37.78
2021-04-27 03:30 | 44313.1458 | 0 | 7.7893 | 37.78
2021-04-27 04:00 | 44313.1667 | 0 | 8.1107 | 37.78
2021-04-27 04:30 | 44313.1875 | 0 | 8.4349 | 37.78
2021-04-27 05:00 | 44313.2083 | 0 | 9.033 | 37.78
2021-04-27 05:30 | 44313.2292 | 0 | 9.707 | 37.78
2021-04-27 06:00 | 44313.25 | 0 | 10.5614 | 37.78
2021-04-27 06:30 | 44313.2708 | 0 | 11.397 | 37.78
2021-04-27 07:00 | 44313.2917 | 0 | 11.6822 | 37.78
2021-04-27 07:30 | 44313.3125 | 0 | 11.2983 | 37.78
2021-04-27 08:00 | 44313.3333 | 0 | 10.9725 | 37.78
2021-04-27 08:30 | 44313.3542 | 0 | 10.3048 | 37.78
2021-04-27 09:00 | 44313.375 | 0 | 9.8068 | 37.78
2021-04-27 09:30 | 44313.3958 | 0 | 9.6987 | 37.78
2021-04-27 10:00 | 44313.4167 | 0 | 10.4689 | 37.78
2021-04-27 10:30 | 44313.4375 | 0 | 11.0038 | 37.78
2021-04-27 11:00 | 44313.4583 | 0 | 11.7338 | 37.78
2021-04-27 11:30 | 44313.4792 | 0 | 11.0517 | 37.78
2021-04-27 12:00 | 44313.5 | 0 | 10.7961 | 37.78
2021-04-27 12:30 | 44313.5208 | 0 | 10.2614 | 37.78
2021-04-27 13:00 | 44313.5417 | 0 | 11.3747 | 37.78
2021-04-27 13:30 | 44313.5625 | 0 | 11.8992 | 37.78
2021-04-27 14:00 | 44313.5833 | 0 | 12.2571 | 37.78
2021-04-27 14:30 | 44313.6042 | 0 | 12.4828 | 37.78
2021-04-27 15:00 | 44313.625 | 0 | 12.3532 | 37.78
2021-04-27 15:30 | 44313.6458 | 0 | 12.2419 | 37.78
2021-04-27 16:00 | 44313.6667 | 0 | 12.2561 | 37.78
2021-04-27 16:30 | 44313.6875 | 0 | 12.7272 | 37.78
2021-04-27 17:00 | 44313.7083 | 0 | 13.1413 | 37.78
2021-04-27 17:30 | 44313.7292 | 0 | 13.7238 | 37.78
2021-04-27 18:00 | 44313.75 | 0 | 13.6605 | 37.78
2021-04-27 18:30 | 44313.7708 | 0 | 13.7166 | 37.78
2021-04-27 19:00 | 44313.7917 | 0 | 13.2778 | 37.78
2021-04-27 19:30 | 44313.8125 | 0 | 13.0791 | 37.78
2021-04-27 20:00 | 44313.8333 | 0 | 12.898 | 37.78
2021-04-27 20:30 | 44313.8542 | 0 | 12.3165 | 37.78
2021-04-27 21:00 | 44313.875 | 0 | 11.7016 | 37.78
2021-04-27 21:30 | 44313.8958 | 0 | 11.2916 | 37.78
2021-04-27 22:00 | 44313.9167 | 0 | 10.895 | 37.78
2021-04-27 22:30 | 44313.9375 | 0 | 10.0239 | 37.78
2021-04-27 23:00 | 44313.9583 | 0 | 9.4375 | 37.78
2021-04-27 23:30 | 44313.9792 | 0 | 8.966 | 37.78
2021-04-28 | 44314 | 0 | 8.5783 | 37.78
2021-04-28 00:30 | 44314.0208 | 0 | 8.1981 | 37.78
2021-04-28 01:00 | 44314.0417 | 0 | 7.9473 | 37.78
2021-04-28 01:30 | 44314.0625 | 0 | 7.8195 | 37.78
2021-04-28 02:00 | 44314.0833 | 0 | 7.6699 | 37.78
2021-04-28 02:30 | 44314.1042 | 0 | 7.6969 | 37.78
2021-04-28 03:00 | 44314.125 | 0 | 7.6393 | 37.78
2021-04-28 03:30 | 44314.1458 | 0 | 7.8246 | 37.78
2021-04-28 04:00 | 44314.1667 | 0 | 8.0542 | 37.78
2021-04-28 04:30 | 44314.1875 | 0 | 8.514 | 37.78
2021-04-28 05:00 | 44314.2083 | 0 | 9.1124 | 37.78
2021-04-28 05:30 | 44314.2292 | 0 | 9.6197 | 37.78
2021-04-28 06:00 | 44314.25 | 0 | 10.7679 | 37.78
2021-04-28 06:30 | 44314.2708 | 0 | 11.6858 | 37.78
2021-04-28 07:00 | 44314.2917 | 0 | 12.1662 | 37.78
2021-04-28 07:30 | 44314.3125 | 0 | 11.3943 | 37.78
2021-04-28 08:00 | 44314.3333 | 0 | 11.1406 | 37.78
2021-04-28 08:30 | 44314.3542 | 0 | 11.5101 | 37.78
2021-04-28 09:00 | 44314.375 | 0 | 10.9493 | 37.78
2021-04-28 09:30 | 44314.3958 | 0 | 9.91 | 37.78
2021-04-28 10:00 | 44314.4167 | 0 | 10.2339 | 37.78
2021-04-28 10:30 | 44314.4375 | 0 | 10.9523 | 37.78
2021-04-28 11:00 | 44314.4583 | 0 | 11.3743 | 37.78
2021-04-28 11:30 | 44314.4792 | 0 | 9.7749 | 37.78
2021-04-28 12:00 | 44314.5 | 0 | 9.9224 | 37.78
2021-04-28 12:30 | 44314.5208 | 0 | 10.0212 | 37.78
2021-04-28 13:00 | 44314.5417 | 0 | 9.7608 | 37.78
2021-04-28 13:30 | 44314.5625 | 0 | 11.1531 | 37.78
2021-04-28 14:00 | 44314.5833 | 0 | 11.7166 | 37.78
2021-04-28 14:30 | 44314.6042 | 0 | 10.9482 | 37.78
2021-04-28 15:00 | 44314.625 | 0 | 12.1287 | 37.78
2021-04-28 15:30 | 44314.6458 | 0 | 11.6882 | 37.78
2021-04-28 16:00 | 44314.6667 | 0 | 12.6078 | 37.78
2021-04-28 16:30 | 44314.6875 | 0 | 13.0213 | 37.78
2021-04-28 17:00 | 44314.7083 | 0 | 13.2321 | 37.78
2021-04-28 17:30 | 44314.7292 | 0 | 13.8128 | 37.78
2021-04-28 18:00 | 44314.75 | 0 | 13.7798 | 37.78
2021-04-28 18:30 | 44314.7708 | 0 | 13.7668 | 37.78
2021-04-28 19:00 | 44314.7917 | 0 | 13.3338 | 37.78
2021-04-28 19:30 | 44314.8125 | 0 | 13.2895 | 37.78
2021-04-28 20:00 | 44314.8333 | 0 | 13.0487 | 37.78
2021-04-28 20:30 | 44314.8542 | 0 | 12.3833 | 37.78
2021-04-28 21:00 | 44314.875 | 0 | 11.9805 | 37.78
2021-04-28 21:30 | 44314.8958 | 0 | 11.6675 | 37.78
2021-04-28 22:00 | 44314.9167 | 0 | 11.0458 | 37.78
2021-04-28 22:30 | 44314.9375 | 0 | 10.414 | 37.78
2021-04-28 23:00 | 44314.9583 | 0 | 9.6734 | 37.78
2021-04-28 23:30 | 44314.9792 | 0 | 9.435 | 37.78
2021-04-29 | 44315 | 0 | 8.8419 | 37.78
2021-04-29 00:30 | 44315.0208 | 0 | 8.4225 | 37.78
2021-04-29 01:00 | 44315.0417 | 0 | 8.1648 | 37.78
2021-04-29 01:30 | 44315.0625 | 0 | 8.043 | 37.78
2021-04-29 02:00 | 44315.0833 | 0 | 7.9151 | 37.78
2021-04-29 02:30 | 44315.1042 | 0 | 8.0025 | 37.78
2021-04-29 03:00 | 44315.125 | 0 | 7.9281 | 37.78
2021-04-29 03:30 | 44315.1458 | 0 | 7.997 | 37.78
2021-04-29 04:00 | 44315.1667 | 0 | 8.2265 | 37.78
2021-04-29 04:30 | 44315.1875 | 0 | 8.5368 | 37.78
2021-04-29 05:00 | 44315.2083 | 0 | 9.1011 | 37.78
2021-04-29 05:30 | 44315.2292 | 0 | 9.8609 | 37.78
2021-04-29 06:00 | 44315.25 | 0 | 10.5047 | 37.78
2021-04-29 06:30 | 44315.2708 | 0 | 11.3309 | 37.78
2021-04-29 07:00 | 44315.2917 | 0 | 12.1074 | 37.78
2021-04-29 07:30 | 44315.3125 | 0 | 12.0227 | 37.78
2021-04-29 08:00 | 44315.3333 | 0 | 11.8448 | 37.78
2021-04-29 08:30 | 44315.3542 | 0 | 11.3046 | 37.78
2021-04-29 09:00 | 44315.375 | 0 | 11.6515 | 37.78
2021-04-29 09:30 | 44315.3958 | 0 | 11.5672 | 37.78
2021-04-29 10:00 | 44315.4167 | 0 | 11.3164 | 37.78
2021-04-29 10:30 | 44315.4375 | 0 | 12.8877 | 37.78
2021-04-29 11:00 | 44315.4583 | 0 | 11.4767 | 37.78
2021-04-29 11:30 | 44315.4792 | 0 | 9.3764 | 37.78
2021-04-29 12:00 | 44315.5 | 0 | 10.348 | 37.78
2021-04-29 12:30 | 44315.5208 | 0 | 11.5251 | 37.78
2021-04-29 13:00 | 44315.5417 | 0 | 12.317 | 37.78
2021-04-29 13:30 | 44315.5625 | 0 | 12.4207 | 37.78
2021-04-29 14:00 | 44315.5833 | 0 | 12.0709 | 37.78
2021-04-29 14:30 | 44315.6042 | 0 | 12.4655 | 37.78
2021-04-29 15:00 | 44315.625 | 0 | 12.2988 | 37.78
2021-04-29 15:30 | 44315.6458 | 0 | 12.2269 | 37.78
2021-04-29 16:00 | 44315.6667 | 0 | 12.5046 | 37.78
2021-04-29 16:30 | 44315.6875 | 0 | 12.8197 | 37.78
2021-04-29 17:00 | 44315.7083 | 0 | 12.9473 | 37.78
2021-04-29 17:30 | 44315.7292 | 0 | 13.4288 | 37.78
2021-04-29 18:00 | 44315.75 | 0 | 13.4425 | 37.78
2021-04-29 18:30 | 44315.7708 | 0 | 13.1497 | 37.78
2021-04-29 19:00 | 44315.7917 | 0 | 12.8754 | 37.78
2021-04-29 19:30 | 44315.8125 | 0 | 12.6989 | 37.78
2021-04-29 20:00 | 44315.8333 | 0 | 12.3161 | 37.78
2021-04-29 20:30 | 44315.8542 | 0 | 11.6647 | 37.78
2021-04-29 21:00 | 44315.875 | 0 | 11.3505 | 37.78
2021-04-29 21:30 | 44315.8958 | 0 | 10.9748 | 37.78
2021-04-29 22:00 | 44315.9167 | 0 | 10.5792 | 37.78
2021-04-29 22:30 | 44315.9375 | 0 | 9.8524 | 37.78
2021-04-29 23:00 | 44315.9583 | 0 | 9.4484 | 37.78
2021-04-29 23:30 | 44315.9792 | 0 | 9.1438 | 37.78
2021-04-30 | 44316 | 0 | 8.5318 | 37.78
2021-04-30 00:30 | 44316.0208 | 0 | 8.1449 | 37.78
2021-04-30 01:00 | 44316.0417 | 0 | 7.8737 | 37.78
2021-04-30 01:30 | 44316.0625 | 0 | 7.6747 | 37.78
2021-04-30 02:00 | 44316.0833 | 0 | 7.6711 | 37.78
2021-04-30 02:30 | 44316.1042 | 0 | 7.3745 | 37.78
2021-04-30 03:00 | 44316.125 | 0 | 7.2448 | 37.78
2021-04-30 03:30 | 44316.1458 | 0 | 7.5057 | 37.78
2021-04-30 04:00 | 44316.1667 | 0 | 7.5097 | 37.78
2021-04-30 04:30 | 44316.1875 | 0 | 7.5294 | 37.78
2021-04-30 05:00 | 44316.2083 | 0 | 7.8584 | 37.78
2021-04-30 05:30 | 44316.2292 | 0 | 7.9531 | 37.78
2021-04-30 06:00 | 44316.25 | 0 | 8.2363 | 37.78
2021-04-30 06:30 | 44316.2708 | 0 | 8.6587 | 37.78
2021-04-30 07:00 | 44316.2917 | 0 | 9.31 | 37.78
2021-04-30 07:30 | 44316.3125 | 0 | 9.7119 | 37.78
2021-04-30 08:00 | 44316.3333 | 0 | 9.9814 | 37.78
2021-04-30 08:30 | 44316.3542 | 0 | 10.2672 | 37.78
2021-04-30 09:00 | 44316.375 | 0 | 9.8721 | 37.78
2021-04-30 09:30 | 44316.3958 | 0 | 9.4654 | 37.78
2021-04-30 10:00 | 44316.4167 | 0 | 9.9406 | 37.78
2021-04-30 10:30 | 44316.4375 | 0 | 10.5876 | 37.78
2021-04-30 11:00 | 44316.4583 | 0 | 10.589 | 37.78
2021-04-30 11:30 | 44316.4792 | 0 | 9.8564 | 37.78
2021-04-30 12:00 | 44316.5 | 0 | 9.7757 | 37.78
2021-04-30 12:30 | 44316.5208 | 0 | 10.3569 | 37.78
2021-04-30 13:00 | 44316.5417 | 0 | 10.1372 | 37.78
2021-04-30 13:30 | 44316.5625 | 0 | 10.3664 | 37.78
2021-04-30 14:00 | 44316.5833 | 0 | 9.5372 | 37.78
2021-04-30 14:30 | 44316.6042 | 0 | 9.4883 | 37.78
2021-04-30 15:00 | 44316.625 | 0 | 9.3898 | 37.78
2021-04-30 15:30 | 44316.6458 | 0 | 9.6151 | 37.78
2021-04-30 16:00 | 44316.6667 | 0 | 10.006 | 37.78
2021-04-30 16:30 | 44316.6875 | 0 | 10.5069 | 37.78
2021-04-30 17:00 | 44316.7083 | 0 | 10.6937 | 37.78
2021-04-30 17:30 | 44316.7292 | 0 | 11.1706 | 37.78
2021-04-30 18:00 | 44316.75 | 0 | 11.1394 | 37.78
2021-04-30 18:30 | 44316.7708 | 0 | 11.059 | 37.78
2021-04-30 19:00 | 44316.7917 | 0 | 10.8353 | 37.78
2021-04-30 19:30 | 44316.8125 | 0 | 10.5982 | 37.78
2021-04-30 20:00 | 44316.8333 | 0 | 10.3989 | 37.78
2021-04-30 20:30 | 44316.8542 | 0 | 9.8373 | 37.78
2021-04-30 21:00 | 44316.875 | 0 | 9.5272 | 37.78
2021-04-30 21:30 | 44316.8958 | 0 | 9.2598 | 37.78
2021-04-30 22:00 | 44316.9167 | 0 | 9.0195 | 37.78
2021-04-30 22:30 | 44316.9375 | 0 | 8.5998 | 37.78
2021-04-30 23:00 | 44316.9583 | 0 | 8.1848 | 37.78
2021-04-30 23:30 | 44316.9792 | 0 | 7.9093 | 37.78
2021-05-01 | 44317 | 0 | 7.5249 | 39.95
2021-05-01 00:30 | 44317.0208 | 0 | 7.3629 | 39.95
2021-05-01 01:00 | 44317.0417 | 0 | 7.1506 | 39.95
2021-05-01 01:30 | 44317.0625 | 0 | 7.0995 | 39.95
2021-05-01 02:00 | 44317.0833 | 0 | 7.0497 | 39.95
2021-05-01 02:30 | 44317.1042 | 0 | 6.9576 | 39.95
2021-05-01 03:00 | 44317.125 | 0 | 6.8557 | 39.95
2021-05-01 03:30 | 44317.1458 | 0 | 6.8714 | 39.95
2021-05-01 04:00 | 44317.1667 | 0 | 6.8926 | 39.95
2021-05-01 04:30 | 44317.1875 | 0 | 6.8565 | 39.95
2021-05-01 05:00 | 44317.2083 | 0 | 6.9861 | 39.95
2021-05-01 05:30 | 44317.2292 | 0 | 7.1699 | 39.95
2021-05-01 06:00 | 44317.25 | 0 | 7.2512 | 39.95
2021-05-01 06:30 | 44317.2708 | 0 | 7.3563 | 39.95
2021-05-01 07:00 | 44317.2917 | 0 | 7.3917 | 39.95
2021-05-01 07:30 | 44317.3125 | 0 | 7.2345 | 39.95
2021-05-01 08:00 | 44317.3333 | 0 | 7.7883 | 39.95
2021-05-01 08:30 | 44317.3542 | 0 | 6.8977 | 39.95
2021-05-01 09:00 | 44317.375 | 0 | 7.6675 | 39.95
2021-05-01 09:30 | 44317.3958 | 0 | 7.9949 | 39.95
2021-05-01 10:00 | 44317.4167 | 0 | 7.7397 | 39.95
2021-05-01 10:30 | 44317.4375 | 0 | 8.1984 | 39.95
2021-05-01 11:00 | 44317.4583 | 0 | 8.9007 | 39.95
2021-05-01 11:30 | 44317.4792 | 0 | 9.3457 | 39.95
2021-05-01 12:00 | 44317.5 | 0 | 9.0839 | 39.95
2021-05-01 12:30 | 44317.5208 | 0 | 9.2729 | 39.95
2021-05-01 13:00 | 44317.5417 | 0 | 8.6536 | 39.95
2021-05-01 13:30 | 44317.5625 | 0 | 8.782 | 39.95
2021-05-01 14:00 | 44317.5833 | 0 | 8.3144 | 39.95
2021-05-01 14:30 | 44317.6042 | 0 | 8.9382 | 39.95
2021-05-01 15:00 | 44317.625 | 0 | 9.0031 | 39.95
2021-05-01 15:30 | 44317.6458 | 0 | 9.5559 | 39.95
2021-05-01 16:00 | 44317.6667 | 0 | 9.7377 | 39.95
2021-05-01 16:30 | 44317.6875 | 0 | 10.2577 | 39.95
2021-05-01 17:00 | 44317.7083 | 0 | 10.7361 | 39.95
2021-05-01 17:30 | 44317.7292 | 0 | 10.986 | 39.95
2021-05-01 18:00 | 44317.75 | 0 | 10.9818 | 39.95
2021-05-01 18:30 | 44317.7708 | 0 | 11.1056 | 39.95
2021-05-01 19:00 | 44317.7917 | 0 | 10.6339 | 39.95
2021-05-01 19:30 | 44317.8125 | 0 | 10.395 | 39.95
2021-05-01 20:00 | 44317.8333 | 0 | 10.1367 | 39.95
2021-05-01 20:30 | 44317.8542 | 0 | 9.7673 | 39.95
2021-05-01 21:00 | 44317.875 | 0 | 9.4091 | 39.95
2021-05-01 21:30 | 44317.8958 | 0 | 9.2673 | 39.95
2021-05-01 22:00 | 44317.9167 | 0 | 9.0347 | 39.95
2021-05-01 22:30 | 44317.9375 | 0 | 8.3523 | 39.95
2021-05-01 23:00 | 44317.9583 | 0 | 7.9537 | 39.95
2021-05-01 23:30 | 44317.9792 | 0 | 7.7499 | 39.95
2021-05-02 | 44318 | 0 | 7.3773 | 39.95
2021-05-02 00:30 | 44318.0208 | 0 | 7.1962 | 39.95
2021-05-02 01:00 | 44318.0417 | 0 | 7.0607 | 39.95
2021-05-02 01:30 | 44318.0625 | 0 | 6.8561 | 39.95
2021-05-02 02:00 | 44318.0833 | 0 | 6.8025 | 39.95
2021-05-02 02:30 | 44318.1042 | 0 | 6.7143 | 39.95
2021-05-02 03:00 | 44318.125 | 0 | 6.7844 | 39.95
2021-05-02 03:30 | 44318.1458 | 0 | 6.8468 | 39.95
2021-05-02 04:00 | 44318.1667 | 0 | 6.851 | 39.95
2021-05-02 04:30 | 44318.1875 | 0 | 6.9501 | 39.95
2021-05-02 05:00 | 44318.2083 | 0 | 7.1394 | 39.95
2021-05-02 05:30 | 44318.2292 | 0 | 7.307 | 39.95
2021-05-02 06:00 | 44318.25 | 0 | 7.694 | 39.95
2021-05-02 06:30 | 44318.2708 | 0 | 7.7769 | 39.95
2021-05-02 07:00 | 44318.2917 | 0 | 7.7718 | 39.95
2021-05-02 07:30 | 44318.3125 | 0 | 7.6966 | 39.95
2021-05-02 08:00 | 44318.3333 | 0 | 7.6855 | 39.95
2021-05-02 08:30 | 44318.3542 | 0 | 7.6774 | 39.95
2021-05-02 09:00 | 44318.375 | 0 | 7.4052 | 39.95
2021-05-02 09:30 | 44318.3958 | 0 | 7.3431 | 39.95
2021-05-02 10:00 | 44318.4167 | 0 | 7.5239 | 39.95
2021-05-02 10:30 | 44318.4375 | 0 | 7.4442 | 39.95
2021-05-02 11:00 | 44318.4583 | 0 | 7.0535 | 39.95
2021-05-02 11:30 | 44318.4792 | 0 | 7.8367 | 39.95
2021-05-02 12:00 | 44318.5 | 0 | 9.0925 | 39.95
2021-05-02 12:30 | 44318.5208 | 0 | 8.5523 | 39.95
2021-05-02 13:00 | 44318.5417 | 0 | 9.2733 | 39.95
2021-05-02 13:30 | 44318.5625 | 0 | 7.9388 | 39.95
2021-05-02 14:00 | 44318.5833 | 0 | 9.2384 | 39.95
2021-05-02 14:30 | 44318.6042 | 0 | 9.4302 | 39.95
2021-05-02 15:00 | 44318.625 | 0 | 9.3532 | 39.95
2021-05-02 15:30 | 44318.6458 | 0 | 10.2588 | 39.95
2021-05-02 16:00 | 44318.6667 | 0 | 10.7497 | 39.95
2021-05-02 16:30 | 44318.6875 | 0 | 11.3958 | 39.95
2021-05-02 17:00 | 44318.7083 | 0 | 11.7663 | 39.95
2021-05-02 17:30 | 44318.7292 | 0 | 12.4319 | 39.95
2021-05-02 18:00 | 44318.75 | 0 | 12.3791 | 39.95
2021-05-02 18:30 | 44318.7708 | 0 | 12.1386 | 39.95
2021-05-02 19:00 | 44318.7917 | 0 | 11.6965 | 39.95
2021-05-02 19:30 | 44318.8125 | 0 | 11.381 | 39.95
2021-05-02 20:00 | 44318.8333 | 0 | 10.8291 | 39.95
2021-05-02 20:30 | 44318.8542 | 0 | 10.473 | 39.95
2021-05-02 21:00 | 44318.875 | 0 | 9.9933 | 39.95
2021-05-02 21:30 | 44318.8958 | 0 | 9.6211 | 39.95
2021-05-02 22:00 | 44318.9167 | 0 | 9.1148 | 39.95
2021-05-02 22:30 | 44318.9375 | 0 | 8.4826 | 39.95
2021-05-02 23:00 | 44318.9583 | 0 | 8.1278 | 39.95
2021-05-02 23:30 | 44318.9792 | 0 | 7.7969 | 39.95
2021-05-03 | 44319 | 0 | 7.4932 | 39.95
2021-05-03 00:30 | 44319.0208 | 0 | 7.3145 | 39.95
2021-05-03 01:00 | 44319.0417 | 0 | 7.2695 | 39.95
2021-05-03 01:30 | 44319.0625 | 0 | 6.9996 | 39.95
2021-05-03 02:00 | 44319.0833 | 0 | 6.7891 | 39.95
2021-05-03 02:30 | 44319.1042 | 0 | 6.7389 | 39.95
2021-05-03 03:00 | 44319.125 | 0 | 6.8244 | 39.95
2021-05-03 03:30 | 44319.1458 | 0 | 6.8897 | 39.95
2021-05-03 04:00 | 44319.1667 | 0 | 7.2074 | 39.95
2021-05-03 04:30 | 44319.1875 | 0 | 7.715 | 39.95
2021-05-03 05:00 | 44319.2083 | 0 | 8.2681 | 39.95
2021-05-03 05:30 | 44319.2292 | 0 | 8.9928 | 39.95
2021-05-03 06:00 | 44319.25 | 0 | 10.1624 | 39.95
2021-05-03 06:30 | 44319.2708 | 0 | 10.9963 | 39.95
2021-05-03 07:00 | 44319.2917 | 0 | 11.3261 | 39.95
2021-05-03 07:30 | 44319.3125 | 0 | 11.2146 | 39.95
2021-05-03 08:00 | 44319.3333 | 0 | 10.9771 | 39.95
2021-05-03 08:30 | 44319.3542 | 0 | 10.0616 | 39.95
2021-05-03 09:00 | 44319.375 | 0 | 9.4448 | 39.95
2021-05-03 09:30 | 44319.3958 | 0 | 9.2386 | 39.95
2021-05-03 10:00 | 44319.4167 | 0 | 9.0541 | 39.95
2021-05-03 10:30 | 44319.4375 | 0 | 8.9124 | 39.95
2021-05-03 11:00 | 44319.4583 | 0 | 8.8727 | 39.95
2021-05-03 11:30 | 44319.4792 | 0 | 8.9972 | 39.95
2021-05-03 12:00 | 44319.5 | 0 | 9.1962 | 39.95
2021-05-03 12:30 | 44319.5208 | 0 | 10.1584 | 39.95
2021-05-03 13:00 | 44319.5417 | 0 | 10.2669 | 39.95
2021-05-03 13:30 | 44319.5625 | 0 | 10.2521 | 39.95
2021-05-03 14:00 | 44319.5833 | 0 | 10.8341 | 39.95
2021-05-03 14:30 | 44319.6042 | 0 | 11.4557 | 39.95
2021-05-03 15:00 | 44319.625 | 0 | 11.4957 | 39.95
2021-05-03 15:30 | 44319.6458 | 0 | 12.175 | 39.95
2021-05-03 16:00 | 44319.6667 | 0 | 12.7907 | 39.95
2021-05-03 16:30 | 44319.6875 | 0 | 13.0361 | 39.95
2021-05-03 17:00 | 44319.7083 | 0 | 13.4951 | 39.95
2021-05-03 17:30 | 44319.7292 | 0 | 14.0289 | 39.95
2021-05-03 18:00 | 44319.75 | 0 | 14.2946 | 39.95
2021-05-03 18:30 | 44319.7708 | 0 | 14.1465 | 39.95
2021-05-03 19:00 | 44319.7917 | 0 | 13.7319 | 39.95
2021-05-03 19:30 | 44319.8125 | 0 | 13.6847 | 39.95
2021-05-03 20:00 | 44319.8333 | 0 | 13.2974 | 39.95
2021-05-03 20:30 | 44319.8542 | 0 | 12.5637 | 39.95
2021-05-03 21:00 | 44319.875 | 0 | 11.7847 | 39.95
2021-05-03 21:30 | 44319.8958 | 0 | 11.5296 | 39.95
2021-05-03 22:00 | 44319.9167 | 0 | 11.2073 | 39.95
2021-05-03 22:30 | 44319.9375 | 0 | 10.4369 | 39.95
2021-05-03 23:00 | 44319.9583 | 0 | 9.949 | 39.95
2021-05-03 23:30 | 44319.9792 | 0 | 9.113 | 39.95
2021-05-04 | 44320 | 0 | 8.4548 | 39.95
2021-05-04 00:30 | 44320.0208 | 0 | 7.9054 | 39.95
2021-05-04 01:00 | 44320.0417 | 0 | 7.918 | 39.95
2021-05-04 01:30 | 44320.0625 | 0 | 7.834 | 39.95
2021-05-04 02:00 | 44320.0833 | 0 | 7.8133 | 39.95
2021-05-04 02:30 | 44320.1042 | 0 | 7.78 | 39.95
2021-05-04 03:00 | 44320.125 | 0 | 7.7838 | 39.95
2021-05-04 03:30 | 44320.1458 | 0 | 8.0272 | 39.95
2021-05-04 04:00 | 44320.1667 | 0 | 8.1184 | 39.95
2021-05-04 04:30 | 44320.1875 | 0 | 8.5777 | 39.95
2021-05-04 05:00 | 44320.2083 | 0 | 9.23 | 39.95
2021-05-04 05:30 | 44320.2292 | 0 | 9.8285 | 39.95
2021-05-04 06:00 | 44320.25 | 0 | 10.6064 | 39.95
2021-05-04 06:30 | 44320.2708 | 0 | 11.5441 | 39.95
2021-05-04 07:00 | 44320.2917 | 0 | 11.513 | 39.95
2021-05-04 07:30 | 44320.3125 | 0 | 12.1376 | 39.95
2021-05-04 08:00 | 44320.3333 | 0 | 11.2805 | 39.95
2021-05-04 08:30 | 44320.3542 | 0 | 12.9002 | 39.95
2021-05-04 09:00 | 44320.375 | 0 | 13.339 | 39.95
2021-05-04 09:30 | 44320.3958 | 0 | 13.55 | 39.95
2021-05-04 10:00 | 44320.4167 | 0 | 13.171 | 39.95
2021-05-04 10:30 | 44320.4375 | 0 | 13.1783 | 39.95
2021-05-04 11:00 | 44320.4583 | 0 | 13.056 | 39.95
2021-05-04 11:30 | 44320.4792 | 0 | 12.6474 | 39.95
2021-05-04 12:00 | 44320.5 | 0 | 12.3481 | 39.95
2021-05-04 12:30 | 44320.5208 | 0 | 12.7628 | 39.95
2021-05-04 13:00 | 44320.5417 | 0 | 12.63 | 39.95
2021-05-04 13:30 | 44320.5625 | 0 | 12.6347 | 39.95
2021-05-04 14:00 | 44320.5833 | 0 | 12.8083 | 39.95
2021-05-04 14:30 | 44320.6042 | 0 | 11.6254 | 39.95
2021-05-04 15:00 | 44320.625 | 0 | 11.4461 | 39.95
2021-05-04 15:30 | 44320.6458 | 0 | 12.0829 | 39.95
2021-05-04 16:00 | 44320.6667 | 0 | 11.9047 | 39.95
2021-05-04 16:30 | 44320.6875 | 0 | 12.8765 | 39.95
2021-05-04 17:00 | 44320.7083 | 0 | 13.3727 | 39.95
2021-05-04 17:30 | 44320.7292 | 0 | 14.1851 | 39.95
2021-05-04 18:00 | 44320.75 | 0 | 14.4927 | 39.95
2021-05-04 18:30 | 44320.7708 | 0 | 14.565 | 39.95
2021-05-04 19:00 | 44320.7917 | 0 | 14.1182 | 39.95
2021-05-04 19:30 | 44320.8125 | 0 | 13.8331 | 39.95
2021-05-04 20:00 | 44320.8333 | 0 | 13.4662 | 39.95
2021-05-04 20:30 | 44320.8542 | 0 | 12.9575 | 39.95
2021-05-04 21:00 | 44320.875 | 0 | 12.367 | 39.95
2021-05-04 21:30 | 44320.8958 | 0 | 11.7437 | 39.95
2021-05-04 22:00 | 44320.9167 | 0 | 11.2751 | 39.95
2021-05-04 22:30 | 44320.9375 | 0 | 10.3883 | 39.95
2021-05-04 23:00 | 44320.9583 | 0 | 9.7137 | 39.95
2021-05-04 23:30 | 44320.9792 | 0 | 9.1948 | 39.95
2021-05-05 | 44321 | 0 | 8.6381 | 39.95
2021-05-05 00:30 | 44321.0208 | 0 | 8.2741 | 39.95
2021-05-05 01:00 | 44321.0417 | 0 | 8.0507 | 39.95
2021-05-05 01:30 | 44321.0625 | 0 | 7.9477 | 39.95
2021-05-05 02:00 | 44321.0833 | 0 | 7.8607 | 39.95
2021-05-05 02:30 | 44321.1042 | 0 | 7.8157 | 39.95
2021-05-05 03:00 | 44321.125 | 0 | 7.8286 | 39.95
2021-05-05 03:30 | 44321.1458 | 0 | 7.8245 | 39.95
2021-05-05 04:00 | 44321.1667 | 0 | 8.2286 | 39.95
2021-05-05 04:30 | 44321.1875 | 0 | 8.5823 | 39.95
2021-05-05 05:00 | 44321.2083 | 0 | 9.1678 | 39.95
2021-05-05 05:30 | 44321.2292 | 0 | 10.0873 | 39.95
2021-05-05 06:00 | 44321.25 | 0 | 11.2051 | 39.95
2021-05-05 06:30 | 44321.2708 | 0 | 12.0052 | 39.95
2021-05-05 07:00 | 44321.2917 | 0 | 12.4303 | 39.95
2021-05-05 07:30 | 44321.3125 | 0 | 11.9146 | 39.95
2021-05-05 08:00 | 44321.3333 | 0 | 11.3158 | 39.95
2021-05-05 08:30 | 44321.3542 | 0 | 10.3735 | 39.95
2021-05-05 09:00 | 44321.375 | 0 | 9.643 | 39.95
2021-05-05 09:30 | 44321.3958 | 0 | 9.3443 | 39.95
2021-05-05 10:00 | 44321.4167 | 0 | 8.7139 | 39.95
2021-05-05 10:30 | 44321.4375 | 0 | 8.7912 | 39.95
2021-05-05 11:00 | 44321.4583 | 0 | 8.5585 | 39.95
2021-05-05 11:30 | 44321.4792 | 0 | 8.5671 | 39.95
2021-05-05 12:00 | 44321.5 | 0 | 8.4722 | 39.95
2021-05-05 12:30 | 44321.5208 | 0 | 8.7952 | 39.95
2021-05-05 13:00 | 44321.5417 | 0 | 9.1107 | 39.95
2021-05-05 13:30 | 44321.5625 | 0 | 9.5395 | 39.95
2021-05-05 14:00 | 44321.5833 | 0 | 9.8685 | 39.95
2021-05-05 14:30 | 44321.6042 | 0 | 10.3902 | 39.95
2021-05-05 15:00 | 44321.625 | 0 | 10.8293 | 39.95
2021-05-05 15:30 | 44321.6458 | 0 | 11.471 | 39.95
2021-05-05 16:00 | 44321.6667 | 0 | 12.0539 | 39.95
2021-05-05 16:30 | 44321.6875 | 0 | 12.6936 | 39.95
2021-05-05 17:00 | 44321.7083 | 0 | 13.1413 | 39.95
2021-05-05 17:30 | 44321.7292 | 0 | 13.5779 | 39.95
2021-05-05 18:00 | 44321.75 | 0 | 13.7664 | 39.95
2021-05-05 18:30 | 44321.7708 | 0 | 13.7432 | 39.95
2021-05-05 19:00 | 44321.7917 | 0 | 13.5963 | 39.95
2021-05-05 19:30 | 44321.8125 | 0 | 13.449 | 39.95
2021-05-05 20:00 | 44321.8333 | 0 | 13.0845 | 39.95
2021-05-05 20:30 | 44321.8542 | 0 | 12.6095 | 39.95
2021-05-05 21:00 | 44321.875 | 0 | 12.1259 | 39.95
2021-05-05 21:30 | 44321.8958 | 0 | 11.5419 | 39.95
2021-05-05 22:00 | 44321.9167 | 0 | 11.2444 | 39.95
2021-05-05 22:30 | 44321.9375 | 0 | 10.3165 | 39.95
2021-05-05 23:00 | 44321.9583 | 0 | 9.5142 | 39.95
2021-05-05 23:30 | 44321.9792 | 0 | 9.2184 | 39.95
2021-05-06 | 44322 | 0 | 8.5148 | 39.95
2021-05-06 00:30 | 44322.0208 | 0 | 8.1464 | 39.95
2021-05-06 01:00 | 44322.0417 | 0 | 7.9348 | 39.95
2021-05-06 01:30 | 44322.0625 | 0 | 7.8784 | 39.95
2021-05-06 02:00 | 44322.0833 | 0 | 7.8266 | 39.95
2021-05-06 02:30 | 44322.1042 | 0 | 7.7475 | 39.95
2021-05-06 03:00 | 44322.125 | 0 | 7.6906 | 39.95
2021-05-06 03:30 | 44322.1458 | 0 | 7.8136 | 39.95
2021-05-06 04:00 | 44322.1667 | 0 | 8.1008 | 39.95
2021-05-06 04:30 | 44322.1875 | 0 | 8.292 | 39.95
2021-05-06 05:00 | 44322.2083 | 0 | 8.8018 | 39.95
2021-05-06 05:30 | 44322.2292 | 0 | 9.7727 | 39.95
2021-05-06 06:00 | 44322.25 | 0 | 10.537 | 39.95
2021-05-06 06:30 | 44322.2708 | 0 | 11.4601 | 39.95
2021-05-06 07:00 | 44322.2917 | 0 | 11.5425 | 39.95
2021-05-06 07:30 | 44322.3125 | 0 | 11.2522 | 39.95
2021-05-06 08:00 | 44322.3333 | 0 | 10.82 | 39.95
2021-05-06 08:30 | 44322.3542 | 0 | 10.1273 | 39.95
2021-05-06 09:00 | 44322.375 | 0 | 9.5945 | 39.95
2021-05-06 09:30 | 44322.3958 | 0 | 9.2493 | 39.95
2021-05-06 10:00 | 44322.4167 | 0 | 9.1682 | 39.95
2021-05-06 10:30 | 44322.4375 | 0 | 8.8746 | 39.95
2021-05-06 11:00 | 44322.4583 | 0 | 9.0377 | 39.95
2021-05-06 11:30 | 44322.4792 | 0 | 9.0701 | 39.95
2021-05-06 12:00 | 44322.5 | 0 | 9.2438 | 39.95
2021-05-06 12:30 | 44322.5208 | 0 | 9.2323 | 39.95
2021-05-06 13:00 | 44322.5417 | 0 | 10.6404 | 39.95
2021-05-06 13:30 | 44322.5625 | 0 | 11.6663 | 39.95
2021-05-06 14:00 | 44322.5833 | 0 | 10.4278 | 39.95
2021-05-06 14:30 | 44322.6042 | 0 | 11.4556 | 39.95
2021-05-06 15:00 | 44322.625 | 0 | 12.4628 | 39.95
2021-05-06 15:30 | 44322.6458 | 0 | 12.6391 | 39.95
2021-05-06 16:00 | 44322.6667 | 0 | 12.5853 | 39.95
2021-05-06 16:30 | 44322.6875 | 0 | 12.9629 | 39.95
2021-05-06 17:00 | 44322.7083 | 0 | 13.3227 | 39.95
2021-05-06 17:30 | 44322.7292 | 0 | 13.6219 | 39.95
2021-05-06 18:00 | 44322.75 | 0 | 13.3331 | 39.95
2021-05-06 18:30 | 44322.7708 | 0 | 13.2366 | 39.95
2021-05-06 19:00 | 44322.7917 | 0 | 13.1165 | 39.95
2021-05-06 19:30 | 44322.8125 | 0 | 12.8186 | 39.95
2021-05-06 20:00 | 44322.8333 | 0 | 12.6408 | 39.95
2021-05-06 20:30 | 44322.8542 | 0 | 12.122 | 39.95
2021-05-06 21:00 | 44322.875 | 0 | 11.8311 | 39.95
2021-05-06 21:30 | 44322.8958 | 0 | 11.4885 | 39.95
2021-05-06 22:00 | 44322.9167 | 0 | 11.0239 | 39.95
2021-05-06 22:30 | 44322.9375 | 0 | 10.1859 | 39.95
2021-05-06 23:00 | 44322.9583 | 0 | 9.5774 | 39.95
2021-05-06 23:30 | 44322.9792 | 0 | 9.1369 | 39.95
2021-05-07 | 44323 | 0 | 8.627 | 39.95
2021-05-07 00:30 | 44323.0208 | 0 | 8.3064 | 39.95
2021-05-07 01:00 | 44323.0417 | 0 | 8.1632 | 39.95
2021-05-07 01:30 | 44323.0625 | 0 | 7.9548 | 39.95
2021-05-07 02:00 | 44323.0833 | 0 | 7.8788 | 39.95
2021-05-07 02:30 | 44323.1042 | 0 | 7.7498 | 39.95
2021-05-07 03:00 | 44323.125 | 0 | 7.6765 | 39.95
2021-05-07 03:30 | 44323.1458 | 0 | 7.8556 | 39.95
2021-05-07 04:00 | 44323.1667 | 0 | 7.8783 | 39.95
2021-05-07 04:30 | 44323.1875 | 0 | 8.0165 | 39.95
2021-05-07 05:00 | 44323.2083 | 0 | 8.3744 | 39.95
2021-05-07 05:30 | 44323.2292 | 0 | 8.5328 | 39.95
2021-05-07 06:00 | 44323.25 | 0 | 8.7449 | 39.95
2021-05-07 06:30 | 44323.2708 | 0 | 9.1595 | 39.95
2021-05-07 07:00 | 44323.2917 | 0 | 9.2218 | 39.95
2021-05-07 07:30 | 44323.3125 | 0 | 9.1172 | 39.95
2021-05-07 08:00 | 44323.3333 | 0 | 9.0327 | 39.95
2021-05-07 08:30 | 44323.3542 | 0 | 8.7106 | 39.95
2021-05-07 09:00 | 44323.375 | 0 | 8.495 | 39.95
2021-05-07 09:30 | 44323.3958 | 0 | 8.2762 | 39.95
2021-05-07 10:00 | 44323.4167 | 0 | 8.0046 | 39.95
2021-05-07 10:30 | 44323.4375 | 0 | 7.6588 | 39.95
2021-05-07 11:00 | 44323.4583 | 0 | 7.4282 | 39.95
2021-05-07 11:30 | 44323.4792 | 0 | 7.4049 | 39.95
2021-05-07 12:00 | 44323.5 | 0 | 7.3799 | 39.95
2021-05-07 12:30 | 44323.5208 | 0 | 8.0893 | 39.95
2021-05-07 13:00 | 44323.5417 | 0 | 8.0015 | 39.95
2021-05-07 13:30 | 44323.5625 | 0 | 9.251 | 39.95
2021-05-07 14:00 | 44323.5833 | 0 | 9.8 | 39.95
2021-05-07 14:30 | 44323.6042 | 0 | 9.9334 | 39.95
2021-05-07 15:00 | 44323.625 | 0 | 9.7082 | 39.95
2021-05-07 15:30 | 44323.6458 | 0 | 10.2719 | 39.95
2021-05-07 16:00 | 44323.6667 | 0 | 10.0915 | 39.95
2021-05-07 16:30 | 44323.6875 | 0 | 10.8894 | 39.95
2021-05-07 17:00 | 44323.7083 | 0 | 11.3787 | 39.95
2021-05-07 17:30 | 44323.7292 | 0 | 11.6403 | 39.95
2021-05-07 18:00 | 44323.75 | 0 | 11.5774 | 39.95
2021-05-07 18:30 | 44323.7708 | 0 | 11.5072 | 39.95
2021-05-07 19:00 | 44323.7917 | 0 | 11.2287 | 39.95
2021-05-07 19:30 | 44323.8125 | 0 | 11.0363 | 39.95
2021-05-07 20:00 | 44323.8333 | 0 | 10.7574 | 39.95
2021-05-07 20:30 | 44323.8542 | 0 | 10.3682 | 39.95
2021-05-07 21:00 | 44323.875 | 0 | 10.2504 | 39.95
2021-05-07 21:30 | 44323.8958 | 0 | 9.8241 | 39.95
2021-05-07 22:00 | 44323.9167 | 0 | 9.4308 | 39.95
2021-05-07 22:30 | 44323.9375 | 0 | 8.9546 | 39.95
2021-05-07 23:00 | 44323.9583 | 0 | 8.5202 | 39.95
2021-05-07 23:30 | 44323.9792 | 0 | 8.2222 | 39.95
2021-05-08 | 44324 | 0 | 7.9294 | 39.95
2021-05-08 00:30 | 44324.0208 | 0 | 7.5362 | 39.95
2021-05-08 01:00 | 44324.0417 | 0 | 7.3679 | 39.95
2021-05-08 01:30 | 44324.0625 | 0 | 7.1959 | 39.95
2021-05-08 02:00 | 44324.0833 | 0 | 7.1327 | 39.95
2021-05-08 02:30 | 44324.1042 | 0 | 7.0842 | 39.95
2021-05-08 03:00 | 44324.125 | 0 | 6.9682 | 39.95
2021-05-08 03:30 | 44324.1458 | 0 | 7.0285 | 39.95
2021-05-08 04:00 | 44324.1667 | 0 | 7.018 | 39.95
2021-05-08 04:30 | 44324.1875 | 0 | 6.9693 | 39.95
2021-05-08 05:00 | 44324.2083 | 0 | 7.1778 | 39.95
2021-05-08 05:30 | 44324.2292 | 0 | 7.3042 | 39.95
2021-05-08 06:00 | 44324.25 | 0 | 7.7282 | 39.95
2021-05-08 06:30 | 44324.2708 | 0 | 7.804 | 39.95
2021-05-08 07:00 | 44324.2917 | 0 | 8.286 | 39.95
2021-05-08 07:30 | 44324.3125 | 0 | 7.8598 | 39.95
2021-05-08 08:00 | 44324.3333 | 0 | 8.4781 | 39.95
2021-05-08 08:30 | 44324.3542 | 0 | 8.5213 | 39.95
2021-05-08 09:00 | 44324.375 | 0 | 8.1931 | 39.95
2021-05-08 09:30 | 44324.3958 | 0 | 9.8128 | 39.95
2021-05-08 10:00 | 44324.4167 | 0 | 9.7513 | 39.95
2021-05-08 10:30 | 44324.4375 | 0 | 7.796 | 39.95
2021-05-08 11:00 | 44324.4583 | 0 | 7.7826 | 39.95
2021-05-08 11:30 | 44324.4792 | 0 | 6.4732 | 39.95
2021-05-08 12:00 | 44324.5 | 0 | 6.7096 | 39.95
2021-05-08 12:30 | 44324.5208 | 0 | 7.5252 | 39.95
2021-05-08 13:00 | 44324.5417 | 0 | 8.1946 | 39.95
2021-05-08 13:30 | 44324.5625 | 0 | 7.9229 | 39.95
2021-05-08 14:00 | 44324.5833 | 0 | 7.5613 | 39.95
2021-05-08 14:30 | 44324.6042 | 0 | 8.5151 | 39.95
2021-05-08 15:00 | 44324.625 | 0 | 8.9381 | 39.95
2021-05-08 15:30 | 44324.6458 | 0 | 9.6752 | 39.95
2021-05-08 16:00 | 44324.6667 | 0 | 10.3564 | 39.95
2021-05-08 16:30 | 44324.6875 | 0 | 10.7385 | 39.95
2021-05-08 17:00 | 44324.7083 | 0 | 11.1679 | 39.95
2021-05-08 17:30 | 44324.7292 | 0 | 11.7763 | 39.95
2021-05-08 18:00 | 44324.75 | 0 | 11.8106 | 39.95
2021-05-08 18:30 | 44324.7708 | 0 | 11.6208 | 39.95
2021-05-08 19:00 | 44324.7917 | 0 | 11.3728 | 39.95
2021-05-08 19:30 | 44324.8125 | 0 | 11.3251 | 39.95
2021-05-08 20:00 | 44324.8333 | 0 | 10.88 | 39.95
2021-05-08 20:30 | 44324.8542 | 0 | 10.4071 | 39.95
2021-05-08 21:00 | 44324.875 | 0 | 9.9786 | 39.95
2021-05-08 21:30 | 44324.8958 | 0 | 9.5307 | 39.95
2021-05-08 22:00 | 44324.9167 | 0 | 9.2514 | 39.95
2021-05-08 22:30 | 44324.9375 | 0 | 8.601 | 39.95
2021-05-08 23:00 | 44324.9583 | 0 | 8.192 | 39.95
2021-05-08 23:30 | 44324.9792 | 0 | 7.8897 | 39.95
2021-05-09 | 44325 | 0 | 7.7562 | 39.95
2021-05-09 00:30 | 44325.0208 | 0 | 7.3802 | 39.95
2021-05-09 01:00 | 44325.0417 | 0 | 7.3318 | 39.95
2021-05-09 01:30 | 44325.0625 | 0 | 7.2014 | 39.95
2021-05-09 02:00 | 44325.0833 | 0 | 7.0806 | 39.95
2021-05-09 02:30 | 44325.1042 | 0 | 7.1088 | 39.95
2021-05-09 03:00 | 44325.125 | 0 | 7.0732 | 39.95
2021-05-09 03:30 | 44325.1458 | 0 | 7.3349 | 39.95
2021-05-09 04:00 | 44325.1667 | 0 | 7.4947 | 39.95
2021-05-09 04:30 | 44325.1875 | 0 | 7.9077 | 39.95
2021-05-09 05:00 | 44325.2083 | 0 | 8.6535 | 39.95
2021-05-09 05:30 | 44325.2292 | 0 | 9.294 | 39.95
2021-05-09 06:00 | 44325.25 | 0 | 10.275 | 39.95
2021-05-09 06:30 | 44325.2708 | 0 | 11.1371 | 39.95
2021-05-09 07:00 | 44325.2917 | 0 | 11.2506 | 39.95
2021-05-09 07:30 | 44325.3125 | 0 | 11.5055 | 39.95
2021-05-09 08:00 | 44325.3333 | 0 | 11.8657 | 39.95
2021-05-09 08:30 | 44325.3542 | 0 | 11.5931 | 39.95
2021-05-09 09:00 | 44325.375 | 0 | 11.0183 | 39.95
2021-05-09 09:30 | 44325.3958 | 0 | 10.0996 | 39.95
2021-05-09 10:00 | 44325.4167 | 0 | 9.7802 | 39.95
2021-05-09 10:30 | 44325.4375 | 0 | 9.7699 | 39.95
2021-05-09 11:00 | 44325.4583 | 0 | 9.8174 | 39.95
2021-05-09 11:30 | 44325.4792 | 0 | 10.0001 | 39.95
2021-05-09 12:00 | 44325.5 | 0 | 10.3612 | 39.95
2021-05-09 12:30 | 44325.5208 | 0 | 10.7477 | 39.95
2021-05-09 13:00 | 44325.5417 | 0 | 11.6137 | 39.95
2021-05-09 13:30 | 44325.5625 | 0 | 11.3095 | 39.95
2021-05-09 14:00 | 44325.5833 | 0 | 12.583 | 39.95
2021-05-09 14:30 | 44325.6042 | 0 | 12.3885 | 39.95
2021-05-09 15:00 | 44325.625 | 0 | 12.3201 | 39.95
2021-05-09 15:30 | 44325.6458 | 0 | 13.594 | 39.95
2021-05-09 16:00 | 44325.6667 | 0 | 13.3578 | 39.95
2021-05-09 16:30 | 44325.6875 | 0 | 13.6065 | 39.95
2021-05-09 17:00 | 44325.7083 | 0 | 13.7341 | 39.95
2021-05-09 17:30 | 44325.7292 | 0 | 14.4452 | 39.95
2021-05-09 18:00 | 44325.75 | 0 | 14.425 | 39.95
2021-05-09 18:30 | 44325.7708 | 0 | 14.479 | 39.95
2021-05-09 19:00 | 44325.7917 | 0 | 13.8686 | 39.95
2021-05-09 19:30 | 44325.8125 | 0 | 13.7816 | 39.95
2021-05-09 20:00 | 44325.8333 | 0 | 13.2914 | 39.95
2021-05-09 20:30 | 44325.8542 | 0 | 12.6656 | 39.95
2021-05-09 21:00 | 44325.875 | 0 | 12.1022 | 39.95
2021-05-09 21:30 | 44325.8958 | 0 | 11.7006 | 39.95
2021-05-09 22:00 | 44325.9167 | 0 | 11.2492 | 39.95
2021-05-09 22:30 | 44325.9375 | 0 | 10.3616 | 39.95
2021-05-09 23:00 | 44325.9583 | 0 | 9.7673 | 39.95
2021-05-09 23:30 | 44325.9792 | 0 | 9.4652 | 39.95
2021-05-10 | 44326 | 0 | 8.9665 | 39.95
2021-05-10 00:30 | 44326.0208 | 0 | 8.3732 | 39.95
2021-05-10 01:00 | 44326.0417 | 0 | 8.2772 | 39.95
2021-05-10 01:30 | 44326.0625 | 0 | 8.204 | 39.95
2021-05-10 02:00 | 44326.0833 | 0 | 7.9806 | 39.95
2021-05-10 02:30 | 44326.1042 | 0 | 7.9414 | 39.95
2021-05-10 03:00 | 44326.125 | 0 | 7.8121 | 39.95
2021-05-10 03:30 | 44326.1458 | 0 | 7.9806 | 39.95
2021-05-10 04:00 | 44326.1667 | 0 | 8.0757 | 39.95
2021-05-10 04:30 | 44326.1875 | 0 | 8.6018 | 39.95
2021-05-10 05:00 | 44326.2083 | 0 | 9.2276 | 39.95
2021-05-10 05:30 | 44326.2292 | 0 | 9.6587 | 39.95
2021-05-10 06:00 | 44326.25 | 0 | 10.5272 | 39.95
2021-05-10 06:30 | 44326.2708 | 0 | 11.3785 | 39.95
2021-05-10 07:00 | 44326.2917 | 0 | 11.649 | 39.95
2021-05-10 07:30 | 44326.3125 | 0 | 11.5193 | 39.95
2021-05-10 08:00 | 44326.3333 | 0 | 11.5997 | 39.95
2021-05-10 08:30 | 44326.3542 | 0 | 10.6045 | 39.95
2021-05-10 09:00 | 44326.375 | 0 | 10.3232 | 39.95
2021-05-10 09:30 | 44326.3958 | 0 | 10.1818 | 39.95
2021-05-10 10:00 | 44326.4167 | 0 | 9.9103 | 39.95
2021-05-10 10:30 | 44326.4375 | 0 | 9.8122 | 39.95
2021-05-10 11:00 | 44326.4583 | 0 | 9.654 | 39.95
2021-05-10 11:30 | 44326.4792 | 0 | 9.626 | 39.95
2021-05-10 12:00 | 44326.5 | 0 | 9.9052 | 39.95
2021-05-10 12:30 | 44326.5208 | 0 | 9.9169 | 39.95
2021-05-10 13:00 | 44326.5417 | 0 | 10.3893 | 39.95
2021-05-10 13:30 | 44326.5625 | 0 | 10.8189 | 39.95
2021-05-10 14:00 | 44326.5833 | 0 | 11.4814 | 39.95
2021-05-10 14:30 | 44326.6042 | 0 | 12.064 | 39.95
2021-05-10 15:00 | 44326.625 | 0 | 12.647 | 39.95
2021-05-10 15:30 | 44326.6458 | 0 | 12.8926 | 39.95
2021-05-10 16:00 | 44326.6667 | 0 | 13.3427 | 39.95
2021-05-10 16:30 | 44326.6875 | 0 | 13.6902 | 39.95
2021-05-10 17:00 | 44326.7083 | 0 | 13.9654 | 39.95
2021-05-10 17:30 | 44326.7292 | 0 | 14.5 | 39.95
2021-05-10 18:00 | 44326.75 | 0 | 14.4811 | 39.95
2021-05-10 18:30 | 44326.7708 | 0 | 14.3623 | 39.95
2021-05-10 19:00 | 44326.7917 | 0 | 13.7755 | 39.95
2021-05-10 19:30 | 44326.8125 | 0 | 13.8365 | 39.95
2021-05-10 20:00 | 44326.8333 | 0 | 13.5811 | 39.95
2021-05-10 20:30 | 44326.8542 | 0 | 13.1005 | 39.95
2021-05-10 21:00 | 44326.875 | 0 | 12.3455 | 39.95
2021-05-10 21:30 | 44326.8958 | 0 | 12.0483 | 39.95
2021-05-10 22:00 | 44326.9167 | 0 | 11.6502 | 39.95
2021-05-10 22:30 | 44326.9375 | 0 | 10.922 | 39.95
2021-05-10 23:00 | 44326.9583 | 0 | 10.2768 | 39.95
2021-05-10 23:30 | 44326.9792 | 0 | 9.8401 | 39.95
2021-05-11 | 44327 | 0 | 9.1491 | 39.95
2021-05-11 00:30 | 44327.0208 | 0 | 8.7067 | 39.95
2021-05-11 01:00 | 44327.0417 | 0 | 8.5895 | 39.95
2021-05-11 01:30 | 44327.0625 | 0 | 8.4688 | 39.95
2021-05-11 02:00 | 44327.0833 | 0 | 8.3211 | 39.95
2021-05-11 02:30 | 44327.1042 | 0 | 8.1899 | 39.95
2021-05-11 03:00 | 44327.125 | 0 | 8.0808 | 39.95
2021-05-11 03:30 | 44327.1458 | 0 | 8.2921 | 39.95
2021-05-11 04:00 | 44327.1667 | 0 | 8.5107 | 39.95
2021-05-11 04:30 | 44327.1875 | 0 | 8.8638 | 39.95
2021-05-11 05:00 | 44327.2083 | 0 | 9.2814 | 39.95
2021-05-11 05:30 | 44327.2292 | 0 | 9.8949 | 39.95
2021-05-11 06:00 | 44327.25 | 0 | 10.8846 | 39.95
2021-05-11 06:30 | 44327.2708 | 0 | 11.8319 | 39.95
2021-05-11 07:00 | 44327.2917 | 0 | 11.9429 | 39.95
2021-05-11 07:30 | 44327.3125 | 0 | 11.8588 | 39.95
2021-05-11 08:00 | 44327.3333 | 0 | 11.5088 | 39.95
2021-05-11 08:30 | 44327.3542 | 0 | 11.3653 | 39.95
2021-05-11 09:00 | 44327.375 | 0 | 11.7593 | 39.95
2021-05-11 09:30 | 44327.3958 | 0 | 11.6973 | 39.95
2021-05-11 10:00 | 44327.4167 | 0 | 10.983 | 39.95
2021-05-11 10:30 | 44327.4375 | 0 | 12.4237 | 39.95
2021-05-11 11:00 | 44327.4583 | 0 | 12.9054 | 39.95
2021-05-11 11:30 | 44327.4792 | 0 | 11.7627 | 39.95
2021-05-11 12:00 | 44327.5 | 0 | 12.3294 | 39.95
2021-05-11 12:30 | 44327.5208 | 0 | 13.0178 | 39.95
2021-05-11 13:00 | 44327.5417 | 0 | 11.9325 | 39.95
2021-05-11 13:30 | 44327.5625 | 0 | 12.2573 | 39.95
2021-05-11 14:00 | 44327.5833 | 0 | 13.0781 | 39.95
2021-05-11 14:30 | 44327.6042 | 0 | 12.2395 | 39.95
2021-05-11 15:00 | 44327.625 | 0 | 13.2036 | 39.95
2021-05-11 15:30 | 44327.6458 | 0 | 13.6484 | 39.95
2021-05-11 16:00 | 44327.6667 | 0 | 13.8316 | 39.95
2021-05-11 16:30 | 44327.6875 | 0 | 14.4029 | 39.95
2021-05-11 17:00 | 44327.7083 | 0 | 13.7168 | 39.95
2021-05-11 17:30 | 44327.7292 | 0 | 14.0341 | 39.95
2021-05-11 18:00 | 44327.75 | 0 | 13.7262 | 39.95
2021-05-11 18:30 | 44327.7708 | 0 | 13.4568 | 39.95
2021-05-11 19:00 | 44327.7917 | 0 | 13.1824 | 39.95
2021-05-11 19:30 | 44327.8125 | 0 | 13.168 | 39.95
2021-05-11 20:00 | 44327.8333 | 0 | 12.9071 | 39.95
2021-05-11 20:30 | 44327.8542 | 0 | 12.5969 | 39.95
2021-05-11 21:00 | 44327.875 | 0 | 11.9419 | 39.95
2021-05-11 21:30 | 44327.8958 | 0 | 11.5032 | 39.95
2021-05-11 22:00 | 44327.9167 | 0 | 11.1078 | 39.95
2021-05-11 22:30 | 44327.9375 | 0 | 10.1649 | 39.95
2021-05-11 23:00 | 44327.9583 | 0 | 9.5412 | 39.95
2021-05-11 23:30 | 44327.9792 | 0 | 9.2529 | 39.95
2021-05-12 | 44328 | 0 | 8.7628 | 39.95
2021-05-12 00:30 | 44328.0208 | 0 | 8.3062 | 39.95
2021-05-12 01:00 | 44328.0417 | 0 | 8.1457 | 39.95
2021-05-12 01:30 | 44328.0625 | 0 | 8.0398 | 39.95
2021-05-12 02:00 | 44328.0833 | 0 | 8.0602 | 39.95
2021-05-12 02:30 | 44328.1042 | 0 | 7.988 | 39.95
2021-05-12 03:00 | 44328.125 | 0 | 7.9571 | 39.95
2021-05-12 03:30 | 44328.1458 | 0 | 8.1133 | 39.95
2021-05-12 04:00 | 44328.1667 | 0 | 8.4895 | 39.95
2021-05-12 04:30 | 44328.1875 | 0 | 8.6571 | 39.95
2021-05-12 05:00 | 44328.2083 | 0 | 9.2405 | 39.95
2021-05-12 05:30 | 44328.2292 | 0 | 9.839 | 39.95
2021-05-12 06:00 | 44328.25 | 0 | 10.9387 | 39.95
2021-05-12 06:30 | 44328.2708 | 0 | 11.7612 | 39.95
2021-05-12 07:00 | 44328.2917 | 0 | 12.1777 | 39.95
2021-05-12 07:30 | 44328.3125 | 0 | 11.6092 | 39.95
2021-05-12 08:00 | 44328.3333 | 0 | 11.4537 | 39.95
2021-05-12 08:30 | 44328.3542 | 0 | 10.7196 | 39.95
2021-05-12 09:00 | 44328.375 | 0 | 10.3813 | 39.95
2021-05-12 09:30 | 44328.3958 | 0 | 10.1109 | 39.95
2021-05-12 10:00 | 44328.4167 | 0 | 9.7433 | 39.95
2021-05-12 10:30 | 44328.4375 | 0 | 9.6878 | 39.95
2021-05-12 11:00 | 44328.4583 | 0 | 9.4079 | 39.95
2021-05-12 11:30 | 44328.4792 | 0 | 9.1842 | 39.95
2021-05-12 12:00 | 44328.5 | 0 | 9.0905 | 39.95
2021-05-12 12:30 | 44328.5208 | 0 | 9.212 | 39.95
2021-05-12 13:00 | 44328.5417 | 0 | 9.4349 | 39.95
2021-05-12 13:30 | 44328.5625 | 0 | 9.7287 | 39.95
2021-05-12 14:00 | 44328.5833 | 0 | 10.0452 | 39.95
2021-05-12 14:30 | 44328.6042 | 0 | 10.6391 | 39.95
2021-05-12 15:00 | 44328.625 | 0 | 11.115 | 39.95
2021-05-12 15:30 | 44328.6458 | 0 | 11.6963 | 39.95
2021-05-12 16:00 | 44328.6667 | 0 | 12.1004 | 39.95
2021-05-12 16:30 | 44328.6875 | 0 | 12.5957 | 39.95
2021-05-12 17:00 | 44328.7083 | 0 | 12.9669 | 39.95
2021-05-12 17:30 | 44328.7292 | 0 | 13.4797 | 39.95
2021-05-12 18:00 | 44328.75 | 0 | 13.4858 | 39.95
2021-05-12 18:30 | 44328.7708 | 0 | 13.5105 | 39.95
2021-05-12 19:00 | 44328.7917 | 0 | 13.2197 | 39.95
2021-05-12 19:30 | 44328.8125 | 0 | 13.0079 | 39.95
2021-05-12 20:00 | 44328.8333 | 0 | 12.6823 | 39.95
2021-05-12 20:30 | 44328.8542 | 0 | 12.3912 | 39.95
2021-05-12 21:00 | 44328.875 | 0 | 11.9979 | 39.95
2021-05-12 21:30 | 44328.8958 | 0 | 11.5459 | 39.95
2021-05-12 22:00 | 44328.9167 | 0 | 10.9693 | 39.95
2021-05-12 22:30 | 44328.9375 | 0 | 10.1093 | 39.95
2021-05-12 23:00 | 44328.9583 | 0 | 9.4912 | 39.95
2021-05-12 23:30 | 44328.9792 | 0 | 9.1249 | 39.95
2021-05-13 | 44329 | 0 | 8.4779 | 39.95
2021-05-13 00:30 | 44329.0208 | 0 | 8.0384 | 39.95
2021-05-13 01:00 | 44329.0417 | 0 | 7.6593 | 39.95
2021-05-13 01:30 | 44329.0625 | 0 | 7.6597 | 39.95
2021-05-13 02:00 | 44329.0833 | 0 | 7.6448 | 39.95
2021-05-13 02:30 | 44329.1042 | 0 | 7.682 | 39.95
2021-05-13 03:00 | 44329.125 | 0 | 7.615 | 39.95
2021-05-13 03:30 | 44329.1458 | 0 | 7.7258 | 39.95
2021-05-13 04:00 | 44329.1667 | 0 | 8.0953 | 39.95
2021-05-13 04:30 | 44329.1875 | 0 | 8.3252 | 39.95
2021-05-13 05:00 | 44329.2083 | 0 | 8.8849 | 39.95
2021-05-13 05:30 | 44329.2292 | 0 | 9.5988 | 39.95
2021-05-13 06:00 | 44329.25 | 0 | 10.5004 | 39.95
2021-05-13 06:30 | 44329.2708 | 0 | 11.5204 | 39.95
2021-05-13 07:00 | 44329.2917 | 0 | 11.7391 | 39.95
2021-05-13 07:30 | 44329.3125 | 0 | 11.4697 | 39.95
2021-05-13 08:00 | 44329.3333 | 0 | 10.958 | 39.95
2021-05-13 08:30 | 44329.3542 | 0 | 10.1694 | 39.95
2021-05-13 09:00 | 44329.375 | 0 | 9.5008 | 39.95
2021-05-13 09:30 | 44329.3958 | 0 | 9.2874 | 39.95
2021-05-13 10:00 | 44329.4167 | 0 | 8.8226 | 39.95
2021-05-13 10:30 | 44329.4375 | 0 | 8.6978 | 39.95
2021-05-13 11:00 | 44329.4583 | 0 | 8.6267 | 39.95
2021-05-13 11:30 | 44329.4792 | 0 | 8.4231 | 39.95
2021-05-13 12:00 | 44329.5 | 0 | 8.1419 | 39.95
2021-05-13 12:30 | 44329.5208 | 0 | 8.4417 | 39.95
2021-05-13 13:00 | 44329.5417 | 0 | 8.5537 | 39.95
2021-05-13 13:30 | 44329.5625 | 0 | 8.9387 | 39.95
2021-05-13 14:00 | 44329.5833 | 0 | 9.4638 | 39.95
2021-05-13 14:30 | 44329.6042 | 0 | 10.0359 | 39.95
2021-05-13 15:00 | 44329.625 | 0 | 10.572 | 39.95
2021-05-13 15:30 | 44329.6458 | 0 | 11.3091 | 39.95
2021-05-13 16:00 | 44329.6667 | 0 | 12.0389 | 39.95
2021-05-13 16:30 | 44329.6875 | 0 | 12.5203 | 39.95
2021-05-13 17:00 | 44329.7083 | 0 | 12.6536 | 39.95
2021-05-13 17:30 | 44329.7292 | 0 | 12.9379 | 39.95
2021-05-13 18:00 | 44329.75 | 0 | 12.9441 | 39.95
2021-05-13 18:30 | 44329.7708 | 0 | 12.8225 | 39.95
2021-05-13 19:00 | 44329.7917 | 0 | 12.3725 | 39.95
2021-05-13 19:30 | 44329.8125 | 0 | 12.4393 | 39.95
2021-05-13 20:00 | 44329.8333 | 0 | 12.151 | 39.95
2021-05-13 20:30 | 44329.8542 | 0 | 11.7469 | 39.95
2021-05-13 21:00 | 44329.875 | 0 | 11.4492 | 39.95
2021-05-13 21:30 | 44329.8958 | 0 | 11.0179 | 39.95
2021-05-13 22:00 | 44329.9167 | 0 | 10.6896 | 39.95
2021-05-13 22:30 | 44329.9375 | 0 | 9.8406 | 39.95
2021-05-13 23:00 | 44329.9583 | 0 | 9.2711 | 39.95
2021-05-13 23:30 | 44329.9792 | 0 | 8.9029 | 39.95
2021-05-14 | 44330 | 0 | 8.4016 | 39.95
2021-05-14 00:30 | 44330.0208 | 0 | 7.9903 | 39.95
2021-05-14 01:00 | 44330.0417 | 0 | 7.8345 | 39.95
2021-05-14 01:30 | 44330.0625 | 0 | 7.6598 | 39.95
2021-05-14 02:00 | 44330.0833 | 0 | 7.5378 | 39.95
2021-05-14 02:30 | 44330.1042 | 0 | 7.5003 | 39.95
2021-05-14 03:00 | 44330.125 | 0 | 7.3604 | 39.95
2021-05-14 03:30 | 44330.1458 | 0 | 7.4849 | 39.95
2021-05-14 04:00 | 44330.1667 | 0 | 7.4967 | 39.95
2021-05-14 04:30 | 44330.1875 | 0 | 7.6283 | 39.95
2021-05-14 05:00 | 44330.2083 | 0 | 7.874 | 39.95
2021-05-14 05:30 | 44330.2292 | 0 | 8.1345 | 39.95
2021-05-14 06:00 | 44330.25 | 0 | 8.581 | 39.95
2021-05-14 06:30 | 44330.2708 | 0 | 8.8908 | 39.95
2021-05-14 07:00 | 44330.2917 | 0 | 8.8888 | 39.95
2021-05-14 07:30 | 44330.3125 | 0 | 8.8754 | 39.95
2021-05-14 08:00 | 44330.3333 | 0 | 9.1008 | 39.95
2021-05-14 08:30 | 44330.3542 | 0 | 8.5426 | 39.95
2021-05-14 09:00 | 44330.375 | 0 | 8.1494 | 39.95
2021-05-14 09:30 | 44330.3958 | 0 | 7.7723 | 39.95
2021-05-14 10:00 | 44330.4167 | 0 | 7.1755 | 39.95
2021-05-14 10:30 | 44330.4375 | 0 | 6.8891 | 39.95
2021-05-14 11:00 | 44330.4583 | 0 | 6.6433 | 39.95
2021-05-14 11:30 | 44330.4792 | 0 | 6.3597 | 39.95
2021-05-14 12:00 | 44330.5 | 0 | 6.4345 | 39.95
2021-05-14 12:30 | 44330.5208 | 0 | 6.636 | 39.95
2021-05-14 13:00 | 44330.5417 | 0 | 6.5868 | 39.95
2021-05-14 13:30 | 44330.5625 | 0 | 6.7855 | 39.95
2021-05-14 14:00 | 44330.5833 | 0 | 7.2923 | 39.95
2021-05-14 14:30 | 44330.6042 | 0 | 7.7652 | 39.95
2021-05-14 15:00 | 44330.625 | 0 | 8.2736 | 39.95
2021-05-14 15:30 | 44330.6458 | 0 | 8.9557 | 39.95
2021-05-14 16:00 | 44330.6667 | 0 | 9.6629 | 39.95
2021-05-14 16:30 | 44330.6875 | 0 | 10.3863 | 39.95
2021-05-14 17:00 | 44330.7083 | 0 | 10.9132 | 39.95
2021-05-14 17:30 | 44330.7292 | 0 | 11.1378 | 39.95
2021-05-14 18:00 | 44330.75 | 0 | 11.1617 | 39.95
2021-05-14 18:30 | 44330.7708 | 0 | 11.1195 | 39.95
2021-05-14 19:00 | 44330.7917 | 0 | 10.9802 | 39.95
2021-05-14 19:30 | 44330.8125 | 0 | 10.7632 | 39.95
2021-05-14 20:00 | 44330.8333 | 0 | 10.5266 | 39.95
2021-05-14 20:30 | 44330.8542 | 0 | 10.141 | 39.95
2021-05-14 21:00 | 44330.875 | 0 | 9.7387 | 39.95
2021-05-14 21:30 | 44330.8958 | 0 | 9.5744 | 39.95
2021-05-14 22:00 | 44330.9167 | 0 | 9.2322 | 39.95
2021-05-14 22:30 | 44330.9375 | 0 | 8.8523 | 39.95
2021-05-14 23:00 | 44330.9583 | 0 | 8.2615 | 39.95
2021-05-14 23:30 | 44330.9792 | 0 | 7.9346 | 39.95
2021-05-15 | 44331 | 0 | 7.5782 | 39.95
2021-05-15 00:30 | 44331.0208 | 0 | 7.2637 | 39.95
2021-05-15 01:00 | 44331.0417 | 0 | 7.0842 | 39.95
2021-05-15 01:30 | 44331.0625 | 0 | 6.9718 | 39.95
2021-05-15 02:00 | 44331.0833 | 0 | 6.9302 | 39.95
2021-05-15 02:30 | 44331.1042 | 0 | 6.7935 | 39.95
2021-05-15 03:00 | 44331.125 | 0 | 6.764 | 39.95
2021-05-15 03:30 | 44331.1458 | 0 | 6.8435 | 39.95
2021-05-15 04:00 | 44331.1667 | 0 | 6.7903 | 39.95
2021-05-15 04:30 | 44331.1875 | 0 | 6.8219 | 39.95
2021-05-15 05:00 | 44331.2083 | 0 | 6.9596 | 39.95
2021-05-15 05:30 | 44331.2292 | 0 | 7.134 | 39.95
2021-05-15 06:00 | 44331.25 | 0 | 7.4034 | 39.95
2021-05-15 06:30 | 44331.2708 | 0 | 7.5418 | 39.95
2021-05-15 07:00 | 44331.2917 | 0 | 7.8022 | 39.95
2021-05-15 07:30 | 44331.3125 | 0 | 7.7221 | 39.95
2021-05-15 08:00 | 44331.3333 | 0 | 7.6593 | 39.95
2021-05-15 08:30 | 44331.3542 | 0 | 7.3651 | 39.95
2021-05-15 09:00 | 44331.375 | 0 | 7.0361 | 39.95
2021-05-15 09:30 | 44331.3958 | 0 | 6.605 | 39.95
2021-05-15 10:00 | 44331.4167 | 0 | 6.2787 | 39.95
2021-05-15 10:30 | 44331.4375 | 0 | 6.0663 | 39.95
2021-05-15 11:00 | 44331.4583 | 0 | 5.9099 | 39.95
2021-05-15 11:30 | 44331.4792 | 0 | 5.8257 | 39.95
2021-05-15 12:00 | 44331.5 | 0 | 5.732 | 39.95
2021-05-15 12:30 | 44331.5208 | 0 | 5.7954 | 39.95
2021-05-15 13:00 | 44331.5417 | 0 | 5.9436 | 39.95
2021-05-15 13:30 | 44331.5625 | 0 | 6.215 | 39.95
2021-05-15 14:00 | 44331.5833 | 0 | 6.8096 | 39.95
2021-05-15 14:30 | 44331.6042 | 0 | 7.2567 | 39.95
2021-05-15 15:00 | 44331.625 | 0 | 7.8916 | 39.95
2021-05-15 15:30 | 44331.6458 | 0 | 8.6787 | 39.95
2021-05-15 16:00 | 44331.6667 | 0 | 9.5566 | 39.95
2021-05-15 16:30 | 44331.6875 | 0 | 10.5546 | 39.95
2021-05-15 17:00 | 44331.7083 | 0 | 11.1276 | 39.95
2021-05-15 17:30 | 44331.7292 | 0 | 11.9356 | 39.95
2021-05-15 18:00 | 44331.75 | 0 | 12.0919 | 39.95
2021-05-15 18:30 | 44331.7708 | 0 | 11.9858 | 39.95
2021-05-15 19:00 | 44331.7917 | 0 | 11.7544 | 39.95
2021-05-15 19:30 | 44331.8125 | 0 | 11.3843 | 39.95
2021-05-15 20:00 | 44331.8333 | 0 | 11.0518 | 39.95
2021-05-15 20:30 | 44331.8542 | 0 | 10.7532 | 39.95
2021-05-15 21:00 | 44331.875 | 0 | 10.1322 | 39.95
2021-05-15 21:30 | 44331.8958 | 0 | 9.7206 | 39.95
2021-05-15 22:00 | 44331.9167 | 0 | 9.3519 | 39.95
2021-05-15 22:30 | 44331.9375 | 0 | 8.6471 | 39.95
2021-05-15 23:00 | 44331.9583 | 0 | 8.0996 | 39.95
2021-05-15 23:30 | 44331.9792 | 0 | 7.7679 | 39.95
2021-05-16 | 44332 | 0 | 7.5394 | 39.95
2021-05-16 00:30 | 44332.0208 | 0 | 7.3627 | 39.95
2021-05-16 01:00 | 44332.0417 | 0 | 7.1724 | 39.95
2021-05-16 01:30 | 44332.0625 | 0 | 6.9697 | 39.95
2021-05-16 02:00 | 44332.0833 | 0 | 7.1684 | 39.95
2021-05-16 02:30 | 44332.1042 | 0 | 7.0991 | 39.95
2021-05-16 03:00 | 44332.125 | 0 | 7.1331 | 39.95
2021-05-16 03:30 | 44332.1458 | 0 | 7.3234 | 39.95
2021-05-16 04:00 | 44332.1667 | 0 | 7.5937 | 39.95
2021-05-16 04:30 | 44332.1875 | 0 | 8.0776 | 39.95
2021-05-16 05:00 | 44332.2083 | 0 | 8.7155 | 39.95
2021-05-16 05:30 | 44332.2292 | 0 | 9.7836 | 39.95
2021-05-16 06:00 | 44332.25 | 0 | 11.1374 | 39.95
2021-05-16 06:30 | 44332.2708 | 0 | 12.5631 | 39.95
2021-05-16 07:00 | 44332.2917 | 0 | 13.0533 | 39.95
2021-05-16 07:30 | 44332.3125 | 0 | 12.5427 | 39.95
2021-05-16 08:00 | 44332.3333 | 0 | 11.7827 | 39.95
2021-05-16 08:30 | 44332.3542 | 0 | 11.0933 | 39.95
2021-05-16 09:00 | 44332.375 | 0 | 10.2462 | 39.95
2021-05-16 09:30 | 44332.3958 | 0 | 9.5664 | 39.95
2021-05-16 10:00 | 44332.4167 | 0 | 8.9784 | 39.95
2021-05-16 10:30 | 44332.4375 | 0 | 8.8552 | 39.95
2021-05-16 11:00 | 44332.4583 | 0 | 8.501 | 39.95
2021-05-16 11:30 | 44332.4792 | 0 | 8.3301 | 39.95
2021-05-16 12:00 | 44332.5 | 0 | 8.2196 | 39.95
2021-05-16 12:30 | 44332.5208 | 0 | 8.4104 | 39.95
2021-05-16 13:00 | 44332.5417 | 0 | 8.4285 | 39.95
2021-05-16 13:30 | 44332.5625 | 0 | 9.4815 | 39.95
2021-05-16 14:00 | 44332.5833 | 0 | 10.6588 | 39.95
2021-05-16 14:30 | 44332.6042 | 0 | 9.6488 | 39.95
2021-05-16 15:00 | 44332.625 | 0 | 10.1433 | 39.95
2021-05-16 15:30 | 44332.6458 | 0 | 10.7569 | 39.95
2021-05-16 16:00 | 44332.6667 | 0 | 11.3692 | 39.95
2021-05-16 16:30 | 44332.6875 | 0 | 12.2793 | 39.95
2021-05-16 17:00 | 44332.7083 | 0 | 13.2954 | 39.95
2021-05-16 17:30 | 44332.7292 | 0 | 14.0146 | 39.95
2021-05-16 18:00 | 44332.75 | 0 | 14.4838 | 39.95
2021-05-16 18:30 | 44332.7708 | 0 | 14.3349 | 39.95
2021-05-16 19:00 | 44332.7917 | 0 | 14.2083 | 39.95
2021-05-16 19:30 | 44332.8125 | 0 | 13.9148 | 39.95
2021-05-16 20:00 | 44332.8333 | 0 | 13.7559 | 39.95
2021-05-16 20:30 | 44332.8542 | 0 | 12.9591 | 39.95
2021-05-16 21:00 | 44332.875 | 0 | 12.4952 | 39.95
2021-05-16 21:30 | 44332.8958 | 0 | 11.986 | 39.95
2021-05-16 22:00 | 44332.9167 | 0 | 11.1008 | 39.95
2021-05-16 22:30 | 44332.9375 | 0 | 10.2626 | 39.95
2021-05-16 23:00 | 44332.9583 | 0 | 9.5822 | 39.95
2021-05-16 23:30 | 44332.9792 | 0 | 9.2209 | 39.95
2021-05-17 | 44333 | 0 | 8.6 | 39.95
2021-05-17 00:30 | 44333.0208 | 0 | 8.2615 | 39.95
2021-05-17 01:00 | 44333.0417 | 0 | 8.0661 | 39.95
2021-05-17 01:30 | 44333.0625 | 0 | 7.9783 | 39.95
2021-05-17 02:00 | 44333.0833 | 0 | 7.8436 | 39.95
2021-05-17 02:30 | 44333.1042 | 0 | 7.7114 | 39.95
2021-05-17 03:00 | 44333.125 | 0 | 7.7819 | 39.95
2021-05-17 03:30 | 44333.1458 | 0 | 7.9758 | 39.95
2021-05-17 04:00 | 44333.1667 | 0 | 8.1784 | 39.95
2021-05-17 04:30 | 44333.1875 | 0 | 8.7197 | 39.95
2021-05-17 05:00 | 44333.2083 | 0 | 9.3974 | 39.95
2021-05-17 05:30 | 44333.2292 | 0 | 10.496 | 39.95
2021-05-17 06:00 | 44333.25 | 0 | 11.6431 | 39.95
2021-05-17 06:30 | 44333.2708 | 0 | 12.8936 | 39.95
2021-05-17 07:00 | 44333.2917 | 0 | 13.2297 | 39.95
2021-05-17 07:30 | 44333.3125 | 0 | 12.7816 | 39.95
2021-05-17 08:00 | 44333.3333 | 0 | 12.0051 | 39.95
2021-05-17 08:30 | 44333.3542 | 0 | 11.1352 | 39.95
2021-05-17 09:00 | 44333.375 | 0 | 10.2556 | 39.95
2021-05-17 09:30 | 44333.3958 | 0 | 9.6055 | 39.95
2021-05-17 10:00 | 44333.4167 | 0 | 9.102 | 39.95
2021-05-17 10:30 | 44333.4375 | 0 | 8.9768 | 39.95
2021-05-17 11:00 | 44333.4583 | 0 | 8.6816 | 39.95
2021-05-17 11:30 | 44333.4792 | 0 | 8.9098 | 39.95
2021-05-17 12:00 | 44333.5 | 0 | 9.9767 | 39.95
2021-05-17 12:30 | 44333.5208 | 0 | 9.2992 | 39.95
2021-05-17 13:00 | 44333.5417 | 0 | 9.6629 | 39.95
2021-05-17 13:30 | 44333.5625 | 0 | 9.523 | 39.95
2021-05-17 14:00 | 44333.5833 | 0 | 10.1 | 39.95
2021-05-17 14:30 | 44333.6042 | 0 | 10.2576 | 39.95
2021-05-17 15:00 | 44333.625 | 0 | 10.7961 | 39.95
2021-05-17 15:30 | 44333.6458 | 0 | 11.3584 | 39.95
2021-05-17 16:00 | 44333.6667 | 0 | 11.9723 | 39.95
2021-05-17 16:30 | 44333.6875 | 0 | 12.7246 | 39.95
2021-05-17 17:00 | 44333.7083 | 0 | 13.4131 | 39.95
2021-05-17 17:30 | 44333.7292 | 0 | 14.2175 | 39.95
2021-05-17 18:00 | 44333.75 | 0 | 14.126 | 39.95
2021-05-17 18:30 | 44333.7708 | 0 | 14.139 | 39.95
2021-05-17 19:00 | 44333.7917 | 0 | 13.8506 | 39.95
2021-05-17 19:30 | 44333.8125 | 0 | 13.7099 | 39.95
2021-05-17 20:00 | 44333.8333 | 0 | 13.4225 | 39.95
2021-05-17 20:30 | 44333.8542 | 0 | 12.9523 | 39.95
2021-05-17 21:00 | 44333.875 | 0 | 12.3272 | 39.95
2021-05-17 21:30 | 44333.8958 | 0 | 11.742 | 39.95
2021-05-17 22:00 | 44333.9167 | 0 | 11.1303 | 39.95
2021-05-17 22:30 | 44333.9375 | 0 | 10.4135 | 39.95
2021-05-17 23:00 | 44333.9583 | 0 | 9.6419 | 39.95
2021-05-17 23:30 | 44333.9792 | 0 | 9.1488 | 39.95
2021-05-18 | 44334 | 0 | 8.7698 | 39.95
2021-05-18 00:30 | 44334.0208 | 0 | 8.2992 | 39.95
2021-05-18 01:00 | 44334.0417 | 0 | 8.1569 | 39.95
2021-05-18 01:30 | 44334.0625 | 0 | 7.8615 | 39.95
2021-05-18 02:00 | 44334.0833 | 0 | 7.8298 | 39.95
2021-05-18 02:30 | 44334.1042 | 0 | 7.7651 | 39.95
2021-05-18 03:00 | 44334.125 | 0 | 7.7227 | 39.95
2021-05-18 03:30 | 44334.1458 | 0 | 8.0487 | 39.95
2021-05-18 04:00 | 44334.1667 | 0 | 8.1709 | 39.95
2021-05-18 04:30 | 44334.1875 | 0 | 8.4565 | 39.95
2021-05-18 05:00 | 44334.2083 | 0 | 9.2432 | 39.95
2021-05-18 05:30 | 44334.2292 | 0 | 10.0428 | 39.95
2021-05-18 06:00 | 44334.25 | 0 | 11.129 | 39.95
2021-05-18 06:30 | 44334.2708 | 0 | 12.2202 | 39.95
2021-05-18 07:00 | 44334.2917 | 0 | 12.4143 | 39.95
2021-05-18 07:30 | 44334.3125 | 0 | 12.5086 | 39.95
2021-05-18 08:00 | 44334.3333 | 0 | 12.5509 | 39.95
2021-05-18 08:30 | 44334.3542 | 0 | 12.5509 | 39.95
2021-05-18 09:00 | 44334.375 | 0 | 12.5509 | 39.95
2021-05-18 09:30 | 44334.3958 | 0 | 12.5509 | 39.95
2021-05-18 10:00 | 44334.4167 | 0 | 12.5509 | 39.95
2021-05-18 10:30 | 44334.4375 | 0 | 12.5509 | 39.95
2021-05-18 11:00 | 44334.4583 | 0 | 12.5509 | 39.95
2021-05-18 11:30 | 44334.4792 | 0 | 12.5509 | 39.95
2021-05-18 12:00 | 44334.5 | 0 | 11.1426 | 39.95
2021-05-18 12:30 | 44334.5208 | 0 | 10.3653 | 39.95
2021-05-18 13:00 | 44334.5417 | 0 | 11.1322 | 39.95
2021-05-18 13:30 | 44334.5625 | 0 | 10.8803 | 39.95
2021-05-18 14:00 | 44334.5833 | 0 | 11.9085 | 39.95
2021-05-18 14:30 | 44334.6042 | 0 | 11.8812 | 39.95
2021-05-18 15:00 | 44334.625 | 0 | 11.4752 | 39.95
2021-05-18 15:30 | 44334.6458 | 0 | 11.8407 | 39.95
2021-05-18 16:00 | 44334.6667 | 0 | 12.3146 | 39.95
2021-05-18 16:30 | 44334.6875 | 0 | 12.6575 | 39.95
2021-05-18 17:00 | 44334.7083 | 0 | 13.4677 | 39.95
2021-05-18 17:30 | 44334.7292 | 0 | 14.0537 | 39.95
2021-05-18 18:00 | 44334.75 | 0 | 13.9911 | 39.95
2021-05-18 18:30 | 44334.7708 | 0 | 14.1598 | 39.95
2021-05-18 19:00 | 44334.7917 | 0 | 13.7646 | 39.95
2021-05-18 19:30 | 44334.8125 | 0 | 13.6851 | 39.95
2021-05-18 20:00 | 44334.8333 | 0 | 13.4179 | 39.95
2021-05-18 20:30 | 44334.8542 | 0 | 12.9462 | 39.95
2021-05-18 21:00 | 44334.875 | 0 | 12.4208 | 39.95
2021-05-18 21:30 | 44334.8958 | 0 | 11.6679 | 39.95
2021-05-18 22:00 | 44334.9167 | 0 | 11.1197 | 39.95
2021-05-18 22:30 | 44334.9375 | 0 | 10.2127 | 39.95
2021-05-18 23:00 | 44334.9583 | 0 | 9.5912 | 39.95
2021-05-18 23:30 | 44334.9792 | 0 | 9.0725 | 39.95
2021-05-19 | 44335 | 0 | 8.6121 | 39.95
2021-05-19 00:30 | 44335.0208 | 0 | 8.1742 | 39.95
2021-05-19 01:00 | 44335.0417 | 0 | 8.04 | 39.95
2021-05-19 01:30 | 44335.0625 | 0 | 7.8964 | 39.95
2021-05-19 02:00 | 44335.0833 | 0 | 7.8345 | 39.95
2021-05-19 02:30 | 44335.1042 | 0 | 7.7371 | 39.95
2021-05-19 03:00 | 44335.125 | 0 | 7.7446 | 39.95
2021-05-19 03:30 | 44335.1458 | 0 | 7.8963 | 39.95
2021-05-19 04:00 | 44335.1667 | 0 | 8.0444 | 39.95
2021-05-19 04:30 | 44335.1875 | 0 | 8.4861 | 39.95
2021-05-19 05:00 | 44335.2083 | 0 | 9.2069 | 39.95
2021-05-19 05:30 | 44335.2292 | 0 | 10.0543 | 39.95
2021-05-19 06:00 | 44335.25 | 0 | 11.0284 | 39.95
2021-05-19 06:30 | 44335.2708 | 0 | 12.0828 | 39.95
2021-05-19 07:00 | 44335.2917 | 0 | 12.5773 | 39.95
2021-05-19 07:30 | 44335.3125 | 0 | 12.2869 | 39.95
2021-05-19 08:00 | 44335.3333 | 0 | 11.7559 | 39.95
2021-05-19 08:30 | 44335.3542 | 0 | 10.9852 | 39.95
2021-05-19 09:00 | 44335.375 | 0 | 10.2441 | 39.95
2021-05-19 09:30 | 44335.3958 | 0 | 9.7885 | 39.95
2021-05-19 10:00 | 44335.4167 | 0 | 9.1644 | 39.95
2021-05-19 10:30 | 44335.4375 | 0 | 8.9537 | 39.95
2021-05-19 11:00 | 44335.4583 | 0 | 9.1923 | 39.95
2021-05-19 11:30 | 44335.4792 | 0 | 10.7935 | 39.95
2021-05-19 12:00 | 44335.5 | 0 | 10.2928 | 39.95
2021-05-19 12:30 | 44335.5208 | 0 | 10.0856 | 39.95
2021-05-19 13:00 | 44335.5417 | 0 | 9.1696 | 39.95
2021-05-19 13:30 | 44335.5625 | 0 | 10.1849 | 39.95
2021-05-19 14:00 | 44335.5833 | 0 | 10.0214 | 39.95
2021-05-19 14:30 | 44335.6042 | 0 | 10.6369 | 39.95
2021-05-19 15:00 | 44335.625 | 0 | 11.1836 | 39.95
2021-05-19 15:30 | 44335.6458 | 0 | 11.5269 | 39.95
2021-05-19 16:00 | 44335.6667 | 0 | 12.0387 | 39.95
2021-05-19 16:30 | 44335.6875 | 0 | 12.5586 | 39.95
2021-05-19 17:00 | 44335.7083 | 0 | 13.2808 | 39.95
2021-05-19 17:30 | 44335.7292 | 0 | 13.4798 | 39.95
2021-05-19 18:00 | 44335.75 | 0 | 13.4964 | 39.95
2021-05-19 18:30 | 44335.7708 | 0 | 14.0513 | 39.95
2021-05-19 19:00 | 44335.7917 | 0 | 13.4716 | 39.95
2021-05-19 19:30 | 44335.8125 | 0 | 13.4093 | 39.95
2021-05-19 20:00 | 44335.8333 | 0 | 13.0822 | 39.95
2021-05-19 20:30 | 44335.8542 | 0 | 12.5253 | 39.95
2021-05-19 21:00 | 44335.875 | 0 | 12.0593 | 39.95
2021-05-19 21:30 | 44335.8958 | 0 | 11.5404 | 39.95
2021-05-19 22:00 | 44335.9167 | 0 | 11.0745 | 39.95
2021-05-19 22:30 | 44335.9375 | 0 | 10.1659 | 39.95
2021-05-19 23:00 | 44335.9583 | 0 | 9.515 | 39.95
2021-05-19 23:30 | 44335.9792 | 0 | 9.0636 | 39.95
2021-05-20 | 44336 | 0 | 8.6258 | 39.95
2021-05-20 00:30 | 44336.0208 | 0 | 8.2983 | 39.95
2021-05-20 01:00 | 44336.0417 | 0 | 7.997 | 39.95
2021-05-20 01:30 | 44336.0625 | 0 | 7.8917 | 39.95
2021-05-20 02:00 | 44336.0833 | 0 | 7.8877 | 39.95
2021-05-20 02:30 | 44336.1042 | 0 | 7.7752 | 39.95
2021-05-20 03:00 | 44336.125 | 0 | 7.7494 | 39.95
2021-05-20 03:30 | 44336.1458 | 0 | 7.9284 | 39.95
2021-05-20 04:00 | 44336.1667 | 0 | 8.1784 | 39.95
2021-05-20 04:30 | 44336.1875 | 0 | 8.5234 | 39.95
2021-05-20 05:00 | 44336.2083 | 0 | 9.2195 | 39.95
2021-05-20 05:30 | 44336.2292 | 0 | 9.8953 | 39.95
2021-05-20 06:00 | 44336.25 | 0 | 11.098 | 39.95
2021-05-20 06:30 | 44336.2708 | 0 | 12.099 | 39.95
2021-05-20 07:00 | 44336.2917 | 0 | 12.5461 | 39.95
2021-05-20 07:30 | 44336.3125 | 0 | 12.4562 | 39.95
2021-05-20 08:00 | 44336.3333 | 0 | 11.6056 | 39.95
2021-05-20 08:30 | 44336.3542 | 0 | 10.8599 | 39.95
2021-05-20 09:00 | 44336.375 | 0 | 10.2362 | 39.95
2021-05-20 09:30 | 44336.3958 | 0 | 9.8775 | 39.95
2021-05-20 10:00 | 44336.4167 | 0 | 9.4554 | 39.95
2021-05-20 10:30 | 44336.4375 | 0 | 9.3285 | 39.95
2021-05-20 11:00 | 44336.4583 | 0 | 9.6694 | 39.95
2021-05-20 11:30 | 44336.4792 | 0 | 9.9866 | 39.95
2021-05-20 12:00 | 44336.5 | 0 | 9.6806 | 39.95
2021-05-20 12:30 | 44336.5208 | 0 | 9.3901 | 39.95
2021-05-20 13:00 | 44336.5417 | 0 | 9.1692 | 39.95
2021-05-20 13:30 | 44336.5625 | 0 | 9.0997 | 39.95
2021-05-20 14:00 | 44336.5833 | 0 | 9.5241 | 39.95
2021-05-20 14:30 | 44336.6042 | 0 | 9.9144 | 39.95
2021-05-20 15:00 | 44336.625 | 0 | 10.4129 | 39.95
2021-05-20 15:30 | 44336.6458 | 0 | 11.0959 | 39.95
2021-05-20 16:00 | 44336.6667 | 0 | 11.7577 | 39.95
2021-05-20 16:30 | 44336.6875 | 0 | 12.357 | 39.95
2021-05-20 17:00 | 44336.7083 | 0 | 12.9552 | 39.95
2021-05-20 17:30 | 44336.7292 | 0 | 13.3341 | 39.95
2021-05-20 18:00 | 44336.75 | 0 | 13.2767 | 39.95
2021-05-20 18:30 | 44336.7708 | 0 | 13.3375 | 39.95
2021-05-20 19:00 | 44336.7917 | 0 | 12.9752 | 39.95
2021-05-20 19:30 | 44336.8125 | 0 | 12.6276 | 39.95
2021-05-20 20:00 | 44336.8333 | 0 | 12.3741 | 39.95
2021-05-20 20:30 | 44336.8542 | 0 | 12.0393 | 39.95
2021-05-20 21:00 | 44336.875 | 0 | 11.6085 | 39.95
2021-05-20 21:30 | 44336.8958 | 0 | 11.3375 | 39.95
2021-05-20 22:00 | 44336.9167 | 0 | 10.9458 | 39.95
2021-05-20 22:30 | 44336.9375 | 0 | 10.2297 | 39.95
2021-05-20 23:00 | 44336.9583 | 0 | 9.643 | 39.95
2021-05-20 23:30 | 44336.9792 | 0 | 9.1516 | 39.95
2021-05-21 | 44337 | 0 | 8.6232 | 39.95
2021-05-21 00:30 | 44337.0208 | 0 | 8.2674 | 39.95
2021-05-21 01:00 | 44337.0417 | 0 | 7.8341 | 39.95
2021-05-21 01:30 | 44337.0625 | 0 | 7.685 | 39.95
2021-05-21 02:00 | 44337.0833 | 0 | 7.6355 | 39.95
2021-05-21 02:30 | 44337.1042 | 0 | 7.4132 | 39.95
2021-05-21 03:00 | 44337.125 | 0 | 7.4789 | 39.95
2021-05-21 03:30 | 44337.1458 | 0 | 7.5631 | 39.95
2021-05-21 04:00 | 44337.1667 | 0 | 7.6137 | 39.95
2021-05-21 04:30 | 44337.1875 | 0 | 7.7815 | 39.95
2021-05-21 05:00 | 44337.2083 | 0 | 8.0544 | 39.95
2021-05-21 05:30 | 44337.2292 | 0 | 8.2637 | 39.95
2021-05-21 06:00 | 44337.25 | 0 | 8.7596 | 39.95
2021-05-21 06:30 | 44337.2708 | 0 | 9.0031 | 39.95
2021-05-21 07:00 | 44337.2917 | 0 | 9.4441 | 39.95
2021-05-21 07:30 | 44337.3125 | 0 | 9.1884 | 39.95
2021-05-21 08:00 | 44337.3333 | 0 | 9.0879 | 39.95
2021-05-21 08:30 | 44337.3542 | 0 | 8.677 | 39.95
2021-05-21 09:00 | 44337.375 | 0 | 8.2562 | 39.95
2021-05-21 09:30 | 44337.3958 | 0 | 7.9354 | 39.95
2021-05-21 10:00 | 44337.4167 | 0 | 7.3177 | 39.95
2021-05-21 10:30 | 44337.4375 | 0 | 7.1252 | 39.95
2021-05-21 11:00 | 44337.4583 | 0 | 7.2999 | 39.95
2021-05-21 11:30 | 44337.4792 | 0 | 7.2299 | 39.95
2021-05-21 12:00 | 44337.5 | 0 | 7.0948 | 39.95
2021-05-21 12:30 | 44337.5208 | 0 | 6.491 | 39.95
2021-05-21 13:00 | 44337.5417 | 0 | 6.9403 | 39.95
2021-05-21 13:30 | 44337.5625 | 0 | 6.8393 | 39.95
2021-05-21 14:00 | 44337.5833 | 0 | 7.2266 | 39.95
2021-05-21 14:30 | 44337.6042 | 0 | 8.4827 | 39.95
2021-05-21 15:00 | 44337.625 | 0 | 9.6348 | 39.95
2021-05-21 15:30 | 44337.6458 | 0 | 9.1034 | 39.95
2021-05-21 16:00 | 44337.6667 | 0 | 9.74 | 39.95
2021-05-21 16:30 | 44337.6875 | 0 | 10.4863 | 39.95
2021-05-21 17:00 | 44337.7083 | 0 | 10.984 | 39.95
2021-05-21 17:30 | 44337.7292 | 0 | 11.3642 | 39.95
2021-05-21 18:00 | 44337.75 | 0 | 11.2699 | 39.95
2021-05-21 18:30 | 44337.7708 | 0 | 11.2211 | 39.95
2021-05-21 19:00 | 44337.7917 | 0 | 10.9338 | 39.95
2021-05-21 19:30 | 44337.8125 | 0 | 10.8205 | 39.95
2021-05-21 20:00 | 44337.8333 | 0 | 10.707 | 39.95
2021-05-21 20:30 | 44337.8542 | 0 | 10.1282 | 39.95
2021-05-21 21:00 | 44337.875 | 0 | 9.7764 | 39.95
2021-05-21 21:30 | 44337.8958 | 0 | 9.4112 | 39.95
2021-05-21 22:00 | 44337.9167 | 0 | 9.1241 | 39.95
2021-05-21 22:30 | 44337.9375 | 0 | 8.5548 | 39.95
2021-05-21 23:00 | 44337.9583 | 0 | 8.1725 | 39.95
2021-05-21 23:30 | 44337.9792 | 0 | 7.8516 | 39.95
2021-05-22 | 44338 | 0 | 7.5905 | 39.95
2021-05-22 00:30 | 44338.0208 | 0 | 7.299 | 39.95
2021-05-22 01:00 | 44338.0417 | 0 | 7.0394 | 39.95
2021-05-22 01:30 | 44338.0625 | 0 | 6.8263 | 39.95
2021-05-22 02:00 | 44338.0833 | 0 | 6.7931 | 39.95
2021-05-22 02:30 | 44338.1042 | 0 | 6.6743 | 39.95
2021-05-22 03:00 | 44338.125 | 0 | 6.727 | 39.95
2021-05-22 03:30 | 44338.1458 | 0 | 6.7717 | 39.95
2021-05-22 04:00 | 44338.1667 | 0 | 6.7107 | 39.95
2021-05-22 04:30 | 44338.1875 | 0 | 6.6362 | 39.95
2021-05-22 05:00 | 44338.2083 | 0 | 6.8814 | 39.95
2021-05-22 05:30 | 44338.2292 | 0 | 6.9767 | 39.95
2021-05-22 06:00 | 44338.25 | 0 | 7.3378 | 39.95
2021-05-22 06:30 | 44338.2708 | 0 | 7.6673 | 39.95
2021-05-22 07:00 | 44338.2917 | 0 | 7.827 | 39.95
2021-05-22 07:30 | 44338.3125 | 0 | 7.7777 | 39.95
2021-05-22 08:00 | 44338.3333 | 0 | 7.6956 | 39.95
2021-05-22 08:30 | 44338.3542 | 0 | 7.4551 | 39.95
2021-05-22 09:00 | 44338.375 | 0 | 7.2022 | 39.95
2021-05-22 09:30 | 44338.3958 | 0 | 6.7603 | 39.95
2021-05-22 10:00 | 44338.4167 | 0 | 6.4461 | 39.95
2021-05-22 10:30 | 44338.4375 | 0 | 6.735 | 39.95
2021-05-22 11:00 | 44338.4583 | 0 | 6.6853 | 39.95
2021-05-22 11:30 | 44338.4792 | 0 | 6.3246 | 39.95
2021-05-22 12:00 | 44338.5 | 0 | 7.0305 | 39.95
2021-05-22 12:30 | 44338.5208 | 0 | 6.3696 | 39.95
2021-05-22 13:00 | 44338.5417 | 0 | 6.3171 | 39.95
2021-05-22 13:30 | 44338.5625 | 0 | 7.7259 | 39.95
2021-05-22 14:00 | 44338.5833 | 0 | 8.0019 | 39.95
2021-05-22 14:30 | 44338.6042 | 0 | 8.125 | 39.95
2021-05-22 15:00 | 44338.625 | 0 | 8.5182 | 39.95
2021-05-22 15:30 | 44338.6458 | 0 | 9.6154 | 39.95
2021-05-22 16:00 | 44338.6667 | 0 | 9.9657 | 39.95
2021-05-22 16:30 | 44338.6875 | 0 | 10.6554 | 39.95
2021-05-22 17:00 | 44338.7083 | 0 | 11.3475 | 39.95
2021-05-22 17:30 | 44338.7292 | 0 | 11.9617 | 39.95
2021-05-22 18:00 | 44338.75 | 0 | 11.9691 | 39.95
2021-05-22 18:30 | 44338.7708 | 0 | 11.875 | 39.95
2021-05-22 19:00 | 44338.7917 | 0 | 11.6233 | 39.95
2021-05-22 19:30 | 44338.8125 | 0 | 11.2267 | 39.95
2021-05-22 20:00 | 44338.8333 | 0 | 10.8448 | 39.95
2021-05-22 20:30 | 44338.8542 | 0 | 10.294 | 39.95
2021-05-22 21:00 | 44338.875 | 0 | 9.9007 | 39.95
2021-05-22 21:30 | 44338.8958 | 0 | 9.5272 | 39.95
2021-05-22 22:00 | 44338.9167 | 0 | 9.1715 | 39.95
2021-05-22 22:30 | 44338.9375 | 0 | 8.4623 | 39.95
2021-05-22 23:00 | 44338.9583 | 0 | 8.0817 | 39.95
2021-05-22 23:30 | 44338.9792 | 0 | 7.671 | 39.95
2021-05-23 | 44339 | 0 | 7.2446 | 39.95
2021-05-23 00:30 | 44339.0208 | 0 | 7.131 | 39.95
2021-05-23 01:00 | 44339.0417 | 0 | 7.0182 | 39.95
2021-05-23 01:30 | 44339.0625 | 0 | 6.8033 | 39.95
2021-05-23 02:00 | 44339.0833 | 0 | 7.0551 | 39.95
2021-05-23 02:30 | 44339.1042 | 0 | 6.9449 | 39.95
2021-05-23 03:00 | 44339.125 | 0 | 6.9629 | 39.95
2021-05-23 03:30 | 44339.1458 | 0 | 7.1634 | 39.95
2021-05-23 04:00 | 44339.1667 | 0 | 7.4821 | 39.95
2021-05-23 04:30 | 44339.1875 | 0 | 7.9891 | 39.95
2021-05-23 05:00 | 44339.2083 | 0 | 8.6535 | 39.95
2021-05-23 05:30 | 44339.2292 | 0 | 9.4426 | 39.95
2021-05-23 06:00 | 44339.25 | 0 | 10.7363 | 39.95
2021-05-23 06:30 | 44339.2708 | 0 | 11.7333 | 39.95
2021-05-23 07:00 | 44339.2917 | 0 | 11.9663 | 39.95
2021-05-23 07:30 | 44339.3125 | 0 | 11.9465 | 39.95
2021-05-23 08:00 | 44339.3333 | 0 | 11.3733 | 39.95
2021-05-23 08:30 | 44339.3542 | 0 | 10.5387 | 39.95
2021-05-23 09:00 | 44339.375 | 0 | 10.1453 | 39.95
2021-05-23 09:30 | 44339.3958 | 0 | 9.6318 | 39.95
2021-05-23 10:00 | 44339.4167 | 0 | 9.5363 | 39.95
2021-05-23 10:30 | 44339.4375 | 0 | 9.317 | 39.95
2021-05-23 11:00 | 44339.4583 | 0 | 9.3584 | 39.95
2021-05-23 11:30 | 44339.4792 | 0 | 10.5325 | 39.95
2021-05-23 12:00 | 44339.5 | 0 | 11.1004 | 39.95
2021-05-23 12:30 | 44339.5208 | 0 | 10.7619 | 39.95
2021-05-23 13:00 | 44339.5417 | 0 | 9.9496 | 39.95
2021-05-23 13:30 | 44339.5625 | 0 | 10.9034 | 39.95
2021-05-23 14:00 | 44339.5833 | 0 | 10.0854 | 39.95
2021-05-23 14:30 | 44339.6042 | 0 | 11.0188 | 39.95
2021-05-23 15:00 | 44339.625 | 0 | 11.0058 | 39.95
2021-05-23 15:30 | 44339.6458 | 0 | 11.742 | 39.95
2021-05-23 16:00 | 44339.6667 | 0 | 11.975 | 39.95
2021-05-23 16:30 | 44339.6875 | 0 | 12.5926 | 39.95
2021-05-23 17:00 | 44339.7083 | 0 | 13.2547 | 39.95
2021-05-23 17:30 | 44339.7292 | 0 | 13.9688 | 39.95
2021-05-23 18:00 | 44339.75 | 0 | 13.9152 | 39.95
2021-05-23 18:30 | 44339.7708 | 0 | 13.801 | 39.95
2021-05-23 19:00 | 44339.7917 | 0 | 13.5481 | 39.95
2021-05-23 19:30 | 44339.8125 | 0 | 13.3417 | 39.95
2021-05-23 20:00 | 44339.8333 | 0 | 13.0077 | 39.95
2021-05-23 20:30 | 44339.8542 | 0 | 12.4524 | 39.95
2021-05-23 21:00 | 44339.875 | 0 | 11.8666 | 39.95
2021-05-23 21:30 | 44339.8958 | 0 | 11.4217 | 39.95
2021-05-23 22:00 | 44339.9167 | 0 | 10.6562 | 39.95
2021-05-23 22:30 | 44339.9375 | 0 | 9.762 | 39.95
2021-05-23 23:00 | 44339.9583 | 0 | 9.2958 | 39.95
2021-05-23 23:30 | 44339.9792 | 0 | 8.9612 | 39.95
2021-05-24 | 44340 | 0 | 8.5396 | 39.95
2021-05-24 00:30 | 44340.0208 | 0 | 8.1036 | 39.95
2021-05-24 01:00 | 44340.0417 | 0 | 7.9581 | 39.95
2021-05-24 01:30 | 44340.0625 | 0 | 7.6778 | 39.95
2021-05-24 02:00 | 44340.0833 | 0 | 7.6873 | 39.95
2021-05-24 02:30 | 44340.1042 | 0 | 7.5799 | 39.95
2021-05-24 03:00 | 44340.125 | 0 | 7.5512 | 39.95
2021-05-24 03:30 | 44340.1458 | 0 | 7.7689 | 39.95
2021-05-24 04:00 | 44340.1667 | 0 | 7.8756 | 39.95
2021-05-24 04:30 | 44340.1875 | 0 | 8.3327 | 39.95
2021-05-24 05:00 | 44340.2083 | 0 | 9.0647 | 39.95
2021-05-24 05:30 | 44340.2292 | 0 | 9.955 | 39.95
2021-05-24 06:00 | 44340.25 | 0 | 10.9076 | 39.95
2021-05-24 06:30 | 44340.2708 | 0 | 11.9197 | 39.95
2021-05-24 07:00 | 44340.2917 | 0 | 12.5175 | 39.95
2021-05-24 07:30 | 44340.3125 | 0 | 12.009 | 39.95
2021-05-24 08:00 | 44340.3333 | 0 | 11.4013 | 39.95
2021-05-24 08:30 | 44340.3542 | 0 | 10.5267 | 39.95
2021-05-24 09:00 | 44340.375 | 0 | 10.0387 | 39.95
2021-05-24 09:30 | 44340.3958 | 0 | 9.5219 | 39.95
2021-05-24 10:00 | 44340.4167 | 0 | 9.2798 | 39.95
2021-05-24 10:30 | 44340.4375 | 0 | 9.3004 | 39.95
2021-05-24 11:00 | 44340.4583 | 0 | 9.0765 | 39.95
2021-05-24 11:30 | 44340.4792 | 0 | 9.019 | 39.95
2021-05-24 12:00 | 44340.5 | 0 | 9.1287 | 39.95
2021-05-24 12:30 | 44340.5208 | 0 | 9.4916 | 39.95
2021-05-24 13:00 | 44340.5417 | 0 | 9.9885 | 39.95
2021-05-24 13:30 | 44340.5625 | 0 | 9.8779 | 39.95
2021-05-24 14:00 | 44340.5833 | 0 | 11.2155 | 39.95
2021-05-24 14:30 | 44340.6042 | 0 | 11.6588 | 39.95
2021-05-24 15:00 | 44340.625 | 0 | 12.1663 | 39.95
2021-05-24 15:30 | 44340.6458 | 0 | 12.344 | 39.95
2021-05-24 16:00 | 44340.6667 | 0 | 12.3969 | 39.95
2021-05-24 16:30 | 44340.6875 | 0 | 12.872 | 39.95
2021-05-24 17:00 | 44340.7083 | 0 | 13.3112 | 39.95
2021-05-24 17:30 | 44340.7292 | 0 | 13.8185 | 39.95
2021-05-24 18:00 | 44340.75 | 0 | 13.8794 | 39.95
2021-05-24 18:30 | 44340.7708 | 0 | 13.7987 | 39.95
2021-05-24 19:00 | 44340.7917 | 0 | 13.3157 | 39.95
2021-05-24 19:30 | 44340.8125 | 0 | 12.8227 | 39.95
2021-05-24 20:00 | 44340.8333 | 0 | 12.326 | 39.95
2021-05-24 20:30 | 44340.8542 | 0 | 12.0559 | 39.95
2021-05-24 21:00 | 44340.875 | 0 | 13.979 | 39.95
2021-05-24 21:30 | 44340.8958 | 0 | 12.6829 | 39.95
2021-05-24 22:00 | 44340.9167 | 0 | 11.3302 | 39.95
2021-05-24 22:30 | 44340.9375 | 0 | 10.2169 | 39.95
2021-05-24 23:00 | 44340.9583 | 0 | 9.487 | 39.95
2021-05-24 23:30 | 44340.9792 | 0 | 8.9425 | 39.95
2021-05-25 | 44341 | 0 | 8.4774 | 39.95
2021-05-25 00:30 | 44341.0208 | 0 | 8.1611 | 39.95
2021-05-25 01:00 | 44341.0417 | 0 | 7.9432 | 39.95
2021-05-25 01:30 | 44341.0625 | 0 | 7.7157 | 39.95
2021-05-25 02:00 | 44341.0833 | 0 | 7.7403 | 39.95
2021-05-25 02:30 | 44341.1042 | 0 | 7.6988 | 39.95
2021-05-25 03:00 | 44341.125 | 0 | 7.7709 | 39.95
2021-05-25 03:30 | 44341.1458 | 0 | 7.9287 | 39.95
2021-05-25 04:00 | 44341.1667 | 0 | 8.1227 | 39.95
2021-05-25 04:30 | 44341.1875 | 0 | 8.6097 | 39.95
2021-05-25 05:00 | 44341.2083 | 0 | 9.2431 | 39.95
2021-05-25 05:30 | 44341.2292 | 0 | 9.9084 | 39.95
2021-05-25 06:00 | 44341.25 | 0 | 11.041 | 39.95
2021-05-25 06:30 | 44341.2708 | 0 | 12.0053 | 39.95
2021-05-25 07:00 | 44341.2917 | 0 | 12.5071 | 39.95
2021-05-25 07:30 | 44341.3125 | 0 | 12.3737 | 39.95
2021-05-25 08:00 | 44341.3333 | 0 | 11.6817 | 39.95
2021-05-25 08:30 | 44341.3542 | 0 | 10.8331 | 39.95
2021-05-25 09:00 | 44341.375 | 0 | 10.1986 | 39.95
2021-05-25 09:30 | 44341.3958 | 0 | 9.7243 | 39.95
2021-05-25 10:00 | 44341.4167 | 0 | 9.3651 | 39.95
2021-05-25 10:30 | 44341.4375 | 0 | 9.1669 | 39.95
2021-05-25 11:00 | 44341.4583 | 0 | 9.2219 | 39.95
2021-05-25 11:30 | 44341.4792 | 0 | 9.0935 | 39.95
2021-05-25 12:00 | 44341.5 | 0 | 9.3342 | 39.95
2021-05-25 12:30 | 44341.5208 | 0 | 9.5414 | 39.95
2021-05-25 13:00 | 44341.5417 | 0 | 9.6864 | 39.95
2021-05-25 13:30 | 44341.5625 | 0 | 10.0629 | 39.95
2021-05-25 14:00 | 44341.5833 | 0 | 10.4706 | 39.95
2021-05-25 14:30 | 44341.6042 | 0 | 10.7307 | 39.95
2021-05-25 15:00 | 44341.625 | 0 | 11.205 | 39.95
2021-05-25 15:30 | 44341.6458 | 0 | 11.7989 | 39.95
2021-05-25 16:00 | 44341.6667 | 0 | 12.1915 | 39.95
2021-05-25 16:30 | 44341.6875 | 0 | 12.4005 | 39.95
2021-05-25 17:00 | 44341.7083 | 0 | 13.0864 | 39.95
2021-05-25 17:30 | 44341.7292 | 0 | 13.758 | 39.95
2021-05-25 18:00 | 44341.75 | 0 | 13.6661 | 39.95
2021-05-25 18:30 | 44341.7708 | 0 | 13.717 | 39.95
2021-05-25 19:00 | 44341.7917 | 0 | 13.0797 | 39.95
2021-05-25 19:30 | 44341.8125 | 0 | 12.8043 | 39.95
2021-05-25 20:00 | 44341.8333 | 0 | 12.8558 | 39.95
2021-05-25 20:30 | 44341.8542 | 0 | 13.1449 | 39.95
2021-05-25 21:00 | 44341.875 | 0 | 12.1082 | 39.95
2021-05-25 21:30 | 44341.8958 | 0 | 11.8964 | 39.95
2021-05-25 22:00 | 44341.9167 | 0 | 11.0294 | 39.95
2021-05-25 22:30 | 44341.9375 | 0 | 10.0864 | 39.95
2021-05-25 23:00 | 44341.9583 | 0 | 9.548 | 39.95
2021-05-25 23:30 | 44341.9792 | 0 | 9.2854 | 39.95
2021-05-26 | 44342 | 0 | 8.7055 | 39.95
2021-05-26 00:30 | 44342.0208 | 0 | 8.3753 | 39.95
2021-05-26 01:00 | 44342.0417 | 0 | 8.0491 | 39.95
2021-05-26 01:30 | 44342.0625 | 0 | 7.9811 | 39.95
2021-05-26 02:00 | 44342.0833 | 0 | 7.886 | 39.95
2021-05-26 02:30 | 44342.1042 | 0 | 7.8056 | 39.95
2021-05-26 03:00 | 44342.125 | 0 | 7.8577 | 39.95
2021-05-26 03:30 | 44342.1458 | 0 | 8.1322 | 39.95
2021-05-26 04:00 | 44342.1667 | 0 | 8.3322 | 39.95
2021-05-26 04:30 | 44342.1875 | 0 | 8.5921 | 39.95
2021-05-26 05:00 | 44342.2083 | 0 | 9.2623 | 39.95
2021-05-26 05:30 | 44342.2292 | 0 | 9.933 | 39.95
2021-05-26 06:00 | 44342.25 | 0 | 11.1578 | 39.95
2021-05-26 06:30 | 44342.2708 | 0 | 12.7934 | 39.95
2021-05-26 07:00 | 44342.2917 | 0 | 13.1029 | 39.95
2021-05-26 07:30 | 44342.3125 | 0 | 13.2004 | 39.95
2021-05-26 08:00 | 44342.3333 | 0 | 12.374 | 39.95
2021-05-26 08:30 | 44342.3542 | 0 | 11.5331 | 39.95
2021-05-26 09:00 | 44342.375 | 0 | 11.5775 | 39.95
2021-05-26 09:30 | 44342.3958 | 0 | 11.2082 | 39.95
2021-05-26 10:00 | 44342.4167 | 0 | 11.256 | 39.95
2021-05-26 10:30 | 44342.4375 | 0 | 10.7134 | 39.95
2021-05-26 11:00 | 44342.4583 | 0 | 10.1084 | 39.95
2021-05-26 11:30 | 44342.4792 | 0 | 9.5296 | 39.95
2021-05-26 12:00 | 44342.5 | 0 | 10.0962 | 39.95
2021-05-26 12:30 | 44342.5208 | 0 | 10.7678 | 39.95
2021-05-26 13:00 | 44342.5417 | 0 | 10.5114 | 39.95
2021-05-26 13:30 | 44342.5625 | 0 | 10.4263 | 39.95
2021-05-26 14:00 | 44342.5833 | 0 | 10.0849 | 39.95
2021-05-26 14:30 | 44342.6042 | 0 | 10.7455 | 39.95
2021-05-26 15:00 | 44342.625 | 0 | 11.282 | 39.95
2021-05-26 15:30 | 44342.6458 | 0 | 12.0934 | 39.95
2021-05-26 16:00 | 44342.6667 | 0 | 12.5812 | 39.95
2021-05-26 16:30 | 44342.6875 | 0 | 12.8342 | 39.95
2021-05-26 17:00 | 44342.7083 | 0 | 13.3586 | 39.95
2021-05-26 17:30 | 44342.7292 | 0 | 13.7323 | 39.95
2021-05-26 18:00 | 44342.75 | 0 | 13.4199 | 39.95
2021-05-26 18:30 | 44342.7708 | 0 | 13.3231 | 39.95
2021-05-26 19:00 | 44342.7917 | 0 | 12.8066 | 39.95
2021-05-26 19:30 | 44342.8125 | 0 | 12.8075 | 39.95
2021-05-26 20:00 | 44342.8333 | 0 | 12.9725 | 39.95
2021-05-26 20:30 | 44342.8542 | 0 | 12.9204 | 39.95
2021-05-26 21:00 | 44342.875 | 0 | 11.9949 | 39.95
2021-05-26 21:30 | 44342.8958 | 0 | 11.849 | 39.95
2021-05-26 22:00 | 44342.9167 | 0 | 10.7958 | 39.95
2021-05-26 22:30 | 44342.9375 | 0 | 9.954 | 39.95
2021-05-26 23:00 | 44342.9583 | 0 | 9.3787 | 39.95
2021-05-26 23:30 | 44342.9792 | 0 | 9.2094 | 39.95
2021-05-27 | 44343 | 0 | 8.6967 | 39.95
2021-05-27 00:30 | 44343.0208 | 0 | 8.3032 | 39.95
2021-05-27 01:00 | 44343.0417 | 0 | 8.028 | 39.95
2021-05-27 01:30 | 44343.0625 | 0 | 7.8565 | 39.95
2021-05-27 02:00 | 44343.0833 | 0 | 7.9359 | 39.95
2021-05-27 02:30 | 44343.1042 | 0 | 7.9647 | 39.95
2021-05-27 03:00 | 44343.125 | 0 | 7.7778 | 39.95
2021-05-27 03:30 | 44343.1458 | 0 | 7.8892 | 39.95
2021-05-27 04:00 | 44343.1667 | 0 | 8.2062 | 39.95
2021-05-27 04:30 | 44343.1875 | 0 | 8.5003 | 39.95
2021-05-27 05:00 | 44343.2083 | 0 | 9.1933 | 39.95
2021-05-27 05:30 | 44343.2292 | 0 | 10.0867 | 39.95
2021-05-27 06:00 | 44343.25 | 0 | 11.2707 | 39.95
2021-05-27 06:30 | 44343.2708 | 0 | 12.2056 | 39.95
2021-05-27 07:00 | 44343.2917 | 0 | 12.8419 | 39.95
2021-05-27 07:30 | 44343.3125 | 0 | 12.5689 | 39.95
2021-05-27 08:00 | 44343.3333 | 0 | 12.1353 | 39.95
2021-05-27 08:30 | 44343.3542 | 0 | 11.161 | 39.95
2021-05-27 09:00 | 44343.375 | 0 | 10.4162 | 39.95
2021-05-27 09:30 | 44343.3958 | 0 | 9.7904 | 39.95
2021-05-27 10:00 | 44343.4167 | 0 | 9.3179 | 39.95
2021-05-27 10:30 | 44343.4375 | 0 | 9.1945 | 39.95
2021-05-27 11:00 | 44343.4583 | 0 | 8.7731 | 39.95
2021-05-27 11:30 | 44343.4792 | 0 | 8.4428 | 39.95
2021-05-27 12:00 | 44343.5 | 0 | 8.5433 | 39.95
2021-05-27 12:30 | 44343.5208 | 0 | 8.4114 | 39.95
2021-05-27 13:00 | 44343.5417 | 0 | 8.4624 | 39.95
2021-05-27 13:30 | 44343.5625 | 0 | 8.8183 | 39.95
2021-05-27 14:00 | 44343.5833 | 0 | 9.3235 | 39.95
2021-05-27 14:30 | 44343.6042 | 0 | 9.8197 | 39.95
2021-05-27 15:00 | 44343.625 | 0 | 10.4673 | 39.95
2021-05-27 15:30 | 44343.6458 | 0 | 11.1596 | 39.95
2021-05-27 16:00 | 44343.6667 | 0 | 11.7287 | 39.95
2021-05-27 16:30 | 44343.6875 | 0 | 12.1751 | 39.95
2021-05-27 17:00 | 44343.7083 | 0 | 12.8119 | 39.95
2021-05-27 17:30 | 44343.7292 | 0 | 13.4486 | 39.95
2021-05-27 18:00 | 44343.75 | 0 | 13.332 | 39.95
2021-05-27 18:30 | 44343.7708 | 0 | 13.2747 | 39.95
2021-05-27 19:00 | 44343.7917 | 0 | 13.235 | 39.95
2021-05-27 19:30 | 44343.8125 | 0 | 12.9537 | 39.95
2021-05-27 20:00 | 44343.8333 | 0 | 12.9013 | 39.95
2021-05-27 20:30 | 44343.8542 | 0 | 12.528 | 39.95
2021-05-27 21:00 | 44343.875 | 0 | 11.9467 | 39.95
2021-05-27 21:30 | 44343.8958 | 0 | 11.4639 | 39.95
2021-05-27 22:00 | 44343.9167 | 0 | 11.0573 | 39.95
2021-05-27 22:30 | 44343.9375 | 0 | 10.3208 | 39.95
2021-05-27 23:00 | 44343.9583 | 0 | 9.658 | 39.95
2021-05-27 23:30 | 44343.9792 | 0 | 9.2088 | 39.95
2021-05-28 | 44344 | 0 | 8.6713 | 39.95
2021-05-28 00:30 | 44344.0208 | 0 | 8.2768 | 39.95
2021-05-28 01:00 | 44344.0417 | 0 | 8.0483 | 39.95
2021-05-28 01:30 | 44344.0625 | 0 | 7.8754 | 39.95
2021-05-28 02:00 | 44344.0833 | 0 | 7.715 | 39.95
2021-05-28 02:30 | 44344.1042 | 0 | 7.6163 | 39.95
2021-05-28 03:00 | 44344.125 | 0 | 7.6063 | 39.95
2021-05-28 03:30 | 44344.1458 | 0 | 7.6452 | 39.95
2021-05-28 04:00 | 44344.1667 | 0 | 7.7036 | 39.95
2021-05-28 04:30 | 44344.1875 | 0 | 7.8774 | 39.95
2021-05-28 05:00 | 44344.2083 | 0 | 8.1486 | 39.95
2021-05-28 05:30 | 44344.2292 | 0 | 8.4248 | 39.95
2021-05-28 06:00 | 44344.25 | 0 | 8.8481 | 39.95
2021-05-28 06:30 | 44344.2708 | 0 | 9.4547 | 39.95
2021-05-28 07:00 | 44344.2917 | 0 | 10.2592 | 39.95
2021-05-28 07:30 | 44344.3125 | 0 | 10.5385 | 39.95
2021-05-28 08:00 | 44344.3333 | 0 | 10.0591 | 39.95
2021-05-28 08:30 | 44344.3542 | 0 | 9.9035 | 39.95
2021-05-28 09:00 | 44344.375 | 0 | 9.8109 | 39.95
2021-05-28 09:30 | 44344.3958 | 0 | 8.8115 | 39.95
2021-05-28 10:00 | 44344.4167 | 0 | 8.4203 | 39.95
2021-05-28 10:30 | 44344.4375 | 0 | 7.6729 | 39.95
2021-05-28 11:00 | 44344.4583 | 0 | 6.9262 | 39.95
2021-05-28 11:30 | 44344.4792 | 0 | 6.695 | 39.95
2021-05-28 12:00 | 44344.5 | 0 | 6.3665 | 39.95
2021-05-28 12:30 | 44344.5208 | 0 | 6.3817 | 39.95
2021-05-28 13:00 | 44344.5417 | 0 | 6.5545 | 39.95
2021-05-28 13:30 | 44344.5625 | 0 | 7.9506 | 39.95
2021-05-28 14:00 | 44344.5833 | 0 | 8.403 | 39.95
2021-05-28 14:30 | 44344.6042 | 0 | 8.6547 | 39.95
2021-05-28 15:00 | 44344.625 | 0 | 9.0773 | 39.95
2021-05-28 15:30 | 44344.6458 | 0 | 9.4276 | 39.95
2021-05-28 16:00 | 44344.6667 | 0 | 10.0229 | 39.95
2021-05-28 16:30 | 44344.6875 | 0 | 10.6774 | 39.95
2021-05-28 17:00 | 44344.7083 | 0 | 11.4306 | 39.95
2021-05-28 17:30 | 44344.7292 | 0 | 11.8733 | 39.95
2021-05-28 18:00 | 44344.75 | 0 | 11.8818 | 39.95
2021-05-28 18:30 | 44344.7708 | 0 | 11.9394 | 39.95
2021-05-28 19:00 | 44344.7917 | 0 | 11.753 | 39.95
2021-05-28 19:30 | 44344.8125 | 0 | 11.6201 | 39.95
2021-05-28 20:00 | 44344.8333 | 0 | 11.4142 | 39.95
2021-05-28 20:30 | 44344.8542 | 0 | 10.9042 | 39.95
2021-05-28 21:00 | 44344.875 | 0 | 10.5252 | 39.95
2021-05-28 21:30 | 44344.8958 | 0 | 10.2429 | 39.95
2021-05-28 22:00 | 44344.9167 | 0 | 9.8956 | 39.95
2021-05-28 22:30 | 44344.9375 | 0 | 9.2456 | 39.95
2021-05-28 23:00 | 44344.9583 | 0 | 8.6117 | 39.95
2021-05-28 23:30 | 44344.9792 | 0 | 8.1168 | 39.95
2021-05-29 | 44345 | 0 | 7.8499 | 39.95
2021-05-29 00:30 | 44345.0208 | 0 | 7.4966 | 39.95
2021-05-29 01:00 | 44345.0417 | 0 | 7.2435 | 39.95
2021-05-29 01:30 | 44345.0625 | 0 | 7.0995 | 39.95
2021-05-29 02:00 | 44345.0833 | 0 | 7.0282 | 39.95
2021-05-29 02:30 | 44345.1042 | 0 | 6.8942 | 39.95
2021-05-29 03:00 | 44345.125 | 0 | 6.8859 | 39.95
2021-05-29 03:30 | 44345.1458 | 0 | 7.0033 | 39.95
2021-05-29 04:00 | 44345.1667 | 0 | 6.9472 | 39.95
2021-05-29 04:30 | 44345.1875 | 0 | 6.867 | 39.95
2021-05-29 05:00 | 44345.2083 | 0 | 7.0998 | 39.95
2021-05-29 05:30 | 44345.2292 | 0 | 7.332 | 39.95
2021-05-29 06:00 | 44345.25 | 0 | 7.7559 | 39.95
2021-05-29 06:30 | 44345.2708 | 0 | 8.179 | 39.95
2021-05-29 07:00 | 44345.2917 | 0 | 8.8728 | 39.95
2021-05-29 07:30 | 44345.3125 | 0 | 8.6495 | 39.95
2021-05-29 08:00 | 44345.3333 | 0 | 8.422 | 39.95
2021-05-29 08:30 | 44345.3542 | 0 | 8.2453 | 39.95
2021-05-29 09:00 | 44345.375 | 0 | 7.9164 | 39.95
2021-05-29 09:30 | 44345.3958 | 0 | 7.8825 | 39.95
2021-05-29 10:00 | 44345.4167 | 0 | 7.2251 | 39.95
2021-05-29 10:30 | 44345.4375 | 0 | 6.6209 | 39.95
2021-05-29 11:00 | 44345.4583 | 0 | 6.5621 | 39.95
2021-05-29 11:30 | 44345.4792 | 0 | 6.6934 | 39.95
2021-05-29 12:00 | 44345.5 | 0 | 6.4548 | 39.95
2021-05-29 12:30 | 44345.5208 | 0 | 8.0507 | 39.95
2021-05-29 13:00 | 44345.5417 | 0 | 7.8195 | 39.95
2021-05-29 13:30 | 44345.5625 | 0 | 7.6279 | 39.95
2021-05-29 14:00 | 44345.5833 | 0 | 7.8247 | 39.95
2021-05-29 14:30 | 44345.6042 | 0 | 8.8692 | 39.95
2021-05-29 15:00 | 44345.625 | 0 | 8.3136 | 39.95
2021-05-29 15:30 | 44345.6458 | 0 | 9.7671 | 39.95
2021-05-29 16:00 | 44345.6667 | 0 | 10.2066 | 39.95
2021-05-29 16:30 | 44345.6875 | 0 | 10.7304 | 39.95
2021-05-29 17:00 | 44345.7083 | 0 | 11.882 | 39.95
2021-05-29 17:30 | 44345.7292 | 0 | 12.3863 | 39.95
2021-05-29 18:00 | 44345.75 | 0 | 12.3585 | 39.95
2021-05-29 18:30 | 44345.7708 | 0 | 12.1263 | 39.95
2021-05-29 19:00 | 44345.7917 | 0 | 11.7657 | 39.95
2021-05-29 19:30 | 44345.8125 | 0 | 11.843 | 39.95
2021-05-29 20:00 | 44345.8333 | 0 | 11.8961 | 39.95
2021-05-29 20:30 | 44345.8542 | 0 | 11.5703 | 39.95
2021-05-29 21:00 | 44345.875 | 0 | 11.0425 | 39.95
2021-05-29 21:30 | 44345.8958 | 0 | 10.5156 | 39.95
2021-05-29 22:00 | 44345.9167 | 0 | 10.0178 | 39.95
2021-05-29 22:30 | 44345.9375 | 0 | 9.1936 | 39.95
2021-05-29 23:00 | 44345.9583 | 0 | 8.6507 | 39.95
2021-05-29 23:30 | 44345.9792 | 0 | 8.2619 | 39.95
2021-05-30 | 44346 | 0 | 8.0143 | 39.95
2021-05-30 00:30 | 44346.0208 | 0 | 7.782 | 39.95
2021-05-30 01:00 | 44346.0417 | 0 | 7.6384 | 39.95
2021-05-30 01:30 | 44346.0625 | 0 | 7.5447 | 39.95
2021-05-30 02:00 | 44346.0833 | 0 | 7.5871 | 39.95
2021-05-30 02:30 | 44346.1042 | 0 | 7.4287 | 39.95
2021-05-30 03:00 | 44346.125 | 0 | 7.4754 | 39.95
2021-05-30 03:30 | 44346.1458 | 0 | 7.9176 | 39.95
2021-05-30 04:00 | 44346.1667 | 0 | 8.1324 | 39.95
2021-05-30 04:30 | 44346.1875 | 0 | 8.6668 | 39.95
2021-05-30 05:00 | 44346.2083 | 0 | 9.4188 | 39.95
2021-05-30 05:30 | 44346.2292 | 0 | 9.8804 | 39.95
2021-05-30 06:00 | 44346.25 | 0 | 11.218 | 39.95
2021-05-30 06:30 | 44346.2708 | 0 | 12.2706 | 39.95
2021-05-30 07:00 | 44346.2917 | 0 | 12.7623 | 39.95
2021-05-30 07:30 | 44346.3125 | 0 | 12.9696 | 39.95
2021-05-30 08:00 | 44346.3333 | 0 | 12.7121 | 39.95
2021-05-30 08:30 | 44346.3542 | 0 | 11.873 | 39.95
2021-05-30 09:00 | 44346.375 | 0 | 11.1065 | 39.95
2021-05-30 09:30 | 44346.3958 | 0 | 10.3764 | 39.95
2021-05-30 10:00 | 44346.4167 | 0 | 9.659 | 39.95
2021-05-30 10:30 | 44346.4375 | 0 | 9.569 | 39.95
2021-05-30 11:00 | 44346.4583 | 0 | 9.3202 | 39.95
2021-05-30 11:30 | 44346.4792 | 0 | 9.7465 | 39.95
2021-05-30 12:00 | 44346.5 | 0 | 10.8002 | 39.95
2021-05-30 12:30 | 44346.5208 | 0 | 11.3255 | 39.95
2021-05-30 13:00 | 44346.5417 | 0 | 11.2197 | 39.95
2021-05-30 13:30 | 44346.5625 | 0 | 10.3175 | 39.95
2021-05-30 14:00 | 44346.5833 | 0 | 11.5653 | 39.95
2021-05-30 14:30 | 44346.6042 | 0 | 11.2269 | 39.95
2021-05-30 15:00 | 44346.625 | 0 | 11.6247 | 39.95
2021-05-30 15:30 | 44346.6458 | 0 | 11.256 | 39.95
2021-05-30 16:00 | 44346.6667 | 0 | 11.8874 | 39.95
2021-05-30 16:30 | 44346.6875 | 0 | 12.5641 | 39.95
2021-05-30 17:00 | 44346.7083 | 0 | 13.4897 | 39.95
2021-05-30 17:30 | 44346.7292 | 0 | 14.465 | 39.95
2021-05-30 18:00 | 44346.75 | 0 | 14.4784 | 39.95
2021-05-30 18:30 | 44346.7708 | 0 | 14.4478 | 39.95
2021-05-30 19:00 | 44346.7917 | 0 | 14.1898 | 39.95
2021-05-30 19:30 | 44346.8125 | 0 | 13.966 | 39.95
2021-05-30 20:00 | 44346.8333 | 0 | 13.7374 | 39.95
2021-05-30 20:30 | 44346.8542 | 0 | 13.053 | 39.95
2021-05-30 21:00 | 44346.875 | 0 | 12.5361 | 39.95
2021-05-30 21:30 | 44346.8958 | 0 | 11.8886 | 39.95
2021-05-30 22:00 | 44346.9167 | 0 | 11.2054 | 39.95
2021-05-30 22:30 | 44346.9375 | 0 | 10.34 | 39.95
2021-05-30 23:00 | 44346.9583 | 0 | 9.7028 | 39.95
2021-05-30 23:30 | 44346.9792 | 0 | 9.1991 | 39.95
2021-05-31 | 44347 | 0 | 8.635 | 39.95
2021-05-31 00:30 | 44347.0208 | 0 | 8.2462 | 39.95
2021-05-31 01:00 | 44347.0417 | 0 | 7.9928 | 39.95
2021-05-31 01:30 | 44347.0625 | 0 | 7.8932 | 39.95
2021-05-31 02:00 | 44347.0833 | 0 | 7.8394 | 39.95
2021-05-31 02:30 | 44347.1042 | 0 | 7.7297 | 39.95
2021-05-31 03:00 | 44347.125 | 0 | 7.6899 | 39.95
2021-05-31 03:30 | 44347.1458 | 0 | 7.85 | 39.95
2021-05-31 04:00 | 44347.1667 | 0 | 8.2411 | 39.95
2021-05-31 04:30 | 44347.1875 | 0 | 8.7239 | 39.95
2021-05-31 05:00 | 44347.2083 | 0 | 9.4616 | 39.95
2021-05-31 05:30 | 44347.2292 | 0 | 10.2419 | 39.95
2021-05-31 06:00 | 44347.25 | 0 | 11.5988 | 39.95
2021-05-31 06:30 | 44347.2708 | 0 | 13.0105 | 39.95
2021-05-31 07:00 | 44347.2917 | 0 | 13.9021 | 39.95
2021-05-31 07:30 | 44347.3125 | 0 | 13.7008 | 39.95
2021-05-31 08:00 | 44347.3333 | 0 | 13.5575 | 39.95
2021-05-31 08:30 | 44347.3542 | 0 | 11.5997 | 39.95
2021-05-31 09:00 | 44347.375 | 0 | 10.7253 | 39.95
2021-05-31 09:30 | 44347.3958 | 0 | 9.9519 | 39.95
2021-05-31 10:00 | 44347.4167 | 0 | 9.5845 | 39.95
2021-05-31 10:30 | 44347.4375 | 0 | 9.6233 | 39.95
2021-05-31 11:00 | 44347.4583 | 0 | 9.1203 | 39.95
2021-05-31 11:30 | 44347.4792 | 0 | 8.8893 | 39.95
2021-05-31 12:00 | 44347.5 | 0 | 8.795 | 39.95
2021-05-31 12:30 | 44347.5208 | 0 | 9.0169 | 39.95
2021-05-31 13:00 | 44347.5417 | 0 | 8.9675 | 39.95
2021-05-31 13:30 | 44347.5625 | 0 | 9.3856 | 39.95
2021-05-31 14:00 | 44347.5833 | 0 | 10.2079 | 39.95
2021-05-31 14:30 | 44347.6042 | 0 | 10.5836 | 39.95
2021-05-31 15:00 | 44347.625 | 0 | 11.4814 | 39.95
2021-05-31 15:30 | 44347.6458 | 0 | 11.7573 | 39.95
2021-05-31 16:00 | 44347.6667 | 0 | 12.4916 | 39.95
2021-05-31 16:30 | 44347.6875 | 0 | 12.7841 | 39.95
2021-05-31 17:00 | 44347.7083 | 0 | 13.6752 | 39.95
2021-05-31 17:30 | 44347.7292 | 0 | 14.0856 | 39.95
2021-05-31 18:00 | 44347.75 | 0 | 14.2946 | 39.95
2021-05-31 18:30 | 44347.7708 | 0 | 14.2863 | 39.95
2021-05-31 19:00 | 44347.7917 | 0 | 14.1237 | 39.95
2021-05-31 19:30 | 44347.8125 | 0 | 14.0341 | 39.95
2021-05-31 20:00 | 44347.8333 | 0 | 13.4542 | 39.95
2021-05-31 20:30 | 44347.8542 | 0 | 12.873 | 39.95
2021-05-31 21:00 | 44347.875 | 0 | 12.4953 | 39.95
2021-05-31 21:30 | 44347.8958 | 0 | 11.9329 | 39.95
2021-05-31 22:00 | 44347.9167 | 0 | 11.1498 | 39.95
2021-05-31 22:30 | 44347.9375 | 0 | 10.306 | 39.95
2021-05-31 23:00 | 44347.9583 | 0 | 9.6531 | 39.95
2021-05-31 23:30 | 44347.9792 | 0 | 9.1651 | 39.95
2021-06-01 | 44348 | 0 | 8.5775 | 39.95
2021-06-01 00:30 | 44348.0208 | 0 | 8.1289 | 39.95
2021-06-01 01:00 | 44348.0417 | 0 | 7.9894 | 39.95
2021-06-01 01:30 | 44348.0625 | 0 | 7.8711 | 39.95
2021-06-01 02:00 | 44348.0833 | 0 | 7.8619 | 39.95
2021-06-01 02:30 | 44348.1042 | 0 | 7.6586 | 39.95
2021-06-01 03:00 | 44348.125 | 0 | 7.7692 | 39.95
2021-06-01 03:30 | 44348.1458 | 0 | 7.9416 | 39.95
2021-06-01 04:00 | 44348.1667 | 0 | 8.1831 | 39.95
2021-06-01 04:30 | 44348.1875 | 0 | 8.5483 | 39.95
2021-06-01 05:00 | 44348.2083 | 0 | 9.1876 | 39.95
2021-06-01 05:30 | 44348.2292 | 0 | 10.0695 | 39.95
2021-06-01 06:00 | 44348.25 | 0 | 11.4436 | 39.95
2021-06-01 06:30 | 44348.2708 | 0 | 12.4555 | 39.95
2021-06-01 07:00 | 44348.2917 | 0 | 13.1532 | 39.95
2021-06-01 07:30 | 44348.3125 | 0 | 13.3105 | 39.95
2021-06-01 08:00 | 44348.3333 | 0 | 12.2667 | 39.95
2021-06-01 08:30 | 44348.3542 | 0 | 11.2092 | 39.95
2021-06-01 09:00 | 44348.375 | 0 | 10.7635 | 39.95
2021-06-01 09:30 | 44348.3958 | 0 | 10.0208 | 39.95
2021-06-01 10:00 | 44348.4167 | 0 | 9.5657 | 39.95
2021-06-01 10:30 | 44348.4375 | 0 | 9.9724 | 39.95
2021-06-01 11:00 | 44348.4583 | 0 | 9.8576 | 39.95
2021-06-01 11:30 | 44348.4792 | 0 | 10.4914 | 39.95
2021-06-01 12:00 | 44348.5 | 0 | 10.3358 | 39.95
2021-06-01 12:30 | 44348.5208 | 0 | 10.8222 | 39.95
2021-06-01 13:00 | 44348.5417 | 0 | 10.7067 | 39.95
2021-06-01 13:30 | 44348.5625 | 0 | 11.1828 | 39.95
2021-06-01 14:00 | 44348.5833 | 0 | 11.5184 | 39.95
2021-06-01 14:30 | 44348.6042 | 0 | 11.6998 | 39.95
2021-06-01 15:00 | 44348.625 | 0 | 11.6708 | 39.95
2021-06-01 15:30 | 44348.6458 | 0 | 11.9749 | 39.95
2021-06-01 16:00 | 44348.6667 | 0 | 11.9469 | 39.95
2021-06-01 16:30 | 44348.6875 | 0 | 12.5414 | 39.95
2021-06-01 17:00 | 44348.7083 | 0 | 13.5374 | 39.95
2021-06-01 17:30 | 44348.7292 | 0 | 14.0965 | 39.95
2021-06-01 18:00 | 44348.75 | 0 | 14.2465 | 39.95
2021-06-01 18:30 | 44348.7708 | 0 | 14.4844 | 39.95
2021-06-01 19:00 | 44348.7917 | 0 | 13.9227 | 39.95
2021-06-01 19:30 | 44348.8125 | 0 | 13.7171 | 39.95
2021-06-01 20:00 | 44348.8333 | 0 | 13.4537 | 39.95
2021-06-01 20:30 | 44348.8542 | 0 | 12.7326 | 39.95
2021-06-01 21:00 | 44348.875 | 0 | 12.2079 | 39.95
2021-06-01 21:30 | 44348.8958 | 0 | 11.7859 | 39.95
2021-06-01 22:00 | 44348.9167 | 0 | 11.109 | 39.95
2021-06-01 22:30 | 44348.9375 | 0 | 10.2719 | 39.95
2021-06-01 23:00 | 44348.9583 | 0 | 9.5474 | 39.95
2021-06-01 23:30 | 44348.9792 | 0 | 9.1956 | 39.95
2021-06-02 | 44349 | 0 | 8.6673 | 39.95
2021-06-02 00:30 | 44349.0208 | 0 | 8.3 | 39.95
2021-06-02 01:00 | 44349.0417 | 0 | 7.9244 | 39.95
2021-06-02 01:30 | 44349.0625 | 0 | 7.815 | 39.95
2021-06-02 02:00 | 44349.0833 | 0 | 7.7222 | 39.95
2021-06-02 02:30 | 44349.1042 | 0 | 7.6999 | 39.95
2021-06-02 03:00 | 44349.125 | 0 | 7.7022 | 39.95
2021-06-02 03:30 | 44349.1458 | 0 | 7.7641 | 39.95
2021-06-02 04:00 | 44349.1667 | 0 | 8.0776 | 39.95
2021-06-02 04:30 | 44349.1875 | 0 | 8.4803 | 39.95
2021-06-02 05:00 | 44349.2083 | 0 | 9.1216 | 39.95
2021-06-02 05:30 | 44349.2292 | 0 | 9.8953 | 39.95
2021-06-02 06:00 | 44349.25 | 0 | 11.0441 | 39.95
2021-06-02 06:30 | 44349.2708 | 0 | 12.1114 | 39.95
2021-06-02 07:00 | 44349.2917 | 0 | 12.8859 | 39.95
2021-06-02 07:30 | 44349.3125 | 0 | 12.8409 | 39.95
2021-06-02 08:00 | 44349.3333 | 0 | 12.6998 | 39.95
2021-06-02 08:30 | 44349.3542 | 0 | 11.2411 | 39.95
2021-06-02 09:00 | 44349.375 | 0 | 11.6181 | 39.95
2021-06-02 09:30 | 44349.3958 | 0 | 10.4266 | 39.95
2021-06-02 10:00 | 44349.4167 | 0 | 9.7283 | 39.95
2021-06-02 10:30 | 44349.4375 | 0 | 11.1258 | 39.95
2021-06-02 11:00 | 44349.4583 | 0 | 12.0922 | 39.95
2021-06-02 11:30 | 44349.4792 | 0 | 12.263 | 39.95
2021-06-02 12:00 | 44349.5 | 0 | 12.2509 | 39.95
2021-06-02 12:30 | 44349.5208 | 0 | 12.2328 | 39.95
2021-06-02 13:00 | 44349.5417 | 0 | 12.4286 | 39.95
2021-06-02 13:30 | 44349.5625 | 0 | 12.2239 | 39.95
2021-06-02 14:00 | 44349.5833 | 0 | 12.4282 | 39.95
2021-06-02 14:30 | 44349.6042 | 0 | 12.5151 | 39.95
2021-06-02 15:00 | 44349.625 | 0 | 12.3634 | 39.95
2021-06-02 15:30 | 44349.6458 | 0 | 12.5455 | 39.95
2021-06-02 16:00 | 44349.6667 | 0 | 13.0061 | 39.95
2021-06-02 16:30 | 44349.6875 | 0 | 13.4566 | 39.95
2021-06-02 17:00 | 44349.7083 | 0 | 14.0718 | 39.95
2021-06-02 17:30 | 44349.7292 | 0 | 14.6288 | 39.95
2021-06-02 18:00 | 44349.75 | 0 | 14.5912 | 39.95
2021-06-02 18:30 | 44349.7708 | 0 | 14.3351 | 39.95
2021-06-02 19:00 | 44349.7917 | 0 | 13.969 | 39.95
2021-06-02 19:30 | 44349.8125 | 0 | 14.0988 | 39.95
2021-06-02 20:00 | 44349.8333 | 0 | 13.6643 | 39.95
2021-06-02 20:30 | 44349.8542 | 0 | 12.8587 | 39.95
2021-06-02 21:00 | 44349.875 | 0 | 12.5679 | 39.95
2021-06-02 21:30 | 44349.8958 | 0 | 11.9603 | 39.95
2021-06-02 22:00 | 44349.9167 | 0 | 11.4003 | 39.95
2021-06-02 22:30 | 44349.9375 | 0 | 10.3547 | 39.95
2021-06-02 23:00 | 44349.9583 | 0 | 9.6193 | 39.95
2021-06-02 23:30 | 44349.9792 | 0 | 9.2092 | 39.95
2021-06-03 | 44350 | 0 | 8.7303 | 39.95
2021-06-03 00:30 | 44350.0208 | 0 | 8.2781 | 39.95
2021-06-03 01:00 | 44350.0417 | 0 | 7.9496 | 39.95
2021-06-03 01:30 | 44350.0625 | 0 | 7.878 | 39.95
2021-06-03 02:00 | 44350.0833 | 0 | 7.7709 | 39.95
2021-06-03 02:30 | 44350.1042 | 0 | 7.7297 | 39.95
2021-06-03 03:00 | 44350.125 | 0 | 7.6816 | 39.95
2021-06-03 03:30 | 44350.1458 | 0 | 7.8385 | 39.95
2021-06-03 04:00 | 44350.1667 | 0 | 8.0782 | 39.95
2021-06-03 04:30 | 44350.1875 | 0 | 8.5419 | 39.95
2021-06-03 05:00 | 44350.2083 | 0 | 9.3511 | 39.95
2021-06-03 05:30 | 44350.2292 | 0 | 10.2164 | 39.95
2021-06-03 06:00 | 44350.25 | 0 | 11.248 | 39.95
2021-06-03 06:30 | 44350.2708 | 0 | 12.3363 | 39.95
2021-06-03 07:00 | 44350.2917 | 0 | 13.1117 | 39.95
2021-06-03 07:30 | 44350.3125 | 0 | 12.8432 | 39.95
2021-06-03 08:00 | 44350.3333 | 0 | 12.1746 | 39.95
2021-06-03 08:30 | 44350.3542 | 0 | 11.2044 | 39.95
2021-06-03 09:00 | 44350.375 | 0 | 10.6733 | 39.95
2021-06-03 09:30 | 44350.3958 | 0 | 10.0958 | 39.95
2021-06-03 10:00 | 44350.4167 | 0 | 9.5334 | 39.95
2021-06-03 10:30 | 44350.4375 | 0 | 9.2491 | 39.95
2021-06-03 11:00 | 44350.4583 | 0 | 8.9807 | 39.95
2021-06-03 11:30 | 44350.4792 | 0 | 8.6396 | 39.95
2021-06-03 12:00 | 44350.5 | 0 | 9.0199 | 39.95
2021-06-03 12:30 | 44350.5208 | 0 | 9.1641 | 39.95
2021-06-03 13:00 | 44350.5417 | 0 | 9.1191 | 39.95
2021-06-03 13:30 | 44350.5625 | 0 | 8.9526 | 39.95
2021-06-03 14:00 | 44350.5833 | 0 | 9.4164 | 39.95
2021-06-03 14:30 | 44350.6042 | 0 | 9.9497 | 39.95
2021-06-03 15:00 | 44350.625 | 0 | 10.3444 | 39.95
2021-06-03 15:30 | 44350.6458 | 0 | 11.1519 | 39.95
2021-06-03 16:00 | 44350.6667 | 0 | 11.7651 | 39.95
2021-06-03 16:30 | 44350.6875 | 0 | 12.3564 | 39.95
2021-06-03 17:00 | 44350.7083 | 0 | 13.2585 | 39.95
2021-06-03 17:30 | 44350.7292 | 0 | 13.6175 | 39.95
2021-06-03 18:00 | 44350.75 | 0 | 13.482 | 39.95
2021-06-03 18:30 | 44350.7708 | 0 | 13.5247 | 39.95
2021-06-03 19:00 | 44350.7917 | 0 | 13.4466 | 39.95
2021-06-03 19:30 | 44350.8125 | 0 | 13.2201 | 39.95
2021-06-03 20:00 | 44350.8333 | 0 | 13.1516 | 39.95
2021-06-03 20:30 | 44350.8542 | 0 | 12.5678 | 39.95
2021-06-03 21:00 | 44350.875 | 0 | 12.1088 | 39.95
2021-06-03 21:30 | 44350.8958 | 0 | 11.7796 | 39.95
2021-06-03 22:00 | 44350.9167 | 0 | 11.0894 | 39.95
2021-06-03 22:30 | 44350.9375 | 0 | 10.3001 | 39.95
2021-06-03 23:00 | 44350.9583 | 0 | 9.5764 | 39.95
2021-06-03 23:30 | 44350.9792 | 0 | 9.122 | 39.95
2021-06-04 | 44351 | 0 | 8.562 | 39.95
2021-06-04 00:30 | 44351.0208 | 0 | 8.2303 | 39.95
2021-06-04 01:00 | 44351.0417 | 0 | 7.9272 | 39.95
2021-06-04 01:30 | 44351.0625 | 0 | 7.7531 | 39.95
2021-06-04 02:00 | 44351.0833 | 0 | 7.7099 | 39.95
2021-06-04 02:30 | 44351.1042 | 0 | 7.4923 | 39.95
2021-06-04 03:00 | 44351.125 | 0 | 7.4757 | 39.95
2021-06-04 03:30 | 44351.1458 | 0 | 7.4625 | 39.95
2021-06-04 04:00 | 44351.1667 | 0 | 7.6058 | 39.95
2021-06-04 04:30 | 44351.1875 | 0 | 7.6578 | 39.95
2021-06-04 05:00 | 44351.2083 | 0 | 7.9747 | 39.95
2021-06-04 05:30 | 44351.2292 | 0 | 8.1929 | 39.95
2021-06-04 06:00 | 44351.25 | 0 | 8.7853 | 39.95
2021-06-04 06:30 | 44351.2708 | 0 | 9.4649 | 39.95
2021-06-04 07:00 | 44351.2917 | 0 | 9.8626 | 39.95
2021-06-04 07:30 | 44351.3125 | 0 | 9.8587 | 39.95
2021-06-04 08:00 | 44351.3333 | 0 | 9.8438 | 39.95
2021-06-04 08:30 | 44351.3542 | 0 | 9.3323 | 39.95
2021-06-04 09:00 | 44351.375 | 0 | 8.6893 | 39.95
2021-06-04 09:30 | 44351.3958 | 0 | 8.1652 | 39.95
2021-06-04 10:00 | 44351.4167 | 0 | 7.6182 | 39.95
2021-06-04 10:30 | 44351.4375 | 0 | 7.2163 | 39.95
2021-06-04 11:00 | 44351.4583 | 0 | 6.7742 | 39.95
2021-06-04 11:30 | 44351.4792 | 0 | 6.507 | 39.95
2021-06-04 12:00 | 44351.5 | 0 | 6.3871 | 39.95
2021-06-04 12:30 | 44351.5208 | 0 | 6.4522 | 39.95
2021-06-04 13:00 | 44351.5417 | 0 | 6.5853 | 39.95
2021-06-04 13:30 | 44351.5625 | 0 | 6.8584 | 39.95
2021-06-04 14:00 | 44351.5833 | 0 | 7.2888 | 39.95
2021-06-04 14:30 | 44351.6042 | 0 | 7.8338 | 39.95
2021-06-04 15:00 | 44351.625 | 0 | 8.4339 | 39.95
2021-06-04 15:30 | 44351.6458 | 0 | 9.0668 | 39.95
2021-06-04 16:00 | 44351.6667 | 0 | 9.8536 | 39.95
2021-06-04 16:30 | 44351.6875 | 0 | 10.7127 | 39.95
2021-06-04 17:00 | 44351.7083 | 0 | 11.5698 | 39.95
2021-06-04 17:30 | 44351.7292 | 0 | 12.0741 | 39.95
2021-06-04 18:00 | 44351.75 | 0 | 12.2512 | 39.95
2021-06-04 18:30 | 44351.7708 | 0 | 12.2623 | 39.95
2021-06-04 19:00 | 44351.7917 | 0 | 12.0255 | 39.95
2021-06-04 19:30 | 44351.8125 | 0 | 11.6165 | 39.95
2021-06-04 20:00 | 44351.8333 | 0 | 11.3355 | 39.95
2021-06-04 20:30 | 44351.8542 | 0 | 10.8917 | 39.95
2021-06-04 21:00 | 44351.875 | 0 | 10.5607 | 39.95
2021-06-04 21:30 | 44351.8958 | 0 | 10.3738 | 39.95
2021-06-04 22:00 | 44351.9167 | 0 | 9.8799 | 39.95
2021-06-04 22:30 | 44351.9375 | 0 | 9.2273 | 39.95
2021-06-04 23:00 | 44351.9583 | 0 | 8.7826 | 39.95
2021-06-04 23:30 | 44351.9792 | 0 | 8.4182 | 39.95
2021-06-05 | 44352 | 0 | 8.0272 | 39.95
2021-06-05 00:30 | 44352.0208 | 0 | 7.5607 | 39.95
2021-06-05 01:00 | 44352.0417 | 0 | 7.3842 | 39.95
2021-06-05 01:30 | 44352.0625 | 0 | 7.2624 | 39.95
2021-06-05 02:00 | 44352.0833 | 0 | 7.2836 | 39.95
2021-06-05 02:30 | 44352.1042 | 0 | 7.0946 | 39.95
2021-06-05 03:00 | 44352.125 | 0 | 7.0878 | 39.95
2021-06-05 03:30 | 44352.1458 | 0 | 7.0628 | 39.95
2021-06-05 04:00 | 44352.1667 | 0 | 7.1141 | 39.95
2021-06-05 04:30 | 44352.1875 | 0 | 7.1184 | 39.95
2021-06-05 05:00 | 44352.2083 | 0 | 7.2833 | 39.95
2021-06-05 05:30 | 44352.2292 | 0 | 7.5465 | 39.95
2021-06-05 06:00 | 44352.25 | 0 | 7.9741 | 39.95
2021-06-05 06:30 | 44352.2708 | 0 | 8.5366 | 39.95
2021-06-05 07:00 | 44352.2917 | 0 | 8.9408 | 39.95
2021-06-05 07:30 | 44352.3125 | 0 | 9.2138 | 39.95
2021-06-05 08:00 | 44352.3333 | 0 | 9.0828 | 39.95
2021-06-05 08:30 | 44352.3542 | 0 | 8.7672 | 39.95
2021-06-05 09:00 | 44352.375 | 0 | 8.3941 | 39.95
2021-06-05 09:30 | 44352.3958 | 0 | 7.8399 | 39.95
2021-06-05 10:00 | 44352.4167 | 0 | 7.251 | 39.95
2021-06-05 10:30 | 44352.4375 | 0 | 6.764 | 39.95
2021-06-05 11:00 | 44352.4583 | 0 | 6.3934 | 39.95
2021-06-05 11:30 | 44352.4792 | 0 | 6.2002 | 39.95
2021-06-05 12:00 | 44352.5 | 0 | 6.0335 | 39.95
2021-06-05 12:30 | 44352.5208 | 0 | 6.0702 | 39.95
2021-06-05 13:00 | 44352.5417 | 0 | 6.2603 | 39.95
2021-06-05 13:30 | 44352.5625 | 0 | 6.5501 | 39.95
2021-06-05 14:00 | 44352.5833 | 0 | 7.0557 | 39.95
2021-06-05 14:30 | 44352.6042 | 0 | 7.5156 | 39.95
2021-06-05 15:00 | 44352.625 | 0 | 8.1423 | 39.95
2021-06-05 15:30 | 44352.6458 | 0 | 9.0486 | 39.95
2021-06-05 16:00 | 44352.6667 | 0 | 9.7944 | 39.95
2021-06-05 16:30 | 44352.6875 | 0 | 10.8652 | 39.95
2021-06-05 17:00 | 44352.7083 | 0 | 11.8807 | 39.95
2021-06-05 17:30 | 44352.7292 | 0 | 12.7895 | 39.95
2021-06-05 18:00 | 44352.75 | 0 | 12.8424 | 39.95
2021-06-05 18:30 | 44352.7708 | 0 | 12.6843 | 39.95
2021-06-05 19:00 | 44352.7917 | 0 | 12.6131 | 39.95
2021-06-05 19:30 | 44352.8125 | 0 | 12.3296 | 39.95
2021-06-05 20:00 | 44352.8333 | 0 | 12.0757 | 39.95
2021-06-05 20:30 | 44352.8542 | 0 | 11.5486 | 39.95
2021-06-05 21:00 | 44352.875 | 0 | 10.8625 | 39.95
2021-06-05 21:30 | 44352.8958 | 0 | 10.3571 | 39.95
2021-06-05 22:00 | 44352.9167 | 0 | 9.7525 | 39.95
2021-06-05 22:30 | 44352.9375 | 0 | 9.0735 | 39.95
2021-06-05 23:00 | 44352.9583 | 0 | 8.4182 | 39.95
2021-06-05 23:30 | 44352.9792 | 0 | 8.0592 | 39.95
2021-06-06 | 44353 | 0 | 7.7185 | 39.95
2021-06-06 00:30 | 44353.0208 | 0 | 7.5007 | 39.95
2021-06-06 01:00 | 44353.0417 | 0 | 7.3028 | 39.95
2021-06-06 01:30 | 44353.0625 | 0 | 7.2567 | 39.95
2021-06-06 02:00 | 44353.0833 | 0 | 7.2472 | 39.95
2021-06-06 02:30 | 44353.1042 | 0 | 7.3028 | 39.95
2021-06-06 03:00 | 44353.125 | 0 | 7.1977 | 39.95
2021-06-06 03:30 | 44353.1458 | 0 | 7.448 | 39.95
2021-06-06 04:00 | 44353.1667 | 0 | 7.7019 | 39.95
2021-06-06 04:30 | 44353.1875 | 0 | 8.1913 | 39.95
2021-06-06 05:00 | 44353.2083 | 0 | 9.0487 | 39.95
2021-06-06 05:30 | 44353.2292 | 0 | 9.9683 | 39.95
2021-06-06 06:00 | 44353.25 | 0 | 11.7621 | 39.95
2021-06-06 06:30 | 44353.2708 | 0 | 13.2819 | 39.95
2021-06-06 07:00 | 44353.2917 | 0 | 14.262 | 39.95
2021-06-06 07:30 | 44353.3125 | 0 | 13.9022 | 39.95
2021-06-06 08:00 | 44353.3333 | 0 | 12.9114 | 39.95
2021-06-06 08:30 | 44353.3542 | 0 | 12.254 | 39.95
2021-06-06 09:00 | 44353.375 | 0 | 11.5059 | 39.95
2021-06-06 09:30 | 44353.3958 | 0 | 10.5709 | 39.95
2021-06-06 10:00 | 44353.4167 | 0 | 9.7954 | 39.95
2021-06-06 10:30 | 44353.4375 | 0 | 9.3806 | 39.95
2021-06-06 11:00 | 44353.4583 | 0 | 9.2116 | 39.95
2021-06-06 11:30 | 44353.4792 | 0 | 9.1435 | 39.95
2021-06-06 12:00 | 44353.5 | 0 | 8.9395 | 39.95
2021-06-06 12:30 | 44353.5208 | 0 | 9.0926 | 39.95
2021-06-06 13:00 | 44353.5417 | 0 | 9.7309 | 39.95
2021-06-06 13:30 | 44353.5625 | 0 | 10.4646 | 39.95
2021-06-06 14:00 | 44353.5833 | 0 | 11.1909 | 39.95
2021-06-06 14:30 | 44353.6042 | 0 | 10.8285 | 39.95
2021-06-06 15:00 | 44353.625 | 0 | 10.5865 | 39.95
2021-06-06 15:30 | 44353.6458 | 0 | 11.4119 | 39.95
2021-06-06 16:00 | 44353.6667 | 0 | 11.9434 | 39.95
2021-06-06 16:30 | 44353.6875 | 0 | 12.7092 | 39.95
2021-06-06 17:00 | 44353.7083 | 0 | 13.7258 | 39.95
2021-06-06 17:30 | 44353.7292 | 0 | 14.5775 | 39.95
2021-06-06 18:00 | 44353.75 | 0 | 14.8727 | 39.95
2021-06-06 18:30 | 44353.7708 | 0 | 15.033 | 39.95
2021-06-06 19:00 | 44353.7917 | 0 | 14.6959 | 39.95
2021-06-06 19:30 | 44353.8125 | 0 | 14.4733 | 39.95
2021-06-06 20:00 | 44353.8333 | 0 | 14.0584 | 39.95
2021-06-06 20:30 | 44353.8542 | 0 | 13.4668 | 39.95
2021-06-06 21:00 | 44353.875 | 0 | 12.8306 | 39.95
2021-06-06 21:30 | 44353.8958 | 0 | 12.2672 | 39.95
2021-06-06 22:00 | 44353.9167 | 0 | 11.3464 | 39.95
2021-06-06 22:30 | 44353.9375 | 0 | 10.4867 | 39.95
2021-06-06 23:00 | 44353.9583 | 0 | 9.9468 | 39.95
2021-06-06 23:30 | 44353.9792 | 0 | 9.3875 | 39.95
2021-06-07 | 44354 | 0 | 8.7918 | 39.95
2021-06-07 00:30 | 44354.0208 | 0 | 8.3504 | 39.95
2021-06-07 01:00 | 44354.0417 | 0 | 8.1062 | 39.95
2021-06-07 01:30 | 44354.0625 | 0 | 7.959 | 39.95
2021-06-07 02:00 | 44354.0833 | 0 | 7.8992 | 39.95
2021-06-07 02:30 | 44354.1042 | 0 | 7.7282 | 39.95
2021-06-07 03:00 | 44354.125 | 0 | 7.7449 | 39.95
2021-06-07 03:30 | 44354.1458 | 0 | 7.9181 | 39.95
2021-06-07 04:00 | 44354.1667 | 0 | 8.2039 | 39.95
2021-06-07 04:30 | 44354.1875 | 0 | 8.7234 | 39.95
2021-06-07 05:00 | 44354.2083 | 0 | 9.6311 | 39.95
2021-06-07 05:30 | 44354.2292 | 0 | 10.6295 | 39.95
2021-06-07 06:00 | 44354.25 | 0 | 12.0029 | 39.95
2021-06-07 06:30 | 44354.2708 | 0 | 13.2191 | 39.95
2021-06-07 07:00 | 44354.2917 | 0 | 14.3605 | 39.95
2021-06-07 07:30 | 44354.3125 | 0 | 13.8831 | 39.95
2021-06-07 08:00 | 44354.3333 | 0 | 12.8823 | 39.95
2021-06-07 08:30 | 44354.3542 | 0 | 11.9536 | 39.95
2021-06-07 09:00 | 44354.375 | 0 | 10.8463 | 39.95
2021-06-07 09:30 | 44354.3958 | 0 | 10.0325 | 39.95
2021-06-07 10:00 | 44354.4167 | 0 | 10.3145 | 39.95
2021-06-07 10:30 | 44354.4375 | 0 | 10.752 | 39.95
2021-06-07 11:00 | 44354.4583 | 0 | 11.8011 | 39.95
2021-06-07 11:30 | 44354.4792 | 0 | 11.8162 | 39.95
2021-06-07 12:00 | 44354.5 | 0 | 11.788 | 39.95
2021-06-07 12:30 | 44354.5208 | 0 | 10.846 | 39.95
2021-06-07 13:00 | 44354.5417 | 0 | 11.1028 | 39.95
2021-06-07 13:30 | 44354.5625 | 0 | 10.9772 | 39.95
2021-06-07 14:00 | 44354.5833 | 0 | 11.3211 | 39.95
2021-06-07 14:30 | 44354.6042 | 0 | 11.9557 | 39.95
2021-06-07 15:00 | 44354.625 | 0 | 11.8638 | 39.95
2021-06-07 15:30 | 44354.6458 | 0 | 12.2121 | 39.95
2021-06-07 16:00 | 44354.6667 | 0 | 12.6439 | 39.95
2021-06-07 16:30 | 44354.6875 | 0 | 13.4257 | 39.95
2021-06-07 17:00 | 44354.7083 | 0 | 14.3958 | 39.95
2021-06-07 17:30 | 44354.7292 | 0 | 15.1131 | 39.95
2021-06-07 18:00 | 44354.75 | 0 | 15.1432 | 39.95
2021-06-07 18:30 | 44354.7708 | 0 | 15.0986 | 39.95
2021-06-07 19:00 | 44354.7917 | 0 | 14.7847 | 39.95
2021-06-07 19:30 | 44354.8125 | 0 | 14.5647 | 39.95
2021-06-07 20:00 | 44354.8333 | 0 | 14.1299 | 39.95
2021-06-07 20:30 | 44354.8542 | 0 | 13.702 | 39.95
2021-06-07 21:00 | 44354.875 | 0 | 12.8218 | 39.95
2021-06-07 21:30 | 44354.8958 | 0 | 12.246 | 39.95
2021-06-07 22:00 | 44354.9167 | 0 | 11.6752 | 39.95
2021-06-07 22:30 | 44354.9375 | 0 | 10.6643 | 39.95
2021-06-07 23:00 | 44354.9583 | 0 | 9.7945 | 39.95
2021-06-07 23:30 | 44354.9792 | 0 | 9.3961 | 39.95
2021-06-08 | 44355 | 0 | 8.7498 | 39.95
2021-06-08 00:30 | 44355.0208 | 0 | 8.2838 | 39.95
2021-06-08 01:00 | 44355.0417 | 0 | 8.0277 | 39.95
2021-06-08 01:30 | 44355.0625 | 0 | 8.0374 | 39.95
2021-06-08 02:00 | 44355.0833 | 0 | 7.9745 | 39.95
2021-06-08 02:30 | 44355.1042 | 0 | 7.8628 | 39.95
2021-06-08 03:00 | 44355.125 | 0 | 7.866 | 39.95
2021-06-08 03:30 | 44355.1458 | 0 | 8.0444 | 39.95
2021-06-08 04:00 | 44355.1667 | 0 | 8.3138 | 39.95
2021-06-08 04:30 | 44355.1875 | 0 | 8.7567 | 39.95
2021-06-08 05:00 | 44355.2083 | 0 | 9.4949 | 39.95
2021-06-08 05:30 | 44355.2292 | 0 | 10.3331 | 39.95
2021-06-08 06:00 | 44355.25 | 0 | 11.5463 | 39.95
2021-06-08 06:30 | 44355.2708 | 0 | 12.9873 | 39.95
2021-06-08 07:00 | 44355.2917 | 0 | 13.7005 | 39.95
2021-06-08 07:30 | 44355.3125 | 0 | 14.0642 | 39.95
2021-06-08 08:00 | 44355.3333 | 0 | 14.3472 | 39.95
2021-06-08 08:30 | 44355.3542 | 0 | 13.8953 | 39.95
2021-06-08 09:00 | 44355.375 | 0 | 12.2976 | 39.95
2021-06-08 09:30 | 44355.3958 | 0 | 12.6381 | 39.95
2021-06-08 10:00 | 44355.4167 | 0 | 13.0169 | 39.95
2021-06-08 10:30 | 44355.4375 | 0 | 11.746 | 39.95
2021-06-08 11:00 | 44355.4583 | 0 | 11.0699 | 39.95
2021-06-08 11:30 | 44355.4792 | 0 | 9.6079 | 39.95
2021-06-08 12:00 | 44355.5 | 0 | 11.2605 | 39.95
2021-06-08 12:30 | 44355.5208 | 0 | 11.8781 | 39.95
2021-06-08 13:00 | 44355.5417 | 0 | 10.0838 | 39.95
2021-06-08 13:30 | 44355.5625 | 0 | 9.644 | 39.95
2021-06-08 14:00 | 44355.5833 | 0 | 10.3053 | 39.95
2021-06-08 14:30 | 44355.6042 | 0 | 10.9526 | 39.95
2021-06-08 15:00 | 44355.625 | 0 | 11.047 | 39.95
2021-06-08 15:30 | 44355.6458 | 0 | 12.0478 | 39.95
2021-06-08 16:00 | 44355.6667 | 0 | 12.8734 | 39.95
2021-06-08 16:30 | 44355.6875 | 0 | 13.6968 | 39.95
2021-06-08 17:00 | 44355.7083 | 0 | 15.0955 | 39.95
2021-06-08 17:30 | 44355.7292 | 0 | 16.4197 | 39.95
2021-06-08 18:00 | 44355.75 | 0 | 16.9411 | 39.95
2021-06-08 18:30 | 44355.7708 | 0 | 17.4011 | 39.95
2021-06-08 19:00 | 44355.7917 | 0 | 17 | 39.95
2021-06-08 19:30 | 44355.8125 | 0 | 16.793 | 39.95
2021-06-08 20:00 | 44355.8333 | 0 | 16.3423 | 39.95
2021-06-08 20:30 | 44355.8542 | 0 | 15.3097 | 39.95
2021-06-08 21:00 | 44355.875 | 0 | 14.7251 | 39.95
2021-06-08 21:30 | 44355.8958 | 0 | 14.1036 | 39.95
2021-06-08 22:00 | 44355.9167 | 0 | 13.1451 | 39.95
2021-06-08 22:30 | 44355.9375 | 0 | 11.8628 | 39.95
2021-06-08 23:00 | 44355.9583 | 0 | 11.0327 | 39.95
2021-06-08 23:30 | 44355.9792 | 0 | 10.1908 | 39.95
2021-06-09 | 44356 | 0 | 9.4175 | 39.95
2021-06-09 00:30 | 44356.0208 | 0 | 8.9637 | 39.95
2021-06-09 01:00 | 44356.0417 | 0 | 8.814 | 39.95
2021-06-09 01:30 | 44356.0625 | 0 | 8.5425 | 39.95
2021-06-09 02:00 | 44356.0833 | 0 | 8.4921 | 39.95
2021-06-09 02:30 | 44356.1042 | 0 | 8.363 | 39.95
2021-06-09 03:00 | 44356.125 | 0 | 8.2822 | 39.95
2021-06-09 03:30 | 44356.1458 | 0 | 8.5015 | 39.95
2021-06-09 04:00 | 44356.1667 | 0 | 8.7087 | 39.95
2021-06-09 04:30 | 44356.1875 | 0 | 9.2839 | 39.95
2021-06-09 05:00 | 44356.2083 | 0 | 10.3419 | 39.95
2021-06-09 05:30 | 44356.2292 | 0 | 11.4531 | 39.95
2021-06-09 06:00 | 44356.25 | 0 | 13.1029 | 39.95
2021-06-09 06:30 | 44356.2708 | 0 | 14.8129 | 39.95
2021-06-09 07:00 | 44356.2917 | 0 | 15.8076 | 39.95
2021-06-09 07:30 | 44356.3125 | 0 | 15.2252 | 39.95
2021-06-09 08:00 | 44356.3333 | 0 | 14.0189 | 39.95
2021-06-09 08:30 | 44356.3542 | 0 | 12.754 | 39.95
2021-06-09 09:00 | 44356.375 | 0 | 11.8934 | 39.95
2021-06-09 09:30 | 44356.3958 | 0 | 11.1491 | 39.95
2021-06-09 10:00 | 44356.4167 | 0 | 10.3982 | 39.95
2021-06-09 10:30 | 44356.4375 | 0 | 9.7974 | 39.95
2021-06-09 11:00 | 44356.4583 | 0 | 9.2817 | 39.95
2021-06-09 11:30 | 44356.4792 | 0 | 9.0263 | 39.95
2021-06-09 12:00 | 44356.5 | 0 | 8.8958 | 39.95
2021-06-09 12:30 | 44356.5208 | 0 | 8.9371 | 39.95
2021-06-09 13:00 | 44356.5417 | 0 | 9.198 | 39.95
2021-06-09 13:30 | 44356.5625 | 0 | 9.5725 | 39.95
2021-06-09 14:00 | 44356.5833 | 0 | 9.9044 | 39.95
2021-06-09 14:30 | 44356.6042 | 0 | 10.5116 | 39.95
2021-06-09 15:00 | 44356.625 | 0 | 11.2556 | 39.95
2021-06-09 15:30 | 44356.6458 | 0 | 12.2162 | 39.95
2021-06-09 16:00 | 44356.6667 | 0 | 12.9996 | 39.95
2021-06-09 16:30 | 44356.6875 | 0 | 14.1687 | 39.95
2021-06-09 17:00 | 44356.7083 | 0 | 15.3816 | 39.95
2021-06-09 17:30 | 44356.7292 | 0 | 16.5213 | 39.95
2021-06-09 18:00 | 44356.75 | 0 | 16.651 | 39.95
2021-06-09 18:30 | 44356.7708 | 0 | 17.1105 | 39.95
2021-06-09 19:00 | 44356.7917 | 0 | 16.8297 | 39.95
2021-06-09 19:30 | 44356.8125 | 0 | 16.8121 | 39.95
2021-06-09 20:00 | 44356.8333 | 0 | 16.534 | 39.95
2021-06-09 20:30 | 44356.8542 | 0 | 15.857 | 39.95
2021-06-09 21:00 | 44356.875 | 0 | 14.9552 | 39.95
2021-06-09 21:30 | 44356.8958 | 0 | 14.167 | 39.95
2021-06-09 22:00 | 44356.9167 | 0 | 13.1732 | 39.95
2021-06-09 22:30 | 44356.9375 | 0 | 12.0092 | 39.95
2021-06-09 23:00 | 44356.9583 | 0 | 11.0716 | 39.95
2021-06-09 23:30 | 44356.9792 | 0 | 10.2785 | 39.95
2021-06-10 | 44357 | 0 | 9.5449 | 39.95
2021-06-10 00:30 | 44357.0208 | 0 | 9.0883 | 39.95
2021-06-10 01:00 | 44357.0417 | 0 | 8.8555 | 39.95
2021-06-10 01:30 | 44357.0625 | 0 | 8.5937 | 39.95
2021-06-10 02:00 | 44357.0833 | 0 | 8.6127 | 39.95
2021-06-10 02:30 | 44357.1042 | 0 | 8.4964 | 39.95
2021-06-10 03:00 | 44357.125 | 0 | 8.3956 | 39.95
2021-06-10 03:30 | 44357.1458 | 0 | 8.5835 | 39.95
2021-06-10 04:00 | 44357.1667 | 0 | 8.8758 | 39.95
2021-06-10 04:30 | 44357.1875 | 0 | 9.4174 | 39.95
2021-06-10 05:00 | 44357.2083 | 0 | 10.3048 | 39.95
2021-06-10 05:30 | 44357.2292 | 0 | 11.3845 | 39.95
2021-06-10 06:00 | 44357.25 | 0 | 13.0949 | 39.95
2021-06-10 06:30 | 44357.2708 | 0 | 14.8524 | 39.95
2021-06-10 07:00 | 44357.2917 | 0 | 15.9166 | 39.95
2021-06-10 07:30 | 44357.3125 | 0 | 15.3091 | 39.95
2021-06-10 08:00 | 44357.3333 | 0 | 14.3215 | 39.95
2021-06-10 08:30 | 44357.3542 | 0 | 14.1005 | 39.95
2021-06-10 09:00 | 44357.375 | 0 | 12.1656 | 39.95
2021-06-10 09:30 | 44357.3958 | 0 | 11.9182 | 39.95
2021-06-10 10:00 | 44357.4167 | 0 | 10.8384 | 39.95
2021-06-10 10:30 | 44357.4375 | 0 | 10.5941 | 39.95
2021-06-10 11:00 | 44357.4583 | 0 | 10.4416 | 39.95
2021-06-10 11:30 | 44357.4792 | 0 | 9.737 | 39.95
2021-06-10 12:00 | 44357.5 | 0 | 9.3106 | 39.95
2021-06-10 12:30 | 44357.5208 | 0 | 9.3775 | 39.95
2021-06-10 13:00 | 44357.5417 | 0 | 9.6706 | 39.95
2021-06-10 13:30 | 44357.5625 | 0 | 9.3042 | 39.95
2021-06-10 14:00 | 44357.5833 | 0 | 10.6574 | 39.95
2021-06-10 14:30 | 44357.6042 | 0 | 10.7568 | 39.95
2021-06-10 15:00 | 44357.625 | 0 | 11.3081 | 39.95
2021-06-10 15:30 | 44357.6458 | 0 | 12.1553 | 39.95
2021-06-10 16:00 | 44357.6667 | 0 | 12.2467 | 39.95
2021-06-10 16:30 | 44357.6875 | 0 | 13.4792 | 39.95
2021-06-10 17:00 | 44357.7083 | 0 | 14.7459 | 39.95
2021-06-10 17:30 | 44357.7292 | 0 | 15.4467 | 39.95
2021-06-10 18:00 | 44357.75 | 0 | 15.7311 | 39.95
2021-06-10 18:30 | 44357.7708 | 0 | 15.9813 | 39.95
2021-06-10 19:00 | 44357.7917 | 0 | 15.7219 | 39.95
2021-06-10 19:30 | 44357.8125 | 0 | 15.541 | 39.95
2021-06-10 20:00 | 44357.8333 | 0 | 15.1984 | 39.95
2021-06-10 20:30 | 44357.8542 | 0 | 14.6854 | 39.95
2021-06-10 21:00 | 44357.875 | 0 | 14.225 | 39.95
2021-06-10 21:30 | 44357.8958 | 0 | 13.5917 | 39.95
2021-06-10 22:00 | 44357.9167 | 0 | 12.9079 | 39.95
2021-06-10 22:30 | 44357.9375 | 0 | 11.794 | 39.95
2021-06-10 23:00 | 44357.9583 | 0 | 10.8821 | 39.95
2021-06-10 23:30 | 44357.9792 | 0 | 10.3148 | 39.95
2021-06-11 | 44358 | 0 | 9.5617 | 39.95
2021-06-11 00:30 | 44358.0208 | 0 | 9.0896 | 39.95
2021-06-11 01:00 | 44358.0417 | 0 | 8.779 | 39.95
2021-06-11 01:30 | 44358.0625 | 0 | 8.4549 | 39.95
2021-06-11 02:00 | 44358.0833 | 0 | 8.4226 | 39.95
2021-06-11 02:30 | 44358.1042 | 0 | 8.3137 | 39.95
2021-06-11 03:00 | 44358.125 | 0 | 8.2524 | 39.95
2021-06-11 03:30 | 44358.1458 | 0 | 8.4083 | 39.95
2021-06-11 04:00 | 44358.1667 | 0 | 8.4269 | 39.95
2021-06-11 04:30 | 44358.1875 | 0 | 8.5193 | 39.95
2021-06-11 05:00 | 44358.2083 | 0 | 9.0951 | 39.95
2021-06-11 05:30 | 44358.2292 | 0 | 9.4432 | 39.95
2021-06-11 06:00 | 44358.25 | 0 | 10.3809 | 39.95
2021-06-11 06:30 | 44358.2708 | 0 | 11.1416 | 39.95
2021-06-11 07:00 | 44358.2917 | 0 | 11.8951 | 39.95
2021-06-11 07:30 | 44358.3125 | 0 | 11.9878 | 39.95
2021-06-11 08:00 | 44358.3333 | 0 | 11.8583 | 39.95
2021-06-11 08:30 | 44358.3542 | 0 | 11.1724 | 39.95
2021-06-11 09:00 | 44358.375 | 0 | 10.411 | 39.95
2021-06-11 09:30 | 44358.3958 | 0 | 9.6344 | 39.95
2021-06-11 10:00 | 44358.4167 | 0 | 8.6828 | 39.95
2021-06-11 10:30 | 44358.4375 | 0 | 8.1028 | 39.95
2021-06-11 11:00 | 44358.4583 | 0 | 7.4696 | 39.95
2021-06-11 11:30 | 44358.4792 | 0 | 7.1435 | 39.95
2021-06-11 12:00 | 44358.5 | 0 | 6.8216 | 39.95
2021-06-11 12:30 | 44358.5208 | 0 | 6.8315 | 39.95
2021-06-11 13:00 | 44358.5417 | 0 | 6.7923 | 39.95
2021-06-11 13:30 | 44358.5625 | 0 | 7.1087 | 39.95
2021-06-11 14:00 | 44358.5833 | 0 | 7.6517 | 39.95
2021-06-11 14:30 | 44358.6042 | 0 | 7.9732 | 39.95
2021-06-11 15:00 | 44358.625 | 0 | 8.7224 | 39.95
2021-06-11 15:30 | 44358.6458 | 0 | 9.5228 | 39.95
2021-06-11 16:00 | 44358.6667 | 0 | 10.1108 | 39.95
2021-06-11 16:30 | 44358.6875 | 0 | 11.0094 | 39.95
2021-06-11 17:00 | 44358.7083 | 0 | 12.0687 | 39.95
2021-06-11 17:30 | 44358.7292 | 0 | 12.5929 | 39.95
2021-06-11 18:00 | 44358.75 | 0 | 12.8493 | 39.95
2021-06-11 18:30 | 44358.7708 | 0 | 12.7834 | 39.95
2021-06-11 19:00 | 44358.7917 | 0 | 12.6985 | 39.95
2021-06-11 19:30 | 44358.8125 | 0 | 12.5369 | 39.95
2021-06-11 20:00 | 44358.8333 | 0 | 12.2436 | 39.95
2021-06-11 20:30 | 44358.8542 | 0 | 11.8391 | 39.95
2021-06-11 21:00 | 44358.875 | 0 | 11.3208 | 39.95
2021-06-11 21:30 | 44358.8958 | 0 | 10.9888 | 39.95
2021-06-11 22:00 | 44358.9167 | 0 | 10.4419 | 39.95
2021-06-11 22:30 | 44358.9375 | 0 | 9.7258 | 39.95
2021-06-11 23:00 | 44358.9583 | 0 | 9.2287 | 39.95
2021-06-11 23:30 | 44358.9792 | 0 | 8.7455 | 39.95
2021-06-12 | 44359 | 0 | 8.3097 | 39.95
2021-06-12 00:30 | 44359.0208 | 0 | 7.9437 | 39.95
2021-06-12 01:00 | 44359.0417 | 0 | 7.758 | 39.95
2021-06-12 01:30 | 44359.0625 | 0 | 7.4983 | 39.95
2021-06-12 02:00 | 44359.0833 | 0 | 7.4144 | 39.95
2021-06-12 02:30 | 44359.1042 | 0 | 7.3987 | 39.95
2021-06-12 03:00 | 44359.125 | 0 | 7.3583 | 39.95
2021-06-12 03:30 | 44359.1458 | 0 | 7.3168 | 39.95
2021-06-12 04:00 | 44359.1667 | 0 | 7.3409 | 39.95
2021-06-12 04:30 | 44359.1875 | 0 | 7.283 | 39.95
2021-06-12 05:00 | 44359.2083 | 0 | 7.6034 | 39.95
2021-06-12 05:30 | 44359.2292 | 0 | 7.9193 | 39.95
2021-06-12 06:00 | 44359.25 | 0 | 8.4343 | 39.95
2021-06-12 06:30 | 44359.2708 | 0 | 9.0253 | 39.95
2021-06-12 07:00 | 44359.2917 | 0 | 9.609 | 39.95
2021-06-12 07:30 | 44359.3125 | 0 | 9.7868 | 39.95
2021-06-12 08:00 | 44359.3333 | 0 | 9.8459 | 39.95
2021-06-12 08:30 | 44359.3542 | 0 | 9.4484 | 39.95
2021-06-12 09:00 | 44359.375 | 0 | 9.5133 | 39.95
2021-06-12 09:30 | 44359.3958 | 0 | 8.6753 | 39.95
2021-06-12 10:00 | 44359.4167 | 0 | 7.8865 | 39.95
2021-06-12 10:30 | 44359.4375 | 0 | 7.653 | 39.95
2021-06-12 11:00 | 44359.4583 | 0 | 6.9698 | 39.95
2021-06-12 11:30 | 44359.4792 | 0 | 6.6035 | 39.95
2021-06-12 12:00 | 44359.5 | 0 | 6.2508 | 39.95
2021-06-12 12:30 | 44359.5208 | 0 | 6.1655 | 39.95
2021-06-12 13:00 | 44359.5417 | 0 | 6.3139 | 39.95
2021-06-12 13:30 | 44359.5625 | 0 | 6.5498 | 39.95
2021-06-12 14:00 | 44359.5833 | 0 | 7.1454 | 39.95
2021-06-12 14:30 | 44359.6042 | 0 | 7.6456 | 39.95
2021-06-12 15:00 | 44359.625 | 0 | 8.2989 | 39.95
2021-06-12 15:30 | 44359.6458 | 0 | 9.1366 | 39.95
2021-06-12 16:00 | 44359.6667 | 0 | 10.0519 | 39.95
2021-06-12 16:30 | 44359.6875 | 0 | 11.0801 | 39.95
2021-06-12 17:00 | 44359.7083 | 0 | 12.2678 | 39.95
2021-06-12 17:30 | 44359.7292 | 0 | 12.9738 | 39.95
2021-06-12 18:00 | 44359.75 | 0 | 13.2235 | 39.95
2021-06-12 18:30 | 44359.7708 | 0 | 13.32 | 39.95
2021-06-12 19:00 | 44359.7917 | 0 | 12.9494 | 39.95
2021-06-12 19:30 | 44359.8125 | 0 | 12.6886 | 39.95
2021-06-12 20:00 | 44359.8333 | 0 | 12.4839 | 39.95
2021-06-12 20:30 | 44359.8542 | 0 | 11.9119 | 39.95
2021-06-12 21:00 | 44359.875 | 0 | 11.4422 | 39.95
2021-06-12 21:30 | 44359.8958 | 0 | 10.9527 | 39.95
2021-06-12 22:00 | 44359.9167 | 0 | 10.3027 | 39.95
2021-06-12 22:30 | 44359.9375 | 0 | 9.4358 | 39.95
2021-06-12 23:00 | 44359.9583 | 0 | 8.6763 | 39.95
2021-06-12 23:30 | 44359.9792 | 0 | 8.3008 | 39.95
2021-06-13 | 44360 | 0 | 7.9853 | 39.95
2021-06-13 00:30 | 44360.0208 | 0 | 7.7445 | 39.95
2021-06-13 01:00 | 44360.0417 | 0 | 7.533 | 39.95
2021-06-13 01:30 | 44360.0625 | 0 | 7.3798 | 39.95
2021-06-13 02:00 | 44360.0833 | 0 | 7.4451 | 39.95
2021-06-13 02:30 | 44360.1042 | 0 | 7.3385 | 39.95
2021-06-13 03:00 | 44360.125 | 0 | 7.3019 | 39.95
2021-06-13 03:30 | 44360.1458 | 0 | 7.6585 | 39.95
2021-06-13 04:00 | 44360.1667 | 0 | 7.9287 | 39.95
2021-06-13 04:30 | 44360.1875 | 0 | 8.4416 | 39.95
2021-06-13 05:00 | 44360.2083 | 0 | 9.3424 | 39.95
2021-06-13 05:30 | 44360.2292 | 0 | 10.4915 | 39.95
2021-06-13 06:00 | 44360.25 | 0 | 12.4276 | 39.95
2021-06-13 06:30 | 44360.2708 | 0 | 13.9688 | 39.95
2021-06-13 07:00 | 44360.2917 | 0 | 15.3398 | 39.95
2021-06-13 07:30 | 44360.3125 | 0 | 15.4339 | 39.95
2021-06-13 08:00 | 44360.3333 | 0 | 14.969 | 39.95
2021-06-13 08:30 | 44360.3542 | 0 | 13.5115 | 39.95
2021-06-13 09:00 | 44360.375 | 0 | 12.526 | 39.95
2021-06-13 09:30 | 44360.3958 | 0 | 11.4587 | 39.95
2021-06-13 10:00 | 44360.4167 | 0 | 10.5345 | 39.95
2021-06-13 10:30 | 44360.4375 | 0 | 10.0257 | 39.95
2021-06-13 11:00 | 44360.4583 | 0 | 9.5414 | 39.95
2021-06-13 11:30 | 44360.4792 | 0 | 9.3914 | 39.95
2021-06-13 12:00 | 44360.5 | 0 | 9.2739 | 39.95
2021-06-13 12:30 | 44360.5208 | 0 | 9.2878 | 39.95
2021-06-13 13:00 | 44360.5417 | 0 | 9.3465 | 39.95
2021-06-13 13:30 | 44360.5625 | 0 | 9.5649 | 39.95
2021-06-13 14:00 | 44360.5833 | 0 | 9.9114 | 39.95
2021-06-13 14:30 | 44360.6042 | 0 | 10.1822 | 39.95
2021-06-13 15:00 | 44360.625 | 0 | 10.5795 | 39.95
2021-06-13 15:30 | 44360.6458 | 0 | 11.2678 | 39.95
2021-06-13 16:00 | 44360.6667 | 0 | 11.9386 | 39.95
2021-06-13 16:30 | 44360.6875 | 0 | 12.763 | 39.95
2021-06-13 17:00 | 44360.7083 | 0 | 13.9925 | 39.95
2021-06-13 17:30 | 44360.7292 | 0 | 14.9801 | 39.95
2021-06-13 18:00 | 44360.75 | 0 | 15.356 | 39.95
2021-06-13 18:30 | 44360.7708 | 0 | 15.4714 | 39.95
2021-06-13 19:00 | 44360.7917 | 0 | 15.065 | 39.95
2021-06-13 19:30 | 44360.8125 | 0 | 15.0409 | 39.95
2021-06-13 20:00 | 44360.8333 | 0 | 14.4197 | 39.95
2021-06-13 20:30 | 44360.8542 | 0 | 13.941 | 39.95
2021-06-13 21:00 | 44360.875 | 0 | 13.276 | 39.95
2021-06-13 21:30 | 44360.8958 | 0 | 12.591 | 39.95
2021-06-13 22:00 | 44360.9167 | 0 | 11.7523 | 39.95
2021-06-13 22:30 | 44360.9375 | 0 | 10.7142 | 39.95
2021-06-13 23:00 | 44360.9583 | 0 | 10.1125 | 39.95
2021-06-13 23:30 | 44360.9792 | 0 | 9.6683 | 39.95
2021-06-14 | 44361 | 0 | 9.0665 | 39.95
2021-06-14 00:30 | 44361.0208 | 0 | 8.5071 | 39.95
2021-06-14 01:00 | 44361.0417 | 0 | 8.3237 | 39.95
2021-06-14 01:30 | 44361.0625 | 0 | 8.1912 | 39.95
2021-06-14 02:00 | 44361.0833 | 0 | 7.9975 | 39.95
2021-06-14 02:30 | 44361.1042 | 0 | 8.0119 | 39.95
2021-06-14 03:00 | 44361.125 | 0 | 7.9742 | 39.95
2021-06-14 03:30 | 44361.1458 | 0 | 8.0718 | 39.95
2021-06-14 04:00 | 44361.1667 | 0 | 8.3313 | 39.95
2021-06-14 04:30 | 44361.1875 | 0 | 8.9197 | 39.95
2021-06-14 05:00 | 44361.2083 | 0 | 9.7438 | 39.95
2021-06-14 05:30 | 44361.2292 | 0 | 10.7069 | 39.95
2021-06-14 06:00 | 44361.25 | 0 | 12.1127 | 39.95
2021-06-14 06:30 | 44361.2708 | 0 | 13.6458 | 39.95
2021-06-14 07:00 | 44361.2917 | 0 | 14.7835 | 39.95
2021-06-14 07:30 | 44361.3125 | 0 | 14.1711 | 39.95
2021-06-14 08:00 | 44361.3333 | 0 | 13.2114 | 39.95
2021-06-14 08:30 | 44361.3542 | 0 | 12.8195 | 39.95
2021-06-14 09:00 | 44361.375 | 0 | 13.7068 | 39.95
2021-06-14 09:30 | 44361.3958 | 0 | 15.109 | 39.95
2021-06-14 10:00 | 44361.4167 | 0 | 14.878 | 39.95
2021-06-14 10:30 | 44361.4375 | 0 | 13.9792 | 39.95
2021-06-14 11:00 | 44361.4583 | 0 | 11.9281 | 39.95
2021-06-14 11:30 | 44361.4792 | 0 | 9.7119 | 39.95
2021-06-14 12:00 | 44361.5 | 0 | 9.4819 | 39.95
2021-06-14 12:30 | 44361.5208 | 0 | 9.2217 | 39.95
2021-06-14 13:00 | 44361.5417 | 0 | 9.3067 | 39.95
2021-06-14 13:30 | 44361.5625 | 0 | 9.644 | 39.95
2021-06-14 14:00 | 44361.5833 | 0 | 10.9622 | 39.95
2021-06-14 14:30 | 44361.6042 | 0 | 10.9023 | 39.95
2021-06-14 15:00 | 44361.625 | 0 | 11.2779 | 39.95
2021-06-14 15:30 | 44361.6458 | 0 | 12.1885 | 39.95
2021-06-14 16:00 | 44361.6667 | 0 | 12.5587 | 39.95
2021-06-14 16:30 | 44361.6875 | 0 | 12.9517 | 39.95
2021-06-14 17:00 | 44361.7083 | 0 | 13.9919 | 39.95
2021-06-14 17:30 | 44361.7292 | 0 | 14.8004 | 39.95
2021-06-14 18:00 | 44361.75 | 0 | 14.9895 | 39.95
2021-06-14 18:30 | 44361.7708 | 0 | 15.1221 | 39.95
2021-06-14 19:00 | 44361.7917 | 0 | 15.0004 | 39.95
2021-06-14 19:30 | 44361.8125 | 0 | 14.8166 | 39.95
2021-06-14 20:00 | 44361.8333 | 0 | 14.6756 | 39.95
2021-06-14 20:30 | 44361.8542 | 0 | 14.1668 | 39.95
2021-06-14 21:00 | 44361.875 | 0 | 13.4266 | 39.95
2021-06-14 21:30 | 44361.8958 | 0 | 12.7596 | 39.95
2021-06-14 22:00 | 44361.9167 | 0 | 12.0341 | 39.95
2021-06-14 22:30 | 44361.9375 | 0 | 10.9594 | 39.95
2021-06-14 23:00 | 44361.9583 | 0 | 10.2963 | 39.95
2021-06-14 23:30 | 44361.9792 | 0 | 9.6672 | 39.95
2021-06-15 | 44362 | 0 | 9.1231 | 39.95
2021-06-15 00:30 | 44362.0208 | 0 | 8.6019 | 39.95
2021-06-15 01:00 | 44362.0417 | 0 | 8.3773 | 39.95
2021-06-15 01:30 | 44362.0625 | 0 | 8.2265 | 39.95
2021-06-15 02:00 | 44362.0833 | 0 | 8.0887 | 39.95
2021-06-15 02:30 | 44362.1042 | 0 | 8.0183 | 39.95
2021-06-15 03:00 | 44362.125 | 0 | 7.9556 | 39.95
2021-06-15 03:30 | 44362.1458 | 0 | 8.1666 | 39.95
2021-06-15 04:00 | 44362.1667 | 0 | 8.4251 | 39.95
2021-06-15 04:30 | 44362.1875 | 0 | 8.8706 | 39.95
2021-06-15 05:00 | 44362.2083 | 0 | 9.7298 | 39.95
2021-06-15 05:30 | 44362.2292 | 0 | 10.7582 | 39.95
2021-06-15 06:00 | 44362.25 | 0 | 12.2034 | 39.95
2021-06-15 06:30 | 44362.2708 | 0 | 13.7695 | 39.95
2021-06-15 07:00 | 44362.2917 | 0 | 14.5667 | 39.95
2021-06-15 07:30 | 44362.3125 | 0 | 14.6505 | 39.95
2021-06-15 08:00 | 44362.3333 | 0 | 14.2428 | 39.95
2021-06-15 08:30 | 44362.3542 | 0 | 13.586 | 39.95
2021-06-15 09:00 | 44362.375 | 0 | 11.9301 | 39.95
2021-06-15 09:30 | 44362.3958 | 0 | 10.8911 | 39.95
2021-06-15 10:00 | 44362.4167 | 0 | 10.3275 | 39.95
2021-06-15 10:30 | 44362.4375 | 0 | 9.9077 | 39.95
2021-06-15 11:00 | 44362.4583 | 0 | 9.4844 | 39.95
2021-06-15 11:30 | 44362.4792 | 0 | 9.3963 | 39.95
2021-06-15 12:00 | 44362.5 | 0 | 9.242 | 39.95
2021-06-15 12:30 | 44362.5208 | 0 | 9.0902 | 39.95
2021-06-15 13:00 | 44362.5417 | 0 | 9.3033 | 39.95
2021-06-15 13:30 | 44362.5625 | 0 | 9.9316 | 39.95
2021-06-15 14:00 | 44362.5833 | 0 | 10.2705 | 39.95
2021-06-15 14:30 | 44362.6042 | 0 | 10.8277 | 39.95
2021-06-15 15:00 | 44362.625 | 0 | 10.9487 | 39.95
2021-06-15 15:30 | 44362.6458 | 0 | 11.8301 | 39.95
2021-06-15 16:00 | 44362.6667 | 0 | 12.2142 | 39.95
2021-06-15 16:30 | 44362.6875 | 0 | 13.0105 | 39.95
2021-06-15 17:00 | 44362.7083 | 0 | 13.8875 | 39.95
2021-06-15 17:30 | 44362.7292 | 0 | 14.3657 | 39.95
2021-06-15 18:00 | 44362.75 | 0 | 14.4518 | 39.95
2021-06-15 18:30 | 44362.7708 | 0 | 14.7344 | 39.95
2021-06-15 19:00 | 44362.7917 | 0 | 14.6064 | 39.95
2021-06-15 19:30 | 44362.8125 | 0 | 14.5156 | 39.95
2021-06-15 20:00 | 44362.8333 | 0 | 14.162 | 39.95
2021-06-15 20:30 | 44362.8542 | 0 | 13.6618 | 39.95
2021-06-15 21:00 | 44362.875 | 0 | 13.0699 | 39.95
2021-06-15 21:30 | 44362.8958 | 0 | 12.3376 | 39.95
2021-06-15 22:00 | 44362.9167 | 0 | 11.6188 | 39.95
2021-06-15 22:30 | 44362.9375 | 0 | 10.773 | 39.95
2021-06-15 23:00 | 44362.9583 | 0 | 10.027 | 39.95
2021-06-15 23:30 | 44362.9792 | 0 | 9.6348 | 39.95
2021-06-16 | 44363 | 0 | 8.8989 | 39.95
2021-06-16 00:30 | 44363.0208 | 0 | 8.6023 | 39.95
2021-06-16 01:00 | 44363.0417 | 0 | 8.3908 | 39.95
2021-06-16 01:30 | 44363.0625 | 0 | 8.2271 | 39.95
2021-06-16 02:00 | 44363.0833 | 0 | 8.0606 | 39.95
2021-06-16 02:30 | 44363.1042 | 0 | 7.8928 | 39.95
2021-06-16 03:00 | 44363.125 | 0 | 7.8883 | 39.95
2021-06-16 03:30 | 44363.1458 | 0 | 8.0475 | 39.95
2021-06-16 04:00 | 44363.1667 | 0 | 8.2537 | 39.95
2021-06-16 04:30 | 44363.1875 | 0 | 8.7075 | 39.95
2021-06-16 05:00 | 44363.2083 | 0 | 9.4475 | 39.95
2021-06-16 05:30 | 44363.2292 | 0 | 10.3423 | 39.95
2021-06-16 06:00 | 44363.25 | 0 | 11.5269 | 39.95
2021-06-16 06:30 | 44363.2708 | 0 | 12.6572 | 39.95
2021-06-16 07:00 | 44363.2917 | 0 | 13.1631 | 39.95
2021-06-16 07:30 | 44363.3125 | 0 | 13.0243 | 39.95
2021-06-16 08:00 | 44363.3333 | 0 | 12.43 | 39.95
2021-06-16 08:30 | 44363.3542 | 0 | 11.515 | 39.95
2021-06-16 09:00 | 44363.375 | 0 | 10.7419 | 39.95
2021-06-16 09:30 | 44363.3958 | 0 | 10.1906 | 39.95
2021-06-16 10:00 | 44363.4167 | 0 | 9.6085 | 39.95
2021-06-16 10:30 | 44363.4375 | 0 | 9.3599 | 39.95
2021-06-16 11:00 | 44363.4583 | 0 | 9.0258 | 39.95
2021-06-16 11:30 | 44363.4792 | 0 | 9.0058 | 39.95
2021-06-16 12:00 | 44363.5 | 0 | 8.6553 | 39.95
2021-06-16 12:30 | 44363.5208 | 0 | 8.8956 | 39.95
2021-06-16 13:00 | 44363.5417 | 0 | 8.9677 | 39.95
2021-06-16 13:30 | 44363.5625 | 0 | 9.2618 | 39.95
2021-06-16 14:00 | 44363.5833 | 0 | 9.5661 | 39.95
2021-06-16 14:30 | 44363.6042 | 0 | 10.1372 | 39.95
2021-06-16 15:00 | 44363.625 | 0 | 10.6304 | 39.95
2021-06-16 15:30 | 44363.6458 | 0 | 11.4058 | 39.95
2021-06-16 16:00 | 44363.6667 | 0 | 11.9151 | 39.95
2021-06-16 16:30 | 44363.6875 | 0 | 12.6278 | 39.95
2021-06-16 17:00 | 44363.7083 | 0 | 13.3501 | 39.95
2021-06-16 17:30 | 44363.7292 | 0 | 13.9609 | 39.95
2021-06-16 18:00 | 44363.75 | 0 | 13.9785 | 39.95
2021-06-16 18:30 | 44363.7708 | 0 | 14.2949 | 39.95
2021-06-16 19:00 | 44363.7917 | 0 | 13.7363 | 39.95
2021-06-16 19:30 | 44363.8125 | 0 | 13.8666 | 39.95
2021-06-16 20:00 | 44363.8333 | 0 | 13.6815 | 39.95
2021-06-16 20:30 | 44363.8542 | 0 | 13.1505 | 39.95
2021-06-16 21:00 | 44363.875 | 0 | 12.6963 | 39.95
2021-06-16 21:30 | 44363.8958 | 0 | 12.185 | 39.95
2021-06-16 22:00 | 44363.9167 | 0 | 11.5204 | 39.95
2021-06-16 22:30 | 44363.9375 | 0 | 10.5662 | 39.95
2021-06-16 23:00 | 44363.9583 | 0 | 9.9886 | 39.95
2021-06-16 23:30 | 44363.9792 | 0 | 9.5182 | 39.95
2021-06-17 | 44364 | 0 | 8.8687 | 39.95
2021-06-17 00:30 | 44364.0208 | 0 | 8.5434 | 39.95
2021-06-17 01:00 | 44364.0417 | 0 | 8.2396 | 39.95
2021-06-17 01:30 | 44364.0625 | 0 | 8.0672 | 39.95
2021-06-17 02:00 | 44364.0833 | 0 | 8.0595 | 39.95
2021-06-17 02:30 | 44364.1042 | 0 | 7.9034 | 39.95
2021-06-17 03:00 | 44364.125 | 0 | 7.8917 | 39.95
2021-06-17 03:30 | 44364.1458 | 0 | 8.0378 | 39.95
2021-06-17 04:00 | 44364.1667 | 0 | 8.3081 | 39.95
2021-06-17 04:30 | 44364.1875 | 0 | 8.7758 | 39.95
2021-06-17 05:00 | 44364.2083 | 0 | 9.4939 | 39.95
2021-06-17 05:30 | 44364.2292 | 0 | 10.4721 | 39.95
2021-06-17 06:00 | 44364.25 | 0 | 11.708 | 39.95
2021-06-17 06:30 | 44364.2708 | 0 | 13.0218 | 39.95
2021-06-17 07:00 | 44364.2917 | 0 | 14.1939 | 39.95
2021-06-17 07:30 | 44364.3125 | 0 | 14.0112 | 39.95
2021-06-17 08:00 | 44364.3333 | 0 | 12.8915 | 39.95
2021-06-17 08:30 | 44364.3542 | 0 | 11.7506 | 39.95
2021-06-17 09:00 | 44364.375 | 0 | 11.0455 | 39.95
2021-06-17 09:30 | 44364.3958 | 0 | 10.4661 | 39.95
2021-06-17 10:00 | 44364.4167 | 0 | 9.6761 | 39.95
2021-06-17 10:30 | 44364.4375 | 0 | 9.438 | 39.95
2021-06-17 11:00 | 44364.4583 | 0 | 9.0178 | 39.95
2021-06-17 11:30 | 44364.4792 | 0 | 8.7495 | 39.95
2021-06-17 12:00 | 44364.5 | 0 | 8.5747 | 39.95
2021-06-17 12:30 | 44364.5208 | 0 | 8.4211 | 39.95
2021-06-17 13:00 | 44364.5417 | 0 | 8.9116 | 39.95
2021-06-17 13:30 | 44364.5625 | 0 | 8.9665 | 39.95
2021-06-17 14:00 | 44364.5833 | 0 | 9.458 | 39.95
2021-06-17 14:30 | 44364.6042 | 0 | 9.888 | 39.95
2021-06-17 15:00 | 44364.625 | 0 | 10.8402 | 39.95
2021-06-17 15:30 | 44364.6458 | 0 | 11.3114 | 39.95
2021-06-17 16:00 | 44364.6667 | 0 | 11.9185 | 39.95
2021-06-17 16:30 | 44364.6875 | 0 | 12.6492 | 39.95
2021-06-17 17:00 | 44364.7083 | 0 | 13.547 | 39.95
2021-06-17 17:30 | 44364.7292 | 0 | 14.0321 | 39.95
2021-06-17 18:00 | 44364.75 | 0 | 14.0945 | 39.95
2021-06-17 18:30 | 44364.7708 | 0 | 14.3302 | 39.95
2021-06-17 19:00 | 44364.7917 | 0 | 14.0922 | 39.95
2021-06-17 19:30 | 44364.8125 | 0 | 14.1013 | 39.95
2021-06-17 20:00 | 44364.8333 | 0 | 13.8225 | 39.95
2021-06-17 20:30 | 44364.8542 | 0 | 13.3102 | 39.95
2021-06-17 21:00 | 44364.875 | 0 | 12.7953 | 39.95
2021-06-17 21:30 | 44364.8958 | 0 | 12.1552 | 39.95
2021-06-17 22:00 | 44364.9167 | 0 | 11.7187 | 39.95
2021-06-17 22:30 | 44364.9375 | 0 | 10.8061 | 39.95
2021-06-17 23:00 | 44364.9583 | 0 | 10.2386 | 39.95
2021-06-17 23:30 | 44364.9792 | 0 | 9.7385 | 39.95
2021-06-18 | 44365 | 0 | 8.9996 | 39.95
2021-06-18 00:30 | 44365.0208 | 0 | 8.4654 | 39.95
2021-06-18 01:00 | 44365.0417 | 0 | 8.3427 | 39.95
2021-06-18 01:30 | 44365.0625 | 0 | 8.0795 | 39.95
2021-06-18 02:00 | 44365.0833 | 0 | 7.9948 | 39.95
2021-06-18 02:30 | 44365.1042 | 0 | 7.923 | 39.95
2021-06-18 03:00 | 44365.125 | 0 | 7.8637 | 39.95
2021-06-18 03:30 | 44365.1458 | 0 | 8.0501 | 39.95
2021-06-18 04:00 | 44365.1667 | 0 | 8.0208 | 39.95
2021-06-18 04:30 | 44365.1875 | 0 | 8.1291 | 39.95
2021-06-18 05:00 | 44365.2083 | 0 | 8.4882 | 39.95
2021-06-18 05:30 | 44365.2292 | 0 | 8.8798 | 39.95
2021-06-18 06:00 | 44365.25 | 0 | 9.4631 | 39.95
2021-06-18 06:30 | 44365.2708 | 0 | 10.1127 | 39.95
2021-06-18 07:00 | 44365.2917 | 0 | 10.7992 | 39.95
2021-06-18 07:30 | 44365.3125 | 0 | 10.7251 | 39.95
2021-06-18 08:00 | 44365.3333 | 0 | 10.5496 | 39.95
2021-06-18 08:30 | 44365.3542 | 0 | 10.0105 | 39.95
2021-06-18 09:00 | 44365.375 | 0 | 9.2614 | 39.95
2021-06-18 09:30 | 44365.3958 | 0 | 8.818 | 39.95
2021-06-18 10:00 | 44365.4167 | 0 | 8.168 | 39.95
2021-06-18 10:30 | 44365.4375 | 0 | 7.6274 | 39.95
2021-06-18 11:00 | 44365.4583 | 0 | 7.3958 | 39.95
2021-06-18 11:30 | 44365.4792 | 0 | 6.9494 | 39.95
2021-06-18 12:00 | 44365.5 | 0 | 6.808 | 39.95
2021-06-18 12:30 | 44365.5208 | 0 | 6.79 | 39.95
2021-06-18 13:00 | 44365.5417 | 0 | 6.9681 | 39.95
2021-06-18 13:30 | 44365.5625 | 0 | 7.1324 | 39.95
2021-06-18 14:00 | 44365.5833 | 0 | 7.4852 | 39.95
2021-06-18 14:30 | 44365.6042 | 0 | 7.8696 | 39.95
2021-06-18 15:00 | 44365.625 | 0 | 8.5087 | 39.95
2021-06-18 15:30 | 44365.6458 | 0 | 9.3295 | 39.95
2021-06-18 16:00 | 44365.6667 | 0 | 10.2423 | 39.95
2021-06-18 16:30 | 44365.6875 | 0 | 11.3665 | 39.95
2021-06-18 17:00 | 44365.7083 | 0 | 12.473 | 39.95
2021-06-18 17:30 | 44365.7292 | 0 | 13.0181 | 39.95
2021-06-18 18:00 | 44365.75 | 0 | 13.3902 | 39.95
2021-06-18 18:30 | 44365.7708 | 0 | 13.592 | 39.95
2021-06-18 19:00 | 44365.7917 | 0 | 13.549 | 39.95
2021-06-18 19:30 | 44365.8125 | 0 | 13.293 | 39.95
2021-06-18 20:00 | 44365.8333 | 0 | 12.9073 | 39.95
2021-06-18 20:30 | 44365.8542 | 0 | 12.4119 | 39.95
2021-06-18 21:00 | 44365.875 | 0 | 11.8741 | 39.95
2021-06-18 21:30 | 44365.8958 | 0 | 11.4718 | 39.95
2021-06-18 22:00 | 44365.9167 | 0 | 10.8759 | 39.95
2021-06-18 22:30 | 44365.9375 | 0 | 10.02 | 39.95
2021-06-18 23:00 | 44365.9583 | 0 | 9.4524 | 39.95
2021-06-18 23:30 | 44365.9792 | 0 | 8.895 | 39.95
2021-06-19 | 44366 | 0 | 8.3935 | 39.95
2021-06-19 00:30 | 44366.0208 | 0 | 8.0142 | 39.95
2021-06-19 01:00 | 44366.0417 | 0 | 7.6114 | 39.95
2021-06-19 01:30 | 44366.0625 | 0 | 7.5378 | 39.95
2021-06-19 02:00 | 44366.0833 | 0 | 7.4634 | 39.95
2021-06-19 02:30 | 44366.1042 | 0 | 7.2747 | 39.95
2021-06-19 03:00 | 44366.125 | 0 | 7.2779 | 39.95
2021-06-19 03:30 | 44366.1458 | 0 | 7.2947 | 39.95
2021-06-19 04:00 | 44366.1667 | 0 | 7.3306 | 39.95
2021-06-19 04:30 | 44366.1875 | 0 | 7.3245 | 39.95
2021-06-19 05:00 | 44366.2083 | 0 | 7.4795 | 39.95
2021-06-19 05:30 | 44366.2292 | 0 | 7.7704 | 39.95
2021-06-19 06:00 | 44366.25 | 0 | 8.296 | 39.95
2021-06-19 06:30 | 44366.2708 | 0 | 8.7106 | 39.95
2021-06-19 07:00 | 44366.2917 | 0 | 9.2097 | 39.95
2021-06-19 07:30 | 44366.3125 | 0 | 9.425 | 39.95
2021-06-19 08:00 | 44366.3333 | 0 | 9.2571 | 39.95
2021-06-19 08:30 | 44366.3542 | 0 | 8.8943 | 39.95
2021-06-19 09:00 | 44366.375 | 0 | 8.2582 | 39.95
2021-06-19 09:30 | 44366.3958 | 0 | 7.8394 | 39.95
2021-06-19 10:00 | 44366.4167 | 0 | 7.3291 | 39.95
2021-06-19 10:30 | 44366.4375 | 0 | 6.863 | 39.95
2021-06-19 11:00 | 44366.4583 | 0 | 6.3209 | 39.95
2021-06-19 11:30 | 44366.4792 | 0 | 6.3811 | 39.95
2021-06-19 12:00 | 44366.5 | 0 | 6.327 | 39.95
2021-06-19 12:30 | 44366.5208 | 0 | 6.2408 | 39.95
2021-06-19 13:00 | 44366.5417 | 0 | 6.2901 | 39.95
2021-06-19 13:30 | 44366.5625 | 0 | 6.5349 | 39.95
2021-06-19 14:00 | 44366.5833 | 0 | 6.9452 | 39.95
2021-06-19 14:30 | 44366.6042 | 0 | 7.6007 | 39.95
2021-06-19 15:00 | 44366.625 | 0 | 8.3567 | 39.95
2021-06-19 15:30 | 44366.6458 | 0 | 8.896 | 39.95
2021-06-19 16:00 | 44366.6667 | 0 | 9.4229 | 39.95
2021-06-19 16:30 | 44366.6875 | 0 | 10.6203 | 39.95
2021-06-19 17:00 | 44366.7083 | 0 | 11.6941 | 39.95
2021-06-19 17:30 | 44366.7292 | 0 | 12.1441 | 39.95
2021-06-19 18:00 | 44366.75 | 0 | 12.3219 | 39.95
2021-06-19 18:30 | 44366.7708 | 0 | 12.2589 | 39.95
2021-06-19 19:00 | 44366.7917 | 0 | 11.988 | 39.95
2021-06-19 19:30 | 44366.8125 | 0 | 11.9054 | 39.95
2021-06-19 20:00 | 44366.8333 | 0 | 11.7747 | 39.95
2021-06-19 20:30 | 44366.8542 | 0 | 11.3965 | 39.95
2021-06-19 21:00 | 44366.875 | 0 | 10.8536 | 39.95
2021-06-19 21:30 | 44366.8958 | 0 | 10.4145 | 39.95
2021-06-19 22:00 | 44366.9167 | 0 | 9.8905 | 39.95
2021-06-19 22:30 | 44366.9375 | 0 | 9.0374 | 39.95
2021-06-19 23:00 | 44366.9583 | 0 | 8.4454 | 39.95
2021-06-19 23:30 | 44366.9792 | 0 | 8.0288 | 39.95
2021-06-20 | 44367 | 0 | 7.7222 | 39.95
2021-06-20 00:30 | 44367.0208 | 0 | 7.5842 | 39.95
2021-06-20 01:00 | 44367.0417 | 0 | 7.2701 | 39.95
2021-06-20 01:30 | 44367.0625 | 0 | 7.1235 | 39.95
2021-06-20 02:00 | 44367.0833 | 0 | 7.1602 | 39.95
2021-06-20 02:30 | 44367.1042 | 0 | 7.0911 | 39.95
2021-06-20 03:00 | 44367.125 | 0 | 7.1256 | 39.95
2021-06-20 03:30 | 44367.1458 | 0 | 7.3857 | 39.95
2021-06-20 04:00 | 44367.1667 | 0 | 7.6787 | 39.95
2021-06-20 04:30 | 44367.1875 | 0 | 8.2065 | 39.95
2021-06-20 05:00 | 44367.2083 | 0 | 9.0866 | 39.95
2021-06-20 05:30 | 44367.2292 | 0 | 10.0315 | 39.95
2021-06-20 06:00 | 44367.25 | 0 | 11.6398 | 39.95
2021-06-20 06:30 | 44367.2708 | 0 | 13.0816 | 39.95
2021-06-20 07:00 | 44367.2917 | 0 | 13.9686 | 39.95
2021-06-20 07:30 | 44367.3125 | 0 | 13.9607 | 39.95
2021-06-20 08:00 | 44367.3333 | 0 | 13.2227 | 39.95
2021-06-20 08:30 | 44367.3542 | 0 | 12.0843 | 39.95
2021-06-20 09:00 | 44367.375 | 0 | 11.1235 | 39.95
2021-06-20 09:30 | 44367.3958 | 0 | 10.5307 | 39.95
2021-06-20 10:00 | 44367.4167 | 0 | 9.8646 | 39.95
2021-06-20 10:30 | 44367.4375 | 0 | 9.4389 | 39.95
2021-06-20 11:00 | 44367.4583 | 0 | 9.1267 | 39.95
2021-06-20 11:30 | 44367.4792 | 0 | 9.0418 | 39.95
2021-06-20 12:00 | 44367.5 | 0 | 8.8497 | 39.95
2021-06-20 12:30 | 44367.5208 | 0 | 8.9196 | 39.95
2021-06-20 13:00 | 44367.5417 | 0 | 8.9757 | 39.95
2021-06-20 13:30 | 44367.5625 | 0 | 9.406 | 39.95
2021-06-20 14:00 | 44367.5833 | 0 | 9.9768 | 39.95
2021-06-20 14:30 | 44367.6042 | 0 | 10.1287 | 39.95
2021-06-20 15:00 | 44367.625 | 0 | 10.4675 | 39.95
2021-06-20 15:30 | 44367.6458 | 0 | 11.1232 | 39.95
2021-06-20 16:00 | 44367.6667 | 0 | 11.583 | 39.95
2021-06-20 16:30 | 44367.6875 | 0 | 12.5001 | 39.95
2021-06-20 17:00 | 44367.7083 | 0 | 13.4337 | 39.95
2021-06-20 17:30 | 44367.7292 | 0 | 14.3216 | 39.95
2021-06-20 18:00 | 44367.75 | 0 | 14.6605 | 39.95
2021-06-20 18:30 | 44367.7708 | 0 | 14.5194 | 39.95
2021-06-20 19:00 | 44367.7917 | 0 | 14.308 | 39.95
2021-06-20 19:30 | 44367.8125 | 0 | 14.1811 | 39.95
2021-06-20 20:00 | 44367.8333 | 0 | 13.8242 | 39.95
2021-06-20 20:30 | 44367.8542 | 0 | 13.2596 | 39.95
2021-06-20 21:00 | 44367.875 | 0 | 12.6209 | 39.95
2021-06-20 21:30 | 44367.8958 | 0 | 12.1156 | 39.95
2021-06-20 22:00 | 44367.9167 | 0 | 11.5063 | 39.95
2021-06-20 22:30 | 44367.9375 | 0 | 10.6159 | 39.95
2021-06-20 23:00 | 44367.9583 | 0 | 9.8107 | 39.95
2021-06-20 23:30 | 44367.9792 | 0 | 9.4047 | 39.95
2021-06-21 | 44368 | 0 | 8.8623 | 39.95
2021-06-21 00:30 | 44368.0208 | 0 | 8.4057 | 39.95
2021-06-21 01:00 | 44368.0417 | 0 | 8.1689 | 39.95
2021-06-21 01:30 | 44368.0625 | 0 | 7.9174 | 39.95
2021-06-21 02:00 | 44368.0833 | 0 | 7.88 | 39.95
2021-06-21 02:30 | 44368.1042 | 0 | 7.7511 | 39.95
2021-06-21 03:00 | 44368.125 | 0 | 7.8849 | 39.95
2021-06-21 03:30 | 44368.1458 | 0 | 7.9662 | 39.95
2021-06-21 04:00 | 44368.1667 | 0 | 8.255 | 39.95
2021-06-21 04:30 | 44368.1875 | 0 | 8.6923 | 39.95
2021-06-21 05:00 | 44368.2083 | 0 | 9.4957 | 39.95
2021-06-21 05:30 | 44368.2292 | 0 | 10.3125 | 39.95
2021-06-21 06:00 | 44368.25 | 0 | 11.8102 | 39.95
2021-06-21 06:30 | 44368.2708 | 0 | 13.1214 | 39.95
2021-06-21 07:00 | 44368.2917 | 0 | 14.0145 | 39.95
2021-06-21 07:30 | 44368.3125 | 0 | 13.6833 | 39.95
2021-06-21 08:00 | 44368.3333 | 0 | 12.7724 | 39.95
2021-06-21 08:30 | 44368.3542 | 0 | 11.6826 | 39.95
2021-06-21 09:00 | 44368.375 | 0 | 10.807 | 39.95
2021-06-21 09:30 | 44368.3958 | 0 | 10.1426 | 39.95
2021-06-21 10:00 | 44368.4167 | 0 | 9.5704 | 39.95
2021-06-21 10:30 | 44368.4375 | 0 | 9.1845 | 39.95
2021-06-21 11:00 | 44368.4583 | 0 | 8.8574 | 39.95
2021-06-21 11:30 | 44368.4792 | 0 | 9.3713 | 39.95
2021-06-21 12:00 | 44368.5 | 0 | 10.012 | 39.95
2021-06-21 12:30 | 44368.5208 | 0 | 9.5679 | 39.95
2021-06-21 13:00 | 44368.5417 | 0 | 9.6505 | 39.95
2021-06-21 13:30 | 44368.5625 | 0 | 10.9175 | 39.95
2021-06-21 14:00 | 44368.5833 | 0 | 10.4184 | 39.95
2021-06-21 14:30 | 44368.6042 | 0 | 10.8345 | 39.95
2021-06-21 15:00 | 44368.625 | 0 | 11.3966 | 39.95
2021-06-21 15:30 | 44368.6458 | 0 | 11.8673 | 39.95
2021-06-21 16:00 | 44368.6667 | 0 | 12.4565 | 39.95
2021-06-21 16:30 | 44368.6875 | 0 | 12.9068 | 39.95
2021-06-21 17:00 | 44368.7083 | 0 | 13.8156 | 39.95
2021-06-21 17:30 | 44368.7292 | 0 | 14.7186 | 39.95
2021-06-21 18:00 | 44368.75 | 0 | 14.9216 | 39.95
2021-06-21 18:30 | 44368.7708 | 0 | 15.1339 | 39.95
2021-06-21 19:00 | 44368.7917 | 0 | 14.9127 | 39.95
2021-06-21 19:30 | 44368.8125 | 0 | 14.6978 | 39.95
2021-06-21 20:00 | 44368.8333 | 0 | 14.3458 | 39.95
2021-06-21 20:30 | 44368.8542 | 0 | 13.6628 | 39.95
2021-06-21 21:00 | 44368.875 | 0 | 12.9301 | 39.95
2021-06-21 21:30 | 44368.8958 | 0 | 12.2586 | 39.95
2021-06-21 22:00 | 44368.9167 | 0 | 11.6642 | 39.95
2021-06-21 22:30 | 44368.9375 | 0 | 10.718 | 39.95
2021-06-21 23:00 | 44368.9583 | 0 | 10.0022 | 39.95
2021-06-21 23:30 | 44368.9792 | 0 | 9.4439 | 39.95
2021-06-22 | 44369 | 0 | 8.7609 | 39.95
2021-06-22 00:30 | 44369.0208 | 0 | 8.445 | 39.95
2021-06-22 01:00 | 44369.0417 | 0 | 8.2739 | 39.95
2021-06-22 01:30 | 44369.0625 | 0 | 7.9856 | 39.95
2021-06-22 02:00 | 44369.0833 | 0 | 8.014 | 39.95
2021-06-22 02:30 | 44369.1042 | 0 | 7.8951 | 39.95
2021-06-22 03:00 | 44369.125 | 0 | 7.8365 | 39.95
2021-06-22 03:30 | 44369.1458 | 0 | 8.0163 | 39.95
2021-06-22 04:00 | 44369.1667 | 0 | 8.3336 | 39.95
2021-06-22 04:30 | 44369.1875 | 0 | 8.7724 | 39.95
2021-06-22 05:00 | 44369.2083 | 0 | 9.432 | 39.95
2021-06-22 05:30 | 44369.2292 | 0 | 10.2332 | 39.95
2021-06-22 06:00 | 44369.25 | 0 | 11.6477 | 39.95
2021-06-22 06:30 | 44369.2708 | 0 | 12.9483 | 39.95
2021-06-22 07:00 | 44369.2917 | 0 | 13.7 | 39.95
2021-06-22 07:30 | 44369.3125 | 0 | 13.3291 | 39.95
2021-06-22 08:00 | 44369.3333 | 0 | 12.5206 | 39.95
2021-06-22 08:30 | 44369.3542 | 0 | 11.8368 | 39.95
2021-06-22 09:00 | 44369.375 | 0 | 12.2034 | 39.95
2021-06-22 09:30 | 44369.3958 | 0 | 11.3686 | 39.95
2021-06-22 10:00 | 44369.4167 | 0 | 10.5153 | 39.95
2021-06-22 10:30 | 44369.4375 | 0 | 10.3419 | 39.95
2021-06-22 11:00 | 44369.4583 | 0 | 9.4285 | 39.95
2021-06-22 11:30 | 44369.4792 | 0 | 9.3304 | 39.95
2021-06-22 12:00 | 44369.5 | 0 | 8.8918 | 39.95
2021-06-22 12:30 | 44369.5208 | 0 | 9.8446 | 39.95
2021-06-22 13:00 | 44369.5417 | 0 | 9.2878 | 39.95
2021-06-22 13:30 | 44369.5625 | 0 | 10.9938 | 39.95
2021-06-22 14:00 | 44369.5833 | 0 | 11.2741 | 39.95
2021-06-22 14:30 | 44369.6042 | 0 | 11.4102 | 39.95
2021-06-22 15:00 | 44369.625 | 0 | 11.3917 | 39.95
2021-06-22 15:30 | 44369.6458 | 0 | 11.7986 | 39.95
2021-06-22 16:00 | 44369.6667 | 0 | 12.2347 | 39.95
2021-06-22 16:30 | 44369.6875 | 0 | 12.8288 | 39.95
2021-06-22 17:00 | 44369.7083 | 0 | 13.8188 | 39.95
2021-06-22 17:30 | 44369.7292 | 0 | 14.3854 | 39.95
2021-06-22 18:00 | 44369.75 | 0 | 14.4335 | 39.95
2021-06-22 18:30 | 44369.7708 | 0 | 14.5337 | 39.95
2021-06-22 19:00 | 44369.7917 | 0 | 14.3507 | 39.95
2021-06-22 19:30 | 44369.8125 | 0 | 14.0578 | 39.95
2021-06-22 20:00 | 44369.8333 | 0 | 13.8922 | 39.95
2021-06-22 20:30 | 44369.8542 | 0 | 13.3084 | 39.95
2021-06-22 21:00 | 44369.875 | 0 | 12.7092 | 39.95
2021-06-22 21:30 | 44369.8958 | 0 | 12.0999 | 39.95
2021-06-22 22:00 | 44369.9167 | 0 | 11.559 | 39.95
2021-06-22 22:30 | 44369.9375 | 0 | 10.5596 | 39.95
2021-06-22 23:00 | 44369.9583 | 0 | 9.8123 | 39.95
2021-06-22 23:30 | 44369.9792 | 0 | 9.4026 | 39.95
2021-06-23 | 44370 | 0 | 8.9203 | 39.95
2021-06-23 00:30 | 44370.0208 | 0 | 8.4596 | 39.95
2021-06-23 01:00 | 44370.0417 | 0 | 8.2442 | 39.95
2021-06-23 01:30 | 44370.0625 | 0 | 7.9575 | 39.95
2021-06-23 02:00 | 44370.0833 | 0 | 7.99 | 39.95
2021-06-23 02:30 | 44370.1042 | 0 | 7.8373 | 39.95
2021-06-23 03:00 | 44370.125 | 0 | 7.7358 | 39.95
2021-06-23 03:30 | 44370.1458 | 0 | 8.0341 | 39.95
2021-06-23 04:00 | 44370.1667 | 0 | 8.3439 | 39.95
2021-06-23 04:30 | 44370.1875 | 0 | 8.7496 | 39.95
2021-06-23 05:00 | 44370.2083 | 0 | 9.4305 | 39.95
2021-06-23 05:30 | 44370.2292 | 0 | 10.0988 | 39.95
2021-06-23 06:00 | 44370.25 | 0 | 11.2801 | 39.95
2021-06-23 06:30 | 44370.2708 | 0 | 12.323 | 39.95
2021-06-23 07:00 | 44370.2917 | 0 | 13.2451 | 39.95
2021-06-23 07:30 | 44370.3125 | 0 | 13.1244 | 39.95
2021-06-23 08:00 | 44370.3333 | 0 | 12.4832 | 39.95
2021-06-23 08:30 | 44370.3542 | 0 | 12.454 | 39.95
2021-06-23 09:00 | 44370.375 | 0 | 12.6388 | 39.95
2021-06-23 09:30 | 44370.3958 | 0 | 11.8858 | 39.95
2021-06-23 10:00 | 44370.4167 | 0 | 11.1405 | 39.95
2021-06-23 10:30 | 44370.4375 | 0 | 10.5009 | 39.95
2021-06-23 11:00 | 44370.4583 | 0 | 9.8949 | 39.95
2021-06-23 11:30 | 44370.4792 | 0 | 9.3362 | 39.95
2021-06-23 12:00 | 44370.5 | 0 | 9.7828 | 39.95
2021-06-23 12:30 | 44370.5208 | 0 | 9.7719 | 39.95
2021-06-23 13:00 | 44370.5417 | 0 | 9.4714 | 39.95
2021-06-23 13:30 | 44370.5625 | 0 | 11.0566 | 39.95
2021-06-23 14:00 | 44370.5833 | 0 | 11.6024 | 39.95
2021-06-23 14:30 | 44370.6042 | 0 | 12.4733 | 39.95
2021-06-23 15:00 | 44370.625 | 0 | 12.264 | 39.95
2021-06-23 15:30 | 44370.6458 | 0 | 12.5407 | 39.95
2021-06-23 16:00 | 44370.6667 | 0 | 12.7179 | 39.95
2021-06-23 16:30 | 44370.6875 | 0 | 13.1033 | 39.95
2021-06-23 17:00 | 44370.7083 | 0 | 13.6943 | 39.95
2021-06-23 17:30 | 44370.7292 | 0 | 14.1152 | 39.95
2021-06-23 18:00 | 44370.75 | 0 | 14.0038 | 39.95
2021-06-23 18:30 | 44370.7708 | 0 | 14.138 | 39.95
2021-06-23 19:00 | 44370.7917 | 0 | 13.9897 | 39.95
2021-06-23 19:30 | 44370.8125 | 0 | 13.7718 | 39.95
2021-06-23 20:00 | 44370.8333 | 0 | 13.3842 | 39.95
2021-06-23 20:30 | 44370.8542 | 0 | 12.8652 | 39.95
2021-06-23 21:00 | 44370.875 | 0 | 12.3562 | 39.95
2021-06-23 21:30 | 44370.8958 | 0 | 11.9024 | 39.95
2021-06-23 22:00 | 44370.9167 | 0 | 11.3457 | 39.95
2021-06-23 22:30 | 44370.9375 | 0 | 10.5379 | 39.95
2021-06-23 23:00 | 44370.9583 | 0 | 9.924 | 39.95
2021-06-23 23:30 | 44370.9792 | 0 | 9.4344 | 39.95
2021-06-24 | 44371 | 0 | 8.9402 | 39.95
2021-06-24 00:30 | 44371.0208 | 0 | 8.454 | 39.95
2021-06-24 01:00 | 44371.0417 | 0 | 8.2178 | 39.95
2021-06-24 01:30 | 44371.0625 | 0 | 8.1159 | 39.95
2021-06-24 02:00 | 44371.0833 | 0 | 8.0489 | 39.95
2021-06-24 02:30 | 44371.1042 | 0 | 8.0297 | 39.95
2021-06-24 03:00 | 44371.125 | 0 | 8.0564 | 39.95
2021-06-24 03:30 | 44371.1458 | 0 | 8.0942 | 39.95
2021-06-24 04:00 | 44371.1667 | 0 | 8.2422 | 39.95
2021-06-24 04:30 | 44371.1875 | 0 | 8.6963 | 39.95
2021-06-24 05:00 | 44371.2083 | 0 | 9.295 | 39.95
2021-06-24 05:30 | 44371.2292 | 0 | 9.7381 | 39.95
2021-06-24 06:00 | 44371.25 | 0 | 10.8275 | 39.95
2021-06-24 06:30 | 44371.2708 | 0 | 12.1207 | 39.95
2021-06-24 07:00 | 44371.2917 | 0 | 13.0527 | 39.95
2021-06-24 07:30 | 44371.3125 | 0 | 13.6201 | 39.95
2021-06-24 08:00 | 44371.3333 | 0 | 13.4514 | 39.95
2021-06-24 08:30 | 44371.3542 | 0 | 13.0228 | 39.95
2021-06-24 09:00 | 44371.375 | 0 | 12.9233 | 39.95
2021-06-24 09:30 | 44371.3958 | 0 | 12.9467 | 39.95
2021-06-24 10:00 | 44371.4167 | 0 | 12.6749 | 39.95
2021-06-24 10:30 | 44371.4375 | 0 | 13.2393 | 39.95
2021-06-24 11:00 | 44371.4583 | 0 | 13.2561 | 39.95
2021-06-24 11:30 | 44371.4792 | 0 | 12.8 | 39.95
2021-06-24 12:00 | 44371.5 | 0 | 12.5031 | 39.95
2021-06-24 12:30 | 44371.5208 | 0 | 12.4393 | 39.95
2021-06-24 13:00 | 44371.5417 | 0 | 12.567 | 39.95
2021-06-24 13:30 | 44371.5625 | 0 | 12.5283 | 39.95
2021-06-24 14:00 | 44371.5833 | 0 | 12.5513 | 39.95
2021-06-24 14:30 | 44371.6042 | 0 | 12.7734 | 39.95
2021-06-24 15:00 | 44371.625 | 0 | 12.8124 | 39.95
2021-06-24 15:30 | 44371.6458 | 0 | 13.0377 | 39.95
2021-06-24 16:00 | 44371.6667 | 0 | 13.1759 | 39.95
2021-06-24 16:30 | 44371.6875 | 0 | 13.9069 | 39.95
2021-06-24 17:00 | 44371.7083 | 0 | 14.1065 | 39.95
2021-06-24 17:30 | 44371.7292 | 0 | 14.2048 | 39.95
2021-06-24 18:00 | 44371.75 | 0 | 14.0163 | 39.95
2021-06-24 18:30 | 44371.7708 | 0 | 13.9078 | 39.95
2021-06-24 19:00 | 44371.7917 | 0 | 13.5577 | 39.95
2021-06-24 19:30 | 44371.8125 | 0 | 13.4408 | 39.95
2021-06-24 20:00 | 44371.8333 | 0 | 13.2633 | 39.95
2021-06-24 20:30 | 44371.8542 | 0 | 13.1176 | 39.95
2021-06-24 21:00 | 44371.875 | 0 | 12.4043 | 39.95
2021-06-24 21:30 | 44371.8958 | 0 | 11.9542 | 39.95
2021-06-24 22:00 | 44371.9167 | 0 | 11.4045 | 39.95
2021-06-24 22:30 | 44371.9375 | 0 | 10.397 | 39.95
2021-06-24 23:00 | 44371.9583 | 0 | 9.8469 | 39.95
2021-06-24 23:30 | 44371.9792 | 0 | 9.3907 | 39.95
2021-06-25 | 44372 | 0 | 8.7922 | 39.95
2021-06-25 00:30 | 44372.0208 | 0 | 8.3899 | 39.95
2021-06-25 01:00 | 44372.0417 | 0 | 8.0904 | 39.95
2021-06-25 01:30 | 44372.0625 | 0 | 7.8226 | 39.95
2021-06-25 02:00 | 44372.0833 | 0 | 7.833 | 39.95
2021-06-25 02:30 | 44372.1042 | 0 | 7.643 | 39.95
2021-06-25 03:00 | 44372.125 | 0 | 7.5725 | 39.95
2021-06-25 03:30 | 44372.1458 | 0 | 7.4717 | 39.95
2021-06-25 04:00 | 44372.1667 | 0 | 7.5218 | 39.95
2021-06-25 04:30 | 44372.1875 | 0 | 7.5625 | 39.95
2021-06-25 05:00 | 44372.2083 | 0 | 7.9359 | 39.95
2021-06-25 05:30 | 44372.2292 | 0 | 8.0289 | 39.95
2021-06-25 06:00 | 44372.25 | 0 | 8.5037 | 39.95
2021-06-25 06:30 | 44372.2708 | 0 | 8.9271 | 39.95
2021-06-25 07:00 | 44372.2917 | 0 | 9.4511 | 39.95
2021-06-25 07:30 | 44372.3125 | 0 | 9.973 | 39.95
2021-06-25 08:00 | 44372.3333 | 0 | 10.6285 | 39.95
2021-06-25 08:30 | 44372.3542 | 0 | 11.4137 | 39.95
2021-06-25 09:00 | 44372.375 | 0 | 11.5545 | 39.95
2021-06-25 09:30 | 44372.3958 | 0 | 11.6273 | 39.95
2021-06-25 10:00 | 44372.4167 | 0 | 11.834 | 39.95
2021-06-25 10:30 | 44372.4375 | 0 | 11.6496 | 39.95
2021-06-25 11:00 | 44372.4583 | 0 | 11.7868 | 39.95
2021-06-25 11:30 | 44372.4792 | 0 | 11.5696 | 39.95
2021-06-25 12:00 | 44372.5 | 0 | 11.4458 | 39.95
2021-06-25 12:30 | 44372.5208 | 0 | 11.1048 | 39.95
2021-06-25 13:00 | 44372.5417 | 0 | 10.3338 | 39.95
2021-06-25 13:30 | 44372.5625 | 0 | 10.9195 | 39.95
2021-06-25 14:00 | 44372.5833 | 0 | 10.9595 | 39.95
2021-06-25 14:30 | 44372.6042 | 0 | 11.1968 | 39.95
2021-06-25 15:00 | 44372.625 | 0 | 11.553 | 39.95
2021-06-25 15:30 | 44372.6458 | 0 | 11.9809 | 39.95
2021-06-25 16:00 | 44372.6667 | 0 | 12.0671 | 39.95
2021-06-25 16:30 | 44372.6875 | 0 | 12.5682 | 39.95
2021-06-25 17:00 | 44372.7083 | 0 | 12.9965 | 39.95
2021-06-25 17:30 | 44372.7292 | 0 | 13.133 | 39.95
2021-06-25 18:00 | 44372.75 | 0 | 13.1981 | 39.95
2021-06-25 18:30 | 44372.7708 | 0 | 13.0385 | 39.95
2021-06-25 19:00 | 44372.7917 | 0 | 12.654 | 39.95
2021-06-25 19:30 | 44372.8125 | 0 | 12.4301 | 39.95
2021-06-25 20:00 | 44372.8333 | 0 | 12.2404 | 39.95
2021-06-25 20:30 | 44372.8542 | 0 | 11.6937 | 39.95
2021-06-25 21:00 | 44372.875 | 0 | 11.098 | 39.95
2021-06-25 21:30 | 44372.8958 | 0 | 10.7118 | 39.95
2021-06-25 22:00 | 44372.9167 | 0 | 10.3814 | 39.95
2021-06-25 22:30 | 44372.9375 | 0 | 9.739 | 39.95
2021-06-25 23:00 | 44372.9583 | 0 | 9.0682 | 39.95
2021-06-25 23:30 | 44372.9792 | 0 | 8.6853 | 39.95
2021-06-26 | 44373 | 0 | 8.1273 | 39.95
2021-06-26 00:30 | 44373.0208 | 0 | 7.7929 | 39.95
2021-06-26 01:00 | 44373.0417 | 0 | 7.486 | 39.95
2021-06-26 01:30 | 44373.0625 | 0 | 7.2666 | 39.95
2021-06-26 02:00 | 44373.0833 | 0 | 7.3446 | 39.95
2021-06-26 02:30 | 44373.1042 | 0 | 7.2822 | 39.95
2021-06-26 03:00 | 44373.125 | 0 | 7.1565 | 39.95
2021-06-26 03:30 | 44373.1458 | 0 | 7.1762 | 39.95
2021-06-26 04:00 | 44373.1667 | 0 | 7.1713 | 39.95
2021-06-26 04:30 | 44373.1875 | 0 | 7.2109 | 39.95
2021-06-26 05:00 | 44373.2083 | 0 | 7.4299 | 39.95
2021-06-26 05:30 | 44373.2292 | 0 | 7.7356 | 39.95
2021-06-26 06:00 | 44373.25 | 0 | 8.1088 | 39.95
2021-06-26 06:30 | 44373.2708 | 0 | 8.4799 | 39.95
2021-06-26 07:00 | 44373.2917 | 0 | 9.0459 | 39.95
2021-06-26 07:30 | 44373.3125 | 0 | 9.6366 | 39.95
2021-06-26 08:00 | 44373.3333 | 0 | 10.3565 | 39.95
2021-06-26 08:30 | 44373.3542 | 0 | 10.7044 | 39.95
2021-06-26 09:00 | 44373.375 | 0 | 10.168 | 39.95
2021-06-26 09:30 | 44373.3958 | 0 | 8.3897 | 39.95
2021-06-26 10:00 | 44373.4167 | 0 | 7.6798 | 39.95
2021-06-26 10:30 | 44373.4375 | 0 | 7.0574 | 39.95
2021-06-26 11:00 | 44373.4583 | 0 | 6.7762 | 39.95
2021-06-26 11:30 | 44373.4792 | 0 | 6.4172 | 39.95
2021-06-26 12:00 | 44373.5 | 0 | 6.3699 | 39.95
2021-06-26 12:30 | 44373.5208 | 0 | 6.1226 | 39.95
2021-06-26 13:00 | 44373.5417 | 0 | 6.1406 | 39.95
2021-06-26 13:30 | 44373.5625 | 0 | 6.7311 | 39.95
2021-06-26 14:00 | 44373.5833 | 0 | 7.1704 | 39.95
2021-06-26 14:30 | 44373.6042 | 0 | 7.7609 | 39.95
2021-06-26 15:00 | 44373.625 | 0 | 8.0597 | 39.95
2021-06-26 15:30 | 44373.6458 | 0 | 8.9304 | 39.95
2021-06-26 16:00 | 44373.6667 | 0 | 9.8295 | 39.95
2021-06-26 16:30 | 44373.6875 | 0 | 10.8533 | 39.95
2021-06-26 17:00 | 44373.7083 | 0 | 11.9261 | 39.95
2021-06-26 17:30 | 44373.7292 | 0 | 12.9092 | 39.95
2021-06-26 18:00 | 44373.75 | 0 | 13.1159 | 39.95
2021-06-26 18:30 | 44373.7708 | 0 | 13.1253 | 39.95
2021-06-26 19:00 | 44373.7917 | 0 | 12.7209 | 39.95
2021-06-26 19:30 | 44373.8125 | 0 | 13.2573 | 39.95
2021-06-26 20:00 | 44373.8333 | 0 | 12.8694 | 39.95
2021-06-26 20:30 | 44373.8542 | 0 | 12.5079 | 39.95
2021-06-26 21:00 | 44373.875 | 0 | 12.2866 | 39.95
2021-06-26 21:30 | 44373.8958 | 0 | 11.3843 | 39.95
2021-06-26 22:00 | 44373.9167 | 0 | 10.6207 | 39.95
2021-06-26 22:30 | 44373.9375 | 0 | 9.953 | 39.95
2021-06-26 23:00 | 44373.9583 | 0 | 9.2893 | 39.95
2021-06-26 23:30 | 44373.9792 | 0 | 8.8904 | 39.95
2021-06-27 | 44374 | 0 | 8.5122 | 39.95
2021-06-27 00:30 | 44374.0208 | 0 | 8.1732 | 39.95
2021-06-27 01:00 | 44374.0417 | 0 | 7.9704 | 39.95
2021-06-27 01:30 | 44374.0625 | 0 | 7.8356 | 39.95
2021-06-27 02:00 | 44374.0833 | 0 | 7.7729 | 39.95
2021-06-27 02:30 | 44374.1042 | 0 | 7.7554 | 39.95
2021-06-27 03:00 | 44374.125 | 0 | 7.7294 | 39.95
2021-06-27 03:30 | 44374.1458 | 0 | 8.0642 | 39.95
2021-06-27 04:00 | 44374.1667 | 0 | 8.2382 | 39.95
2021-06-27 04:30 | 44374.1875 | 0 | 8.5723 | 39.95
2021-06-27 05:00 | 44374.2083 | 0 | 9.1149 | 39.95
2021-06-27 05:30 | 44374.2292 | 0 | 9.9026 | 39.95
2021-06-27 06:00 | 44374.25 | 0 | 11.4537 | 39.95
2021-06-27 06:30 | 44374.2708 | 0 | 12.89 | 39.95
2021-06-27 07:00 | 44374.2917 | 0 | 13.9951 | 39.95
2021-06-27 07:30 | 44374.3125 | 0 | 13.7932 | 39.95
2021-06-27 08:00 | 44374.3333 | 0 | 13.2197 | 39.95
2021-06-27 08:30 | 44374.3542 | 0 | 12.5373 | 39.95
2021-06-27 09:00 | 44374.375 | 0 | 11.5653 | 39.95
2021-06-27 09:30 | 44374.3958 | 0 | 10.6746 | 39.95
2021-06-27 10:00 | 44374.4167 | 0 | 10.1317 | 39.95
2021-06-27 10:30 | 44374.4375 | 0 | 9.6548 | 39.95
2021-06-27 11:00 | 44374.4583 | 0 | 9.2231 | 39.95
2021-06-27 11:30 | 44374.4792 | 0 | 8.667 | 39.95
2021-06-27 12:00 | 44374.5 | 0 | 8.9202 | 39.95
2021-06-27 12:30 | 44374.5208 | 0 | 8.7414 | 39.95
2021-06-27 13:00 | 44374.5417 | 0 | 9.9599 | 39.95
2021-06-27 13:30 | 44374.5625 | 0 | 9.4516 | 39.95
2021-06-27 14:00 | 44374.5833 | 0 | 9.9089 | 39.95
2021-06-27 14:30 | 44374.6042 | 0 | 10.1978 | 39.95
2021-06-27 15:00 | 44374.625 | 0 | 10.8488 | 39.95
2021-06-27 15:30 | 44374.6458 | 0 | 11.8639 | 39.95
2021-06-27 16:00 | 44374.6667 | 0 | 12.3082 | 39.95
2021-06-27 16:30 | 44374.6875 | 0 | 12.9151 | 39.95
2021-06-27 17:00 | 44374.7083 | 0 | 13.6483 | 39.95
2021-06-27 17:30 | 44374.7292 | 0 | 15.0995 | 39.95
2021-06-27 18:00 | 44374.75 | 0 | 15.4261 | 39.95
2021-06-27 18:30 | 44374.7708 | 0 | 15.5922 | 39.95
2021-06-27 19:00 | 44374.7917 | 0 | 15.362 | 39.95
2021-06-27 19:30 | 44374.8125 | 0 | 14.9209 | 39.95
2021-06-27 20:00 | 44374.8333 | 0 | 14.5484 | 39.95
2021-06-27 20:30 | 44374.8542 | 0 | 13.6912 | 39.95
2021-06-27 21:00 | 44374.875 | 0 | 13.1719 | 39.95
2021-06-27 21:30 | 44374.8958 | 0 | 12.6176 | 39.95
2021-06-27 22:00 | 44374.9167 | 0 | 11.7194 | 39.95
2021-06-27 22:30 | 44374.9375 | 0 | 10.7615 | 39.95
2021-06-27 23:00 | 44374.9583 | 0 | 9.9699 | 39.95
2021-06-27 23:30 | 44374.9792 | 0 | 9.3821 | 39.95
2021-06-28 | 44375 | 0 | 8.8989 | 39.95
2021-06-28 00:30 | 44375.0208 | 0 | 8.4755 | 39.95
2021-06-28 01:00 | 44375.0417 | 0 | 8.2556 | 39.95
2021-06-28 01:30 | 44375.0625 | 0 | 8.1013 | 39.95
2021-06-28 02:00 | 44375.0833 | 0 | 8.1274 | 39.95
2021-06-28 02:30 | 44375.1042 | 0 | 8.0041 | 39.95
2021-06-28 03:00 | 44375.125 | 0 | 7.9436 | 39.95
2021-06-28 03:30 | 44375.1458 | 0 | 8.0813 | 39.95
2021-06-28 04:00 | 44375.1667 | 0 | 8.3631 | 39.95
2021-06-28 04:30 | 44375.1875 | 0 | 8.6499 | 39.95
2021-06-28 05:00 | 44375.2083 | 0 | 9.4599 | 39.95
2021-06-28 05:30 | 44375.2292 | 0 | 10.3668 | 39.95
2021-06-28 06:00 | 44375.25 | 0 | 11.5287 | 39.95
2021-06-28 06:30 | 44375.2708 | 0 | 12.7731 | 39.95
2021-06-28 07:00 | 44375.2917 | 0 | 13.4245 | 39.95
2021-06-28 07:30 | 44375.3125 | 0 | 13.0877 | 39.95
2021-06-28 08:00 | 44375.3333 | 0 | 12.4292 | 39.95
2021-06-28 08:30 | 44375.3542 | 0 | 12.0335 | 39.95
2021-06-28 09:00 | 44375.375 | 0 | 11.1494 | 39.95
2021-06-28 09:30 | 44375.3958 | 0 | 10.4992 | 39.95
2021-06-28 10:00 | 44375.4167 | 0 | 9.7985 | 39.95
2021-06-28 10:30 | 44375.4375 | 0 | 9.366 | 39.95
2021-06-28 11:00 | 44375.4583 | 0 | 9.6056 | 39.95
2021-06-28 11:30 | 44375.4792 | 0 | 9.8031 | 39.95
2021-06-28 12:00 | 44375.5 | 0 | 9.7823 | 39.95
2021-06-28 12:30 | 44375.5208 | 0 | 8.7042 | 39.95
2021-06-28 13:00 | 44375.5417 | 0 | 9.8892 | 39.95
2021-06-28 13:30 | 44375.5625 | 0 | 10.6284 | 39.95
2021-06-28 14:00 | 44375.5833 | 0 | 9.8181 | 39.95
2021-06-28 14:30 | 44375.6042 | 0 | 10.536 | 39.95
2021-06-28 15:00 | 44375.625 | 0 | 11.1944 | 39.95
2021-06-28 15:30 | 44375.6458 | 0 | 11.3112 | 39.95
2021-06-28 16:00 | 44375.6667 | 0 | 12.1614 | 39.95
2021-06-28 16:30 | 44375.6875 | 0 | 12.7207 | 39.95
2021-06-28 17:00 | 44375.7083 | 0 | 13.5287 | 39.95
2021-06-28 17:30 | 44375.7292 | 0 | 14.448 | 39.95
2021-06-28 18:00 | 44375.75 | 0 | 14.5958 | 39.95
2021-06-28 18:30 | 44375.7708 | 0 | 14.8561 | 39.95
2021-06-28 19:00 | 44375.7917 | 0 | 14.1913 | 39.95
2021-06-28 19:30 | 44375.8125 | 0 | 13.8442 | 39.95
2021-06-28 20:00 | 44375.8333 | 0 | 13.6373 | 39.95
2021-06-28 20:30 | 44375.8542 | 0 | 12.8837 | 39.95
2021-06-28 21:00 | 44375.875 | 0 | 12.5778 | 39.95
2021-06-28 21:30 | 44375.8958 | 0 | 11.8121 | 39.95
2021-06-28 22:00 | 44375.9167 | 0 | 11.0463 | 39.95
2021-06-28 22:30 | 44375.9375 | 0 | 10.4158 | 39.95
2021-06-28 23:00 | 44375.9583 | 0 | 9.8243 | 39.95
2021-06-28 23:30 | 44375.9792 | 0 | 9.2487 | 39.95
2021-06-29 | 44376 | 0 | 8.6883 | 39.95
2021-06-29 00:30 | 44376.0208 | 0 | 8.4171 | 39.95
2021-06-29 01:00 | 44376.0417 | 0 | 8.1714 | 39.95
2021-06-29 01:30 | 44376.0625 | 0 | 8.0105 | 39.95
2021-06-29 02:00 | 44376.0833 | 0 | 7.9768 | 39.95
2021-06-29 02:30 | 44376.1042 | 0 | 7.8251 | 39.95
2021-06-29 03:00 | 44376.125 | 0 | 7.7867 | 39.95
2021-06-29 03:30 | 44376.1458 | 0 | 7.9748 | 39.95
2021-06-29 04:00 | 44376.1667 | 0 | 8.2804 | 39.95
2021-06-29 04:30 | 44376.1875 | 0 | 8.6041 | 39.95
2021-06-29 05:00 | 44376.2083 | 0 | 9.38 | 39.95
2021-06-29 05:30 | 44376.2292 | 0 | 9.9165 | 39.95
2021-06-29 06:00 | 44376.25 | 0 | 10.8163 | 39.95
2021-06-29 06:30 | 44376.2708 | 0 | 11.5421 | 39.95
2021-06-29 07:00 | 44376.2917 | 0 | 12.4475 | 39.95
2021-06-29 07:30 | 44376.3125 | 0 | 12.9653 | 39.95
2021-06-29 08:00 | 44376.3333 | 0 | 13.3378 | 39.95
2021-06-29 08:30 | 44376.3542 | 0 | 13.6201 | 39.95
2021-06-29 09:00 | 44376.375 | 0 | 12.7108 | 39.95
2021-06-29 09:30 | 44376.3958 | 0 | 10.6653 | 39.95
2021-06-29 10:00 | 44376.4167 | 0 | 10.0749 | 39.95
2021-06-29 10:30 | 44376.4375 | 0 | 9.8292 | 39.95
2021-06-29 11:00 | 44376.4583 | 0 | 10.3814 | 39.95
2021-06-29 11:30 | 44376.4792 | 0 | 12.8696 | 39.95
2021-06-29 12:00 | 44376.5 | 0 | 11.1887 | 39.95
2021-06-29 12:30 | 44376.5208 | 0 | 10.5368 | 39.95
2021-06-29 13:00 | 44376.5417 | 0 | 11.3464 | 39.95
2021-06-29 13:30 | 44376.5625 | 0 | 12.2589 | 39.95
2021-06-29 14:00 | 44376.5833 | 0 | 11.7331 | 39.95
2021-06-29 14:30 | 44376.6042 | 0 | 11.0887 | 39.95
2021-06-29 15:00 | 44376.625 | 0 | 11.1165 | 39.95
2021-06-29 15:30 | 44376.6458 | 0 | 11.9111 | 39.95
2021-06-29 16:00 | 44376.6667 | 0 | 12.1239 | 39.95
2021-06-29 16:30 | 44376.6875 | 0 | 12.7665 | 39.95
2021-06-29 17:00 | 44376.7083 | 0 | 13.5533 | 39.95
2021-06-29 17:30 | 44376.7292 | 0 | 14.5234 | 39.95
2021-06-29 18:00 | 44376.75 | 0 | 14.6358 | 39.95
2021-06-29 18:30 | 44376.7708 | 0 | 14.8411 | 39.95
2021-06-29 19:00 | 44376.7917 | 0 | 14.2257 | 39.95
2021-06-29 19:30 | 44376.8125 | 0 | 13.8932 | 39.95
2021-06-29 20:00 | 44376.8333 | 0 | 13.666 | 39.95
2021-06-29 20:30 | 44376.8542 | 0 | 12.9277 | 39.95
2021-06-29 21:00 | 44376.875 | 0 | 12.5918 | 39.95
2021-06-29 21:30 | 44376.8958 | 0 | 11.8215 | 39.95
2021-06-29 22:00 | 44376.9167 | 0 | 11.0636 | 39.95
2021-06-29 22:30 | 44376.9375 | 0 | 10.4294 | 39.95
2021-06-29 23:00 | 44376.9583 | 0 | 9.8128 | 39.95
2021-06-29 23:30 | 44376.9792 | 0 | 9.2759 | 39.95
2021-06-30 | 44377 | 0 | 8.7203 | 39.95
2021-06-30 00:30 | 44377.0208 | 0 | 8.4273 | 39.95
2021-06-30 01:00 | 44377.0417 | 0 | 8.2005 | 39.95
2021-06-30 01:30 | 44377.0625 | 0 | 8.0333 | 39.95
2021-06-30 02:00 | 44377.0833 | 0 | 8.0121 | 39.95
2021-06-30 02:30 | 44377.1042 | 0 | 7.8152 | 39.95
2021-06-30 03:00 | 44377.125 | 0 | 7.8164 | 39.95
2021-06-30 03:30 | 44377.1458 | 0 | 8.0016 | 39.95
2021-06-30 04:00 | 44377.1667 | 0 | 8.3152 | 39.95
2021-06-30 04:30 | 44377.1875 | 0 | 8.6336 | 39.95
2021-06-30 05:00 | 44377.2083 | 0 | 9.345 | 39.95
2021-06-30 05:30 | 44377.2292 | 0 | 9.9269 | 39.95
2021-06-30 06:00 | 44377.25 | 0 | 10.8486 | 39.95
2021-06-30 06:30 | 44377.2708 | 0 | 11.5197 | 39.95
2021-06-30 07:00 | 44377.2917 | 0 | 12.5069 | 39.95
2021-06-30 07:30 | 44377.3125 | 0 | 12.9827 | 39.95
2021-06-30 08:00 | 44377.3333 | 0 | 13.3384 | 39.95
2021-06-30 08:30 | 44377.3542 | 0 | 13.6618 | 39.95
2021-06-30 09:00 | 44377.375 | 0 | 12.7466 | 39.95
2021-06-30 09:30 | 44377.3958 | 0 | 10.6308 | 39.95
2021-06-30 10:00 | 44377.4167 | 0 | 10.0356 | 39.95
2021-06-30 10:30 | 44377.4375 | 0 | 9.8536 | 39.95
2021-06-30 11:00 | 44377.4583 | 0 | 10.373 | 39.95
2021-06-30 11:30 | 44377.4792 | 0 | 12.9344 | 39.95
2021-06-30 12:00 | 44377.5 | 0 | 11.1765 | 39.95
2021-06-30 12:30 | 44377.5208 | 0 | 10.5447 | 39.95
2021-06-30 13:00 | 44377.5417 | 0 | 11.3116 | 39.95
2021-06-30 13:30 | 44377.5625 | 0 | 12.2649 | 39.95
2021-06-30 14:00 | 44377.5833 | 0 | 11.7682 | 39.95
2021-06-30 14:30 | 44377.6042 | 0 | 11.07 | 39.95
2021-06-30 15:00 | 44377.625 | 0 | 11.094 | 39.95
2021-06-30 15:30 | 44377.6458 | 0 | 11.9292 | 39.95
2021-06-30 16:00 | 44377.6667 | 0 | 12.6031 | 39.95
2021-06-30 16:30 | 44377.6875 | 0 | 13.2394 | 39.95
2021-06-30 17:00 | 44377.7083 | 0 | 13.8865 | 39.95
2021-06-30 17:30 | 44377.7292 | 0 | 15.0024 | 39.95
2021-06-30 18:00 | 44377.75 | 0 | 15.4932 | 39.95
2021-06-30 18:30 | 44377.7708 | 0 | 15.2768 | 39.95
2021-06-30 19:00 | 44377.7917 | 0 | 14.8762 | 39.95
2021-06-30 19:30 | 44377.8125 | 0 | 14.2901 | 39.95
2021-06-30 20:00 | 44377.8333 | 0 | 13.9186 | 39.95
2021-06-30 20:30 | 44377.8542 | 0 | 13.3805 | 39.95
2021-06-30 21:00 | 44377.875 | 0 | 12.7455 | 39.95
2021-06-30 21:30 | 44377.8958 | 0 | 12.0362 | 39.95
2021-06-30 22:00 | 44377.9167 | 0 | 11.3095 | 39.95
2021-06-30 22:30 | 44377.9375 | 0 | 10.5129 | 39.95
2021-06-30 23:00 | 44377.9583 | 0 | 9.7472 | 39.95
2021-06-30 23:30 | 44377.9792 | 0 | 9.3624 | 39.95
2021-07-01 | 44378 | 0 | 8.8196 | 39.95
2021-07-01 00:30 | 44378.0208 | 0 | 8.4027 | 39.95
2021-07-01 01:00 | 44378.0417 | 0 | 8.0681 | 39.95
2021-07-01 01:30 | 44378.0625 | 0 | 7.9862 | 39.95
2021-07-01 02:00 | 44378.0833 | 0 | 8.0389 | 39.95
2021-07-01 02:30 | 44378.1042 | 0 | 7.9094 | 39.95
2021-07-01 03:00 | 44378.125 | 0 | 7.8654 | 39.95
2021-07-01 03:30 | 44378.1458 | 0 | 8.0226 | 39.95
2021-07-01 04:00 | 44378.1667 | 0 | 8.3841 | 39.95
2021-07-01 04:30 | 44378.1875 | 0 | 8.635 | 39.95
2021-07-01 05:00 | 44378.2083 | 0 | 9.1259 | 39.95
2021-07-01 05:30 | 44378.2292 | 0 | 9.95 | 39.95
2021-07-01 06:00 | 44378.25 | 0 | 10.9518 | 39.95
2021-07-01 06:30 | 44378.2708 | 0 | 11.6899 | 39.95
2021-07-01 07:00 | 44378.2917 | 0 | 12.5361 | 39.95
2021-07-01 07:30 | 44378.3125 | 0 | 13.2101 | 39.95
2021-07-01 08:00 | 44378.3333 | 0 | 12.6434 | 39.95
2021-07-01 08:30 | 44378.3542 | 0 | 12.6411 | 39.95
2021-07-01 09:00 | 44378.375 | 0 | 11.3956 | 39.95
2021-07-01 09:30 | 44378.3958 | 0 | 10.6553 | 39.95
2021-07-01 10:00 | 44378.4167 | 0 | 10.9854 | 39.95
2021-07-01 10:30 | 44378.4375 | 0 | 12.0188 | 39.95
2021-07-01 11:00 | 44378.4583 | 0 | 10.3876 | 39.95
2021-07-01 11:30 | 44378.4792 | 0 | 11.9196 | 39.95
2021-07-01 12:00 | 44378.5 | 0 | 11.9774 | 39.95
2021-07-01 12:30 | 44378.5208 | 0 | 12.8946 | 39.95
2021-07-01 13:00 | 44378.5417 | 0 | 12.9198 | 39.95
2021-07-01 13:30 | 44378.5625 | 0 | 12.6697 | 39.95
2021-07-01 14:00 | 44378.5833 | 0 | 12.6267 | 39.95
2021-07-01 14:30 | 44378.6042 | 0 | 11.5574 | 39.95
2021-07-01 15:00 | 44378.625 | 0 | 13.1556 | 39.95
2021-07-01 15:30 | 44378.6458 | 0 | 13.1328 | 39.95
2021-07-01 16:00 | 44378.6667 | 0 | 13.526 | 39.95
2021-07-01 16:30 | 44378.6875 | 0 | 14.2125 | 39.95
2021-07-01 17:00 | 44378.7083 | 0 | 14.7692 | 39.95
2021-07-01 17:30 | 44378.7292 | 0 | 15.3772 | 39.95
2021-07-01 18:00 | 44378.75 | 0 | 15.4296 | 39.95
2021-07-01 18:30 | 44378.7708 | 0 | 15.1312 | 39.95
2021-07-01 19:00 | 44378.7917 | 0 | 14.625 | 39.95
2021-07-01 19:30 | 44378.8125 | 0 | 14.3577 | 39.95
2021-07-01 20:00 | 44378.8333 | 0 | 13.8572 | 39.95
2021-07-01 20:30 | 44378.8542 | 0 | 12.9876 | 39.95
2021-07-01 21:00 | 44378.875 | 0 | 12.5795 | 39.95
2021-07-01 21:30 | 44378.8958 | 0 | 12.0439 | 39.95
2021-07-01 22:00 | 44378.9167 | 0 | 11.3514 | 39.95
2021-07-01 22:30 | 44378.9375 | 0 | 10.4296 | 39.95
2021-07-01 23:00 | 44378.9583 | 0 | 9.943 | 39.95
2021-07-01 23:30 | 44378.9792 | 0 | 9.55 | 39.95
2021-07-02 | 44379 | 0 | 8.9515 | 39.95
2021-07-02 00:30 | 44379.0208 | 0 | 8.5207 | 39.95
2021-07-02 01:00 | 44379.0417 | 0 | 8.2319 | 39.95
2021-07-02 01:30 | 44379.0625 | 0 | 8.046 | 39.95
2021-07-02 02:00 | 44379.0833 | 0 | 7.9983 | 39.95
2021-07-02 02:30 | 44379.1042 | 0 | 7.9547 | 39.95
2021-07-02 03:00 | 44379.125 | 0 | 7.9496 | 39.95
2021-07-02 03:30 | 44379.1458 | 0 | 7.99 | 39.95
2021-07-02 04:00 | 44379.1667 | 0 | 8.3876 | 39.95
2021-07-02 04:30 | 44379.1875 | 0 | 8.5205 | 39.95
2021-07-02 05:00 | 44379.2083 | 0 | 9.1465 | 39.95
2021-07-02 05:30 | 44379.2292 | 0 | 9.8959 | 39.95
2021-07-02 06:00 | 44379.25 | 0 | 10.6078 | 39.95
2021-07-02 06:30 | 44379.2708 | 0 | 11.4003 | 39.95
2021-07-02 07:00 | 44379.2917 | 0 | 12.2192 | 39.95
2021-07-02 07:30 | 44379.3125 | 0 | 12.7978 | 39.95
2021-07-02 08:00 | 44379.3333 | 0 | 13.5153 | 39.95
2021-07-02 08:30 | 44379.3542 | 0 | 12.8409 | 39.95
2021-07-02 09:00 | 44379.375 | 0 | 12.2796 | 39.95
2021-07-02 09:30 | 44379.3958 | 0 | 11.957 | 39.95
2021-07-02 10:00 | 44379.4167 | 0 | 11.0038 | 39.95
2021-07-02 10:30 | 44379.4375 | 0 | 12.7563 | 39.95
2021-07-02 11:00 | 44379.4583 | 0 | 11.2918 | 39.95
2021-07-02 11:30 | 44379.4792 | 0 | 10.4215 | 39.95
2021-07-02 12:00 | 44379.5 | 0 | 10.8314 | 39.95
2021-07-02 12:30 | 44379.5208 | 0 | 12.6964 | 39.95
2021-07-02 13:00 | 44379.5417 | 0 | 13.265 | 39.95
2021-07-02 13:30 | 44379.5625 | 0 | 11.6523 | 39.95
2021-07-02 14:00 | 44379.5833 | 0 | 12.0907 | 39.95
2021-07-02 14:30 | 44379.6042 | 0 | 12.4444 | 39.95
2021-07-02 15:00 | 44379.625 | 0 | 12.3239 | 39.95
2021-07-02 15:30 | 44379.6458 | 0 | 12.3302 | 39.95
2021-07-02 16:00 | 44379.6667 | 0 | 12.1727 | 39.95
2021-07-02 16:30 | 44379.6875 | 0 | 12.9446 | 39.95
2021-07-02 17:00 | 44379.7083 | 0 | 13.6592 | 39.95
2021-07-02 17:30 | 44379.7292 | 0 | 14.3848 | 39.95
2021-07-02 18:00 | 44379.75 | 0 | 14.5986 | 39.95
2021-07-02 18:30 | 44379.7708 | 0 | 14.4426 | 39.95
2021-07-02 19:00 | 44379.7917 | 0 | 13.9762 | 39.95
2021-07-02 19:30 | 44379.8125 | 0 | 13.6945 | 39.95
2021-07-02 20:00 | 44379.8333 | 0 | 13.042 | 39.95
2021-07-02 20:30 | 44379.8542 | 0 | 12.574 | 39.95
2021-07-02 21:00 | 44379.875 | 0 | 12.1058 | 39.95
2021-07-02 21:30 | 44379.8958 | 0 | 11.6479 | 39.95
2021-07-02 22:00 | 44379.9167 | 0 | 10.8935 | 39.95
2021-07-02 22:30 | 44379.9375 | 0 | 10.1594 | 39.95
2021-07-02 23:00 | 44379.9583 | 0 | 9.6205 | 39.95
2021-07-02 23:30 | 44379.9792 | 0 | 9.3018 | 39.95
2021-07-03 | 44380 | 0 | 8.7661 | 39.95
2021-07-03 00:30 | 44380.0208 | 0 | 8.2062 | 39.95
2021-07-03 01:00 | 44380.0417 | 0 | 7.9192 | 39.95
2021-07-03 01:30 | 44380.0625 | 0 | 7.9115 | 39.95
2021-07-03 02:00 | 44380.0833 | 0 | 7.8522 | 39.95
2021-07-03 02:30 | 44380.1042 | 0 | 7.5646 | 39.95
2021-07-03 03:00 | 44380.125 | 0 | 7.5997 | 39.95
2021-07-03 03:30 | 44380.1458 | 0 | 7.7291 | 39.95
2021-07-03 04:00 | 44380.1667 | 0 | 7.7526 | 39.95
2021-07-03 04:30 | 44380.1875 | 0 | 7.8997 | 39.95
2021-07-03 05:00 | 44380.2083 | 0 | 8.1884 | 39.95
2021-07-03 05:30 | 44380.2292 | 0 | 8.1769 | 39.95
2021-07-03 06:00 | 44380.25 | 0 | 8.4715 | 39.95
2021-07-03 06:30 | 44380.2708 | 0 | 8.6945 | 39.95
2021-07-03 07:00 | 44380.2917 | 0 | 9.4426 | 39.95
2021-07-03 07:30 | 44380.3125 | 0 | 10.0639 | 39.95
2021-07-03 08:00 | 44380.3333 | 0 | 10.8043 | 39.95
2021-07-03 08:30 | 44380.3542 | 0 | 11.13 | 39.95
2021-07-03 09:00 | 44380.375 | 0 | 11.5717 | 39.95
2021-07-03 09:30 | 44380.3958 | 0 | 12.2338 | 39.95
2021-07-03 10:00 | 44380.4167 | 0 | 12.1162 | 39.95
2021-07-03 10:30 | 44380.4375 | 0 | 12.5161 | 39.95
2021-07-03 11:00 | 44380.4583 | 0 | 12.7117 | 39.95
2021-07-03 11:30 | 44380.4792 | 0 | 12.7268 | 39.95
2021-07-03 12:00 | 44380.5 | 0 | 12.2886 | 39.95
2021-07-03 12:30 | 44380.5208 | 0 | 11.9804 | 39.95
2021-07-03 13:00 | 44380.5417 | 0 | 12.3393 | 39.95
2021-07-03 13:30 | 44380.5625 | 0 | 11.781 | 39.95
2021-07-03 14:00 | 44380.5833 | 0 | 11.8984 | 39.95
2021-07-03 14:30 | 44380.6042 | 0 | 11.8609 | 39.95
2021-07-03 15:00 | 44380.625 | 0 | 11.6676 | 39.95
2021-07-03 15:30 | 44380.6458 | 0 | 11.9657 | 39.95
2021-07-03 16:00 | 44380.6667 | 0 | 11.8589 | 39.95
2021-07-03 16:30 | 44380.6875 | 0 | 12.2309 | 39.95
2021-07-03 17:00 | 44380.7083 | 0 | 12.9111 | 39.95
2021-07-03 17:30 | 44380.7292 | 0 | 13.2445 | 39.95
2021-07-03 18:00 | 44380.75 | 0 | 13.0465 | 39.95
2021-07-03 18:30 | 44380.7708 | 0 | 12.9255 | 39.95
2021-07-03 19:00 | 44380.7917 | 0 | 12.5518 | 39.95
2021-07-03 19:30 | 44380.8125 | 0 | 12.378 | 39.95
2021-07-03 20:00 | 44380.8333 | 0 | 12.0611 | 39.95
2021-07-03 20:30 | 44380.8542 | 0 | 11.5867 | 39.95
2021-07-03 21:00 | 44380.875 | 0 | 11.0658 | 39.95
2021-07-03 21:30 | 44380.8958 | 0 | 10.6704 | 39.95
2021-07-03 22:00 | 44380.9167 | 0 | 10.2032 | 39.95
2021-07-03 22:30 | 44380.9375 | 0 | 9.5716 | 39.95
2021-07-03 23:00 | 44380.9583 | 0 | 8.9803 | 39.95
2021-07-03 23:30 | 44380.9792 | 0 | 8.5977 | 39.95
2021-07-04 | 44381 | 0 | 8.1889 | 39.95
2021-07-04 00:30 | 44381.0208 | 0 | 7.7636 | 39.95
2021-07-04 01:00 | 44381.0417 | 0 | 7.4683 | 39.95
2021-07-04 01:30 | 44381.0625 | 0 | 7.2426 | 39.95
2021-07-04 02:00 | 44381.0833 | 0 | 7.1871 | 39.95
2021-07-04 02:30 | 44381.1042 | 0 | 7.1513 | 39.95
2021-07-04 03:00 | 44381.125 | 0 | 7.1144 | 39.95
2021-07-04 03:30 | 44381.1458 | 0 | 7.1794 | 39.95
2021-07-04 04:00 | 44381.1667 | 0 | 7.1026 | 39.95
2021-07-04 04:30 | 44381.1875 | 0 | 7.1256 | 39.95
2021-07-04 05:00 | 44381.2083 | 0 | 7.1937 | 39.95
2021-07-04 05:30 | 44381.2292 | 0 | 7.3142 | 39.95
2021-07-04 06:00 | 44381.25 | 0 | 7.704 | 39.95
2021-07-04 06:30 | 44381.2708 | 0 | 8.0669 | 39.95
2021-07-04 07:00 | 44381.2917 | 0 | 8.4068 | 39.95
2021-07-04 07:30 | 44381.3125 | 0 | 8.4704 | 39.95
2021-07-04 08:00 | 44381.3333 | 0 | 8.3286 | 39.95
2021-07-04 08:30 | 44381.3542 | 0 | 8.1608 | 39.95
2021-07-04 09:00 | 44381.375 | 0 | 7.979 | 39.95
2021-07-04 09:30 | 44381.3958 | 0 | 7.7311 | 39.95
2021-07-04 10:00 | 44381.4167 | 0 | 7.3709 | 39.95
2021-07-04 10:30 | 44381.4375 | 0 | 7.0609 | 39.95
2021-07-04 11:00 | 44381.4583 | 0 | 6.5014 | 39.95
2021-07-04 11:30 | 44381.4792 | 0 | 6.4205 | 39.95
2021-07-04 12:00 | 44381.5 | 0 | 5.9865 | 39.95
2021-07-04 12:30 | 44381.5208 | 0 | 6.4737 | 39.95
2021-07-04 13:00 | 44381.5417 | 0 | 7.1614 | 39.95
2021-07-04 13:30 | 44381.5625 | 0 | 8.2997 | 39.95
2021-07-04 14:00 | 44381.5833 | 0 | 8.0837 | 39.95
2021-07-04 14:30 | 44381.6042 | 0 | 7.7408 | 39.95
2021-07-04 15:00 | 44381.625 | 0 | 8.6413 | 39.95
2021-07-04 15:30 | 44381.6458 | 0 | 9.2423 | 39.95
2021-07-04 16:00 | 44381.6667 | 0 | 9.6007 | 39.95
2021-07-04 16:30 | 44381.6875 | 0 | 10.3551 | 39.95
2021-07-04 17:00 | 44381.7083 | 0 | 11.0825 | 39.95
2021-07-04 17:30 | 44381.7292 | 0 | 11.9209 | 39.95
2021-07-04 18:00 | 44381.75 | 0 | 12.1567 | 39.95
2021-07-04 18:30 | 44381.7708 | 0 | 12.1077 | 39.95
2021-07-04 19:00 | 44381.7917 | 0 | 11.8524 | 39.95
2021-07-04 19:30 | 44381.8125 | 0 | 11.6141 | 39.95
2021-07-04 20:00 | 44381.8333 | 0 | 11.4042 | 39.95
2021-07-04 20:30 | 44381.8542 | 0 | 10.7939 | 39.95
2021-07-04 21:00 | 44381.875 | 0 | 10.2456 | 39.95
2021-07-04 21:30 | 44381.8958 | 0 | 9.9549 | 39.95
2021-07-04 22:00 | 44381.9167 | 0 | 9.5339 | 39.95
2021-07-04 22:30 | 44381.9375 | 0 | 8.889 | 39.95
2021-07-04 23:00 | 44381.9583 | 0 | 8.3691 | 39.95
2021-07-04 23:30 | 44381.9792 | 0 | 8.0151 | 39.95
2021-07-05 | 44382 | 0 | 7.6837 | 39.95
2021-07-05 00:30 | 44382.0208 | 0 | 7.4104 | 39.95
2021-07-05 01:00 | 44382.0417 | 0 | 7.2045 | 39.95
2021-07-05 01:30 | 44382.0625 | 0 | 7.1169 | 39.95
2021-07-05 02:00 | 44382.0833 | 0 | 7.1107 | 39.95
2021-07-05 02:30 | 44382.1042 | 0 | 7.0259 | 39.95
2021-07-05 03:00 | 44382.125 | 0 | 7.0809 | 39.95
2021-07-05 03:30 | 44382.1458 | 0 | 7.385 | 39.95
2021-07-05 04:00 | 44382.1667 | 0 | 7.6911 | 39.95
2021-07-05 04:30 | 44382.1875 | 0 | 8.0248 | 39.95
2021-07-05 05:00 | 44382.2083 | 0 | 8.6442 | 39.95
2021-07-05 05:30 | 44382.2292 | 0 | 9.5877 | 39.95
2021-07-05 06:00 | 44382.25 | 0 | 10.682 | 39.95
2021-07-05 06:30 | 44382.2708 | 0 | 12.053 | 39.95
2021-07-05 07:00 | 44382.2917 | 0 | 13.1072 | 39.95
2021-07-05 07:30 | 44382.3125 | 0 | 13.4835 | 39.95
2021-07-05 08:00 | 44382.3333 | 0 | 13.2238 | 39.95
2021-07-05 08:30 | 44382.3542 | 0 | 12.9679 | 39.95
2021-07-05 09:00 | 44382.375 | 0 | 11.8247 | 39.95
2021-07-05 09:30 | 44382.3958 | 0 | 11.5274 | 39.95
2021-07-05 10:00 | 44382.4167 | 0 | 10.0986 | 39.95
2021-07-05 10:30 | 44382.4375 | 0 | 9.4593 | 39.95
2021-07-05 11:00 | 44382.4583 | 0 | 9.1364 | 39.95
2021-07-05 11:30 | 44382.4792 | 0 | 9.4 | 39.95
2021-07-05 12:00 | 44382.5 | 0 | 9.2335 | 39.95
2021-07-05 12:30 | 44382.5208 | 0 | 8.998 | 39.95
2021-07-05 13:00 | 44382.5417 | 0 | 8.3975 | 39.95
2021-07-05 13:30 | 44382.5625 | 0 | 9.3865 | 39.95
2021-07-05 14:00 | 44382.5833 | 0 | 9.4201 | 39.95
2021-07-05 14:30 | 44382.6042 | 0 | 10.0506 | 39.95
2021-07-05 15:00 | 44382.625 | 0 | 11.1709 | 39.95
2021-07-05 15:30 | 44382.6458 | 0 | 20.7509 | 39.95
2021-07-05 16:00 | 44382.6667 | 0 | 22.2502 | 39.95
2021-07-05 16:30 | 44382.6875 | 0 | 12.8873 | 39.95
2021-07-05 17:00 | 44382.7083 | 0 | 14.1468 | 39.95
2021-07-05 17:30 | 44382.7292 | 0 | 15.2853 | 39.95
2021-07-05 18:00 | 44382.75 | 0 | 15.6063 | 39.95
2021-07-05 18:30 | 44382.7708 | 0 | 16.0704 | 39.95
2021-07-05 19:00 | 44382.7917 | 0 | 15.874 | 39.95
2021-07-05 19:30 | 44382.8125 | 0 | 15.8143 | 39.95
2021-07-05 20:00 | 44382.8333 | 0 | 15.3941 | 39.95
2021-07-05 20:30 | 44382.8542 | 0 | 14.6483 | 39.95
2021-07-05 21:00 | 44382.875 | 0 | 13.8773 | 39.95
2021-07-05 21:30 | 44382.8958 | 0 | 13.3205 | 39.95
2021-07-05 22:00 | 44382.9167 | 0 | 12.3984 | 39.95
2021-07-05 22:30 | 44382.9375 | 0 | 11.2699 | 39.95
2021-07-05 23:00 | 44382.9583 | 0 | 10.5234 | 39.95
2021-07-05 23:30 | 44382.9792 | 0 | 9.7863 | 39.95
2021-07-06 | 44383 | 0 | 8.9976 | 39.95
2021-07-06 00:30 | 44383.0208 | 0 | 8.4935 | 39.95
2021-07-06 01:00 | 44383.0417 | 0 | 8.2337 | 39.95
2021-07-06 01:30 | 44383.0625 | 0 | 8.1376 | 39.95
2021-07-06 02:00 | 44383.0833 | 0 | 8.077 | 39.95
2021-07-06 02:30 | 44383.1042 | 0 | 7.967 | 39.95
2021-07-06 03:00 | 44383.125 | 0 | 7.953 | 39.95
2021-07-06 03:30 | 44383.1458 | 0 | 8.1772 | 39.95
2021-07-06 04:00 | 44383.1667 | 0 | 8.5813 | 39.95
2021-07-06 04:30 | 44383.1875 | 0 | 8.8607 | 39.95
2021-07-06 05:00 | 44383.2083 | 0 | 9.6534 | 39.95
2021-07-06 05:30 | 44383.2292 | 0 | 10.6137 | 39.95
2021-07-06 06:00 | 44383.25 | 0 | 11.7914 | 39.95
2021-07-06 06:30 | 44383.2708 | 0 | 13.1344 | 39.95
2021-07-06 07:00 | 44383.2917 | 0 | 14.3929 | 39.95
2021-07-06 07:30 | 44383.3125 | 0 | 14.9235 | 39.95
2021-07-06 08:00 | 44383.3333 | 0 | 15.1763 | 39.95
2021-07-06 08:30 | 44383.3542 | 0 | 14.7988 | 39.95
2021-07-06 09:00 | 44383.375 | 0 | 14.2324 | 39.95
2021-07-06 09:30 | 44383.3958 | 0 | 13.3144 | 39.95
2021-07-06 10:00 | 44383.4167 | 0 | 12.0215 | 39.95
2021-07-06 10:30 | 44383.4375 | 0 | 10.8426 | 39.95
2021-07-06 11:00 | 44383.4583 | 0 | 11.3637 | 39.95
2021-07-06 11:30 | 44383.4792 | 0 | 9.3657 | 39.95
2021-07-06 12:00 | 44383.5 | 0 | 10.2976 | 39.95
2021-07-06 12:30 | 44383.5208 | 0 | 9.8324 | 39.95
2021-07-06 13:00 | 44383.5417 | 0 | 9.4786 | 39.95
2021-07-06 13:30 | 44383.5625 | 0 | 9.708 | 39.95
2021-07-06 14:00 | 44383.5833 | 0 | 9.9677 | 39.95
2021-07-06 14:30 | 44383.6042 | 0 | 10.5737 | 39.95
2021-07-06 15:00 | 44383.625 | 0 | 10.5422 | 39.95
2021-07-06 15:30 | 44383.6458 | 0 | 11.3858 | 39.95
2021-07-06 16:00 | 44383.6667 | 0 | 12.1717 | 39.95
2021-07-06 16:30 | 44383.6875 | 0 | 12.886 | 39.95
2021-07-06 17:00 | 44383.7083 | 0 | 14.2055 | 39.95
2021-07-06 17:30 | 44383.7292 | 0 | 15.368 | 39.95
2021-07-06 18:00 | 44383.75 | 0 | 15.8753 | 39.95
2021-07-06 18:30 | 44383.7708 | 0 | 16.2235 | 39.95
2021-07-06 19:00 | 44383.7917 | 0 | 16.0443 | 39.95
2021-07-06 19:30 | 44383.8125 | 0 | 16.0993 | 39.95
2021-07-06 20:00 | 44383.8333 | 0 | 15.7073 | 39.95
2021-07-06 20:30 | 44383.8542 | 0 | 14.9266 | 39.95
2021-07-06 21:00 | 44383.875 | 0 | 14.3642 | 39.95
2021-07-06 21:30 | 44383.8958 | 0 | 13.8025 | 39.95
2021-07-06 22:00 | 44383.9167 | 0 | 12.8844 | 39.95
2021-07-06 22:30 | 44383.9375 | 0 | 11.6583 | 39.95
2021-07-06 23:00 | 44383.9583 | 0 | 10.8787 | 39.95
2021-07-06 23:30 | 44383.9792 | 0 | 10.2537 | 39.95
2021-07-07 | 44384 | 0 | 9.588 | 39.95
2021-07-07 00:30 | 44384.0208 | 0 | 9.0948 | 39.95
2021-07-07 01:00 | 44384.0417 | 0 | 8.8278 | 39.95
2021-07-07 01:30 | 44384.0625 | 0 | 8.657 | 39.95
2021-07-07 02:00 | 44384.0833 | 0 | 8.6147 | 39.95
2021-07-07 02:30 | 44384.1042 | 0 | 8.5715 | 39.95
2021-07-07 03:00 | 44384.125 | 0 | 8.4139 | 39.95
2021-07-07 03:30 | 44384.1458 | 0 | 8.5514 | 39.95
2021-07-07 04:00 | 44384.1667 | 0 | 9.0127 | 39.95
2021-07-07 04:30 | 44384.1875 | 0 | 9.4075 | 39.95
2021-07-07 05:00 | 44384.2083 | 0 | 10.3027 | 39.95
2021-07-07 05:30 | 44384.2292 | 0 | 11.3984 | 39.95
2021-07-07 06:00 | 44384.25 | 0 | 12.742 | 39.95
2021-07-07 06:30 | 44384.2708 | 0 | 14.0605 | 39.95
2021-07-07 07:00 | 44384.2917 | 0 | 15.2467 | 39.95
2021-07-07 07:30 | 44384.3125 | 0 | 15.3474 | 39.95
2021-07-07 08:00 | 44384.3333 | 0 | 14.5981 | 39.95
2021-07-07 08:30 | 44384.3542 | 0 | 13.7573 | 39.95
2021-07-07 09:00 | 44384.375 | 0 | 12.7484 | 39.95
2021-07-07 09:30 | 44384.3958 | 0 | 11.6541 | 39.95
2021-07-07 10:00 | 44384.4167 | 0 | 10.8946 | 39.95
2021-07-07 10:30 | 44384.4375 | 0 | 10.362 | 39.95
2021-07-07 11:00 | 44384.4583 | 0 | 9.6451 | 39.95
2021-07-07 11:30 | 44384.4792 | 0 | 9.5703 | 39.95
2021-07-07 12:00 | 44384.5 | 0 | 9.2449 | 39.95
2021-07-07 12:30 | 44384.5208 | 0 | 9.5424 | 39.95
2021-07-07 13:00 | 44384.5417 | 0 | 9.2808 | 39.95
2021-07-07 13:30 | 44384.5625 | 0 | 9.2304 | 39.95
2021-07-07 14:00 | 44384.5833 | 0 | 9.8985 | 39.95
2021-07-07 14:30 | 44384.6042 | 0 | 10.4944 | 39.95
2021-07-07 15:00 | 44384.625 | 0 | 10.8251 | 39.95
2021-07-07 15:30 | 44384.6458 | 0 | 11.2176 | 39.95
2021-07-07 16:00 | 44384.6667 | 0 | 11.84 | 39.95
2021-07-07 16:30 | 44384.6875 | 0 | 12.6865 | 39.95
2021-07-07 17:00 | 44384.7083 | 0 | 13.8642 | 39.95
2021-07-07 17:30 | 44384.7292 | 0 | 14.8112 | 39.95
2021-07-07 18:00 | 44384.75 | 0 | 15.1164 | 39.95
2021-07-07 18:30 | 44384.7708 | 0 | 15.5758 | 39.95
2021-07-07 19:00 | 44384.7917 | 0 | 15.4095 | 39.95
2021-07-07 19:30 | 44384.8125 | 0 | 15.224 | 39.95
2021-07-07 20:00 | 44384.8333 | 0 | 15.073 | 39.95
2021-07-07 20:30 | 44384.8542 | 0 | 14.5683 | 39.95
2021-07-07 21:00 | 44384.875 | 0 | 13.8395 | 39.95
2021-07-07 21:30 | 44384.8958 | 0 | 13.429 | 39.95
2021-07-07 22:00 | 44384.9167 | 0 | 12.6016 | 39.95
2021-07-07 22:30 | 44384.9375 | 0 | 11.2445 | 39.95
2021-07-07 23:00 | 44384.9583 | 0 | 10.4239 | 39.95
2021-07-07 23:30 | 44384.9792 | 0 | 9.8575 | 39.95
2021-07-08 | 44385 | 0 | 9.1517 | 39.95
2021-07-08 00:30 | 44385.0208 | 0 | 8.7945 | 39.95
2021-07-08 01:00 | 44385.0417 | 0 | 8.4809 | 39.95
2021-07-08 01:30 | 44385.0625 | 0 | 8.3673 | 39.95
2021-07-08 02:00 | 44385.0833 | 0 | 8.1864 | 39.95
2021-07-08 02:30 | 44385.1042 | 0 | 8.0655 | 39.95
2021-07-08 03:00 | 44385.125 | 0 | 7.9876 | 39.95
2021-07-08 03:30 | 44385.1458 | 0 | 8.3123 | 39.95
2021-07-08 04:00 | 44385.1667 | 0 | 8.5225 | 39.95
2021-07-08 04:30 | 44385.1875 | 0 | 8.9074 | 39.95
2021-07-08 05:00 | 44385.2083 | 0 | 9.8769 | 39.95
2021-07-08 05:30 | 44385.2292 | 0 | 10.7139 | 39.95
2021-07-08 06:00 | 44385.25 | 0 | 12.1604 | 39.95
2021-07-08 06:30 | 44385.2708 | 0 | 13.1506 | 39.95
2021-07-08 07:00 | 44385.2917 | 0 | 13.9316 | 39.95
2021-07-08 07:30 | 44385.3125 | 0 | 13.8599 | 39.95
2021-07-08 08:00 | 44385.3333 | 0 | 13.7869 | 39.95
2021-07-08 08:30 | 44385.3542 | 0 | 13.6518 | 39.95
2021-07-08 09:00 | 44385.375 | 0 | 13.7928 | 39.95
2021-07-08 09:30 | 44385.3958 | 0 | 13.4974 | 39.95
2021-07-08 10:00 | 44385.4167 | 0 | 12.612 | 39.95
2021-07-08 10:30 | 44385.4375 | 0 | 12.202 | 39.95
2021-07-08 11:00 | 44385.4583 | 0 | 11.3485 | 39.95
2021-07-08 11:30 | 44385.4792 | 0 | 10.8744 | 39.95
2021-07-08 12:00 | 44385.5 | 0 | 9.8182 | 39.95
2021-07-08 12:30 | 44385.5208 | 0 | 11.1486 | 39.95
2021-07-08 13:00 | 44385.5417 | 0 | 11.0243 | 39.95
2021-07-08 13:30 | 44385.5625 | 0 | 11.1998 | 39.95
2021-07-08 14:00 | 44385.5833 | 0 | 11.6256 | 39.95
2021-07-08 14:30 | 44385.6042 | 0 | 12.0452 | 39.95
2021-07-08 15:00 | 44385.625 | 0 | 11.9116 | 39.95
2021-07-08 15:30 | 44385.6458 | 0 | 11.7917 | 39.95
2021-07-08 16:00 | 44385.6667 | 0 | 12.5249 | 39.95
2021-07-08 16:30 | 44385.6875 | 0 | 13.0928 | 39.95
2021-07-08 17:00 | 44385.7083 | 0 | 13.8689 | 39.95
2021-07-08 17:30 | 44385.7292 | 0 | 14.5467 | 39.95
2021-07-08 18:00 | 44385.75 | 0 | 14.9987 | 39.95
2021-07-08 18:30 | 44385.7708 | 0 | 15.2626 | 39.95
2021-07-08 19:00 | 44385.7917 | 0 | 15.0276 | 39.95
2021-07-08 19:30 | 44385.8125 | 0 | 15.2538 | 39.95
2021-07-08 20:00 | 44385.8333 | 0 | 14.9147 | 39.95
2021-07-08 20:30 | 44385.8542 | 0 | 14.305 | 39.95
2021-07-08 21:00 | 44385.875 | 0 | 13.6431 | 39.95
2021-07-08 21:30 | 44385.8958 | 0 | 12.964 | 39.95
2021-07-08 22:00 | 44385.9167 | 0 | 12.3131 | 39.95
2021-07-08 22:30 | 44385.9375 | 0 | 11.0787 | 39.95
2021-07-08 23:00 | 44385.9583 | 0 | 10.3816 | 39.95
2021-07-08 23:30 | 44385.9792 | 0 | 9.7069 | 39.95
2021-07-09 | 44386 | 0 | 9.0785 | 39.95
2021-07-09 00:30 | 44386.0208 | 0 | 8.5735 | 39.95
2021-07-09 01:00 | 44386.0417 | 0 | 8.3203 | 39.95
2021-07-09 01:30 | 44386.0625 | 0 | 8.223 | 39.95
2021-07-09 02:00 | 44386.0833 | 0 | 8.1809 | 39.95
2021-07-09 02:30 | 44386.1042 | 0 | 8.0615 | 39.95
2021-07-09 03:00 | 44386.125 | 0 | 7.9538 | 39.95
2021-07-09 03:30 | 44386.1458 | 0 | 8.1726 | 39.95
2021-07-09 04:00 | 44386.1667 | 0 | 8.3247 | 39.95
2021-07-09 04:30 | 44386.1875 | 0 | 8.8316 | 39.95
2021-07-09 05:00 | 44386.2083 | 0 | 9.3029 | 39.95
2021-07-09 05:30 | 44386.2292 | 0 | 10.3023 | 39.95
2021-07-09 06:00 | 44386.25 | 0 | 11.1212 | 39.95
2021-07-09 06:30 | 44386.2708 | 0 | 12.1413 | 39.95
2021-07-09 07:00 | 44386.2917 | 0 | 12.8941 | 39.95
2021-07-09 07:30 | 44386.3125 | 0 | 13.6433 | 39.95
2021-07-09 08:00 | 44386.3333 | 0 | 13.9885 | 39.95
2021-07-09 08:30 | 44386.3542 | 0 | 14.2199 | 39.95
2021-07-09 09:00 | 44386.375 | 0 | 14.3476 | 39.95
2021-07-09 09:30 | 44386.3958 | 0 | 14.0183 | 39.95
2021-07-09 10:00 | 44386.4167 | 0 | 12.8779 | 39.95
2021-07-09 10:30 | 44386.4375 | 0 | 13.3367 | 39.95
2021-07-09 11:00 | 44386.4583 | 0 | 13.5075 | 39.95
2021-07-09 11:30 | 44386.4792 | 0 | 13.2584 | 39.95
2021-07-09 12:00 | 44386.5 | 0 | 12.6476 | 39.95
2021-07-09 12:30 | 44386.5208 | 0 | 11.4471 | 39.95
2021-07-09 13:00 | 44386.5417 | 0 | 9.6264 | 39.95
2021-07-09 13:30 | 44386.5625 | 0 | 9.9352 | 39.95
2021-07-09 14:00 | 44386.5833 | 0 | 10.3574 | 39.95
2021-07-09 14:30 | 44386.6042 | 0 | 11.0394 | 39.95
2021-07-09 15:00 | 44386.625 | 0 | 12.4866 | 39.95
2021-07-09 15:30 | 44386.6458 | 0 | 11.8154 | 39.95
2021-07-09 16:00 | 44386.6667 | 0 | 11.9908 | 39.95
2021-07-09 16:30 | 44386.6875 | 0 | 12.7216 | 39.95
2021-07-09 17:00 | 44386.7083 | 0 | 13.3082 | 39.95
2021-07-09 17:30 | 44386.7292 | 0 | 13.8383 | 39.95
2021-07-09 18:00 | 44386.75 | 0 | 14.0432 | 39.95
2021-07-09 18:30 | 44386.7708 | 0 | 14.1449 | 39.95
2021-07-09 19:00 | 44386.7917 | 0 | 14.0294 | 39.95
2021-07-09 19:30 | 44386.8125 | 0 | 13.8419 | 39.95
2021-07-09 20:00 | 44386.8333 | 0 | 13.48 | 39.95
2021-07-09 20:30 | 44386.8542 | 0 | 12.944 | 39.95
2021-07-09 21:00 | 44386.875 | 0 | 12.5109 | 39.95
2021-07-09 21:30 | 44386.8958 | 0 | 12.0307 | 39.95
2021-07-09 22:00 | 44386.9167 | 0 | 11.581 | 39.95
2021-07-09 22:30 | 44386.9375 | 0 | 10.6658 | 39.95
2021-07-09 23:00 | 44386.9583 | 0 | 10.0727 | 39.95
2021-07-09 23:30 | 44386.9792 | 0 | 9.5761 | 39.95
2021-07-10 | 44387 | 0 | 9.0599 | 39.95
2021-07-10 00:30 | 44387.0208 | 0 | 8.472 | 39.95
2021-07-10 01:00 | 44387.0417 | 0 | 8.2822 | 39.95
2021-07-10 01:30 | 44387.0625 | 0 | 8.1261 | 39.95
2021-07-10 02:00 | 44387.0833 | 0 | 7.9653 | 39.95
2021-07-10 02:30 | 44387.1042 | 0 | 7.9836 | 39.95
2021-07-10 03:00 | 44387.125 | 0 | 7.8562 | 39.95
2021-07-10 03:30 | 44387.1458 | 0 | 7.9651 | 39.95
2021-07-10 04:00 | 44387.1667 | 0 | 8.0108 | 39.95
2021-07-10 04:30 | 44387.1875 | 0 | 8.0057 | 39.95
2021-07-10 05:00 | 44387.2083 | 0 | 8.5059 | 39.95
2021-07-10 05:30 | 44387.2292 | 0 | 8.6846 | 39.95
2021-07-10 06:00 | 44387.25 | 0 | 9.1177 | 39.95
2021-07-10 06:30 | 44387.2708 | 0 | 9.625 | 39.95
2021-07-10 07:00 | 44387.2917 | 0 | 10.0108 | 39.95
2021-07-10 07:30 | 44387.3125 | 0 | 10.0903 | 39.95
2021-07-10 08:00 | 44387.3333 | 0 | 10.0695 | 39.95
2021-07-10 08:30 | 44387.3542 | 0 | 9.765 | 39.95
2021-07-10 09:00 | 44387.375 | 0 | 9.4376 | 39.95
2021-07-10 09:30 | 44387.3958 | 0 | 8.7609 | 39.95
2021-07-10 10:00 | 44387.4167 | 0 | 8.0485 | 39.95
2021-07-10 10:30 | 44387.4375 | 0 | 7.5094 | 39.95
2021-07-10 11:00 | 44387.4583 | 0 | 7.3262 | 39.95
2021-07-10 11:30 | 44387.4792 | 0 | 7.0153 | 39.95
2021-07-10 12:00 | 44387.5 | 0 | 6.573 | 39.95
2021-07-10 12:30 | 44387.5208 | 0 | 6.3714 | 39.95
2021-07-10 13:00 | 44387.5417 | 0 | 6.6315 | 39.95
2021-07-10 13:30 | 44387.5625 | 0 | 7.0445 | 39.95
2021-07-10 14:00 | 44387.5833 | 0 | 7.5285 | 39.95
2021-07-10 14:30 | 44387.6042 | 0 | 7.9649 | 39.95
2021-07-10 15:00 | 44387.625 | 0 | 8.4388 | 39.95
2021-07-10 15:30 | 44387.6458 | 0 | 9.3202 | 39.95
2021-07-10 16:00 | 44387.6667 | 0 | 10.1696 | 39.95
2021-07-10 16:30 | 44387.6875 | 0 | 11.3047 | 39.95
2021-07-10 17:00 | 44387.7083 | 0 | 12.3918 | 39.95
2021-07-10 17:30 | 44387.7292 | 0 | 13.0452 | 39.95
2021-07-10 18:00 | 44387.75 | 0 | 13.3978 | 39.95
2021-07-10 18:30 | 44387.7708 | 0 | 13.2303 | 39.95
2021-07-10 19:00 | 44387.7917 | 0 | 12.8099 | 39.95
2021-07-10 19:30 | 44387.8125 | 0 | 12.8267 | 39.95
2021-07-10 20:00 | 44387.8333 | 0 | 12.6445 | 39.95
2021-07-10 20:30 | 44387.8542 | 0 | 12.049 | 39.95
2021-07-10 21:00 | 44387.875 | 0 | 11.722 | 39.95
2021-07-10 21:30 | 44387.8958 | 0 | 11.3559 | 39.95
2021-07-10 22:00 | 44387.9167 | 0 | 10.8701 | 39.95
2021-07-10 22:30 | 44387.9375 | 0 | 10.2884 | 39.95
2021-07-10 23:00 | 44387.9583 | 0 | 9.7248 | 39.95
2021-07-10 23:30 | 44387.9792 | 0 | 9.17 | 39.95
2021-07-11 | 44388 | 0 | 8.6299 | 39.95
2021-07-11 00:30 | 44388.0208 | 0 | 8.16 | 39.95
2021-07-11 01:00 | 44388.0417 | 0 | 8.0045 | 39.95
2021-07-11 01:30 | 44388.0625 | 0 | 7.675 | 39.95
2021-07-11 02:00 | 44388.0833 | 0 | 7.4253 | 39.95
2021-07-11 02:30 | 44388.1042 | 0 | 7.4087 | 39.95
2021-07-11 03:00 | 44388.125 | 0 | 7.3343 | 39.95
2021-07-11 03:30 | 44388.1458 | 0 | 7.3151 | 39.95
2021-07-11 04:00 | 44388.1667 | 0 | 7.2558 | 39.95
2021-07-11 04:30 | 44388.1875 | 0 | 7.2564 | 39.95
2021-07-11 05:00 | 44388.2083 | 0 | 7.5224 | 39.95
2021-07-11 05:30 | 44388.2292 | 0 | 7.7077 | 39.95
2021-07-11 06:00 | 44388.25 | 0 | 8.1346 | 39.95
2021-07-11 06:30 | 44388.2708 | 0 | 8.5628 | 39.95
2021-07-11 07:00 | 44388.2917 | 0 | 9.1239 | 39.95
2021-07-11 07:30 | 44388.3125 | 0 | 9.1864 | 39.95
2021-07-11 08:00 | 44388.3333 | 0 | 9.053 | 39.95
2021-07-11 08:30 | 44388.3542 | 0 | 8.8417 | 39.95
2021-07-11 09:00 | 44388.375 | 0 | 8.5198 | 39.95
2021-07-11 09:30 | 44388.3958 | 0 | 8.1022 | 39.95
2021-07-11 10:00 | 44388.4167 | 0 | 7.5223 | 39.95
2021-07-11 10:30 | 44388.4375 | 0 | 7.1456 | 39.95
2021-07-11 11:00 | 44388.4583 | 0 | 6.6873 | 39.95
2021-07-11 11:30 | 44388.4792 | 0 | 6.3476 | 39.95
2021-07-11 12:00 | 44388.5 | 0 | 6.1707 | 39.95
2021-07-11 12:30 | 44388.5208 | 0 | 6.0862 | 39.95
2021-07-11 13:00 | 44388.5417 | 0 | 6.856 | 39.95
2021-07-11 13:30 | 44388.5625 | 0 | 7.3715 | 39.95
2021-07-11 14:00 | 44388.5833 | 0 | 8.3818 | 39.95
2021-07-11 14:30 | 44388.6042 | 0 | 7.6327 | 39.95
2021-07-11 15:00 | 44388.625 | 0 | 8.7795 | 39.95
2021-07-11 15:30 | 44388.6458 | 0 | 9.8837 | 39.95
2021-07-11 16:00 | 44388.6667 | 0 | 10.2849 | 39.95
2021-07-11 16:30 | 44388.6875 | 0 | 11.0351 | 39.95
2021-07-11 17:00 | 44388.7083 | 0 | 11.8019 | 39.95
2021-07-11 17:30 | 44388.7292 | 0 | 12.6856 | 39.95
2021-07-11 18:00 | 44388.75 | 0 | 12.9389 | 39.95
2021-07-11 18:30 | 44388.7708 | 0 | 12.9438 | 39.95
2021-07-11 19:00 | 44388.7917 | 0 | 12.68 | 39.95
2021-07-11 19:30 | 44388.8125 | 0 | 12.4971 | 39.95
2021-07-11 20:00 | 44388.8333 | 0 | 12.2182 | 39.95
2021-07-11 20:30 | 44388.8542 | 0 | 11.754 | 39.95
2021-07-11 21:00 | 44388.875 | 0 | 11.1896 | 39.95
2021-07-11 21:30 | 44388.8958 | 0 | 10.6918 | 39.95
2021-07-11 22:00 | 44388.9167 | 0 | 10.2678 | 39.95
2021-07-11 22:30 | 44388.9375 | 0 | 9.2163 | 39.95
2021-07-11 23:00 | 44388.9583 | 0 | 8.681 | 39.95
2021-07-11 23:30 | 44388.9792 | 0 | 8.2676 | 39.95
2021-07-12 | 44389 | 0 | 7.8402 | 39.95
2021-07-12 00:30 | 44389.0208 | 0 | 7.6695 | 39.95
2021-07-12 01:00 | 44389.0417 | 0 | 7.4245 | 39.95
2021-07-12 01:30 | 44389.0625 | 0 | 7.3898 | 39.95
2021-07-12 02:00 | 44389.0833 | 0 | 7.3334 | 39.95
2021-07-12 02:30 | 44389.1042 | 0 | 7.2656 | 39.95
2021-07-12 03:00 | 44389.125 | 0 | 7.2579 | 39.95
2021-07-12 03:30 | 44389.1458 | 0 | 7.6864 | 39.95
2021-07-12 04:00 | 44389.1667 | 0 | 7.8946 | 39.95
2021-07-12 04:30 | 44389.1875 | 0 | 8.4303 | 39.95
2021-07-12 05:00 | 44389.2083 | 0 | 9.3428 | 39.95
2021-07-12 05:30 | 44389.2292 | 0 | 10.3601 | 39.95
2021-07-12 06:00 | 44389.25 | 0 | 11.9247 | 39.95
2021-07-12 06:30 | 44389.2708 | 0 | 13.4049 | 39.95
2021-07-12 07:00 | 44389.2917 | 0 | 14.1784 | 39.95
2021-07-12 07:30 | 44389.3125 | 0 | 14.3198 | 39.95
2021-07-12 08:00 | 44389.3333 | 0 | 13.3992 | 39.95
2021-07-12 08:30 | 44389.3542 | 0 | 12.2156 | 39.95
2021-07-12 09:00 | 44389.375 | 0 | 11.4221 | 39.95
2021-07-12 09:30 | 44389.3958 | 0 | 10.5791 | 39.95
2021-07-12 10:00 | 44389.4167 | 0 | 9.7605 | 39.95
2021-07-12 10:30 | 44389.4375 | 0 | 9.204 | 39.95
2021-07-12 11:00 | 44389.4583 | 0 | 9.3225 | 39.95
2021-07-12 11:30 | 44389.4792 | 0 | 11.45 | 39.95
2021-07-12 12:00 | 44389.5 | 0 | 9.006 | 39.95
2021-07-12 12:30 | 44389.5208 | 0 | 10.6536 | 39.95
2021-07-12 13:00 | 44389.5417 | 0 | 11.0432 | 39.95
2021-07-12 13:30 | 44389.5625 | 0 | 10.8206 | 39.95
2021-07-12 14:00 | 44389.5833 | 0 | 11.2146 | 39.95
2021-07-12 14:30 | 44389.6042 | 0 | 11.6085 | 39.95
2021-07-12 15:00 | 44389.625 | 0 | 11.7552 | 39.95
2021-07-12 15:30 | 44389.6458 | 0 | 11.7384 | 39.95
2021-07-12 16:00 | 44389.6667 | 0 | 12.5628 | 39.95
2021-07-12 16:30 | 44389.6875 | 0 | 13.1936 | 39.95
2021-07-12 17:00 | 44389.7083 | 0 | 14.0848 | 39.95
2021-07-12 17:30 | 44389.7292 | 0 | 15.221 | 39.95
2021-07-12 18:00 | 44389.75 | 0 | 15.735 | 39.95
2021-07-12 18:30 | 44389.7708 | 0 | 15.8215 | 39.95
2021-07-12 19:00 | 44389.7917 | 0 | 15.6174 | 39.95
2021-07-12 19:30 | 44389.8125 | 0 | 15.3534 | 39.95
2021-07-12 20:00 | 44389.8333 | 0 | 15.0753 | 39.95
2021-07-12 20:30 | 44389.8542 | 0 | 14.4577 | 39.95
2021-07-12 21:00 | 44389.875 | 0 | 13.6347 | 39.95
2021-07-12 21:30 | 44389.8958 | 0 | 12.9245 | 39.95
2021-07-12 22:00 | 44389.9167 | 0 | 12.1452 | 39.95
2021-07-12 22:30 | 44389.9375 | 0 | 11.0735 | 39.95
2021-07-12 23:00 | 44389.9583 | 0 | 10.2521 | 39.95
2021-07-12 23:30 | 44389.9792 | 0 | 9.4112 | 39.95
2021-07-13 | 44390 | 0 | 8.8272 | 39.95
2021-07-13 00:30 | 44390.0208 | 0 | 8.3444 | 39.95
2021-07-13 01:00 | 44390.0417 | 0 | 8.3467 | 39.95
2021-07-13 01:30 | 44390.0625 | 0 | 8.1153 | 39.95
2021-07-13 02:00 | 44390.0833 | 0 | 8.0961 | 39.95
2021-07-13 02:30 | 44390.1042 | 0 | 7.9859 | 39.95
2021-07-13 03:00 | 44390.125 | 0 | 7.93 | 39.95
2021-07-13 03:30 | 44390.1458 | 0 | 8.0644 | 39.95
2021-07-13 04:00 | 44390.1667 | 0 | 8.436 | 39.95
2021-07-13 04:30 | 44390.1875 | 0 | 8.8546 | 39.95
2021-07-13 05:00 | 44390.2083 | 0 | 9.6235 | 39.95
2021-07-13 05:30 | 44390.2292 | 0 | 10.8161 | 39.95
2021-07-13 06:00 | 44390.25 | 0 | 12.0949 | 39.95
2021-07-13 06:30 | 44390.2708 | 0 | 13.6728 | 39.95
2021-07-13 07:00 | 44390.2917 | 0 | 14.52 | 39.95
2021-07-13 07:30 | 44390.3125 | 0 | 13.7246 | 39.95
2021-07-13 08:00 | 44390.3333 | 0 | 12.5386 | 39.95
2021-07-13 08:30 | 44390.3542 | 0 | 11.8852 | 39.95
2021-07-13 09:00 | 44390.375 | 0 | 11.2812 | 39.95
2021-07-13 09:30 | 44390.3958 | 0 | 10.4598 | 39.95
2021-07-13 10:00 | 44390.4167 | 0 | 9.7965 | 39.95
2021-07-13 10:30 | 44390.4375 | 0 | 9.4893 | 39.95
2021-07-13 11:00 | 44390.4583 | 0 | 9.0102 | 39.95
2021-07-13 11:30 | 44390.4792 | 0 | 8.8225 | 39.95
2021-07-13 12:00 | 44390.5 | 0 | 8.6213 | 39.95
2021-07-13 12:30 | 44390.5208 | 0 | 8.7252 | 39.95
2021-07-13 13:00 | 44390.5417 | 0 | 9.6842 | 39.95
2021-07-13 13:30 | 44390.5625 | 0 | 9.7418 | 39.95
2021-07-13 14:00 | 44390.5833 | 0 | 11.4456 | 39.95
2021-07-13 14:30 | 44390.6042 | 0 | 11.9537 | 39.95
2021-07-13 15:00 | 44390.625 | 0 | 11.6711 | 39.95
2021-07-13 15:30 | 44390.6458 | 0 | 11.3604 | 39.95
2021-07-13 16:00 | 44390.6667 | 0 | 11.7111 | 39.95
2021-07-13 16:30 | 44390.6875 | 0 | 12.6841 | 39.95
2021-07-13 17:00 | 44390.7083 | 0 | 13.5427 | 39.95
2021-07-13 17:30 | 44390.7292 | 0 | 14.3769 | 39.95
2021-07-13 18:00 | 44390.75 | 0 | 14.7565 | 39.95
2021-07-13 18:30 | 44390.7708 | 0 | 15.2623 | 39.95
2021-07-13 19:00 | 44390.7917 | 0 | 14.8792 | 39.95
2021-07-13 19:30 | 44390.8125 | 0 | 14.8587 | 39.95
2021-07-13 20:00 | 44390.8333 | 0 | 14.6519 | 39.95
2021-07-13 20:30 | 44390.8542 | 0 | 14.0903 | 39.95
2021-07-13 21:00 | 44390.875 | 0 | 13.3746 | 39.95
2021-07-13 21:30 | 44390.8958 | 0 | 12.6496 | 39.95
2021-07-13 22:00 | 44390.9167 | 0 | 11.7808 | 39.95
2021-07-13 22:30 | 44390.9375 | 0 | 10.8437 | 39.95
2021-07-13 23:00 | 44390.9583 | 0 | 10.0434 | 39.95
2021-07-13 23:30 | 44390.9792 | 0 | 9.447 | 39.95
2021-07-14 | 44391 | 0 | 8.9405 | 39.95
2021-07-14 00:30 | 44391.0208 | 0 | 8.3507 | 39.95
2021-07-14 01:00 | 44391.0417 | 0 | 8.1119 | 39.95
2021-07-14 01:30 | 44391.0625 | 0 | 8.0489 | 39.95
2021-07-14 02:00 | 44391.0833 | 0 | 7.9762 | 39.95
2021-07-14 02:30 | 44391.1042 | 0 | 7.9017 | 39.95
2021-07-14 03:00 | 44391.125 | 0 | 7.9834 | 39.95
2021-07-14 03:30 | 44391.1458 | 0 | 8.0412 | 39.95
2021-07-14 04:00 | 44391.1667 | 0 | 8.2892 | 39.95
2021-07-14 04:30 | 44391.1875 | 0 | 8.7647 | 39.95
2021-07-14 05:00 | 44391.2083 | 0 | 9.4722 | 39.95
2021-07-14 05:30 | 44391.2292 | 0 | 10.501 | 39.95
2021-07-14 06:00 | 44391.25 | 0 | 11.7669 | 39.95
2021-07-14 06:30 | 44391.2708 | 0 | 13.1843 | 39.95
2021-07-14 07:00 | 44391.2917 | 0 | 14.0624 | 39.95
2021-07-14 07:30 | 44391.3125 | 0 | 14.5051 | 39.95
2021-07-14 08:00 | 44391.3333 | 0 | 14.1657 | 39.95
2021-07-14 08:30 | 44391.3542 | 0 | 13.1284 | 39.95
2021-07-14 09:00 | 44391.375 | 0 | 11.6303 | 39.95
2021-07-14 09:30 | 44391.3958 | 0 | 10.4985 | 39.95
2021-07-14 10:00 | 44391.4167 | 0 | 10.5557 | 39.95
2021-07-14 10:30 | 44391.4375 | 0 | 9.283 | 39.95
2021-07-14 11:00 | 44391.4583 | 0 | 10.8992 | 39.95
2021-07-14 11:30 | 44391.4792 | 0 | 9.1718 | 39.95
2021-07-14 12:00 | 44391.5 | 0 | 10.2382 | 39.95
2021-07-14 12:30 | 44391.5208 | 0 | 9.33 | 39.95
2021-07-14 13:00 | 44391.5417 | 0 | 9.8365 | 39.95
2021-07-14 13:30 | 44391.5625 | 0 | 11.0092 | 39.95
2021-07-14 14:00 | 44391.5833 | 0 | 11.357 | 39.95
2021-07-14 14:30 | 44391.6042 | 0 | 11.2477 | 39.95
2021-07-14 15:00 | 44391.625 | 0 | 10.972 | 39.95
2021-07-14 15:30 | 44391.6458 | 0 | 11.0326 | 39.95
2021-07-14 16:00 | 44391.6667 | 0 | 11.8707 | 39.95
2021-07-14 16:30 | 44391.6875 | 0 | 12.4764 | 39.95
2021-07-14 17:00 | 44391.7083 | 0 | 13.6094 | 39.95
2021-07-14 17:30 | 44391.7292 | 0 | 14.4999 | 39.95
2021-07-14 18:00 | 44391.75 | 0 | 14.6396 | 39.95
2021-07-14 18:30 | 44391.7708 | 0 | 14.826 | 39.95
2021-07-14 19:00 | 44391.7917 | 0 | 14.5523 | 39.95
2021-07-14 19:30 | 44391.8125 | 0 | 14.4988 | 39.95
2021-07-14 20:00 | 44391.8333 | 0 | 14.0395 | 39.95
2021-07-14 20:30 | 44391.8542 | 0 | 13.3243 | 39.95
2021-07-14 21:00 | 44391.875 | 0 | 12.6259 | 39.95
2021-07-14 21:30 | 44391.8958 | 0 | 12.0916 | 39.95
2021-07-14 22:00 | 44391.9167 | 0 | 11.4832 | 39.95
2021-07-14 22:30 | 44391.9375 | 0 | 10.6743 | 39.95
2021-07-14 23:00 | 44391.9583 | 0 | 9.8424 | 39.95
2021-07-14 23:30 | 44391.9792 | 0 | 9.2722 | 39.95
2021-07-15 | 44392 | 0 | 8.7454 | 39.95
2021-07-15 00:30 | 44392.0208 | 0 | 8.3795 | 39.95
2021-07-15 01:00 | 44392.0417 | 0 | 8.1234 | 39.95
2021-07-15 01:30 | 44392.0625 | 0 | 7.9787 | 39.95
2021-07-15 02:00 | 44392.0833 | 0 | 8.052 | 39.95
2021-07-15 02:30 | 44392.1042 | 0 | 7.8778 | 39.95
2021-07-15 03:00 | 44392.125 | 0 | 7.8702 | 39.95
2021-07-15 03:30 | 44392.1458 | 0 | 7.9353 | 39.95
2021-07-15 04:00 | 44392.1667 | 0 | 8.3354 | 39.95
2021-07-15 04:30 | 44392.1875 | 0 | 8.5961 | 39.95
2021-07-15 05:00 | 44392.2083 | 0 | 9.3175 | 39.95
2021-07-15 05:30 | 44392.2292 | 0 | 10.0852 | 39.95
2021-07-15 06:00 | 44392.25 | 0 | 11.1982 | 39.95
2021-07-15 06:30 | 44392.2708 | 0 | 12.2168 | 39.95
2021-07-15 07:00 | 44392.2917 | 0 | 13.0679 | 39.95
2021-07-15 07:30 | 44392.3125 | 0 | 13.8025 | 39.95
2021-07-15 08:00 | 44392.3333 | 0 | 13.8892 | 39.95
2021-07-15 08:30 | 44392.3542 | 0 | 12.9679 | 39.95
2021-07-15 09:00 | 44392.375 | 0 | 12.8591 | 39.95
2021-07-15 09:30 | 44392.3958 | 0 | 12.548 | 39.95
2021-07-15 10:00 | 44392.4167 | 0 | 11.5588 | 39.95
2021-07-15 10:30 | 44392.4375 | 0 | 11.3216 | 39.95
2021-07-15 11:00 | 44392.4583 | 0 | 11.2834 | 39.95
2021-07-15 11:30 | 44392.4792 | 0 | 10.8573 | 39.95
2021-07-15 12:00 | 44392.5 | 0 | 9.9752 | 39.95
2021-07-15 12:30 | 44392.5208 | 0 | 11.2804 | 39.95
2021-07-15 13:00 | 44392.5417 | 0 | 10.5027 | 39.95
2021-07-15 13:30 | 44392.5625 | 0 | 10.9736 | 39.95
2021-07-15 14:00 | 44392.5833 | 0 | 10.785 | 39.95
2021-07-15 14:30 | 44392.6042 | 0 | 11.5153 | 39.95
2021-07-15 15:00 | 44392.625 | 0 | 11.8089 | 39.95
2021-07-15 15:30 | 44392.6458 | 0 | 11.5511 | 39.95
2021-07-15 16:00 | 44392.6667 | 0 | 12.3194 | 39.95
2021-07-15 16:30 | 44392.6875 | 0 | 12.945 | 39.95
2021-07-15 17:00 | 44392.7083 | 0 | 13.4033 | 39.95
2021-07-15 17:30 | 44392.7292 | 0 | 14.0237 | 39.95
2021-07-15 18:00 | 44392.75 | 0 | 13.935 | 39.95
2021-07-15 18:30 | 44392.7708 | 0 | 14.1274 | 39.95
2021-07-15 19:00 | 44392.7917 | 0 | 14.134 | 39.95
2021-07-15 19:30 | 44392.8125 | 0 | 14.0323 | 39.95
2021-07-15 20:00 | 44392.8333 | 0 | 13.6627 | 39.95
2021-07-15 20:30 | 44392.8542 | 0 | 13.0098 | 39.95
2021-07-15 21:00 | 44392.875 | 0 | 12.3534 | 39.95
2021-07-15 21:30 | 44392.8958 | 0 | 12.0705 | 39.95
2021-07-15 22:00 | 44392.9167 | 0 | 11.5957 | 39.95
2021-07-15 22:30 | 44392.9375 | 0 | 10.696 | 39.95
2021-07-15 23:00 | 44392.9583 | 0 | 9.9208 | 39.95
2021-07-15 23:30 | 44392.9792 | 0 | 9.3136 | 39.95
2021-07-16 | 44393 | 0 | 8.8011 | 39.95
2021-07-16 00:30 | 44393.0208 | 0 | 8.3884 | 39.95
2021-07-16 01:00 | 44393.0417 | 0 | 8.1334 | 39.95
2021-07-16 01:30 | 44393.0625 | 0 | 7.9985 | 39.95
2021-07-16 02:00 | 44393.0833 | 0 | 7.9885 | 39.95
2021-07-16 02:30 | 44393.1042 | 0 | 7.8356 | 39.95
2021-07-16 03:00 | 44393.125 | 0 | 7.8453 | 39.95
2021-07-16 03:30 | 44393.1458 | 0 | 8.1031 | 39.95
2021-07-16 04:00 | 44393.1667 | 0 | 8.2783 | 39.95
2021-07-16 04:30 | 44393.1875 | 0 | 8.5659 | 39.95
2021-07-16 05:00 | 44393.2083 | 0 | 9.2263 | 39.95
2021-07-16 05:30 | 44393.2292 | 0 | 10.2063 | 39.95
2021-07-16 06:00 | 44393.25 | 0 | 10.956 | 39.95
2021-07-16 06:30 | 44393.2708 | 0 | 11.851 | 39.95
2021-07-16 07:00 | 44393.2917 | 0 | 12.8708 | 39.95
2021-07-16 07:30 | 44393.3125 | 0 | 12.5706 | 39.95
2021-07-16 08:00 | 44393.3333 | 0 | 12.244 | 39.95
2021-07-16 08:30 | 44393.3542 | 0 | 11.8535 | 39.95
2021-07-16 09:00 | 44393.375 | 0 | 12.6734 | 39.95
2021-07-16 09:30 | 44393.3958 | 0 | 12.7133 | 39.95
2021-07-16 10:00 | 44393.4167 | 0 | 11.6745 | 39.95
2021-07-16 10:30 | 44393.4375 | 0 | 10.8392 | 39.95
2021-07-16 11:00 | 44393.4583 | 0 | 9.7431 | 39.95
2021-07-16 11:30 | 44393.4792 | 0 | 10.725 | 39.95
2021-07-16 12:00 | 44393.5 | 0 | 11.7372 | 39.95
2021-07-16 12:30 | 44393.5208 | 0 | 11.9411 | 39.95
2021-07-16 13:00 | 44393.5417 | 0 | 12.4305 | 39.95
2021-07-16 13:30 | 44393.5625 | 0 | 11.624 | 39.95
2021-07-16 14:00 | 44393.5833 | 0 | 12.1034 | 39.95
2021-07-16 14:30 | 44393.6042 | 0 | 11.7299 | 39.95
2021-07-16 15:00 | 44393.625 | 0 | 11.7066 | 39.95
2021-07-16 15:30 | 44393.6458 | 0 | 12.6818 | 39.95
2021-07-16 16:00 | 44393.6667 | 0 | 12.3639 | 39.95
2021-07-16 16:30 | 44393.6875 | 0 | 12.8568 | 39.95
2021-07-16 17:00 | 44393.7083 | 0 | 13.6475 | 39.95
2021-07-16 17:30 | 44393.7292 | 0 | 13.9718 | 39.95
2021-07-16 18:00 | 44393.75 | 0 | 13.9476 | 39.95
2021-07-16 18:30 | 44393.7708 | 0 | 13.9519 | 39.95
2021-07-16 19:00 | 44393.7917 | 0 | 13.9152 | 39.95
2021-07-16 19:30 | 44393.8125 | 0 | 13.8545 | 39.95
2021-07-16 20:00 | 44393.8333 | 0 | 13.5075 | 39.95
2021-07-16 20:30 | 44393.8542 | 0 | 13.0308 | 39.95
2021-07-16 21:00 | 44393.875 | 0 | 12.5789 | 39.95
2021-07-16 21:30 | 44393.8958 | 0 | 12.1858 | 39.95
2021-07-16 22:00 | 44393.9167 | 0 | 11.6564 | 39.95
2021-07-16 22:30 | 44393.9375 | 0 | 10.7599 | 39.95
2021-07-16 23:00 | 44393.9583 | 0 | 9.9628 | 39.95
2021-07-16 23:30 | 44393.9792 | 0 | 9.5435 | 39.95
2021-07-17 | 44394 | 0 | 8.9461 | 39.95
2021-07-17 00:30 | 44394.0208 | 0 | 8.3808 | 39.95
2021-07-17 01:00 | 44394.0417 | 0 | 8.0901 | 39.95
2021-07-17 01:30 | 44394.0625 | 0 | 8.1282 | 39.95
2021-07-17 02:00 | 44394.0833 | 0 | 7.8788 | 39.95
2021-07-17 02:30 | 44394.1042 | 0 | 7.7867 | 39.95
2021-07-17 03:00 | 44394.125 | 0 | 7.766 | 39.95
2021-07-17 03:30 | 44394.1458 | 0 | 7.738 | 39.95
2021-07-17 04:00 | 44394.1667 | 0 | 7.6741 | 39.95
2021-07-17 04:30 | 44394.1875 | 0 | 7.821 | 39.95
2021-07-17 05:00 | 44394.2083 | 0 | 8.0627 | 39.95
2021-07-17 05:30 | 44394.2292 | 0 | 8.5409 | 39.95
2021-07-17 06:00 | 44394.25 | 0 | 8.993 | 39.95
2021-07-17 06:30 | 44394.2708 | 0 | 9.6073 | 39.95
2021-07-17 07:00 | 44394.2917 | 0 | 10.0992 | 39.95
2021-07-17 07:30 | 44394.3125 | 0 | 9.946 | 39.95
2021-07-17 08:00 | 44394.3333 | 0 | 9.6891 | 39.95
2021-07-17 08:30 | 44394.3542 | 0 | 9.2296 | 39.95
2021-07-17 09:00 | 44394.375 | 0 | 8.7542 | 39.95
2021-07-17 09:30 | 44394.3958 | 0 | 8.2656 | 39.95
2021-07-17 10:00 | 44394.4167 | 0 | 7.6101 | 39.95
2021-07-17 10:30 | 44394.4375 | 0 | 7.1427 | 39.95
2021-07-17 11:00 | 44394.4583 | 0 | 6.6491 | 39.95
2021-07-17 11:30 | 44394.4792 | 0 | 6.4584 | 39.95
2021-07-17 12:00 | 44394.5 | 0 | 6.2923 | 39.95
2021-07-17 12:30 | 44394.5208 | 0 | 6.2554 | 39.95
2021-07-17 13:00 | 44394.5417 | 0 | 6.4639 | 39.95
2021-07-17 13:30 | 44394.5625 | 0 | 6.7004 | 39.95
2021-07-17 14:00 | 44394.5833 | 0 | 6.9864 | 39.95
2021-07-17 14:30 | 44394.6042 | 0 | 7.5098 | 39.95
2021-07-17 15:00 | 44394.625 | 0 | 8.2043 | 39.95
2021-07-17 15:30 | 44394.6458 | 0 | 8.8291 | 39.95
2021-07-17 16:00 | 44394.6667 | 0 | 9.642 | 39.95
2021-07-17 16:30 | 44394.6875 | 0 | 10.5073 | 39.95
2021-07-17 17:00 | 44394.7083 | 0 | 11.455 | 39.95
2021-07-17 17:30 | 44394.7292 | 0 | 12.022 | 39.95
2021-07-17 18:00 | 44394.75 | 0 | 12.1638 | 39.95
2021-07-17 18:30 | 44394.7708 | 0 | 12.348 | 39.95
2021-07-17 19:00 | 44394.7917 | 0 | 12.0876 | 39.95
2021-07-17 19:30 | 44394.8125 | 0 | 11.804 | 39.95
2021-07-17 20:00 | 44394.8333 | 0 | 11.56 | 39.95
2021-07-17 20:30 | 44394.8542 | 0 | 11.2522 | 39.95
2021-07-17 21:00 | 44394.875 | 0 | 10.8798 | 39.95
2021-07-17 21:30 | 44394.8958 | 0 | 10.6238 | 39.95
2021-07-17 22:00 | 44394.9167 | 0 | 10.3235 | 39.95
2021-07-17 22:30 | 44394.9375 | 0 | 9.664 | 39.95
2021-07-17 23:00 | 44394.9583 | 0 | 9.0784 | 39.95
2021-07-17 23:30 | 44394.9792 | 0 | 8.6851 | 39.95
2021-07-18 | 44395 | 0 | 8.1914 | 39.95
2021-07-18 00:30 | 44395.0208 | 0 | 7.7044 | 39.95
2021-07-18 01:00 | 44395.0417 | 0 | 7.4826 | 39.95
2021-07-18 01:30 | 44395.0625 | 0 | 7.3311 | 39.95
2021-07-18 02:00 | 44395.0833 | 0 | 7.2664 | 39.95
2021-07-18 02:30 | 44395.1042 | 0 | 7.1184 | 39.95
2021-07-18 03:00 | 44395.125 | 0 | 7.1877 | 39.95
2021-07-18 03:30 | 44395.1458 | 0 | 7.2713 | 39.95
2021-07-18 04:00 | 44395.1667 | 0 | 7.1854 | 39.95
2021-07-18 04:30 | 44395.1875 | 0 | 7.1464 | 39.95
2021-07-18 05:00 | 44395.2083 | 0 | 7.2959 | 39.95
2021-07-18 05:30 | 44395.2292 | 0 | 7.5144 | 39.95
2021-07-18 06:00 | 44395.25 | 0 | 7.9772 | 39.95
2021-07-18 06:30 | 44395.2708 | 0 | 8.1815 | 39.95
2021-07-18 07:00 | 44395.2917 | 0 | 8.3498 | 39.95
2021-07-18 07:30 | 44395.3125 | 0 | 8.6069 | 39.95
2021-07-18 08:00 | 44395.3333 | 0 | 8.4947 | 39.95
2021-07-18 08:30 | 44395.3542 | 0 | 8.2859 | 39.95
2021-07-18 09:00 | 44395.375 | 0 | 7.9094 | 39.95
2021-07-18 09:30 | 44395.3958 | 0 | 7.4932 | 39.95
2021-07-18 10:00 | 44395.4167 | 0 | 7.074 | 39.95
2021-07-18 10:30 | 44395.4375 | 0 | 6.6542 | 39.95
2021-07-18 11:00 | 44395.4583 | 0 | 6.3016 | 39.95
2021-07-18 11:30 | 44395.4792 | 0 | 5.9932 | 39.95
2021-07-18 12:00 | 44395.5 | 0 | 5.905 | 39.95
2021-07-18 12:30 | 44395.5208 | 0 | 5.8125 | 39.95
2021-07-18 13:00 | 44395.5417 | 0 | 5.7395 | 39.95
2021-07-18 13:30 | 44395.5625 | 0 | 5.9789 | 39.95
2021-07-18 14:00 | 44395.5833 | 0 | 6.4474 | 39.95
2021-07-18 14:30 | 44395.6042 | 0 | 7.1423 | 39.95
2021-07-18 15:00 | 44395.625 | 0 | 7.8071 | 39.95
2021-07-18 15:30 | 44395.6458 | 0 | 8.5824 | 39.95
2021-07-18 16:00 | 44395.6667 | 0 | 9.6016 | 39.95
2021-07-18 16:30 | 44395.6875 | 0 | 10.8119 | 39.95
2021-07-18 17:00 | 44395.7083 | 0 | 11.7877 | 39.95
2021-07-18 17:30 | 44395.7292 | 0 | 12.6847 | 39.95
2021-07-18 18:00 | 44395.75 | 0 | 13.1531 | 39.95
2021-07-18 18:30 | 44395.7708 | 0 | 13.1408 | 39.95
2021-07-18 19:00 | 44395.7917 | 0 | 12.9019 | 39.95
2021-07-18 19:30 | 44395.8125 | 0 | 12.7462 | 39.95
2021-07-18 20:00 | 44395.8333 | 0 | 12.4139 | 39.95
2021-07-18 20:30 | 44395.8542 | 0 | 11.968 | 39.95
2021-07-18 21:00 | 44395.875 | 0 | 11.3469 | 39.95
2021-07-18 21:30 | 44395.8958 | 0 | 10.7918 | 39.95
2021-07-18 22:00 | 44395.9167 | 0 | 10.1365 | 39.95
2021-07-18 22:30 | 44395.9375 | 0 | 9.1941 | 39.95
2021-07-18 23:00 | 44395.9583 | 0 | 8.5822 | 39.95
2021-07-18 23:30 | 44395.9792 | 0 | 8.1726 | 39.95
2021-07-19 | 44396 | 0 | 7.849 | 39.95
2021-07-19 00:30 | 44396.0208 | 0 | 7.5644 | 39.95
2021-07-19 01:00 | 44396.0417 | 0 | 7.3851 | 39.95
2021-07-19 01:30 | 44396.0625 | 0 | 7.3317 | 39.95
2021-07-19 02:00 | 44396.0833 | 0 | 7.2839 | 39.95
2021-07-19 02:30 | 44396.1042 | 0 | 7.23 | 39.95
2021-07-19 03:00 | 44396.125 | 0 | 7.2232 | 39.95
2021-07-19 03:30 | 44396.1458 | 0 | 7.5247 | 39.95
2021-07-19 04:00 | 44396.1667 | 0 | 7.8643 | 39.95
2021-07-19 04:30 | 44396.1875 | 0 | 8.1755 | 39.95
2021-07-19 05:00 | 44396.2083 | 0 | 9.0336 | 39.95
2021-07-19 05:30 | 44396.2292 | 0 | 10.0375 | 39.95
2021-07-19 06:00 | 44396.25 | 0 | 11.7654 | 39.95
2021-07-19 06:30 | 44396.2708 | 0 | 13.4281 | 39.95
2021-07-19 07:00 | 44396.2917 | 0 | 14.6577 | 39.95
2021-07-19 07:30 | 44396.3125 | 0 | 15.139 | 39.95
2021-07-19 08:00 | 44396.3333 | 0 | 13.5414 | 39.95
2021-07-19 08:30 | 44396.3542 | 0 | 13.0417 | 39.95
2021-07-19 09:00 | 44396.375 | 0 | 11.9138 | 39.95
2021-07-19 09:30 | 44396.3958 | 0 | 10.6154 | 39.95
2021-07-19 10:00 | 44396.4167 | 0 | 9.7453 | 39.95
2021-07-19 10:30 | 44396.4375 | 0 | 9.3181 | 39.95
2021-07-19 11:00 | 44396.4583 | 0 | 8.7043 | 39.95
2021-07-19 11:30 | 44396.4792 | 0 | 8.5016 | 39.95
2021-07-19 12:00 | 44396.5 | 0 | 8.3097 | 39.95
2021-07-19 12:30 | 44396.5208 | 0 | 8.1291 | 39.95
2021-07-19 13:00 | 44396.5417 | 0 | 8.2943 | 39.95
2021-07-19 13:30 | 44396.5625 | 0 | 8.6399 | 39.95
2021-07-19 14:00 | 44396.5833 | 0 | 9.2341 | 39.95
2021-07-19 14:30 | 44396.6042 | 0 | 10.1939 | 39.95
2021-07-19 15:00 | 44396.625 | 0 | 10.2546 | 39.95
2021-07-19 15:30 | 44396.6458 | 0 | 11.0838 | 39.95
2021-07-19 16:00 | 44396.6667 | 0 | 11.5228 | 39.95
2021-07-19 16:30 | 44396.6875 | 0 | 12.3546 | 39.95
2021-07-19 17:00 | 44396.7083 | 0 | 13.4095 | 39.95
2021-07-19 17:30 | 44396.7292 | 0 | 14.6006 | 39.95
2021-07-19 18:00 | 44396.75 | 0 | 15.0419 | 39.95
2021-07-19 18:30 | 44396.7708 | 0 | 15.5393 | 39.95
2021-07-19 19:00 | 44396.7917 | 0 | 15.0911 | 39.95
2021-07-19 19:30 | 44396.8125 | 0 | 14.8761 | 39.95
2021-07-19 20:00 | 44396.8333 | 0 | 14.49 | 39.95
2021-07-19 20:30 | 44396.8542 | 0 | 13.7818 | 39.95
2021-07-19 21:00 | 44396.875 | 0 | 13.214 | 39.95
2021-07-19 21:30 | 44396.8958 | 0 | 12.6053 | 39.95
2021-07-19 22:00 | 44396.9167 | 0 | 11.8004 | 39.95
2021-07-19 22:30 | 44396.9375 | 0 | 10.7537 | 39.95
2021-07-19 23:00 | 44396.9583 | 0 | 10.0387 | 39.95
2021-07-19 23:30 | 44396.9792 | 0 | 9.4691 | 39.95
2021-07-20 | 44397 | 0 | 8.8626 | 39.95
2021-07-20 00:30 | 44397.0208 | 0 | 8.5158 | 39.95
2021-07-20 01:00 | 44397.0417 | 0 | 8.4435 | 39.95
2021-07-20 01:30 | 44397.0625 | 0 | 8.1902 | 39.95
2021-07-20 02:00 | 44397.0833 | 0 | 8.1365 | 39.95
2021-07-20 02:30 | 44397.1042 | 0 | 7.9647 | 39.95
2021-07-20 03:00 | 44397.125 | 0 | 8.0083 | 39.95
2021-07-20 03:30 | 44397.1458 | 0 | 8.1692 | 39.95
2021-07-20 04:00 | 44397.1667 | 0 | 8.4438 | 39.95
2021-07-20 04:30 | 44397.1875 | 0 | 8.8954 | 39.95
2021-07-20 05:00 | 44397.2083 | 0 | 9.939 | 39.95
2021-07-20 05:30 | 44397.2292 | 0 | 11.1468 | 39.95
2021-07-20 06:00 | 44397.25 | 0 | 12.9205 | 39.95
2021-07-20 06:30 | 44397.2708 | 0 | 14.8708 | 39.95
2021-07-20 07:00 | 44397.2917 | 0 | 15.8081 | 39.95
2021-07-20 07:30 | 44397.3125 | 0 | 15.4031 | 39.95
2021-07-20 08:00 | 44397.3333 | 0 | 13.8103 | 39.95
2021-07-20 08:30 | 44397.3542 | 0 | 12.458 | 39.95
2021-07-20 09:00 | 44397.375 | 0 | 11.3602 | 39.95
2021-07-20 09:30 | 44397.3958 | 0 | 10.492 | 39.95
2021-07-20 10:00 | 44397.4167 | 0 | 9.8431 | 39.95
2021-07-20 10:30 | 44397.4375 | 0 | 9.3734 | 39.95
2021-07-20 11:00 | 44397.4583 | 0 | 8.9571 | 39.95
2021-07-20 11:30 | 44397.4792 | 0 | 8.623 | 39.95
2021-07-20 12:00 | 44397.5 | 0 | 8.4437 | 39.95
2021-07-20 12:30 | 44397.5208 | 0 | 8.6645 | 39.95
2021-07-20 13:00 | 44397.5417 | 0 | 8.5908 | 39.95
2021-07-20 13:30 | 44397.5625 | 0 | 8.8392 | 39.95
2021-07-20 14:00 | 44397.5833 | 0 | 9.1736 | 39.95
2021-07-20 14:30 | 44397.6042 | 0 | 9.9809 | 39.95
2021-07-20 15:00 | 44397.625 | 0 | 10.4775 | 39.95
2021-07-20 15:30 | 44397.6458 | 0 | 10.9581 | 39.95
2021-07-20 16:00 | 44397.6667 | 0 | 11.8767 | 39.95
2021-07-20 16:30 | 44397.6875 | 0 | 12.7702 | 39.95
2021-07-20 17:00 | 44397.7083 | 0 | 13.9872 | 39.95
2021-07-20 17:30 | 44397.7292 | 0 | 15.2569 | 39.95
2021-07-20 18:00 | 44397.75 | 0 | 15.7245 | 39.95
2021-07-20 18:30 | 44397.7708 | 0 | 16.1087 | 39.95
2021-07-20 19:00 | 44397.7917 | 0 | 16.0503 | 39.95
2021-07-20 19:30 | 44397.8125 | 0 | 15.7371 | 39.95
2021-07-20 20:00 | 44397.8333 | 0 | 15.4087 | 39.95
2021-07-20 20:30 | 44397.8542 | 0 | 14.619 | 39.95
2021-07-20 21:00 | 44397.875 | 0 | 14.054 | 39.95
2021-07-20 21:30 | 44397.8958 | 0 | 13.1711 | 39.95
2021-07-20 22:00 | 44397.9167 | 0 | 12.3426 | 39.95
2021-07-20 22:30 | 44397.9375 | 0 | 11.1359 | 39.95
2021-07-20 23:00 | 44397.9583 | 0 | 10.3839 | 39.95
2021-07-20 23:30 | 44397.9792 | 0 | 9.7782 | 39.95
2021-07-21 | 44398 | 0 | 9.077 | 39.95
2021-07-21 00:30 | 44398.0208 | 0 | 8.8007 | 39.95
2021-07-21 01:00 | 44398.0417 | 0 | 8.6132 | 39.95
2021-07-21 01:30 | 44398.0625 | 0 | 8.3872 | 39.95
2021-07-21 02:00 | 44398.0833 | 0 | 8.2943 | 39.95
2021-07-21 02:30 | 44398.1042 | 0 | 8.1706 | 39.95
2021-07-21 03:00 | 44398.125 | 0 | 8.2597 | 39.95
2021-07-21 03:30 | 44398.1458 | 0 | 8.3092 | 39.95
2021-07-21 04:00 | 44398.1667 | 0 | 8.4966 | 39.95
2021-07-21 04:30 | 44398.1875 | 0 | 9.1073 | 39.95
2021-07-21 05:00 | 44398.2083 | 0 | 9.9128 | 39.95
2021-07-21 05:30 | 44398.2292 | 0 | 11.2353 | 39.95
2021-07-21 06:00 | 44398.25 | 0 | 12.7512 | 39.95
2021-07-21 06:30 | 44398.2708 | 0 | 14.1355 | 39.95
2021-07-21 07:00 | 44398.2917 | 0 | 15.5193 | 39.95
2021-07-21 07:30 | 44398.3125 | 0 | 15.1886 | 39.95
2021-07-21 08:00 | 44398.3333 | 0 | 14.1735 | 39.95
2021-07-21 08:30 | 44398.3542 | 0 | 12.5714 | 39.95
2021-07-21 09:00 | 44398.375 | 0 | 11.5258 | 39.95
2021-07-21 09:30 | 44398.3958 | 0 | 10.9729 | 39.95
2021-07-21 10:00 | 44398.4167 | 0 | 10.4284 | 39.95
2021-07-21 10:30 | 44398.4375 | 0 | 10.1965 | 39.95
2021-07-21 11:00 | 44398.4583 | 0 | 9.6487 | 39.95
2021-07-21 11:30 | 44398.4792 | 0 | 9.437 | 39.95
2021-07-21 12:00 | 44398.5 | 0 | 9.3702 | 39.95
2021-07-21 12:30 | 44398.5208 | 0 | 9.3337 | 39.95
2021-07-21 13:00 | 44398.5417 | 0 | 9.3697 | 39.95
2021-07-21 13:30 | 44398.5625 | 0 | 10.1164 | 39.95
2021-07-21 14:00 | 44398.5833 | 0 | 10.2224 | 39.95
2021-07-21 14:30 | 44398.6042 | 0 | 10.5221 | 39.95
2021-07-21 15:00 | 44398.625 | 0 | 10.9647 | 39.95
2021-07-21 15:30 | 44398.6458 | 0 | 11.7534 | 39.95
2021-07-21 16:00 | 44398.6667 | 0 | 12.3083 | 39.95
2021-07-21 16:30 | 44398.6875 | 0 | 13.6097 | 39.95
2021-07-21 17:00 | 44398.7083 | 0 | 15.1548 | 39.95
2021-07-21 17:30 | 44398.7292 | 0 | 16.5671 | 39.95
2021-07-21 18:00 | 44398.75 | 0 | 17.2071 | 39.95
2021-07-21 18:30 | 44398.7708 | 0 | 17.7574 | 39.95
2021-07-21 19:00 | 44398.7917 | 0 | 17.3657 | 39.95
2021-07-21 19:30 | 44398.8125 | 0 | 17.4493 | 39.95
2021-07-21 20:00 | 44398.8333 | 0 | 17.1416 | 39.95
2021-07-21 20:30 | 44398.8542 | 0 | 16.3642 | 39.95
2021-07-21 21:00 | 44398.875 | 0 | 15.4145 | 39.95
2021-07-21 21:30 | 44398.8958 | 0 | 14.5497 | 39.95
2021-07-21 22:00 | 44398.9167 | 0 | 13.6217 | 39.95
2021-07-21 22:30 | 44398.9375 | 0 | 12.3506 | 39.95
2021-07-21 23:00 | 44398.9583 | 0 | 11.214 | 39.95
2021-07-21 23:30 | 44398.9792 | 0 | 10.3947 | 39.95
2021-07-22 | 44399 | 0 | 9.7178 | 39.95
2021-07-22 00:30 | 44399.0208 | 0 | 9.2376 | 39.95
2021-07-22 01:00 | 44399.0417 | 0 | 9.0252 | 39.95
2021-07-22 01:30 | 44399.0625 | 0 | 8.7057 | 39.95
2021-07-22 02:00 | 44399.0833 | 0 | 8.6608 | 39.95
2021-07-22 02:30 | 44399.1042 | 0 | 8.5983 | 39.95
2021-07-22 03:00 | 44399.125 | 0 | 8.6393 | 39.95
2021-07-22 03:30 | 44399.1458 | 0 | 8.7527 | 39.95
2021-07-22 04:00 | 44399.1667 | 0 | 9.0908 | 39.95
2021-07-22 04:30 | 44399.1875 | 0 | 9.608 | 39.95
2021-07-22 05:00 | 44399.2083 | 0 | 10.8475 | 39.95
2021-07-22 05:30 | 44399.2292 | 0 | 12.0639 | 39.95
2021-07-22 06:00 | 44399.25 | 0 | 14.0744 | 39.95
2021-07-22 06:30 | 44399.2708 | 0 | 15.7694 | 39.95
2021-07-22 07:00 | 44399.2917 | 0 | 16.9596 | 39.95
2021-07-22 07:30 | 44399.3125 | 0 | 16.552 | 39.95
2021-07-22 08:00 | 44399.3333 | 0 | 15.4071 | 39.95
2021-07-22 08:30 | 44399.3542 | 0 | 26.4022 | 39.95
2021-07-22 09:00 | 44399.375 | 0 | 24.621 | 39.95
2021-07-22 09:30 | 44399.3958 | 0 | 22.6726 | 39.95
2021-07-22 10:00 | 44399.4167 | 0 | 20.6892 | 39.95
2021-07-22 10:30 | 44399.4375 | 0 | 19.6174 | 39.95
2021-07-22 11:00 | 44399.4583 | 0 | 19.0127 | 39.95
2021-07-22 11:30 | 44399.4792 | 0 | 18.2385 | 39.95
2021-07-22 12:00 | 44399.5 | 0 | 17.4467 | 39.95
2021-07-22 12:30 | 44399.5208 | 0 | 17.4165 | 39.95
2021-07-22 13:00 | 44399.5417 | 0 | 17.3552 | 39.95
2021-07-22 13:30 | 44399.5625 | 0 | 17.7496 | 39.95
2021-07-22 14:00 | 44399.5833 | 0 | 9.7375 | 39.95
2021-07-22 14:30 | 44399.6042 | 0 | 10.1167 | 39.95
2021-07-22 15:00 | 44399.625 | 0 | 10.63 | 39.95
2021-07-22 15:30 | 44399.6458 | 0 | 11.215 | 39.95
2021-07-22 16:00 | 44399.6667 | 0 | 12.1566 | 39.95
2021-07-22 16:30 | 44399.6875 | 0 | 13.1616 | 39.95
2021-07-22 17:00 | 44399.7083 | 0 | 14.3928 | 39.95
2021-07-22 17:30 | 44399.7292 | 0 | 15.5606 | 39.95
2021-07-22 18:00 | 44399.75 | 0 | 16.1687 | 39.95
2021-07-22 18:30 | 44399.7708 | 0 | 16.5629 | 39.95
2021-07-22 19:00 | 44399.7917 | 0 | 16.621 | 39.95
2021-07-22 19:30 | 44399.8125 | 0 | 16.5457 | 39.95
2021-07-22 20:00 | 44399.8333 | 0 | 16.3171 | 39.95
2021-07-22 20:30 | 44399.8542 | 0 | 15.5287 | 39.95
2021-07-22 21:00 | 44399.875 | 0 | 14.6625 | 39.95
2021-07-22 21:30 | 44399.8958 | 0 | 13.8969 | 39.95
2021-07-22 22:00 | 44399.9167 | 0 | 13.0692 | 39.95
2021-07-22 22:30 | 44399.9375 | 0 | 11.7802 | 39.95
2021-07-22 23:00 | 44399.9583 | 0 | 10.8597 | 39.95
2021-07-22 23:30 | 44399.9792 | 0 | 10.199 | 39.95
2021-07-23 | 44400 | 0 | 9.4971 | 39.95
2021-07-23 00:30 | 44400.0208 | 0 | 9.0052 | 39.95
2021-07-23 01:00 | 44400.0417 | 0 | 8.7438 | 39.95
2021-07-23 01:30 | 44400.0625 | 0 | 8.4876 | 39.95
2021-07-23 02:00 | 44400.0833 | 0 | 8.5068 | 39.95
2021-07-23 02:30 | 44400.1042 | 0 | 8.3943 | 39.95
2021-07-23 03:00 | 44400.125 | 0 | 8.4166 | 39.95
2021-07-23 03:30 | 44400.1458 | 0 | 8.5965 | 39.95
2021-07-23 04:00 | 44400.1667 | 0 | 8.6948 | 39.95
2021-07-23 04:30 | 44400.1875 | 0 | 9.3324 | 39.95
2021-07-23 05:00 | 44400.2083 | 0 | 10.1308 | 39.95
2021-07-23 05:30 | 44400.2292 | 0 | 11.228 | 39.95
2021-07-23 06:00 | 44400.25 | 0 | 12.6615 | 39.95
2021-07-23 06:30 | 44400.2708 | 0 | 14.5111 | 39.95
2021-07-23 07:00 | 44400.2917 | 0 | 15.5981 | 39.95
2021-07-23 07:30 | 44400.3125 | 0 | 15.7473 | 39.95
2021-07-23 08:00 | 44400.3333 | 0 | 15.5349 | 39.95
2021-07-23 08:30 | 44400.3542 | 0 | 14.5851 | 39.95
2021-07-23 09:00 | 44400.375 | 0 | 14.2137 | 39.95
2021-07-23 09:30 | 44400.3958 | 0 | 14.4535 | 39.95
2021-07-23 10:00 | 44400.4167 | 0 | 13.509 | 39.95
2021-07-23 10:30 | 44400.4375 | 0 | 12.401 | 39.95
2021-07-23 11:00 | 44400.4583 | 0 | 11.9519 | 39.95
2021-07-23 11:30 | 44400.4792 | 0 | 10.5973 | 39.95
2021-07-23 12:00 | 44400.5 | 0 | 10.8611 | 39.95
2021-07-23 12:30 | 44400.5208 | 0 | 12.0074 | 39.95
2021-07-23 13:00 | 44400.5417 | 0 | 12.594 | 39.95
2021-07-23 13:30 | 44400.5625 | 0 | 12.362 | 39.95
2021-07-23 14:00 | 44400.5833 | 0 | 12.5984 | 39.95
2021-07-23 14:30 | 44400.6042 | 0 | 12.693 | 39.95
2021-07-23 15:00 | 44400.625 | 0 | 13.1993 | 39.95
2021-07-23 15:30 | 44400.6458 | 0 | 13.2416 | 39.95
2021-07-23 16:00 | 44400.6667 | 0 | 13.8066 | 39.95
2021-07-23 16:30 | 44400.6875 | 0 | 14.4924 | 39.95
2021-07-23 17:00 | 44400.7083 | 0 | 15.0004 | 39.95
2021-07-23 17:30 | 44400.7292 | 0 | 15.4647 | 39.95
2021-07-23 18:00 | 44400.75 | 0 | 15.6241 | 39.95
2021-07-23 18:30 | 44400.7708 | 0 | 15.7978 | 39.95
2021-07-23 19:00 | 44400.7917 | 0 | 15.4576 | 39.95
2021-07-23 19:30 | 44400.8125 | 0 | 15.2277 | 39.95
2021-07-23 20:00 | 44400.8333 | 0 | 15.1114 | 39.95
2021-07-23 20:30 | 44400.8542 | 0 | 14.5191 | 39.95
2021-07-23 21:00 | 44400.875 | 0 | 13.746 | 39.95
2021-07-23 21:30 | 44400.8958 | 0 | 13.183 | 39.95
2021-07-23 22:00 | 44400.9167 | 0 | 12.4321 | 39.95
2021-07-23 22:30 | 44400.9375 | 0 | 11.5007 | 39.95
2021-07-23 23:00 | 44400.9583 | 0 | 10.6431 | 39.95
2021-07-23 23:30 | 44400.9792 | 0 | 9.9686 | 39.95
2021-07-24 | 44401 | 0 | 9.2837 | 39.95
2021-07-24 00:30 | 44401.0208 | 0 | 8.8422 | 39.95
2021-07-24 01:00 | 44401.0417 | 0 | 8.4272 | 39.95
2021-07-24 01:30 | 44401.0625 | 0 | 8.2592 | 39.95
2021-07-24 02:00 | 44401.0833 | 0 | 8.1616 | 39.95
2021-07-24 02:30 | 44401.1042 | 0 | 8.001 | 39.95
2021-07-24 03:00 | 44401.125 | 0 | 8.0174 | 39.95
2021-07-24 03:30 | 44401.1458 | 0 | 8.0723 | 39.95
2021-07-24 04:00 | 44401.1667 | 0 | 7.9434 | 39.95
2021-07-24 04:30 | 44401.1875 | 0 | 8.0072 | 39.95
2021-07-24 05:00 | 44401.2083 | 0 | 8.3272 | 39.95
2021-07-24 05:30 | 44401.2292 | 0 | 8.6568 | 39.95
2021-07-24 06:00 | 44401.25 | 0 | 9.1068 | 39.95
2021-07-24 06:30 | 44401.2708 | 0 | 9.6759 | 39.95
2021-07-24 07:00 | 44401.2917 | 0 | 10.5256 | 39.95
2021-07-24 07:30 | 44401.3125 | 0 | 10.724 | 39.95
2021-07-24 08:00 | 44401.3333 | 0 | 10.6543 | 39.95
2021-07-24 08:30 | 44401.3542 | 0 | 9.6329 | 39.95
2021-07-24 09:00 | 44401.375 | 0 | 8.8603 | 39.95
2021-07-24 09:30 | 44401.3958 | 0 | 8.303 | 39.95
2021-07-24 10:00 | 44401.4167 | 0 | 7.6334 | 39.95
2021-07-24 10:30 | 44401.4375 | 0 | 7.3313 | 39.95
2021-07-24 11:00 | 44401.4583 | 0 | 6.8266 | 39.95
2021-07-24 11:30 | 44401.4792 | 0 | 7.2638 | 39.95
2021-07-24 12:00 | 44401.5 | 0 | 6.1876 | 39.95
2021-07-24 12:30 | 44401.5208 | 0 | 6.1156 | 39.95
2021-07-24 13:00 | 44401.5417 | 0 | 6.3432 | 39.95
2021-07-24 13:30 | 44401.5625 | 0 | 6.6098 | 39.95
2021-07-24 14:00 | 44401.5833 | 0 | 7.1221 | 39.95
2021-07-24 14:30 | 44401.6042 | 0 | 7.485 | 39.95
2021-07-24 15:00 | 44401.625 | 0 | 8.1702 | 39.95
2021-07-24 15:30 | 44401.6458 | 0 | 8.9286 | 39.95
2021-07-24 16:00 | 44401.6667 | 0 | 9.6102 | 39.95
2021-07-24 16:30 | 44401.6875 | 0 | 10.4447 | 39.95
2021-07-24 17:00 | 44401.7083 | 0 | 11.2227 | 39.95
2021-07-24 17:30 | 44401.7292 | 0 | 11.9544 | 39.95
2021-07-24 18:00 | 44401.75 | 0 | 12.0624 | 39.95
2021-07-24 18:30 | 44401.7708 | 0 | 12.3631 | 39.95
2021-07-24 19:00 | 44401.7917 | 0 | 12.0592 | 39.95
2021-07-24 19:30 | 44401.8125 | 0 | 11.926 | 39.95
2021-07-24 20:00 | 44401.8333 | 0 | 11.8129 | 39.95
2021-07-24 20:30 | 44401.8542 | 0 | 11.3492 | 39.95
2021-07-24 21:00 | 44401.875 | 0 | 11.0226 | 39.95
2021-07-24 21:30 | 44401.8958 | 0 | 10.6805 | 39.95
2021-07-24 22:00 | 44401.9167 | 0 | 10.364 | 39.95
2021-07-24 22:30 | 44401.9375 | 0 | 9.8213 | 39.95
2021-07-24 23:00 | 44401.9583 | 0 | 9.1175 | 39.95
2021-07-24 23:30 | 44401.9792 | 0 | 8.6369 | 39.95
2021-07-25 | 44402 | 0 | 8.0939 | 39.95
2021-07-25 00:30 | 44402.0208 | 0 | 7.7757 | 39.95
2021-07-25 01:00 | 44402.0417 | 0 | 7.6168 | 39.95
2021-07-25 01:30 | 44402.0625 | 0 | 7.4474 | 39.95
2021-07-25 02:00 | 44402.0833 | 0 | 7.2836 | 39.95
2021-07-25 02:30 | 44402.1042 | 0 | 7.2801 | 39.95
2021-07-25 03:00 | 44402.125 | 0 | 7.1425 | 39.95
2021-07-25 03:30 | 44402.1458 | 0 | 7.2726 | 39.95
2021-07-25 04:00 | 44402.1667 | 0 | 7.2123 | 39.95
2021-07-25 04:30 | 44402.1875 | 0 | 7.264 | 39.95
2021-07-25 05:00 | 44402.2083 | 0 | 7.3466 | 39.95
2021-07-25 05:30 | 44402.2292 | 0 | 7.633 | 39.95
2021-07-25 06:00 | 44402.25 | 0 | 7.9792 | 39.95
2021-07-25 06:30 | 44402.2708 | 0 | 8.3398 | 39.95
2021-07-25 07:00 | 44402.2917 | 0 | 8.9322 | 39.95
2021-07-25 07:30 | 44402.3125 | 0 | 8.7912 | 39.95
2021-07-25 08:00 | 44402.3333 | 0 | 8.675 | 39.95
2021-07-25 08:30 | 44402.3542 | 0 | 8.3666 | 39.95
2021-07-25 09:00 | 44402.375 | 0 | 8.05 | 39.95
2021-07-25 09:30 | 44402.3958 | 0 | 7.5863 | 39.95
2021-07-25 10:00 | 44402.4167 | 0 | 7.0923 | 39.95
2021-07-25 10:30 | 44402.4375 | 0 | 6.7771 | 39.95
2021-07-25 11:00 | 44402.4583 | 0 | 6.2608 | 39.95
2021-07-25 11:30 | 44402.4792 | 0 | 6.053 | 39.95
2021-07-25 12:00 | 44402.5 | 0 | 5.9796 | 39.95
2021-07-25 12:30 | 44402.5208 | 0 | 5.91 | 39.95
2021-07-25 13:00 | 44402.5417 | 0 | 5.9318 | 39.95
2021-07-25 13:30 | 44402.5625 | 0 | 6.1789 | 39.95
2021-07-25 14:00 | 44402.5833 | 0 | 6.7315 | 39.95
2021-07-25 14:30 | 44402.6042 | 0 | 7.2459 | 39.95
2021-07-25 15:00 | 44402.625 | 0 | 7.9297 | 39.95
2021-07-25 15:30 | 44402.6458 | 0 | 8.6442 | 39.95
2021-07-25 16:00 | 44402.6667 | 0 | 9.6938 | 39.95
2021-07-25 16:30 | 44402.6875 | 0 | 10.8042 | 39.95
2021-07-25 17:00 | 44402.7083 | 0 | 11.9105 | 39.95
2021-07-25 17:30 | 44402.7292 | 0 | 12.8339 | 39.95
2021-07-25 18:00 | 44402.75 | 0 | 13.3662 | 39.95
2021-07-25 18:30 | 44402.7708 | 0 | 13.6015 | 39.95
2021-07-25 19:00 | 44402.7917 | 0 | 13.1801 | 39.95
2021-07-25 19:30 | 44402.8125 | 0 | 13.0737 | 39.95
2021-07-25 20:00 | 44402.8333 | 0 | 12.7802 | 39.95
2021-07-25 20:30 | 44402.8542 | 0 | 12.392 | 39.95
2021-07-25 21:00 | 44402.875 | 0 | 11.6036 | 39.95
2021-07-25 21:30 | 44402.8958 | 0 | 11.1914 | 39.95
2021-07-25 22:00 | 44402.9167 | 0 | 10.402 | 39.95
2021-07-25 22:30 | 44402.9375 | 0 | 9.6116 | 39.95
2021-07-25 23:00 | 44402.9583 | 0 | 8.9384 | 39.95
2021-07-25 23:30 | 44402.9792 | 0 | 8.3892 | 39.95
2021-07-26 | 44403 | 0 | 7.9955 | 39.95
2021-07-26 00:30 | 44403.0208 | 0 | 7.7698 | 39.95
2021-07-26 01:00 | 44403.0417 | 0 | 7.521 | 39.95
2021-07-26 01:30 | 44403.0625 | 0 | 7.4681 | 39.95
2021-07-26 02:00 | 44403.0833 | 0 | 7.5065 | 39.95
2021-07-26 02:30 | 44403.1042 | 0 | 7.5112 | 39.95
2021-07-26 03:00 | 44403.125 | 0 | 7.499 | 39.95
2021-07-26 03:30 | 44403.1458 | 0 | 7.8015 | 39.95
2021-07-26 04:00 | 44403.1667 | 0 | 7.9901 | 39.95
2021-07-26 04:30 | 44403.1875 | 0 | 8.3827 | 39.95
2021-07-26 05:00 | 44403.2083 | 0 | 9.361 | 39.95
2021-07-26 05:30 | 44403.2292 | 0 | 10.5014 | 39.95
2021-07-26 06:00 | 44403.25 | 0 | 11.9949 | 39.95
2021-07-26 06:30 | 44403.2708 | 0 | 14.0923 | 39.95
2021-07-26 07:00 | 44403.2917 | 0 | 15.3289 | 39.95
2021-07-26 07:30 | 44403.3125 | 0 | 14.7177 | 39.95
2021-07-26 08:00 | 44403.3333 | 0 | 13.1904 | 39.95
2021-07-26 08:30 | 44403.3542 | 0 | 11.922 | 39.95
2021-07-26 09:00 | 44403.375 | 0 | 10.8569 | 39.95
2021-07-26 09:30 | 44403.3958 | 0 | 10.4534 | 39.95
2021-07-26 10:00 | 44403.4167 | 0 | 9.4998 | 39.95
2021-07-26 10:30 | 44403.4375 | 0 | 9.3343 | 39.95
2021-07-26 11:00 | 44403.4583 | 0 | 8.9253 | 39.95
2021-07-26 11:30 | 44403.4792 | 0 | 8.6439 | 39.95
2021-07-26 12:00 | 44403.5 | 0 | 8.4223 | 39.95
2021-07-26 12:30 | 44403.5208 | 0 | 9.6598 | 39.95
2021-07-26 13:00 | 44403.5417 | 0 | 10.6324 | 39.95
2021-07-26 13:30 | 44403.5625 | 0 | 8.9605 | 39.95
2021-07-26 14:00 | 44403.5833 | 0 | 9.5925 | 39.95
2021-07-26 14:30 | 44403.6042 | 0 | 9.4271 | 39.95
2021-07-26 15:00 | 44403.625 | 0 | 9.7662 | 39.95
2021-07-26 15:30 | 44403.6458 | 0 | 10.7243 | 39.95
2021-07-26 16:00 | 44403.6667 | 0 | 11.1513 | 39.95
2021-07-26 16:30 | 44403.6875 | 0 | 12.5373 | 39.95
2021-07-26 17:00 | 44403.7083 | 0 | 13.4398 | 39.95
2021-07-26 17:30 | 44403.7292 | 0 | 14.5089 | 39.95
2021-07-26 18:00 | 44403.75 | 0 | 15.067 | 39.95
2021-07-26 18:30 | 44403.7708 | 0 | 15.3598 | 39.95
2021-07-26 19:00 | 44403.7917 | 0 | 15.1486 | 39.95
2021-07-26 19:30 | 44403.8125 | 0 | 15.0119 | 39.95
2021-07-26 20:00 | 44403.8333 | 0 | 14.6465 | 39.95
2021-07-26 20:30 | 44403.8542 | 0 | 14.0621 | 39.95
2021-07-26 21:00 | 44403.875 | 0 | 13.1701 | 39.95
2021-07-26 21:30 | 44403.8958 | 0 | 12.6656 | 39.95
2021-07-26 22:00 | 44403.9167 | 0 | 12.0414 | 39.95
2021-07-26 22:30 | 44403.9375 | 0 | 10.9723 | 39.95
2021-07-26 23:00 | 44403.9583 | 0 | 10.1734 | 39.95
2021-07-26 23:30 | 44403.9792 | 0 | 9.5621 | 39.95
2021-07-27 | 44404 | 0 | 8.9779 | 39.95
2021-07-27 00:30 | 44404.0208 | 0 | 8.5822 | 39.95
2021-07-27 01:00 | 44404.0417 | 0 | 8.3779 | 39.95
2021-07-27 01:30 | 44404.0625 | 0 | 8.2224 | 39.95
2021-07-27 02:00 | 44404.0833 | 0 | 8.1734 | 39.95
2021-07-27 02:30 | 44404.1042 | 0 | 8.0993 | 39.95
2021-07-27 03:00 | 44404.125 | 0 | 8.0982 | 39.95
2021-07-27 03:30 | 44404.1458 | 0 | 8.3488 | 39.95
2021-07-27 04:00 | 44404.1667 | 0 | 8.6395 | 39.95
2021-07-27 04:30 | 44404.1875 | 0 | 9.1407 | 39.95
2021-07-27 05:00 | 44404.2083 | 0 | 10.2071 | 39.95
2021-07-27 05:30 | 44404.2292 | 0 | 11.2437 | 39.95
2021-07-27 06:00 | 44404.25 | 0 | 12.8263 | 39.95
2021-07-27 06:30 | 44404.2708 | 0 | 14.9793 | 39.95
2021-07-27 07:00 | 44404.2917 | 0 | 15.8724 | 39.95
2021-07-27 07:30 | 44404.3125 | 0 | 15.219 | 39.95
2021-07-27 08:00 | 44404.3333 | 0 | 14.1296 | 39.95
2021-07-27 08:30 | 44404.3542 | 0 | 12.6968 | 39.95
2021-07-27 09:00 | 44404.375 | 0 | 11.4798 | 39.95
2021-07-27 09:30 | 44404.3958 | 0 | 10.8042 | 39.95
2021-07-27 10:00 | 44404.4167 | 0 | 9.8961 | 39.95
2021-07-27 10:30 | 44404.4375 | 0 | 9.4663 | 39.95
2021-07-27 11:00 | 44404.4583 | 0 | 9.0213 | 39.95
2021-07-27 11:30 | 44404.4792 | 0 | 8.6538 | 39.95
2021-07-27 12:00 | 44404.5 | 0 | 8.5217 | 39.95
2021-07-27 12:30 | 44404.5208 | 0 | 8.5295 | 39.95
2021-07-27 13:00 | 44404.5417 | 0 | 8.475 | 39.95
2021-07-27 13:30 | 44404.5625 | 0 | 8.6855 | 39.95
2021-07-27 14:00 | 44404.5833 | 0 | 9.1461 | 39.95
2021-07-27 14:30 | 44404.6042 | 0 | 9.7536 | 39.95
2021-07-27 15:00 | 44404.625 | 0 | 10.1967 | 39.95
2021-07-27 15:30 | 44404.6458 | 0 | 10.8825 | 39.95
2021-07-27 16:00 | 44404.6667 | 0 | 11.5894 | 39.95
2021-07-27 16:30 | 44404.6875 | 0 | 12.3468 | 39.95
2021-07-27 17:00 | 44404.7083 | 0 | 13.2476 | 39.95
2021-07-27 17:30 | 44404.7292 | 0 | 14.2081 | 39.95
2021-07-27 18:00 | 44404.75 | 0 | 14.4955 | 39.95
2021-07-27 18:30 | 44404.7708 | 0 | 14.9528 | 39.95
2021-07-27 19:00 | 44404.7917 | 0 | 14.7225 | 39.95
2021-07-27 19:30 | 44404.8125 | 0 | 14.5045 | 39.95
2021-07-27 20:00 | 44404.8333 | 0 | 14.0483 | 39.95
2021-07-27 20:30 | 44404.8542 | 0 | 13.7774 | 39.95
2021-07-27 21:00 | 44404.875 | 0 | 12.967 | 39.95
2021-07-27 21:30 | 44404.8958 | 0 | 12.5498 | 39.95
2021-07-27 22:00 | 44404.9167 | 0 | 11.7832 | 39.95
2021-07-27 22:30 | 44404.9375 | 0 | 10.8159 | 39.95
2021-07-27 23:00 | 44404.9583 | 0 | 10.0599 | 39.95
2021-07-27 23:30 | 44404.9792 | 0 | 9.5443 | 39.95
2021-07-28 | 44405 | 0 | 9.0491 | 39.95
2021-07-28 00:30 | 44405.0208 | 0 | 8.6745 | 39.95
2021-07-28 01:00 | 44405.0417 | 0 | 8.3448 | 39.95
2021-07-28 01:30 | 44405.0625 | 0 | 8.2463 | 39.95
2021-07-28 02:00 | 44405.0833 | 0 | 8.1076 | 39.95
2021-07-28 02:30 | 44405.1042 | 0 | 8.0738 | 39.95
2021-07-28 03:00 | 44405.125 | 0 | 8.1106 | 39.95
2021-07-28 03:30 | 44405.1458 | 0 | 8.2541 | 39.95
2021-07-28 04:00 | 44405.1667 | 0 | 8.4162 | 39.95
2021-07-28 04:30 | 44405.1875 | 0 | 8.869 | 39.95
2021-07-28 05:00 | 44405.2083 | 0 | 9.6242 | 39.95
2021-07-28 05:30 | 44405.2292 | 0 | 10.7717 | 39.95
2021-07-28 06:00 | 44405.25 | 0 | 12.3731 | 39.95
2021-07-28 06:30 | 44405.2708 | 0 | 13.7504 | 39.95
2021-07-28 07:00 | 44405.2917 | 0 | 14.7407 | 39.95
2021-07-28 07:30 | 44405.3125 | 0 | 13.9778 | 39.95
2021-07-28 08:00 | 44405.3333 | 0 | 13.4402 | 39.95
2021-07-28 08:30 | 44405.3542 | 0 | 11.942 | 39.95
2021-07-28 09:00 | 44405.375 | 0 | 10.9892 | 39.95
2021-07-28 09:30 | 44405.3958 | 0 | 10.1296 | 39.95
2021-07-28 10:00 | 44405.4167 | 0 | 9.5193 | 39.95
2021-07-28 10:30 | 44405.4375 | 0 | 9.0932 | 39.95
2021-07-28 11:00 | 44405.4583 | 0 | 8.6574 | 39.95
2021-07-28 11:30 | 44405.4792 | 0 | 8.3993 | 39.95
2021-07-28 12:00 | 44405.5 | 0 | 8.7691 | 39.95
2021-07-28 12:30 | 44405.5208 | 0 | 9.1442 | 39.95
2021-07-28 13:00 | 44405.5417 | 0 | 8.8093 | 39.95
2021-07-28 13:30 | 44405.5625 | 0 | 9.0447 | 39.95
2021-07-28 14:00 | 44405.5833 | 0 | 9.6357 | 39.95
2021-07-28 14:30 | 44405.6042 | 0 | 10.0485 | 39.95
2021-07-28 15:00 | 44405.625 | 0 | 10.4864 | 39.95
2021-07-28 15:30 | 44405.6458 | 0 | 11.1533 | 39.95
2021-07-28 16:00 | 44405.6667 | 0 | 11.5814 | 39.95
2021-07-28 16:30 | 44405.6875 | 0 | 12.3336 | 39.95
2021-07-28 17:00 | 44405.7083 | 0 | 13.0183 | 39.95
2021-07-28 17:30 | 44405.7292 | 0 | 13.8633 | 39.95
2021-07-28 18:00 | 44405.75 | 0 | 14.1754 | 39.95
2021-07-28 18:30 | 44405.7708 | 0 | 14.5075 | 39.95
2021-07-28 19:00 | 44405.7917 | 0 | 14.056 | 39.95
2021-07-28 19:30 | 44405.8125 | 0 | 13.9674 | 39.95
2021-07-28 20:00 | 44405.8333 | 0 | 13.6364 | 39.95
2021-07-28 20:30 | 44405.8542 | 0 | 13.1562 | 39.95
2021-07-28 21:00 | 44405.875 | 0 | 12.6366 | 39.95
2021-07-28 21:30 | 44405.8958 | 0 | 12.105 | 39.95
2021-07-28 22:00 | 44405.9167 | 0 | 11.2575 | 39.95
2021-07-28 22:30 | 44405.9375 | 0 | 10.565 | 39.95
2021-07-28 23:00 | 44405.9583 | 0 | 9.775 | 39.95
2021-07-28 23:30 | 44405.9792 | 0 | 9.2801 | 39.95
2021-07-29 | 44406 | 0 | 8.7141 | 39.95
2021-07-29 00:30 | 44406.0208 | 0 | 8.3728 | 39.95
2021-07-29 01:00 | 44406.0417 | 0 | 8.2375 | 39.95
2021-07-29 01:30 | 44406.0625 | 0 | 8.0047 | 39.95
2021-07-29 02:00 | 44406.0833 | 0 | 7.9673 | 39.95
2021-07-29 02:30 | 44406.1042 | 0 | 7.9148 | 39.95
2021-07-29 03:00 | 44406.125 | 0 | 7.9335 | 39.95
2021-07-29 03:30 | 44406.1458 | 0 | 8.0214 | 39.95
2021-07-29 04:00 | 44406.1667 | 0 | 8.1933 | 39.95
2021-07-29 04:30 | 44406.1875 | 0 | 8.5747 | 39.95
2021-07-29 05:00 | 44406.2083 | 0 | 9.3673 | 39.95
2021-07-29 05:30 | 44406.2292 | 0 | 10.324 | 39.95
2021-07-29 06:00 | 44406.25 | 0 | 11.3881 | 39.95
2021-07-29 06:30 | 44406.2708 | 0 | 12.3617 | 39.95
2021-07-29 07:00 | 44406.2917 | 0 | 13.2323 | 39.95
2021-07-29 07:30 | 44406.3125 | 0 | 13.4756 | 39.95
2021-07-29 08:00 | 44406.3333 | 0 | 12.6221 | 39.95
2021-07-29 08:30 | 44406.3542 | 0 | 11.8097 | 39.95
2021-07-29 09:00 | 44406.375 | 0 | 10.9633 | 39.95
2021-07-29 09:30 | 44406.3958 | 0 | 9.865 | 39.95
2021-07-29 10:00 | 44406.4167 | 0 | 9.4059 | 39.95
2021-07-29 10:30 | 44406.4375 | 0 | 9.1519 | 39.95
2021-07-29 11:00 | 44406.4583 | 0 | 8.9131 | 39.95
2021-07-29 11:30 | 44406.4792 | 0 | 8.8035 | 39.95
2021-07-29 12:00 | 44406.5 | 0 | 8.5332 | 39.95
2021-07-29 12:30 | 44406.5208 | 0 | 8.6109 | 39.95
2021-07-29 13:00 | 44406.5417 | 0 | 8.8529 | 39.95
2021-07-29 13:30 | 44406.5625 | 0 | 9.4545 | 39.95
2021-07-29 14:00 | 44406.5833 | 0 | 10.0866 | 39.95
2021-07-29 14:30 | 44406.6042 | 0 | 10.652 | 39.95
2021-07-29 15:00 | 44406.625 | 0 | 10.3666 | 39.95
2021-07-29 15:30 | 44406.6458 | 0 | 11.0187 | 39.95
2021-07-29 16:00 | 44406.6667 | 0 | 11.4767 | 39.95
2021-07-29 16:30 | 44406.6875 | 0 | 12.2259 | 39.95
2021-07-29 17:00 | 44406.7083 | 0 | 12.6544 | 39.95
2021-07-29 17:30 | 44406.7292 | 0 | 13.3699 | 39.95
2021-07-29 18:00 | 44406.75 | 0 | 13.6919 | 39.95
2021-07-29 18:30 | 44406.7708 | 0 | 14.0158 | 39.95
2021-07-29 19:00 | 44406.7917 | 0 | 13.6246 | 39.95
2021-07-29 19:30 | 44406.8125 | 0 | 13.5316 | 39.95
2021-07-29 20:00 | 44406.8333 | 0 | 13.3125 | 39.95
2021-07-29 20:30 | 44406.8542 | 0 | 12.8104 | 39.95
2021-07-29 21:00 | 44406.875 | 0 | 12.3847 | 39.95
2021-07-29 21:30 | 44406.8958 | 0 | 11.9201 | 39.95
2021-07-29 22:00 | 44406.9167 | 0 | 11.34 | 39.95
2021-07-29 22:30 | 44406.9375 | 0 | 10.5561 | 39.95
2021-07-29 23:00 | 44406.9583 | 0 | 9.7968 | 39.95
2021-07-29 23:30 | 44406.9792 | 0 | 9.4048 | 39.95
2021-07-30 | 44407 | 0 | 8.8861 | 39.95
2021-07-30 00:30 | 44407.0208 | 0 | 8.3948 | 39.95
2021-07-30 01:00 | 44407.0417 | 0 | 8.2208 | 39.95
2021-07-30 01:30 | 44407.0625 | 0 | 8.0476 | 39.95
2021-07-30 02:00 | 44407.0833 | 0 | 7.9689 | 39.95
2021-07-30 02:30 | 44407.1042 | 0 | 7.8929 | 39.95
2021-07-30 03:00 | 44407.125 | 0 | 7.8629 | 39.95
2021-07-30 03:30 | 44407.1458 | 0 | 8.0563 | 39.95
2021-07-30 04:00 | 44407.1667 | 0 | 8.186 | 39.95
2021-07-30 04:30 | 44407.1875 | 0 | 8.6972 | 39.95
2021-07-30 05:00 | 44407.2083 | 0 | 9.4693 | 39.95
2021-07-30 05:30 | 44407.2292 | 0 | 10.5978 | 39.95
2021-07-30 06:00 | 44407.25 | 0 | 11.8935 | 39.95
2021-07-30 06:30 | 44407.2708 | 0 | 13.3934 | 39.95
2021-07-30 07:00 | 44407.2917 | 0 | 13.9124 | 39.95
2021-07-30 07:30 | 44407.3125 | 0 | 13.7886 | 39.95
2021-07-30 08:00 | 44407.3333 | 0 | 12.8121 | 39.95
2021-07-30 08:30 | 44407.3542 | 0 | 11.7068 | 39.95
2021-07-30 09:00 | 44407.375 | 0 | 10.7825 | 39.95
2021-07-30 09:30 | 44407.3958 | 0 | 10.1982 | 39.95
2021-07-30 10:00 | 44407.4167 | 0 | 9.3847 | 39.95
2021-07-30 10:30 | 44407.4375 | 0 | 9.037 | 39.95
2021-07-30 11:00 | 44407.4583 | 0 | 8.7965 | 39.95
2021-07-30 11:30 | 44407.4792 | 0 | 8.6282 | 39.95
2021-07-30 12:00 | 44407.5 | 0 | 8.1802 | 39.95
2021-07-30 12:30 | 44407.5208 | 0 | 8.021 | 39.95
2021-07-30 13:00 | 44407.5417 | 0 | 8.1768 | 39.95
2021-07-30 13:30 | 44407.5625 | 0 | 8.3003 | 39.95
2021-07-30 14:00 | 44407.5833 | 0 | 8.8521 | 39.95
2021-07-30 14:30 | 44407.6042 | 0 | 9.1805 | 39.95
2021-07-30 15:00 | 44407.625 | 0 | 9.7356 | 39.95
2021-07-30 15:30 | 44407.6458 | 0 | 10.6223 | 39.95
2021-07-30 16:00 | 44407.6667 | 0 | 11.5543 | 39.95
2021-07-30 16:30 | 44407.6875 | 0 | 12.3423 | 39.95
2021-07-30 17:00 | 44407.7083 | 0 | 12.6485 | 39.95
2021-07-30 17:30 | 44407.7292 | 0 | 13.255 | 39.95
2021-07-30 18:00 | 44407.75 | 0 | 13.4615 | 39.95
2021-07-30 18:30 | 44407.7708 | 0 | 13.6661 | 39.95
2021-07-30 19:00 | 44407.7917 | 0 | 13.538 | 39.95
2021-07-30 19:30 | 44407.8125 | 0 | 13.5461 | 39.95
2021-07-30 20:00 | 44407.8333 | 0 | 13.4229 | 39.95
2021-07-30 20:30 | 44407.8542 | 0 | 13.0225 | 39.95
2021-07-30 21:00 | 44407.875 | 0 | 12.5627 | 39.95
2021-07-30 21:30 | 44407.8958 | 0 | 12.2147 | 39.95
2021-07-30 22:00 | 44407.9167 | 0 | 11.6734 | 39.95
2021-07-30 22:30 | 44407.9375 | 0 | 10.702 | 39.95
2021-07-30 23:00 | 44407.9583 | 0 | 9.9478 | 39.95
2021-07-30 23:30 | 44407.9792 | 0 | 9.5203 | 39.95
2021-07-31 | 44408 | 0 | 8.9918 | 39.95
2021-07-31 00:30 | 44408.0208 | 0 | 8.4114 | 39.95
2021-07-31 01:00 | 44408.0417 | 0 | 8.2818 | 39.95
2021-07-31 01:30 | 44408.0625 | 0 | 8.0627 | 39.95
2021-07-31 02:00 | 44408.0833 | 0 | 7.8798 | 39.95
2021-07-31 02:30 | 44408.1042 | 0 | 7.7133 | 39.95
2021-07-31 03:00 | 44408.125 | 0 | 7.7068 | 39.95
2021-07-31 03:30 | 44408.1458 | 0 | 7.8235 | 39.95
2021-07-31 04:00 | 44408.1667 | 0 | 7.8074 | 39.95
2021-07-31 04:30 | 44408.1875 | 0 | 7.9291 | 39.95
2021-07-31 05:00 | 44408.2083 | 0 | 8.3173 | 39.95
2021-07-31 05:30 | 44408.2292 | 0 | 8.7168 | 39.95
2021-07-31 06:00 | 44408.25 | 0 | 9.2379 | 39.95
2021-07-31 06:30 | 44408.2708 | 0 | 9.757 | 39.95
2021-07-31 07:00 | 44408.2917 | 0 | 10.3614 | 39.95
2021-07-31 07:30 | 44408.3125 | 0 | 10.4617 | 39.95
2021-07-31 08:00 | 44408.3333 | 0 | 10.2201 | 39.95
2021-07-31 08:30 | 44408.3542 | 0 | 9.4312 | 39.95
2021-07-31 09:00 | 44408.375 | 0 | 8.8638 | 39.95
2021-07-31 09:30 | 44408.3958 | 0 | 8.0907 | 39.95
2021-07-31 10:00 | 44408.4167 | 0 | 7.383 | 39.95
2021-07-31 10:30 | 44408.4375 | 0 | 6.8229 | 39.95
2021-07-31 11:00 | 44408.4583 | 0 | 6.5108 | 39.95
2021-07-31 11:30 | 44408.4792 | 0 | 6.2385 | 39.95
2021-07-31 12:00 | 44408.5 | 0 | 6.0079 | 39.95
2021-07-31 12:30 | 44408.5208 | 0 | 6.0354 | 39.95
2021-07-31 13:00 | 44408.5417 | 0 | 6.0725 | 39.95
2021-07-31 13:30 | 44408.5625 | 0 | 6.1894 | 39.95
2021-07-31 14:00 | 44408.5833 | 0 | 6.6967 | 39.95
2021-07-31 14:30 | 44408.6042 | 0 | 7.2298 | 39.95
2021-07-31 15:00 | 44408.625 | 0 | 7.9128 | 39.95
2021-07-31 15:30 | 44408.6458 | 0 | 8.6944 | 39.95
2021-07-31 16:00 | 44408.6667 | 0 | 9.4882 | 39.95
2021-07-31 16:30 | 44408.6875 | 0 | 10.2781 | 39.95
2021-07-31 17:00 | 44408.7083 | 0 | 11.108 | 39.95
2021-07-31 17:30 | 44408.7292 | 0 | 11.7589 | 39.95
2021-07-31 18:00 | 44408.75 | 0 | 12.1675 | 39.95
2021-07-31 18:30 | 44408.7708 | 0 | 12.4044 | 39.95
2021-07-31 19:00 | 44408.7917 | 0 | 12.0504 | 39.95
2021-07-31 19:30 | 44408.8125 | 0 | 11.8447 | 39.95
2021-07-31 20:00 | 44408.8333 | 0 | 11.4973 | 39.95
2021-07-31 20:30 | 44408.8542 | 0 | 11.0392 | 39.95
2021-07-31 21:00 | 44408.875 | 0 | 10.5992 | 39.95
2021-07-31 21:30 | 44408.8958 | 0 | 10.2883 | 39.95
2021-07-31 22:00 | 44408.9167 | 0 | 9.8942 | 39.95
2021-07-31 22:30 | 44408.9375 | 0 | 9.1907 | 39.95
2021-07-31 23:00 | 44408.9583 | 0 | 8.5827 | 39.95
2021-07-31 23:30 | 44408.9792 | 0 | 8.2305 | 39.95
2021-08-01 | 44409 | 0 | 7.8051 | 39.95
2021-08-01 00:30 | 44409.0208 | 0 | 7.5325 | 39.95
2021-08-01 01:00 | 44409.0417 | 0 | 7.3271 | 39.95
2021-08-01 01:30 | 44409.0625 | 0 | 7.0157 | 39.95
2021-08-01 02:00 | 44409.0833 | 0 | 6.9976 | 39.95
2021-08-01 02:30 | 44409.1042 | 0 | 7.0123 | 39.95
2021-08-01 03:00 | 44409.125 | 0 | 7.0068 | 39.95
2021-08-01 03:30 | 44409.1458 | 0 | 7.0442 | 39.95
2021-08-01 04:00 | 44409.1667 | 0 | 6.9756 | 39.95
2021-08-01 04:30 | 44409.1875 | 0 | 6.9471 | 39.95
2021-08-01 05:00 | 44409.2083 | 0 | 7.0269 | 39.95
2021-08-01 05:30 | 44409.2292 | 0 | 7.2575 | 39.95
2021-08-01 06:00 | 44409.25 | 0 | 7.5772 | 39.95
2021-08-01 06:30 | 44409.2708 | 0 | 7.9128 | 39.95
2021-08-01 07:00 | 44409.2917 | 0 | 8.0156 | 39.95
2021-08-01 07:30 | 44409.3125 | 0 | 8.0568 | 39.95
2021-08-01 08:00 | 44409.3333 | 0 | 7.8707 | 39.95
2021-08-01 08:30 | 44409.3542 | 0 | 7.6713 | 39.95
2021-08-01 09:00 | 44409.375 | 0 | 7.5861 | 39.95
2021-08-01 09:30 | 44409.3958 | 0 | 7.3013 | 39.95
2021-08-01 10:00 | 44409.4167 | 0 | 6.8849 | 39.95
2021-08-01 10:30 | 44409.4375 | 0 | 6.5884 | 39.95
2021-08-01 11:00 | 44409.4583 | 0 | 6.4489 | 39.95
2021-08-01 11:30 | 44409.4792 | 0 | 6.3242 | 39.95
2021-08-01 12:00 | 44409.5 | 0 | 6.2272 | 39.95
2021-08-01 12:30 | 44409.5208 | 0 | 6.1968 | 39.95
2021-08-01 13:00 | 44409.5417 | 0 | 6.5024 | 39.95
2021-08-01 13:30 | 44409.5625 | 0 | 6.593 | 39.95
2021-08-01 14:00 | 44409.5833 | 0 | 7.0868 | 39.95
2021-08-01 14:30 | 44409.6042 | 0 | 7.5148 | 39.95
2021-08-01 15:00 | 44409.625 | 0 | 8.0862 | 39.95
2021-08-01 15:30 | 44409.6458 | 0 | 8.832 | 39.95
2021-08-01 16:00 | 44409.6667 | 0 | 9.617 | 39.95
2021-08-01 16:30 | 44409.6875 | 0 | 10.3528 | 39.95
2021-08-01 17:00 | 44409.7083 | 0 | 11.3124 | 39.95
2021-08-01 17:30 | 44409.7292 | 0 | 11.9497 | 39.95
2021-08-01 18:00 | 44409.75 | 0 | 12.2681 | 39.95
2021-08-01 18:30 | 44409.7708 | 0 | 12.3166 | 39.95
2021-08-01 19:00 | 44409.7917 | 0 | 11.8115 | 39.95
2021-08-01 19:30 | 44409.8125 | 0 | 11.2221 | 39.95
2021-08-01 20:00 | 44409.8333 | 0 | 10.945 | 39.95
2021-08-01 20:30 | 44409.8542 | 0 | 10.3724 | 39.95
2021-08-01 21:00 | 44409.875 | 0 | 10.0011 | 39.95
2021-08-01 21:30 | 44409.8958 | 0 | 9.7244 | 39.95
2021-08-01 22:00 | 44409.9167 | 0 | 9.2757 | 39.95
2021-08-01 22:30 | 44409.9375 | 0 | 8.619 | 39.95
2021-08-01 23:00 | 44409.9583 | 0 | 8.1434 | 39.95
2021-08-01 23:30 | 44409.9792 | 0 | 7.7479 | 39.95
2021-08-02 | 44410 | 0 | 7.4877 | 39.95
2021-08-02 00:30 | 44410.0208 | 0 | 7.2662 | 39.95
2021-08-02 01:00 | 44410.0417 | 0 | 7.0462 | 39.95
2021-08-02 01:30 | 44410.0625 | 0 | 7.0292 | 39.95
2021-08-02 02:00 | 44410.0833 | 0 | 6.9996 | 39.95
2021-08-02 02:30 | 44410.1042 | 0 | 6.9475 | 39.95
2021-08-02 03:00 | 44410.125 | 0 | 6.962 | 39.95
2021-08-02 03:30 | 44410.1458 | 0 | 7.2927 | 39.95
2021-08-02 04:00 | 44410.1667 | 0 | 7.5186 | 39.95
2021-08-02 04:30 | 44410.1875 | 0 | 7.8887 | 39.95
2021-08-02 05:00 | 44410.2083 | 0 | 8.3323 | 39.95
2021-08-02 05:30 | 44410.2292 | 0 | 8.9947 | 39.95
2021-08-02 06:00 | 44410.25 | 0 | 9.8179 | 39.95
2021-08-02 06:30 | 44410.2708 | 0 | 10.6345 | 39.95
2021-08-02 07:00 | 44410.2917 | 0 | 11.0765 | 39.95
2021-08-02 07:30 | 44410.3125 | 0 | 10.6786 | 39.95
2021-08-02 08:00 | 44410.3333 | 0 | 11.3856 | 39.95
2021-08-02 08:30 | 44410.3542 | 0 | 10.5706 | 39.95
2021-08-02 09:00 | 44410.375 | 0 | 10.0669 | 39.95
2021-08-02 09:30 | 44410.3958 | 0 | 10.1088 | 39.95
2021-08-02 10:00 | 44410.4167 | 0 | 10.1345 | 39.95
2021-08-02 10:30 | 44410.4375 | 0 | 9.104 | 39.95
2021-08-02 11:00 | 44410.4583 | 0 | 9.4153 | 39.95
2021-08-02 11:30 | 44410.4792 | 0 | 10.2172 | 39.95
2021-08-02 12:00 | 44410.5 | 0 | 9.7171 | 39.95
2021-08-02 12:30 | 44410.5208 | 0 | 11.1742 | 39.95
2021-08-02 13:00 | 44410.5417 | 0 | 9.7473 | 39.95
2021-08-02 13:30 | 44410.5625 | 0 | 10.2083 | 39.95
2021-08-02 14:00 | 44410.5833 | 0 | 10.7879 | 39.95
2021-08-02 14:30 | 44410.6042 | 0 | 11.4089 | 39.95
2021-08-02 15:00 | 44410.625 | 0 | 11.3379 | 39.95
2021-08-02 15:30 | 44410.6458 | 0 | 11.5413 | 39.95
2021-08-02 16:00 | 44410.6667 | 0 | 11.9019 | 39.95
2021-08-02 16:30 | 44410.6875 | 0 | 12.3576 | 39.95
2021-08-02 17:00 | 44410.7083 | 0 | 12.9298 | 39.95
2021-08-02 17:30 | 44410.7292 | 0 | 13.5198 | 39.95
2021-08-02 18:00 | 44410.75 | 0 | 13.7903 | 39.95
2021-08-02 18:30 | 44410.7708 | 0 | 13.7988 | 39.95
2021-08-02 19:00 | 44410.7917 | 0 | 13.4285 | 39.95
2021-08-02 19:30 | 44410.8125 | 0 | 13.1404 | 39.95
2021-08-02 20:00 | 44410.8333 | 0 | 12.6467 | 39.95
2021-08-02 20:30 | 44410.8542 | 0 | 12.1237 | 39.95
2021-08-02 21:00 | 44410.875 | 0 | 11.655 | 39.95
2021-08-02 21:30 | 44410.8958 | 0 | 11.1967 | 39.95
2021-08-02 22:00 | 44410.9167 | 0 | 10.7124 | 39.95
2021-08-02 22:30 | 44410.9375 | 0 | 10.0571 | 39.95
2021-08-02 23:00 | 44410.9583 | 0 | 9.3861 | 39.95
2021-08-02 23:30 | 44410.9792 | 0 | 8.9135 | 39.95
2021-08-03 | 44411 | 0 | 8.5175 | 39.95
2021-08-03 00:30 | 44411.0208 | 0 | 8.0907 | 39.95
2021-08-03 01:00 | 44411.0417 | 0 | 7.8595 | 39.95
2021-08-03 01:30 | 44411.0625 | 0 | 7.7959 | 39.95
2021-08-03 02:00 | 44411.0833 | 0 | 7.7534 | 39.95
2021-08-03 02:30 | 44411.1042 | 0 | 7.6547 | 39.95
2021-08-03 03:00 | 44411.125 | 0 | 7.6949 | 39.95
2021-08-03 03:30 | 44411.1458 | 0 | 7.8106 | 39.95
2021-08-03 04:00 | 44411.1667 | 0 | 8.0058 | 39.95
2021-08-03 04:30 | 44411.1875 | 0 | 8.3299 | 39.95
2021-08-03 05:00 | 44411.2083 | 0 | 8.7772 | 39.95
2021-08-03 05:30 | 44411.2292 | 0 | 9.3735 | 39.95
2021-08-03 06:00 | 44411.25 | 0 | 9.9109 | 39.95
2021-08-03 06:30 | 44411.2708 | 0 | 10.6169 | 39.95
2021-08-03 07:00 | 44411.2917 | 0 | 11.5813 | 39.95
2021-08-03 07:30 | 44411.3125 | 0 | 11.9824 | 39.95
2021-08-03 08:00 | 44411.3333 | 0 | 12.6654 | 39.95
2021-08-03 08:30 | 44411.3542 | 0 | 12.9219 | 39.95
2021-08-03 09:00 | 44411.375 | 0 | 12.0221 | 39.95
2021-08-03 09:30 | 44411.3958 | 0 | 11.2038 | 39.95
2021-08-03 10:00 | 44411.4167 | 0 | 9.7302 | 39.95
2021-08-03 10:30 | 44411.4375 | 0 | 9.7378 | 39.95
2021-08-03 11:00 | 44411.4583 | 0 | 8.5733 | 39.95
2021-08-03 11:30 | 44411.4792 | 0 | 9.1045 | 39.95
2021-08-03 12:00 | 44411.5 | 0 | 10.5891 | 39.95
2021-08-03 12:30 | 44411.5208 | 0 | 11.6345 | 39.95
2021-08-03 13:00 | 44411.5417 | 0 | 10.7351 | 39.95
2021-08-03 13:30 | 44411.5625 | 0 | 11.3554 | 39.95
2021-08-03 14:00 | 44411.5833 | 0 | 11.9705 | 39.95
2021-08-03 14:30 | 44411.6042 | 0 | 11.5887 | 39.95
2021-08-03 15:00 | 44411.625 | 0 | 11.7945 | 39.95
2021-08-03 15:30 | 44411.6458 | 0 | 12.2711 | 39.95
2021-08-03 16:00 | 44411.6667 | 0 | 12.3832 | 39.95
2021-08-03 16:30 | 44411.6875 | 0 | 12.6639 | 39.95
2021-08-03 17:00 | 44411.7083 | 0 | 12.9258 | 39.95
2021-08-03 17:30 | 44411.7292 | 0 | 13.7523 | 39.95
2021-08-03 18:00 | 44411.75 | 0 | 13.8837 | 39.95
2021-08-03 18:30 | 44411.7708 | 0 | 13.9646 | 39.95
2021-08-03 19:00 | 44411.7917 | 0 | 13.5732 | 39.95
2021-08-03 19:30 | 44411.8125 | 0 | 13.1662 | 39.95
2021-08-03 20:00 | 44411.8333 | 0 | 12.8626 | 39.95
2021-08-03 20:30 | 44411.8542 | 0 | 12.2409 | 39.95
2021-08-03 21:00 | 44411.875 | 0 | 11.6095 | 39.95
2021-08-03 21:30 | 44411.8958 | 0 | 11.2121 | 39.95
2021-08-03 22:00 | 44411.9167 | 0 | 10.6607 | 39.95
2021-08-03 22:30 | 44411.9375 | 0 | 9.8612 | 39.95
2021-08-03 23:00 | 44411.9583 | 0 | 9.3816 | 39.95
2021-08-03 23:30 | 44411.9792 | 0 | 9 | 39.95
2021-08-04 | 44412 | 0 | 8.5639 | 39.95
2021-08-04 00:30 | 44412.0208 | 0 | 8.1744 | 39.95
2021-08-04 01:00 | 44412.0417 | 0 | 7.9452 | 39.95
2021-08-04 01:30 | 44412.0625 | 0 | 7.7536 | 39.95
2021-08-04 02:00 | 44412.0833 | 0 | 7.6619 | 39.95
2021-08-04 02:30 | 44412.1042 | 0 | 7.6549 | 39.95
2021-08-04 03:00 | 44412.125 | 0 | 7.6114 | 39.95
2021-08-04 03:30 | 44412.1458 | 0 | 7.7456 | 39.95
2021-08-04 04:00 | 44412.1667 | 0 | 7.873 | 39.95
2021-08-04 04:30 | 44412.1875 | 0 | 8.1812 | 39.95
2021-08-04 05:00 | 44412.2083 | 0 | 8.6692 | 39.95
2021-08-04 05:30 | 44412.2292 | 0 | 9.4722 | 39.95
2021-08-04 06:00 | 44412.25 | 0 | 10.0569 | 39.95
2021-08-04 06:30 | 44412.2708 | 0 | 10.7805 | 39.95
2021-08-04 07:00 | 44412.2917 | 0 | 11.5066 | 39.95
2021-08-04 07:30 | 44412.3125 | 0 | 11.4086 | 39.95
2021-08-04 08:00 | 44412.3333 | 0 | 11.1312 | 39.95
2021-08-04 08:30 | 44412.3542 | 0 | 10.6573 | 39.95
2021-08-04 09:00 | 44412.375 | 0 | 9.8376 | 39.95
2021-08-04 09:30 | 44412.3958 | 0 | 9.3954 | 39.95
2021-08-04 10:00 | 44412.4167 | 0 | 8.703 | 39.95
2021-08-04 10:30 | 44412.4375 | 0 | 8.2598 | 39.95
2021-08-04 11:00 | 44412.4583 | 0 | 7.9506 | 39.95
2021-08-04 11:30 | 44412.4792 | 0 | 7.8184 | 39.95
2021-08-04 12:00 | 44412.5 | 0 | 7.5836 | 39.95
2021-08-04 12:30 | 44412.5208 | 0 | 7.6822 | 39.95
2021-08-04 13:00 | 44412.5417 | 0 | 7.8916 | 39.95
2021-08-04 13:30 | 44412.5625 | 0 | 8.1436 | 39.95
2021-08-04 14:00 | 44412.5833 | 0 | 8.5312 | 39.95
2021-08-04 14:30 | 44412.6042 | 0 | 8.9694 | 39.95
2021-08-04 15:00 | 44412.625 | 0 | 9.561 | 39.95
2021-08-04 15:30 | 44412.6458 | 0 | 10.2298 | 39.95
2021-08-04 16:00 | 44412.6667 | 0 | 11.1432 | 39.95
2021-08-04 16:30 | 44412.6875 | 0 | 12.2573 | 39.95
2021-08-04 17:00 | 44412.7083 | 0 | 12.9669 | 39.95
2021-08-04 17:30 | 44412.7292 | 0 | 14.1719 | 39.95
2021-08-04 18:00 | 44412.75 | 0 | 15.0495 | 39.95
2021-08-04 18:30 | 44412.7708 | 0 | 15.4181 | 39.95
2021-08-04 19:00 | 44412.7917 | 0 | 14.9413 | 39.95
2021-08-04 19:30 | 44412.8125 | 0 | 14.5979 | 39.95
2021-08-04 20:00 | 44412.8333 | 0 | 14.242 | 39.95
2021-08-04 20:30 | 44412.8542 | 0 | 13.6745 | 39.95
2021-08-04 21:00 | 44412.875 | 0 | 13.0132 | 39.95
2021-08-04 21:30 | 44412.8958 | 0 | 12.3473 | 39.95
2021-08-04 22:00 | 44412.9167 | 0 | 11.6637 | 39.95
2021-08-04 22:30 | 44412.9375 | 0 | 10.8546 | 39.95
2021-08-04 23:00 | 44412.9583 | 0 | 10.091 | 39.95
2021-08-04 23:30 | 44412.9792 | 0 | 9.5599 | 39.95
2021-08-05 | 44413 | 0 | 9.0552 | 39.95
2021-08-05 00:30 | 44413.0208 | 0 | 8.5373 | 39.95
2021-08-05 01:00 | 44413.0417 | 0 | 8.3158 | 39.95
2021-08-05 01:30 | 44413.0625 | 0 | 8.0481 | 39.95
2021-08-05 02:00 | 44413.0833 | 0 | 8.01 | 39.95
2021-08-05 02:30 | 44413.1042 | 0 | 7.9838 | 39.95
2021-08-05 03:00 | 44413.125 | 0 | 8.0194 | 39.95
2021-08-05 03:30 | 44413.1458 | 0 | 8.119 | 39.95
2021-08-05 04:00 | 44413.1667 | 0 | 8.3967 | 39.95
2021-08-05 04:30 | 44413.1875 | 0 | 8.7243 | 39.95
2021-08-05 05:00 | 44413.2083 | 0 | 9.4079 | 39.95
2021-08-05 05:30 | 44413.2292 | 0 | 10.1119 | 39.95
2021-08-05 06:00 | 44413.25 | 0 | 11.1476 | 39.95
2021-08-05 06:30 | 44413.2708 | 0 | 12.3428 | 39.95
2021-08-05 07:00 | 44413.2917 | 0 | 13.1595 | 39.95
2021-08-05 07:30 | 44413.3125 | 0 | 13.5531 | 39.95
2021-08-05 08:00 | 44413.3333 | 0 | 12.894 | 39.95
2021-08-05 08:30 | 44413.3542 | 0 | 12.0951 | 39.95
2021-08-05 09:00 | 44413.375 | 0 | 11.0777 | 39.95
2021-08-05 09:30 | 44413.3958 | 0 | 10.4746 | 39.95
2021-08-05 10:00 | 44413.4167 | 0 | 9.8051 | 39.95
2021-08-05 10:30 | 44413.4375 | 0 | 9.4079 | 39.95
2021-08-05 11:00 | 44413.4583 | 0 | 9.1443 | 39.95
2021-08-05 11:30 | 44413.4792 | 0 | 8.9086 | 39.95
2021-08-05 12:00 | 44413.5 | 0 | 8.7254 | 39.95
2021-08-05 12:30 | 44413.5208 | 0 | 8.5238 | 39.95
2021-08-05 13:00 | 44413.5417 | 0 | 8.6291 | 39.95
2021-08-05 13:30 | 44413.5625 | 0 | 8.6983 | 39.95
2021-08-05 14:00 | 44413.5833 | 0 | 8.9474 | 39.95
2021-08-05 14:30 | 44413.6042 | 0 | 9.3799 | 39.95
2021-08-05 15:00 | 44413.625 | 0 | 10.0117 | 39.95
2021-08-05 15:30 | 44413.6458 | 0 | 10.6543 | 39.95
2021-08-05 16:00 | 44413.6667 | 0 | 11.349 | 39.95
2021-08-05 16:30 | 44413.6875 | 0 | 12.4173 | 39.95
2021-08-05 17:00 | 44413.7083 | 0 | 13.048 | 39.95
2021-08-05 17:30 | 44413.7292 | 0 | 14.1666 | 39.95
2021-08-05 18:00 | 44413.75 | 0 | 14.8935 | 39.95
2021-08-05 18:30 | 44413.7708 | 0 | 15.0719 | 39.95
2021-08-05 19:00 | 44413.7917 | 0 | 14.6381 | 39.95
2021-08-05 19:30 | 44413.8125 | 0 | 14.4138 | 39.95
2021-08-05 20:00 | 44413.8333 | 0 | 14.1155 | 39.95
2021-08-05 20:30 | 44413.8542 | 0 | 13.4678 | 39.95
2021-08-05 21:00 | 44413.875 | 0 | 12.8144 | 39.95
2021-08-05 21:30 | 44413.8958 | 0 | 12.194 | 39.95
2021-08-05 22:00 | 44413.9167 | 0 | 11.6592 | 39.95
2021-08-05 22:30 | 44413.9375 | 0 | 10.8659 | 39.95
2021-08-05 23:00 | 44413.9583 | 0 | 10.019 | 39.95
2021-08-05 23:30 | 44413.9792 | 0 | 9.523 | 39.95
2021-08-06 | 44414 | 0 | 8.935 | 39.95
2021-08-06 00:30 | 44414.0208 | 0 | 8.6305 | 39.95
2021-08-06 01:00 | 44414.0417 | 0 | 8.2445 | 39.95
2021-08-06 01:30 | 44414.0625 | 0 | 8.0977 | 39.95
2021-08-06 02:00 | 44414.0833 | 0 | 8.0082 | 39.95
2021-08-06 02:30 | 44414.1042 | 0 | 7.9599 | 39.95
2021-08-06 03:00 | 44414.125 | 0 | 7.9355 | 39.95
2021-08-06 03:30 | 44414.1458 | 0 | 8.1452 | 39.95
2021-08-06 04:00 | 44414.1667 | 0 | 8.4296 | 39.95
2021-08-06 04:30 | 44414.1875 | 0 | 8.8286 | 39.95
2021-08-06 05:00 | 44414.2083 | 0 | 9.4587 | 39.95
2021-08-06 05:30 | 44414.2292 | 0 | 10.1455 | 39.95
2021-08-06 06:00 | 44414.25 | 0 | 10.9381 | 39.95
2021-08-06 06:30 | 44414.2708 | 0 | 12.1017 | 39.95
2021-08-06 07:00 | 44414.2917 | 0 | 13.0718 | 39.95
2021-08-06 07:30 | 44414.3125 | 0 | 13.0726 | 39.95
2021-08-06 08:00 | 44414.3333 | 0 | 12.7245 | 39.95
2021-08-06 08:30 | 44414.3542 | 0 | 12.0121 | 39.95
2021-08-06 09:00 | 44414.375 | 0 | 11.1723 | 39.95
2021-08-06 09:30 | 44414.3958 | 0 | 10.3965 | 39.95
2021-08-06 10:00 | 44414.4167 | 0 | 9.6121 | 39.95
2021-08-06 10:30 | 44414.4375 | 0 | 9.2781 | 39.95
2021-08-06 11:00 | 44414.4583 | 0 | 8.8514 | 39.95
2021-08-06 11:30 | 44414.4792 | 0 | 8.5856 | 39.95
2021-08-06 12:00 | 44414.5 | 0 | 8.2133 | 39.95
2021-08-06 12:30 | 44414.5208 | 0 | 8.1335 | 39.95
2021-08-06 13:00 | 44414.5417 | 0 | 8.1279 | 39.95
2021-08-06 13:30 | 44414.5625 | 0 | 8.4975 | 39.95
2021-08-06 14:00 | 44414.5833 | 0 | 8.6467 | 39.95
2021-08-06 14:30 | 44414.6042 | 0 | 8.9828 | 39.95
2021-08-06 15:00 | 44414.625 | 0 | 9.7464 | 39.95
2021-08-06 15:30 | 44414.6458 | 0 | 10.4056 | 39.95
2021-08-06 16:00 | 44414.6667 | 0 | 11.034 | 39.95
2021-08-06 16:30 | 44414.6875 | 0 | 11.9152 | 39.95
2021-08-06 17:00 | 44414.7083 | 0 | 12.5904 | 39.95
2021-08-06 17:30 | 44414.7292 | 0 | 13.4239 | 39.95
2021-08-06 18:00 | 44414.75 | 0 | 13.8809 | 39.95
2021-08-06 18:30 | 44414.7708 | 0 | 14.2796 | 39.95
2021-08-06 19:00 | 44414.7917 | 0 | 13.9224 | 39.95
2021-08-06 19:30 | 44414.8125 | 0 | 13.7905 | 39.95
2021-08-06 20:00 | 44414.8333 | 0 | 13.5328 | 39.95
2021-08-06 20:30 | 44414.8542 | 0 | 12.8642 | 39.95
2021-08-06 21:00 | 44414.875 | 0 | 12.2127 | 39.95
2021-08-06 21:30 | 44414.8958 | 0 | 11.7652 | 39.95
2021-08-06 22:00 | 44414.9167 | 0 | 11.2199 | 39.95
2021-08-06 22:30 | 44414.9375 | 0 | 10.4814 | 39.95
2021-08-06 23:00 | 44414.9583 | 0 | 9.9799 | 39.95
2021-08-06 23:30 | 44414.9792 | 0 | 9.5804 | 39.95
2021-08-07 | 44415 | 0 | 8.8584 | 39.95
2021-08-07 00:30 | 44415.0208 | 0 | 8.4663 | 39.95
2021-08-07 01:00 | 44415.0417 | 0 | 8.1132 | 39.95
2021-08-07 01:30 | 44415.0625 | 0 | 7.9937 | 39.95
2021-08-07 02:00 | 44415.0833 | 0 | 7.8315 | 39.95
2021-08-07 02:30 | 44415.1042 | 0 | 7.7142 | 39.95
2021-08-07 03:00 | 44415.125 | 0 | 7.7625 | 39.95
2021-08-07 03:30 | 44415.1458 | 0 | 7.7603 | 39.95
2021-08-07 04:00 | 44415.1667 | 0 | 7.5841 | 39.95
2021-08-07 04:30 | 44415.1875 | 0 | 7.6957 | 39.95
2021-08-07 05:00 | 44415.2083 | 0 | 7.8084 | 39.95
2021-08-07 05:30 | 44415.2292 | 0 | 8.1142 | 39.95
2021-08-07 06:00 | 44415.25 | 0 | 8.5227 | 39.95
2021-08-07 06:30 | 44415.2708 | 0 | 9.0047 | 39.95
2021-08-07 07:00 | 44415.2917 | 0 | 9.6118 | 39.95
2021-08-07 07:30 | 44415.3125 | 0 | 10.0779 | 39.95
2021-08-07 08:00 | 44415.3333 | 0 | 10.574 | 39.95
2021-08-07 08:30 | 44415.3542 | 0 | 10.697 | 39.95
2021-08-07 09:00 | 44415.375 | 0 | 8.6549 | 39.95
2021-08-07 09:30 | 44415.3958 | 0 | 8.9218 | 39.95
2021-08-07 10:00 | 44415.4167 | 0 | 8.5177 | 39.95
2021-08-07 10:30 | 44415.4375 | 0 | 8.0544 | 39.95
2021-08-07 11:00 | 44415.4583 | 0 | 6.9781 | 39.95
2021-08-07 11:30 | 44415.4792 | 0 | 6.9168 | 39.95
2021-08-07 12:00 | 44415.5 | 0 | 6.5996 | 39.95
2021-08-07 12:30 | 44415.5208 | 0 | 6.4728 | 39.95
2021-08-07 13:00 | 44415.5417 | 0 | 6.5056 | 39.95
2021-08-07 13:30 | 44415.5625 | 0 | 6.7197 | 39.95
2021-08-07 14:00 | 44415.5833 | 0 | 7.1473 | 39.95
2021-08-07 14:30 | 44415.6042 | 0 | 7.4764 | 39.95
2021-08-07 15:00 | 44415.625 | 0 | 7.9618 | 39.95
2021-08-07 15:30 | 44415.6458 | 0 | 8.7213 | 39.95
2021-08-07 16:00 | 44415.6667 | 0 | 9.4421 | 39.95
2021-08-07 16:30 | 44415.6875 | 0 | 10.3619 | 39.95
2021-08-07 17:00 | 44415.7083 | 0 | 11.1989 | 39.95
2021-08-07 17:30 | 44415.7292 | 0 | 12.1731 | 39.95
2021-08-07 18:00 | 44415.75 | 0 | 12.7411 | 39.95
2021-08-07 18:30 | 44415.7708 | 0 | 12.9129 | 39.95
2021-08-07 19:00 | 44415.7917 | 0 | 12.5299 | 39.95
2021-08-07 19:30 | 44415.8125 | 0 | 12.4137 | 39.95
2021-08-07 20:00 | 44415.8333 | 0 | 12.163 | 39.95
2021-08-07 20:30 | 44415.8542 | 0 | 11.5707 | 39.95
2021-08-07 21:00 | 44415.875 | 0 | 11.0035 | 39.95
2021-08-07 21:30 | 44415.8958 | 0 | 10.843 | 39.95
2021-08-07 22:00 | 44415.9167 | 0 | 10.2789 | 39.95
2021-08-07 22:30 | 44415.9375 | 0 | 9.6873 | 39.95
2021-08-07 23:00 | 44415.9583 | 0 | 9.0893 | 39.95
2021-08-07 23:30 | 44415.9792 | 0 | 8.5313 | 39.95
2021-08-08 | 44416 | 0 | 8.1542 | 39.95
2021-08-08 00:30 | 44416.0208 | 0 | 7.8058 | 39.95
2021-08-08 01:00 | 44416.0417 | 0 | 7.5468 | 39.95
2021-08-08 01:30 | 44416.0625 | 0 | 7.3335 | 39.95
2021-08-08 02:00 | 44416.0833 | 0 | 7.1684 | 39.95
2021-08-08 02:30 | 44416.1042 | 0 | 7.158 | 39.95
2021-08-08 03:00 | 44416.125 | 0 | 7.1965 | 39.95
2021-08-08 03:30 | 44416.1458 | 0 | 7.1913 | 39.95
2021-08-08 04:00 | 44416.1667 | 0 | 7.174 | 39.95
2021-08-08 04:30 | 44416.1875 | 0 | 7.2597 | 39.95
2021-08-08 05:00 | 44416.2083 | 0 | 7.4352 | 39.95
2021-08-08 05:30 | 44416.2292 | 0 | 7.4601 | 39.95
2021-08-08 06:00 | 44416.25 | 0 | 7.8028 | 39.95
2021-08-08 06:30 | 44416.2708 | 0 | 8.1032 | 39.95
2021-08-08 07:00 | 44416.2917 | 0 | 8.5305 | 39.95
2021-08-08 07:30 | 44416.3125 | 0 | 8.5132 | 39.95
2021-08-08 08:00 | 44416.3333 | 0 | 8.347 | 39.95
2021-08-08 08:30 | 44416.3542 | 0 | 8.0814 | 39.95
2021-08-08 09:00 | 44416.375 | 0 | 7.7478 | 39.95
2021-08-08 09:30 | 44416.3958 | 0 | 7.3633 | 39.95
2021-08-08 10:00 | 44416.4167 | 0 | 6.6854 | 39.95
2021-08-08 10:30 | 44416.4375 | 0 | 6.3124 | 39.95
2021-08-08 11:00 | 44416.4583 | 0 | 6.0839 | 39.95
2021-08-08 11:30 | 44416.4792 | 0 | 5.9445 | 39.95
2021-08-08 12:00 | 44416.5 | 0 | 6.2336 | 39.95
2021-08-08 12:30 | 44416.5208 | 0 | 7.1047 | 39.95
2021-08-08 13:00 | 44416.5417 | 0 | 7.7427 | 39.95
2021-08-08 13:30 | 44416.5625 | 0 | 8.3234 | 39.95
2021-08-08 14:00 | 44416.5833 | 0 | 7.1154 | 39.95
2021-08-08 14:30 | 44416.6042 | 0 | 7.256 | 39.95
2021-08-08 15:00 | 44416.625 | 0 | 8.2519 | 39.95
2021-08-08 15:30 | 44416.6458 | 0 | 9.4847 | 39.95
2021-08-08 16:00 | 44416.6667 | 0 | 10.0002 | 39.95
2021-08-08 16:30 | 44416.6875 | 0 | 10.1893 | 39.95
2021-08-08 17:00 | 44416.7083 | 0 | 11.0422 | 39.95
2021-08-08 17:30 | 44416.7292 | 0 | 11.807 | 39.95
2021-08-08 18:00 | 44416.75 | 0 | 12.2489 | 39.95
2021-08-08 18:30 | 44416.7708 | 0 | 12.3242 | 39.95
2021-08-08 19:00 | 44416.7917 | 0 | 11.9554 | 39.95
2021-08-08 19:30 | 44416.8125 | 0 | 11.7918 | 39.95
2021-08-08 20:00 | 44416.8333 | 0 | 11.5836 | 39.95
2021-08-08 20:30 | 44416.8542 | 0 | 11.106 | 39.95
2021-08-08 21:00 | 44416.875 | 0 | 10.6981 | 39.95
2021-08-08 21:30 | 44416.8958 | 0 | 10.2253 | 39.95
2021-08-08 22:00 | 44416.9167 | 0 | 9.6695 | 39.95
2021-08-08 22:30 | 44416.9375 | 0 | 8.9305 | 39.95
2021-08-08 23:00 | 44416.9583 | 0 | 8.4087 | 39.95
2021-08-08 23:30 | 44416.9792 | 0 | 8.0683 | 39.95
2021-08-09 | 44417 | 0 | 7.6319 | 39.95
2021-08-09 00:30 | 44417.0208 | 0 | 7.4392 | 39.95
2021-08-09 01:00 | 44417.0417 | 0 | 7.2136 | 39.95
2021-08-09 01:30 | 44417.0625 | 0 | 7.1299 | 39.95
2021-08-09 02:00 | 44417.0833 | 0 | 7.1521 | 39.95
2021-08-09 02:30 | 44417.1042 | 0 | 6.9958 | 39.95
2021-08-09 03:00 | 44417.125 | 0 | 7.1241 | 39.95
2021-08-09 03:30 | 44417.1458 | 0 | 7.2575 | 39.95
2021-08-09 04:00 | 44417.1667 | 0 | 7.5043 | 39.95
2021-08-09 04:30 | 44417.1875 | 0 | 7.952 | 39.95
2021-08-09 05:00 | 44417.2083 | 0 | 8.679 | 39.95
2021-08-09 05:30 | 44417.2292 | 0 | 9.4098 | 39.95
2021-08-09 06:00 | 44417.25 | 0 | 10.4803 | 39.95
2021-08-09 06:30 | 44417.2708 | 0 | 12.0071 | 39.95
2021-08-09 07:00 | 44417.2917 | 0 | 13.0481 | 39.95
2021-08-09 07:30 | 44417.3125 | 0 | 13.7047 | 39.95
2021-08-09 08:00 | 44417.3333 | 0 | 13.5612 | 39.95
2021-08-09 08:30 | 44417.3542 | 0 | 13.0787 | 39.95
2021-08-09 09:00 | 44417.375 | 0 | 12.5936 | 39.95
2021-08-09 09:30 | 44417.3958 | 0 | 11.5398 | 39.95
2021-08-09 10:00 | 44417.4167 | 0 | 12.0156 | 39.95
2021-08-09 10:30 | 44417.4375 | 0 | 12.0093 | 39.95
2021-08-09 11:00 | 44417.4583 | 0 | 10.9728 | 39.95
2021-08-09 11:30 | 44417.4792 | 0 | 11.4572 | 39.95
2021-08-09 12:00 | 44417.5 | 0 | 10.9481 | 39.95
2021-08-09 12:30 | 44417.5208 | 0 | 9.3482 | 39.95
2021-08-09 13:00 | 44417.5417 | 0 | 8.8222 | 39.95
2021-08-09 13:30 | 44417.5625 | 0 | 9.9158 | 39.95
2021-08-09 14:00 | 44417.5833 | 0 | 11.2637 | 39.95
2021-08-09 14:30 | 44417.6042 | 0 | 10.8639 | 39.95
2021-08-09 15:00 | 44417.625 | 0 | 10.8574 | 39.95
2021-08-09 15:30 | 44417.6458 | 0 | 11.2085 | 39.95
2021-08-09 16:00 | 44417.6667 | 0 | 11.891 | 39.95
2021-08-09 16:30 | 44417.6875 | 0 | 12.667 | 39.95
2021-08-09 17:00 | 44417.7083 | 0 | 13.4948 | 39.95
2021-08-09 17:30 | 44417.7292 | 0 | 14.3469 | 39.95
2021-08-09 18:00 | 44417.75 | 0 | 14.7971 | 39.95
2021-08-09 18:30 | 44417.7708 | 0 | 15.0688 | 39.95
2021-08-09 19:00 | 44417.7917 | 0 | 14.4404 | 39.95
2021-08-09 19:30 | 44417.8125 | 0 | 14.4663 | 39.95
2021-08-09 20:00 | 44417.8333 | 0 | 13.7926 | 39.95
2021-08-09 20:30 | 44417.8542 | 0 | 13.3416 | 39.95
2021-08-09 21:00 | 44417.875 | 0 | 12.5085 | 39.95
2021-08-09 21:30 | 44417.8958 | 0 | 12.0904 | 39.95
2021-08-09 22:00 | 44417.9167 | 0 | 11.2404 | 39.95
2021-08-09 22:30 | 44417.9375 | 0 | 10.4427 | 39.95
2021-08-09 23:00 | 44417.9583 | 0 | 9.7501 | 39.95
2021-08-09 23:30 | 44417.9792 | 0 | 9.1799 | 39.95
2021-08-10 | 44418 | 0 | 8.756 | 39.95
2021-08-10 00:30 | 44418.0208 | 0 | 8.237 | 39.95
2021-08-10 01:00 | 44418.0417 | 0 | 8.083 | 39.95
2021-08-10 01:30 | 44418.0625 | 0 | 7.9192 | 39.95
2021-08-10 02:00 | 44418.0833 | 0 | 7.8645 | 39.95
2021-08-10 02:30 | 44418.1042 | 0 | 7.9188 | 39.95
2021-08-10 03:00 | 44418.125 | 0 | 7.8555 | 39.95
2021-08-10 03:30 | 44418.1458 | 0 | 7.9041 | 39.95
2021-08-10 04:00 | 44418.1667 | 0 | 8.0482 | 39.95
2021-08-10 04:30 | 44418.1875 | 0 | 8.4675 | 39.95
2021-08-10 05:00 | 44418.2083 | 0 | 9.235 | 39.95
2021-08-10 05:30 | 44418.2292 | 0 | 10.0194 | 39.95
2021-08-10 06:00 | 44418.25 | 0 | 11.0845 | 39.95
2021-08-10 06:30 | 44418.2708 | 0 | 12.4658 | 39.95
2021-08-10 07:00 | 44418.2917 | 0 | 13.7676 | 39.95
2021-08-10 07:30 | 44418.3125 | 0 | 13.8036 | 39.95
2021-08-10 08:00 | 44418.3333 | 0 | 13.7207 | 39.95
2021-08-10 08:30 | 44418.3542 | 0 | 13.1749 | 39.95
2021-08-10 09:00 | 44418.375 | 0 | 11.8692 | 39.95
2021-08-10 09:30 | 44418.3958 | 0 | 10.8602 | 39.95
2021-08-10 10:00 | 44418.4167 | 0 | 10.0482 | 39.95
2021-08-10 10:30 | 44418.4375 | 0 | 10.0542 | 39.95
2021-08-10 11:00 | 44418.4583 | 0 | 9.161 | 39.95
2021-08-10 11:30 | 44418.4792 | 0 | 10.5081 | 39.95
2021-08-10 12:00 | 44418.5 | 0 | 11.4659 | 39.95
2021-08-10 12:30 | 44418.5208 | 0 | 11.29 | 39.95
2021-08-10 13:00 | 44418.5417 | 0 | 11.0661 | 39.95
2021-08-10 13:30 | 44418.5625 | 0 | 11.1144 | 39.95
2021-08-10 14:00 | 44418.5833 | 0 | 10.6424 | 39.95
2021-08-10 14:30 | 44418.6042 | 0 | 9.9952 | 39.95
2021-08-10 15:00 | 44418.625 | 0 | 9.5727 | 39.95
2021-08-10 15:30 | 44418.6458 | 0 | 10.8522 | 39.95
2021-08-10 16:00 | 44418.6667 | 0 | 11.2885 | 39.95
2021-08-10 16:30 | 44418.6875 | 0 | 11.9233 | 39.95
2021-08-10 17:00 | 44418.7083 | 0 | 12.7271 | 39.95
2021-08-10 17:30 | 44418.7292 | 0 | 13.7202 | 39.95
2021-08-10 18:00 | 44418.75 | 0 | 14.3134 | 39.95
2021-08-10 18:30 | 44418.7708 | 0 | 14.3638 | 39.95
2021-08-10 19:00 | 44418.7917 | 0 | 13.9503 | 39.95
2021-08-10 19:30 | 44418.8125 | 0 | 14.0509 | 39.95
2021-08-10 20:00 | 44418.8333 | 0 | 13.7817 | 39.95
2021-08-10 20:30 | 44418.8542 | 0 | 13.3577 | 39.95
2021-08-10 21:00 | 44418.875 | 0 | 12.7163 | 39.95
2021-08-10 21:30 | 44418.8958 | 0 | 12.1557 | 39.95
2021-08-10 22:00 | 44418.9167 | 0 | 11.4816 | 39.95
2021-08-10 22:30 | 44418.9375 | 0 | 10.6397 | 39.95
2021-08-10 23:00 | 44418.9583 | 0 | 9.8581 | 39.95
2021-08-10 23:30 | 44418.9792 | 0 | 9.2369 | 39.95
2021-08-11 | 44419 | 0 | 8.6922 | 39.95
2021-08-11 00:30 | 44419.0208 | 0 | 8.2673 | 39.95
2021-08-11 01:00 | 44419.0417 | 0 | 8.0772 | 39.95
2021-08-11 01:30 | 44419.0625 | 0 | 7.9487 | 39.95
2021-08-11 02:00 | 44419.0833 | 0 | 7.9335 | 39.95
2021-08-11 02:30 | 44419.1042 | 0 | 7.8597 | 39.95
2021-08-11 03:00 | 44419.125 | 0 | 7.738 | 39.95
2021-08-11 03:30 | 44419.1458 | 0 | 7.9371 | 39.95
2021-08-11 04:00 | 44419.1667 | 0 | 8.2501 | 39.95
2021-08-11 04:30 | 44419.1875 | 0 | 8.7049 | 39.95
2021-08-11 05:00 | 44419.2083 | 0 | 9.3147 | 39.95
2021-08-11 05:30 | 44419.2292 | 0 | 10.2202 | 39.95
2021-08-11 06:00 | 44419.25 | 0 | 11.2281 | 39.95
2021-08-11 06:30 | 44419.2708 | 0 | 11.5629 | 39.95
2021-08-11 07:00 | 44419.2917 | 0 | 12.0859 | 39.95
2021-08-11 07:30 | 44419.3125 | 0 | 11.818 | 39.95
2021-08-11 08:00 | 44419.3333 | 0 | 12.3143 | 39.95
2021-08-11 08:30 | 44419.3542 | 0 | 12.0439 | 39.95
2021-08-11 09:00 | 44419.375 | 0 | 12.2333 | 39.95
2021-08-11 09:30 | 44419.3958 | 0 | 10.9509 | 39.95
2021-08-11 10:00 | 44419.4167 | 0 | 9.5186 | 39.95
2021-08-11 10:30 | 44419.4375 | 0 | 8.7809 | 39.95
2021-08-11 11:00 | 44419.4583 | 0 | 9.9801 | 39.95
2021-08-11 11:30 | 44419.4792 | 0 | 9.0426 | 39.95
2021-08-11 12:00 | 44419.5 | 0 | 9.8852 | 39.95
2021-08-11 12:30 | 44419.5208 | 0 | 8.7456 | 39.95
2021-08-11 13:00 | 44419.5417 | 0 | 8.3417 | 39.95
2021-08-11 13:30 | 44419.5625 | 0 | 8.7581 | 39.95
2021-08-11 14:00 | 44419.5833 | 0 | 8.6963 | 39.95
2021-08-11 14:30 | 44419.6042 | 0 | 9.2524 | 39.95
2021-08-11 15:00 | 44419.625 | 0 | 10.0455 | 39.95
2021-08-11 15:30 | 44419.6458 | 0 | 10.5659 | 39.95
2021-08-11 16:00 | 44419.6667 | 0 | 11.1068 | 39.95
2021-08-11 16:30 | 44419.6875 | 0 | 11.3327 | 39.95
2021-08-11 17:00 | 44419.7083 | 0 | 11.9115 | 39.95
2021-08-11 17:30 | 44419.7292 | 0 | 12.751 | 39.95
2021-08-11 18:00 | 44419.75 | 0 | 13.1388 | 39.95
2021-08-11 18:30 | 44419.7708 | 0 | 13.3608 | 39.95
2021-08-11 19:00 | 44419.7917 | 0 | 13.0032 | 39.95
2021-08-11 19:30 | 44419.8125 | 0 | 12.6218 | 39.95
2021-08-11 20:00 | 44419.8333 | 0 | 12.3582 | 39.95
2021-08-11 20:30 | 44419.8542 | 0 | 11.8854 | 39.95
2021-08-11 21:00 | 44419.875 | 0 | 11.3914 | 39.95
2021-08-11 21:30 | 44419.8958 | 0 | 11.0798 | 39.95
2021-08-11 22:00 | 44419.9167 | 0 | 10.4953 | 39.95
2021-08-11 22:30 | 44419.9375 | 0 | 9.6486 | 39.95
2021-08-11 23:00 | 44419.9583 | 0 | 9.0268 | 39.95
2021-08-11 23:30 | 44419.9792 | 0 | 8.5831 | 39.95
2021-08-12 | 44420 | 0 | 8.1786 | 39.95
2021-08-12 00:30 | 44420.0208 | 0 | 7.7643 | 39.95
2021-08-12 01:00 | 44420.0417 | 0 | 7.6716 | 39.95
2021-08-12 01:30 | 44420.0625 | 0 | 7.5376 | 39.95
2021-08-12 02:00 | 44420.0833 | 0 | 7.4669 | 39.95
2021-08-12 02:30 | 44420.1042 | 0 | 7.2953 | 39.95
2021-08-12 03:00 | 44420.125 | 0 | 7.3694 | 39.95
2021-08-12 03:30 | 44420.1458 | 0 | 7.4257 | 39.95
2021-08-12 04:00 | 44420.1667 | 0 | 7.5921 | 39.95
2021-08-12 04:30 | 44420.1875 | 0 | 8.2706 | 39.95
2021-08-12 05:00 | 44420.2083 | 0 | 8.7217 | 39.95
2021-08-12 05:30 | 44420.2292 | 0 | 9.5136 | 39.95
2021-08-12 06:00 | 44420.25 | 0 | 10.3845 | 39.95
2021-08-12 06:30 | 44420.2708 | 0 | 11.4951 | 39.95
2021-08-12 07:00 | 44420.2917 | 0 | 11.9309 | 39.95
2021-08-12 07:30 | 44420.3125 | 0 | 11.759 | 39.95
2021-08-12 08:00 | 44420.3333 | 0 | 11.1824 | 39.95
2021-08-12 08:30 | 44420.3542 | 0 | 10.3686 | 39.95
2021-08-12 09:00 | 44420.375 | 0 | 9.8601 | 39.95
2021-08-12 09:30 | 44420.3958 | 0 | 9.2663 | 39.95
2021-08-12 10:00 | 44420.4167 | 0 | 8.7739 | 39.95
2021-08-12 10:30 | 44420.4375 | 0 | 8.3302 | 39.95
2021-08-12 11:00 | 44420.4583 | 0 | 8.1224 | 39.95
2021-08-12 11:30 | 44420.4792 | 0 | 7.8638 | 39.95
2021-08-12 12:00 | 44420.5 | 0 | 7.7213 | 39.95
2021-08-12 12:30 | 44420.5208 | 0 | 7.982 | 39.95
2021-08-12 13:00 | 44420.5417 | 0 | 8.0092 | 39.95
2021-08-12 13:30 | 44420.5625 | 0 | 8.2847 | 39.95
2021-08-12 14:00 | 44420.5833 | 0 | 8.8059 | 39.95
2021-08-12 14:30 | 44420.6042 | 0 | 9.0236 | 39.95
2021-08-12 15:00 | 44420.625 | 0 | 9.6708 | 39.95
2021-08-12 15:30 | 44420.6458 | 0 | 10.1267 | 39.95
2021-08-12 16:00 | 44420.6667 | 0 | 10.6569 | 39.95
2021-08-12 16:30 | 44420.6875 | 0 | 11.2495 | 39.95
2021-08-12 17:00 | 44420.7083 | 0 | 11.9501 | 39.95
2021-08-12 17:30 | 44420.7292 | 0 | 12.4501 | 39.95
2021-08-12 18:00 | 44420.75 | 0 | 12.7817 | 39.95
2021-08-12 18:30 | 44420.7708 | 0 | 13.0636 | 39.95
2021-08-12 19:00 | 44420.7917 | 0 | 12.5145 | 39.95
2021-08-12 19:30 | 44420.8125 | 0 | 12.1573 | 39.95
2021-08-12 20:00 | 44420.8333 | 0 | 11.9137 | 39.95
2021-08-12 20:30 | 44420.8542 | 0 | 11.5798 | 39.95
2021-08-12 21:00 | 44420.875 | 0 | 11.1281 | 39.95
2021-08-12 21:30 | 44420.8958 | 0 | 11.2946 | 39.95
2021-08-12 22:00 | 44420.9167 | 0 | 10.8425 | 39.95
2021-08-12 22:30 | 44420.9375 | 0 | 10.0829 | 39.95
2021-08-12 23:00 | 44420.9583 | 0 | 9.4515 | 39.95
2021-08-12 23:30 | 44420.9792 | 0 | 9.1109 | 39.95
2021-08-13 | 44421 | 0 | 8.4508 | 39.95
2021-08-13 00:30 | 44421.0208 | 0 | 8.0721 | 39.95
2021-08-13 01:00 | 44421.0417 | 0 | 7.9494 | 39.95
2021-08-13 01:30 | 44421.0625 | 0 | 7.6563 | 39.95
2021-08-13 02:00 | 44421.0833 | 0 | 7.6454 | 39.95
2021-08-13 02:30 | 44421.1042 | 0 | 7.4225 | 39.95
2021-08-13 03:00 | 44421.125 | 0 | 7.4299 | 39.95
2021-08-13 03:30 | 44421.1458 | 0 | 7.4736 | 39.95
2021-08-13 04:00 | 44421.1667 | 0 | 7.6575 | 39.95
2021-08-13 04:30 | 44421.1875 | 0 | 8.0688 | 39.95
2021-08-13 05:00 | 44421.2083 | 0 | 8.6872 | 39.95
2021-08-13 05:30 | 44421.2292 | 0 | 9.2524 | 39.95
2021-08-13 06:00 | 44421.25 | 0 | 10.0436 | 39.95
2021-08-13 06:30 | 44421.2708 | 0 | 10.8197 | 39.95
2021-08-13 07:00 | 44421.2917 | 0 | 11.6353 | 39.95
2021-08-13 07:30 | 44421.3125 | 0 | 11.1718 | 39.95
2021-08-13 08:00 | 44421.3333 | 0 | 10.7917 | 39.95
2021-08-13 08:30 | 44421.3542 | 0 | 10.11 | 39.95
2021-08-13 09:00 | 44421.375 | 0 | 9.4605 | 39.95
2021-08-13 09:30 | 44421.3958 | 0 | 8.8166 | 39.95
2021-08-13 10:00 | 44421.4167 | 0 | 8.4576 | 39.95
2021-08-13 10:30 | 44421.4375 | 0 | 8.1775 | 39.95
2021-08-13 11:00 | 44421.4583 | 0 | 8.1009 | 39.95
2021-08-13 11:30 | 44421.4792 | 0 | 7.854 | 39.95
2021-08-13 12:00 | 44421.5 | 0 | 8.0048 | 39.95
2021-08-13 12:30 | 44421.5208 | 0 | 8.1953 | 39.95
2021-08-13 13:00 | 44421.5417 | 0 | 9.1719 | 39.95
2021-08-13 13:30 | 44421.5625 | 0 | 9.6177 | 39.95
2021-08-13 14:00 | 44421.5833 | 0 | 9.3924 | 39.95
2021-08-13 14:30 | 44421.6042 | 0 | 8.9753 | 39.95
2021-08-13 15:00 | 44421.625 | 0 | 9.3608 | 39.95
2021-08-13 15:30 | 44421.6458 | 0 | 10.2888 | 39.95
2021-08-13 16:00 | 44421.6667 | 0 | 11.3045 | 39.95
2021-08-13 16:30 | 44421.6875 | 0 | 11.7852 | 39.95
2021-08-13 17:00 | 44421.7083 | 0 | 12.1625 | 39.95
2021-08-13 17:30 | 44421.7292 | 0 | 12.3051 | 39.95
2021-08-13 18:00 | 44421.75 | 0 | 12.2966 | 39.95
2021-08-13 18:30 | 44421.7708 | 0 | 12.1974 | 39.95
2021-08-13 19:00 | 44421.7917 | 0 | 12.0067 | 39.95
2021-08-13 19:30 | 44421.8125 | 0 | 11.7156 | 39.95
2021-08-13 20:00 | 44421.8333 | 0 | 11.3882 | 39.95
2021-08-13 20:30 | 44421.8542 | 0 | 10.9323 | 39.95
2021-08-13 21:00 | 44421.875 | 0 | 10.5979 | 39.95
2021-08-13 21:30 | 44421.8958 | 0 | 10.2884 | 39.95
2021-08-13 22:00 | 44421.9167 | 0 | 9.8997 | 39.95
2021-08-13 22:30 | 44421.9375 | 0 | 9.3751 | 39.95
2021-08-13 23:00 | 44421.9583 | 0 | 8.8459 | 39.95
2021-08-13 23:30 | 44421.9792 | 0 | 8.3563 | 39.95
2021-08-14 | 44422 | 0 | 7.9142 | 39.95
2021-08-14 00:30 | 44422.0208 | 0 | 7.6325 | 39.95
2021-08-14 01:00 | 44422.0417 | 0 | 7.3922 | 39.95
2021-08-14 01:30 | 44422.0625 | 0 | 7.2563 | 39.95
2021-08-14 02:00 | 44422.0833 | 0 | 7.2082 | 39.95
2021-08-14 02:30 | 44422.1042 | 0 | 7.0332 | 39.95
2021-08-14 03:00 | 44422.125 | 0 | 7.1088 | 39.95
2021-08-14 03:30 | 44422.1458 | 0 | 7.1821 | 39.95
2021-08-14 04:00 | 44422.1667 | 0 | 7.2072 | 39.95
2021-08-14 04:30 | 44422.1875 | 0 | 7.407 | 39.95
2021-08-14 05:00 | 44422.2083 | 0 | 7.5738 | 39.95
2021-08-14 05:30 | 44422.2292 | 0 | 7.8612 | 39.95
2021-08-14 06:00 | 44422.25 | 0 | 8.2064 | 39.95
2021-08-14 06:30 | 44422.2708 | 0 | 8.6619 | 39.95
2021-08-14 07:00 | 44422.2917 | 0 | 8.9218 | 39.95
2021-08-14 07:30 | 44422.3125 | 0 | 9.1457 | 39.95
2021-08-14 08:00 | 44422.3333 | 0 | 9.4083 | 39.95
2021-08-14 08:30 | 44422.3542 | 0 | 9.0273 | 39.95
2021-08-14 09:00 | 44422.375 | 0 | 9.065 | 39.95
2021-08-14 09:30 | 44422.3958 | 0 | 8.3388 | 39.95
2021-08-14 10:00 | 44422.4167 | 0 | 7.735 | 39.95
2021-08-14 10:30 | 44422.4375 | 0 | 7.2392 | 39.95
2021-08-14 11:00 | 44422.4583 | 0 | 6.9126 | 39.95
2021-08-14 11:30 | 44422.4792 | 0 | 6.8956 | 39.95
2021-08-14 12:00 | 44422.5 | 0 | 6.6278 | 39.95
2021-08-14 12:30 | 44422.5208 | 0 | 6.4812 | 39.95
2021-08-14 13:00 | 44422.5417 | 0 | 6.6804 | 39.95
2021-08-14 13:30 | 44422.5625 | 0 | 6.4899 | 39.95
2021-08-14 14:00 | 44422.5833 | 0 | 6.7133 | 39.95
2021-08-14 14:30 | 44422.6042 | 0 | 7.2566 | 39.95
2021-08-14 15:00 | 44422.625 | 0 | 7.7721 | 39.95
2021-08-14 15:30 | 44422.6458 | 0 | 8.4012 | 39.95
2021-08-14 16:00 | 44422.6667 | 0 | 9.1368 | 39.95
2021-08-14 16:30 | 44422.6875 | 0 | 9.9155 | 39.95
2021-08-14 17:00 | 44422.7083 | 0 | 10.3571 | 39.95
2021-08-14 17:30 | 44422.7292 | 0 | 10.7391 | 39.95
2021-08-14 18:00 | 44422.75 | 0 | 11.0909 | 39.95
2021-08-14 18:30 | 44422.7708 | 0 | 11.0468 | 39.95
2021-08-14 19:00 | 44422.7917 | 0 | 10.9363 | 39.95
2021-08-14 19:30 | 44422.8125 | 0 | 10.7979 | 39.95
2021-08-14 20:00 | 44422.8333 | 0 | 10.4867 | 39.95
2021-08-14 20:30 | 44422.8542 | 0 | 10.1211 | 39.95
2021-08-14 21:00 | 44422.875 | 0 | 9.7916 | 39.95
2021-08-14 21:30 | 44422.8958 | 0 | 9.5671 | 39.95
2021-08-14 22:00 | 44422.9167 | 0 | 9.1538 | 39.95
2021-08-14 22:30 | 44422.9375 | 0 | 8.7948 | 39.95
2021-08-14 23:00 | 44422.9583 | 0 | 8.3295 | 39.95
2021-08-14 23:30 | 44422.9792 | 0 | 8.0377 | 39.95
2021-08-15 | 44423 | 0 | 7.4701 | 39.95
2021-08-15 00:30 | 44423.0208 | 0 | 7.2569 | 39.95
2021-08-15 01:00 | 44423.0417 | 0 | 7.1303 | 39.95
2021-08-15 01:30 | 44423.0625 | 0 | 6.8281 | 39.95
2021-08-15 02:00 | 44423.0833 | 0 | 6.8318 | 39.95
2021-08-15 02:30 | 44423.1042 | 0 | 6.8263 | 39.95
2021-08-15 03:00 | 44423.125 | 0 | 6.6829 | 39.95
2021-08-15 03:30 | 44423.1458 | 0 | 6.7541 | 39.95
2021-08-15 04:00 | 44423.1667 | 0 | 6.7147 | 39.95
2021-08-15 04:30 | 44423.1875 | 0 | 6.6865 | 39.95
2021-08-15 05:00 | 44423.2083 | 0 | 6.8358 | 39.95
2021-08-15 05:30 | 44423.2292 | 0 | 6.9302 | 39.95
2021-08-15 06:00 | 44423.25 | 0 | 7.1587 | 39.95
2021-08-15 06:30 | 44423.2708 | 0 | 7.3935 | 39.95
2021-08-15 07:00 | 44423.2917 | 0 | 7.3086 | 39.95
2021-08-15 07:30 | 44423.3125 | 0 | 7.2992 | 39.95
2021-08-15 08:00 | 44423.3333 | 0 | 7.1263 | 39.95
2021-08-15 08:30 | 44423.3542 | 0 | 6.9252 | 39.95
2021-08-15 09:00 | 44423.375 | 0 | 6.6018 | 39.95
2021-08-15 09:30 | 44423.3958 | 0 | 6.2964 | 39.95
2021-08-15 10:00 | 44423.4167 | 0 | 5.9777 | 39.95
2021-08-15 10:30 | 44423.4375 | 0 | 6.1184 | 39.95
2021-08-15 11:00 | 44423.4583 | 0 | 5.4647 | 39.95
2021-08-15 11:30 | 44423.4792 | 0 | 5.6356 | 39.95
2021-08-15 12:00 | 44423.5 | 0 | 6.1685 | 39.95
2021-08-15 12:30 | 44423.5208 | 0 | 5.5933 | 39.95
2021-08-15 13:00 | 44423.5417 | 0 | 5.3924 | 39.95
2021-08-15 13:30 | 44423.5625 | 0 | 5.8066 | 39.95
2021-08-15 14:00 | 44423.5833 | 0 | 7.9824 | 39.95
2021-08-15 14:30 | 44423.6042 | 0 | 9.4423 | 39.95
2021-08-15 15:00 | 44423.625 | 0 | 9.494 | 39.95
2021-08-15 15:30 | 44423.6458 | 0 | 8.9431 | 39.95
2021-08-15 16:00 | 44423.6667 | 0 | 8.5252 | 39.95
2021-08-15 16:30 | 44423.6875 | 0 | 9.6396 | 39.95
2021-08-15 17:00 | 44423.7083 | 0 | 10.4378 | 39.95
2021-08-15 17:30 | 44423.7292 | 0 | 11.1339 | 39.95
2021-08-15 18:00 | 44423.75 | 0 | 11.6452 | 39.95
2021-08-15 18:30 | 44423.7708 | 0 | 11.6204 | 39.95
2021-08-15 19:00 | 44423.7917 | 0 | 11.3291 | 39.95
2021-08-15 19:30 | 44423.8125 | 0 | 10.9774 | 39.95
2021-08-15 20:00 | 44423.8333 | 0 | 10.769 | 39.95
2021-08-15 20:30 | 44423.8542 | 0 | 10.2843 | 39.95
2021-08-15 21:00 | 44423.875 | 0 | 9.8462 | 39.95
2021-08-15 21:30 | 44423.8958 | 0 | 9.5083 | 39.95
2021-08-15 22:00 | 44423.9167 | 0 | 8.9888 | 39.95
2021-08-15 22:30 | 44423.9375 | 0 | 8.4172 | 39.95
2021-08-15 23:00 | 44423.9583 | 0 | 7.7766 | 39.95
2021-08-15 23:30 | 44423.9792 | 0 | 7.4917 | 39.95
2021-08-16 | 44424 | 0 | 7.2436 | 39.95
2021-08-16 00:30 | 44424.0208 | 0 | 7.0446 | 39.95
2021-08-16 01:00 | 44424.0417 | 0 | 6.8001 | 39.95
2021-08-16 01:30 | 44424.0625 | 0 | 6.692 | 39.95
2021-08-16 02:00 | 44424.0833 | 0 | 6.7652 | 39.95
2021-08-16 02:30 | 44424.1042 | 0 | 6.7239 | 39.95
2021-08-16 03:00 | 44424.125 | 0 | 6.6569 | 39.95
2021-08-16 03:30 | 44424.1458 | 0 | 6.8278 | 39.95
2021-08-16 04:00 | 44424.1667 | 0 | 7.1864 | 39.95
2021-08-16 04:30 | 44424.1875 | 0 | 7.5845 | 39.95
2021-08-16 05:00 | 44424.2083 | 0 | 8.2834 | 39.95
2021-08-16 05:30 | 44424.2292 | 0 | 9.0908 | 39.95
2021-08-16 06:00 | 44424.25 | 0 | 9.8645 | 39.95
2021-08-16 06:30 | 44424.2708 | 0 | 10.9841 | 39.95
2021-08-16 07:00 | 44424.2917 | 0 | 11.5409 | 39.95
2021-08-16 07:30 | 44424.3125 | 0 | 11.3287 | 39.95
2021-08-16 08:00 | 44424.3333 | 0 | 10.8883 | 39.95
2021-08-16 08:30 | 44424.3542 | 0 | 10.1929 | 39.95
2021-08-16 09:00 | 44424.375 | 0 | 9.6306 | 39.95
2021-08-16 09:30 | 44424.3958 | 0 | 9.2268 | 39.95
2021-08-16 10:00 | 44424.4167 | 0 | 8.8445 | 39.95
2021-08-16 10:30 | 44424.4375 | 0 | 8.7359 | 39.95
2021-08-16 11:00 | 44424.4583 | 0 | 8.5431 | 39.95
2021-08-16 11:30 | 44424.4792 | 0 | 8.3923 | 39.95
2021-08-16 12:00 | 44424.5 | 0 | 8.2301 | 39.95
2021-08-16 12:30 | 44424.5208 | 0 | 8.4844 | 39.95
2021-08-16 13:00 | 44424.5417 | 0 | 9.5751 | 39.95
2021-08-16 13:30 | 44424.5625 | 0 | 10.9979 | 39.95
2021-08-16 14:00 | 44424.5833 | 0 | 9.4686 | 39.95
2021-08-16 14:30 | 44424.6042 | 0 | 10.5136 | 39.95
2021-08-16 15:00 | 44424.625 | 0 | 11.0527 | 39.95
2021-08-16 15:30 | 44424.6458 | 0 | 11.3976 | 39.95
2021-08-16 16:00 | 44424.6667 | 0 | 11.7166 | 39.95
2021-08-16 16:30 | 44424.6875 | 0 | 12.1327 | 39.95
2021-08-16 17:00 | 44424.7083 | 0 | 12.6749 | 39.95
2021-08-16 17:30 | 44424.7292 | 0 | 13.3262 | 39.95
2021-08-16 18:00 | 44424.75 | 0 | 13.6682 | 39.95
2021-08-16 18:30 | 44424.7708 | 0 | 13.5493 | 39.95
2021-08-16 19:00 | 44424.7917 | 0 | 13.0189 | 39.95
2021-08-16 19:30 | 44424.8125 | 0 | 12.7287 | 39.95
2021-08-16 20:00 | 44424.8333 | 0 | 12.2984 | 39.95
2021-08-16 20:30 | 44424.8542 | 0 | 11.9208 | 39.95
2021-08-16 21:00 | 44424.875 | 0 | 11.4884 | 39.95
2021-08-16 21:30 | 44424.8958 | 0 | 10.9565 | 39.95
2021-08-16 22:00 | 44424.9167 | 0 | 10.3994 | 39.95
2021-08-16 22:30 | 44424.9375 | 0 | 9.6956 | 39.95
2021-08-16 23:00 | 44424.9583 | 0 | 9.0099 | 39.95
2021-08-16 23:30 | 44424.9792 | 0 | 8.593 | 39.95
2021-08-17 | 44425 | 0 | 8.1604 | 39.95
2021-08-17 00:30 | 44425.0208 | 0 | 7.8184 | 39.95
2021-08-17 01:00 | 44425.0417 | 0 | 7.7814 | 39.95
2021-08-17 01:30 | 44425.0625 | 0 | 7.5402 | 39.95
2021-08-17 02:00 | 44425.0833 | 0 | 7.5283 | 39.95
2021-08-17 02:30 | 44425.1042 | 0 | 7.3959 | 39.95
2021-08-17 03:00 | 44425.125 | 0 | 7.4364 | 39.95
2021-08-17 03:30 | 44425.1458 | 0 | 7.6024 | 39.95
2021-08-17 04:00 | 44425.1667 | 0 | 7.7134 | 39.95
2021-08-17 04:30 | 44425.1875 | 0 | 8.0793 | 39.95
2021-08-17 05:00 | 44425.2083 | 0 | 8.8985 | 39.95
2021-08-17 05:30 | 44425.2292 | 0 | 9.433 | 39.95
2021-08-17 06:00 | 44425.25 | 0 | 10.5086 | 39.95
2021-08-17 06:30 | 44425.2708 | 0 | 11.4574 | 39.95
2021-08-17 07:00 | 44425.2917 | 0 | 11.8289 | 39.95
2021-08-17 07:30 | 44425.3125 | 0 | 11.5558 | 39.95
2021-08-17 08:00 | 44425.3333 | 0 | 10.914 | 39.95
2021-08-17 08:30 | 44425.3542 | 0 | 9.9537 | 39.95
2021-08-17 09:00 | 44425.375 | 0 | 9.2257 | 39.95
2021-08-17 09:30 | 44425.3958 | 0 | 8.6993 | 39.95
2021-08-17 10:00 | 44425.4167 | 0 | 8.3274 | 39.95
2021-08-17 10:30 | 44425.4375 | 0 | 8.0999 | 39.95
2021-08-17 11:00 | 44425.4583 | 0 | 7.8335 | 39.95
2021-08-17 11:30 | 44425.4792 | 0 | 7.7267 | 39.95
2021-08-17 12:00 | 44425.5 | 0 | 7.8188 | 39.95
2021-08-17 12:30 | 44425.5208 | 0 | 7.8889 | 39.95
2021-08-17 13:00 | 44425.5417 | 0 | 7.9905 | 39.95
2021-08-17 13:30 | 44425.5625 | 0 | 8.3382 | 39.95
2021-08-17 14:00 | 44425.5833 | 0 | 8.9134 | 39.95
2021-08-17 14:30 | 44425.6042 | 0 | 9.4556 | 39.95
2021-08-17 15:00 | 44425.625 | 0 | 9.8136 | 39.95
2021-08-17 15:30 | 44425.6458 | 0 | 10.534 | 39.95
2021-08-17 16:00 | 44425.6667 | 0 | 11.3233 | 39.95
2021-08-17 16:30 | 44425.6875 | 0 | 11.8876 | 39.95
2021-08-17 17:00 | 44425.7083 | 0 | 12.3537 | 39.95
2021-08-17 17:30 | 44425.7292 | 0 | 13.1239 | 39.95
2021-08-17 18:00 | 44425.75 | 0 | 13.5713 | 39.95
2021-08-17 18:30 | 44425.7708 | 0 | 13.5862 | 39.95
2021-08-17 19:00 | 44425.7917 | 0 | 13.1771 | 39.95
2021-08-17 19:30 | 44425.8125 | 0 | 12.9996 | 39.95
2021-08-17 20:00 | 44425.8333 | 0 | 12.5831 | 39.95
2021-08-17 20:30 | 44425.8542 | 0 | 12.1333 | 39.95
2021-08-17 21:00 | 44425.875 | 0 | 11.4707 | 39.95
2021-08-17 21:30 | 44425.8958 | 0 | 11.0851 | 39.95
2021-08-17 22:00 | 44425.9167 | 0 | 10.5129 | 39.95
2021-08-17 22:30 | 44425.9375 | 0 | 9.861 | 39.95
2021-08-17 23:00 | 44425.9583 | 0 | 9.269 | 39.95
2021-08-17 23:30 | 44425.9792 | 0 | 8.6984 | 39.95
2021-08-18 | 44426 | 0 | 8.229 | 39.95
2021-08-18 00:30 | 44426.0208 | 0 | 7.9766 | 39.95
2021-08-18 01:00 | 44426.0417 | 0 | 7.7891 | 39.95
2021-08-18 01:30 | 44426.0625 | 0 | 7.5927 | 39.95
2021-08-18 02:00 | 44426.0833 | 0 | 7.6042 | 39.95
2021-08-18 02:30 | 44426.1042 | 0 | 7.5207 | 39.95
2021-08-18 03:00 | 44426.125 | 0 | 7.5686 | 39.95
2021-08-18 03:30 | 44426.1458 | 0 | 7.7193 | 39.95
2021-08-18 04:00 | 44426.1667 | 0 | 7.9588 | 39.95
2021-08-18 04:30 | 44426.1875 | 0 | 8.3478 | 39.95
2021-08-18 05:00 | 44426.2083 | 0 | 8.9788 | 39.95
2021-08-18 05:30 | 44426.2292 | 0 | 9.7976 | 39.95
2021-08-18 06:00 | 44426.25 | 0 | 10.678 | 39.95
2021-08-18 06:30 | 44426.2708 | 0 | 11.5455 | 39.95
2021-08-18 07:00 | 44426.2917 | 0 | 12.034 | 39.95
2021-08-18 07:30 | 44426.3125 | 0 | 11.646 | 39.95
2021-08-18 08:00 | 44426.3333 | 0 | 12.6657 | 39.95
2021-08-18 08:30 | 44426.3542 | 0 | 13.3732 | 39.95
2021-08-18 09:00 | 44426.375 | 0 | 13.4072 | 39.95
2021-08-18 09:30 | 44426.3958 | 0 | 13.0076 | 39.95
2021-08-18 10:00 | 44426.4167 | 0 | 12.3536 | 39.95
2021-08-18 10:30 | 44426.4375 | 0 | 12.3355 | 39.95
2021-08-18 11:00 | 44426.4583 | 0 | 11.4696 | 39.95
2021-08-18 11:30 | 44426.4792 | 0 | 11.0351 | 39.95
2021-08-18 12:00 | 44426.5 | 0 | 11.1603 | 39.95
2021-08-18 12:30 | 44426.5208 | 0 | 12.6436 | 39.95
2021-08-18 13:00 | 44426.5417 | 0 | 11.8539 | 39.95
2021-08-18 13:30 | 44426.5625 | 0 | 11.7482 | 39.95
2021-08-18 14:00 | 44426.5833 | 0 | 12.0854 | 39.95
2021-08-18 14:30 | 44426.6042 | 0 | 12.0556 | 39.95
2021-08-18 15:00 | 44426.625 | 0 | 12.2308 | 39.95
2021-08-18 15:30 | 44426.6458 | 0 | 12.769 | 39.95
2021-08-18 16:00 | 44426.6667 | 0 | 12.6258 | 39.95
2021-08-18 16:30 | 44426.6875 | 0 | 12.7122 | 39.95
2021-08-18 17:00 | 44426.7083 | 0 | 13.3747 | 39.95
2021-08-18 17:30 | 44426.7292 | 0 | 14.0565 | 39.95
2021-08-18 18:00 | 44426.75 | 0 | 14.6593 | 39.95
2021-08-18 18:30 | 44426.7708 | 0 | 14.8311 | 39.95
2021-08-18 19:00 | 44426.7917 | 0 | 14.5353 | 39.95
2021-08-18 19:30 | 44426.8125 | 0 | 14.3122 | 39.95
2021-08-18 20:00 | 44426.8333 | 0 | 13.6909 | 39.95
2021-08-18 20:30 | 44426.8542 | 0 | 13.0758 | 39.95
2021-08-18 21:00 | 44426.875 | 0 | 12.4671 | 39.95
2021-08-18 21:30 | 44426.8958 | 0 | 11.9675 | 39.95
2021-08-18 22:00 | 44426.9167 | 0 | 11.1711 | 39.95
2021-08-18 22:30 | 44426.9375 | 0 | 10.2192 | 39.95
2021-08-18 23:00 | 44426.9583 | 0 | 9.5484 | 39.95
2021-08-18 23:30 | 44426.9792 | 0 | 8.9808 | 39.95
2021-08-19 | 44427 | 0 | 8.4705 | 39.95
2021-08-19 00:30 | 44427.0208 | 0 | 8.1389 | 39.95
2021-08-19 01:00 | 44427.0417 | 0 | 7.9639 | 39.95
2021-08-19 01:30 | 44427.0625 | 0 | 7.8072 | 39.95
2021-08-19 02:00 | 44427.0833 | 0 | 7.8275 | 39.95
2021-08-19 02:30 | 44427.1042 | 0 | 7.7156 | 39.95
2021-08-19 03:00 | 44427.125 | 0 | 7.7048 | 39.95
2021-08-19 03:30 | 44427.1458 | 0 | 7.8734 | 39.95
2021-08-19 04:00 | 44427.1667 | 0 | 8.1459 | 39.95
2021-08-19 04:30 | 44427.1875 | 0 | 8.5901 | 39.95
2021-08-19 05:00 | 44427.2083 | 0 | 9.2589 | 39.95
2021-08-19 05:30 | 44427.2292 | 0 | 10.0938 | 39.95
2021-08-19 06:00 | 44427.25 | 0 | 11.0896 | 39.95
2021-08-19 06:30 | 44427.2708 | 0 | 12.3474 | 39.95
2021-08-19 07:00 | 44427.2917 | 0 | 12.838 | 39.95
2021-08-19 07:30 | 44427.3125 | 0 | 12.3751 | 39.95
2021-08-19 08:00 | 44427.3333 | 0 | 11.7 | 39.95
2021-08-19 08:30 | 44427.3542 | 0 | 10.6348 | 39.95
2021-08-19 09:00 | 44427.375 | 0 | 9.8128 | 39.95
2021-08-19 09:30 | 44427.3958 | 0 | 9.2946 | 39.95
2021-08-19 10:00 | 44427.4167 | 0 | 9.2473 | 39.95
2021-08-19 10:30 | 44427.4375 | 0 | 9.7461 | 39.95
2021-08-19 11:00 | 44427.4583 | 0 | 8.7724 | 39.95
2021-08-19 11:30 | 44427.4792 | 0 | 7.8971 | 39.95
2021-08-19 12:00 | 44427.5 | 0 | 8.3343 | 39.95
2021-08-19 12:30 | 44427.5208 | 0 | 9.3894 | 39.95
2021-08-19 13:00 | 44427.5417 | 0 | 11.5276 | 39.95
2021-08-19 13:30 | 44427.5625 | 0 | 9.5489 | 39.95
2021-08-19 14:00 | 44427.5833 | 0 | 10.3183 | 39.95
2021-08-19 14:30 | 44427.6042 | 0 | 9.1329 | 39.95
2021-08-19 15:00 | 44427.625 | 0 | 10.3214 | 39.95
2021-08-19 15:30 | 44427.6458 | 0 | 11.3583 | 39.95
2021-08-19 16:00 | 44427.6667 | 0 | 11.7538 | 39.95
2021-08-19 16:30 | 44427.6875 | 0 | 11.7259 | 39.95
2021-08-19 17:00 | 44427.7083 | 0 | 12.5428 | 39.95
2021-08-19 17:30 | 44427.7292 | 0 | 13.3803 | 39.95
2021-08-19 18:00 | 44427.75 | 0 | 13.9802 | 39.95
2021-08-19 18:30 | 44427.7708 | 0 | 14.2803 | 39.95
2021-08-19 19:00 | 44427.7917 | 0 | 13.7581 | 39.95
2021-08-19 19:30 | 44427.8125 | 0 | 13.4037 | 39.95
2021-08-19 20:00 | 44427.8333 | 0 | 13.2901 | 39.95
2021-08-19 20:30 | 44427.8542 | 0 | 13.0189 | 39.95
2021-08-19 21:00 | 44427.875 | 0 | 12.4214 | 39.95
2021-08-19 21:30 | 44427.8958 | 0 | 11.716 | 39.95
2021-08-19 22:00 | 44427.9167 | 0 | 11.044 | 39.95
2021-08-19 22:30 | 44427.9375 | 0 | 10.3028 | 39.95
2021-08-19 23:00 | 44427.9583 | 0 | 9.6567 | 39.95
2021-08-19 23:30 | 44427.9792 | 0 | 9.1627 | 39.95
2021-08-20 | 44428 | 0 | 8.7836 | 39.95
2021-08-20 00:30 | 44428.0208 | 0 | 8.286 | 39.95
2021-08-20 01:00 | 44428.0417 | 0 | 8.1462 | 39.95
2021-08-20 01:30 | 44428.0625 | 0 | 7.8951 | 39.95
2021-08-20 02:00 | 44428.0833 | 0 | 7.7808 | 39.95
2021-08-20 02:30 | 44428.1042 | 0 | 7.8015 | 39.95
2021-08-20 03:00 | 44428.125 | 0 | 7.7496 | 39.95
2021-08-20 03:30 | 44428.1458 | 0 | 7.846 | 39.95
2021-08-20 04:00 | 44428.1667 | 0 | 8.071 | 39.95
2021-08-20 04:30 | 44428.1875 | 0 | 8.4687 | 39.95
2021-08-20 05:00 | 44428.2083 | 0 | 9.2428 | 39.95
2021-08-20 05:30 | 44428.2292 | 0 | 10.0072 | 39.95
2021-08-20 06:00 | 44428.25 | 0 | 10.8287 | 39.95
2021-08-20 06:30 | 44428.2708 | 0 | 11.8222 | 39.95
2021-08-20 07:00 | 44428.2917 | 0 | 12.268 | 39.95
2021-08-20 07:30 | 44428.3125 | 0 | 11.8572 | 39.95
2021-08-20 08:00 | 44428.3333 | 0 | 11.3137 | 39.95
2021-08-20 08:30 | 44428.3542 | 0 | 10.4187 | 39.95
2021-08-20 09:00 | 44428.375 | 0 | 9.7198 | 39.95
2021-08-20 09:30 | 44428.3958 | 0 | 9.2704 | 39.95
2021-08-20 10:00 | 44428.4167 | 0 | 8.7832 | 39.95
2021-08-20 10:30 | 44428.4375 | 0 | 8.5006 | 39.95
2021-08-20 11:00 | 44428.4583 | 0 | 8.3993 | 39.95
2021-08-20 11:30 | 44428.4792 | 0 | 8.6815 | 39.95
2021-08-20 12:00 | 44428.5 | 0 | 8.4127 | 39.95
2021-08-20 12:30 | 44428.5208 | 0 | 8.4844 | 39.95
2021-08-20 13:00 | 44428.5417 | 0 | 9.7341 | 39.95
2021-08-20 13:30 | 44428.5625 | 0 | 9.0426 | 39.95
2021-08-20 14:00 | 44428.5833 | 0 | 9.0067 | 39.95
2021-08-20 14:30 | 44428.6042 | 0 | 9.4881 | 39.95
2021-08-20 15:00 | 44428.625 | 0 | 10.1056 | 39.95
2021-08-20 15:30 | 44428.6458 | 0 | 10.5753 | 39.95
2021-08-20 16:00 | 44428.6667 | 0 | 11.2582 | 39.95
2021-08-20 16:30 | 44428.6875 | 0 | 12.1304 | 39.95
2021-08-20 17:00 | 44428.7083 | 0 | 12.2232 | 39.95
2021-08-20 17:30 | 44428.7292 | 0 | 12.8196 | 39.95
2021-08-20 18:00 | 44428.75 | 0 | 12.9219 | 39.95
2021-08-20 18:30 | 44428.7708 | 0 | 13.0563 | 39.95
2021-08-20 19:00 | 44428.7917 | 0 | 12.7721 | 39.95
2021-08-20 19:30 | 44428.8125 | 0 | 12.7167 | 39.95
2021-08-20 20:00 | 44428.8333 | 0 | 12.4528 | 39.95
2021-08-20 20:30 | 44428.8542 | 0 | 11.9891 | 39.95
2021-08-20 21:00 | 44428.875 | 0 | 11.4708 | 39.95
2021-08-20 21:30 | 44428.8958 | 0 | 11.1653 | 39.95
2021-08-20 22:00 | 44428.9167 | 0 | 10.5604 | 39.95
2021-08-20 22:30 | 44428.9375 | 0 | 10.0404 | 39.95
2021-08-20 23:00 | 44428.9583 | 0 | 9.5873 | 39.95
2021-08-20 23:30 | 44428.9792 | 0 | 9.0803 | 39.95
2021-08-21 | 44429 | 0 | 8.5489 | 39.95
2021-08-21 00:30 | 44429.0208 | 0 | 8.1202 | 39.95
2021-08-21 01:00 | 44429.0417 | 0 | 7.8947 | 39.95
2021-08-21 01:30 | 44429.0625 | 0 | 7.6565 | 39.95
2021-08-21 02:00 | 44429.0833 | 0 | 7.6068 | 39.95
2021-08-21 02:30 | 44429.1042 | 0 | 7.3867 | 39.95
2021-08-21 03:00 | 44429.125 | 0 | 7.3641 | 39.95
2021-08-21 03:30 | 44429.1458 | 0 | 7.4219 | 39.95
2021-08-21 04:00 | 44429.1667 | 0 | 7.4217 | 39.95
2021-08-21 04:30 | 44429.1875 | 0 | 7.5774 | 39.95
2021-08-21 05:00 | 44429.2083 | 0 | 7.8683 | 39.95
2021-08-21 05:30 | 44429.2292 | 0 | 7.9742 | 39.95
2021-08-21 06:00 | 44429.25 | 0 | 8.3965 | 39.95
2021-08-21 06:30 | 44429.2708 | 0 | 8.7282 | 39.95
2021-08-21 07:00 | 44429.2917 | 0 | 8.7514 | 39.95
2021-08-21 07:30 | 44429.3125 | 0 | 8.4902 | 39.95
2021-08-21 08:00 | 44429.3333 | 0 | 8.3773 | 39.95
2021-08-21 08:30 | 44429.3542 | 0 | 7.92 | 39.95
2021-08-21 09:00 | 44429.375 | 0 | 7.6011 | 39.95
2021-08-21 09:30 | 44429.3958 | 0 | 7.152 | 39.95
2021-08-21 10:00 | 44429.4167 | 0 | 6.7012 | 39.95
2021-08-21 10:30 | 44429.4375 | 0 | 6.3732 | 39.95
2021-08-21 11:00 | 44429.4583 | 0 | 6.0884 | 39.95
2021-08-21 11:30 | 44429.4792 | 0 | 5.8604 | 39.95
2021-08-21 12:00 | 44429.5 | 0 | 5.8447 | 39.95
2021-08-21 12:30 | 44429.5208 | 0 | 5.8079 | 39.95
2021-08-21 13:00 | 44429.5417 | 0 | 6.0905 | 39.95
2021-08-21 13:30 | 44429.5625 | 0 | 6.2507 | 39.95
2021-08-21 14:00 | 44429.5833 | 0 | 6.7537 | 39.95
2021-08-21 14:30 | 44429.6042 | 0 | 7.1423 | 39.95
2021-08-21 15:00 | 44429.625 | 0 | 7.8561 | 39.95
2021-08-21 15:30 | 44429.6458 | 0 | 8.5051 | 39.95
2021-08-21 16:00 | 44429.6667 | 0 | 9.0513 | 39.95
2021-08-21 16:30 | 44429.6875 | 0 | 9.828 | 39.95
2021-08-21 17:00 | 44429.7083 | 0 | 10.2002 | 39.95
2021-08-21 17:30 | 44429.7292 | 0 | 10.6058 | 39.95
2021-08-21 18:00 | 44429.75 | 0 | 11.0163 | 39.95
2021-08-21 18:30 | 44429.7708 | 0 | 11.1778 | 39.95
2021-08-21 19:00 | 44429.7917 | 0 | 10.81 | 39.95
2021-08-21 19:30 | 44429.8125 | 0 | 10.735 | 39.95
2021-08-21 20:00 | 44429.8333 | 0 | 10.4931 | 39.95
2021-08-21 20:30 | 44429.8542 | 0 | 10.1449 | 39.95
2021-08-21 21:00 | 44429.875 | 0 | 9.834 | 39.95
2021-08-21 21:30 | 44429.8958 | 0 | 9.5509 | 39.95
2021-08-21 22:00 | 44429.9167 | 0 | 9.2729 | 39.95
2021-08-21 22:30 | 44429.9375 | 0 | 8.8351 | 39.95
2021-08-21 23:00 | 44429.9583 | 0 | 8.4089 | 39.95
2021-08-21 23:30 | 44429.9792 | 0 | 7.9339 | 39.95
2021-08-22 | 44430 | 0 | 7.5603 | 39.95
2021-08-22 00:30 | 44430.0208 | 0 | 7.3927 | 39.95
2021-08-22 01:00 | 44430.0417 | 0 | 7.0665 | 39.95
2021-08-22 01:30 | 44430.0625 | 0 | 7.0187 | 39.95
2021-08-22 02:00 | 44430.0833 | 0 | 6.9028 | 39.95
2021-08-22 02:30 | 44430.1042 | 0 | 6.8207 | 39.95
2021-08-22 03:00 | 44430.125 | 0 | 6.8764 | 39.95
2021-08-22 03:30 | 44430.1458 | 0 | 6.8209 | 39.95
2021-08-22 04:00 | 44430.1667 | 0 | 6.7875 | 39.95
2021-08-22 04:30 | 44430.1875 | 0 | 6.8275 | 39.95
2021-08-22 05:00 | 44430.2083 | 0 | 7.0203 | 39.95
2021-08-22 05:30 | 44430.2292 | 0 | 7.0227 | 39.95
2021-08-22 06:00 | 44430.25 | 0 | 7.2986 | 39.95
2021-08-22 06:30 | 44430.2708 | 0 | 7.4517 | 39.95
2021-08-22 07:00 | 44430.2917 | 0 | 7.4313 | 39.95
2021-08-22 07:30 | 44430.3125 | 0 | 7.337 | 39.95
2021-08-22 08:00 | 44430.3333 | 0 | 7.1483 | 39.95
2021-08-22 08:30 | 44430.3542 | 0 | 6.9313 | 39.95
2021-08-22 09:00 | 44430.375 | 0 | 6.6652 | 39.95
2021-08-22 09:30 | 44430.3958 | 0 | 6.2673 | 39.95
2021-08-22 10:00 | 44430.4167 | 0 | 5.9819 | 39.95
2021-08-22 10:30 | 44430.4375 | 0 | 5.7353 | 39.95
2021-08-22 11:00 | 44430.4583 | 0 | 5.4335 | 39.95
2021-08-22 11:30 | 44430.4792 | 0 | 5.2556 | 39.95
2021-08-22 12:00 | 44430.5 | 0 | 5.2035 | 39.95
2021-08-22 12:30 | 44430.5208 | 0 | 5.2367 | 39.95
2021-08-22 13:00 | 44430.5417 | 0 | 5.5136 | 39.95
2021-08-22 13:30 | 44430.5625 | 0 | 5.7554 | 39.95
2021-08-22 14:00 | 44430.5833 | 0 | 6.291 | 39.95
2021-08-22 14:30 | 44430.6042 | 0 | 6.7017 | 39.95
2021-08-22 15:00 | 44430.625 | 0 | 7.3987 | 39.95
2021-08-22 15:30 | 44430.6458 | 0 | 8.174 | 39.95
2021-08-22 16:00 | 44430.6667 | 0 | 8.9531 | 39.95
2021-08-22 16:30 | 44430.6875 | 0 | 9.7649 | 39.95
2021-08-22 17:00 | 44430.7083 | 0 | 10.5149 | 39.95
2021-08-22 17:30 | 44430.7292 | 0 | 11.0694 | 39.95
2021-08-22 18:00 | 44430.75 | 0 | 11.7201 | 39.95
2021-08-22 18:30 | 44430.7708 | 0 | 11.8796 | 39.95
2021-08-22 19:00 | 44430.7917 | 0 | 11.4859 | 39.95
2021-08-22 19:30 | 44430.8125 | 0 | 11.76 | 39.95
2021-08-22 20:00 | 44430.8333 | 0 | 11.6236 | 39.95
2021-08-22 20:30 | 44430.8542 | 0 | 11.1206 | 39.95
2021-08-22 21:00 | 44430.875 | 0 | 10.672 | 39.95
2021-08-22 21:30 | 44430.8958 | 0 | 10.3241 | 39.95
2021-08-22 22:00 | 44430.9167 | 0 | 9.6916 | 39.95
2021-08-22 22:30 | 44430.9375 | 0 | 9.0353 | 39.95
2021-08-22 23:00 | 44430.9583 | 0 | 8.4957 | 39.95
2021-08-22 23:30 | 44430.9792 | 0 | 8.1764 | 39.95
2021-08-23 | 44431 | 0 | 7.8312 | 39.95
2021-08-23 00:30 | 44431.0208 | 0 | 7.636 | 39.95
2021-08-23 01:00 | 44431.0417 | 0 | 7.4782 | 39.95
2021-08-23 01:30 | 44431.0625 | 0 | 7.4146 | 39.95
2021-08-23 02:00 | 44431.0833 | 0 | 7.3959 | 39.95
2021-08-23 02:30 | 44431.1042 | 0 | 7.2875 | 39.95
2021-08-23 03:00 | 44431.125 | 0 | 7.4462 | 39.95
2021-08-23 03:30 | 44431.1458 | 0 | 7.6092 | 39.95
2021-08-23 04:00 | 44431.1667 | 0 | 7.8233 | 39.95
2021-08-23 04:30 | 44431.1875 | 0 | 8.3451 | 39.95
2021-08-23 05:00 | 44431.2083 | 0 | 8.6614 | 39.95
2021-08-23 05:30 | 44431.2292 | 0 | 9.266 | 39.95
2021-08-23 06:00 | 44431.25 | 0 | 10.2173 | 39.95
2021-08-23 06:30 | 44431.2708 | 0 | 11.1593 | 39.95
2021-08-23 07:00 | 44431.2917 | 0 | 11.6174 | 39.95
2021-08-23 07:30 | 44431.3125 | 0 | 11.4015 | 39.95
2021-08-23 08:00 | 44431.3333 | 0 | 10.9145 | 39.95
2021-08-23 08:30 | 44431.3542 | 0 | 10.3121 | 39.95
2021-08-23 09:00 | 44431.375 | 0 | 9.1425 | 39.95
2021-08-23 09:30 | 44431.3958 | 0 | 9.2421 | 39.95
2021-08-23 10:00 | 44431.4167 | 0 | 9.5436 | 39.95
2021-08-23 10:30 | 44431.4375 | 0 | 9.3713 | 39.95
2021-08-23 11:00 | 44431.4583 | 0 | 8.7282 | 39.95
2021-08-23 11:30 | 44431.4792 | 0 | 8.3578 | 39.95
2021-08-23 12:00 | 44431.5 | 0 | 8.1798 | 39.95
2021-08-23 12:30 | 44431.5208 | 0 | 8.1611 | 39.95
2021-08-23 13:00 | 44431.5417 | 0 | 8.0371 | 39.95
2021-08-23 13:30 | 44431.5625 | 0 | 8.3925 | 39.95
2021-08-23 14:00 | 44431.5833 | 0 | 8.9579 | 39.95
2021-08-23 14:30 | 44431.6042 | 0 | 9.3481 | 39.95
2021-08-23 15:00 | 44431.625 | 0 | 9.691 | 39.95
2021-08-23 15:30 | 44431.6458 | 0 | 10.5929 | 39.95
2021-08-23 16:00 | 44431.6667 | 0 | 11.2146 | 39.95
2021-08-23 16:30 | 44431.6875 | 0 | 11.8777 | 39.95
2021-08-23 17:00 | 44431.7083 | 0 | 12.3459 | 39.95
2021-08-23 17:30 | 44431.7292 | 0 | 13.1082 | 39.95
2021-08-23 18:00 | 44431.75 | 0 | 13.7766 | 39.95
2021-08-23 18:30 | 44431.7708 | 0 | 13.9247 | 39.95
2021-08-23 19:00 | 44431.7917 | 0 | 13.5959 | 39.95
2021-08-23 19:30 | 44431.8125 | 0 | 13.2278 | 39.95
2021-08-23 20:00 | 44431.8333 | 0 | 12.8566 | 39.95
2021-08-23 20:30 | 44431.8542 | 0 | 12.3862 | 39.95
2021-08-23 21:00 | 44431.875 | 0 | 11.7583 | 39.95
2021-08-23 21:30 | 44431.8958 | 0 | 11.2312 | 39.95
2021-08-23 22:00 | 44431.9167 | 0 | 10.6973 | 39.95
2021-08-23 22:30 | 44431.9375 | 0 | 9.8669 | 39.95
2021-08-23 23:00 | 44431.9583 | 0 | 9.1762 | 39.95
2021-08-23 23:30 | 44431.9792 | 0 | 8.8089 | 39.95
2021-08-24 | 44432 | 0 | 8.3651 | 39.95
2021-08-24 00:30 | 44432.0208 | 0 | 8.0663 | 39.95
2021-08-24 01:00 | 44432.0417 | 0 | 7.7685 | 39.95
2021-08-24 01:30 | 44432.0625 | 0 | 7.6991 | 39.95
2021-08-24 02:00 | 44432.0833 | 0 | 7.6086 | 39.95
2021-08-24 02:30 | 44432.1042 | 0 | 7.5969 | 39.95
2021-08-24 03:00 | 44432.125 | 0 | 7.6541 | 39.95
2021-08-24 03:30 | 44432.1458 | 0 | 7.8386 | 39.95
2021-08-24 04:00 | 44432.1667 | 0 | 7.9414 | 39.95
2021-08-24 04:30 | 44432.1875 | 0 | 8.5277 | 39.95
2021-08-24 05:00 | 44432.2083 | 0 | 9.1719 | 39.95
2021-08-24 05:30 | 44432.2292 | 0 | 9.8208 | 39.95
2021-08-24 06:00 | 44432.25 | 0 | 10.7105 | 39.95
2021-08-24 06:30 | 44432.2708 | 0 | 11.5092 | 39.95
2021-08-24 07:00 | 44432.2917 | 0 | 11.8276 | 39.95
2021-08-24 07:30 | 44432.3125 | 0 | 11.7422 | 39.95
2021-08-24 08:00 | 44432.3333 | 0 | 12.465 | 39.95
2021-08-24 08:30 | 44432.3542 | 0 | 13.286 | 39.95
2021-08-24 09:00 | 44432.375 | 0 | 11.7876 | 39.95
2021-08-24 09:30 | 44432.3958 | 0 | 11.1279 | 39.95
2021-08-24 10:00 | 44432.4167 | 0 | 11.0547 | 39.95
2021-08-24 10:30 | 44432.4375 | 0 | 10.6544 | 39.95
2021-08-24 11:00 | 44432.4583 | 0 | 10.2284 | 39.95
2021-08-24 11:30 | 44432.4792 | 0 | 10.2284 | 39.95
2021-08-24 12:00 | 44432.5 | 0 | 10.2284 | 39.95
2021-08-24 12:30 | 44432.5208 | 0 | 8.7315 | 39.95
2021-08-24 13:00 | 44432.5417 | 0 | 7.5346 | 39.95
2021-08-24 13:30 | 44432.5625 | 0 | 7.7921 | 39.95
2021-08-24 14:00 | 44432.5833 | 0 | 8.2215 | 39.95
2021-08-24 14:30 | 44432.6042 | 0 | 8.7708 | 39.95
2021-08-24 15:00 | 44432.625 | 0 | 9.5915 | 39.95
2021-08-24 15:30 | 44432.6458 | 0 | 10.3711 | 39.95
2021-08-24 16:00 | 44432.6667 | 0 | 11.0948 | 39.95
2021-08-24 16:30 | 44432.6875 | 0 | 11.9543 | 39.95
2021-08-24 17:00 | 44432.7083 | 0 | 12.6551 | 39.95
2021-08-24 17:30 | 44432.7292 | 0 | 13.6973 | 39.95
2021-08-24 18:00 | 44432.75 | 0 | 14.3689 | 39.95
2021-08-24 18:30 | 44432.7708 | 0 | 14.8451 | 39.95
2021-08-24 19:00 | 44432.7917 | 0 | 14.6768 | 39.95
2021-08-24 19:30 | 44432.8125 | 0 | 14.5999 | 39.95
2021-08-24 20:00 | 44432.8333 | 0 | 14.326 | 39.95
2021-08-24 20:30 | 44432.8542 | 0 | 13.8133 | 39.95
2021-08-24 21:00 | 44432.875 | 0 | 12.7962 | 39.95
2021-08-24 21:30 | 44432.8958 | 0 | 12.3006 | 39.95
2021-08-24 22:00 | 44432.9167 | 0 | 11.5538 | 39.95
2021-08-24 22:30 | 44432.9375 | 0 | 10.4605 | 39.95
2021-08-24 23:00 | 44432.9583 | 0 | 9.7809 | 39.95
2021-08-24 23:30 | 44432.9792 | 0 | 9.372 | 39.95
2021-08-25 | 44433 | 0 | 9.0408 | 39.95
2021-08-25 00:30 | 44433.0208 | 0 | 8.4689 | 39.95
2021-08-25 01:00 | 44433.0417 | 0 | 8.1431 | 39.95
2021-08-25 01:30 | 44433.0625 | 0 | 7.9303 | 39.95
2021-08-25 02:00 | 44433.0833 | 0 | 7.9168 | 39.95
2021-08-25 02:30 | 44433.1042 | 0 | 7.8128 | 39.95
2021-08-25 03:00 | 44433.125 | 0 | 7.8701 | 39.95
2021-08-25 03:30 | 44433.1458 | 0 | 8.0561 | 39.95
2021-08-25 04:00 | 44433.1667 | 0 | 8.2848 | 39.95
2021-08-25 04:30 | 44433.1875 | 0 | 8.7128 | 39.95
2021-08-25 05:00 | 44433.2083 | 0 | 9.6432 | 39.95
2021-08-25 05:30 | 44433.2292 | 0 | 10.5773 | 39.95
2021-08-25 06:00 | 44433.25 | 0 | 11.8133 | 39.95
2021-08-25 06:30 | 44433.2708 | 0 | 13.1275 | 39.95
2021-08-25 07:00 | 44433.2917 | 0 | 13.5326 | 39.95
2021-08-25 07:30 | 44433.3125 | 0 | 12.6084 | 39.95
2021-08-25 08:00 | 44433.3333 | 0 | 11.8241 | 39.95
2021-08-25 08:30 | 44433.3542 | 0 | 10.9058 | 39.95
2021-08-25 09:00 | 44433.375 | 0 | 9.7881 | 39.95
2021-08-25 09:30 | 44433.3958 | 0 | 9.0656 | 39.95
2021-08-25 10:00 | 44433.4167 | 0 | 8.6566 | 39.95
2021-08-25 10:30 | 44433.4375 | 0 | 8.0921 | 39.95
2021-08-25 11:00 | 44433.4583 | 0 | 7.8058 | 39.95
2021-08-25 11:30 | 44433.4792 | 0 | 7.6939 | 39.95
2021-08-25 12:00 | 44433.5 | 0 | 7.5523 | 39.95
2021-08-25 12:30 | 44433.5208 | 0 | 7.4865 | 39.95
2021-08-25 13:00 | 44433.5417 | 0 | 7.5983 | 39.95
2021-08-25 13:30 | 44433.5625 | 0 | 8.0368 | 39.95
2021-08-25 14:00 | 44433.5833 | 0 | 8.403 | 39.95
2021-08-25 14:30 | 44433.6042 | 0 | 8.7552 | 39.95
2021-08-25 15:00 | 44433.625 | 0 | 9.4419 | 39.95
2021-08-25 15:30 | 44433.6458 | 0 | 10.2306 | 39.95
2021-08-25 16:00 | 44433.6667 | 0 | 10.9434 | 39.95
2021-08-25 16:30 | 44433.6875 | 0 | 11.7294 | 39.95
2021-08-25 17:00 | 44433.7083 | 0 | 12.3837 | 39.95
2021-08-25 17:30 | 44433.7292 | 0 | 13.3532 | 39.95
2021-08-25 18:00 | 44433.75 | 0 | 14.1482 | 39.95
2021-08-25 18:30 | 44433.7708 | 0 | 14.705 | 39.95
2021-08-25 19:00 | 44433.7917 | 0 | 14.6707 | 39.95
2021-08-25 19:30 | 44433.8125 | 0 | 14.5672 | 39.95
2021-08-25 20:00 | 44433.8333 | 0 | 14.2096 | 39.95
2021-08-25 20:30 | 44433.8542 | 0 | 13.6453 | 39.95
2021-08-25 21:00 | 44433.875 | 0 | 12.8871 | 39.95
2021-08-25 21:30 | 44433.8958 | 0 | 12.4858 | 39.95
2021-08-25 22:00 | 44433.9167 | 0 | 11.7984 | 39.95
2021-08-25 22:30 | 44433.9375 | 0 | 10.8905 | 39.95
2021-08-25 23:00 | 44433.9583 | 0 | 10.0778 | 39.95
2021-08-25 23:30 | 44433.9792 | 0 | 9.5223 | 39.95
2021-08-26 | 44434 | 0 | 8.9139 | 39.95
2021-08-26 00:30 | 44434.0208 | 0 | 8.4858 | 39.95
2021-08-26 01:00 | 44434.0417 | 0 | 8.1152 | 39.95
2021-08-26 01:30 | 44434.0625 | 0 | 8.0772 | 39.95
2021-08-26 02:00 | 44434.0833 | 0 | 7.9303 | 39.95
2021-08-26 02:30 | 44434.1042 | 0 | 7.8701 | 39.95
2021-08-26 03:00 | 44434.125 | 0 | 7.9897 | 39.95
2021-08-26 03:30 | 44434.1458 | 0 | 7.9891 | 39.95
2021-08-26 04:00 | 44434.1667 | 0 | 8.3164 | 39.95
2021-08-26 04:30 | 44434.1875 | 0 | 8.8163 | 39.95
2021-08-26 05:00 | 44434.2083 | 0 | 9.6215 | 39.95
2021-08-26 05:30 | 44434.2292 | 0 | 10.5202 | 39.95
2021-08-26 06:00 | 44434.25 | 0 | 11.8855 | 39.95
2021-08-26 06:30 | 44434.2708 | 0 | 13.2398 | 39.95
2021-08-26 07:00 | 44434.2917 | 0 | 13.7519 | 39.95
2021-08-26 07:30 | 44434.3125 | 0 | 13.0333 | 39.95
2021-08-26 08:00 | 44434.3333 | 0 | 13.1168 | 39.95
2021-08-26 08:30 | 44434.3542 | 0 | 13.0199 | 39.95
2021-08-26 09:00 | 44434.375 | 0 | 13.0199 | 39.95
2021-08-26 09:30 | 44434.3958 | 0 | 13.0199 | 39.95
2021-08-26 10:00 | 44434.4167 | 0 | 13.0199 | 39.95
2021-08-26 10:30 | 44434.4375 | 0 | 8.7794 | 39.95
2021-08-26 11:00 | 44434.4583 | 0 | 8.1894 | 39.95
2021-08-26 11:30 | 44434.4792 | 0 | 7.8803 | 39.95
2021-08-26 12:00 | 44434.5 | 0 | 7.8502 | 39.95
2021-08-26 12:30 | 44434.5208 | 0 | 7.6134 | 39.95
2021-08-26 13:00 | 44434.5417 | 0 | 7.6633 | 39.95
2021-08-26 13:30 | 44434.5625 | 0 | 8.0206 | 39.95
2021-08-26 14:00 | 44434.5833 | 0 | 8.4162 | 39.95
2021-08-26 14:30 | 44434.6042 | 0 | 8.856 | 39.95
2021-08-26 15:00 | 44434.625 | 0 | 9.407 | 39.95
2021-08-26 15:30 | 44434.6458 | 0 | 10.2044 | 39.95
2021-08-26 16:00 | 44434.6667 | 0 | 10.8935 | 39.95
2021-08-26 16:30 | 44434.6875 | 0 | 11.6226 | 39.95
2021-08-26 17:00 | 44434.7083 | 0 | 12.3495 | 39.95
2021-08-26 17:30 | 44434.7292 | 0 | 13.4552 | 39.95
2021-08-26 18:00 | 44434.75 | 0 | 14.2798 | 39.95
2021-08-26 18:30 | 44434.7708 | 0 | 14.5676 | 39.95
2021-08-26 19:00 | 44434.7917 | 0 | 14.2981 | 39.95
2021-08-26 19:30 | 44434.8125 | 0 | 14.3023 | 39.95
2021-08-26 20:00 | 44434.8333 | 0 | 14.0038 | 39.95
2021-08-26 20:30 | 44434.8542 | 0 | 13.5434 | 39.95
2021-08-26 21:00 | 44434.875 | 0 | 12.884 | 39.95
2021-08-26 21:30 | 44434.8958 | 0 | 12.3677 | 39.95
2021-08-26 22:00 | 44434.9167 | 0 | 11.6769 | 39.95
2021-08-26 22:30 | 44434.9375 | 0 | 10.7603 | 39.95
2021-08-26 23:00 | 44434.9583 | 0 | 10.0496 | 39.95
2021-08-26 23:30 | 44434.9792 | 0 | 9.4306 | 39.95
2021-08-27 | 44435 | 0 | 8.932 | 39.95
2021-08-27 00:30 | 44435.0208 | 0 | 8.5349 | 39.95
2021-08-27 01:00 | 44435.0417 | 0 | 8.3512 | 39.95
2021-08-27 01:30 | 44435.0625 | 0 | 8.1068 | 39.95
2021-08-27 02:00 | 44435.0833 | 0 | 8.0187 | 39.95
2021-08-27 02:30 | 44435.1042 | 0 | 7.9319 | 39.95
2021-08-27 03:00 | 44435.125 | 0 | 7.8831 | 39.95
2021-08-27 03:30 | 44435.1458 | 0 | 8.1271 | 39.95
2021-08-27 04:00 | 44435.1667 | 0 | 8.4251 | 39.95
2021-08-27 04:30 | 44435.1875 | 0 | 8.8184 | 39.95
2021-08-27 05:00 | 44435.2083 | 0 | 9.7134 | 39.95
2021-08-27 05:30 | 44435.2292 | 0 | 10.6157 | 39.95
2021-08-27 06:00 | 44435.25 | 0 | 11.9487 | 39.95
2021-08-27 06:30 | 44435.2708 | 0 | 13.2385 | 39.95
2021-08-27 07:00 | 44435.2917 | 0 | 13.6106 | 39.95
2021-08-27 07:30 | 44435.3125 | 0 | 12.8427 | 39.95
2021-08-27 08:00 | 44435.3333 | 0 | 11.168 | 39.95
2021-08-27 08:30 | 44435.3542 | 0 | 0.11809 | 39.95
2021-08-27 09:00 | 44435.375 | 0 | 0.022333 | 39.95
2021-08-27 09:30 | 44435.3958 | 0 | 0.022333 | 39.95
2021-08-27 10:00 | 44435.4167 | 0 | 0.022333 | 39.95
2021-08-27 10:30 | 44435.4375 | 0 | 0.022333 | 39.95
2021-08-27 11:00 | 44435.4583 | 0 | 0.022333 | 39.95
2021-08-27 11:30 | 44435.4792 | 0 | 0.022333 | 39.95
2021-08-27 12:00 | 44435.5 | 0 | 1.4264 | 39.95
2021-08-27 12:30 | 44435.5208 | 0 | 7.4271 | 39.95
2021-08-27 13:00 | 44435.5417 | 0 | 7.5442 | 39.95
2021-08-27 13:30 | 44435.5625 | 0 | 7.8665 | 39.95
2021-08-27 14:00 | 44435.5833 | 0 | 8.1245 | 39.95
2021-08-27 14:30 | 44435.6042 | 0 | 8.7285 | 39.95
2021-08-27 15:00 | 44435.625 | 0 | 9.1447 | 39.95
2021-08-27 15:30 | 44435.6458 | 0 | 9.9543 | 39.95
2021-08-27 16:00 | 44435.6667 | 0 | 10.7256 | 39.95
2021-08-27 16:30 | 44435.6875 | 0 | 11.567 | 39.95
2021-08-27 17:00 | 44435.7083 | 0 | 12.1606 | 39.95
2021-08-27 17:30 | 44435.7292 | 0 | 12.8182 | 39.95
2021-08-27 18:00 | 44435.75 | 0 | 13.3491 | 39.95
2021-08-27 18:30 | 44435.7708 | 0 | 13.5288 | 39.95
2021-08-27 19:00 | 44435.7917 | 0 | 13.2768 | 39.95
2021-08-27 19:30 | 44435.8125 | 0 | 13.1431 | 39.95
2021-08-27 20:00 | 44435.8333 | 0 | 12.991 | 39.95
2021-08-27 20:30 | 44435.8542 | 0 | 12.461 | 39.95
2021-08-27 21:00 | 44435.875 | 0 | 12.0178 | 39.95
2021-08-27 21:30 | 44435.8958 | 0 | 11.6027 | 39.95
2021-08-27 22:00 | 44435.9167 | 0 | 11.081 | 39.95
2021-08-27 22:30 | 44435.9375 | 0 | 10.3931 | 39.95
2021-08-27 23:00 | 44435.9583 | 0 | 9.8432 | 39.95
2021-08-27 23:30 | 44435.9792 | 0 | 9.2525 | 39.95
2021-08-28 | 44436 | 0 | 8.7199 | 39.95
2021-08-28 00:30 | 44436.0208 | 0 | 8.2545 | 39.95
2021-08-28 01:00 | 44436.0417 | 0 | 8.0402 | 39.95
2021-08-28 01:30 | 44436.0625 | 0 | 7.8037 | 39.95
2021-08-28 02:00 | 44436.0833 | 0 | 7.6587 | 39.95
2021-08-28 02:30 | 44436.1042 | 0 | 7.5402 | 39.95
2021-08-28 03:00 | 44436.125 | 0 | 7.6489 | 39.95
2021-08-28 03:30 | 44436.1458 | 0 | 7.6583 | 39.95
2021-08-28 04:00 | 44436.1667 | 0 | 7.6863 | 39.95
2021-08-28 04:30 | 44436.1875 | 0 | 7.8168 | 39.95
2021-08-28 05:00 | 44436.2083 | 0 | 8.3019 | 39.95
2021-08-28 05:30 | 44436.2292 | 0 | 8.6455 | 39.95
2021-08-28 06:00 | 44436.25 | 0 | 9.2413 | 39.95
2021-08-28 06:30 | 44436.2708 | 0 | 9.6505 | 39.95
2021-08-28 07:00 | 44436.2917 | 0 | 9.838 | 39.95
2021-08-28 07:30 | 44436.3125 | 0 | 9.5161 | 39.95
2021-08-28 08:00 | 44436.3333 | 0 | 9.051 | 39.95
2021-08-28 08:30 | 44436.3542 | 0 | 8.4341 | 39.95
2021-08-28 09:00 | 44436.375 | 0 | 7.7247 | 39.95
2021-08-28 09:30 | 44436.3958 | 0 | 7.3428 | 39.95
2021-08-28 10:00 | 44436.4167 | 0 | 6.5954 | 39.95
2021-08-28 10:30 | 44436.4375 | 0 | 6.1315 | 39.95
2021-08-28 11:00 | 44436.4583 | 0 | 5.7352 | 39.95
2021-08-28 11:30 | 44436.4792 | 0 | 5.3915 | 39.95
2021-08-28 12:00 | 44436.5 | 0 | 5.4067 | 39.95
2021-08-28 12:30 | 44436.5208 | 0 | 5.3743 | 39.95
2021-08-28 13:00 | 44436.5417 | 0 | 5.5383 | 39.95
2021-08-28 13:30 | 44436.5625 | 0 | 5.7021 | 39.95
2021-08-28 14:00 | 44436.5833 | 0 | 6.1518 | 39.95
2021-08-28 14:30 | 44436.6042 | 0 | 6.7279 | 39.95
2021-08-28 15:00 | 44436.625 | 0 | 7.3661 | 39.95
2021-08-28 15:30 | 44436.6458 | 0 | 8.1082 | 39.95
2021-08-28 16:00 | 44436.6667 | 0 | 8.7726 | 39.95
2021-08-28 16:30 | 44436.6875 | 0 | 9.6858 | 39.95
2021-08-28 17:00 | 44436.7083 | 0 | 10.4674 | 39.95
2021-08-28 17:30 | 44436.7292 | 0 | 11.0221 | 39.95
2021-08-28 18:00 | 44436.75 | 0 | 11.5412 | 39.95
2021-08-28 18:30 | 44436.7708 | 0 | 11.6166 | 39.95
2021-08-28 19:00 | 44436.7917 | 0 | 11.3828 | 39.95
2021-08-28 19:30 | 44436.8125 | 0 | 11.1229 | 39.95
2021-08-28 20:00 | 44436.8333 | 0 | 11.0559 | 39.95
2021-08-28 20:30 | 44436.8542 | 0 | 10.4748 | 39.95
2021-08-28 21:00 | 44436.875 | 0 | 10.1442 | 39.95
2021-08-28 21:30 | 44436.8958 | 0 | 9.9604 | 39.95
2021-08-28 22:00 | 44436.9167 | 0 | 9.547 | 39.95
2021-08-28 22:30 | 44436.9375 | 0 | 8.9691 | 39.95
2021-08-28 23:00 | 44436.9583 | 0 | 8.6417 | 39.95
2021-08-28 23:30 | 44436.9792 | 0 | 8.1296 | 39.95
2021-08-29 | 44437 | 0 | 7.7166 | 39.95
2021-08-29 00:30 | 44437.0208 | 0 | 7.4318 | 39.95
2021-08-29 01:00 | 44437.0417 | 0 | 7.2414 | 39.95
2021-08-29 01:30 | 44437.0625 | 0 | 7.078 | 39.95
2021-08-29 02:00 | 44437.0833 | 0 | 7.046 | 39.95
2021-08-29 02:30 | 44437.1042 | 0 | 6.8871 | 39.95
2021-08-29 03:00 | 44437.125 | 0 | 6.9622 | 39.95
2021-08-29 03:30 | 44437.1458 | 0 | 6.9457 | 39.95
2021-08-29 04:00 | 44437.1667 | 0 | 6.8712 | 39.95
2021-08-29 04:30 | 44437.1875 | 0 | 6.932 | 39.95
2021-08-29 05:00 | 44437.2083 | 0 | 7.0457 | 39.95
2021-08-29 05:30 | 44437.2292 | 0 | 7.2506 | 39.95
2021-08-29 06:00 | 44437.25 | 0 | 7.5213 | 39.95
2021-08-29 06:30 | 44437.2708 | 0 | 7.8162 | 39.95
2021-08-29 07:00 | 44437.2917 | 0 | 7.9808 | 39.95
2021-08-29 07:30 | 44437.3125 | 0 | 7.5445 | 39.95
2021-08-29 08:00 | 44437.3333 | 0 | 8.52 | 39.95
2021-08-29 08:30 | 44437.3542 | 0 | 9.3814 | 39.95
2021-08-29 09:00 | 44437.375 | 0 | 9.0693 | 39.95
2021-08-29 09:30 | 44437.3958 | 0 | 8.1036 | 39.95
2021-08-29 10:00 | 44437.4167 | 0 | 7.4059 | 39.95
2021-08-29 10:30 | 44437.4375 | 0 | 6.2175 | 39.95
2021-08-29 11:00 | 44437.4583 | 0 | 5.6913 | 39.95
2021-08-29 11:30 | 44437.4792 | 0 | 5.1252 | 39.95
2021-08-29 12:00 | 44437.5 | 0 | 5.0755 | 39.95
2021-08-29 12:30 | 44437.5208 | 0 | 5.2478 | 39.95
2021-08-29 13:00 | 44437.5417 | 0 | 4.9732 | 39.95
2021-08-29 13:30 | 44437.5625 | 0 | 5.8182 | 39.95
2021-08-29 14:00 | 44437.5833 | 0 | 5.8143 | 39.95
2021-08-29 14:30 | 44437.6042 | 0 | 6.4031 | 39.95
2021-08-29 15:00 | 44437.625 | 0 | 7.1094 | 39.95
2021-08-29 15:30 | 44437.6458 | 0 | 7.9828 | 39.95
2021-08-29 16:00 | 44437.6667 | 0 | 8.7502 | 39.95
2021-08-29 16:30 | 44437.6875 | 0 | 9.7626 | 39.95
2021-08-29 17:00 | 44437.7083 | 0 | 10.4865 | 39.95
2021-08-29 17:30 | 44437.7292 | 0 | 11.1458 | 39.95
2021-08-29 18:00 | 44437.75 | 0 | 11.8991 | 39.95
2021-08-29 18:30 | 44437.7708 | 0 | 11.9589 | 39.95
2021-08-29 19:00 | 44437.7917 | 0 | 11.5168 | 39.95
2021-08-29 19:30 | 44437.8125 | 0 | 11.3212 | 39.95
2021-08-29 20:00 | 44437.8333 | 0 | 10.9944 | 39.95
2021-08-29 20:30 | 44437.8542 | 0 | 10.5909 | 39.95
2021-08-29 21:00 | 44437.875 | 0 | 10.0618 | 39.95
2021-08-29 21:30 | 44437.8958 | 0 | 9.7463 | 39.95
2021-08-29 22:00 | 44437.9167 | 0 | 9.2567 | 39.95
2021-08-29 22:30 | 44437.9375 | 0 | 8.5882 | 39.95
2021-08-29 23:00 | 44437.9583 | 0 | 8.1013 | 39.95
2021-08-29 23:30 | 44437.9792 | 0 | 7.7836 | 39.95
2021-08-30 | 44438 | 0 | 7.3789 | 39.95
2021-08-30 00:30 | 44438.0208 | 0 | 7.1893 | 39.95
2021-08-30 01:00 | 44438.0417 | 0 | 7.0557 | 39.95
2021-08-30 01:30 | 44438.0625 | 0 | 6.9213 | 39.95
2021-08-30 02:00 | 44438.0833 | 0 | 6.9712 | 39.95
2021-08-30 02:30 | 44438.1042 | 0 | 6.9849 | 39.95
2021-08-30 03:00 | 44438.125 | 0 | 6.9453 | 39.95
2021-08-30 03:30 | 44438.1458 | 0 | 7.2068 | 39.95
2021-08-30 04:00 | 44438.1667 | 0 | 7.5981 | 39.95
2021-08-30 04:30 | 44438.1875 | 0 | 8.0421 | 39.95
2021-08-30 05:00 | 44438.2083 | 0 | 8.5962 | 39.95
2021-08-30 05:30 | 44438.2292 | 0 | 9.3667 | 39.95
2021-08-30 06:00 | 44438.25 | 0 | 10.3839 | 39.95
2021-08-30 06:30 | 44438.2708 | 0 | 11.2495 | 39.95
2021-08-30 07:00 | 44438.2917 | 0 | 11.4703 | 39.95
2021-08-30 07:30 | 44438.3125 | 0 | 11.0268 | 39.95
2021-08-30 08:00 | 44438.3333 | 0 | 9.1032 | 39.95
2021-08-30 08:30 | 44438.3542 | 0 | 9.9201 | 39.95
2021-08-30 09:00 | 44438.375 | 0 | 9.8009 | 39.95
2021-08-30 09:30 | 44438.3958 | 0 | 9.3775 | 39.95
2021-08-30 10:00 | 44438.4167 | 0 | 8.1617 | 39.95
2021-08-30 10:30 | 44438.4375 | 0 | 7.889 | 39.95
2021-08-30 11:00 | 44438.4583 | 0 | 7.7756 | 39.95
2021-08-30 11:30 | 44438.4792 | 0 | 7.6209 | 39.95
2021-08-30 12:00 | 44438.5 | 0 | 7.7631 | 39.95
2021-08-30 12:30 | 44438.5208 | 0 | 7.7058 | 39.95
2021-08-30 13:00 | 44438.5417 | 0 | 7.9764 | 39.95
2021-08-30 13:30 | 44438.5625 | 0 | 8.3055 | 39.95
2021-08-30 14:00 | 44438.5833 | 0 | 8.7087 | 39.95
2021-08-30 14:30 | 44438.6042 | 0 | 9.0842 | 39.95
2021-08-30 15:00 | 44438.625 | 0 | 9.7579 | 39.95
2021-08-30 15:30 | 44438.6458 | 0 | 10.8767 | 39.95
2021-08-30 16:00 | 44438.6667 | 0 | 11.3293 | 39.95
2021-08-30 16:30 | 44438.6875 | 0 | 11.8333 | 39.95
2021-08-30 17:00 | 44438.7083 | 0 | 12.2025 | 39.95
2021-08-30 17:30 | 44438.7292 | 0 | 13.3362 | 39.95
2021-08-30 18:00 | 44438.75 | 0 | 13.6392 | 39.95
2021-08-30 18:30 | 44438.7708 | 0 | 14.0292 | 39.95
2021-08-30 19:00 | 44438.7917 | 0 | 13.6593 | 39.95
2021-08-30 19:30 | 44438.8125 | 0 | 13.3219 | 39.95
2021-08-30 20:00 | 44438.8333 | 0 | 12.8856 | 39.95
2021-08-30 20:30 | 44438.8542 | 0 | 12.3924 | 39.95
2021-08-30 21:00 | 44438.875 | 0 | 11.6938 | 39.95
2021-08-30 21:30 | 44438.8958 | 0 | 11.3804 | 39.95
2021-08-30 22:00 | 44438.9167 | 0 | 10.8176 | 39.95
2021-08-30 22:30 | 44438.9375 | 0 | 9.9153 | 39.95
2021-08-30 23:00 | 44438.9583 | 0 | 9.3134 | 39.95
2021-08-30 23:30 | 44438.9792 | 0 | 8.8447 | 39.95
2021-08-31 | 44439 | 0 | 8.2898 | 39.95
2021-08-31 00:30 | 44439.0208 | 0 | 7.9464 | 39.95
2021-08-31 01:00 | 44439.0417 | 0 | 7.6939 | 39.95
2021-08-31 01:30 | 44439.0625 | 0 | 7.5953 | 39.95
2021-08-31 02:00 | 44439.0833 | 0 | 7.5094 | 39.95
2021-08-31 02:30 | 44439.1042 | 0 | 7.4738 | 39.95
2021-08-31 03:00 | 44439.125 | 0 | 7.474 | 39.95
2021-08-31 03:30 | 44439.1458 | 0 | 7.6337 | 39.95
2021-08-31 04:00 | 44439.1667 | 0 | 7.812 | 39.95
2021-08-31 04:30 | 44439.1875 | 0 | 8.295 | 39.95
2021-08-31 05:00 | 44439.2083 | 0 | 8.8682 | 39.95
2021-08-31 05:30 | 44439.2292 | 0 | 9.5249 | 39.95
2021-08-31 06:00 | 44439.25 | 0 | 10.619 | 39.95
2021-08-31 06:30 | 44439.2708 | 0 | 11.4915 | 39.95
2021-08-31 07:00 | 44439.2917 | 0 | 12.2155 | 39.95
2021-08-31 07:30 | 44439.3125 | 0 | 11.3877 | 39.95
2021-08-31 08:00 | 44439.3333 | 0 | 11.72 | 39.95
2021-08-31 08:30 | 44439.3542 | 0 | 11.5693 | 39.95
2021-08-31 09:00 | 44439.375 | 0 | 11.8645 | 39.95
2021-08-31 09:30 | 44439.3958 | 0 | 10.602 | 39.95
2021-08-31 10:00 | 44439.4167 | 0 | 11.1339 | 39.95
2021-08-31 10:30 | 44439.4375 | 0 | 11.3929 | 39.95
2021-08-31 11:00 | 44439.4583 | 0 | 10.7928 | 39.95
2021-08-31 11:30 | 44439.4792 | 0 | 10.2324 | 39.95
2021-08-31 12:00 | 44439.5 | 0 | 9.2894 | 39.95
2021-08-31 12:30 | 44439.5208 | 0 | 8.1646 | 39.95
2021-08-31 13:00 | 44439.5417 | 0 | 8.2866 | 39.95
2021-08-31 13:30 | 44439.5625 | 0 | 8.8158 | 39.95
2021-08-31 14:00 | 44439.5833 | 0 | 9.5001 | 39.95
2021-08-31 14:30 | 44439.6042 | 0 | 9.9711 | 39.95
2021-08-31 15:00 | 44439.625 | 0 | 10.3996 | 39.95
2021-08-31 15:30 | 44439.6458 | 0 | 11.0152 | 39.95
2021-08-31 16:00 | 44439.6667 | 0 | 11.8427 | 39.95
2021-08-31 16:30 | 44439.6875 | 0 | 12.7135 | 39.95
2021-08-31 17:00 | 44439.7083 | 0 | 13.1368 | 39.95
2021-08-31 17:30 | 44439.7292 | 0 | 13.8383 | 39.95
2021-08-31 18:00 | 44439.75 | 0 | 14.0082 | 39.95
2021-08-31 18:30 | 44439.7708 | 0 | 14.3271 | 39.95
2021-08-31 19:00 | 44439.7917 | 0 | 13.7855 | 39.95
2021-08-31 19:30 | 44439.8125 | 0 | 13.5191 | 39.95
2021-08-31 20:00 | 44439.8333 | 0 | 13.273 | 39.95
2021-08-31 20:30 | 44439.8542 | 0 | 12.7595 | 39.95
2021-08-31 21:00 | 44439.875 | 0 | 12.1315 | 39.95
2021-08-31 21:30 | 44439.8958 | 0 | 11.6995 | 39.95
2021-08-31 22:00 | 44439.9167 | 0 | 11.2145 | 39.95
2021-08-31 22:30 | 44439.9375 | 0 | 10.4776 | 39.95
2021-08-31 23:00 | 44439.9583 | 0 | 9.6599 | 39.95
2021-08-31 23:30 | 44439.9792 | 0 | 9.0519 | 39.95
2021-09-01 | 44440 | 0 | 8.4957 | 39.95
2021-09-01 00:30 | 44440.0208 | 0 | 8.2112 | 39.95
2021-09-01 01:00 | 44440.0417 | 0 | 8.0645 | 39.95
2021-09-01 01:30 | 44440.0625 | 0 | 7.9206 | 39.95
2021-09-01 02:00 | 44440.0833 | 0 | 7.8784 | 39.95
2021-09-01 02:30 | 44440.1042 | 0 | 7.7174 | 39.95
2021-09-01 03:00 | 44440.125 | 0 | 7.7451 | 39.95
2021-09-01 03:30 | 44440.1458 | 0 | 7.909 | 39.95
2021-09-01 04:00 | 44440.1667 | 0 | 8.1846 | 39.95
2021-09-01 04:30 | 44440.1875 | 0 | 8.6268 | 39.95
2021-09-01 05:00 | 44440.2083 | 0 | 9.3423 | 39.95
2021-09-01 05:30 | 44440.2292 | 0 | 9.8065 | 39.95
2021-09-01 06:00 | 44440.25 | 0 | 10.7962 | 39.95
2021-09-01 06:30 | 44440.2708 | 0 | 11.7194 | 39.95
2021-09-01 07:00 | 44440.2917 | 0 | 12.3252 | 39.95
2021-09-01 07:30 | 44440.3125 | 0 | 12.5652 | 39.95
2021-09-01 08:00 | 44440.3333 | 0 | 12.4568 | 39.95
2021-09-01 08:30 | 44440.3542 | 0 | 10.8591 | 39.95
2021-09-01 09:00 | 44440.375 | 0 | 9.6189 | 39.95
2021-09-01 09:30 | 44440.3958 | 0 | 9.2556 | 39.95
2021-09-01 10:00 | 44440.4167 | 0 | 9.0604 | 39.95
2021-09-01 10:30 | 44440.4375 | 0 | 9.1261 | 39.95
2021-09-01 11:00 | 44440.4583 | 0 | 9.0268 | 39.95
2021-09-01 11:30 | 44440.4792 | 0 | 9.1413 | 39.95
2021-09-01 12:00 | 44440.5 | 0 | 9.1417 | 39.95
2021-09-01 12:30 | 44440.5208 | 0 | 9.1785 | 39.95
2021-09-01 13:00 | 44440.5417 | 0 | 9.2885 | 39.95
2021-09-01 13:30 | 44440.5625 | 0 | 9.6338 | 39.95
2021-09-01 14:00 | 44440.5833 | 0 | 10.2194 | 39.95
2021-09-01 14:30 | 44440.6042 | 0 | 10.6599 | 39.95
2021-09-01 15:00 | 44440.625 | 0 | 11.1058 | 39.95
2021-09-01 15:30 | 44440.6458 | 0 | 11.7176 | 39.95
2021-09-01 16:00 | 44440.6667 | 0 | 12.3476 | 39.95
2021-09-01 16:30 | 44440.6875 | 0 | 12.8679 | 39.95
2021-09-01 17:00 | 44440.7083 | 0 | 13.203 | 39.95
2021-09-01 17:30 | 44440.7292 | 0 | 13.925 | 39.95
2021-09-01 18:00 | 44440.75 | 0 | 14.3548 | 39.95
2021-09-01 18:30 | 44440.7708 | 0 | 14.442 | 39.95
2021-09-01 19:00 | 44440.7917 | 0 | 14.1446 | 39.95
2021-09-01 19:30 | 44440.8125 | 0 | 13.9766 | 39.95
2021-09-01 20:00 | 44440.8333 | 0 | 13.4605 | 39.95
2021-09-01 20:30 | 44440.8542 | 0 | 12.9183 | 39.95
2021-09-01 21:00 | 44440.875 | 0 | 12.5362 | 39.95
2021-09-01 21:30 | 44440.8958 | 0 | 12.1701 | 39.95
2021-09-01 22:00 | 44440.9167 | 0 | 11.4156 | 39.95
2021-09-01 22:30 | 44440.9375 | 0 | 10.6139 | 39.95
2021-09-01 23:00 | 44440.9583 | 0 | 9.9063 | 39.95
2021-09-01 23:30 | 44440.9792 | 0 | 9.4963 | 39.95
2021-09-02 | 44441 | 0 | 8.8466 | 39.95
2021-09-02 00:30 | 44441.0208 | 0 | 8.4463 | 39.95
2021-09-02 01:00 | 44441.0417 | 0 | 8.1733 | 39.95
2021-09-02 01:30 | 44441.0625 | 0 | 8.0508 | 39.95
2021-09-02 02:00 | 44441.0833 | 0 | 8.0027 | 39.95
2021-09-02 02:30 | 44441.1042 | 0 | 7.9078 | 39.95
2021-09-02 03:00 | 44441.125 | 0 | 7.9669 | 39.95
2021-09-02 03:30 | 44441.1458 | 0 | 8.0563 | 39.95
2021-09-02 04:00 | 44441.1667 | 0 | 8.2138 | 39.95
2021-09-02 04:30 | 44441.1875 | 0 | 8.7539 | 39.95
2021-09-02 05:00 | 44441.2083 | 0 | 9.3388 | 39.95
2021-09-02 05:30 | 44441.2292 | 0 | 10.0723 | 39.95
2021-09-02 06:00 | 44441.25 | 0 | 10.6607 | 39.95
2021-09-02 06:30 | 44441.2708 | 0 | 11.5363 | 39.95
2021-09-02 07:00 | 44441.2917 | 0 | 11.7053 | 39.95
2021-09-02 07:30 | 44441.3125 | 0 | 11.4645 | 39.95
2021-09-02 08:00 | 44441.3333 | 0 | 11.5179 | 39.95
2021-09-02 08:30 | 44441.3542 | 0 | 10.8596 | 39.95
2021-09-02 09:00 | 44441.375 | 0 | 10.9515 | 39.95
2021-09-02 09:30 | 44441.3958 | 0 | 10.0902 | 39.95
2021-09-02 10:00 | 44441.4167 | 0 | 10.0335 | 39.95
2021-09-02 10:30 | 44441.4375 | 0 | 10.3691 | 39.95
2021-09-02 11:00 | 44441.4583 | 0 | 10.0831 | 39.95
2021-09-02 11:30 | 44441.4792 | 0 | 10.602 | 39.95
2021-09-02 12:00 | 44441.5 | 0 | 10.0761 | 39.95
2021-09-02 12:30 | 44441.5208 | 0 | 9.97 | 39.95
2021-09-02 13:00 | 44441.5417 | 0 | 9.4899 | 39.95
2021-09-02 13:30 | 44441.5625 | 0 | 9.7258 | 39.95
2021-09-02 14:00 | 44441.5833 | 0 | 9.672 | 39.95
2021-09-02 14:30 | 44441.6042 | 0 | 10.556 | 39.95
2021-09-02 15:00 | 44441.625 | 0 | 10.5536 | 39.95
2021-09-02 15:30 | 44441.6458 | 0 | 11.2314 | 39.95
2021-09-02 16:00 | 44441.6667 | 0 | 12.0489 | 39.95
2021-09-02 16:30 | 44441.6875 | 0 | 12.2802 | 39.95
2021-09-02 17:00 | 44441.7083 | 0 | 12.5671 | 39.95
2021-09-02 17:30 | 44441.7292 | 0 | 13.1427 | 39.95
2021-09-02 18:00 | 44441.75 | 0 | 13.5992 | 39.95
2021-09-02 18:30 | 44441.7708 | 0 | 13.7271 | 39.95
2021-09-02 19:00 | 44441.7917 | 0 | 13.5002 | 39.95
2021-09-02 19:30 | 44441.8125 | 0 | 13.2992 | 39.95
2021-09-02 20:00 | 44441.8333 | 0 | 12.9906 | 39.95
2021-09-02 20:30 | 44441.8542 | 0 | 12.5431 | 39.95
2021-09-02 21:00 | 44441.875 | 0 | 12.0679 | 39.95
2021-09-02 21:30 | 44441.8958 | 0 | 11.5053 | 39.95
2021-09-02 22:00 | 44441.9167 | 0 | 10.9598 | 39.95
2021-09-02 22:30 | 44441.9375 | 0 | 9.9671 | 39.95
2021-09-02 23:00 | 44441.9583 | 0 | 9.4586 | 39.95
2021-09-02 23:30 | 44441.9792 | 0 | 9.0024 | 39.95
2021-09-03 | 44442 | 0 | 8.4356 | 39.95
2021-09-03 00:30 | 44442.0208 | 0 | 7.9772 | 39.95
2021-09-03 01:00 | 44442.0417 | 0 | 7.8255 | 39.95
2021-09-03 01:30 | 44442.0625 | 0 | 7.5947 | 39.95
2021-09-03 02:00 | 44442.0833 | 0 | 7.6637 | 39.95
2021-09-03 02:30 | 44442.1042 | 0 | 7.7029 | 39.95
2021-09-03 03:00 | 44442.125 | 0 | 7.7122 | 39.95
2021-09-03 03:30 | 44442.1458 | 0 | 7.8176 | 39.95
2021-09-03 04:00 | 44442.1667 | 0 | 8.0112 | 39.95
2021-09-03 04:30 | 44442.1875 | 0 | 8.4738 | 39.95
2021-09-03 05:00 | 44442.2083 | 0 | 9.2776 | 39.95
2021-09-03 05:30 | 44442.2292 | 0 | 9.8016 | 39.95
2021-09-03 06:00 | 44442.25 | 0 | 10.4556 | 39.95
2021-09-03 06:30 | 44442.2708 | 0 | 11.2682 | 39.95
2021-09-03 07:00 | 44442.2917 | 0 | 12.3116 | 39.95
2021-09-03 07:30 | 44442.3125 | 0 | 11.6916 | 39.95
2021-09-03 08:00 | 44442.3333 | 0 | 11.3392 | 39.95
2021-09-03 08:30 | 44442.3542 | 0 | 12.5507 | 39.95
2021-09-03 09:00 | 44442.375 | 0 | 10.8592 | 39.95
2021-09-03 09:30 | 44442.3958 | 0 | 9.7483 | 39.95
2021-09-03 10:00 | 44442.4167 | 0 | 9.2639 | 39.95
2021-09-03 10:30 | 44442.4375 | 0 | 8.7077 | 39.95
2021-09-03 11:00 | 44442.4583 | 0 | 8.2717 | 39.95
2021-09-03 11:30 | 44442.4792 | 0 | 8.1772 | 39.95
2021-09-03 12:00 | 44442.5 | 0 | 7.8348 | 39.95
2021-09-03 12:30 | 44442.5208 | 0 | 7.9323 | 39.95
2021-09-03 13:00 | 44442.5417 | 0 | 7.8589 | 39.95
2021-09-03 13:30 | 44442.5625 | 0 | 8.4316 | 39.95
2021-09-03 14:00 | 44442.5833 | 0 | 9.4225 | 39.95
2021-09-03 14:30 | 44442.6042 | 0 | 9.6739 | 39.95
2021-09-03 15:00 | 44442.625 | 0 | 10.2445 | 39.95
2021-09-03 15:30 | 44442.6458 | 0 | 11.2869 | 39.95
2021-09-03 16:00 | 44442.6667 | 0 | 11.744 | 39.95
2021-09-03 16:30 | 44442.6875 | 0 | 12.3165 | 39.95
2021-09-03 17:00 | 44442.7083 | 0 | 12.3709 | 39.95
2021-09-03 17:30 | 44442.7292 | 0 | 13.0442 | 39.95
2021-09-03 18:00 | 44442.75 | 0 | 13.1612 | 39.95
2021-09-03 18:30 | 44442.7708 | 0 | 13.069 | 39.95
2021-09-03 19:00 | 44442.7917 | 0 | 12.7404 | 39.95
2021-09-03 19:30 | 44442.8125 | 0 | 12.7179 | 39.95
2021-09-03 20:00 | 44442.8333 | 0 | 12.5059 | 39.95
2021-09-03 20:30 | 44442.8542 | 0 | 11.8835 | 39.95
2021-09-03 21:00 | 44442.875 | 0 | 11.4692 | 39.95
2021-09-03 21:30 | 44442.8958 | 0 | 11.0806 | 39.95
2021-09-03 22:00 | 44442.9167 | 0 | 10.6542 | 39.95
2021-09-03 22:30 | 44442.9375 | 0 | 10.0638 | 39.95
2021-09-03 23:00 | 44442.9583 | 0 | 9.5318 | 39.95
2021-09-03 23:30 | 44442.9792 | 0 | 9.0631 | 39.95
2021-09-04 | 44443 | 0 | 8.6425 | 39.95
2021-09-04 00:30 | 44443.0208 | 0 | 8.1319 | 39.95
2021-09-04 01:00 | 44443.0417 | 0 | 7.772 | 39.95
2021-09-04 01:30 | 44443.0625 | 0 | 7.6506 | 39.95
2021-09-04 02:00 | 44443.0833 | 0 | 7.6601 | 39.95
2021-09-04 02:30 | 44443.1042 | 0 | 7.5472 | 39.95
2021-09-04 03:00 | 44443.125 | 0 | 7.4384 | 39.95
2021-09-04 03:30 | 44443.1458 | 0 | 7.513 | 39.95
2021-09-04 04:00 | 44443.1667 | 0 | 7.4833 | 39.95
2021-09-04 04:30 | 44443.1875 | 0 | 7.6148 | 39.95
2021-09-04 05:00 | 44443.2083 | 0 | 7.9199 | 39.95
2021-09-04 05:30 | 44443.2292 | 0 | 8.1636 | 39.95
2021-09-04 06:00 | 44443.25 | 0 | 8.4331 | 39.95
2021-09-04 06:30 | 44443.2708 | 0 | 8.8802 | 39.95
2021-09-04 07:00 | 44443.2917 | 0 | 8.5954 | 39.95
2021-09-04 07:30 | 44443.3125 | 0 | 8.0116 | 39.95
2021-09-04 08:00 | 44443.3333 | 0 | 7.9737 | 39.95
2021-09-04 08:30 | 44443.3542 | 0 | 7.5829 | 39.95
2021-09-04 09:00 | 44443.375 | 0 | 7.9158 | 39.95
2021-09-04 09:30 | 44443.3958 | 0 | 6.9147 | 39.95
2021-09-04 10:00 | 44443.4167 | 0 | 6.8867 | 39.95
2021-09-04 10:30 | 44443.4375 | 0 | 7.4509 | 39.95
2021-09-04 11:00 | 44443.4583 | 0 | 6.8706 | 39.95
2021-09-04 11:30 | 44443.4792 | 0 | 7.3947 | 39.95
2021-09-04 12:00 | 44443.5 | 0 | 7.5401 | 39.95
2021-09-04 12:30 | 44443.5208 | 0 | 7.2483 | 39.95
2021-09-04 13:00 | 44443.5417 | 0 | 6.7988 | 39.95
2021-09-04 13:30 | 44443.5625 | 0 | 6.4955 | 39.95
2021-09-04 14:00 | 44443.5833 | 0 | 6.7881 | 39.95
2021-09-04 14:30 | 44443.6042 | 0 | 7.2519 | 39.95
2021-09-04 15:00 | 44443.625 | 0 | 7.716 | 39.95
2021-09-04 15:30 | 44443.6458 | 0 | 8.4327 | 39.95
2021-09-04 16:00 | 44443.6667 | 0 | 9.156 | 39.95
2021-09-04 16:30 | 44443.6875 | 0 | 9.9134 | 39.95
2021-09-04 17:00 | 44443.7083 | 0 | 10.375 | 39.95
2021-09-04 17:30 | 44443.7292 | 0 | 10.8076 | 39.95
2021-09-04 18:00 | 44443.75 | 0 | 11.0769 | 39.95
2021-09-04 18:30 | 44443.7708 | 0 | 11.2728 | 39.95
2021-09-04 19:00 | 44443.7917 | 0 | 11.0235 | 39.95
2021-09-04 19:30 | 44443.8125 | 0 | 10.9001 | 39.95
2021-09-04 20:00 | 44443.8333 | 0 | 10.5706 | 39.95
2021-09-04 20:30 | 44443.8542 | 0 | 10.2642 | 39.95
2021-09-04 21:00 | 44443.875 | 0 | 9.8939 | 39.95
2021-09-04 21:30 | 44443.8958 | 0 | 9.6437 | 39.95
2021-09-04 22:00 | 44443.9167 | 0 | 9.2627 | 39.95
2021-09-04 22:30 | 44443.9375 | 0 | 8.8764 | 39.95
2021-09-04 23:00 | 44443.9583 | 0 | 8.4424 | 39.95
2021-09-04 23:30 | 44443.9792 | 0 | 7.8817 | 39.95
2021-09-05 | 44444 | 0 | 7.5565 | 39.95
2021-09-05 00:30 | 44444.0208 | 0 | 7.3424 | 39.95
2021-09-05 01:00 | 44444.0417 | 0 | 7.1992 | 39.95
2021-09-05 01:30 | 44444.0625 | 0 | 7.0147 | 39.95
2021-09-05 02:00 | 44444.0833 | 0 | 6.9736 | 39.95
2021-09-05 02:30 | 44444.1042 | 0 | 6.8694 | 39.95
2021-09-05 03:00 | 44444.125 | 0 | 6.8432 | 39.95
2021-09-05 03:30 | 44444.1458 | 0 | 6.8133 | 39.95
2021-09-05 04:00 | 44444.1667 | 0 | 6.7724 | 39.95
2021-09-05 04:30 | 44444.1875 | 0 | 6.8314 | 39.95
2021-09-05 05:00 | 44444.2083 | 0 | 6.6165 | 39.95
2021-09-05 05:30 | 44444.2292 | 0 | 6.6771 | 39.95
2021-09-05 06:00 | 44444.25 | 0 | 6.8298 | 39.95
2021-09-05 06:30 | 44444.2708 | 0 | 6.9753 | 39.95
2021-09-05 07:00 | 44444.2917 | 0 | 6.8344 | 39.95
2021-09-05 07:30 | 44444.3125 | 0 | 7.4286 | 39.95
2021-09-05 08:00 | 44444.3333 | 0 | 8.0931 | 39.95
2021-09-05 08:30 | 44444.3542 | 0 | 7.8915 | 39.95
2021-09-05 09:00 | 44444.375 | 0 | 7.9723 | 39.95
2021-09-05 09:30 | 44444.3958 | 0 | 7.6013 | 39.95
2021-09-05 10:00 | 44444.4167 | 0 | 6.4332 | 39.95
2021-09-05 10:30 | 44444.4375 | 0 | 5.3178 | 39.95
2021-09-05 11:00 | 44444.4583 | 0 | 6.2452 | 39.95
2021-09-05 11:30 | 44444.4792 | 0 | 7.0207 | 39.95
2021-09-05 12:00 | 44444.5 | 0 | 8.8583 | 39.95
2021-09-05 12:30 | 44444.5208 | 0 | 9.6688 | 39.95
2021-09-05 13:00 | 44444.5417 | 0 | 8.9509 | 39.95
2021-09-05 13:30 | 44444.5625 | 0 | 9.709 | 39.95
2021-09-05 14:00 | 44444.5833 | 0 | 9.7761 | 39.95
2021-09-05 14:30 | 44444.6042 | 0 | 9.9018 | 39.95
2021-09-05 15:00 | 44444.625 | 0 | 10.1348 | 39.95
2021-09-05 15:30 | 44444.6458 | 0 | 10.537 | 39.95
2021-09-05 16:00 | 44444.6667 | 0 | 10.5706 | 39.95
2021-09-05 16:30 | 44444.6875 | 0 | 10.9382 | 39.95
2021-09-05 17:00 | 44444.7083 | 0 | 11.2099 | 39.95
2021-09-05 17:30 | 44444.7292 | 0 | 11.4257 | 39.95
2021-09-05 18:00 | 44444.75 | 0 | 11.3904 | 39.95
2021-09-05 18:30 | 44444.7708 | 0 | 11.3283 | 39.95
2021-09-05 19:00 | 44444.7917 | 0 | 11.219 | 39.95
2021-09-05 19:30 | 44444.8125 | 0 | 11.0857 | 39.95
2021-09-05 20:00 | 44444.8333 | 0 | 11.0446 | 39.95
2021-09-05 20:30 | 44444.8542 | 0 | 10.4586 | 39.95
2021-09-05 21:00 | 44444.875 | 0 | 9.9838 | 39.95
2021-09-05 21:30 | 44444.8958 | 0 | 9.6722 | 39.95
2021-09-05 22:00 | 44444.9167 | 0 | 9.1837 | 39.95
2021-09-05 22:30 | 44444.9375 | 0 | 8.5579 | 39.95
2021-09-05 23:00 | 44444.9583 | 0 | 8.0852 | 39.95
2021-09-05 23:30 | 44444.9792 | 0 | 7.7847 | 39.95
2021-09-06 | 44445 | 0 | 7.4058 | 39.95
2021-09-06 00:30 | 44445.0208 | 0 | 7.1852 | 39.95
2021-09-06 01:00 | 44445.0417 | 0 | 7.005 | 39.95
2021-09-06 01:30 | 44445.0625 | 0 | 6.9155 | 39.95
2021-09-06 02:00 | 44445.0833 | 0 | 6.9776 | 39.95
2021-09-06 02:30 | 44445.1042 | 0 | 6.8076 | 39.95
2021-09-06 03:00 | 44445.125 | 0 | 6.9638 | 39.95
2021-09-06 03:30 | 44445.1458 | 0 | 7.0732 | 39.95
2021-09-06 04:00 | 44445.1667 | 0 | 7.477 | 39.95
2021-09-06 04:30 | 44445.1875 | 0 | 8.0172 | 39.95
2021-09-06 05:00 | 44445.2083 | 0 | 8.5892 | 39.95
2021-09-06 05:30 | 44445.2292 | 0 | 9.417 | 39.95
2021-09-06 06:00 | 44445.25 | 0 | 10.4779 | 39.95
2021-09-06 06:30 | 44445.2708 | 0 | 11.5073 | 39.95
2021-09-06 07:00 | 44445.2917 | 0 | 12.0117 | 39.95
2021-09-06 07:30 | 44445.3125 | 0 | 11.7686 | 39.95
2021-09-06 08:00 | 44445.3333 | 0 | 10.9402 | 39.95
2021-09-06 08:30 | 44445.3542 | 0 | 10.3517 | 39.95
2021-09-06 09:00 | 44445.375 | 0 | 9.4855 | 39.95
2021-09-06 09:30 | 44445.3958 | 0 | 8.5649 | 39.95
2021-09-06 10:00 | 44445.4167 | 0 | 8.2816 | 39.95
2021-09-06 10:30 | 44445.4375 | 0 | 8.1211 | 39.95
2021-09-06 11:00 | 44445.4583 | 0 | 8.5363 | 39.95
2021-09-06 11:30 | 44445.4792 | 0 | 7.7176 | 39.95
2021-09-06 12:00 | 44445.5 | 0 | 7.4994 | 39.95
2021-09-06 12:30 | 44445.5208 | 0 | 7.3046 | 39.95
2021-09-06 13:00 | 44445.5417 | 0 | 7.239 | 39.95
2021-09-06 13:30 | 44445.5625 | 0 | 7.5684 | 39.95
2021-09-06 14:00 | 44445.5833 | 0 | 8.3048 | 39.95
2021-09-06 14:30 | 44445.6042 | 0 | 8.4579 | 39.95
2021-09-06 15:00 | 44445.625 | 0 | 9.2094 | 39.95
2021-09-06 15:30 | 44445.6458 | 0 | 9.8306 | 39.95
2021-09-06 16:00 | 44445.6667 | 0 | 10.603 | 39.95
2021-09-06 16:30 | 44445.6875 | 0 | 11.3819 | 39.95
2021-09-06 17:00 | 44445.7083 | 0 | 12.0355 | 39.95
2021-09-06 17:30 | 44445.7292 | 0 | 12.6708 | 39.95
2021-09-06 18:00 | 44445.75 | 0 | 13.3704 | 39.95
2021-09-06 18:30 | 44445.7708 | 0 | 13.8778 | 39.95
2021-09-06 19:00 | 44445.7917 | 0 | 13.4664 | 39.95
2021-09-06 19:30 | 44445.8125 | 0 | 13.3561 | 39.95
2021-09-06 20:00 | 44445.8333 | 0 | 12.887 | 39.95
2021-09-06 20:30 | 44445.8542 | 0 | 12.422 | 39.95
2021-09-06 21:00 | 44445.875 | 0 | 11.9499 | 39.95
2021-09-06 21:30 | 44445.8958 | 0 | 11.5893 | 39.95
2021-09-06 22:00 | 44445.9167 | 0 | 10.8706 | 39.95
2021-09-06 22:30 | 44445.9375 | 0 | 10.1246 | 39.95
2021-09-06 23:00 | 44445.9583 | 0 | 9.4379 | 39.95
2021-09-06 23:30 | 44445.9792 | 0 | 8.9231 | 39.95
2021-09-07 | 44446 | 0 | 8.3252 | 39.95
2021-09-07 00:30 | 44446.0208 | 0 | 7.9939 | 39.95
2021-09-07 01:00 | 44446.0417 | 0 | 7.7779 | 39.95
2021-09-07 01:30 | 44446.0625 | 0 | 7.6637 | 39.95
2021-09-07 02:00 | 44446.0833 | 0 | 7.6661 | 39.95
2021-09-07 02:30 | 44446.1042 | 0 | 7.5164 | 39.95
2021-09-07 03:00 | 44446.125 | 0 | 7.6211 | 39.95
2021-09-07 03:30 | 44446.1458 | 0 | 7.6818 | 39.95
2021-09-07 04:00 | 44446.1667 | 0 | 7.9872 | 39.95
2021-09-07 04:30 | 44446.1875 | 0 | 8.4112 | 39.95
2021-09-07 05:00 | 44446.2083 | 0 | 9.1268 | 39.95
2021-09-07 05:30 | 44446.2292 | 0 | 9.8757 | 39.95
2021-09-07 06:00 | 44446.25 | 0 | 10.9311 | 39.95
2021-09-07 06:30 | 44446.2708 | 0 | 11.746 | 39.95
2021-09-07 07:00 | 44446.2917 | 0 | 11.891 | 39.95
2021-09-07 07:30 | 44446.3125 | 0 | 11.2861 | 39.95
2021-09-07 08:00 | 44446.3333 | 0 | 10.493 | 39.95
2021-09-07 08:30 | 44446.3542 | 0 | 9.5379 | 39.95
2021-09-07 09:00 | 44446.375 | 0 | 8.9177 | 39.95
2021-09-07 09:30 | 44446.3958 | 0 | 8.2246 | 39.95
2021-09-07 10:00 | 44446.4167 | 0 | 7.8028 | 39.95
2021-09-07 10:30 | 44446.4375 | 0 | 7.5597 | 39.95
2021-09-07 11:00 | 44446.4583 | 0 | 7.3348 | 39.95
2021-09-07 11:30 | 44446.4792 | 0 | 7.2696 | 39.95
2021-09-07 12:00 | 44446.5 | 0 | 7.1204 | 39.95
2021-09-07 12:30 | 44446.5208 | 0 | 7.2221 | 39.95
2021-09-07 13:00 | 44446.5417 | 0 | 7.4714 | 39.95
2021-09-07 13:30 | 44446.5625 | 0 | 7.7633 | 39.95
2021-09-07 14:00 | 44446.5833 | 0 | 8.2777 | 39.95
2021-09-07 14:30 | 44446.6042 | 0 | 8.754 | 39.95
2021-09-07 15:00 | 44446.625 | 0 | 9.402 | 39.95
2021-09-07 15:30 | 44446.6458 | 0 | 10.1342 | 39.95
2021-09-07 16:00 | 44446.6667 | 0 | 10.8396 | 39.95
2021-09-07 16:30 | 44446.6875 | 0 | 11.6674 | 39.95
2021-09-07 17:00 | 44446.7083 | 0 | 12.1794 | 39.95
2021-09-07 17:30 | 44446.7292 | 0 | 12.9942 | 39.95
2021-09-07 18:00 | 44446.75 | 0 | 13.5145 | 39.95
2021-09-07 18:30 | 44446.7708 | 0 | 13.8499 | 39.95
2021-09-07 19:00 | 44446.7917 | 0 | 13.6267 | 39.95
2021-09-07 19:30 | 44446.8125 | 0 | 13.461 | 39.95
2021-09-07 20:00 | 44446.8333 | 0 | 13.2274 | 39.95
2021-09-07 20:30 | 44446.8542 | 0 | 12.802 | 39.95
2021-09-07 21:00 | 44446.875 | 0 | 12.1335 | 39.95
2021-09-07 21:30 | 44446.8958 | 0 | 11.7307 | 39.95
2021-09-07 22:00 | 44446.9167 | 0 | 10.9655 | 39.95
2021-09-07 22:30 | 44446.9375 | 0 | 10.0266 | 39.95
2021-09-07 23:00 | 44446.9583 | 0 | 9.211 | 39.95
2021-09-07 23:30 | 44446.9792 | 0 | 8.7926 | 39.95
2021-09-08 | 44447 | 0 | 8.3175 | 39.95
2021-09-08 00:30 | 44447.0208 | 0 | 8.0194 | 39.95
2021-09-08 01:00 | 44447.0417 | 0 | 7.8941 | 39.95
2021-09-08 01:30 | 44447.0625 | 0 | 7.7516 | 39.95
2021-09-08 02:00 | 44447.0833 | 0 | 7.7088 | 39.95
2021-09-08 02:30 | 44447.1042 | 0 | 7.5408 | 39.95
2021-09-08 03:00 | 44447.125 | 0 | 7.7064 | 39.95
2021-09-08 03:30 | 44447.1458 | 0 | 7.7774 | 39.95
2021-09-08 04:00 | 44447.1667 | 0 | 7.8751 | 39.95
2021-09-08 04:30 | 44447.1875 | 0 | 8.4765 | 39.95
2021-09-08 05:00 | 44447.2083 | 0 | 9.2424 | 39.95
2021-09-08 05:30 | 44447.2292 | 0 | 10.012 | 39.95
2021-09-08 06:00 | 44447.25 | 0 | 11.1566 | 39.95
2021-09-08 06:30 | 44447.2708 | 0 | 11.8113 | 39.95
2021-09-08 07:00 | 44447.2917 | 0 | 11.9148 | 39.95
2021-09-08 07:30 | 44447.3125 | 0 | 11.5116 | 39.95
2021-09-08 08:00 | 44447.3333 | 0 | 10.6664 | 39.95
2021-09-08 08:30 | 44447.3542 | 0 | 9.8363 | 39.95
2021-09-08 09:00 | 44447.375 | 0 | 8.9266 | 39.95
2021-09-08 09:30 | 44447.3958 | 0 | 8.4717 | 39.95
2021-09-08 10:00 | 44447.4167 | 0 | 8.2413 | 39.95
2021-09-08 10:30 | 44447.4375 | 0 | 7.9149 | 39.95
2021-09-08 11:00 | 44447.4583 | 0 | 8.9141 | 39.95
2021-09-08 11:30 | 44447.4792 | 0 | 9.7901 | 39.95
2021-09-08 12:00 | 44447.5 | 0 | 9.3642 | 39.95
2021-09-08 12:30 | 44447.5208 | 0 | 9.2324 | 39.95
2021-09-08 13:00 | 44447.5417 | 0 | 8.2503 | 39.95
2021-09-08 13:30 | 44447.5625 | 0 | 8.8245 | 39.95
2021-09-08 14:00 | 44447.5833 | 0 | 10.2671 | 39.95
2021-09-08 14:30 | 44447.6042 | 0 | 9.693 | 39.95
2021-09-08 15:00 | 44447.625 | 0 | 9.9222 | 39.95
2021-09-08 15:30 | 44447.6458 | 0 | 10.7969 | 39.95
2021-09-08 16:00 | 44447.6667 | 0 | 11.1403 | 39.95
2021-09-08 16:30 | 44447.6875 | 0 | 11.9282 | 39.95
2021-09-08 17:00 | 44447.7083 | 0 | 12.5105 | 39.95
2021-09-08 17:30 | 44447.7292 | 0 | 13.2346 | 39.95
2021-09-08 18:00 | 44447.75 | 0 | 13.5698 | 39.95
2021-09-08 18:30 | 44447.7708 | 0 | 14.1355 | 39.95
2021-09-08 19:00 | 44447.7917 | 0 | 13.9001 | 39.95
2021-09-08 19:30 | 44447.8125 | 0 | 13.539 | 39.95
2021-09-08 20:00 | 44447.8333 | 0 | 13.2005 | 39.95
2021-09-08 20:30 | 44447.8542 | 0 | 12.6616 | 39.95
2021-09-08 21:00 | 44447.875 | 0 | 12.2101 | 39.95
2021-09-08 21:30 | 44447.8958 | 0 | 11.8959 | 39.95
2021-09-08 22:00 | 44447.9167 | 0 | 10.9893 | 39.95
2021-09-08 22:30 | 44447.9375 | 0 | 10.1636 | 39.95
2021-09-08 23:00 | 44447.9583 | 0 | 9.6618 | 39.95
2021-09-08 23:30 | 44447.9792 | 0 | 9.2369 | 39.95
2021-09-09 | 44448 | 0 | 8.3854 | 39.95
2021-09-09 00:30 | 44448.0208 | 0 | 7.987 | 39.95
2021-09-09 01:00 | 44448.0417 | 0 | 7.8462 | 39.95
2021-09-09 01:30 | 44448.0625 | 0 | 7.7384 | 39.95
2021-09-09 02:00 | 44448.0833 | 0 | 7.7422 | 39.95
2021-09-09 02:30 | 44448.1042 | 0 | 7.5915 | 39.95
2021-09-09 03:00 | 44448.125 | 0 | 7.5985 | 39.95
2021-09-09 03:30 | 44448.1458 | 0 | 7.7452 | 39.95
2021-09-09 04:00 | 44448.1667 | 0 | 7.9756 | 39.95
2021-09-09 04:30 | 44448.1875 | 0 | 8.5584 | 39.95
2021-09-09 05:00 | 44448.2083 | 0 | 9.0365 | 39.95
2021-09-09 05:30 | 44448.2292 | 0 | 9.7793 | 39.95
2021-09-09 06:00 | 44448.25 | 0 | 10.595 | 39.95
2021-09-09 06:30 | 44448.2708 | 0 | 11.471 | 39.95
2021-09-09 07:00 | 44448.2917 | 0 | 11.5651 | 39.95
2021-09-09 07:30 | 44448.3125 | 0 | 10.9307 | 39.95
2021-09-09 08:00 | 44448.3333 | 0 | 10.1912 | 39.95
2021-09-09 08:30 | 44448.3542 | 0 | 9.5395 | 39.95
2021-09-09 09:00 | 44448.375 | 0 | 8.8427 | 39.95
2021-09-09 09:30 | 44448.3958 | 0 | 8.6011 | 39.95
2021-09-09 10:00 | 44448.4167 | 0 | 9.582 | 39.95
2021-09-09 10:30 | 44448.4375 | 0 | 9.9633 | 39.95
2021-09-09 11:00 | 44448.4583 | 0 | 9.6965 | 39.95
2021-09-09 11:30 | 44448.4792 | 0 | 8.2007 | 39.95
2021-09-09 12:00 | 44448.5 | 0 | 7.8149 | 39.95
2021-09-09 12:30 | 44448.5208 | 0 | 7.7732 | 39.95
2021-09-09 13:00 | 44448.5417 | 0 | 7.9234 | 39.95
2021-09-09 13:30 | 44448.5625 | 0 | 8.2798 | 39.95
2021-09-09 14:00 | 44448.5833 | 0 | 8.5578 | 39.95
2021-09-09 14:30 | 44448.6042 | 0 | 9.1777 | 39.95
2021-09-09 15:00 | 44448.625 | 0 | 9.7989 | 39.95
2021-09-09 15:30 | 44448.6458 | 0 | 10.3297 | 39.95
2021-09-09 16:00 | 44448.6667 | 0 | 11.0742 | 39.95
2021-09-09 16:30 | 44448.6875 | 0 | 11.7757 | 39.95
2021-09-09 17:00 | 44448.7083 | 0 | 12.2682 | 39.95
2021-09-09 17:30 | 44448.7292 | 0 | 12.9789 | 39.95
2021-09-09 18:00 | 44448.75 | 0 | 13.3374 | 39.95
2021-09-09 18:30 | 44448.7708 | 0 | 13.6287 | 39.95
2021-09-09 19:00 | 44448.7917 | 0 | 13.406 | 39.95
2021-09-09 19:30 | 44448.8125 | 0 | 13.3304 | 39.95
2021-09-09 20:00 | 44448.8333 | 0 | 12.9677 | 39.95
2021-09-09 20:30 | 44448.8542 | 0 | 12.5741 | 39.95
2021-09-09 21:00 | 44448.875 | 0 | 12.001 | 39.95
2021-09-09 21:30 | 44448.8958 | 0 | 11.438 | 39.95
2021-09-09 22:00 | 44448.9167 | 0 | 10.9452 | 39.95
2021-09-09 22:30 | 44448.9375 | 0 | 9.9124 | 39.95
2021-09-09 23:00 | 44448.9583 | 0 | 9.3531 | 39.95
2021-09-09 23:30 | 44448.9792 | 0 | 8.8729 | 39.95
2021-09-10 | 44449 | 0 | 8.2264 | 39.95
2021-09-10 00:30 | 44449.0208 | 0 | 7.9432 | 39.95
2021-09-10 01:00 | 44449.0417 | 0 | 7.7703 | 39.95
2021-09-10 01:30 | 44449.0625 | 0 | 7.5728 | 39.95
2021-09-10 02:00 | 44449.0833 | 0 | 7.5633 | 39.95
2021-09-10 02:30 | 44449.1042 | 0 | 7.5376 | 39.95
2021-09-10 03:00 | 44449.125 | 0 | 7.4774 | 39.95
2021-09-10 03:30 | 44449.1458 | 0 | 7.5358 | 39.95
2021-09-10 04:00 | 44449.1667 | 0 | 7.6309 | 39.95
2021-09-10 04:30 | 44449.1875 | 0 | 8.3825 | 39.95
2021-09-10 05:00 | 44449.2083 | 0 | 9.0065 | 39.95
2021-09-10 05:30 | 44449.2292 | 0 | 9.6642 | 39.95
2021-09-10 06:00 | 44449.25 | 0 | 10.4768 | 39.95
2021-09-10 06:30 | 44449.2708 | 0 | 11.1923 | 39.95
2021-09-10 07:00 | 44449.2917 | 0 | 11.448 | 39.95
2021-09-10 07:30 | 44449.3125 | 0 | 10.8561 | 39.95
2021-09-10 08:00 | 44449.3333 | 0 | 10.1429 | 39.95
2021-09-10 08:30 | 44449.3542 | 0 | 9.3666 | 39.95
2021-09-10 09:00 | 44449.375 | 0 | 8.9791 | 39.95
2021-09-10 09:30 | 44449.3958 | 0 | 8.6061 | 39.95
2021-09-10 10:00 | 44449.4167 | 0 | 8.2822 | 39.95
2021-09-10 10:30 | 44449.4375 | 0 | 8.0378 | 39.95
2021-09-10 11:00 | 44449.4583 | 0 | 8.1609 | 39.95
2021-09-10 11:30 | 44449.4792 | 0 | 8.0973 | 39.95
2021-09-10 12:00 | 44449.5 | 0 | 8.2033 | 39.95
2021-09-10 12:30 | 44449.5208 | 0 | 8.2462 | 39.95
2021-09-10 13:00 | 44449.5417 | 0 | 8.4815 | 39.95
2021-09-10 13:30 | 44449.5625 | 0 | 8.8373 | 39.95
2021-09-10 14:00 | 44449.5833 | 0 | 9.6062 | 39.95
2021-09-10 14:30 | 44449.6042 | 0 | 10.0233 | 39.95
2021-09-10 15:00 | 44449.625 | 0 | 10.5744 | 39.95
2021-09-10 15:30 | 44449.6458 | 0 | 11.1107 | 39.95
2021-09-10 16:00 | 44449.6667 | 0 | 11.71 | 39.95
2021-09-10 16:30 | 44449.6875 | 0 | 12.4328 | 39.95
2021-09-10 17:00 | 44449.7083 | 0 | 12.6932 | 39.95
2021-09-10 17:30 | 44449.7292 | 0 | 12.8809 | 39.95
2021-09-10 18:00 | 44449.75 | 0 | 13.1616 | 39.95
2021-09-10 18:30 | 44449.7708 | 0 | 13.4039 | 39.95
2021-09-10 19:00 | 44449.7917 | 0 | 13.1105 | 39.95
2021-09-10 19:30 | 44449.8125 | 0 | 12.8061 | 39.95
2021-09-10 20:00 | 44449.8333 | 0 | 12.3077 | 39.95
2021-09-10 20:30 | 44449.8542 | 0 | 11.8503 | 39.95
2021-09-10 21:00 | 44449.875 | 0 | 11.3844 | 39.95
2021-09-10 21:30 | 44449.8958 | 0 | 11.2023 | 39.95
2021-09-10 22:00 | 44449.9167 | 0 | 10.5828 | 39.95
2021-09-10 22:30 | 44449.9375 | 0 | 9.7903 | 39.95
2021-09-10 23:00 | 44449.9583 | 0 | 9.244 | 39.95
2021-09-10 23:30 | 44449.9792 | 0 | 8.7838 | 39.95
2021-09-11 | 44450 | 0 | 8.2359 | 39.95
2021-09-11 00:30 | 44450.0208 | 0 | 7.9188 | 39.95
2021-09-11 01:00 | 44450.0417 | 0 | 7.7967 | 39.95
2021-09-11 01:30 | 44450.0625 | 0 | 7.5708 | 39.95
2021-09-11 02:00 | 44450.0833 | 0 | 7.4222 | 39.95
2021-09-11 02:30 | 44450.1042 | 0 | 7.305 | 39.95
2021-09-11 03:00 | 44450.125 | 0 | 7.2523 | 39.95
2021-09-11 03:30 | 44450.1458 | 0 | 7.4014 | 39.95
2021-09-11 04:00 | 44450.1667 | 0 | 7.3547 | 39.95
2021-09-11 04:30 | 44450.1875 | 0 | 7.5529 | 39.95
2021-09-11 05:00 | 44450.2083 | 0 | 7.8981 | 39.95
2021-09-11 05:30 | 44450.2292 | 0 | 8.0633 | 39.95
2021-09-11 06:00 | 44450.25 | 0 | 8.4136 | 39.95
2021-09-11 06:30 | 44450.2708 | 0 | 8.3172 | 39.95
2021-09-11 07:00 | 44450.2917 | 0 | 8.2377 | 39.95
2021-09-11 07:30 | 44450.3125 | 0 | 7.8825 | 39.95
2021-09-11 08:00 | 44450.3333 | 0 | 7.625 | 39.95
2021-09-11 08:30 | 44450.3542 | 0 | 7.2028 | 39.95
2021-09-11 09:00 | 44450.375 | 0 | 6.8718 | 39.95
2021-09-11 09:30 | 44450.3958 | 0 | 6.574 | 39.95
2021-09-11 10:00 | 44450.4167 | 0 | 6.0669 | 39.95
2021-09-11 10:30 | 44450.4375 | 0 | 5.9894 | 39.95
2021-09-11 11:00 | 44450.4583 | 0 | 5.721 | 39.95
2021-09-11 11:30 | 44450.4792 | 0 | 5.4913 | 39.95
2021-09-11 12:00 | 44450.5 | 0 | 5.4381 | 39.95
2021-09-11 12:30 | 44450.5208 | 0 | 5.4542 | 39.95
2021-09-11 13:00 | 44450.5417 | 0 | 5.658 | 39.95
2021-09-11 13:30 | 44450.5625 | 0 | 5.8636 | 39.95
2021-09-11 14:00 | 44450.5833 | 0 | 6.2584 | 39.95
2021-09-11 14:30 | 44450.6042 | 0 | 6.8241 | 39.95
2021-09-11 15:00 | 44450.625 | 0 | 7.5057 | 39.95
2021-09-11 15:30 | 44450.6458 | 0 | 8.2194 | 39.95
2021-09-11 16:00 | 44450.6667 | 0 | 8.9773 | 39.95
2021-09-11 16:30 | 44450.6875 | 0 | 9.9106 | 39.95
2021-09-11 17:00 | 44450.7083 | 0 | 10.5761 | 39.95
2021-09-11 17:30 | 44450.7292 | 0 | 10.8619 | 39.95
2021-09-11 18:00 | 44450.75 | 0 | 11.2703 | 39.95
2021-09-11 18:30 | 44450.7708 | 0 | 11.4639 | 39.95
2021-09-11 19:00 | 44450.7917 | 0 | 11.0502 | 39.95
2021-09-11 19:30 | 44450.8125 | 0 | 10.7941 | 39.95
2021-09-11 20:00 | 44450.8333 | 0 | 10.6814 | 39.95
2021-09-11 20:30 | 44450.8542 | 0 | 10.1528 | 39.95
2021-09-11 21:00 | 44450.875 | 0 | 9.9553 | 39.95
2021-09-11 21:30 | 44450.8958 | 0 | 9.6804 | 39.95
2021-09-11 22:00 | 44450.9167 | 0 | 9.3344 | 39.95
2021-09-11 22:30 | 44450.9375 | 0 | 8.8887 | 39.95
2021-09-11 23:00 | 44450.9583 | 0 | 8.3361 | 39.95
2021-09-11 23:30 | 44450.9792 | 0 | 8.0021 | 39.95
2021-09-12 | 44451 | 0 | 7.5891 | 39.95
2021-09-12 00:30 | 44451.0208 | 0 | 7.3422 | 39.95
2021-09-12 01:00 | 44451.0417 | 0 | 7.0909 | 39.95
2021-09-12 01:30 | 44451.0625 | 0 | 7.0237 | 39.95
2021-09-12 02:00 | 44451.0833 | 0 | 6.9754 | 39.95
2021-09-12 02:30 | 44451.1042 | 0 | 6.9288 | 39.95
2021-09-12 03:00 | 44451.125 | 0 | 6.8618 | 39.95
2021-09-12 03:30 | 44451.1458 | 0 | 6.8898 | 39.95
2021-09-12 04:00 | 44451.1667 | 0 | 6.6754 | 39.95
2021-09-12 04:30 | 44451.1875 | 0 | 6.839 | 39.95
2021-09-12 05:00 | 44451.2083 | 0 | 6.9119 | 39.95
2021-09-12 05:30 | 44451.2292 | 0 | 7.038 | 39.95
2021-09-12 06:00 | 44451.25 | 0 | 7.2035 | 39.95
2021-09-12 06:30 | 44451.2708 | 0 | 6.9046 | 39.95
2021-09-12 07:00 | 44451.2917 | 0 | 6.8181 | 39.95
2021-09-12 07:30 | 44451.3125 | 0 | 6.5163 | 39.95
2021-09-12 08:00 | 44451.3333 | 0 | 6.1699 | 39.95
2021-09-12 08:30 | 44451.3542 | 0 | 5.9811 | 39.95
2021-09-12 09:00 | 44451.375 | 0 | 5.6506 | 39.95
2021-09-12 09:30 | 44451.3958 | 0 | 5.328 | 39.95
2021-09-12 10:00 | 44451.4167 | 0 | 5.1944 | 39.95
2021-09-12 10:30 | 44451.4375 | 0 | 5.0866 | 39.95
2021-09-12 11:00 | 44451.4583 | 0 | 4.8967 | 39.95
2021-09-12 11:30 | 44451.4792 | 0 | 4.9148 | 39.95
2021-09-12 12:00 | 44451.5 | 0 | 4.7034 | 39.95
2021-09-12 12:30 | 44451.5208 | 0 | 4.7353 | 39.95
2021-09-12 13:00 | 44451.5417 | 0 | 5.1676 | 39.95
2021-09-12 13:30 | 44451.5625 | 0 | 5.2289 | 39.95
2021-09-12 14:00 | 44451.5833 | 0 | 5.9437 | 39.95
2021-09-12 14:30 | 44451.6042 | 0 | 6.4933 | 39.95
2021-09-12 15:00 | 44451.625 | 0 | 7.1113 | 39.95
2021-09-12 15:30 | 44451.6458 | 0 | 7.765 | 39.95
2021-09-12 16:00 | 44451.6667 | 0 | 8.7402 | 39.95
2021-09-12 16:30 | 44451.6875 | 0 | 9.791 | 39.95
2021-09-12 17:00 | 44451.7083 | 0 | 10.4265 | 39.95
2021-09-12 17:30 | 44451.7292 | 0 | 11.1051 | 39.95
2021-09-12 18:00 | 44451.75 | 0 | 11.5917 | 39.95
2021-09-12 18:30 | 44451.7708 | 0 | 11.9786 | 39.95
2021-09-12 19:00 | 44451.7917 | 0 | 11.5615 | 39.95
2021-09-12 19:30 | 44451.8125 | 0 | 11.1571 | 39.95
2021-09-12 20:00 | 44451.8333 | 0 | 10.8474 | 39.95
2021-09-12 20:30 | 44451.8542 | 0 | 10.3434 | 39.95
2021-09-12 21:00 | 44451.875 | 0 | 9.9316 | 39.95
2021-09-12 21:30 | 44451.8958 | 0 | 9.6158 | 39.95
2021-09-12 22:00 | 44451.9167 | 0 | 9.2435 | 39.95
2021-09-12 22:30 | 44451.9375 | 0 | 8.6627 | 39.95
2021-09-12 23:00 | 44451.9583 | 0 | 8.2673 | 39.95
2021-09-12 23:30 | 44451.9792 | 0 | 7.8788 | 39.95
2021-09-13 | 44452 | 0 | 7.4143 | 39.95
2021-09-13 00:30 | 44452.0208 | 0 | 7.303 | 39.95
2021-09-13 01:00 | 44452.0417 | 0 | 7.173 | 39.95
2021-09-13 01:30 | 44452.0625 | 0 | 7.1145 | 39.95
2021-09-13 02:00 | 44452.0833 | 0 | 7.0539 | 39.95
2021-09-13 02:30 | 44452.1042 | 0 | 6.9344 | 39.95
2021-09-13 03:00 | 44452.125 | 0 | 7.068 | 39.95
2021-09-13 03:30 | 44452.1458 | 0 | 7.2909 | 39.95
2021-09-13 04:00 | 44452.1667 | 0 | 7.4517 | 39.95
2021-09-13 04:30 | 44452.1875 | 0 | 7.867 | 39.95
2021-09-13 05:00 | 44452.2083 | 0 | 8.5875 | 39.95
2021-09-13 05:30 | 44452.2292 | 0 | 9.107 | 39.95
2021-09-13 06:00 | 44452.25 | 0 | 9.8867 | 39.95
2021-09-13 06:30 | 44452.2708 | 0 | 10.6679 | 39.95
2021-09-13 07:00 | 44452.2917 | 0 | 11.1973 | 39.95
2021-09-13 07:30 | 44452.3125 | 0 | 10.6426 | 39.95
2021-09-13 08:00 | 44452.3333 | 0 | 10.121 | 39.95
2021-09-13 08:30 | 44452.3542 | 0 | 9.7047 | 39.95
2021-09-13 09:00 | 44452.375 | 0 | 9.4437 | 39.95
2021-09-13 09:30 | 44452.3958 | 0 | 9.1732 | 39.95
2021-09-13 10:00 | 44452.4167 | 0 | 8.9664 | 39.95
2021-09-13 10:30 | 44452.4375 | 0 | 9.0292 | 39.95
2021-09-13 11:00 | 44452.4583 | 0 | 9.297 | 39.95
2021-09-13 11:30 | 44452.4792 | 0 | 9.2153 | 39.95
2021-09-13 12:00 | 44452.5 | 0 | 9.3622 | 39.95
2021-09-13 12:30 | 44452.5208 | 0 | 9.984 | 39.95
2021-09-13 13:00 | 44452.5417 | 0 | 12.8845 | 39.95
2021-09-13 13:30 | 44452.5625 | 0 | 11.233 | 39.95
2021-09-13 14:00 | 44452.5833 | 0 | 11.0264 | 39.95
2021-09-13 14:30 | 44452.6042 | 0 | 13.1935 | 39.95
2021-09-13 15:00 | 44452.625 | 0 | 12.2378 | 39.95
2021-09-13 15:30 | 44452.6458 | 0 | 11.765 | 39.95
2021-09-13 16:00 | 44452.6667 | 0 | 11.8162 | 39.95
2021-09-13 16:30 | 44452.6875 | 0 | 12.7184 | 39.95
2021-09-13 17:00 | 44452.7083 | 0 | 12.9751 | 39.95
2021-09-13 17:30 | 44452.7292 | 0 | 13.6357 | 39.95
2021-09-13 18:00 | 44452.75 | 0 | 14.1565 | 39.95
2021-09-13 18:30 | 44452.7708 | 0 | 14.4508 | 39.95
2021-09-13 19:00 | 44452.7917 | 0 | 14.0259 | 39.95
2021-09-13 19:30 | 44452.8125 | 0 | 13.5741 | 39.95
2021-09-13 20:00 | 44452.8333 | 0 | 13.234 | 39.95
2021-09-13 20:30 | 44452.8542 | 0 | 12.4771 | 39.95
2021-09-13 21:00 | 44452.875 | 0 | 12.096 | 39.95
2021-09-13 21:30 | 44452.8958 | 0 | 11.6896 | 39.95
2021-09-13 22:00 | 44452.9167 | 0 | 10.8948 | 39.95
2021-09-13 22:30 | 44452.9375 | 0 | 9.9414 | 39.95
2021-09-13 23:00 | 44452.9583 | 0 | 9.2655 | 39.95
2021-09-13 23:30 | 44452.9792 | 0 | 8.7868 | 39.95
2021-09-14 | 44453 | 0 | 8.2938 | 39.95
2021-09-14 00:30 | 44453.0208 | 0 | 7.8488 | 39.95
2021-09-14 01:00 | 44453.0417 | 0 | 7.7466 | 39.95
2021-09-14 01:30 | 44453.0625 | 0 | 7.5205 | 39.95
2021-09-14 02:00 | 44453.0833 | 0 | 7.5933 | 39.95
2021-09-14 02:30 | 44453.1042 | 0 | 7.437 | 39.95
2021-09-14 03:00 | 44453.125 | 0 | 7.4569 | 39.95
2021-09-14 03:30 | 44453.1458 | 0 | 7.5746 | 39.95
2021-09-14 04:00 | 44453.1667 | 0 | 7.6965 | 39.95
2021-09-14 04:30 | 44453.1875 | 0 | 8.1971 | 39.95
2021-09-14 05:00 | 44453.2083 | 0 | 8.7982 | 39.95
2021-09-14 05:30 | 44453.2292 | 0 | 9.437 | 39.95
2021-09-14 06:00 | 44453.25 | 0 | 10.0131 | 39.95
2021-09-14 06:30 | 44453.2708 | 0 | 10.6221 | 39.95
2021-09-14 07:00 | 44453.2917 | 0 | 10.8133 | 39.95
2021-09-14 07:30 | 44453.3125 | 0 | 10.2426 | 39.95
2021-09-14 08:00 | 44453.3333 | 0 | 9.4811 | 39.95
2021-09-14 08:30 | 44453.3542 | 0 | 8.7853 | 39.95
2021-09-14 09:00 | 44453.375 | 0 | 8.1786 | 39.95
2021-09-14 09:30 | 44453.3958 | 0 | 7.745 | 39.95
2021-09-14 10:00 | 44453.4167 | 0 | 7.4038 | 39.95
2021-09-14 10:30 | 44453.4375 | 0 | 7.2495 | 39.95
2021-09-14 11:00 | 44453.4583 | 0 | 6.7725 | 39.95
2021-09-14 11:30 | 44453.4792 | 0 | 6.6958 | 39.95
2021-09-14 12:00 | 44453.5 | 0 | 6.763 | 39.95
2021-09-14 12:30 | 44453.5208 | 0 | 6.7354 | 39.95
2021-09-14 13:00 | 44453.5417 | 0 | 6.9575 | 39.95
2021-09-14 13:30 | 44453.5625 | 0 | 7.0945 | 39.95
2021-09-14 14:00 | 44453.5833 | 0 | 7.7674 | 39.95
2021-09-14 14:30 | 44453.6042 | 0 | 8.4139 | 39.95
2021-09-14 15:00 | 44453.625 | 0 | 8.9124 | 39.95
2021-09-14 15:30 | 44453.6458 | 0 | 9.7876 | 39.95
2021-09-14 16:00 | 44453.6667 | 0 | 10.4382 | 39.95
2021-09-14 16:30 | 44453.6875 | 0 | 11.1957 | 39.95
2021-09-14 17:00 | 44453.7083 | 0 | 11.9254 | 39.95
2021-09-14 17:30 | 44453.7292 | 0 | 12.6972 | 39.95
2021-09-14 18:00 | 44453.75 | 0 | 13.3586 | 39.95
2021-09-14 18:30 | 44453.7708 | 0 | 13.6117 | 39.95
2021-09-14 19:00 | 44453.7917 | 0 | 13.4927 | 39.95
2021-09-14 19:30 | 44453.8125 | 0 | 13.2346 | 39.95
2021-09-14 20:00 | 44453.8333 | 0 | 12.9004 | 39.95
2021-09-14 20:30 | 44453.8542 | 0 | 12.1936 | 39.95
2021-09-14 21:00 | 44453.875 | 0 | 11.7433 | 39.95
2021-09-14 21:30 | 44453.8958 | 0 | 11.1669 | 39.95
2021-09-14 22:00 | 44453.9167 | 0 | 10.5569 | 39.95
2021-09-14 22:30 | 44453.9375 | 0 | 9.7078 | 39.95
2021-09-14 23:00 | 44453.9583 | 0 | 9.1972 | 39.95
2021-09-14 23:30 | 44453.9792 | 0 | 8.7697 | 39.95
2021-09-15 | 44454 | 0 | 8.3514 | 39.95
2021-09-15 00:30 | 44454.0208 | 0 | 8.0542 | 39.95
2021-09-15 01:00 | 44454.0417 | 0 | 7.8056 | 39.95
2021-09-15 01:30 | 44454.0625 | 0 | 7.7536 | 39.95
2021-09-15 02:00 | 44454.0833 | 0 | 7.7382 | 39.95
2021-09-15 02:30 | 44454.1042 | 0 | 7.6601 | 39.95
2021-09-15 03:00 | 44454.125 | 0 | 7.6641 | 39.95
2021-09-15 03:30 | 44454.1458 | 0 | 7.7152 | 39.95
2021-09-15 04:00 | 44454.1667 | 0 | 7.9329 | 39.95
2021-09-15 04:30 | 44454.1875 | 0 | 8.5827 | 39.95
2021-09-15 05:00 | 44454.2083 | 0 | 9.0768 | 39.95
2021-09-15 05:30 | 44454.2292 | 0 | 9.9079 | 39.95
2021-09-15 06:00 | 44454.25 | 0 | 10.8564 | 39.95
2021-09-15 06:30 | 44454.2708 | 0 | 11.2733 | 39.95
2021-09-15 07:00 | 44454.2917 | 0 | 11.4035 | 39.95
2021-09-15 07:30 | 44454.3125 | 0 | 10.7741 | 39.95
2021-09-15 08:00 | 44454.3333 | 0 | 10.0659 | 39.95
2021-09-15 08:30 | 44454.3542 | 0 | 9.1174 | 39.95
2021-09-15 09:00 | 44454.375 | 0 | 8.5224 | 39.95
2021-09-15 09:30 | 44454.3958 | 0 | 7.985 | 39.95
2021-09-15 10:00 | 44454.4167 | 0 | 7.6021 | 39.95
2021-09-15 10:30 | 44454.4375 | 0 | 7.3273 | 39.95
2021-09-15 11:00 | 44454.4583 | 0 | 7.2181 | 39.95
2021-09-15 11:30 | 44454.4792 | 0 | 7.3589 | 39.95
2021-09-15 12:00 | 44454.5 | 0 | 7.2567 | 39.95
2021-09-15 12:30 | 44454.5208 | 0 | 7.2481 | 39.95
2021-09-15 13:00 | 44454.5417 | 0 | 7.6747 | 39.95
2021-09-15 13:30 | 44454.5625 | 0 | 8.0553 | 39.95
2021-09-15 14:00 | 44454.5833 | 0 | 8.4348 | 39.95
2021-09-15 14:30 | 44454.6042 | 0 | 9.1119 | 39.95
2021-09-15 15:00 | 44454.625 | 0 | 9.5938 | 39.95
2021-09-15 15:30 | 44454.6458 | 0 | 10.2281 | 39.95
2021-09-15 16:00 | 44454.6667 | 0 | 10.8695 | 39.95
2021-09-15 16:30 | 44454.6875 | 0 | 11.8251 | 39.95
2021-09-15 17:00 | 44454.7083 | 0 | 12.3494 | 39.95
2021-09-15 17:30 | 44454.7292 | 0 | 13.0136 | 39.95
2021-09-15 18:00 | 44454.75 | 0 | 13.4035 | 39.95
2021-09-15 18:30 | 44454.7708 | 0 | 13.6336 | 39.95
2021-09-15 19:00 | 44454.7917 | 0 | 13.4511 | 39.95
2021-09-15 19:30 | 44454.8125 | 0 | 13.1787 | 39.95
2021-09-15 20:00 | 44454.8333 | 0 | 12.9331 | 39.95
2021-09-15 20:30 | 44454.8542 | 0 | 12.3043 | 39.95
2021-09-15 21:00 | 44454.875 | 0 | 11.8341 | 39.95
2021-09-15 21:30 | 44454.8958 | 0 | 11.3504 | 39.95
2021-09-15 22:00 | 44454.9167 | 0 | 10.7444 | 39.95
2021-09-15 22:30 | 44454.9375 | 0 | 9.9842 | 39.95
2021-09-15 23:00 | 44454.9583 | 0 | 9.352 | 39.95
2021-09-15 23:30 | 44454.9792 | 0 | 8.8073 | 39.95
2021-09-16 | 44455 | 0 | 8.2559 | 39.95
2021-09-16 00:30 | 44455.0208 | 0 | 8.0464 | 39.95
2021-09-16 01:00 | 44455.0417 | 0 | 7.7479 | 39.95
2021-09-16 01:30 | 44455.0625 | 0 | 7.6748 | 39.95
2021-09-16 02:00 | 44455.0833 | 0 | 7.6659 | 39.95
2021-09-16 02:30 | 44455.1042 | 0 | 7.6881 | 39.95
2021-09-16 03:00 | 44455.125 | 0 | 7.6267 | 39.95
2021-09-16 03:30 | 44455.1458 | 0 | 7.7116 | 39.95
2021-09-16 04:00 | 44455.1667 | 0 | 8.0421 | 39.95
2021-09-16 04:30 | 44455.1875 | 0 | 8.5214 | 39.95
2021-09-16 05:00 | 44455.2083 | 0 | 8.8578 | 39.95
2021-09-16 05:30 | 44455.2292 | 0 | 9.6137 | 39.95
2021-09-16 06:00 | 44455.25 | 0 | 10.5023 | 39.95
2021-09-16 06:30 | 44455.2708 | 0 | 11.1923 | 39.95
2021-09-16 07:00 | 44455.2917 | 0 | 11.2084 | 39.95
2021-09-16 07:30 | 44455.3125 | 0 | 10.4676 | 39.95
2021-09-16 08:00 | 44455.3333 | 0 | 9.7216 | 39.95
2021-09-16 08:30 | 44455.3542 | 0 | 9.0778 | 39.95
2021-09-16 09:00 | 44455.375 | 0 | 8.5789 | 39.95
2021-09-16 09:30 | 44455.3958 | 0 | 8.2932 | 39.95
2021-09-16 10:00 | 44455.4167 | 0 | 7.8981 | 39.95
2021-09-16 10:30 | 44455.4375 | 0 | 7.8464 | 39.95
2021-09-16 11:00 | 44455.4583 | 0 | 7.5474 | 39.95
2021-09-16 11:30 | 44455.4792 | 0 | 7.8429 | 39.95
2021-09-16 12:00 | 44455.5 | 0 | 8.0704 | 39.95
2021-09-16 12:30 | 44455.5208 | 0 | 8.1919 | 39.95
2021-09-16 13:00 | 44455.5417 | 0 | 8.6995 | 39.95
2021-09-16 13:30 | 44455.5625 | 0 | 8.3928 | 39.95
2021-09-16 14:00 | 44455.5833 | 0 | 8.8932 | 39.95
2021-09-16 14:30 | 44455.6042 | 0 | 9.2512 | 39.95
2021-09-16 15:00 | 44455.625 | 0 | 9.5078 | 39.95
2021-09-16 15:30 | 44455.6458 | 0 | 10.2396 | 39.95
2021-09-16 16:00 | 44455.6667 | 0 | 10.9552 | 39.95
2021-09-16 16:30 | 44455.6875 | 0 | 11.7912 | 39.95
2021-09-16 17:00 | 44455.7083 | 0 | 12.1616 | 39.95
2021-09-16 17:30 | 44455.7292 | 0 | 12.6767 | 39.95
2021-09-16 18:00 | 44455.75 | 0 | 13.303 | 39.95
2021-09-16 18:30 | 44455.7708 | 0 | 13.475 | 39.95
2021-09-16 19:00 | 44455.7917 | 0 | 13.263 | 39.95
2021-09-16 19:30 | 44455.8125 | 0 | 13.2341 | 39.95
2021-09-16 20:00 | 44455.8333 | 0 | 12.7614 | 39.95
2021-09-16 20:30 | 44455.8542 | 0 | 12.2695 | 39.95
2021-09-16 21:00 | 44455.875 | 0 | 11.8132 | 39.95
2021-09-16 21:30 | 44455.8958 | 0 | 11.4342 | 39.95
2021-09-16 22:00 | 44455.9167 | 0 | 10.8144 | 39.95
2021-09-16 22:30 | 44455.9375 | 0 | 10.041 | 39.95
2021-09-16 23:00 | 44455.9583 | 0 | 9.3335 | 39.95
2021-09-16 23:30 | 44455.9792 | 0 | 8.9719 | 39.95
2021-09-17 | 44456 | 0 | 8.4574 | 39.95
2021-09-17 00:30 | 44456.0208 | 0 | 8.0467 | 39.95
2021-09-17 01:00 | 44456.0417 | 0 | 7.8691 | 39.95
2021-09-17 01:30 | 44456.0625 | 0 | 7.6396 | 39.95
2021-09-17 02:00 | 44456.0833 | 0 | 7.6321 | 39.95
2021-09-17 02:30 | 44456.1042 | 0 | 7.6416 | 39.95
2021-09-17 03:00 | 44456.125 | 0 | 7.5231 | 39.95
2021-09-17 03:30 | 44456.1458 | 0 | 7.4106 | 39.95
2021-09-17 04:00 | 44456.1667 | 0 | 7.7239 | 39.95
2021-09-17 04:30 | 44456.1875 | 0 | 8.2583 | 39.95
2021-09-17 05:00 | 44456.2083 | 0 | 8.7846 | 39.95
2021-09-17 05:30 | 44456.2292 | 0 | 9.4893 | 39.95
2021-09-17 06:00 | 44456.25 | 0 | 10.1149 | 39.95
2021-09-17 06:30 | 44456.2708 | 0 | 10.6853 | 39.95
2021-09-17 07:00 | 44456.2917 | 0 | 11.0577 | 39.95
2021-09-17 07:30 | 44456.3125 | 0 | 10.4761 | 39.95
2021-09-17 08:00 | 44456.3333 | 0 | 9.8127 | 39.95
2021-09-17 08:30 | 44456.3542 | 0 | 9.2354 | 39.95
2021-09-17 09:00 | 44456.375 | 0 | 8.7425 | 39.95
2021-09-17 09:30 | 44456.3958 | 0 | 8.4071 | 39.95
2021-09-17 10:00 | 44456.4167 | 0 | 8.2552 | 39.95
2021-09-17 10:30 | 44456.4375 | 0 | 8.3421 | 39.95
2021-09-17 11:00 | 44456.4583 | 0 | 8.3928 | 39.95
2021-09-17 11:30 | 44456.4792 | 0 | 7.9263 | 39.95
2021-09-17 12:00 | 44456.5 | 0 | 7.8941 | 39.95
2021-09-17 12:30 | 44456.5208 | 0 | 7.5161 | 39.95
2021-09-17 13:00 | 44456.5417 | 0 | 7.573 | 39.95
2021-09-17 13:30 | 44456.5625 | 0 | 8.554 | 39.95
2021-09-17 14:00 | 44456.5833 | 0 | 8.8515 | 39.95
2021-09-17 14:30 | 44456.6042 | 0 | 8.6958 | 39.95
2021-09-17 15:00 | 44456.625 | 0 | 9.3877 | 39.95
2021-09-17 15:30 | 44456.6458 | 0 | 9.9887 | 39.95
2021-09-17 16:00 | 44456.6667 | 0 | 10.8274 | 39.95
2021-09-17 16:30 | 44456.6875 | 0 | 11.5689 | 39.95
2021-09-17 17:00 | 44456.7083 | 0 | 11.9351 | 39.95
2021-09-17 17:30 | 44456.7292 | 0 | 12.3021 | 39.95
2021-09-17 18:00 | 44456.75 | 0 | 12.7187 | 39.95
2021-09-17 18:30 | 44456.7708 | 0 | 12.9362 | 39.95
2021-09-17 19:00 | 44456.7917 | 0 | 12.7024 | 39.95
2021-09-17 19:30 | 44456.8125 | 0 | 12.4845 | 39.95
2021-09-17 20:00 | 44456.8333 | 0 | 12.0453 | 39.95
2021-09-17 20:30 | 44456.8542 | 0 | 11.5973 | 39.95
2021-09-17 21:00 | 44456.875 | 0 | 11.2832 | 39.95
2021-09-17 21:30 | 44456.8958 | 0 | 10.9481 | 39.95
2021-09-17 22:00 | 44456.9167 | 0 | 10.47 | 39.95
2021-09-17 22:30 | 44456.9375 | 0 | 9.7471 | 39.95
2021-09-17 23:00 | 44456.9583 | 0 | 9.3665 | 39.95
2021-09-17 23:30 | 44456.9792 | 0 | 8.8572 | 39.95
2021-09-18 | 44457 | 0 | 8.1717 | 39.95
2021-09-18 00:30 | 44457.0208 | 0 | 7.8685 | 39.95
2021-09-18 01:00 | 44457.0417 | 0 | 7.7949 | 39.95
2021-09-18 01:30 | 44457.0625 | 0 | 7.5446 | 39.95
2021-09-18 02:00 | 44457.0833 | 0 | 7.5374 | 39.95
2021-09-18 02:30 | 44457.1042 | 0 | 7.5225 | 39.95
2021-09-18 03:00 | 44457.125 | 0 | 7.5335 | 39.95
2021-09-18 03:30 | 44457.1458 | 0 | 7.5692 | 39.95
2021-09-18 04:00 | 44457.1667 | 0 | 7.585 | 39.95
2021-09-18 04:30 | 44457.1875 | 0 | 7.6935 | 39.95
2021-09-18 05:00 | 44457.2083 | 0 | 7.8585 | 39.95
2021-09-18 05:30 | 44457.2292 | 0 | 8.0784 | 39.95
2021-09-18 06:00 | 44457.25 | 0 | 8.2745 | 39.95
2021-09-18 06:30 | 44457.2708 | 0 | 8.3117 | 39.95
2021-09-18 07:00 | 44457.2917 | 0 | 8.265 | 39.95
2021-09-18 07:30 | 44457.3125 | 0 | 7.9324 | 39.95
2021-09-18 08:00 | 44457.3333 | 0 | 7.1523 | 39.95
2021-09-18 08:30 | 44457.3542 | 0 | 6.8581 | 39.95
2021-09-18 09:00 | 44457.375 | 0 | 7.6162 | 39.95
2021-09-18 09:30 | 44457.3958 | 0 | 7.5708 | 39.95
2021-09-18 10:00 | 44457.4167 | 0 | 6.2785 | 39.95
2021-09-18 10:30 | 44457.4375 | 0 | 6.399 | 39.95
2021-09-18 11:00 | 44457.4583 | 0 | 5.772 | 39.95
2021-09-18 11:30 | 44457.4792 | 0 | 5.5097 | 39.95
2021-09-18 12:00 | 44457.5 | 0 | 5.1856 | 39.95
2021-09-18 12:30 | 44457.5208 | 0 | 5.1299 | 39.95
2021-09-18 13:00 | 44457.5417 | 0 | 5.5528 | 39.95
2021-09-18 13:30 | 44457.5625 | 0 | 6.2388 | 39.95
2021-09-18 14:00 | 44457.5833 | 0 | 6.9255 | 39.95
2021-09-18 14:30 | 44457.6042 | 0 | 6.7701 | 39.95
2021-09-18 15:00 | 44457.625 | 0 | 7.0432 | 39.95
2021-09-18 15:30 | 44457.6458 | 0 | 7.7949 | 39.95
2021-09-18 16:00 | 44457.6667 | 0 | 8.3149 | 39.95
2021-09-18 16:30 | 44457.6875 | 0 | 9.7389 | 39.95
2021-09-18 17:00 | 44457.7083 | 0 | 10.1795 | 39.95
2021-09-18 17:30 | 44457.7292 | 0 | 10.5312 | 39.95
2021-09-18 18:00 | 44457.75 | 0 | 10.8836 | 39.95
2021-09-18 18:30 | 44457.7708 | 0 | 11.0157 | 39.95
2021-09-18 19:00 | 44457.7917 | 0 | 10.6556 | 39.95
2021-09-18 19:30 | 44457.8125 | 0 | 10.5652 | 39.95
2021-09-18 20:00 | 44457.8333 | 0 | 10.309 | 39.95
2021-09-18 20:30 | 44457.8542 | 0 | 9.8931 | 39.95
2021-09-18 21:00 | 44457.875 | 0 | 9.5372 | 39.95
2021-09-18 21:30 | 44457.8958 | 0 | 9.3771 | 39.95
2021-09-18 22:00 | 44457.9167 | 0 | 9.2005 | 39.95
2021-09-18 22:30 | 44457.9375 | 0 | 8.7944 | 39.95
2021-09-18 23:00 | 44457.9583 | 0 | 8.4681 | 39.95
2021-09-18 23:30 | 44457.9792 | 0 | 8.071 | 39.95
2021-09-19 | 44458 | 0 | 7.583 | 39.95
2021-09-19 00:30 | 44458.0208 | 0 | 7.2033 | 39.95
2021-09-19 01:00 | 44458.0417 | 0 | 7.1449 | 39.95
2021-09-19 01:30 | 44458.0625 | 0 | 6.966 | 39.95
2021-09-19 02:00 | 44458.0833 | 0 | 6.8825 | 39.95
2021-09-19 02:30 | 44458.1042 | 0 | 6.8191 | 39.95
2021-09-19 03:00 | 44458.125 | 0 | 6.843 | 39.95
2021-09-19 03:30 | 44458.1458 | 0 | 6.8002 | 39.95
2021-09-19 04:00 | 44458.1667 | 0 | 6.7834 | 39.95
2021-09-19 04:30 | 44458.1875 | 0 | 6.8693 | 39.95
2021-09-19 05:00 | 44458.2083 | 0 | 6.9414 | 39.95
2021-09-19 05:30 | 44458.2292 | 0 | 7.0678 | 39.95
2021-09-19 06:00 | 44458.25 | 0 | 7.1527 | 39.95
2021-09-19 06:30 | 44458.2708 | 0 | 6.9473 | 39.95
2021-09-19 07:00 | 44458.2917 | 0 | 6.8935 | 39.95
2021-09-19 07:30 | 44458.3125 | 0 | 6.6038 | 39.95
2021-09-19 08:00 | 44458.3333 | 0 | 6.2881 | 39.95
2021-09-19 08:30 | 44458.3542 | 0 | 6.1292 | 39.95
2021-09-19 09:00 | 44458.375 | 0 | 5.9334 | 39.95
2021-09-19 09:30 | 44458.3958 | 0 | 5.959 | 39.95
2021-09-19 10:00 | 44458.4167 | 0 | 5.6243 | 39.95
2021-09-19 10:30 | 44458.4375 | 0 | 5.5091 | 39.95
2021-09-19 11:00 | 44458.4583 | 0 | 5.2973 | 39.95
2021-09-19 11:30 | 44458.4792 | 0 | 5.2033 | 39.95
2021-09-19 12:00 | 44458.5 | 0 | 5.2928 | 39.95
2021-09-19 12:30 | 44458.5208 | 0 | 5.2816 | 39.95
2021-09-19 13:00 | 44458.5417 | 0 | 5.4812 | 39.95
2021-09-19 13:30 | 44458.5625 | 0 | 5.899 | 39.95
2021-09-19 14:00 | 44458.5833 | 0 | 6.4613 | 39.95
2021-09-19 14:30 | 44458.6042 | 0 | 6.9263 | 39.95
2021-09-19 15:00 | 44458.625 | 0 | 7.6881 | 39.95
2021-09-19 15:30 | 44458.6458 | 0 | 8.4428 | 39.95
2021-09-19 16:00 | 44458.6667 | 0 | 9.2066 | 39.95
2021-09-19 16:30 | 44458.6875 | 0 | 9.9574 | 39.95
2021-09-19 17:00 | 44458.7083 | 0 | 10.5273 | 39.95
2021-09-19 17:30 | 44458.7292 | 0 | 10.887 | 39.95
2021-09-19 18:00 | 44458.75 | 0 | 11.3054 | 39.95
2021-09-19 18:30 | 44458.7708 | 0 | 11.4925 | 39.95
2021-09-19 19:00 | 44458.7917 | 0 | 11.264 | 39.95
2021-09-19 19:30 | 44458.8125 | 0 | 10.8012 | 39.95
2021-09-19 20:00 | 44458.8333 | 0 | 10.5513 | 39.95
2021-09-19 20:30 | 44458.8542 | 0 | 10.1379 | 39.95
2021-09-19 21:00 | 44458.875 | 0 | 9.8404 | 39.95
2021-09-19 21:30 | 44458.8958 | 0 | 9.5254 | 39.95
2021-09-19 22:00 | 44458.9167 | 0 | 9.0512 | 39.95
2021-09-19 22:30 | 44458.9375 | 0 | 8.4057 | 39.95
2021-09-19 23:00 | 44458.9583 | 0 | 8.0174 | 39.95
2021-09-19 23:30 | 44458.9792 | 0 | 7.7631 | 39.95
2021-09-20 | 44459 | 0 | 7.2884 | 39.95
2021-09-20 00:30 | 44459.0208 | 0 | 7.1002 | 39.95
2021-09-20 01:00 | 44459.0417 | 0 | 6.9418 | 39.95
2021-09-20 01:30 | 44459.0625 | 0 | 6.8523 | 39.95
2021-09-20 02:00 | 44459.0833 | 0 | 6.8976 | 39.95
2021-09-20 02:30 | 44459.1042 | 0 | 6.7515 | 39.95
2021-09-20 03:00 | 44459.125 | 0 | 6.962 | 39.95
2021-09-20 03:30 | 44459.1458 | 0 | 7.1346 | 39.95
2021-09-20 04:00 | 44459.1667 | 0 | 7.3748 | 39.95
2021-09-20 04:30 | 44459.1875 | 0 | 7.7147 | 39.95
2021-09-20 05:00 | 44459.2083 | 0 | 8.2395 | 39.95
2021-09-20 05:30 | 44459.2292 | 0 | 8.7913 | 39.95
2021-09-20 06:00 | 44459.25 | 0 | 9.4507 | 39.95
2021-09-20 06:30 | 44459.2708 | 0 | 10.2163 | 39.95
2021-09-20 07:00 | 44459.2917 | 0 | 9.8378 | 39.95
2021-09-20 07:30 | 44459.3125 | 0 | 9.8306 | 39.95
2021-09-20 08:00 | 44459.3333 | 0 | 9.9526 | 39.95
2021-09-20 08:30 | 44459.3542 | 0 | 8.9779 | 39.95
2021-09-20 09:00 | 44459.375 | 0 | 8.595 | 39.95
2021-09-20 09:30 | 44459.3958 | 0 | 8.5763 | 39.95
2021-09-20 10:00 | 44459.4167 | 0 | 8.0361 | 39.95
2021-09-20 10:30 | 44459.4375 | 0 | 8.3663 | 39.95
2021-09-20 11:00 | 44459.4583 | 0 | 8.3325 | 39.95
2021-09-20 11:30 | 44459.4792 | 0 | 8.3102 | 39.95
2021-09-20 12:00 | 44459.5 | 0 | 8.2253 | 39.95
2021-09-20 12:30 | 44459.5208 | 0 | 8.3729 | 39.95
2021-09-20 13:00 | 44459.5417 | 0 | 8.5323 | 39.95
2021-09-20 13:30 | 44459.5625 | 0 | 9.0005 | 39.95
2021-09-20 14:00 | 44459.5833 | 0 | 9.5117 | 39.95
2021-09-20 14:30 | 44459.6042 | 0 | 9.9017 | 39.95
2021-09-20 15:00 | 44459.625 | 0 | 10.9528 | 39.95
2021-09-20 15:30 | 44459.6458 | 0 | 11.4029 | 39.95
2021-09-20 16:00 | 44459.6667 | 0 | 11.5978 | 39.95
2021-09-20 16:30 | 44459.6875 | 0 | 12.3788 | 39.95
2021-09-20 17:00 | 44459.7083 | 0 | 12.6747 | 39.95
2021-09-20 17:30 | 44459.7292 | 0 | 13.2417 | 39.95
2021-09-20 18:00 | 44459.75 | 0 | 13.698 | 39.95
2021-09-20 18:30 | 44459.7708 | 0 | 13.6714 | 39.95
2021-09-20 19:00 | 44459.7917 | 0 | 13.3795 | 39.95
2021-09-20 19:30 | 44459.8125 | 0 | 12.9493 | 39.95
2021-09-20 20:00 | 44459.8333 | 0 | 12.7252 | 39.95
2021-09-20 20:30 | 44459.8542 | 0 | 12.0032 | 39.95
2021-09-20 21:00 | 44459.875 | 0 | 11.667 | 39.95
2021-09-20 21:30 | 44459.8958 | 0 | 11.4293 | 39.95
2021-09-20 22:00 | 44459.9167 | 0 | 10.824 | 39.95
2021-09-20 22:30 | 44459.9375 | 0 | 10.086 | 39.95
2021-09-20 23:00 | 44459.9583 | 0 | 9.4006 | 39.95
2021-09-20 23:30 | 44459.9792 | 0 | 9.0008 | 39.95
2021-09-21 | 44460 | 0 | 8.4224 | 39.95
2021-09-21 00:30 | 44460.0208 | 0 | 8.2283 | 39.95
2021-09-21 01:00 | 44460.0417 | 0 | 7.8963 | 39.95
2021-09-21 01:30 | 44460.0625 | 0 | 7.6714 | 39.95
2021-09-21 02:00 | 44460.0833 | 0 | 7.5637 | 39.95
2021-09-21 02:30 | 44460.1042 | 0 | 7.4587 | 39.95
2021-09-21 03:00 | 44460.125 | 0 | 7.495 | 39.95
2021-09-21 03:30 | 44460.1458 | 0 | 7.5609 | 39.95
2021-09-21 04:00 | 44460.1667 | 0 | 7.7416 | 39.95
2021-09-21 04:30 | 44460.1875 | 0 | 8.1358 | 39.95
2021-09-21 05:00 | 44460.2083 | 0 | 8.7435 | 39.95
2021-09-21 05:30 | 44460.2292 | 0 | 9.3054 | 39.95
2021-09-21 06:00 | 44460.25 | 0 | 9.9143 | 39.95
2021-09-21 06:30 | 44460.2708 | 0 | 10.423 | 39.95
2021-09-21 07:00 | 44460.2917 | 0 | 10.3301 | 39.95
2021-09-21 07:30 | 44460.3125 | 0 | 10.167 | 39.95
2021-09-21 08:00 | 44460.3333 | 0 | 9.7858 | 39.95
2021-09-21 08:30 | 44460.3542 | 0 | 9.622 | 39.95
2021-09-21 09:00 | 44460.375 | 0 | 8.9862 | 39.95
2021-09-21 09:30 | 44460.3958 | 0 | 8.4665 | 39.95
2021-09-21 10:00 | 44460.4167 | 0 | 8.12 | 39.95
2021-09-21 10:30 | 44460.4375 | 0 | 8.1701 | 39.95
2021-09-21 11:00 | 44460.4583 | 0 | 7.5951 | 39.95
2021-09-21 11:30 | 44460.4792 | 0 | 7.5229 | 39.95
2021-09-21 12:00 | 44460.5 | 0 | 7.2381 | 39.95
2021-09-21 12:30 | 44460.5208 | 0 | 7.198 | 39.95
2021-09-21 13:00 | 44460.5417 | 0 | 7.5303 | 39.95
2021-09-21 13:30 | 44460.5625 | 0 | 8.1795 | 39.95
2021-09-21 14:00 | 44460.5833 | 0 | 8.6088 | 39.95
2021-09-21 14:30 | 44460.6042 | 0 | 9.5435 | 39.95
2021-09-21 15:00 | 44460.625 | 0 | 9.4835 | 39.95
2021-09-21 15:30 | 44460.6458 | 0 | 9.5542 | 39.95
2021-09-21 16:00 | 44460.6667 | 0 | 10.4792 | 39.95
2021-09-21 16:30 | 44460.6875 | 0 | 11.5735 | 39.95
2021-09-21 17:00 | 44460.7083 | 0 | 12.2841 | 39.95
2021-09-21 17:30 | 44460.7292 | 0 | 12.8422 | 39.95
2021-09-21 18:00 | 44460.75 | 0 | 13.464 | 39.95
2021-09-21 18:30 | 44460.7708 | 0 | 13.8773 | 39.95
2021-09-21 19:00 | 44460.7917 | 0 | 13.5553 | 39.95
2021-09-21 19:30 | 44460.8125 | 0 | 13.2606 | 39.95
2021-09-21 20:00 | 44460.8333 | 0 | 12.9553 | 39.95
2021-09-21 20:30 | 44460.8542 | 0 | 12.4627 | 39.95
2021-09-21 21:00 | 44460.875 | 0 | 12.103 | 39.95
2021-09-21 21:30 | 44460.8958 | 0 | 11.6677 | 39.95
2021-09-21 22:00 | 44460.9167 | 0 | 10.9871 | 39.95
2021-09-21 22:30 | 44460.9375 | 0 | 10.0809 | 39.95
2021-09-21 23:00 | 44460.9583 | 0 | 9.431 | 39.95
2021-09-21 23:30 | 44460.9792 | 0 | 9.016 | 39.95
2021-09-22 | 44461 | 0 | 8.5836 | 39.95
2021-09-22 00:30 | 44461.0208 | 0 | 8.1462 | 39.95
2021-09-22 01:00 | 44461.0417 | 0 | 8.055 | 39.95
2021-09-22 01:30 | 44461.0625 | 0 | 7.9689 | 39.95
2021-09-22 02:00 | 44461.0833 | 0 | 7.8818 | 39.95
2021-09-22 02:30 | 44461.1042 | 0 | 7.7596 | 39.95
2021-09-22 03:00 | 44461.125 | 0 | 7.7645 | 39.95
2021-09-22 03:30 | 44461.1458 | 0 | 7.905 | 39.95
2021-09-22 04:00 | 44461.1667 | 0 | 8.1694 | 39.95
2021-09-22 04:30 | 44461.1875 | 0 | 8.519 | 39.95
2021-09-22 05:00 | 44461.2083 | 0 | 9.168 | 39.95
2021-09-22 05:30 | 44461.2292 | 0 | 9.8644 | 39.95
2021-09-22 06:00 | 44461.25 | 0 | 10.5752 | 39.95
2021-09-22 06:30 | 44461.2708 | 0 | 10.9651 | 39.95
2021-09-22 07:00 | 44461.2917 | 0 | 10.8875 | 39.95
2021-09-22 07:30 | 44461.3125 | 0 | 10.3601 | 39.95
2021-09-22 08:00 | 44461.3333 | 0 | 9.7306 | 39.95
2021-09-22 08:30 | 44461.3542 | 0 | 9.0632 | 39.95
2021-09-22 09:00 | 44461.375 | 0 | 8.2713 | 39.95
2021-09-22 09:30 | 44461.3958 | 0 | 8.0129 | 39.95
2021-09-22 10:00 | 44461.4167 | 0 | 7.4249 | 39.95
2021-09-22 10:30 | 44461.4375 | 0 | 7.2704 | 39.95
2021-09-22 11:00 | 44461.4583 | 0 | 7.0169 | 39.95
2021-09-22 11:30 | 44461.4792 | 0 | 7.1308 | 39.95
2021-09-22 12:00 | 44461.5 | 0 | 7.1301 | 39.95
2021-09-22 12:30 | 44461.5208 | 0 | 7.4082 | 39.95
2021-09-22 13:00 | 44461.5417 | 0 | 7.5138 | 39.95
2021-09-22 13:30 | 44461.5625 | 0 | 7.9494 | 39.95
2021-09-22 14:00 | 44461.5833 | 0 | 8.7168 | 39.95
2021-09-22 14:30 | 44461.6042 | 0 | 9.352 | 39.95
2021-09-22 15:00 | 44461.625 | 0 | 9.5934 | 39.95
2021-09-22 15:30 | 44461.6458 | 0 | 9.9896 | 39.95
2021-09-22 16:00 | 44461.6667 | 0 | 10.7782 | 39.95
2021-09-22 16:30 | 44461.6875 | 0 | 11.5977 | 39.95
2021-09-22 17:00 | 44461.7083 | 0 | 12.0329 | 39.95
2021-09-22 17:30 | 44461.7292 | 0 | 12.5773 | 39.95
2021-09-22 18:00 | 44461.75 | 0 | 13.1427 | 39.95
2021-09-22 18:30 | 44461.7708 | 0 | 13.5062 | 39.95
2021-09-22 19:00 | 44461.7917 | 0 | 13.1579 | 39.95
2021-09-22 19:30 | 44461.8125 | 0 | 13.0555 | 39.95
2021-09-22 20:00 | 44461.8333 | 0 | 12.8166 | 39.95
2021-09-22 20:30 | 44461.8542 | 0 | 12.3958 | 39.95
2021-09-22 21:00 | 44461.875 | 0 | 11.8712 | 39.95
2021-09-22 21:30 | 44461.8958 | 0 | 11.4192 | 39.95
2021-09-22 22:00 | 44461.9167 | 0 | 10.7104 | 39.95
2021-09-22 22:30 | 44461.9375 | 0 | 9.8796 | 39.95
2021-09-22 23:00 | 44461.9583 | 0 | 9.3758 | 39.95
2021-09-22 23:30 | 44461.9792 | 0 | 9.0677 | 39.95
2021-09-23 | 44462 | 0 | 8.5136 | 39.95
2021-09-23 00:30 | 44462.0208 | 0 | 8.0124 | 39.95
2021-09-23 01:00 | 44462.0417 | 0 | 7.9784 | 39.95
2021-09-23 01:30 | 44462.0625 | 0 | 7.8366 | 39.95
2021-09-23 02:00 | 44462.0833 | 0 | 7.8856 | 39.95
2021-09-23 02:30 | 44462.1042 | 0 | 7.7182 | 39.95
2021-09-23 03:00 | 44462.125 | 0 | 7.5744 | 39.95
2021-09-23 03:30 | 44462.1458 | 0 | 7.7545 | 39.95
2021-09-23 04:00 | 44462.1667 | 0 | 8.106 | 39.95
2021-09-23 04:30 | 44462.1875 | 0 | 8.5556 | 39.95
2021-09-23 05:00 | 44462.2083 | 0 | 9.1309 | 39.95
2021-09-23 05:30 | 44462.2292 | 0 | 9.8787 | 39.95
2021-09-23 06:00 | 44462.25 | 0 | 10.4994 | 39.95
2021-09-23 06:30 | 44462.2708 | 0 | 10.7179 | 39.95
2021-09-23 07:00 | 44462.2917 | 0 | 10.7253 | 39.95
2021-09-23 07:30 | 44462.3125 | 0 | 10.2057 | 39.95
2021-09-23 08:00 | 44462.3333 | 0 | 9.6369 | 39.95
2021-09-23 08:30 | 44462.3542 | 0 | 9.0831 | 39.95
2021-09-23 09:00 | 44462.375 | 0 | 8.4902 | 39.95
2021-09-23 09:30 | 44462.3958 | 0 | 8.0514 | 39.95
2021-09-23 10:00 | 44462.4167 | 0 | 7.658 | 39.95
2021-09-23 10:30 | 44462.4375 | 0 | 7.6424 | 39.95
2021-09-23 11:00 | 44462.4583 | 0 | 7.3305 | 39.95
2021-09-23 11:30 | 44462.4792 | 0 | 7.5517 | 39.95
2021-09-23 12:00 | 44462.5 | 0 | 7.6583 | 39.95
2021-09-23 12:30 | 44462.5208 | 0 | 7.6874 | 39.95
2021-09-23 13:00 | 44462.5417 | 0 | 7.9052 | 39.95
2021-09-23 13:30 | 44462.5625 | 0 | 8.2791 | 39.95
2021-09-23 14:00 | 44462.5833 | 0 | 8.8091 | 39.95
2021-09-23 14:30 | 44462.6042 | 0 | 9.3273 | 39.95
2021-09-23 15:00 | 44462.625 | 0 | 10.0141 | 39.95
2021-09-23 15:30 | 44462.6458 | 0 | 10.4268 | 39.95
2021-09-23 16:00 | 44462.6667 | 0 | 11.19 | 39.95
2021-09-23 16:30 | 44462.6875 | 0 | 11.8595 | 39.95
2021-09-23 17:00 | 44462.7083 | 0 | 12.3663 | 39.95
2021-09-23 17:30 | 44462.7292 | 0 | 12.9562 | 39.95
2021-09-23 18:00 | 44462.75 | 0 | 13.2591 | 39.95
2021-09-23 18:30 | 44462.7708 | 0 | 13.6235 | 39.95
2021-09-23 19:00 | 44462.7917 | 0 | 13.3107 | 39.95
2021-09-23 19:30 | 44462.8125 | 0 | 12.8924 | 39.95
2021-09-23 20:00 | 44462.8333 | 0 | 12.5666 | 39.95
2021-09-23 20:30 | 44462.8542 | 0 | 12.1252 | 39.95
2021-09-23 21:00 | 44462.875 | 0 | 11.6226 | 39.95
2021-09-23 21:30 | 44462.8958 | 0 | 11.2619 | 39.95
2021-09-23 22:00 | 44462.9167 | 0 | 10.7051 | 39.95
2021-09-23 22:30 | 44462.9375 | 0 | 9.856 | 39.95
2021-09-23 23:00 | 44462.9583 | 0 | 9.2732 | 39.95
2021-09-23 23:30 | 44462.9792 | 0 | 8.8361 | 39.95
2021-09-24 | 44463 | 0 | 8.4633 | 39.95
2021-09-24 00:30 | 44463.0208 | 0 | 8.0868 | 39.95
2021-09-24 01:00 | 44463.0417 | 0 | 7.889 | 39.95
2021-09-24 01:30 | 44463.0625 | 0 | 7.8854 | 39.95
2021-09-24 02:00 | 44463.0833 | 0 | 7.785 | 39.95
2021-09-24 02:30 | 44463.1042 | 0 | 7.7124 | 39.95
2021-09-24 03:00 | 44463.125 | 0 | 7.6637 | 39.95
2021-09-24 03:30 | 44463.1458 | 0 | 7.8253 | 39.95
2021-09-24 04:00 | 44463.1667 | 0 | 8.0761 | 39.95
2021-09-24 04:30 | 44463.1875 | 0 | 8.4904 | 39.95
2021-09-24 05:00 | 44463.2083 | 0 | 8.9185 | 39.95
2021-09-24 05:30 | 44463.2292 | 0 | 9.2797 | 39.95
2021-09-24 06:00 | 44463.25 | 0 | 10.0202 | 39.95
2021-09-24 06:30 | 44463.2708 | 0 | 10.202 | 39.95
2021-09-24 07:00 | 44463.2917 | 0 | 10.4253 | 39.95
2021-09-24 07:30 | 44463.3125 | 0 | 9.993 | 39.95
2021-09-24 08:00 | 44463.3333 | 0 | 9.6745 | 39.95
2021-09-24 08:30 | 44463.3542 | 0 | 9.3394 | 39.95
2021-09-24 09:00 | 44463.375 | 0 | 8.8443 | 39.95
2021-09-24 09:30 | 44463.3958 | 0 | 8.6438 | 39.95
2021-09-24 10:00 | 44463.4167 | 0 | 8.2335 | 39.95
2021-09-24 10:30 | 44463.4375 | 0 | 8.2242 | 39.95
2021-09-24 11:00 | 44463.4583 | 0 | 7.9659 | 39.95
2021-09-24 11:30 | 44463.4792 | 0 | 8.2015 | 39.95
2021-09-24 12:00 | 44463.5 | 0 | 8.1448 | 39.95
2021-09-24 12:30 | 44463.5208 | 0 | 8.0319 | 39.95
2021-09-24 13:00 | 44463.5417 | 0 | 8.1641 | 39.95
2021-09-24 13:30 | 44463.5625 | 0 | 8.4071 | 39.95
2021-09-24 14:00 | 44463.5833 | 0 | 8.9017 | 39.95
2021-09-24 14:30 | 44463.6042 | 0 | 9.4439 | 39.95
2021-09-24 15:00 | 44463.625 | 0 | 9.9675 | 39.95
2021-09-24 15:30 | 44463.6458 | 0 | 10.6337 | 39.95
2021-09-24 16:00 | 44463.6667 | 0 | 11.3436 | 39.95
2021-09-24 16:30 | 44463.6875 | 0 | 11.9749 | 39.95
2021-09-24 17:00 | 44463.7083 | 0 | 12.2459 | 39.95
2021-09-24 17:30 | 44463.7292 | 0 | 12.615 | 39.95
2021-09-24 18:00 | 44463.75 | 0 | 12.9211 | 39.95
2021-09-24 18:30 | 44463.7708 | 0 | 13.0301 | 39.95
2021-09-24 19:00 | 44463.7917 | 0 | 12.6668 | 39.95
2021-09-24 19:30 | 44463.8125 | 0 | 12.4697 | 39.95
2021-09-24 20:00 | 44463.8333 | 0 | 12.0157 | 39.95
2021-09-24 20:30 | 44463.8542 | 0 | 11.5427 | 39.95
2021-09-24 21:00 | 44463.875 | 0 | 11.1726 | 39.95
2021-09-24 21:30 | 44463.8958 | 0 | 10.8875 | 39.95
2021-09-24 22:00 | 44463.9167 | 0 | 10.5615 | 39.95
2021-09-24 22:30 | 44463.9375 | 0 | 9.901 | 39.95
2021-09-24 23:00 | 44463.9583 | 0 | 9.282 | 39.95
2021-09-24 23:30 | 44463.9792 | 0 | 8.7784 | 39.95
2021-09-25 | 44464 | 0 | 8.2627 | 39.95
2021-09-25 00:30 | 44464.0208 | 0 | 8.0064 | 39.95
2021-09-25 01:00 | 44464.0417 | 0 | 7.7802 | 39.95
2021-09-25 01:30 | 44464.0625 | 0 | 7.6955 | 39.95
2021-09-25 02:00 | 44464.0833 | 0 | 7.5356 | 39.95
2021-09-25 02:30 | 44464.1042 | 0 | 7.5207 | 39.95
2021-09-25 03:00 | 44464.125 | 0 | 7.45 | 39.95
2021-09-25 03:30 | 44464.1458 | 0 | 7.4776 | 39.95
2021-09-25 04:00 | 44464.1667 | 0 | 7.5829 | 39.95
2021-09-25 04:30 | 44464.1875 | 0 | 7.8345 | 39.95
2021-09-25 05:00 | 44464.2083 | 0 | 7.9116 | 39.95
2021-09-25 05:30 | 44464.2292 | 0 | 7.9243 | 39.95
2021-09-25 06:00 | 44464.25 | 0 | 7.9915 | 39.95
2021-09-25 06:30 | 44464.2708 | 0 | 7.8559 | 39.95
2021-09-25 07:00 | 44464.2917 | 0 | 7.5225 | 39.95
2021-09-25 07:30 | 44464.3125 | 0 | 7.2033 | 39.95
2021-09-25 08:00 | 44464.3333 | 0 | 7.2173 | 39.95
2021-09-25 08:30 | 44464.3542 | 0 | 7.2308 | 39.95
2021-09-25 09:00 | 44464.375 | 0 | 7.309 | 39.95
2021-09-25 09:30 | 44464.3958 | 0 | 7.1338 | 39.95
2021-09-25 10:00 | 44464.4167 | 0 | 6.2609 | 39.95
2021-09-25 10:30 | 44464.4375 | 0 | 6.3581 | 39.95
2021-09-25 11:00 | 44464.4583 | 0 | 6.3725 | 39.95
2021-09-25 11:30 | 44464.4792 | 0 | 6.2865 | 39.95
2021-09-25 12:00 | 44464.5 | 0 | 7.1919 | 39.95
2021-09-25 12:30 | 44464.5208 | 0 | 8.5541 | 39.95
2021-09-25 13:00 | 44464.5417 | 0 | 8.5556 | 39.95
2021-09-25 13:30 | 44464.5625 | 0 | 8.4723 | 39.95
2021-09-25 14:00 | 44464.5833 | 0 | 6.6847 | 39.95
2021-09-25 14:30 | 44464.6042 | 0 | 8.0006 | 39.95
2021-09-25 15:00 | 44464.625 | 0 | 8.022 | 39.95
2021-09-25 15:30 | 44464.6458 | 0 | 9.1621 | 39.95
2021-09-25 16:00 | 44464.6667 | 0 | 10.2519 | 39.95
2021-09-25 16:30 | 44464.6875 | 0 | 10.2947 | 39.95
2021-09-25 17:00 | 44464.7083 | 0 | 10.4497 | 39.95
2021-09-25 17:30 | 44464.7292 | 0 | 10.6458 | 39.95
2021-09-25 18:00 | 44464.75 | 0 | 10.9825 | 39.95
2021-09-25 18:30 | 44464.7708 | 0 | 10.9418 | 39.95
2021-09-25 19:00 | 44464.7917 | 0 | 10.5757 | 39.95
2021-09-25 19:30 | 44464.8125 | 0 | 10.5764 | 39.95
2021-09-25 20:00 | 44464.8333 | 0 | 10.4036 | 39.95
2021-09-25 20:30 | 44464.8542 | 0 | 10.1362 | 39.95
2021-09-25 21:00 | 44464.875 | 0 | 9.8311 | 39.95
2021-09-25 21:30 | 44464.8958 | 0 | 9.7743 | 39.95
2021-09-25 22:00 | 44464.9167 | 0 | 9.4605 | 39.95
2021-09-25 22:30 | 44464.9375 | 0 | 8.9564 | 39.95
2021-09-25 23:00 | 44464.9583 | 0 | 8.4759 | 39.95
2021-09-25 23:30 | 44464.9792 | 0 | 8.2417 | 39.95
2021-09-26 | 44465 | 0 | 7.7487 | 39.95
2021-09-26 00:30 | 44465.0208 | 0 | 7.5152 | 39.95
2021-09-26 01:00 | 44465.0417 | 0 | 7.2957 | 39.95
2021-09-26 01:30 | 44465.0625 | 0 | 7.1901 | 39.95
2021-09-26 02:00 | 44465.0833 | 0 | 7.169 | 39.95
2021-09-26 02:30 | 44465.1042 | 0 | 7.0668 | 39.95
2021-09-26 03:00 | 44465.125 | 0 | 6.9678 | 39.95
2021-09-26 03:30 | 44465.1458 | 0 | 7.0368 | 39.95
2021-09-26 04:00 | 44465.1667 | 0 | 6.9789 | 39.95
2021-09-26 04:30 | 44465.1875 | 0 | 6.9511 | 39.95
2021-09-26 05:00 | 44465.2083 | 0 | 7.0328 | 39.95
2021-09-26 05:30 | 44465.2292 | 0 | 7.1602 | 39.95
2021-09-26 06:00 | 44465.25 | 0 | 7.6824 | 39.95
2021-09-26 06:30 | 44465.2708 | 0 | 7.6842 | 39.95
2021-09-26 07:00 | 44465.2917 | 0 | 7.1518 | 39.95
2021-09-26 07:30 | 44465.3125 | 0 | 6.8838 | 39.95
2021-09-26 08:00 | 44465.3333 | 0 | 6.5887 | 39.95
2021-09-26 08:30 | 44465.3542 | 0 | 7.105 | 39.95
2021-09-26 09:00 | 44465.375 | 0 | 8.3968 | 39.95
2021-09-26 09:30 | 44465.3958 | 0 | 8.451 | 39.95
2021-09-26 10:00 | 44465.4167 | 0 | 7.0049 | 39.95
2021-09-26 10:30 | 44465.4375 | 0 | 6.74 | 39.95
2021-09-26 11:00 | 44465.4583 | 0 | 6.4821 | 39.95
2021-09-26 11:30 | 44465.4792 | 0 | 7.2579 | 39.95
2021-09-26 12:00 | 44465.5 | 0 | 7.4761 | 39.95
2021-09-26 12:30 | 44465.5208 | 0 | 7.8276 | 39.95
2021-09-26 13:00 | 44465.5417 | 0 | 7.7382 | 39.95
2021-09-26 13:30 | 44465.5625 | 0 | 7.815 | 39.95
2021-09-26 14:00 | 44465.5833 | 0 | 8.4738 | 39.95
2021-09-26 14:30 | 44465.6042 | 0 | 8.7138 | 39.95
2021-09-26 15:00 | 44465.625 | 0 | 8.937 | 39.95
2021-09-26 15:30 | 44465.6458 | 0 | 9.3787 | 39.95
2021-09-26 16:00 | 44465.6667 | 0 | 9.9015 | 39.95
2021-09-26 16:30 | 44465.6875 | 0 | 10.208 | 39.95
2021-09-26 17:00 | 44465.7083 | 0 | 10.7418 | 39.95
2021-09-26 17:30 | 44465.7292 | 0 | 11.0282 | 39.95
2021-09-26 18:00 | 44465.75 | 0 | 11.3226 | 39.95
2021-09-26 18:30 | 44465.7708 | 0 | 11.3643 | 39.95
2021-09-26 19:00 | 44465.7917 | 0 | 10.9854 | 39.95
2021-09-26 19:30 | 44465.8125 | 0 | 10.6772 | 39.95
2021-09-26 20:00 | 44465.8333 | 0 | 10.443 | 39.95
2021-09-26 20:30 | 44465.8542 | 0 | 9.9626 | 39.95
2021-09-26 21:00 | 44465.875 | 0 | 9.637 | 39.95
2021-09-26 21:30 | 44465.8958 | 0 | 9.376 | 39.95
2021-09-26 22:00 | 44465.9167 | 0 | 8.8769 | 39.95
2021-09-26 22:30 | 44465.9375 | 0 | 8.45 | 39.95
2021-09-26 23:00 | 44465.9583 | 0 | 8.0052 | 39.95
2021-09-26 23:30 | 44465.9792 | 0 | 7.6627 | 39.95
2021-09-27 | 44466 | 0 | 7.4277 | 39.95
2021-09-27 00:30 | 44466.0208 | 0 | 7.1829 | 39.95
2021-09-27 01:00 | 44466.0417 | 0 | 7.0965 | 39.95
2021-09-27 01:30 | 44466.0625 | 0 | 6.966 | 39.95
2021-09-27 02:00 | 44466.0833 | 0 | 7.0328 | 39.95
2021-09-27 02:30 | 44466.1042 | 0 | 7.0328 | 39.95
2021-09-27 03:00 | 44466.125 | 0 | 7.0424 | 39.95
2021-09-27 03:30 | 44466.1458 | 0 | 7.2294 | 39.95
2021-09-27 04:00 | 44466.1667 | 0 | 7.5123 | 39.95
2021-09-27 04:30 | 44466.1875 | 0 | 7.911 | 39.95
2021-09-27 05:00 | 44466.2083 | 0 | 8.3017 | 39.95
2021-09-27 05:30 | 44466.2292 | 0 | 8.911 | 39.95
2021-09-27 06:00 | 44466.25 | 0 | 9.7677 | 39.95
2021-09-27 06:30 | 44466.2708 | 0 | 10.2648 | 39.95
2021-09-27 07:00 | 44466.2917 | 0 | 11.6002 | 39.95
2021-09-27 07:30 | 44466.3125 | 0 | 11.5754 | 39.95
2021-09-27 08:00 | 44466.3333 | 0 | 11.2554 | 39.95
2021-09-27 08:30 | 44466.3542 | 0 | 10.9744 | 39.95
2021-09-27 09:00 | 44466.375 | 0 | 10.9931 | 39.95
2021-09-27 09:30 | 44466.3958 | 0 | 11.5425 | 39.95
2021-09-27 10:00 | 44466.4167 | 0 | 11.6837 | 39.95
2021-09-27 10:30 | 44466.4375 | 0 | 10.8561 | 39.95
2021-09-27 11:00 | 44466.4583 | 0 | 11.1337 | 39.95
2021-09-27 11:30 | 44466.4792 | 0 | 11.1303 | 39.95
2021-09-27 12:00 | 44466.5 | 0 | 11.1569 | 39.95
2021-09-27 12:30 | 44466.5208 | 0 | 11.2236 | 39.95
2021-09-27 13:00 | 44466.5417 | 0 | 11.2168 | 39.95
2021-09-27 13:30 | 44466.5625 | 0 | 11.5069 | 39.95
2021-09-27 14:00 | 44466.5833 | 0 | 11.5027 | 39.95
2021-09-27 14:30 | 44466.6042 | 0 | 11.5349 | 39.95
2021-09-27 15:00 | 44466.625 | 0 | 11.0711 | 39.95
2021-09-27 15:30 | 44466.6458 | 0 | 11.3943 | 39.95
2021-09-27 16:00 | 44466.6667 | 0 | 11.3589 | 39.95
2021-09-27 16:30 | 44466.6875 | 0 | 12.0036 | 39.95
2021-09-27 17:00 | 44466.7083 | 0 | 12.4375 | 39.95
2021-09-27 17:30 | 44466.7292 | 0 | 12.845 | 39.95
2021-09-27 18:00 | 44466.75 | 0 | 13.3587 | 39.95
2021-09-27 18:30 | 44466.7708 | 0 | 13.4927 | 39.95
2021-09-27 19:00 | 44466.7917 | 0 | 13.0847 | 39.95
2021-09-27 19:30 | 44466.8125 | 0 | 12.6216 | 39.95
2021-09-27 20:00 | 44466.8333 | 0 | 12.6481 | 39.95
2021-09-27 20:30 | 44466.8542 | 0 | 11.8899 | 39.95
2021-09-27 21:00 | 44466.875 | 0 | 11.3819 | 39.95
2021-09-27 21:30 | 44466.8958 | 0 | 11.0104 | 39.95
2021-09-27 22:00 | 44466.9167 | 0 | 10.4205 | 39.95
2021-09-27 22:30 | 44466.9375 | 0 | 9.5774 | 39.95
2021-09-27 23:00 | 44466.9583 | 0 | 9.0479 | 39.95
2021-09-27 23:30 | 44466.9792 | 0 | 8.491 | 39.95
2021-09-28 | 44467 | 0 | 8.0509 | 39.95
2021-09-28 00:30 | 44467.0208 | 0 | 7.8074 | 39.95
2021-09-28 01:00 | 44467.0417 | 0 | 7.6736 | 39.95
2021-09-28 01:30 | 44467.0625 | 0 | 7.5428 | 39.95
2021-09-28 02:00 | 44467.0833 | 0 | 7.5189 | 39.95
2021-09-28 02:30 | 44467.1042 | 0 | 7.4613 | 39.95
2021-09-28 03:00 | 44467.125 | 0 | 7.3567 | 39.95
2021-09-28 03:30 | 44467.1458 | 0 | 7.4901 | 39.95
2021-09-28 04:00 | 44467.1667 | 0 | 7.745 | 39.95
2021-09-28 04:30 | 44467.1875 | 0 | 8.2619 | 39.95
2021-09-28 05:00 | 44467.2083 | 0 | 8.7943 | 39.95
2021-09-28 05:30 | 44467.2292 | 0 | 9.3719 | 39.95
2021-09-28 06:00 | 44467.25 | 0 | 9.8304 | 39.95
2021-09-28 06:30 | 44467.2708 | 0 | 10.6396 | 39.95
2021-09-28 07:00 | 44467.2917 | 0 | 11.5659 | 39.95
2021-09-28 07:30 | 44467.3125 | 0 | 11.3172 | 39.95
2021-09-28 08:00 | 44467.3333 | 0 | 10.9139 | 39.95
2021-09-28 08:30 | 44467.3542 | 0 | 11.5156 | 39.95
2021-09-28 09:00 | 44467.375 | 0 | 11.7473 | 39.95
2021-09-28 09:30 | 44467.3958 | 0 | 10.8527 | 39.95
2021-09-28 10:00 | 44467.4167 | 0 | 10.1007 | 39.95
2021-09-28 10:30 | 44467.4375 | 0 | 10.9921 | 39.95
2021-09-28 11:00 | 44467.4583 | 0 | 10.4873 | 39.95
2021-09-28 11:30 | 44467.4792 | 0 | 8.3935 | 39.95
2021-09-28 12:00 | 44467.5 | 0 | 9.6554 | 39.95
2021-09-28 12:30 | 44467.5208 | 0 | 9.6129 | 39.95
2021-09-28 13:00 | 44467.5417 | 0 | 10.3683 | 39.95
2021-09-28 13:30 | 44467.5625 | 0 | 10.6801 | 39.95
2021-09-28 14:00 | 44467.5833 | 0 | 11.376 | 39.95
2021-09-28 14:30 | 44467.6042 | 0 | 10.9733 | 39.95
2021-09-28 15:00 | 44467.625 | 0 | 10.4444 | 39.95
2021-09-28 15:30 | 44467.6458 | 0 | 10.5033 | 39.95
2021-09-28 16:00 | 44467.6667 | 0 | 10.8646 | 39.95
2021-09-28 16:30 | 44467.6875 | 0 | 11.4911 | 39.95
2021-09-28 17:00 | 44467.7083 | 0 | 11.8706 | 39.95
2021-09-28 17:30 | 44467.7292 | 0 | 12.6684 | 39.95
2021-09-28 18:00 | 44467.75 | 0 | 13.1797 | 39.95
2021-09-28 18:30 | 44467.7708 | 0 | 13.4379 | 39.95
2021-09-28 19:00 | 44467.7917 | 0 | 12.9242 | 39.95
2021-09-28 19:30 | 44467.8125 | 0 | 12.7224 | 39.95
2021-09-28 20:00 | 44467.8333 | 0 | 12.4159 | 39.95
2021-09-28 20:30 | 44467.8542 | 0 | 12.0496 | 39.95
2021-09-28 21:00 | 44467.875 | 0 | 11.5011 | 39.95
2021-09-28 21:30 | 44467.8958 | 0 | 11.1424 | 39.95
2021-09-28 22:00 | 44467.9167 | 0 | 10.4684 | 39.95
2021-09-28 22:30 | 44467.9375 | 0 | 9.6469 | 39.95
2021-09-28 23:00 | 44467.9583 | 0 | 9.1469 | 39.95
2021-09-28 23:30 | 44467.9792 | 0 | 8.6564 | 39.95
2021-09-29 | 44468 | 0 | 8.2261 | 39.95
2021-09-29 00:30 | 44468.0208 | 0 | 7.9522 | 39.95
2021-09-29 01:00 | 44468.0417 | 0 | 7.6609 | 39.95
2021-09-29 01:30 | 44468.0625 | 0 | 7.5541 | 39.95
2021-09-29 02:00 | 44468.0833 | 0 | 7.4963 | 39.95
2021-09-29 02:30 | 44468.1042 | 0 | 7.6265 | 39.95
2021-09-29 03:00 | 44468.125 | 0 | 7.4871 | 39.95
2021-09-29 03:30 | 44468.1458 | 0 | 7.5943 | 39.95
2021-09-29 04:00 | 44468.1667 | 0 | 7.8295 | 39.95
2021-09-29 04:30 | 44468.1875 | 0 | 8.2192 | 39.95
2021-09-29 05:00 | 44468.2083 | 0 | 8.8386 | 39.95
2021-09-29 05:30 | 44468.2292 | 0 | 9.4086 | 39.95
2021-09-29 06:00 | 44468.25 | 0 | 9.9067 | 39.95
2021-09-29 06:30 | 44468.2708 | 0 | 11.1103 | 39.95
2021-09-29 07:00 | 44468.2917 | 0 | 11.2329 | 39.95
2021-09-29 07:30 | 44468.3125 | 0 | 10.9331 | 39.95
2021-09-29 08:00 | 44468.3333 | 0 | 10.7603 | 39.95
2021-09-29 08:30 | 44468.3542 | 0 | 10.0854 | 39.95
2021-09-29 09:00 | 44468.375 | 0 | 10.6876 | 39.95
2021-09-29 09:30 | 44468.3958 | 0 | 11.2868 | 39.95
2021-09-29 10:00 | 44468.4167 | 0 | 11.1955 | 39.95
2021-09-29 10:30 | 44468.4375 | 0 | 10.6359 | 39.95
2021-09-29 11:00 | 44468.4583 | 0 | 9.009 | 39.95
2021-09-29 11:30 | 44468.4792 | 0 | 7.5605 | 39.95
2021-09-29 12:00 | 44468.5 | 0 | 7.8393 | 39.95
2021-09-29 12:30 | 44468.5208 | 0 | 9.0753 | 39.95
2021-09-29 13:00 | 44468.5417 | 0 | 10.0284 | 39.95
2021-09-29 13:30 | 44468.5625 | 0 | 9.6685 | 39.95
2021-09-29 14:00 | 44468.5833 | 0 | 10.1189 | 39.95
2021-09-29 14:30 | 44468.6042 | 0 | 9.6927 | 39.95
2021-09-29 15:00 | 44468.625 | 0 | 10.836 | 39.95
2021-09-29 15:30 | 44468.6458 | 0 | 11.6971 | 39.95
2021-09-29 16:00 | 44468.6667 | 0 | 11.6844 | 39.95
2021-09-29 16:30 | 44468.6875 | 0 | 11.9556 | 39.95
2021-09-29 17:00 | 44468.7083 | 0 | 11.8641 | 39.95
2021-09-29 17:30 | 44468.7292 | 0 | 12.3583 | 39.95
2021-09-29 18:00 | 44468.75 | 0 | 12.5238 | 39.95
2021-09-29 18:30 | 44468.7708 | 0 | 12.53 | 39.95
2021-09-29 19:00 | 44468.7917 | 0 | 12.4204 | 39.95
2021-09-29 19:30 | 44468.8125 | 0 | 11.8902 | 39.95
2021-09-29 20:00 | 44468.8333 | 0 | 11.5444 | 39.95
2021-09-29 20:30 | 44468.8542 | 0 | 11.1518 | 39.95
2021-09-29 21:00 | 44468.875 | 0 | 10.5402 | 39.95
2021-09-29 21:30 | 44468.8958 | 0 | 10.2764 | 39.95
2021-09-29 22:00 | 44468.9167 | 0 | 10.102 | 39.95
2021-09-29 22:30 | 44468.9375 | 0 | 9.3653 | 39.95
2021-09-29 23:00 | 44468.9583 | 0 | 8.7522 | 39.95
2021-09-29 23:30 | 44468.9792 | 0 | 8.426 | 39.95
2021-09-30 | 44469 | 0 | 7.8621 | 39.95
2021-09-30 00:30 | 44469.0208 | 0 | 7.7329 | 39.95
2021-09-30 01:00 | 44469.0417 | 0 | 7.5533 | 39.95
2021-09-30 01:30 | 44469.0625 | 0 | 7.4183 | 39.95
2021-09-30 02:00 | 44469.0833 | 0 | 7.4406 | 39.95
2021-09-30 02:30 | 44469.1042 | 0 | 7.3068 | 39.95
2021-09-30 03:00 | 44469.125 | 0 | 7.21 | 39.95
2021-09-30 03:30 | 44469.1458 | 0 | 7.3173 | 39.95
2021-09-30 04:00 | 44469.1667 | 0 | 7.4283 | 39.95
2021-09-30 04:30 | 44469.1875 | 0 | 7.9451 | 39.95
2021-09-30 05:00 | 44469.2083 | 0 | 8.3997 | 39.95
2021-09-30 05:30 | 44469.2292 | 0 | 8.9363 | 39.95
2021-09-30 06:00 | 44469.25 | 0 | 9.2838 | 39.95
2021-09-30 06:30 | 44469.2708 | 0 | 9.8639 | 39.95
2021-09-30 07:00 | 44469.2917 | 0 | 10.2479 | 39.95
2021-09-30 07:30 | 44469.3125 | 0 | 10.6084 | 39.95
2021-09-30 08:00 | 44469.3333 | 0 | 10.566 | 39.95
2021-09-30 08:30 | 44469.3542 | 0 | 11.2383 | 39.95
2021-09-30 09:00 | 44469.375 | 0 | 10.8348 | 39.95
2021-09-30 09:30 | 44469.3958 | 0 | 8.9475 | 39.95
2021-09-30 10:00 | 44469.4167 | 0 | 9.227 | 39.95
2021-09-30 10:30 | 44469.4375 | 0 | 9.0117 | 39.95
2021-09-30 11:00 | 44469.4583 | 0 | 8.8286 | 39.95
2021-09-30 11:30 | 44469.4792 | 0 | 9.9959 | 39.95
2021-09-30 12:00 | 44469.5 | 0 | 8.4857 | 39.95
2021-09-30 12:30 | 44469.5208 | 0 | 10.2756 | 39.95
2021-09-30 13:00 | 44469.5417 | 0 | 10.0079 | 39.95
2021-09-30 13:30 | 44469.5625 | 0 | 9.3176 | 39.95
2021-09-30 14:00 | 44469.5833 | 0 | 11.5849 | 39.95
2021-09-30 14:30 | 44469.6042 | 0 | 11.6181 | 39.95
2021-09-30 15:00 | 44469.625 | 0 | 10.9225 | 39.95
2021-09-30 15:30 | 44469.6458 | 0 | 10.6791 | 39.95
2021-09-30 16:00 | 44469.6667 | 0 | 11.9817 | 39.95
2021-09-30 16:30 | 44469.6875 | 0 | 12.5946 | 39.95
2021-09-30 17:00 | 44469.7083 | 0 | 12.4385 | 39.95
2021-09-30 17:30 | 44469.7292 | 0 | 12.4498 | 39.95
2021-09-30 18:00 | 44469.75 | 0 | 12.3839 | 39.95
2021-09-30 18:30 | 44469.7708 | 0 | 12.6179 | 39.95
2021-09-30 19:00 | 44469.7917 | 0 | 12.4361 | 39.95
2021-09-30 19:30 | 44469.8125 | 0 | 12.155 | 39.95
2021-09-30 20:00 | 44469.8333 | 0 | 11.7826 | 39.95
2021-09-30 20:30 | 44469.8542 | 0 | 11.1718 | 39.95
2021-09-30 21:00 | 44469.875 | 0 | 10.7372 | 39.95
2021-09-30 21:30 | 44469.8958 | 0 | 10.6008 | 39.95
2021-09-30 22:00 | 44469.9167 | 0 | 10.2457 | 39.95
2021-09-30 22:30 | 44469.9375 | 0 | 9.7427 | 39.95
2021-09-30 23:00 | 44469.9583 | 0 | 9.0982 | 39.95
2021-09-30 23:30 | 44469.9792 | 0 | 8.72 | 39.95
2021-10-01 | 44470 | 0 | 8.1393 | 39.95
2021-10-01 00:30 | 44470.0208 | 0 | 7.8186 | 39.95
2021-10-01 01:00 | 44470.0417 | 0 | 7.7135 | 39.95
2021-10-01 01:30 | 44470.0625 | 0 | 7.409 | 39.95
2021-10-01 02:00 | 44470.0833 | 0 | 7.4108 | 39.95
2021-10-01 02:30 | 44470.1042 | 0 | 7.303 | 39.95
2021-10-01 03:00 | 44470.125 | 0 | 7.2028 | 39.95
2021-10-01 03:30 | 44470.1458 | 0 | 7.2762 | 39.95
2021-10-01 04:00 | 44470.1667 | 0 | 7.3261 | 39.95
2021-10-01 04:30 | 44470.1875 | 0 | 7.8429 | 39.95
2021-10-01 05:00 | 44470.2083 | 0 | 8.4335 | 39.95
2021-10-01 05:30 | 44470.2292 | 0 | 8.6021 | 39.95
2021-10-01 06:00 | 44470.25 | 0 | 9.1102 | 39.95
2021-10-01 06:30 | 44470.2708 | 0 | 9.8998 | 39.95
2021-10-01 07:00 | 44470.2917 | 0 | 10.2249 | 39.95
2021-10-01 07:30 | 44470.3125 | 0 | 10.6514 | 39.95
2021-10-01 08:00 | 44470.3333 | 0 | 11.5353 | 39.95
2021-10-01 08:30 | 44470.3542 | 0 | 11.5127 | 39.95
2021-10-01 09:00 | 44470.375 | 0 | 10.884 | 39.95
2021-10-01 09:30 | 44470.3958 | 0 | 10.0013 | 39.95
2021-10-01 10:00 | 44470.4167 | 0 | 10.9068 | 39.95
2021-10-01 10:30 | 44470.4375 | 0 | 10.8639 | 39.95
2021-10-01 11:00 | 44470.4583 | 0 | 10.7325 | 39.95
2021-10-01 11:30 | 44470.4792 | 0 | 10.7822 | 39.95
2021-10-01 12:00 | 44470.5 | 0 | 9.08 | 39.95
2021-10-01 12:30 | 44470.5208 | 0 | 7.6928 | 39.95
2021-10-01 13:00 | 44470.5417 | 0 | 8.5105 | 39.95
2021-10-01 13:30 | 44470.5625 | 0 | 9.1909 | 39.95
2021-10-01 14:00 | 44470.5833 | 0 | 8.5266 | 39.95
2021-10-01 14:30 | 44470.6042 | 0 | 8.9377 | 39.95
2021-10-01 15:00 | 44470.625 | 0 | 9.1188 | 39.95
2021-10-01 15:30 | 44470.6458 | 0 | 9.7433 | 39.95
2021-10-01 16:00 | 44470.6667 | 0 | 10.6893 | 39.95
2021-10-01 16:30 | 44470.6875 | 0 | 11.3905 | 39.95
2021-10-01 17:00 | 44470.7083 | 0 | 11.4325 | 39.95
2021-10-01 17:30 | 44470.7292 | 0 | 11.8289 | 39.95
2021-10-01 18:00 | 44470.75 | 0 | 12.058 | 39.95
2021-10-01 18:30 | 44470.7708 | 0 | 12.0586 | 39.95
2021-10-01 19:00 | 44470.7917 | 0 | 11.5626 | 39.95
2021-10-01 19:30 | 44470.8125 | 0 | 11.4232 | 39.95
2021-10-01 20:00 | 44470.8333 | 0 | 11.0426 | 39.95
2021-10-01 20:30 | 44470.8542 | 0 | 10.5012 | 39.95
2021-10-01 21:00 | 44470.875 | 0 | 10.1221 | 39.95
2021-10-01 21:30 | 44470.8958 | 0 | 9.8769 | 39.95
2021-10-01 22:00 | 44470.9167 | 0 | 9.5929 | 39.95
2021-10-01 22:30 | 44470.9375 | 0 | 9.0195 | 39.95
2021-10-01 23:00 | 44470.9583 | 0 | 8.625 | 39.95
2021-10-01 23:30 | 44470.9792 | 0 | 8.5884 | 39.95
2021-10-02 | 44471 | 0 | 8.1002 | 39.95
2021-10-02 00:30 | 44471.0208 | 0 | 7.6549 | 39.95
2021-10-02 01:00 | 44471.0417 | 0 | 7.5082 | 39.95
2021-10-02 01:30 | 44471.0625 | 0 | 7.3429 | 39.95
2021-10-02 02:00 | 44471.0833 | 0 | 7.2491 | 39.95
2021-10-02 02:30 | 44471.1042 | 0 | 7.1821 | 39.95
2021-10-02 03:00 | 44471.125 | 0 | 7.0575 | 39.95
2021-10-02 03:30 | 44471.1458 | 0 | 7.0273 | 39.95
2021-10-02 04:00 | 44471.1667 | 0 | 6.938 | 39.95
2021-10-02 04:30 | 44471.1875 | 0 | 7.003 | 39.95
2021-10-02 05:00 | 44471.2083 | 0 | 7.1961 | 39.95
2021-10-02 05:30 | 44471.2292 | 0 | 7.2543 | 39.95
2021-10-02 06:00 | 44471.25 | 0 | 7.348 | 39.95
2021-10-02 06:30 | 44471.2708 | 0 | 6.7973 | 39.95
2021-10-02 07:00 | 44471.2917 | 0 | 6.5424 | 39.95
2021-10-02 07:30 | 44471.3125 | 0 | 6.0972 | 39.95
2021-10-02 08:00 | 44471.3333 | 0 | 5.8869 | 39.95
2021-10-02 08:30 | 44471.3542 | 0 | 5.586 | 39.95
2021-10-02 09:00 | 44471.375 | 0 | 5.2411 | 39.95
2021-10-02 09:30 | 44471.3958 | 0 | 5.3341 | 39.95
2021-10-02 10:00 | 44471.4167 | 0 | 5.0514 | 39.95
2021-10-02 10:30 | 44471.4375 | 0 | 4.9878 | 39.95
2021-10-02 11:00 | 44471.4583 | 0 | 5.237 | 39.95
2021-10-02 11:30 | 44471.4792 | 0 | 5.3763 | 39.95
2021-10-02 12:00 | 44471.5 | 0 | 5.3624 | 39.95
2021-10-02 12:30 | 44471.5208 | 0 | 6.2433 | 39.95
2021-10-02 13:00 | 44471.5417 | 0 | 6.1318 | 39.95
2021-10-02 13:30 | 44471.5625 | 0 | 5.7707 | 39.95
2021-10-02 14:00 | 44471.5833 | 0 | 7.4519 | 39.95
2021-10-02 14:30 | 44471.6042 | 0 | 7.3262 | 39.95
2021-10-02 15:00 | 44471.625 | 0 | 7.6837 | 39.95
2021-10-02 15:30 | 44471.6458 | 0 | 8.0989 | 39.95
2021-10-02 16:00 | 44471.6667 | 0 | 8.703 | 39.95
2021-10-02 16:30 | 44471.6875 | 0 | 9.6892 | 39.95
2021-10-02 17:00 | 44471.7083 | 0 | 10.0141 | 39.95
2021-10-02 17:30 | 44471.7292 | 0 | 10.3867 | 39.95
2021-10-02 18:00 | 44471.75 | 0 | 10.7714 | 39.95
2021-10-02 18:30 | 44471.7708 | 0 | 11.0211 | 39.95
2021-10-02 19:00 | 44471.7917 | 0 | 10.5426 | 39.95
2021-10-02 19:30 | 44471.8125 | 0 | 10.3982 | 39.95
2021-10-02 20:00 | 44471.8333 | 0 | 10.0224 | 39.95
2021-10-02 20:30 | 44471.8542 | 0 | 9.6899 | 39.95
2021-10-02 21:00 | 44471.875 | 0 | 9.2706 | 39.95
2021-10-02 21:30 | 44471.8958 | 0 | 9.1729 | 39.95
2021-10-02 22:00 | 44471.9167 | 0 | 8.9511 | 39.95
2021-10-02 22:30 | 44471.9375 | 0 | 8.3822 | 39.95
2021-10-02 23:00 | 44471.9583 | 0 | 8.0402 | 39.95
2021-10-02 23:30 | 44471.9792 | 0 | 7.6848 | 39.95
2021-10-03 | 44472 | 0 | 7.2125 | 39.95
2021-10-03 00:30 | 44472.0208 | 0 | 6.9869 | 39.95
2021-10-03 01:00 | 44472.0417 | 0 | 6.8708 | 39.95
2021-10-03 01:30 | 44472.0625 | 0 | 6.8141 | 39.95
2021-10-03 02:00 | 44472.0833 | 0 | 6.5936 | 39.95
2021-10-03 02:30 | 44472.1042 | 0 | 6.6831 | 39.95
2021-10-03 03:00 | 44472.125 | 0 | 6.629 | 39.95
2021-10-03 03:30 | 44472.1458 | 0 | 6.6368 | 39.95
2021-10-03 04:00 | 44472.1667 | 0 | 6.6292 | 39.95
2021-10-03 04:30 | 44472.1875 | 0 | 6.5992 | 39.95
2021-10-03 05:00 | 44472.2083 | 0 | 6.6922 | 39.95
2021-10-03 05:30 | 44472.2292 | 0 | 6.6479 | 39.95
2021-10-03 06:00 | 44472.25 | 0 | 6.368 | 39.95
2021-10-03 06:30 | 44472.2708 | 0 | 6.2171 | 39.95
2021-10-03 07:00 | 44472.2917 | 0 | 6.0985 | 39.95
2021-10-03 07:30 | 44472.3125 | 0 | 5.5836 | 39.95
2021-10-03 08:00 | 44472.3333 | 0 | 5.4345 | 39.95
2021-10-03 08:30 | 44472.3542 | 0 | 5.284 | 39.95
2021-10-03 09:00 | 44472.375 | 0 | 5.1216 | 39.95
2021-10-03 09:30 | 44472.3958 | 0 | 5.2373 | 39.95
2021-10-03 10:00 | 44472.4167 | 0 | 4.9836 | 39.95
2021-10-03 10:30 | 44472.4375 | 0 | 4.9882 | 39.95
2021-10-03 11:00 | 44472.4583 | 0 | 4.7647 | 39.95
2021-10-03 11:30 | 44472.4792 | 0 | 4.7607 | 39.95
2021-10-03 12:00 | 44472.5 | 0 | 4.7836 | 39.95
2021-10-03 12:30 | 44472.5208 | 0 | 5.4408 | 39.95
2021-10-03 13:00 | 44472.5417 | 0 | 6.3485 | 39.95
2021-10-03 13:30 | 44472.5625 | 0 | 6.1524 | 39.95
2021-10-03 14:00 | 44472.5833 | 0 | 6.3978 | 39.95
2021-10-03 14:30 | 44472.6042 | 0 | 6.9634 | 39.95
2021-10-03 15:00 | 44472.625 | 0 | 7.6093 | 39.95
2021-10-03 15:30 | 44472.6458 | 0 | 8.4969 | 39.95
2021-10-03 16:00 | 44472.6667 | 0 | 9.1247 | 39.95
2021-10-03 16:30 | 44472.6875 | 0 | 9.8604 | 39.95
2021-10-03 17:00 | 44472.7083 | 0 | 10.1352 | 39.95
2021-10-03 17:30 | 44472.7292 | 0 | 10.4925 | 39.95
2021-10-03 18:00 | 44472.75 | 0 | 11.0121 | 39.95
2021-10-03 18:30 | 44472.7708 | 0 | 11.1166 | 39.95
2021-10-03 19:00 | 44472.7917 | 0 | 10.9104 | 39.95
2021-10-03 19:30 | 44472.8125 | 0 | 10.6322 | 39.95
2021-10-03 20:00 | 44472.8333 | 0 | 10.3036 | 39.95
2021-10-03 20:30 | 44472.8542 | 0 | 9.9252 | 39.95
2021-10-03 21:00 | 44472.875 | 0 | 9.6673 | 39.95
2021-10-03 21:30 | 44472.8958 | 0 | 9.6256 | 39.95
2021-10-03 22:00 | 44472.9167 | 0 | 9.2071 | 39.95
2021-10-03 22:30 | 44472.9375 | 0 | 8.6817 | 39.95
2021-10-03 23:00 | 44472.9583 | 0 | 8.2206 | 39.95
2021-10-03 23:30 | 44472.9792 | 0 | 7.9663 | 39.95
2021-10-04 | 44473 | 0 | 7.5715 | 39.95
2021-10-04 00:30 | 44473.0208 | 0 | 7.3162 | 39.95
2021-10-04 01:00 | 44473.0417 | 0 | 7.1821 | 39.95
2021-10-04 01:30 | 44473.0625 | 0 | 7.0073 | 39.95
2021-10-04 02:00 | 44473.0833 | 0 | 6.9121 | 39.95
2021-10-04 02:30 | 44473.1042 | 0 | 6.8175 | 39.95
2021-10-04 03:00 | 44473.125 | 0 | 6.7032 | 39.95
2021-10-04 03:30 | 44473.1458 | 0 | 6.9511 | 39.95
2021-10-04 04:00 | 44473.1667 | 0 | 6.9133 | 39.95
2021-10-04 04:30 | 44473.1875 | 0 | 7.2112 | 39.95
2021-10-04 05:00 | 44473.2083 | 0 | 7.2988 | 39.95
2021-10-04 05:30 | 44473.2292 | 0 | 7.3454 | 39.95
2021-10-04 06:00 | 44473.25 | 0 | 7.3478 | 39.95
2021-10-04 06:30 | 44473.2708 | 0 | 7.0356 | 39.95
2021-10-04 07:00 | 44473.2917 | 0 | 7.1603 | 39.95
2021-10-04 07:30 | 44473.3125 | 0 | 6.8336 | 39.95
2021-10-04 08:00 | 44473.3333 | 0 | 7.107 | 39.95
2021-10-04 08:30 | 44473.3542 | 0 | 6.3822 | 39.95
2021-10-04 09:00 | 44473.375 | 0 | 6.322 | 39.95
2021-10-04 09:30 | 44473.3958 | 0 | 6.5079 | 39.95
2021-10-04 10:00 | 44473.4167 | 0 | 6.4986 | 39.95
2021-10-04 10:30 | 44473.4375 | 0 | 6.7221 | 39.95
2021-10-04 11:00 | 44473.4583 | 0 | 6.7722 | 39.95
2021-10-04 11:30 | 44473.4792 | 0 | 7.0189 | 39.95
2021-10-04 12:00 | 44473.5 | 0 | 7.2981 | 39.95
2021-10-04 12:30 | 44473.5208 | 0 | 7.9332 | 39.95
2021-10-04 13:00 | 44473.5417 | 0 | 8.5627 | 39.95
2021-10-04 13:30 | 44473.5625 | 0 | 9.3801 | 39.95
2021-10-04 14:00 | 44473.5833 | 0 | 10.4952 | 39.95
2021-10-04 14:30 | 44473.6042 | 0 | 11.4704 | 39.95
2021-10-04 15:00 | 44473.625 | 0 | 12.3637 | 39.95
2021-10-04 15:30 | 44473.6458 | 0 | 13.1268 | 39.95
2021-10-04 16:00 | 44473.6667 | 0 | 13.9629 | 39.95
2021-10-04 16:30 | 44473.6875 | 0 | 15.0355 | 39.95
2021-10-04 17:00 | 44473.7083 | 0 | 15.285 | 39.95
2021-10-04 17:30 | 44473.7292 | 0 | 15.2769 | 39.95
2021-10-04 18:00 | 44473.75 | 0 | 15.5498 | 39.95
2021-10-04 18:30 | 44473.7708 | 0 | 16.0548 | 39.95
2021-10-04 19:00 | 44473.7917 | 0 | 15.5493 | 39.95
2021-10-04 19:30 | 44473.8125 | 0 | 15.1479 | 39.95
2021-10-04 20:00 | 44473.8333 | 0 | 14.2375 | 39.95
2021-10-04 20:30 | 44473.8542 | 0 | 13.5047 | 39.95
2021-10-04 21:00 | 44473.875 | 0 | 12.55 | 39.95
2021-10-04 21:30 | 44473.8958 | 0 | 11.8186 | 39.95
2021-10-04 22:00 | 44473.9167 | 0 | 10.925 | 39.95
2021-10-04 22:30 | 44473.9375 | 0 | 10.0427 | 39.95
2021-10-04 23:00 | 44473.9583 | 0 | 9.2559 | 39.95
2021-10-04 23:30 | 44473.9792 | 0 | 8.9542 | 39.95
2021-10-05 | 44474 | 0 | 8.4202 | 39.95
2021-10-05 00:30 | 44474.0208 | 0 | 8.2395 | 39.95
2021-10-05 01:00 | 44474.0417 | 0 | 7.9488 | 39.95
2021-10-05 01:30 | 44474.0625 | 0 | 7.7513 | 39.95
2021-10-05 02:00 | 44474.0833 | 0 | 7.61 | 39.95
2021-10-05 02:30 | 44474.1042 | 0 | 7.5062 | 39.95
2021-10-05 03:00 | 44474.125 | 0 | 7.3567 | 39.95
2021-10-05 03:30 | 44474.1458 | 0 | 7.4959 | 39.95
2021-10-05 04:00 | 44474.1667 | 0 | 7.6407 | 39.95
2021-10-05 04:30 | 44474.1875 | 0 | 8.1347 | 39.95
2021-10-05 05:00 | 44474.2083 | 0 | 8.6164 | 39.95
2021-10-05 05:30 | 44474.2292 | 0 | 9.0399 | 39.95
2021-10-05 06:00 | 44474.25 | 0 | 9.3586 | 39.95
2021-10-05 06:30 | 44474.2708 | 0 | 9.957 | 39.95
2021-10-05 07:00 | 44474.2917 | 0 | 10.0946 | 39.95
2021-10-05 07:30 | 44474.3125 | 0 | 9.8829 | 39.95
2021-10-05 08:00 | 44474.3333 | 0 | 9.4721 | 39.95
2021-10-05 08:30 | 44474.3542 | 0 | 9.2179 | 39.95
2021-10-05 09:00 | 44474.375 | 0 | 8.9928 | 39.95
2021-10-05 09:30 | 44474.3958 | 0 | 9.0431 | 39.95
2021-10-05 10:00 | 44474.4167 | 0 | 8.8902 | 39.95
2021-10-05 10:30 | 44474.4375 | 0 | 8.9383 | 39.95
2021-10-05 11:00 | 44474.4583 | 0 | 9.015 | 39.95
2021-10-05 11:30 | 44474.4792 | 0 | 9.3584 | 39.95
2021-10-05 12:00 | 44474.5 | 0 | 9.5386 | 39.95
2021-10-05 12:30 | 44474.5208 | 0 | 9.6898 | 39.95
2021-10-05 13:00 | 44474.5417 | 0 | 10.0954 | 39.95
2021-10-05 13:30 | 44474.5625 | 0 | 10.4584 | 39.95
2021-10-05 14:00 | 44474.5833 | 0 | 11.1674 | 39.95
2021-10-05 14:30 | 44474.6042 | 0 | 11.7329 | 39.95
2021-10-05 15:00 | 44474.625 | 0 | 12.0759 | 39.95
2021-10-05 15:30 | 44474.6458 | 0 | 12.5826 | 39.95
2021-10-05 16:00 | 44474.6667 | 0 | 13.4727 | 39.95
2021-10-05 16:30 | 44474.6875 | 0 | 14.26 | 39.95
2021-10-05 17:00 | 44474.7083 | 0 | 14.2134 | 39.95
2021-10-05 17:30 | 44474.7292 | 0 | 14.4782 | 39.95
2021-10-05 18:00 | 44474.75 | 0 | 14.6327 | 39.95
2021-10-05 18:30 | 44474.7708 | 0 | 14.8234 | 39.95
2021-10-05 19:00 | 44474.7917 | 0 | 14.3117 | 39.95
2021-10-05 19:30 | 44474.8125 | 0 | 14.1484 | 39.95
2021-10-05 20:00 | 44474.8333 | 0 | 13.365 | 39.95
2021-10-05 20:30 | 44474.8542 | 0 | 12.767 | 39.95
2021-10-05 21:00 | 44474.875 | 0 | 12.1376 | 39.95
2021-10-05 21:30 | 44474.8958 | 0 | 11.7586 | 39.95
2021-10-05 22:00 | 44474.9167 | 0 | 11.0326 | 39.95
2021-10-05 22:30 | 44474.9375 | 0 | 10.3472 | 39.95
2021-10-05 23:00 | 44474.9583 | 0 | 9.6763 | 39.95
2021-10-05 23:30 | 44474.9792 | 0 | 9.1532 | 39.95
2021-10-06 | 44475 | 0 | 8.6096 | 39.95
2021-10-06 00:30 | 44475.0208 | 0 | 8.2154 | 39.95
2021-10-06 01:00 | 44475.0417 | 0 | 7.9093 | 39.95
2021-10-06 01:30 | 44475.0625 | 0 | 7.7756 | 39.95
2021-10-06 02:00 | 44475.0833 | 0 | 7.7237 | 39.95
2021-10-06 02:30 | 44475.1042 | 0 | 7.5637 | 39.95
2021-10-06 03:00 | 44475.125 | 0 | 7.5148 | 39.95
2021-10-06 03:30 | 44475.1458 | 0 | 7.6221 | 39.95
2021-10-06 04:00 | 44475.1667 | 0 | 7.9631 | 39.95
2021-10-06 04:30 | 44475.1875 | 0 | 8.2611 | 39.95
2021-10-06 05:00 | 44475.2083 | 0 | 8.6621 | 39.95
2021-10-06 05:30 | 44475.2292 | 0 | 9.275 | 39.95
2021-10-06 06:00 | 44475.25 | 0 | 9.5941 | 39.95
2021-10-06 06:30 | 44475.2708 | 0 | 9.8286 | 39.95
2021-10-06 07:00 | 44475.2917 | 0 | 9.9189 | 39.95
2021-10-06 07:30 | 44475.3125 | 0 | 9.6342 | 39.95
2021-10-06 08:00 | 44475.3333 | 0 | 9.0071 | 39.95
2021-10-06 08:30 | 44475.3542 | 0 | 8.5565 | 39.95
2021-10-06 09:00 | 44475.375 | 0 | 8.3532 | 39.95
2021-10-06 09:30 | 44475.3958 | 0 | 8.1196 | 39.95
2021-10-06 10:00 | 44475.4167 | 0 | 8.207 | 39.95
2021-10-06 10:30 | 44475.4375 | 0 | 8.3023 | 39.95
2021-10-06 11:00 | 44475.4583 | 0 | 8.3448 | 39.95
2021-10-06 11:30 | 44475.4792 | 0 | 8.4025 | 39.95
2021-10-06 12:00 | 44475.5 | 0 | 8.3361 | 39.95
2021-10-06 12:30 | 44475.5208 | 0 | 8.5522 | 39.95
2021-10-06 13:00 | 44475.5417 | 0 | 8.7912 | 39.95
2021-10-06 13:30 | 44475.5625 | 0 | 9.1548 | 39.95
2021-10-06 14:00 | 44475.5833 | 0 | 9.6627 | 39.95
2021-10-06 14:30 | 44475.6042 | 0 | 10.1193 | 39.95
2021-10-06 15:00 | 44475.625 | 0 | 10.5998 | 39.95
2021-10-06 15:30 | 44475.6458 | 0 | 11.2367 | 39.95
2021-10-06 16:00 | 44475.6667 | 0 | 11.9696 | 39.95
2021-10-06 16:30 | 44475.6875 | 0 | 12.856 | 39.95
2021-10-06 17:00 | 44475.7083 | 0 | 13.0662 | 39.95
2021-10-06 17:30 | 44475.7292 | 0 | 13.3704 | 39.95
2021-10-06 18:00 | 44475.75 | 0 | 13.7442 | 39.95
2021-10-06 18:30 | 44475.7708 | 0 | 13.9905 | 39.95
2021-10-06 19:00 | 44475.7917 | 0 | 13.5264 | 39.95
2021-10-06 19:30 | 44475.8125 | 0 | 13.1525 | 39.95
2021-10-06 20:00 | 44475.8333 | 0 | 12.8635 | 39.95
2021-10-06 20:30 | 44475.8542 | 0 | 12.3147 | 39.95
2021-10-06 21:00 | 44475.875 | 0 | 11.7816 | 39.95
2021-10-06 21:30 | 44475.8958 | 0 | 11.537 | 39.95
2021-10-06 22:00 | 44475.9167 | 0 | 10.9131 | 39.95
2021-10-06 22:30 | 44475.9375 | 0 | 10.1447 | 39.95
2021-10-06 23:00 | 44475.9583 | 0 | 9.6065 | 39.95
2021-10-06 23:30 | 44475.9792 | 0 | 9.1973 | 39.95
2021-10-07 | 44476 | 0 | 8.6677 | 39.95
2021-10-07 00:30 | 44476.0208 | 0 | 8.2754 | 39.95
2021-10-07 01:00 | 44476.0417 | 0 | 7.9501 | 39.95
2021-10-07 01:30 | 44476.0625 | 0 | 7.7015 | 39.95
2021-10-07 02:00 | 44476.0833 | 0 | 7.6597 | 39.95
2021-10-07 02:30 | 44476.1042 | 0 | 7.5473 | 39.95
2021-10-07 03:00 | 44476.125 | 0 | 7.5283 | 39.95
2021-10-07 03:30 | 44476.1458 | 0 | 7.6203 | 39.95
2021-10-07 04:00 | 44476.1667 | 0 | 7.8563 | 39.95
2021-10-07 04:30 | 44476.1875 | 0 | 8.2256 | 39.95
2021-10-07 05:00 | 44476.2083 | 0 | 8.6787 | 39.95
2021-10-07 05:30 | 44476.2292 | 0 | 9.0482 | 39.95
2021-10-07 06:00 | 44476.25 | 0 | 9.4865 | 39.95
2021-10-07 06:30 | 44476.2708 | 0 | 9.7719 | 39.95
2021-10-07 07:00 | 44476.2917 | 0 | 10.1625 | 39.95
2021-10-07 07:30 | 44476.3125 | 0 | 10.0445 | 39.95
2021-10-07 08:00 | 44476.3333 | 0 | 9.4868 | 39.95
2021-10-07 08:30 | 44476.3542 | 0 | 9.2118 | 39.95
2021-10-07 09:00 | 44476.375 | 0 | 8.8484 | 39.95
2021-10-07 09:30 | 44476.3958 | 0 | 8.7242 | 39.95
2021-10-07 10:00 | 44476.4167 | 0 | 8.7701 | 39.95
2021-10-07 10:30 | 44476.4375 | 0 | 8.8519 | 39.95
2021-10-07 11:00 | 44476.4583 | 0 | 8.811 | 39.95
2021-10-07 11:30 | 44476.4792 | 0 | 8.8806 | 39.95
2021-10-07 12:00 | 44476.5 | 0 | 8.9059 | 39.95
2021-10-07 12:30 | 44476.5208 | 0 | 8.9225 | 39.95
2021-10-07 13:00 | 44476.5417 | 0 | 9.4499 | 39.95
2021-10-07 13:30 | 44476.5625 | 0 | 10.3551 | 39.95
2021-10-07 14:00 | 44476.5833 | 0 | 12.284 | 39.95
2021-10-07 14:30 | 44476.6042 | 0 | 12.3669 | 39.95
2021-10-07 15:00 | 44476.625 | 0 | 12.4933 | 39.95
2021-10-07 15:30 | 44476.6458 | 0 | 11.9978 | 39.95
2021-10-07 16:00 | 44476.6667 | 0 | 12.1382 | 39.95
2021-10-07 16:30 | 44476.6875 | 0 | 12.391 | 39.95
2021-10-07 17:00 | 44476.7083 | 0 | 12.7836 | 39.95
2021-10-07 17:30 | 44476.7292 | 0 | 13.1448 | 39.95
2021-10-07 18:00 | 44476.75 | 0 | 13.4223 | 39.95
2021-10-07 18:30 | 44476.7708 | 0 | 13.5876 | 39.95
2021-10-07 19:00 | 44476.7917 | 0 | 13.4014 | 39.95
2021-10-07 19:30 | 44476.8125 | 0 | 13.108 | 39.95
2021-10-07 20:00 | 44476.8333 | 0 | 12.689 | 39.95
2021-10-07 20:30 | 44476.8542 | 0 | 12.1803 | 39.95
2021-10-07 21:00 | 44476.875 | 0 | 11.7083 | 39.95
2021-10-07 21:30 | 44476.8958 | 0 | 11.333 | 39.95
2021-10-07 22:00 | 44476.9167 | 0 | 10.9094 | 39.95
2021-10-07 22:30 | 44476.9375 | 0 | 10.009 | 39.95
2021-10-07 23:00 | 44476.9583 | 0 | 9.5146 | 39.95
2021-10-07 23:30 | 44476.9792 | 0 | 9.0492 | 39.95
2021-10-08 | 44477 | 0 | 8.6504 | 39.95
2021-10-08 00:30 | 44477.0208 | 0 | 8.3919 | 39.95
2021-10-08 01:00 | 44477.0417 | 0 | 8.1312 | 39.95
2021-10-08 01:30 | 44477.0625 | 0 | 7.9162 | 39.95
2021-10-08 02:00 | 44477.0833 | 0 | 7.8611 | 39.95
2021-10-08 02:30 | 44477.1042 | 0 | 7.8384 | 39.95
2021-10-08 03:00 | 44477.125 | 0 | 7.6962 | 39.95
2021-10-08 03:30 | 44477.1458 | 0 | 7.7531 | 39.95
2021-10-08 04:00 | 44477.1667 | 0 | 8.0844 | 39.95
2021-10-08 04:30 | 44477.1875 | 0 | 8.5398 | 39.95
2021-10-08 05:00 | 44477.2083 | 0 | 8.8875 | 39.95
2021-10-08 05:30 | 44477.2292 | 0 | 9.2747 | 39.95
2021-10-08 06:00 | 44477.25 | 0 | 9.6637 | 39.95
2021-10-08 06:30 | 44477.2708 | 0 | 10.0674 | 39.95
2021-10-08 07:00 | 44477.2917 | 0 | 10.4249 | 39.95
2021-10-08 07:30 | 44477.3125 | 0 | 10.1569 | 39.95
2021-10-08 08:00 | 44477.3333 | 0 | 9.9905 | 39.95
2021-10-08 08:30 | 44477.3542 | 0 | 9.8152 | 39.95
2021-10-08 09:00 | 44477.375 | 0 | 9.4487 | 39.95
2021-10-08 09:30 | 44477.3958 | 0 | 9.3842 | 39.95
2021-10-08 10:00 | 44477.4167 | 0 | 9.4783 | 39.95
2021-10-08 10:30 | 44477.4375 | 0 | 9.5632 | 39.95
2021-10-08 11:00 | 44477.4583 | 0 | 9.5535 | 39.95
2021-10-08 11:30 | 44477.4792 | 0 | 9.944 | 39.95
2021-10-08 12:00 | 44477.5 | 0 | 9.6395 | 39.95
2021-10-08 12:30 | 44477.5208 | 0 | 9.9972 | 39.95
2021-10-08 13:00 | 44477.5417 | 0 | 9.9764 | 39.95
2021-10-08 13:30 | 44477.5625 | 0 | 10.1833 | 39.95
2021-10-08 14:00 | 44477.5833 | 0 | 10.5579 | 39.95
2021-10-08 14:30 | 44477.6042 | 0 | 11.2217 | 39.95
2021-10-08 15:00 | 44477.625 | 0 | 11.5951 | 39.95
2021-10-08 15:30 | 44477.6458 | 0 | 12.1906 | 39.95
2021-10-08 16:00 | 44477.6667 | 0 | 12.7964 | 39.95
2021-10-08 16:30 | 44477.6875 | 0 | 13.3717 | 39.95
2021-10-08 17:00 | 44477.7083 | 0 | 13.372 | 39.95
2021-10-08 17:30 | 44477.7292 | 0 | 13.3251 | 39.95
2021-10-08 18:00 | 44477.75 | 0 | 13.6251 | 39.95
2021-10-08 18:30 | 44477.7708 | 0 | 13.8548 | 39.95
2021-10-08 19:00 | 44477.7917 | 0 | 13.5377 | 39.95
2021-10-08 19:30 | 44477.8125 | 0 | 13.0796 | 39.95
2021-10-08 20:00 | 44477.8333 | 0 | 12.6756 | 39.95
2021-10-08 20:30 | 44477.8542 | 0 | 12.273 | 39.95
2021-10-08 21:00 | 44477.875 | 0 | 11.7715 | 39.95
2021-10-08 21:30 | 44477.8958 | 0 | 11.5746 | 39.95
2021-10-08 22:00 | 44477.9167 | 0 | 11.243 | 39.95
2021-10-08 22:30 | 44477.9375 | 0 | 10.4278 | 39.95
2021-10-08 23:00 | 44477.9583 | 0 | 9.9764 | 39.95
2021-10-08 23:30 | 44477.9792 | 0 | 9.4356 | 39.95
2021-10-09 | 44478 | 0 | 8.9098 | 39.95
2021-10-09 00:30 | 44478.0208 | 0 | 8.5363 | 39.95
2021-10-09 01:00 | 44478.0417 | 0 | 8.1778 | 39.95
2021-10-09 01:30 | 44478.0625 | 0 | 8.0294 | 39.95
2021-10-09 02:00 | 44478.0833 | 0 | 7.918 | 39.95
2021-10-09 02:30 | 44478.1042 | 0 | 7.7063 | 39.95
2021-10-09 03:00 | 44478.125 | 0 | 7.5615 | 39.95
2021-10-09 03:30 | 44478.1458 | 0 | 7.6828 | 39.95
2021-10-09 04:00 | 44478.1667 | 0 | 7.7706 | 39.95
2021-10-09 04:30 | 44478.1875 | 0 | 7.7967 | 39.95
2021-10-09 05:00 | 44478.2083 | 0 | 8.1094 | 39.95
2021-10-09 05:30 | 44478.2292 | 0 | 8.2236 | 39.95
2021-10-09 06:00 | 44478.25 | 0 | 8.1641 | 39.95
2021-10-09 06:30 | 44478.2708 | 0 | 8.0576 | 39.95
2021-10-09 07:00 | 44478.2917 | 0 | 8.1462 | 39.95
2021-10-09 07:30 | 44478.3125 | 0 | 8.6113 | 39.95
2021-10-09 08:00 | 44478.3333 | 0 | 8.5765 | 39.95
2021-10-09 08:30 | 44478.3542 | 0 | 8.1717 | 39.95
2021-10-09 09:00 | 44478.375 | 0 | 8.7343 | 39.95
2021-10-09 09:30 | 44478.3958 | 0 | 8.5876 | 39.95
2021-10-09 10:00 | 44478.4167 | 0 | 8.029 | 39.95
2021-10-09 10:30 | 44478.4375 | 0 | 7.3106 | 39.95
2021-10-09 11:00 | 44478.4583 | 0 | 7.1673 | 39.95
2021-10-09 11:30 | 44478.4792 | 0 | 7.1714 | 39.95
2021-10-09 12:00 | 44478.5 | 0 | 7.1219 | 39.95
2021-10-09 12:30 | 44478.5208 | 0 | 7.1874 | 39.95
2021-10-09 13:00 | 44478.5417 | 0 | 7.4781 | 39.95
2021-10-09 13:30 | 44478.5625 | 0 | 7.8566 | 39.95
2021-10-09 14:00 | 44478.5833 | 0 | 8.1989 | 39.95
2021-10-09 14:30 | 44478.6042 | 0 | 8.7577 | 39.95
2021-10-09 15:00 | 44478.625 | 0 | 9.3447 | 39.95
2021-10-09 15:30 | 44478.6458 | 0 | 9.9298 | 39.95
2021-10-09 16:00 | 44478.6667 | 0 | 10.391 | 39.95
2021-10-09 16:30 | 44478.6875 | 0 | 10.8977 | 39.95
2021-10-09 17:00 | 44478.7083 | 0 | 11.2997 | 39.95
2021-10-09 17:30 | 44478.7292 | 0 | 11.4042 | 39.95
2021-10-09 18:00 | 44478.75 | 0 | 11.722 | 39.95
2021-10-09 18:30 | 44478.7708 | 0 | 12.023 | 39.95
2021-10-09 19:00 | 44478.7917 | 0 | 11.6819 | 39.95
2021-10-09 19:30 | 44478.8125 | 0 | 11.4611 | 39.95
2021-10-09 20:00 | 44478.8333 | 0 | 11.1157 | 39.95
2021-10-09 20:30 | 44478.8542 | 0 | 10.8054 | 39.95
2021-10-09 21:00 | 44478.875 | 0 | 10.5559 | 39.95
2021-10-09 21:30 | 44478.8958 | 0 | 10.2596 | 39.95
2021-10-09 22:00 | 44478.9167 | 0 | 10.0248 | 39.95
2021-10-09 22:30 | 44478.9375 | 0 | 9.4029 | 39.95
2021-10-09 23:00 | 44478.9583 | 0 | 9.0541 | 39.95
2021-10-09 23:30 | 44478.9792 | 0 | 8.7218 | 39.95
2021-10-10 | 44479 | 0 | 8.2748 | 39.95
2021-10-10 00:30 | 44479.0208 | 0 | 7.9638 | 39.95
2021-10-10 01:00 | 44479.0417 | 0 | 7.8581 | 39.95
2021-10-10 01:30 | 44479.0625 | 0 | 7.5845 | 39.95
2021-10-10 02:00 | 44479.0833 | 0 | 7.5365 | 39.95
2021-10-10 02:30 | 44479.1042 | 0 | 7.4222 | 39.95
2021-10-10 03:00 | 44479.125 | 0 | 7.5049 | 39.95
2021-10-10 03:30 | 44479.1458 | 0 | 7.493 | 39.95
2021-10-10 04:00 | 44479.1667 | 0 | 7.4676 | 39.95
2021-10-10 04:30 | 44479.1875 | 0 | 7.3806 | 39.95
2021-10-10 05:00 | 44479.2083 | 0 | 7.3876 | 39.95
2021-10-10 05:30 | 44479.2292 | 0 | 7.2808 | 39.95
2021-10-10 06:00 | 44479.25 | 0 | 7.0992 | 39.95
2021-10-10 06:30 | 44479.2708 | 0 | 6.8744 | 39.95
2021-10-10 07:00 | 44479.2917 | 0 | 6.7211 | 39.95
2021-10-10 07:30 | 44479.3125 | 0 | 6.5129 | 39.95
2021-10-10 08:00 | 44479.3333 | 0 | 6.3481 | 39.95
2021-10-10 08:30 | 44479.3542 | 0 | 6.3644 | 39.95
2021-10-10 09:00 | 44479.375 | 0 | 6.3026 | 39.95
2021-10-10 09:30 | 44479.3958 | 0 | 6.3451 | 39.95
2021-10-10 10:00 | 44479.4167 | 0 | 6.0864 | 39.95
2021-10-10 10:30 | 44479.4375 | 0 | 6.2833 | 39.95
2021-10-10 11:00 | 44479.4583 | 0 | 6.3235 | 39.95
2021-10-10 11:30 | 44479.4792 | 0 | 6.3414 | 39.95
2021-10-10 12:00 | 44479.5 | 0 | 6.4192 | 39.95
2021-10-10 12:30 | 44479.5208 | 0 | 6.5598 | 39.95
2021-10-10 13:00 | 44479.5417 | 0 | 6.9446 | 39.95
2021-10-10 13:30 | 44479.5625 | 0 | 7.4625 | 39.95
2021-10-10 14:00 | 44479.5833 | 0 | 7.9678 | 39.95
2021-10-10 14:30 | 44479.6042 | 0 | 8.3803 | 39.95
2021-10-10 15:00 | 44479.625 | 0 | 9.1312 | 39.95
2021-10-10 15:30 | 44479.6458 | 0 | 9.7188 | 39.95
2021-10-10 16:00 | 44479.6667 | 0 | 10.1167 | 39.95
2021-10-10 16:30 | 44479.6875 | 0 | 10.7994 | 39.95
2021-10-10 17:00 | 44479.7083 | 0 | 11.1637 | 39.95
2021-10-10 17:30 | 44479.7292 | 0 | 11.4989 | 39.95
2021-10-10 18:00 | 44479.75 | 0 | 11.9896 | 39.95
2021-10-10 18:30 | 44479.7708 | 0 | 12.2011 | 39.95
2021-10-10 19:00 | 44479.7917 | 0 | 12.0529 | 39.95
2021-10-10 19:30 | 44479.8125 | 0 | 11.7591 | 39.95
2021-10-10 20:00 | 44479.8333 | 0 | 11.4057 | 39.95
2021-10-10 20:30 | 44479.8542 | 0 | 11.0168 | 39.95
2021-10-10 21:00 | 44479.875 | 0 | 10.5924 | 39.95
2021-10-10 21:30 | 44479.8958 | 0 | 10.2112 | 39.95
2021-10-10 22:00 | 44479.9167 | 0 | 9.7179 | 39.95
2021-10-10 22:30 | 44479.9375 | 0 | 9.12 | 39.95
2021-10-10 23:00 | 44479.9583 | 0 | 8.61 | 39.95
2021-10-10 23:30 | 44479.9792 | 0 | 8.2175 | 39.95
2021-10-11 | 44480 | 0 | 7.9255 | 39.95
2021-10-11 00:30 | 44480.0208 | 0 | 7.7349 | 39.95
2021-10-11 01:00 | 44480.0417 | 0 | 7.5264 | 39.95
2021-10-11 01:30 | 44480.0625 | 0 | 7.3486 | 39.95
2021-10-11 02:00 | 44480.0833 | 0 | 7.3259 | 39.95
2021-10-11 02:30 | 44480.1042 | 0 | 7.244 | 39.95
2021-10-11 03:00 | 44480.125 | 0 | 7.1357 | 39.95
2021-10-11 03:30 | 44480.1458 | 0 | 7.46 | 39.95
2021-10-11 04:00 | 44480.1667 | 0 | 7.6236 | 39.95
2021-10-11 04:30 | 44480.1875 | 0 | 8.1669 | 39.95
2021-10-11 05:00 | 44480.2083 | 0 | 8.3989 | 39.95
2021-10-11 05:30 | 44480.2292 | 0 | 9.2129 | 39.95
2021-10-11 06:00 | 44480.25 | 0 | 9.6388 | 39.95
2021-10-11 06:30 | 44480.2708 | 0 | 9.9157 | 39.95
2021-10-11 07:00 | 44480.2917 | 0 | 10.7429 | 39.95
2021-10-11 07:30 | 44480.3125 | 0 | 10.5584 | 39.95
2021-10-11 08:00 | 44480.3333 | 0 | 11.3212 | 39.95
2021-10-11 08:30 | 44480.3542 | 0 | 10.6937 | 39.95
2021-10-11 09:00 | 44480.375 | 0 | 10.2284 | 39.95
2021-10-11 09:30 | 44480.3958 | 0 | 9.8663 | 39.95
2021-10-11 10:00 | 44480.4167 | 0 | 9.7325 | 39.95
2021-10-11 10:30 | 44480.4375 | 0 | 9.9912 | 39.95
2021-10-11 11:00 | 44480.4583 | 0 | 10.4921 | 39.95
2021-10-11 11:30 | 44480.4792 | 0 | 10.9558 | 39.95
2021-10-11 12:00 | 44480.5 | 0 | 10.3589 | 39.95
2021-10-11 12:30 | 44480.5208 | 0 | 11.7274 | 39.95
2021-10-11 13:00 | 44480.5417 | 0 | 11.9737 | 39.95
2021-10-11 13:30 | 44480.5625 | 0 | 12.6181 | 39.95
2021-10-11 14:00 | 44480.5833 | 0 | 11.8738 | 39.95
2021-10-11 14:30 | 44480.6042 | 0 | 12.8204 | 39.95
2021-10-11 15:00 | 44480.625 | 0 | 12.3209 | 39.95
2021-10-11 15:30 | 44480.6458 | 0 | 12.2573 | 39.95
2021-10-11 16:00 | 44480.6667 | 0 | 13.3511 | 39.95
2021-10-11 16:30 | 44480.6875 | 0 | 13.7979 | 39.95
2021-10-11 17:00 | 44480.7083 | 0 | 13.8879 | 39.95
2021-10-11 17:30 | 44480.7292 | 0 | 14.2673 | 39.95
2021-10-11 18:00 | 44480.75 | 0 | 14.4422 | 39.95
2021-10-11 18:30 | 44480.7708 | 0 | 14.6729 | 39.95
2021-10-11 19:00 | 44480.7917 | 0 | 14.3934 | 39.95
2021-10-11 19:30 | 44480.8125 | 0 | 14.1838 | 39.95
2021-10-11 20:00 | 44480.8333 | 0 | 13.6106 | 39.95
2021-10-11 20:30 | 44480.8542 | 0 | 13.0685 | 39.95
2021-10-11 21:00 | 44480.875 | 0 | 12.5058 | 39.95
2021-10-11 21:30 | 44480.8958 | 0 | 12.0291 | 39.95
2021-10-11 22:00 | 44480.9167 | 0 | 11.4345 | 39.95
2021-10-11 22:30 | 44480.9375 | 0 | 10.5598 | 39.95
2021-10-11 23:00 | 44480.9583 | 0 | 9.8811 | 39.95
2021-10-11 23:30 | 44480.9792 | 0 | 9.4706 | 39.95
2021-10-12 | 44481 | 0 | 9.0077 | 39.95
2021-10-12 00:30 | 44481.0208 | 0 | 8.5942 | 39.95
2021-10-12 01:00 | 44481.0417 | 0 | 8.3339 | 39.95
2021-10-12 01:30 | 44481.0625 | 0 | 8.0744 | 39.95
2021-10-12 02:00 | 44481.0833 | 0 | 7.9415 | 39.95
2021-10-12 02:30 | 44481.1042 | 0 | 7.8522 | 39.95
2021-10-12 03:00 | 44481.125 | 0 | 7.6783 | 39.95
2021-10-12 03:30 | 44481.1458 | 0 | 7.8048 | 39.95
2021-10-12 04:00 | 44481.1667 | 0 | 7.9463 | 39.95
2021-10-12 04:30 | 44481.1875 | 0 | 8.6128 | 39.95
2021-10-12 05:00 | 44481.2083 | 0 | 9.2707 | 39.95
2021-10-12 05:30 | 44481.2292 | 0 | 9.6205 | 39.95
2021-10-12 06:00 | 44481.25 | 0 | 10.5728 | 39.95
2021-10-12 06:30 | 44481.2708 | 0 | 11.3468 | 39.95
2021-10-12 07:00 | 44481.2917 | 0 | 11.996 | 39.95
2021-10-12 07:30 | 44481.3125 | 0 | 12.258 | 39.95
2021-10-12 08:00 | 44481.3333 | 0 | 11.3737 | 39.95
2021-10-12 08:30 | 44481.3542 | 0 | 11.3448 | 39.95
2021-10-12 09:00 | 44481.375 | 0 | 11.3468 | 39.95
2021-10-12 09:30 | 44481.3958 | 0 | 10.946 | 39.95
2021-10-12 10:00 | 44481.4167 | 0 | 11.5817 | 39.95
2021-10-12 10:30 | 44481.4375 | 0 | 11.3661 | 39.95
2021-10-12 11:00 | 44481.4583 | 0 | 11.3606 | 39.95
2021-10-12 11:30 | 44481.4792 | 0 | 11.246 | 39.95
2021-10-12 12:00 | 44481.5 | 0 | 11.9102 | 39.95
2021-10-12 12:30 | 44481.5208 | 0 | 11.2967 | 39.95
2021-10-12 13:00 | 44481.5417 | 0 | 10.3622 | 39.95
2021-10-12 13:30 | 44481.5625 | 0 | 12.1098 | 39.95
2021-10-12 14:00 | 44481.5833 | 0 | 11.9452 | 39.95
2021-10-12 14:30 | 44481.6042 | 0 | 11.4439 | 39.95
2021-10-12 15:00 | 44481.625 | 0 | 12.063 | 39.95
2021-10-12 15:30 | 44481.6458 | 0 | 12.6899 | 39.95
2021-10-12 16:00 | 44481.6667 | 0 | 12.1237 | 39.95
2021-10-12 16:30 | 44481.6875 | 0 | 12.3332 | 39.95
2021-10-12 17:00 | 44481.7083 | 0 | 12.3616 | 39.95
2021-10-12 17:30 | 44481.7292 | 0 | 12.8041 | 39.95
2021-10-12 18:00 | 44481.75 | 0 | 13.236 | 39.95
2021-10-12 18:30 | 44481.7708 | 0 | 13.4588 | 39.95
2021-10-12 19:00 | 44481.7917 | 0 | 13.2764 | 39.95
2021-10-12 19:30 | 44481.8125 | 0 | 13.0572 | 39.95
2021-10-12 20:00 | 44481.8333 | 0 | 12.5894 | 39.95
2021-10-12 20:30 | 44481.8542 | 0 | 12.1414 | 39.95
2021-10-12 21:00 | 44481.875 | 0 | 11.8415 | 39.95
2021-10-12 21:30 | 44481.8958 | 0 | 11.3818 | 39.95
2021-10-12 22:00 | 44481.9167 | 0 | 10.7595 | 39.95
2021-10-12 22:30 | 44481.9375 | 0 | 9.8598 | 39.95
2021-10-12 23:00 | 44481.9583 | 0 | 9.5003 | 39.95
2021-10-12 23:30 | 44481.9792 | 0 | 9.1364 | 39.95
2021-10-13 | 44482 | 0 | 8.6006 | 39.95
2021-10-13 00:30 | 44482.0208 | 0 | 8.1473 | 39.95
2021-10-13 01:00 | 44482.0417 | 0 | 7.8003 | 39.95
2021-10-13 01:30 | 44482.0625 | 0 | 7.7695 | 39.95
2021-10-13 02:00 | 44482.0833 | 0 | 7.777 | 39.95
2021-10-13 02:30 | 44482.1042 | 0 | 7.6575 | 39.95
2021-10-13 03:00 | 44482.125 | 0 | 7.5313 | 39.95
2021-10-13 03:30 | 44482.1458 | 0 | 7.7528 | 39.95
2021-10-13 04:00 | 44482.1667 | 0 | 8.1581 | 39.95
2021-10-13 04:30 | 44482.1875 | 0 | 8.5438 | 39.95
2021-10-13 05:00 | 44482.2083 | 0 | 9.2658 | 39.95
2021-10-13 05:30 | 44482.2292 | 0 | 9.7614 | 39.95
2021-10-13 06:00 | 44482.25 | 0 | 10.311 | 39.95
2021-10-13 06:30 | 44482.2708 | 0 | 10.8123 | 39.95
2021-10-13 07:00 | 44482.2917 | 0 | 11.0539 | 39.95
2021-10-13 07:30 | 44482.3125 | 0 | 10.4666 | 39.95
2021-10-13 08:00 | 44482.3333 | 0 | 11.6414 | 39.95
2021-10-13 08:30 | 44482.3542 | 0 | 10.7679 | 39.95
2021-10-13 09:00 | 44482.375 | 0 | 10.8266 | 39.95
2021-10-13 09:30 | 44482.3958 | 0 | 11.0481 | 39.95
2021-10-13 10:00 | 44482.4167 | 0 | 11.1832 | 39.95
2021-10-13 10:30 | 44482.4375 | 0 | 10.855 | 39.95
2021-10-13 11:00 | 44482.4583 | 0 | 9.2565 | 39.95
2021-10-13 11:30 | 44482.4792 | 0 | 10.3456 | 39.95
2021-10-13 12:00 | 44482.5 | 0 | 10.4824 | 39.95
2021-10-13 12:30 | 44482.5208 | 0 | 9.565 | 39.95
2021-10-13 13:00 | 44482.5417 | 0 | 10.543 | 39.95
2021-10-13 13:30 | 44482.5625 | 0 | 11.2342 | 39.95
2021-10-13 14:00 | 44482.5833 | 0 | 11.9566 | 39.95
2021-10-13 14:30 | 44482.6042 | 0 | 11.0952 | 39.95
2021-10-13 15:00 | 44482.625 | 0 | 10.6129 | 39.95
2021-10-13 15:30 | 44482.6458 | 0 | 11.1537 | 39.95
2021-10-13 16:00 | 44482.6667 | 0 | 12.3493 | 39.95
2021-10-13 16:30 | 44482.6875 | 0 | 12.6746 | 39.95
2021-10-13 17:00 | 44482.7083 | 0 | 12.6808 | 39.95
2021-10-13 17:30 | 44482.7292 | 0 | 13.2256 | 39.95
2021-10-13 18:00 | 44482.75 | 0 | 13.7083 | 39.95
2021-10-13 18:30 | 44482.7708 | 0 | 13.8887 | 39.95
2021-10-13 19:00 | 44482.7917 | 0 | 13.7964 | 39.95
2021-10-13 19:30 | 44482.8125 | 0 | 13.3972 | 39.95
2021-10-13 20:00 | 44482.8333 | 0 | 12.9663 | 39.95
2021-10-13 20:30 | 44482.8542 | 0 | 12.601 | 39.95
2021-10-13 21:00 | 44482.875 | 0 | 12.1311 | 39.95
2021-10-13 21:30 | 44482.8958 | 0 | 11.6888 | 39.95
2021-10-13 22:00 | 44482.9167 | 0 | 11.2663 | 39.95
2021-10-13 22:30 | 44482.9375 | 0 | 10.4346 | 39.95
2021-10-13 23:00 | 44482.9583 | 0 | 9.8684 | 39.95
2021-10-13 23:30 | 44482.9792 | 0 | 9.2397 | 39.95
2021-10-14 | 44483 | 0 | 8.8765 | 39.95
2021-10-14 00:30 | 44483.0208 | 0 | 8.35 | 39.95
2021-10-14 01:00 | 44483.0417 | 0 | 8.3122 | 39.95
2021-10-14 01:30 | 44483.0625 | 0 | 8.0513 | 39.95
2021-10-14 02:00 | 44483.0833 | 0 | 8.0971 | 39.95
2021-10-14 02:30 | 44483.1042 | 0 | 7.959 | 39.95
2021-10-14 03:00 | 44483.125 | 0 | 7.9058 | 39.95
2021-10-14 03:30 | 44483.1458 | 0 | 8.1741 | 39.95
2021-10-14 04:00 | 44483.1667 | 0 | 8.3852 | 39.95
2021-10-14 04:30 | 44483.1875 | 0 | 8.711 | 39.95
2021-10-14 05:00 | 44483.2083 | 0 | 9.3996 | 39.95
2021-10-14 05:30 | 44483.2292 | 0 | 10.3029 | 39.95
2021-10-14 06:00 | 44483.25 | 0 | 11.236 | 39.95
2021-10-14 06:30 | 44483.2708 | 0 | 11.871 | 39.95
2021-10-14 07:00 | 44483.2917 | 0 | 12.8501 | 39.95
2021-10-14 07:30 | 44483.3125 | 0 | 13.1379 | 39.95
2021-10-14 08:00 | 44483.3333 | 0 | 13.4054 | 39.95
2021-10-14 08:30 | 44483.3542 | 0 | 12.9488 | 39.95
2021-10-14 09:00 | 44483.375 | 0 | 12.3124 | 39.95
2021-10-14 09:30 | 44483.3958 | 0 | 10.9515 | 39.95
2021-10-14 10:00 | 44483.4167 | 0 | 10.0885 | 39.95
2021-10-14 10:30 | 44483.4375 | 0 | 10.7478 | 39.95
2021-10-14 11:00 | 44483.4583 | 0 | 11.2209 | 39.95
2021-10-14 11:30 | 44483.4792 | 0 | 10.888 | 39.95
2021-10-14 12:00 | 44483.5 | 0 | 10.9421 | 39.95
2021-10-14 12:30 | 44483.5208 | 0 | 10.1825 | 39.95
2021-10-14 13:00 | 44483.5417 | 0 | 9.6728 | 39.95
2021-10-14 13:30 | 44483.5625 | 0 | 9.8556 | 39.95
2021-10-14 14:00 | 44483.5833 | 0 | 9.7446 | 39.95
2021-10-14 14:30 | 44483.6042 | 0 | 10.4133 | 39.95
2021-10-14 15:00 | 44483.625 | 0 | 11.0155 | 39.95
2021-10-14 15:30 | 44483.6458 | 0 | 11.8333 | 39.95
2021-10-14 16:00 | 44483.6667 | 0 | 12.3238 | 39.95
2021-10-14 16:30 | 44483.6875 | 0 | 13.0175 | 39.95
2021-10-14 17:00 | 44483.7083 | 0 | 13.1577 | 39.95
2021-10-14 17:30 | 44483.7292 | 0 | 13.6527 | 39.95
2021-10-14 18:00 | 44483.75 | 0 | 13.9895 | 39.95
2021-10-14 18:30 | 44483.7708 | 0 | 14.1481 | 39.95
2021-10-14 19:00 | 44483.7917 | 0 | 13.7826 | 39.95
2021-10-14 19:30 | 44483.8125 | 0 | 13.672 | 39.95
2021-10-14 20:00 | 44483.8333 | 0 | 13.314 | 39.95
2021-10-14 20:30 | 44483.8542 | 0 | 12.8346 | 39.95
2021-10-14 21:00 | 44483.875 | 0 | 12.4793 | 39.95
2021-10-14 21:30 | 44483.8958 | 0 | 12.1717 | 39.95
2021-10-14 22:00 | 44483.9167 | 0 | 11.8309 | 39.95
2021-10-14 22:30 | 44483.9375 | 0 | 10.9274 | 39.95
2021-10-14 23:00 | 44483.9583 | 0 | 10.4037 | 39.95
2021-10-14 23:30 | 44483.9792 | 0 | 9.9956 | 39.95
2021-10-15 | 44484 | 0 | 9.3272 | 39.95
2021-10-15 00:30 | 44484.0208 | 0 | 8.9014 | 39.95
2021-10-15 01:00 | 44484.0417 | 0 | 8.7213 | 39.95
2021-10-15 01:30 | 44484.0625 | 0 | 8.6513 | 39.95
2021-10-15 02:00 | 44484.0833 | 0 | 8.4916 | 39.95
2021-10-15 02:30 | 44484.1042 | 0 | 8.4522 | 39.95
2021-10-15 03:00 | 44484.125 | 0 | 8.279 | 39.95
2021-10-15 03:30 | 44484.1458 | 0 | 8.5944 | 39.95
2021-10-15 04:00 | 44484.1667 | 0 | 8.8199 | 39.95
2021-10-15 04:30 | 44484.1875 | 0 | 9.2876 | 39.95
2021-10-15 05:00 | 44484.2083 | 0 | 9.788 | 39.95
2021-10-15 05:30 | 44484.2292 | 0 | 10.2862 | 39.95
2021-10-15 06:00 | 44484.25 | 0 | 10.9772 | 39.95
2021-10-15 06:30 | 44484.2708 | 0 | 11.8389 | 39.95
2021-10-15 07:00 | 44484.2917 | 0 | 11.8182 | 39.95
2021-10-15 07:30 | 44484.3125 | 0 | 12.8364 | 39.95
2021-10-15 08:00 | 44484.3333 | 0 | 13.3747 | 39.95
2021-10-15 08:30 | 44484.3542 | 0 | 12.6143 | 39.95
2021-10-15 09:00 | 44484.375 | 0 | 10.8176 | 39.95
2021-10-15 09:30 | 44484.3958 | 0 | 12.8177 | 39.95
2021-10-15 10:00 | 44484.4167 | 0 | 12.8487 | 39.95
2021-10-15 10:30 | 44484.4375 | 0 | 12.2257 | 39.95
2021-10-15 11:00 | 44484.4583 | 0 | 11.0837 | 39.95
2021-10-15 11:30 | 44484.4792 | 0 | 10.2805 | 39.95
2021-10-15 12:00 | 44484.5 | 0 | 9.6451 | 39.95
2021-10-15 12:30 | 44484.5208 | 0 | 9.6488 | 39.95
2021-10-15 13:00 | 44484.5417 | 0 | 9.8219 | 39.95
2021-10-15 13:30 | 44484.5625 | 0 | 10.0961 | 39.95
2021-10-15 14:00 | 44484.5833 | 0 | 10.6612 | 39.95
2021-10-15 14:30 | 44484.6042 | 0 | 11.3806 | 39.95
2021-10-15 15:00 | 44484.625 | 0 | 11.9325 | 39.95
2021-10-15 15:30 | 44484.6458 | 0 | 12.8916 | 39.95
2021-10-15 16:00 | 44484.6667 | 0 | 13.4909 | 39.95
2021-10-15 16:30 | 44484.6875 | 0 | 14.0926 | 39.95
2021-10-15 17:00 | 44484.7083 | 0 | 14.1842 | 39.95
2021-10-15 17:30 | 44484.7292 | 0 | 14.3249 | 39.95
2021-10-15 18:00 | 44484.75 | 0 | 14.1835 | 39.95
2021-10-15 18:30 | 44484.7708 | 0 | 14.5877 | 39.95
2021-10-15 19:00 | 44484.7917 | 0 | 14.0862 | 39.95
2021-10-15 19:30 | 44484.8125 | 0 | 13.6156 | 39.95
2021-10-15 20:00 | 44484.8333 | 0 | 12.9939 | 39.95
2021-10-15 20:30 | 44484.8542 | 0 | 12.2691 | 39.95
2021-10-15 21:00 | 44484.875 | 0 | 11.7191 | 39.95
2021-10-15 21:30 | 44484.8958 | 0 | 11.194 | 39.95
2021-10-15 22:00 | 44484.9167 | 0 | 10.6555 | 39.95
2021-10-15 22:30 | 44484.9375 | 0 | 10.0698 | 39.95
2021-10-15 23:00 | 44484.9583 | 0 | 9.4286 | 39.95
2021-10-15 23:30 | 44484.9792 | 0 | 9.047 | 39.95
2021-10-16 | 44485 | 0 | 8.4151 | 39.95
2021-10-16 00:30 | 44485.0208 | 0 | 8.0185 | 39.95
2021-10-16 01:00 | 44485.0417 | 0 | 7.8498 | 39.95
2021-10-16 01:30 | 44485.0625 | 0 | 7.7059 | 39.95
2021-10-16 02:00 | 44485.0833 | 0 | 7.5663 | 39.95
2021-10-16 02:30 | 44485.1042 | 0 | 7.452 | 39.95
2021-10-16 03:00 | 44485.125 | 0 | 7.3322 | 39.95
2021-10-16 03:30 | 44485.1458 | 0 | 7.3553 | 39.95
2021-10-16 04:00 | 44485.1667 | 0 | 7.4275 | 39.95
2021-10-16 04:30 | 44485.1875 | 0 | 7.4554 | 39.95
2021-10-16 05:00 | 44485.2083 | 0 | 7.678 | 39.95
2021-10-16 05:30 | 44485.2292 | 0 | 7.5868 | 39.95
2021-10-16 06:00 | 44485.25 | 0 | 7.4189 | 39.95
2021-10-16 06:30 | 44485.2708 | 0 | 7.1605 | 39.95
2021-10-16 07:00 | 44485.2917 | 0 | 6.8654 | 39.95
2021-10-16 07:30 | 44485.3125 | 0 | 6.5814 | 39.95
2021-10-16 08:00 | 44485.3333 | 0 | 6.341 | 39.95
2021-10-16 08:30 | 44485.3542 | 0 | 6.0004 | 39.95
2021-10-16 09:00 | 44485.375 | 0 | 5.8787 | 39.95
2021-10-16 09:30 | 44485.3958 | 0 | 5.668 | 39.95
2021-10-16 10:00 | 44485.4167 | 0 | 5.3498 | 39.95
2021-10-16 10:30 | 44485.4375 | 0 | 5.2798 | 39.95
2021-10-16 11:00 | 44485.4583 | 0 | 5.1525 | 39.95
2021-10-16 11:30 | 44485.4792 | 0 | 5.2013 | 39.95
2021-10-16 12:00 | 44485.5 | 0 | 5.2292 | 39.95
2021-10-16 12:30 | 44485.5208 | 0 | 5.2571 | 39.95
2021-10-16 13:00 | 44485.5417 | 0 | 5.6289 | 39.95
2021-10-16 13:30 | 44485.5625 | 0 | 5.9178 | 39.95
2021-10-16 14:00 | 44485.5833 | 0 | 6.3401 | 39.95
2021-10-16 14:30 | 44485.6042 | 0 | 6.8022 | 39.95
2021-10-16 15:00 | 44485.625 | 0 | 7.3029 | 39.95
2021-10-16 15:30 | 44485.6458 | 0 | 7.9922 | 39.95
2021-10-16 16:00 | 44485.6667 | 0 | 8.6968 | 39.95
2021-10-16 16:30 | 44485.6875 | 0 | 9.479 | 39.95
2021-10-16 17:00 | 44485.7083 | 0 | 10.0378 | 39.95
2021-10-16 17:30 | 44485.7292 | 0 | 10.4341 | 39.95
2021-10-16 18:00 | 44485.75 | 0 | 10.7115 | 39.95
2021-10-16 18:30 | 44485.7708 | 0 | 11.1031 | 39.95
2021-10-16 19:00 | 44485.7917 | 0 | 10.809 | 39.95
2021-10-16 19:30 | 44485.8125 | 0 | 10.7088 | 39.95
2021-10-16 20:00 | 44485.8333 | 0 | 10.4394 | 39.95
2021-10-16 20:30 | 44485.8542 | 0 | 10.0239 | 39.95
2021-10-16 21:00 | 44485.875 | 0 | 9.6101 | 39.95
2021-10-16 21:30 | 44485.8958 | 0 | 9.3816 | 39.95
2021-10-16 22:00 | 44485.9167 | 0 | 9.1111 | 39.95
2021-10-16 22:30 | 44485.9375 | 0 | 8.5551 | 39.95
2021-10-16 23:00 | 44485.9583 | 0 | 8.1723 | 39.95
2021-10-16 23:30 | 44485.9792 | 0 | 7.9382 | 39.95
2021-10-17 | 44486 | 0 | 7.496 | 39.95
2021-10-17 00:30 | 44486.0208 | 0 | 7.2456 | 39.95
2021-10-17 01:00 | 44486.0417 | 0 | 6.9804 | 39.95
2021-10-17 01:30 | 44486.0625 | 0 | 6.8773 | 39.95
2021-10-17 02:00 | 44486.0833 | 0 | 6.7966 | 39.95
2021-10-17 02:30 | 44486.1042 | 0 | 6.7761 | 39.95
2021-10-17 03:00 | 44486.125 | 0 | 6.7787 | 39.95
2021-10-17 03:30 | 44486.1458 | 0 | 6.8312 | 39.95
2021-10-17 04:00 | 44486.1667 | 0 | 6.7002 | 39.95
2021-10-17 04:30 | 44486.1875 | 0 | 6.7571 | 39.95
2021-10-17 05:00 | 44486.2083 | 0 | 6.7925 | 39.95
2021-10-17 05:30 | 44486.2292 | 0 | 6.6823 | 39.95
2021-10-17 06:00 | 44486.25 | 0 | 6.4884 | 39.95
2021-10-17 06:30 | 44486.2708 | 0 | 6.2453 | 39.95
2021-10-17 07:00 | 44486.2917 | 0 | 5.6689 | 39.95
2021-10-17 07:30 | 44486.3125 | 0 | 5.4157 | 39.95
2021-10-17 08:00 | 44486.3333 | 0 | 5.2556 | 39.95
2021-10-17 08:30 | 44486.3542 | 0 | 5.1607 | 39.95
2021-10-17 09:00 | 44486.375 | 0 | 5.1097 | 39.95
2021-10-17 09:30 | 44486.3958 | 0 | 4.9654 | 39.95
2021-10-17 10:00 | 44486.4167 | 0 | 4.7892 | 39.95
2021-10-17 10:30 | 44486.4375 | 0 | 4.5689 | 39.95
2021-10-17 11:00 | 44486.4583 | 0 | 4.64 | 39.95
2021-10-17 11:30 | 44486.4792 | 0 | 4.7015 | 39.95
2021-10-17 12:00 | 44486.5 | 0 | 4.7167 | 39.95
2021-10-17 12:30 | 44486.5208 | 0 | 4.8045 | 39.95
2021-10-17 13:00 | 44486.5417 | 0 | 5.2603 | 39.95
2021-10-17 13:30 | 44486.5625 | 0 | 5.6628 | 39.95
2021-10-17 14:00 | 44486.5833 | 0 | 6.164 | 39.95
2021-10-17 14:30 | 44486.6042 | 0 | 6.8139 | 39.95
2021-10-17 15:00 | 44486.625 | 0 | 7.519 | 39.95
2021-10-17 15:30 | 44486.6458 | 0 | 8.2813 | 39.95
2021-10-17 16:00 | 44486.6667 | 0 | 8.9414 | 39.95
2021-10-17 16:30 | 44486.6875 | 0 | 9.8102 | 39.95
2021-10-17 17:00 | 44486.7083 | 0 | 10.5604 | 39.95
2021-10-17 17:30 | 44486.7292 | 0 | 10.8829 | 39.95
2021-10-17 18:00 | 44486.75 | 0 | 11.3982 | 39.95
2021-10-17 18:30 | 44486.7708 | 0 | 11.8554 | 39.95
2021-10-17 19:00 | 44486.7917 | 0 | 11.4883 | 39.95
2021-10-17 19:30 | 44486.8125 | 0 | 11.1522 | 39.95
2021-10-17 20:00 | 44486.8333 | 0 | 10.7402 | 39.95
2021-10-17 20:30 | 44486.8542 | 0 | 10.5038 | 39.95
2021-10-17 21:00 | 44486.875 | 0 | 9.9451 | 39.95
2021-10-17 21:30 | 44486.8958 | 0 | 9.7307 | 39.95
2021-10-17 22:00 | 44486.9167 | 0 | 9.094 | 39.95
2021-10-17 22:30 | 44486.9375 | 0 | 8.5166 | 39.95
2021-10-17 23:00 | 44486.9583 | 0 | 8.0478 | 39.95
2021-10-17 23:30 | 44486.9792 | 0 | 7.6307 | 39.95
2021-10-18 | 44487 | 0 | 7.3263 | 39.95
2021-10-18 00:30 | 44487.0208 | 0 | 7.2324 | 39.95
2021-10-18 01:00 | 44487.0417 | 0 | 7.0512 | 39.95
2021-10-18 01:30 | 44487.0625 | 0 | 6.983 | 39.95
2021-10-18 02:00 | 44487.0833 | 0 | 7.0043 | 39.95
2021-10-18 02:30 | 44487.1042 | 0 | 7.0917 | 39.95
2021-10-18 03:00 | 44487.125 | 0 | 7.0203 | 39.95
2021-10-18 03:30 | 44487.1458 | 0 | 7.2916 | 39.95
2021-10-18 04:00 | 44487.1667 | 0 | 7.5541 | 39.95
2021-10-18 04:30 | 44487.1875 | 0 | 7.9043 | 39.95
2021-10-18 05:00 | 44487.2083 | 0 | 8.4946 | 39.95
2021-10-18 05:30 | 44487.2292 | 0 | 9.0964 | 39.95
2021-10-18 06:00 | 44487.25 | 0 | 9.4939 | 39.95
2021-10-18 06:30 | 44487.2708 | 0 | 10.0558 | 39.95
2021-10-18 07:00 | 44487.2917 | 0 | 9.3935 | 39.95
2021-10-18 07:30 | 44487.3125 | 0 | 10.5123 | 39.95
2021-10-18 08:00 | 44487.3333 | 0 | 10.3039 | 39.95
2021-10-18 08:30 | 44487.3542 | 0 | 10.7252 | 39.95
2021-10-18 09:00 | 44487.375 | 0 | 11.4427 | 39.95
2021-10-18 09:30 | 44487.3958 | 0 | 11.0179 | 39.95
2021-10-18 10:00 | 44487.4167 | 0 | 9.7945 | 39.95
2021-10-18 10:30 | 44487.4375 | 0 | 10.546 | 39.95
2021-10-18 11:00 | 44487.4583 | 0 | 11.3391 | 39.95
2021-10-18 11:30 | 44487.4792 | 0 | 10.3689 | 39.95
2021-10-18 12:00 | 44487.5 | 0 | 11.1465 | 39.95
2021-10-18 12:30 | 44487.5208 | 0 | 12.7508 | 39.95
2021-10-18 13:00 | 44487.5417 | 0 | 11.6055 | 39.95
2021-10-18 13:30 | 44487.5625 | 0 | 12.8676 | 39.95
2021-10-18 14:00 | 44487.5833 | 0 | 12.7253 | 39.95
2021-10-18 14:30 | 44487.6042 | 0 | 13.3265 | 39.95
2021-10-18 15:00 | 44487.625 | 0 | 13.2629 | 39.95
2021-10-18 15:30 | 44487.6458 | 0 | 13.5443 | 39.95
2021-10-18 16:00 | 44487.6667 | 0 | 12.8617 | 39.95
2021-10-18 16:30 | 44487.6875 | 0 | 12.6734 | 39.95
2021-10-18 17:00 | 44487.7083 | 0 | 12.9343 | 39.95
2021-10-18 17:30 | 44487.7292 | 0 | 13.1644 | 39.95
2021-10-18 18:00 | 44487.75 | 0 | 13.3806 | 39.95
2021-10-18 18:30 | 44487.7708 | 0 | 13.5965 | 39.95
2021-10-18 19:00 | 44487.7917 | 0 | 13.1033 | 39.95
2021-10-18 19:30 | 44487.8125 | 0 | 12.8524 | 39.95
2021-10-18 20:00 | 44487.8333 | 0 | 12.2833 | 39.95
2021-10-18 20:30 | 44487.8542 | 0 | 11.8628 | 39.95
2021-10-18 21:00 | 44487.875 | 0 | 11.2761 | 39.95
2021-10-18 21:30 | 44487.8958 | 0 | 10.9084 | 39.95
2021-10-18 22:00 | 44487.9167 | 0 | 10.3835 | 39.95
2021-10-18 22:30 | 44487.9375 | 0 | 9.5837 | 39.95
2021-10-18 23:00 | 44487.9583 | 0 | 9.0167 | 39.95
2021-10-18 23:30 | 44487.9792 | 0 | 8.5396 | 39.95
2021-10-19 | 44488 | 0 | 8.1347 | 39.95
2021-10-19 00:30 | 44488.0208 | 0 | 7.8957 | 39.95
2021-10-19 01:00 | 44488.0417 | 0 | 7.6323 | 39.95
2021-10-19 01:30 | 44488.0625 | 0 | 7.4811 | 39.95
2021-10-19 02:00 | 44488.0833 | 0 | 7.5027 | 39.95
2021-10-19 02:30 | 44488.1042 | 0 | 7.4442 | 39.95
2021-10-19 03:00 | 44488.125 | 0 | 7.4156 | 39.95
2021-10-19 03:30 | 44488.1458 | 0 | 7.6218 | 39.95
2021-10-19 04:00 | 44488.1667 | 0 | 7.6488 | 39.95
2021-10-19 04:30 | 44488.1875 | 0 | 8.2787 | 39.95
2021-10-19 05:00 | 44488.2083 | 0 | 8.7467 | 39.95
2021-10-19 05:30 | 44488.2292 | 0 | 9.2096 | 39.95
2021-10-19 06:00 | 44488.25 | 0 | 9.364 | 39.95
2021-10-19 06:30 | 44488.2708 | 0 | 10.375 | 39.95
2021-10-19 07:00 | 44488.2917 | 0 | 10.4119 | 39.95
2021-10-19 07:30 | 44488.3125 | 0 | 10.5975 | 39.95
2021-10-19 08:00 | 44488.3333 | 0 | 8.7579 | 39.95
2021-10-19 08:30 | 44488.3542 | 0 | 8.4597 | 39.95
2021-10-19 09:00 | 44488.375 | 0 | 8.1194 | 39.95
2021-10-19 09:30 | 44488.3958 | 0 | 8.2467 | 39.95
2021-10-19 10:00 | 44488.4167 | 0 | 7.9028 | 39.95
2021-10-19 10:30 | 44488.4375 | 0 | 8.2184 | 39.95
2021-10-19 11:00 | 44488.4583 | 0 | 8.1388 | 39.95
2021-10-19 11:30 | 44488.4792 | 0 | 8.2206 | 39.95
2021-10-19 12:00 | 44488.5 | 0 | 8.2229 | 39.95
2021-10-19 12:30 | 44488.5208 | 0 | 8.654 | 39.95
2021-10-19 13:00 | 44488.5417 | 0 | 8.8929 | 39.95
2021-10-19 13:30 | 44488.5625 | 0 | 9.5331 | 39.95
2021-10-19 14:00 | 44488.5833 | 0 | 10.2827 | 39.95
2021-10-19 14:30 | 44488.6042 | 0 | 10.6664 | 39.95
2021-10-19 15:00 | 44488.625 | 0 | 11.1834 | 39.95
2021-10-19 15:30 | 44488.6458 | 0 | 11.4217 | 39.95
2021-10-19 16:00 | 44488.6667 | 0 | 12.4703 | 39.95
2021-10-19 16:30 | 44488.6875 | 0 | 12.8773 | 39.95
2021-10-19 17:00 | 44488.7083 | 0 | 13.4335 | 39.95
2021-10-19 17:30 | 44488.7292 | 0 | 13.7187 | 39.95
2021-10-19 18:00 | 44488.75 | 0 | 13.9174 | 39.95
2021-10-19 18:30 | 44488.7708 | 0 | 14.3078 | 39.95
2021-10-19 19:00 | 44488.7917 | 0 | 14.1217 | 39.95
2021-10-19 19:30 | 44488.8125 | 0 | 13.866 | 39.95
2021-10-19 20:00 | 44488.8333 | 0 | 13.3409 | 39.95
2021-10-19 20:30 | 44488.8542 | 0 | 12.6699 | 39.95
2021-10-19 21:00 | 44488.875 | 0 | 12.2335 | 39.95
2021-10-19 21:30 | 44488.8958 | 0 | 11.805 | 39.95
2021-10-19 22:00 | 44488.9167 | 0 | 11.1136 | 39.95
2021-10-19 22:30 | 44488.9375 | 0 | 10.1482 | 39.95
2021-10-19 23:00 | 44488.9583 | 0 | 9.445 | 39.95
2021-10-19 23:30 | 44488.9792 | 0 | 8.863 | 39.95
2021-10-20 | 44489 | 0 | 8.5672 | 39.95
2021-10-20 00:30 | 44489.0208 | 0 | 8.3106 | 39.95
2021-10-20 01:00 | 44489.0417 | 0 | 8.1001 | 39.95
2021-10-20 01:30 | 44489.0625 | 0 | 7.876 | 39.95
2021-10-20 02:00 | 44489.0833 | 0 | 7.9791 | 39.95
2021-10-20 02:30 | 44489.1042 | 0 | 7.8726 | 39.95
2021-10-20 03:00 | 44489.125 | 0 | 7.7781 | 39.95
2021-10-20 03:30 | 44489.1458 | 0 | 7.9925 | 39.95
2021-10-20 04:00 | 44489.1667 | 0 | 8.1038 | 39.95
2021-10-20 04:30 | 44489.1875 | 0 | 8.4708 | 39.95
2021-10-20 05:00 | 44489.2083 | 0 | 9.0194 | 39.95
2021-10-20 05:30 | 44489.2292 | 0 | 9.5152 | 39.95
2021-10-20 06:00 | 44489.25 | 0 | 10.1487 | 39.95
2021-10-20 06:30 | 44489.2708 | 0 | 10.3884 | 39.95
2021-10-20 07:00 | 44489.2917 | 0 | 10.5142 | 39.95
2021-10-20 07:30 | 44489.3125 | 0 | 10.3307 | 39.95
2021-10-20 08:00 | 44489.3333 | 0 | 9.9306 | 39.95
2021-10-20 08:30 | 44489.3542 | 0 | 9.7743 | 39.95
2021-10-20 09:00 | 44489.375 | 0 | 9.644 | 39.95
2021-10-20 09:30 | 44489.3958 | 0 | 9.9622 | 39.95
2021-10-20 10:00 | 44489.4167 | 0 | 9.7482 | 39.95
2021-10-20 10:30 | 44489.4375 | 0 | 9.7728 | 39.95
2021-10-20 11:00 | 44489.4583 | 0 | 9.7932 | 39.95
2021-10-20 11:30 | 44489.4792 | 0 | 9.8353 | 39.95
2021-10-20 12:00 | 44489.5 | 0 | 9.845 | 39.95
2021-10-20 12:30 | 44489.5208 | 0 | 10.8558 | 39.95
2021-10-20 13:00 | 44489.5417 | 0 | 9.8033 | 39.95
2021-10-20 13:30 | 44489.5625 | 0 | 10.7507 | 39.95
2021-10-20 14:00 | 44489.5833 | 0 | 12.5657 | 39.95
2021-10-20 14:30 | 44489.6042 | 0 | 13.1631 | 39.95
2021-10-20 15:00 | 44489.625 | 0 | 13.1864 | 39.95
2021-10-20 15:30 | 44489.6458 | 0 | 12.6135 | 39.95
2021-10-20 16:00 | 44489.6667 | 0 | 13.082 | 39.95
2021-10-20 16:30 | 44489.6875 | 0 | 13.0899 | 39.95
2021-10-20 17:00 | 44489.7083 | 0 | 13.589 | 39.95
2021-10-20 17:30 | 44489.7292 | 0 | 13.9173 | 39.95
2021-10-20 18:00 | 44489.75 | 0 | 14.3651 | 39.95
2021-10-20 18:30 | 44489.7708 | 0 | 14.4752 | 39.95
2021-10-20 19:00 | 44489.7917 | 0 | 14.1275 | 39.95
2021-10-20 19:30 | 44489.8125 | 0 | 13.9054 | 39.95
2021-10-20 20:00 | 44489.8333 | 0 | 13.3423 | 39.95
2021-10-20 20:30 | 44489.8542 | 0 | 12.4943 | 39.95
2021-10-20 21:00 | 44489.875 | 0 | 11.8694 | 39.95
2021-10-20 21:30 | 44489.8958 | 0 | 11.5062 | 39.95
2021-10-20 22:00 | 44489.9167 | 0 | 10.9566 | 39.95
2021-10-20 22:30 | 44489.9375 | 0 | 10.0898 | 39.95
2021-10-20 23:00 | 44489.9583 | 0 | 9.526 | 39.95
2021-10-20 23:30 | 44489.9792 | 0 | 9.0771 | 39.95
2021-10-21 | 44490 | 0 | 8.6219 | 39.95
2021-10-21 00:30 | 44490.0208 | 0 | 8.2448 | 39.95
2021-10-21 01:00 | 44490.0417 | 0 | 8.0755 | 39.95
2021-10-21 01:30 | 44490.0625 | 0 | 8.0089 | 39.95
2021-10-21 02:00 | 44490.0833 | 0 | 7.9288 | 39.95
2021-10-21 02:30 | 44490.1042 | 0 | 7.7161 | 39.95
2021-10-21 03:00 | 44490.125 | 0 | 7.6772 | 39.95
2021-10-21 03:30 | 44490.1458 | 0 | 7.9329 | 39.95
2021-10-21 04:00 | 44490.1667 | 0 | 8.0702 | 39.95
2021-10-21 04:30 | 44490.1875 | 0 | 8.3788 | 39.95
2021-10-21 05:00 | 44490.2083 | 0 | 8.9917 | 39.95
2021-10-21 05:30 | 44490.2292 | 0 | 9.3898 | 39.95
2021-10-21 06:00 | 44490.25 | 0 | 9.8163 | 39.95
2021-10-21 06:30 | 44490.2708 | 0 | 10.4695 | 39.95
2021-10-21 07:00 | 44490.2917 | 0 | 10.582 | 39.95
2021-10-21 07:30 | 44490.3125 | 0 | 10.0904 | 39.95
2021-10-21 08:00 | 44490.3333 | 0 | 10.1905 | 39.95
2021-10-21 08:30 | 44490.3542 | 0 | 11.1771 | 39.95
2021-10-21 09:00 | 44490.375 | 0 | 11.1276 | 39.95
2021-10-21 09:30 | 44490.3958 | 0 | 11.0513 | 39.95
2021-10-21 10:00 | 44490.4167 | 0 | 10.5788 | 39.95
2021-10-21 10:30 | 44490.4375 | 0 | 10.6324 | 39.95
2021-10-21 11:00 | 44490.4583 | 0 | 10.5692 | 39.95
2021-10-21 11:30 | 44490.4792 | 0 | 10.9778 | 39.95
2021-10-21 12:00 | 44490.5 | 0 | 10.8696 | 39.95
2021-10-21 12:30 | 44490.5208 | 0 | 12.1996 | 39.95
2021-10-21 13:00 | 44490.5417 | 0 | 13.0265 | 39.95
2021-10-21 13:30 | 44490.5625 | 0 | 11.8152 | 39.95
2021-10-21 14:00 | 44490.5833 | 0 | 12.108 | 39.95
2021-10-21 14:30 | 44490.6042 | 0 | 12.8291 | 39.95
2021-10-21 15:00 | 44490.625 | 0 | 10.2145 | 39.95
2021-10-21 15:30 | 44490.6458 | 0 | 11.891 | 39.95
2021-10-21 16:00 | 44490.6667 | 0 | 13.1714 | 39.95
2021-10-21 16:30 | 44490.6875 | 0 | 13.3828 | 39.95
2021-10-21 17:00 | 44490.7083 | 0 | 13.7312 | 39.95
2021-10-21 17:30 | 44490.7292 | 0 | 14.065 | 39.95
2021-10-21 18:00 | 44490.75 | 0 | 13.9802 | 39.95
2021-10-21 18:30 | 44490.7708 | 0 | 14.0975 | 39.95
2021-10-21 19:00 | 44490.7917 | 0 | 13.6336 | 39.95
2021-10-21 19:30 | 44490.8125 | 0 | 13.4904 | 39.95
2021-10-21 20:00 | 44490.8333 | 0 | 13.1528 | 39.95
2021-10-21 20:30 | 44490.8542 | 0 | 12.5191 | 39.95
2021-10-21 21:00 | 44490.875 | 0 | 11.91 | 39.95
2021-10-21 21:30 | 44490.8958 | 0 | 11.9584 | 39.95
2021-10-21 22:00 | 44490.9167 | 0 | 11.2732 | 39.95
2021-10-21 22:30 | 44490.9375 | 0 | 10.4061 | 39.95
2021-10-21 23:00 | 44490.9583 | 0 | 9.8246 | 39.95
2021-10-21 23:30 | 44490.9792 | 0 | 9.3399 | 39.95
2021-10-22 | 44491 | 0 | 8.7975 | 39.95
2021-10-22 00:30 | 44491.0208 | 0 | 8.4784 | 39.95
2021-10-22 01:00 | 44491.0417 | 0 | 8.3074 | 39.95
2021-10-22 01:30 | 44491.0625 | 0 | 8.1648 | 39.95
2021-10-22 02:00 | 44491.0833 | 0 | 8.1131 | 39.95
2021-10-22 02:30 | 44491.1042 | 0 | 8.0554 | 39.95
2021-10-22 03:00 | 44491.125 | 0 | 8.0316 | 39.95
2021-10-22 03:30 | 44491.1458 | 0 | 8.176 | 39.95
2021-10-22 04:00 | 44491.1667 | 0 | 8.278 | 39.95
2021-10-22 04:30 | 44491.1875 | 0 | 8.8658 | 39.95
2021-10-22 05:00 | 44491.2083 | 0 | 9.3566 | 39.95
2021-10-22 05:30 | 44491.2292 | 0 | 9.8394 | 39.95
2021-10-22 06:00 | 44491.25 | 0 | 10.5893 | 39.95
2021-10-22 06:30 | 44491.2708 | 0 | 11.0338 | 39.95
2021-10-22 07:00 | 44491.2917 | 0 | 11.3666 | 39.95
2021-10-22 07:30 | 44491.3125 | 0 | 12.0632 | 39.95
2021-10-22 08:00 | 44491.3333 | 0 | 12.5613 | 39.95
2021-10-22 08:30 | 44491.3542 | 0 | 13.5743 | 39.95
2021-10-22 09:00 | 44491.375 | 0 | 14.3152 | 39.95
2021-10-22 09:30 | 44491.3958 | 0 | 14.3707 | 39.95
2021-10-22 10:00 | 44491.4167 | 0 | 13.0402 | 39.95
2021-10-22 10:30 | 44491.4375 | 0 | 11.0318 | 39.95
2021-10-22 11:00 | 44491.4583 | 0 | 9.3825 | 39.95
2021-10-22 11:30 | 44491.4792 | 0 | 9.2112 | 39.95
2021-10-22 12:00 | 44491.5 | 0 | 8.8849 | 39.95
2021-10-22 12:30 | 44491.5208 | 0 | 10.4328 | 39.95
2021-10-22 13:00 | 44491.5417 | 0 | 11.8301 | 39.95
2021-10-22 13:30 | 44491.5625 | 0 | 10.5655 | 39.95
2021-10-22 14:00 | 44491.5833 | 0 | 10.4774 | 39.95
2021-10-22 14:30 | 44491.6042 | 0 | 10.8505 | 39.95
2021-10-22 15:00 | 44491.625 | 0 | 11.5723 | 39.95
2021-10-22 15:30 | 44491.6458 | 0 | 12.5395 | 39.95
2021-10-22 16:00 | 44491.6667 | 0 | 12.9533 | 39.95
2021-10-22 16:30 | 44491.6875 | 0 | 13.4045 | 39.95
2021-10-22 17:00 | 44491.7083 | 0 | 13.5998 | 39.95
2021-10-22 17:30 | 44491.7292 | 0 | 13.7682 | 39.95
2021-10-22 18:00 | 44491.75 | 0 | 14.0141 | 39.95
2021-10-22 18:30 | 44491.7708 | 0 | 14.125 | 39.95
2021-10-22 19:00 | 44491.7917 | 0 | 13.6054 | 39.95
2021-10-22 19:30 | 44491.8125 | 0 | 13.5388 | 39.95
2021-10-22 20:00 | 44491.8333 | 0 | 13.1323 | 39.95
2021-10-22 20:30 | 44491.8542 | 0 | 12.9646 | 39.95
2021-10-22 21:00 | 44491.875 | 0 | 12.6302 | 39.95
2021-10-22 21:30 | 44491.8958 | 0 | 12.2178 | 39.95
2021-10-22 22:00 | 44491.9167 | 0 | 11.863 | 39.95
2021-10-22 22:30 | 44491.9375 | 0 | 10.9854 | 39.95
2021-10-22 23:00 | 44491.9583 | 0 | 10.4279 | 39.95
2021-10-22 23:30 | 44491.9792 | 0 | 9.9267 | 39.95
2021-10-23 | 44492 | 0 | 9.2996 | 39.95
2021-10-23 00:30 | 44492.0208 | 0 | 8.8808 | 39.95
2021-10-23 01:00 | 44492.0417 | 0 | 8.5396 | 39.95
2021-10-23 01:30 | 44492.0625 | 0 | 8.4015 | 39.95
2021-10-23 02:00 | 44492.0833 | 0 | 8.2512 | 39.95
2021-10-23 02:30 | 44492.1042 | 0 | 8.037 | 39.95
2021-10-23 03:00 | 44492.125 | 0 | 7.9091 | 39.95
2021-10-23 03:30 | 44492.1458 | 0 | 7.9608 | 39.95
2021-10-23 04:00 | 44492.1667 | 0 | 7.9917 | 39.95
2021-10-23 04:30 | 44492.1875 | 0 | 8.2723 | 39.95
2021-10-23 05:00 | 44492.2083 | 0 | 8.4303 | 39.95
2021-10-23 05:30 | 44492.2292 | 0 | 8.511 | 39.95
2021-10-23 06:00 | 44492.25 | 0 | 8.7242 | 39.95
2021-10-23 06:30 | 44492.2708 | 0 | 8.9512 | 39.95
2021-10-23 07:00 | 44492.2917 | 0 | 9.0437 | 39.95
2021-10-23 07:30 | 44492.3125 | 0 | 9.0289 | 39.95
2021-10-23 08:00 | 44492.3333 | 0 | 10.1623 | 39.95
2021-10-23 08:30 | 44492.3542 | 0 | 10.1287 | 39.95
2021-10-23 09:00 | 44492.375 | 0 | 10.6107 | 39.95
2021-10-23 09:30 | 44492.3958 | 0 | 10.0832 | 39.95
2021-10-23 10:00 | 44492.4167 | 0 | 9.161 | 39.95
2021-10-23 10:30 | 44492.4375 | 0 | 9.6342 | 39.95
2021-10-23 11:00 | 44492.4583 | 0 | 8.9911 | 39.95
2021-10-23 11:30 | 44492.4792 | 0 | 9.0447 | 39.95
2021-10-23 12:00 | 44492.5 | 0 | 8.4056 | 39.95
2021-10-23 12:30 | 44492.5208 | 0 | 8.6368 | 39.95
2021-10-23 13:00 | 44492.5417 | 0 | 9.0181 | 39.95
2021-10-23 13:30 | 44492.5625 | 0 | 9.5118 | 39.95
2021-10-23 14:00 | 44492.5833 | 0 | 10.0451 | 39.95
2021-10-23 14:30 | 44492.6042 | 0 | 10.3657 | 39.95
2021-10-23 15:00 | 44492.625 | 0 | 11.014 | 39.95
2021-10-23 15:30 | 44492.6458 | 0 | 11.6799 | 39.95
2021-10-23 16:00 | 44492.6667 | 0 | 13.3455 | 39.95
2021-10-23 16:30 | 44492.6875 | 0 | 13.2555 | 39.95
2021-10-23 17:00 | 44492.7083 | 0 | 12.6922 | 39.95
2021-10-23 17:30 | 44492.7292 | 0 | 12.9278 | 39.95
2021-10-23 18:00 | 44492.75 | 0 | 13.0232 | 39.95
2021-10-23 18:30 | 44492.7708 | 0 | 13.4297 | 39.95
2021-10-23 19:00 | 44492.7917 | 0 | 13.2983 | 39.95
2021-10-23 19:30 | 44492.8125 | 0 | 12.9957 | 39.95
2021-10-23 20:00 | 44492.8333 | 0 | 12.7894 | 39.95
2021-10-23 20:30 | 44492.8542 | 0 | 12.3574 | 39.95
2021-10-23 21:00 | 44492.875 | 0 | 11.9957 | 39.95
2021-10-23 21:30 | 44492.8958 | 0 | 11.623 | 39.95
2021-10-23 22:00 | 44492.9167 | 0 | 11.1051 | 39.95
2021-10-23 22:30 | 44492.9375 | 0 | 10.4057 | 39.95
2021-10-23 23:00 | 44492.9583 | 0 | 9.917 | 39.95
2021-10-23 23:30 | 44492.9792 | 0 | 9.5978 | 39.95
2021-10-24 | 44493 | 0 | 9.0609 | 39.95
2021-10-24 00:30 | 44493.0208 | 0 | 8.7589 | 39.95
2021-10-24 01:00 | 44493.0417 | 0 | 8.5506 | 39.95
2021-10-24 01:30 | 44493.0625 | 0 | 8.2586 | 39.95
2021-10-24 02:00 | 44493.0833 | 0 | 8.1857 | 39.95
2021-10-24 02:30 | 44493.1042 | 0 | 7.9452 | 39.95
2021-10-24 03:00 | 44493.125 | 0 | 7.9236 | 39.95
2021-10-24 03:30 | 44493.1458 | 0 | 7.905 | 39.95
2021-10-24 04:00 | 44493.1667 | 0 | 7.7904 | 39.95
2021-10-24 04:30 | 44493.1875 | 0 | 7.7393 | 39.95
2021-10-24 05:00 | 44493.2083 | 0 | 7.6664 | 39.95
2021-10-24 05:30 | 44493.2292 | 0 | 7.5883 | 39.95
2021-10-24 06:00 | 44493.25 | 0 | 7.452 | 39.95
2021-10-24 06:30 | 44493.2708 | 0 | 7.1536 | 39.95
2021-10-24 07:00 | 44493.2917 | 0 | 7.6356 | 39.95
2021-10-24 07:30 | 44493.3125 | 0 | 7.2796 | 39.95
2021-10-24 08:00 | 44493.3333 | 0 | 7.5773 | 39.95
2021-10-24 08:30 | 44493.3542 | 0 | 7.5508 | 39.95
2021-10-24 09:00 | 44493.375 | 0 | 7.6422 | 39.95
2021-10-24 09:30 | 44493.3958 | 0 | 7.9407 | 39.95
2021-10-24 10:00 | 44493.4167 | 0 | 7.927 | 39.95
2021-10-24 10:30 | 44493.4375 | 0 | 8.0712 | 39.95
2021-10-24 11:00 | 44493.4583 | 0 | 8.3729 | 39.95
2021-10-24 11:30 | 44493.4792 | 0 | 8.5019 | 39.95
2021-10-24 12:00 | 44493.5 | 0 | 8.9905 | 39.95
2021-10-24 12:30 | 44493.5208 | 0 | 9.1813 | 39.95
2021-10-24 13:00 | 44493.5417 | 0 | 10.2671 | 39.95
2021-10-24 13:30 | 44493.5625 | 0 | 10.5591 | 39.95
2021-10-24 14:00 | 44493.5833 | 0 | 11.5506 | 39.95
2021-10-24 14:30 | 44493.6042 | 0 | 11.8587 | 39.95
2021-10-24 15:00 | 44493.625 | 0 | 13.5139 | 39.95
2021-10-24 15:30 | 44493.6458 | 0 | 14.5899 | 39.95
2021-10-24 16:00 | 44493.6667 | 0 | 14.2408 | 39.95
2021-10-24 16:30 | 44493.6875 | 0 | 14.4381 | 39.95
2021-10-24 17:00 | 44493.7083 | 0 | 14.4369 | 39.95
2021-10-24 17:30 | 44493.7292 | 0 | 15.1259 | 39.95
2021-10-24 18:00 | 44493.75 | 0 | 15.6052 | 39.95
2021-10-24 18:30 | 44493.7708 | 0 | 16.0464 | 39.95
2021-10-24 19:00 | 44493.7917 | 0 | 15.5056 | 39.95
2021-10-24 19:30 | 44493.8125 | 0 | 15.1018 | 39.95
2021-10-24 20:00 | 44493.8333 | 0 | 14.379 | 39.95
2021-10-24 20:30 | 44493.8542 | 0 | 13.7983 | 39.95
2021-10-24 21:00 | 44493.875 | 0 | 13.0697 | 39.95
2021-10-24 21:30 | 44493.8958 | 0 | 12.3528 | 39.95
2021-10-24 22:00 | 44493.9167 | 0 | 11.4395 | 39.95
2021-10-24 22:30 | 44493.9375 | 0 | 10.3656 | 39.95
2021-10-24 23:00 | 44493.9583 | 0 | 9.6148 | 39.95
2021-10-24 23:30 | 44493.9792 | 0 | 9.3808 | 39.95
2021-10-25 | 44494 | 0 | 8.8878 | 39.95
2021-10-25 00:30 | 44494.0208 | 0 | 8.7085 | 39.95
2021-10-25 01:00 | 44494.0417 | 0 | 8.3997 | 39.95
2021-10-25 01:30 | 44494.0625 | 0 | 8.3077 | 39.95
2021-10-25 02:00 | 44494.0833 | 0 | 8.2437 | 39.95
2021-10-25 02:30 | 44494.1042 | 0 | 8.1959 | 39.95
2021-10-25 03:00 | 44494.125 | 0 | 8.0714 | 39.95
2021-10-25 03:30 | 44494.1458 | 0 | 8.4086 | 39.95
2021-10-25 04:00 | 44494.1667 | 0 | 8.6293 | 39.95
2021-10-25 04:30 | 44494.1875 | 0 | 8.9316 | 39.95
2021-10-25 05:00 | 44494.2083 | 0 | 9.5229 | 39.95
2021-10-25 05:30 | 44494.2292 | 0 | 9.9712 | 39.95
2021-10-25 06:00 | 44494.25 | 0 | 10.9298 | 39.95
2021-10-25 06:30 | 44494.2708 | 0 | 11.4653 | 39.95
2021-10-25 07:00 | 44494.2917 | 0 | 11.9047 | 39.95
2021-10-25 07:30 | 44494.3125 | 0 | 12.0931 | 39.95
2021-10-25 08:00 | 44494.3333 | 0 | 12.233 | 39.95
2021-10-25 08:30 | 44494.3542 | 0 | 11.4879 | 39.95
2021-10-25 09:00 | 44494.375 | 0 | 11.792 | 39.95
2021-10-25 09:30 | 44494.3958 | 0 | 12.9461 | 39.95
2021-10-25 10:00 | 44494.4167 | 0 | 11.7911 | 39.95
2021-10-25 10:30 | 44494.4375 | 0 | 12.3471 | 39.95
2021-10-25 11:00 | 44494.4583 | 0 | 12.5865 | 39.95
2021-10-25 11:30 | 44494.4792 | 0 | 14.799 | 39.95
2021-10-25 12:00 | 44494.5 | 0 | 15.3195 | 39.95
2021-10-25 12:30 | 44494.5208 | 0 | 14.9068 | 39.95
2021-10-25 13:00 | 44494.5417 | 0 | 14.4244 | 39.95
2021-10-25 13:30 | 44494.5625 | 0 | 13.7757 | 39.95
2021-10-25 14:00 | 44494.5833 | 0 | 12.7654 | 39.95
2021-10-25 14:30 | 44494.6042 | 0 | 13.3833 | 39.95
2021-10-25 15:00 | 44494.625 | 0 | 13.0277 | 39.95
2021-10-25 15:30 | 44494.6458 | 0 | 13.3923 | 39.95
2021-10-25 16:00 | 44494.6667 | 0 | 13.8706 | 39.95
2021-10-25 16:30 | 44494.6875 | 0 | 14.1173 | 39.95
2021-10-25 17:00 | 44494.7083 | 0 | 14.5039 | 39.95
2021-10-25 17:30 | 44494.7292 | 0 | 14.8989 | 39.95
2021-10-25 18:00 | 44494.75 | 0 | 15.0154 | 39.95
2021-10-25 18:30 | 44494.7708 | 0 | 15.0195 | 39.95
2021-10-25 19:00 | 44494.7917 | 0 | 14.777 | 39.95
2021-10-25 19:30 | 44494.8125 | 0 | 14.2691 | 39.95
2021-10-25 20:00 | 44494.8333 | 0 | 13.8443 | 39.95
2021-10-25 20:30 | 44494.8542 | 0 | 13.2683 | 39.95
2021-10-25 21:00 | 44494.875 | 0 | 12.6935 | 39.95
2021-10-25 21:30 | 44494.8958 | 0 | 12.277 | 39.95
2021-10-25 22:00 | 44494.9167 | 0 | 11.7366 | 39.95
2021-10-25 22:30 | 44494.9375 | 0 | 10.9092 | 39.95
2021-10-25 23:00 | 44494.9583 | 0 | 10.2603 | 39.95
2021-10-25 23:30 | 44494.9792 | 0 | 9.6282 | 39.95
2021-10-26 | 44495 | 0 | 9.2357 | 39.95
2021-10-26 00:30 | 44495.0208 | 0 | 8.7005 | 39.95
2021-10-26 01:00 | 44495.0417 | 0 | 8.5817 | 39.95
2021-10-26 01:30 | 44495.0625 | 0 | 8.5192 | 39.95
2021-10-26 02:00 | 44495.0833 | 0 | 8.4217 | 39.95
2021-10-26 02:30 | 44495.1042 | 0 | 8.3628 | 39.95
2021-10-26 03:00 | 44495.125 | 0 | 8.3066 | 39.95
2021-10-26 03:30 | 44495.1458 | 0 | 8.4946 | 39.95
2021-10-26 04:00 | 44495.1667 | 0 | 8.6826 | 39.95
2021-10-26 04:30 | 44495.1875 | 0 | 9.2389 | 39.95
2021-10-26 05:00 | 44495.2083 | 0 | 9.7411 | 39.95
2021-10-26 05:30 | 44495.2292 | 0 | 10.2291 | 39.95
2021-10-26 06:00 | 44495.25 | 0 | 10.6608 | 39.95
2021-10-26 06:30 | 44495.2708 | 0 | 11.5988 | 39.95
2021-10-26 07:00 | 44495.2917 | 0 | 12.054 | 39.95
2021-10-26 07:30 | 44495.3125 | 0 | 12.3579 | 39.95
2021-10-26 08:00 | 44495.3333 | 0 | 12.3325 | 39.95
2021-10-26 08:30 | 44495.3542 | 0 | 13.1286 | 39.95
2021-10-26 09:00 | 44495.375 | 0 | 13.5198 | 39.95
2021-10-26 09:30 | 44495.3958 | 0 | 13.4737 | 39.95
2021-10-26 10:00 | 44495.4167 | 0 | 11.7395 | 39.95
2021-10-26 10:30 | 44495.4375 | 0 | 10.9531 | 39.95
2021-10-26 11:00 | 44495.4583 | 0 | 11.3806 | 39.95
2021-10-26 11:30 | 44495.4792 | 0 | 12.2932 | 39.95
2021-10-26 12:00 | 44495.5 | 0 | 12.667 | 39.95
2021-10-26 12:30 | 44495.5208 | 0 | 11.7837 | 39.95
2021-10-26 13:00 | 44495.5417 | 0 | 11.8336 | 39.95
2021-10-26 13:30 | 44495.5625 | 0 | 13.0758 | 39.95
2021-10-26 14:00 | 44495.5833 | 0 | 13.2614 | 39.95
2021-10-26 14:30 | 44495.6042 | 0 | 12.9912 | 39.95
2021-10-26 15:00 | 44495.625 | 0 | 13.6204 | 39.95
2021-10-26 15:30 | 44495.6458 | 0 | 14.3201 | 39.95
2021-10-26 16:00 | 44495.6667 | 0 | 14.2274 | 39.95
2021-10-26 16:30 | 44495.6875 | 0 | 14.1876 | 39.95
2021-10-26 17:00 | 44495.7083 | 0 | 14.3279 | 39.95
2021-10-26 17:30 | 44495.7292 | 0 | 14.1965 | 39.95
2021-10-26 18:00 | 44495.75 | 0 | 14.3785 | 39.95
2021-10-26 18:30 | 44495.7708 | 0 | 15.0052 | 39.95
2021-10-26 19:00 | 44495.7917 | 0 | 14.6812 | 39.95
2021-10-26 19:30 | 44495.8125 | 0 | 14.4556 | 39.95
2021-10-26 20:00 | 44495.8333 | 0 | 13.956 | 39.95
2021-10-26 20:30 | 44495.8542 | 0 | 13.517 | 39.95
2021-10-26 21:00 | 44495.875 | 0 | 13.1387 | 39.95
2021-10-26 21:30 | 44495.8958 | 0 | 12.6667 | 39.95
2021-10-26 22:00 | 44495.9167 | 0 | 11.9805 | 39.95
2021-10-26 22:30 | 44495.9375 | 0 | 11.2381 | 39.95
2021-10-26 23:00 | 44495.9583 | 0 | 10.7074 | 39.95
2021-10-26 23:30 | 44495.9792 | 0 | 10.0803 | 39.95
2021-10-27 | 44496 | 0 | 9.4802 | 39.95
2021-10-27 00:30 | 44496.0208 | 0 | 9.2074 | 39.95
2021-10-27 01:00 | 44496.0417 | 0 | 9.0637 | 39.95
2021-10-27 01:30 | 44496.0625 | 0 | 8.7248 | 39.95
2021-10-27 02:00 | 44496.0833 | 0 | 8.7392 | 39.95
2021-10-27 02:30 | 44496.1042 | 0 | 8.5936 | 39.95
2021-10-27 03:00 | 44496.125 | 0 | 8.4131 | 39.95
2021-10-27 03:30 | 44496.1458 | 0 | 8.6837 | 39.95
2021-10-27 04:00 | 44496.1667 | 0 | 8.9159 | 39.95
2021-10-27 04:30 | 44496.1875 | 0 | 9.3503 | 39.95
2021-10-27 05:00 | 44496.2083 | 0 | 9.9254 | 39.95
2021-10-27 05:30 | 44496.2292 | 0 | 10.4606 | 39.95
2021-10-27 06:00 | 44496.25 | 0 | 10.8726 | 39.95
2021-10-27 06:30 | 44496.2708 | 0 | 12.0258 | 39.95
2021-10-27 07:00 | 44496.2917 | 0 | 12.4936 | 39.95
2021-10-27 07:30 | 44496.3125 | 0 | 11.8102 | 39.95
2021-10-27 08:00 | 44496.3333 | 0 | 11.4396 | 39.95
2021-10-27 08:30 | 44496.3542 | 0 | 11.664 | 39.95
2021-10-27 09:00 | 44496.375 | 0 | 12.0691 | 39.95
2021-10-27 09:30 | 44496.3958 | 0 | 12.0878 | 39.95
2021-10-27 10:00 | 44496.4167 | 0 | 11.8004 | 39.95
2021-10-27 10:30 | 44496.4375 | 0 | 12.7414 | 39.95
2021-10-27 11:00 | 44496.4583 | 0 | 13.1207 | 39.95
2021-10-27 11:30 | 44496.4792 | 0 | 12.4508 | 39.95
2021-10-27 12:00 | 44496.5 | 0 | 11.8516 | 39.95
2021-10-27 12:30 | 44496.5208 | 0 | 12.1606 | 39.95
2021-10-27 13:00 | 44496.5417 | 0 | 12.5119 | 39.95
2021-10-27 13:30 | 44496.5625 | 0 | 13.0203 | 39.95
2021-10-27 14:00 | 44496.5833 | 0 | 13.4718 | 39.95
2021-10-27 14:30 | 44496.6042 | 0 | 13.5879 | 39.95
2021-10-27 15:00 | 44496.625 | 0 | 13.7814 | 39.95
2021-10-27 15:30 | 44496.6458 | 0 | 14.5936 | 39.95
2021-10-27 16:00 | 44496.6667 | 0 | 15.0865 | 39.95
2021-10-27 16:30 | 44496.6875 | 0 | 15.6306 | 39.95
2021-10-27 17:00 | 44496.7083 | 0 | 15.5953 | 39.95
2021-10-27 17:30 | 44496.7292 | 0 | 15.8259 | 39.95
2021-10-27 18:00 | 44496.75 | 0 | 15.8666 | 39.95
2021-10-27 18:30 | 44496.7708 | 0 | 16.3062 | 39.95
2021-10-27 19:00 | 44496.7917 | 0 | 16.2678 | 39.95
2021-10-27 19:30 | 44496.8125 | 0 | 15.8049 | 39.95
2021-10-27 20:00 | 44496.8333 | 0 | 15.3783 | 39.95
2021-10-27 20:30 | 44496.8542 | 0 | 14.8015 | 39.95
2021-10-27 21:00 | 44496.875 | 0 | 14.3555 | 39.95
2021-10-27 21:30 | 44496.8958 | 0 | 14.0122 | 39.95
2021-10-27 22:00 | 44496.9167 | 0 | 13.0646 | 39.95
2021-10-27 22:30 | 44496.9375 | 0 | 12.1683 | 39.95
2021-10-27 23:00 | 44496.9583 | 0 | 11.4198 | 39.95
2021-10-27 23:30 | 44496.9792 | 0 | 10.8661 | 39.95
2021-10-28 | 44497 | 0 | 10.3378 | 39.95
2021-10-28 00:30 | 44497.0208 | 0 | 9.867 | 39.95
2021-10-28 01:00 | 44497.0417 | 0 | 9.7311 | 39.95
2021-10-28 01:30 | 44497.0625 | 0 | 9.4936 | 39.95
2021-10-28 02:00 | 44497.0833 | 0 | 9.4259 | 39.95
2021-10-28 02:30 | 44497.1042 | 0 | 9.2617 | 39.95
2021-10-28 03:00 | 44497.125 | 0 | 9.2241 | 39.95
2021-10-28 03:30 | 44497.1458 | 0 | 9.3879 | 39.95
2021-10-28 04:00 | 44497.1667 | 0 | 9.6146 | 39.95
2021-10-28 04:30 | 44497.1875 | 0 | 10.0962 | 39.95
2021-10-28 05:00 | 44497.2083 | 0 | 10.7051 | 39.95
2021-10-28 05:30 | 44497.2292 | 0 | 11.2285 | 39.95
2021-10-28 06:00 | 44497.25 | 0 | 11.9851 | 39.95
2021-10-28 06:30 | 44497.2708 | 0 | 12.3367 | 39.95
2021-10-28 07:00 | 44497.2917 | 0 | 13.1785 | 39.95
2021-10-28 07:30 | 44497.3125 | 0 | 13.5959 | 39.95
2021-10-28 08:00 | 44497.3333 | 0 | 13.9043 | 39.95
2021-10-28 08:30 | 44497.3542 | 0 | 13.7132 | 39.95
2021-10-28 09:00 | 44497.375 | 0 | 12.8661 | 39.95
2021-10-28 09:30 | 44497.3958 | 0 | 12.8912 | 39.95
2021-10-28 10:00 | 44497.4167 | 0 | 13.4338 | 39.95
2021-10-28 10:30 | 44497.4375 | 0 | 13.263 | 39.95
2021-10-28 11:00 | 44497.4583 | 0 | 13.2689 | 39.95
2021-10-28 11:30 | 44497.4792 | 0 | 13.4353 | 39.95
2021-10-28 12:00 | 44497.5 | 0 | 13.6244 | 39.95
2021-10-28 12:30 | 44497.5208 | 0 | 13.7126 | 39.95
2021-10-28 13:00 | 44497.5417 | 0 | 13.9431 | 39.95
2021-10-28 13:30 | 44497.5625 | 0 | 14.0521 | 39.95
2021-10-28 14:00 | 44497.5833 | 0 | 14.5564 | 39.95
2021-10-28 14:30 | 44497.6042 | 0 | 15.4389 | 39.95
2021-10-28 15:00 | 44497.625 | 0 | 15.7138 | 39.95
2021-10-28 15:30 | 44497.6458 | 0 | 16.449 | 39.95
2021-10-28 16:00 | 44497.6667 | 0 | 17.2554 | 39.95
2021-10-28 16:30 | 44497.6875 | 0 | 17.4224 | 39.95
2021-10-28 17:00 | 44497.7083 | 0 | 16.9945 | 39.95
2021-10-28 17:30 | 44497.7292 | 0 | 16.8332 | 39.95
2021-10-28 18:00 | 44497.75 | 0 | 16.8757 | 39.95
2021-10-28 18:30 | 44497.7708 | 0 | 17.1243 | 39.95
2021-10-28 19:00 | 44497.7917 | 0 | 16.802 | 39.95
2021-10-28 19:30 | 44497.8125 | 0 | 16.6434 | 39.95
2021-10-28 20:00 | 44497.8333 | 0 | 16.1788 | 39.95
2021-10-28 20:30 | 44497.8542 | 0 | 15.623 | 39.95
2021-10-28 21:00 | 44497.875 | 0 | 15.092 | 39.95
2021-10-28 21:30 | 44497.8958 | 0 | 14.5908 | 39.95
2021-10-28 22:00 | 44497.9167 | 0 | 13.7534 | 39.95
2021-10-28 22:30 | 44497.9375 | 0 | 12.7283 | 39.95
2021-10-28 23:00 | 44497.9583 | 0 | 12.1425 | 39.95
2021-10-28 23:30 | 44497.9792 | 0 | 11.4524 | 39.95
2021-10-29 | 44498 | 0 | 10.7883 | 39.95
2021-10-29 00:30 | 44498.0208 | 0 | 10.3739 | 39.95
2021-10-29 01:00 | 44498.0417 | 0 | 9.865 | 39.95
2021-10-29 01:30 | 44498.0625 | 0 | 9.7296 | 39.95
2021-10-29 02:00 | 44498.0833 | 0 | 9.6574 | 39.95
2021-10-29 02:30 | 44498.1042 | 0 | 9.3561 | 39.95
2021-10-29 03:00 | 44498.125 | 0 | 9.1307 | 39.95
2021-10-29 03:30 | 44498.1458 | 0 | 9.331 | 39.95
2021-10-29 04:00 | 44498.1667 | 0 | 9.4676 | 39.95
2021-10-29 04:30 | 44498.1875 | 0 | 9.4646 | 39.95
2021-10-29 05:00 | 44498.2083 | 0 | 9.5439 | 39.95
2021-10-29 05:30 | 44498.2292 | 0 | 9.4668 | 39.95
2021-10-29 06:00 | 44498.25 | 0 | 9.7083 | 39.95
2021-10-29 06:30 | 44498.2708 | 0 | 9.4323 | 39.95
2021-10-29 07:00 | 44498.2917 | 0 | 9.7035 | 39.95
2021-10-29 07:30 | 44498.3125 | 0 | 10.2528 | 39.95
2021-10-29 08:00 | 44498.3333 | 0 | 11.4598 | 39.95
2021-10-29 08:30 | 44498.3542 | 0 | 11.8259 | 39.95
2021-10-29 09:00 | 44498.375 | 0 | 11.4082 | 39.95
2021-10-29 09:30 | 44498.3958 | 0 | 10.0721 | 39.95
2021-10-29 10:00 | 44498.4167 | 0 | 11.4267 | 39.95
2021-10-29 10:30 | 44498.4375 | 0 | 11.506 | 39.95
2021-10-29 11:00 | 44498.4583 | 0 | 11.5955 | 39.95
2021-10-29 11:30 | 44498.4792 | 0 | 12.259 | 39.95
2021-10-29 12:00 | 44498.5 | 0 | 11.877 | 39.95
2021-10-29 12:30 | 44498.5208 | 0 | 12.2909 | 39.95
2021-10-29 13:00 | 44498.5417 | 0 | 11.2946 | 39.95
2021-10-29 13:30 | 44498.5625 | 0 | 11.8099 | 39.95
2021-10-29 14:00 | 44498.5833 | 0 | 12.9327 | 39.95
2021-10-29 14:30 | 44498.6042 | 0 | 13.5645 | 39.95
2021-10-29 15:00 | 44498.625 | 0 | 12.8783 | 39.95
2021-10-29 15:30 | 44498.6458 | 0 | 12.4653 | 39.95
2021-10-29 16:00 | 44498.6667 | 0 | 12.1847 | 39.95
2021-10-29 16:30 | 44498.6875 | 0 | 12.1717 | 39.95
2021-10-29 17:00 | 44498.7083 | 0 | 12.2718 | 39.95
2021-10-29 17:30 | 44498.7292 | 0 | 12.2387 | 39.95
2021-10-29 18:00 | 44498.75 | 0 | 12.3995 | 39.95
2021-10-29 18:30 | 44498.7708 | 0 | 12.6066 | 39.95
2021-10-29 19:00 | 44498.7917 | 0 | 12.3878 | 39.95
2021-10-29 19:30 | 44498.8125 | 0 | 12.2666 | 39.95
2021-10-29 20:00 | 44498.8333 | 0 | 11.916 | 39.95
2021-10-29 20:30 | 44498.8542 | 0 | 11.6048 | 39.95
2021-10-29 21:00 | 44498.875 | 0 | 11.3416 | 39.95
2021-10-29 21:30 | 44498.8958 | 0 | 11.0502 | 39.95
2021-10-29 22:00 | 44498.9167 | 0 | 10.6976 | 39.95
2021-10-29 22:30 | 44498.9375 | 0 | 10.0131 | 39.95
2021-10-29 23:00 | 44498.9583 | 0 | 9.5345 | 39.95
2021-10-29 23:30 | 44498.9792 | 0 | 9.1917 | 39.95
2021-10-30 | 44499 | 0 | 8.7321 | 39.95
2021-10-30 00:30 | 44499.0208 | 0 | 8.438 | 39.95
2021-10-30 01:00 | 44499.0417 | 0 | 8.1637 | 39.95
2021-10-30 01:30 | 44499.0625 | 0 | 8.0195 | 39.95
2021-10-30 02:00 | 44499.0833 | 0 | 8.0517 | 39.95
2021-10-30 02:30 | 44499.1042 | 0 | 7.9895 | 39.95
2021-10-30 03:00 | 44499.125 | 0 | 7.8555 | 39.95
2021-10-30 03:30 | 44499.1458 | 0 | 7.8749 | 39.95
2021-10-30 04:00 | 44499.1667 | 0 | 7.9311 | 39.95
2021-10-30 04:30 | 44499.1875 | 0 | 8.186 | 39.95
2021-10-30 05:00 | 44499.2083 | 0 | 8.1123 | 39.95
2021-10-30 05:30 | 44499.2292 | 0 | 7.9705 | 39.95
2021-10-30 06:00 | 44499.25 | 0 | 7.9273 | 39.95
2021-10-30 06:30 | 44499.2708 | 0 | 7.8845 | 39.95
2021-10-30 07:00 | 44499.2917 | 0 | 8.5017 | 39.95
2021-10-30 07:30 | 44499.3125 | 0 | 8.4712 | 39.95
2021-10-30 08:00 | 44499.3333 | 0 | 8.2953 | 39.95
2021-10-30 08:30 | 44499.3542 | 0 | 8.1215 | 39.95
2021-10-30 09:00 | 44499.375 | 0 | 8.1476 | 39.95
2021-10-30 09:30 | 44499.3958 | 0 | 8.2759 | 39.95
2021-10-30 10:00 | 44499.4167 | 0 | 8.3526 | 39.95
2021-10-30 10:30 | 44499.4375 | 0 | 9.3367 | 39.95
2021-10-30 11:00 | 44499.4583 | 0 | 10.168 | 39.95
2021-10-30 11:30 | 44499.4792 | 0 | 10.0758 | 39.95
2021-10-30 12:00 | 44499.5 | 0 | 10.6216 | 39.95
2021-10-30 12:30 | 44499.5208 | 0 | 10.5743 | 39.95
2021-10-30 13:00 | 44499.5417 | 0 | 12.0744 | 39.95
2021-10-30 13:30 | 44499.5625 | 0 | 12.7426 | 39.95
2021-10-30 14:00 | 44499.5833 | 0 | 13.2975 | 39.95
2021-10-30 14:30 | 44499.6042 | 0 | 14.2978 | 39.95
2021-10-30 15:00 | 44499.625 | 0 | 14.4327 | 39.95
2021-10-30 15:30 | 44499.6458 | 0 | 15.4344 | 39.95
2021-10-30 16:00 | 44499.6667 | 0 | 15.2428 | 39.95
2021-10-30 16:30 | 44499.6875 | 0 | 14.9328 | 39.95
2021-10-30 17:00 | 44499.7083 | 0 | 14.8498 | 39.95
2021-10-30 17:30 | 44499.7292 | 0 | 13.9441 | 39.95
2021-10-30 18:00 | 44499.75 | 0 | 13.668 | 39.95
2021-10-30 18:30 | 44499.7708 | 0 | 13.7253 | 39.95
2021-10-30 19:00 | 44499.7917 | 0 | 13.5825 | 39.95
2021-10-30 19:30 | 44499.8125 | 0 | 13.0784 | 39.95
2021-10-30 20:00 | 44499.8333 | 0 | 12.5195 | 39.95
2021-10-30 20:30 | 44499.8542 | 0 | 11.8779 | 39.95
2021-10-30 21:00 | 44499.875 | 0 | 11.4738 | 39.95
2021-10-30 21:30 | 44499.8958 | 0 | 11.0373 | 39.95
2021-10-30 22:00 | 44499.9167 | 0 | 10.4847 | 39.95
2021-10-30 22:30 | 44499.9375 | 0 | 9.9935 | 39.95
2021-10-30 23:00 | 44499.9583 | 0 | 9.6174 | 39.95
2021-10-30 23:30 | 44499.9792 | 0 | 9.3347 | 39.95
2021-10-31 | 44500 | 0 | 8.6207 | 39.95
2021-10-31 00:30 | 44500.0208 | 0 | 8.4827 | 39.95
2021-10-31 01:00 | 44500.0417 | 0 | 8.356 | 39.95
2021-10-31 01:30 | 44500.0625 | 0 | 8.077 | 39.95
2021-10-31 02:00 | 44500.0833 | 0 | 7.9981 | 39.95
2021-10-31 02:30 | 44500.1042 | 0 | 7.835 | 39.95
2021-10-31 03:00 | 44500.125 | 0 | 7.7494 | 39.95
2021-10-31 03:30 | 44500.1458 | 0 | 7.7993 | 39.95
2021-10-31 04:00 | 44500.1667 | 0 | 7.7174 | 39.95
2021-10-31 04:30 | 44500.1875 | 0 | 7.6835 | 39.95
2021-10-31 05:00 | 44500.2083 | 0 | 7.6328 | 39.95
2021-10-31 05:30 | 44500.2292 | 0 | 7.356 | 39.95
2021-10-31 06:00 | 44500.25 | 0 | 7.2875 | 39.95
2021-10-31 06:30 | 44500.2708 | 0 | 7.1263 | 39.95
2021-10-31 07:00 | 44500.2917 | 0 | 6.7874 | 39.95
2021-10-31 07:30 | 44500.3125 | 0 | 6.9983 | 39.95
2021-10-31 08:00 | 44500.3333 | 0 | 7.2504 | 39.95
2021-10-31 08:30 | 44500.3542 | 0 | 6.6469 | 39.95
2021-10-31 09:00 | 44500.375 | 0 | 6.5317 | 39.95
2021-10-31 09:30 | 44500.3958 | 0 | 6.808 | 39.95
2021-10-31 10:00 | 44500.4167 | 0 | 7.897 | 39.95
2021-10-31 10:30 | 44500.4375 | 0 | 7.0868 | 39.95
2021-10-31 11:00 | 44500.4583 | 0 | 7.9098 | 39.95
2021-10-31 11:30 | 44500.4792 | 0 | 7.5922 | 39.95
2021-10-31 12:00 | 44500.5 | 0 | 7.6914 | 39.95
2021-10-31 12:30 | 44500.5208 | 0 | 7.6851 | 39.95
2021-10-31 13:00 | 44500.5417 | 0 | 7.0505 | 39.95
2021-10-31 13:30 | 44500.5625 | 0 | 8.7633 | 39.95
2021-10-31 14:00 | 44500.5833 | 0 | 7.5966 | 39.95
2021-10-31 14:30 | 44500.6042 | 0 | 7.6781 | 39.95
2021-10-31 15:00 | 44500.625 | 0 | 7.3945 | 39.95
2021-10-31 15:30 | 44500.6458 | 0 | 8.69 | 39.95
2021-10-31 16:00 | 44500.6667 | 0 | 8.4957 | 39.95
2021-10-31 16:30 | 44500.6875 | 0 | 9.129 | 39.95
2021-10-31 17:00 | 44500.7083 | 0 | 9.6768 | 39.95
2021-10-31 17:30 | 44500.7292 | 0 | 10.359 | 39.95
2021-10-31 18:00 | 44500.75 | 0 | 10.8756 | 39.95
2021-10-31 18:30 | 44500.7708 | 0 | 11.3353 | 39.95
2021-10-31 19:00 | 44500.7917 | 0 | 11.1166 | 39.95
2021-10-31 19:30 | 44500.8125 | 0 | 10.8172 | 39.95
2021-10-31 20:00 | 44500.8333 | 0 | 10.5619 | 39.95
2021-10-31 20:30 | 44500.8542 | 0 | 10.3044 | 39.95
2021-10-31 21:00 | 44500.875 | 0 | 9.8433 | 39.95
2021-10-31 21:30 | 44500.8958 | 0 | 9.4038 | 39.95
2021-10-31 22:00 | 44500.9167 | 0 | 9.0611 | 39.95
2021-10-31 22:30 | 44500.9375 | 0 | 8.3811 | 39.95
2021-10-31 23:00 | 44500.9583 | 0 | 7.9682 | 39.95
2021-10-31 23:30 | 44500.9792 | 0 | 7.7405 | 39.95
2021-11-01 | 44501 | 0 | 7.4565 | 37.78
2021-11-01 00:30 | 44501.0208 | 0 | 7.2509 | 37.78
2021-11-01 01:00 | 44501.0417 | 0 | 7.3069 | 37.78
2021-11-01 01:30 | 44501.0625 | 0 | 7.0958 | 37.78
2021-11-01 02:00 | 44501.0833 | 0 | 7.0761 | 37.78
2021-11-01 02:30 | 44501.1042 | 0 | 7.1193 | 37.78
2021-11-01 03:00 | 44501.125 | 0 | 7.1435 | 37.78
2021-11-01 03:30 | 44501.1458 | 0 | 7.3348 | 37.78
2021-11-01 04:00 | 44501.1667 | 0 | 7.334 | 37.78
2021-11-01 04:30 | 44501.1875 | 0 | 7.8463 | 37.78
2021-11-01 05:00 | 44501.2083 | 0 | 8.5532 | 37.78
2021-11-01 05:30 | 44501.2292 | 0 | 8.8822 | 37.78
2021-11-01 06:00 | 44501.25 | 0 | 9.5369 | 37.78
2021-11-01 06:30 | 44501.2708 | 0 | 10.6322 | 37.78
2021-11-01 07:00 | 44501.2917 | 0 | 11.2494 | 37.78
2021-11-01 07:30 | 44501.3125 | 0 | 11.2039 | 37.78
2021-11-01 08:00 | 44501.3333 | 0 | 11.1796 | 37.78
2021-11-01 08:30 | 44501.3542 | 0 | 10.447 | 37.78
2021-11-01 09:00 | 44501.375 | 0 | 10.9259 | 37.78
2021-11-01 09:30 | 44501.3958 | 0 | 10.3372 | 37.78
2021-11-01 10:00 | 44501.4167 | 0 | 10.3175 | 37.78
2021-11-01 10:30 | 44501.4375 | 0 | 10.4046 | 37.78
2021-11-01 11:00 | 44501.4583 | 0 | 9.8412 | 37.78
2021-11-01 11:30 | 44501.4792 | 0 | 9.3822 | 37.78
2021-11-01 12:00 | 44501.5 | 0 | 9.4667 | 37.78
2021-11-01 12:30 | 44501.5208 | 0 | 9.8594 | 37.78
2021-11-01 13:00 | 44501.5417 | 0 | 10.5947 | 37.78
2021-11-01 13:30 | 44501.5625 | 0 | 10.7098 | 37.78
2021-11-01 14:00 | 44501.5833 | 0 | 10.3404 | 37.78
2021-11-01 14:30 | 44501.6042 | 0 | 11.8518 | 37.78
2021-11-01 15:00 | 44501.625 | 0 | 11.8052 | 37.78
2021-11-01 15:30 | 44501.6458 | 0 | 11.9286 | 37.78
2021-11-01 16:00 | 44501.6667 | 0 | 12.0898 | 37.78
2021-11-01 16:30 | 44501.6875 | 0 | 12.185 | 37.78
2021-11-01 17:00 | 44501.7083 | 0 | 12.3168 | 37.78
2021-11-01 17:30 | 44501.7292 | 0 | 12.951 | 37.78
2021-11-01 18:00 | 44501.75 | 0 | 13.2039 | 37.78
2021-11-01 18:30 | 44501.7708 | 0 | 13.6683 | 37.78
2021-11-01 19:00 | 44501.7917 | 0 | 13.3493 | 37.78
2021-11-01 19:30 | 44501.8125 | 0 | 13.0248 | 37.78
2021-11-01 20:00 | 44501.8333 | 0 | 12.7577 | 37.78
2021-11-01 20:30 | 44501.8542 | 0 | 12.119 | 37.78
2021-11-01 21:00 | 44501.875 | 0 | 11.6703 | 37.78
2021-11-01 21:30 | 44501.8958 | 0 | 11.3346 | 37.78
2021-11-01 22:00 | 44501.9167 | 0 | 10.737 | 37.78
2021-11-01 22:30 | 44501.9375 | 0 | 9.8744 | 37.78
2021-11-01 23:00 | 44501.9583 | 0 | 9.4455 | 37.78
2021-11-01 23:30 | 44501.9792 | 0 | 9.1106 | 37.78
2021-11-02 | 44502 | 0 | 8.5303 | 37.78
2021-11-02 00:30 | 44502.0208 | 0 | 8.2761 | 37.78
2021-11-02 01:00 | 44502.0417 | 0 | 8.0328 | 37.78
2021-11-02 01:30 | 44502.0625 | 0 | 7.895 | 37.78
2021-11-02 02:00 | 44502.0833 | 0 | 7.7524 | 37.78
2021-11-02 02:30 | 44502.1042 | 0 | 7.7312 | 37.78
2021-11-02 03:00 | 44502.125 | 0 | 7.6917 | 37.78
2021-11-02 03:30 | 44502.1458 | 0 | 7.7264 | 37.78
2021-11-02 04:00 | 44502.1667 | 0 | 7.9501 | 37.78
2021-11-02 04:30 | 44502.1875 | 0 | 8.3812 | 37.78
2021-11-02 05:00 | 44502.2083 | 0 | 8.961 | 37.78
2021-11-02 05:30 | 44502.2292 | 0 | 9.4643 | 37.78
2021-11-02 06:00 | 44502.25 | 0 | 9.9154 | 37.78
2021-11-02 06:30 | 44502.2708 | 0 | 10.9394 | 37.78
2021-11-02 07:00 | 44502.2917 | 0 | 11.5474 | 37.78
2021-11-02 07:30 | 44502.3125 | 0 | 11.7931 | 37.78
2021-11-02 08:00 | 44502.3333 | 0 | 11.9201 | 37.78
2021-11-02 08:30 | 44502.3542 | 0 | 11.6236 | 37.78
2021-11-02 09:00 | 44502.375 | 0 | 11.124 | 37.78
2021-11-02 09:30 | 44502.3958 | 0 | 11.9661 | 37.78
2021-11-02 10:00 | 44502.4167 | 0 | 10.8578 | 37.78
2021-11-02 10:30 | 44502.4375 | 0 | 11.3658 | 37.78
2021-11-02 11:00 | 44502.4583 | 0 | 9.7812 | 37.78
2021-11-02 11:30 | 44502.4792 | 0 | 9.826 | 37.78
2021-11-02 12:00 | 44502.5 | 0 | 10.2534 | 37.78
2021-11-02 12:30 | 44502.5208 | 0 | 9.8943 | 37.78
2021-11-02 13:00 | 44502.5417 | 0 | 10.7723 | 37.78
2021-11-02 13:30 | 44502.5625 | 0 | 10.8747 | 37.78
2021-11-02 14:00 | 44502.5833 | 0 | 11.6416 | 37.78
2021-11-02 14:30 | 44502.6042 | 0 | 12.4348 | 37.78
2021-11-02 15:00 | 44502.625 | 0 | 12.6522 | 37.78
2021-11-02 15:30 | 44502.6458 | 0 | 12.3485 | 37.78
2021-11-02 16:00 | 44502.6667 | 0 | 12.3282 | 37.78
2021-11-02 16:30 | 44502.6875 | 0 | 12.8003 | 37.78
2021-11-02 17:00 | 44502.7083 | 0 | 12.7568 | 37.78
2021-11-02 17:30 | 44502.7292 | 0 | 13.0301 | 37.78
2021-11-02 18:00 | 44502.75 | 0 | 13.3568 | 37.78
2021-11-02 18:30 | 44502.7708 | 0 | 13.6791 | 37.78
2021-11-02 19:00 | 44502.7917 | 0 | 13.5502 | 37.78
2021-11-02 19:30 | 44502.8125 | 0 | 13.2701 | 37.78
2021-11-02 20:00 | 44502.8333 | 0 | 12.8688 | 37.78
2021-11-02 20:30 | 44502.8542 | 0 | 12.2934 | 37.78
2021-11-02 21:00 | 44502.875 | 0 | 11.8929 | 37.78
2021-11-02 21:30 | 44502.8958 | 0 | 11.4917 | 37.78
2021-11-02 22:00 | 44502.9167 | 0 | 11.1389 | 37.78
2021-11-02 22:30 | 44502.9375 | 0 | 10.1371 | 37.78
2021-11-02 23:00 | 44502.9583 | 0 | 9.653 | 37.78
2021-11-02 23:30 | 44502.9792 | 0 | 9.2698 | 37.78
2021-11-03 | 44503 | 0 | 8.8601 | 37.78
2021-11-03 00:30 | 44503.0208 | 0 | 8.5877 | 37.78
2021-11-03 01:00 | 44503.0417 | 0 | 8.313 | 37.78
2021-11-03 01:30 | 44503.0625 | 0 | 8.2303 | 37.78
2021-11-03 02:00 | 44503.0833 | 0 | 7.9934 | 37.78
2021-11-03 02:30 | 44503.1042 | 0 | 7.9687 | 37.78
2021-11-03 03:00 | 44503.125 | 0 | 7.8641 | 37.78
2021-11-03 03:30 | 44503.1458 | 0 | 8.0137 | 37.78
2021-11-03 04:00 | 44503.1667 | 0 | 8.2295 | 37.78
2021-11-03 04:30 | 44503.1875 | 0 | 8.5713 | 37.78
2021-11-03 05:00 | 44503.2083 | 0 | 9.246 | 37.78
2021-11-03 05:30 | 44503.2292 | 0 | 9.4121 | 37.78
2021-11-03 06:00 | 44503.25 | 0 | 9.8487 | 37.78
2021-11-03 06:30 | 44503.2708 | 0 | 9.9525 | 37.78
2021-11-03 07:00 | 44503.2917 | 0 | 10.254 | 37.78
2021-11-03 07:30 | 44503.3125 | 0 | 9.963 | 37.78
2021-11-03 08:00 | 44503.3333 | 0 | 9.5599 | 37.78
2021-11-03 08:30 | 44503.3542 | 0 | 10.1439 | 37.78
2021-11-03 09:00 | 44503.375 | 0 | 11.3717 | 37.78
2021-11-03 09:30 | 44503.3958 | 0 | 11.8398 | 37.78
2021-11-03 10:00 | 44503.4167 | 0 | 12.2805 | 37.78
2021-11-03 10:30 | 44503.4375 | 0 | 11.076 | 37.78
2021-11-03 11:00 | 44503.4583 | 0 | 11.1838 | 37.78
2021-11-03 11:30 | 44503.4792 | 0 | 10.4958 | 37.78
2021-11-03 12:00 | 44503.5 | 0 | 10.801 | 37.78
2021-11-03 12:30 | 44503.5208 | 0 | 10.9005 | 37.78
2021-11-03 13:00 | 44503.5417 | 0 | 11.66 | 37.78
2021-11-03 13:30 | 44503.5625 | 0 | 11.1384 | 37.78
2021-11-03 14:00 | 44503.5833 | 0 | 10.7564 | 37.78
2021-11-03 14:30 | 44503.6042 | 0 | 11.2081 | 37.78
2021-11-03 15:00 | 44503.625 | 0 | 11.1129 | 37.78
2021-11-03 15:30 | 44503.6458 | 0 | 11.6645 | 37.78
2021-11-03 16:00 | 44503.6667 | 0 | 12.1022 | 37.78
2021-11-03 16:30 | 44503.6875 | 0 | 12.5863 | 37.78
2021-11-03 17:00 | 44503.7083 | 0 | 12.6886 | 37.78
2021-11-03 17:30 | 44503.7292 | 0 | 13.2691 | 37.78
2021-11-03 18:00 | 44503.75 | 0 | 13.3463 | 37.78
2021-11-03 18:30 | 44503.7708 | 0 | 14.0686 | 37.78
2021-11-03 19:00 | 44503.7917 | 0 | 13.7199 | 37.78
2021-11-03 19:30 | 44503.8125 | 0 | 13.4626 | 37.78
2021-11-03 20:00 | 44503.8333 | 0 | 12.951 | 37.78
2021-11-03 20:30 | 44503.8542 | 0 | 12.4577 | 37.78
2021-11-03 21:00 | 44503.875 | 0 | 11.8146 | 37.78
2021-11-03 21:30 | 44503.8958 | 0 | 11.5729 | 37.78
2021-11-03 22:00 | 44503.9167 | 0 | 10.9208 | 37.78
2021-11-03 22:30 | 44503.9375 | 0 | 10.1841 | 37.78
2021-11-03 23:00 | 44503.9583 | 0 | 9.4857 | 37.78
2021-11-03 23:30 | 44503.9792 | 0 | 9.0963 | 37.78
2021-11-04 | 44504 | 0 | 8.6991 | 37.78
2021-11-04 00:30 | 44504.0208 | 0 | 8.388 | 37.78
2021-11-04 01:00 | 44504.0417 | 0 | 8.1835 | 37.78
2021-11-04 01:30 | 44504.0625 | 0 | 8.0587 | 37.78
2021-11-04 02:00 | 44504.0833 | 0 | 7.9954 | 37.78
2021-11-04 02:30 | 44504.1042 | 0 | 7.8926 | 37.78
2021-11-04 03:00 | 44504.125 | 0 | 7.7019 | 37.78
2021-11-04 03:30 | 44504.1458 | 0 | 8.0483 | 37.78
2021-11-04 04:00 | 44504.1667 | 0 | 8.2258 | 37.78
2021-11-04 04:30 | 44504.1875 | 0 | 8.5183 | 37.78
2021-11-04 05:00 | 44504.2083 | 0 | 9.0548 | 37.78
2021-11-04 05:30 | 44504.2292 | 0 | 9.4085 | 37.78
2021-11-04 06:00 | 44504.25 | 0 | 9.4862 | 37.78
2021-11-04 06:30 | 44504.2708 | 0 | 10.1852 | 37.78
2021-11-04 07:00 | 44504.2917 | 0 | 10.3354 | 37.78
2021-11-04 07:30 | 44504.3125 | 0 | 10.6466 | 37.78
2021-11-04 08:00 | 44504.3333 | 0 | 9.9242 | 37.78
2021-11-04 08:30 | 44504.3542 | 0 | 9.734 | 37.78
2021-11-04 09:00 | 44504.375 | 0 | 9.1204 | 37.78
2021-11-04 09:30 | 44504.3958 | 0 | 9.8233 | 37.78
2021-11-04 10:00 | 44504.4167 | 0 | 10.5418 | 37.78
2021-11-04 10:30 | 44504.4375 | 0 | 10.954 | 37.78
2021-11-04 11:00 | 44504.4583 | 0 | 10.0196 | 37.78
2021-11-04 11:30 | 44504.4792 | 0 | 9.3946 | 37.78
2021-11-04 12:00 | 44504.5 | 0 | 9.0499 | 37.78
2021-11-04 12:30 | 44504.5208 | 0 | 9.6493 | 37.78
2021-11-04 13:00 | 44504.5417 | 0 | 9.5149 | 37.78
2021-11-04 13:30 | 44504.5625 | 0 | 9.4736 | 37.78
2021-11-04 14:00 | 44504.5833 | 0 | 9.9882 | 37.78
2021-11-04 14:30 | 44504.6042 | 0 | 10.5284 | 37.78
2021-11-04 15:00 | 44504.625 | 0 | 10.9864 | 37.78
2021-11-04 15:30 | 44504.6458 | 0 | 11.5176 | 37.78
2021-11-04 16:00 | 44504.6667 | 0 | 12.0086 | 37.78
2021-11-04 16:30 | 44504.6875 | 0 | 13.1312 | 37.78
2021-11-04 17:00 | 44504.7083 | 0 | 13.2645 | 37.78
2021-11-04 17:30 | 44504.7292 | 0 | 13.4346 | 37.78
2021-11-04 18:00 | 44504.75 | 0 | 13.6555 | 37.78
2021-11-04 18:30 | 44504.7708 | 0 | 14.0472 | 37.78
2021-11-04 19:00 | 44504.7917 | 0 | 13.7355 | 37.78
2021-11-04 19:30 | 44504.8125 | 0 | 13.2691 | 37.78
2021-11-04 20:00 | 44504.8333 | 0 | 12.8733 | 37.78
2021-11-04 20:30 | 44504.8542 | 0 | 12.4178 | 37.78
2021-11-04 21:00 | 44504.875 | 0 | 11.873 | 37.78
2021-11-04 21:30 | 44504.8958 | 0 | 11.7023 | 37.78
2021-11-04 22:00 | 44504.9167 | 0 | 11.1867 | 37.78
2021-11-04 22:30 | 44504.9375 | 0 | 10.3903 | 37.78
2021-11-04 23:00 | 44504.9583 | 0 | 9.9318 | 37.78
2021-11-04 23:30 | 44504.9792 | 0 | 9.4803 | 37.78
2021-11-05 | 44505 | 0 | 8.9024 | 37.78
2021-11-05 00:30 | 44505.0208 | 0 | 8.6668 | 37.78
2021-11-05 01:00 | 44505.0417 | 0 | 8.4383 | 37.78
2021-11-05 01:30 | 44505.0625 | 0 | 8.1674 | 37.78
2021-11-05 02:00 | 44505.0833 | 0 | 8.1411 | 37.78
2021-11-05 02:30 | 44505.1042 | 0 | 7.963 | 37.78
2021-11-05 03:00 | 44505.125 | 0 | 8.0495 | 37.78
2021-11-05 03:30 | 44505.1458 | 0 | 8.1182 | 37.78
2021-11-05 04:00 | 44505.1667 | 0 | 8.4239 | 37.78
2021-11-05 04:30 | 44505.1875 | 0 | 8.8844 | 37.78
2021-11-05 05:00 | 44505.2083 | 0 | 9.315 | 37.78
2021-11-05 05:30 | 44505.2292 | 0 | 9.7742 | 37.78
2021-11-05 06:00 | 44505.25 | 0 | 10.299 | 37.78
2021-11-05 06:30 | 44505.2708 | 0 | 10.3937 | 37.78
2021-11-05 07:00 | 44505.2917 | 0 | 11.4885 | 37.78
2021-11-05 07:30 | 44505.3125 | 0 | 12.2652 | 37.78
2021-11-05 08:00 | 44505.3333 | 0 | 12.2314 | 37.78
2021-11-05 08:30 | 44505.3542 | 0 | 12.0441 | 37.78
2021-11-05 09:00 | 44505.375 | 0 | 11.3767 | 37.78
2021-11-05 09:30 | 44505.3958 | 0 | 9.9946 | 37.78
2021-11-05 10:00 | 44505.4167 | 0 | 10.3203 | 37.78
2021-11-05 10:30 | 44505.4375 | 0 | 11.3376 | 37.78
2021-11-05 11:00 | 44505.4583 | 0 | 10.1369 | 37.78
2021-11-05 11:30 | 44505.4792 | 0 | 10.2614 | 37.78
2021-11-05 12:00 | 44505.5 | 0 | 11.0885 | 37.78
2021-11-05 12:30 | 44505.5208 | 0 | 11.4263 | 37.78
2021-11-05 13:00 | 44505.5417 | 0 | 11.2894 | 37.78
2021-11-05 13:30 | 44505.5625 | 0 | 11.29 | 37.78
2021-11-05 14:00 | 44505.5833 | 0 | 11.8523 | 37.78
2021-11-05 14:30 | 44505.6042 | 0 | 11.5128 | 37.78
2021-11-05 15:00 | 44505.625 | 0 | 10.2916 | 37.78
2021-11-05 15:30 | 44505.6458 | 0 | 10.9237 | 37.78
2021-11-05 16:00 | 44505.6667 | 0 | 11.6102 | 37.78
2021-11-05 16:30 | 44505.6875 | 0 | 12.6638 | 37.78
2021-11-05 17:00 | 44505.7083 | 0 | 12.2807 | 37.78
2021-11-05 17:30 | 44505.7292 | 0 | 12.8076 | 37.78
2021-11-05 18:00 | 44505.75 | 0 | 12.8476 | 37.78
2021-11-05 18:30 | 44505.7708 | 0 | 13.2724 | 37.78
2021-11-05 19:00 | 44505.7917 | 0 | 13.0824 | 37.78
2021-11-05 19:30 | 44505.8125 | 0 | 12.7714 | 37.78
2021-11-05 20:00 | 44505.8333 | 0 | 12.4532 | 37.78
2021-11-05 20:30 | 44505.8542 | 0 | 12.1713 | 37.78
2021-11-05 21:00 | 44505.875 | 0 | 11.5283 | 37.78
2021-11-05 21:30 | 44505.8958 | 0 | 11.3215 | 37.78
2021-11-05 22:00 | 44505.9167 | 0 | 10.8293 | 37.78
2021-11-05 22:30 | 44505.9375 | 0 | 10.3467 | 37.78
2021-11-05 23:00 | 44505.9583 | 0 | 9.7241 | 37.78
2021-11-05 23:30 | 44505.9792 | 0 | 9.3288 | 37.78
2021-11-06 | 44506 | 0 | 8.8874 | 37.78
2021-11-06 00:30 | 44506.0208 | 0 | 8.5763 | 37.78
2021-11-06 01:00 | 44506.0417 | 0 | 8.2374 | 37.78
2021-11-06 01:30 | 44506.0625 | 0 | 8.1669 | 37.78
2021-11-06 02:00 | 44506.0833 | 0 | 7.9756 | 37.78
2021-11-06 02:30 | 44506.1042 | 0 | 7.8863 | 37.78
2021-11-06 03:00 | 44506.125 | 0 | 7.7168 | 37.78
2021-11-06 03:30 | 44506.1458 | 0 | 7.872 | 37.78
2021-11-06 04:00 | 44506.1667 | 0 | 7.9138 | 37.78
2021-11-06 04:30 | 44506.1875 | 0 | 7.9441 | 37.78
2021-11-06 05:00 | 44506.2083 | 0 | 7.9258 | 37.78
2021-11-06 05:30 | 44506.2292 | 0 | 7.8371 | 37.78
2021-11-06 06:00 | 44506.25 | 0 | 7.7629 | 37.78
2021-11-06 06:30 | 44506.2708 | 0 | 7.4855 | 37.78
2021-11-06 07:00 | 44506.2917 | 0 | 7.3474 | 37.78
2021-11-06 07:30 | 44506.3125 | 0 | 7.5521 | 37.78
2021-11-06 08:00 | 44506.3333 | 0 | 9.4341 | 37.78
2021-11-06 08:30 | 44506.3542 | 0 | 9.792 | 37.78
2021-11-06 09:00 | 44506.375 | 0 | 8.8663 | 37.78
2021-11-06 09:30 | 44506.3958 | 0 | 9.3175 | 37.78
2021-11-06 10:00 | 44506.4167 | 0 | 7.1157 | 37.78
2021-11-06 10:30 | 44506.4375 | 0 | 6.6453 | 37.78
2021-11-06 11:00 | 44506.4583 | 0 | 7.9863 | 37.78
2021-11-06 11:30 | 44506.4792 | 0 | 8.9574 | 37.78
2021-11-06 12:00 | 44506.5 | 0 | 8.5039 | 37.78
2021-11-06 12:30 | 44506.5208 | 0 | 7.2322 | 37.78
2021-11-06 13:00 | 44506.5417 | 0 | 7.413 | 37.78
2021-11-06 13:30 | 44506.5625 | 0 | 7.9439 | 37.78
2021-11-06 14:00 | 44506.5833 | 0 | 7.4968 | 37.78
2021-11-06 14:30 | 44506.6042 | 0 | 8.7419 | 37.78
2021-11-06 15:00 | 44506.625 | 0 | 9.4301 | 37.78
2021-11-06 15:30 | 44506.6458 | 0 | 9.7213 | 37.78
2021-11-06 16:00 | 44506.6667 | 0 | 10.1508 | 37.78
2021-11-06 16:30 | 44506.6875 | 0 | 10.3835 | 37.78
2021-11-06 17:00 | 44506.7083 | 0 | 10.8797 | 37.78
2021-11-06 17:30 | 44506.7292 | 0 | 11.1919 | 37.78
2021-11-06 18:00 | 44506.75 | 0 | 11.4973 | 37.78
2021-11-06 18:30 | 44506.7708 | 0 | 11.7968 | 37.78
2021-11-06 19:00 | 44506.7917 | 0 | 11.6869 | 37.78
2021-11-06 19:30 | 44506.8125 | 0 | 11.2534 | 37.78
2021-11-06 20:00 | 44506.8333 | 0 | 11.0538 | 37.78
2021-11-06 20:30 | 44506.8542 | 0 | 10.5839 | 37.78
2021-11-06 21:00 | 44506.875 | 0 | 10.2209 | 37.78
2021-11-06 21:30 | 44506.8958 | 0 | 10.0766 | 37.78
2021-11-06 22:00 | 44506.9167 | 0 | 9.7914 | 37.78
2021-11-06 22:30 | 44506.9375 | 0 | 9.3242 | 37.78
2021-11-06 23:00 | 44506.9583 | 0 | 8.9952 | 37.78
2021-11-06 23:30 | 44506.9792 | 0 | 8.589 | 37.78
2021-11-07 | 44507 | 0 | 8.1343 | 37.78
2021-11-07 00:30 | 44507.0208 | 0 | 7.9155 | 37.78
2021-11-07 01:00 | 44507.0417 | 0 | 7.7368 | 37.78
2021-11-07 01:30 | 44507.0625 | 0 | 7.5425 | 37.78
2021-11-07 02:00 | 44507.0833 | 0 | 7.5627 | 37.78
2021-11-07 02:30 | 44507.1042 | 0 | 7.5061 | 37.78
2021-11-07 03:00 | 44507.125 | 0 | 7.4448 | 37.78
2021-11-07 03:30 | 44507.1458 | 0 | 7.3899 | 37.78
2021-11-07 04:00 | 44507.1667 | 0 | 7.4024 | 37.78
2021-11-07 04:30 | 44507.1875 | 0 | 7.3841 | 37.78
2021-11-07 05:00 | 44507.2083 | 0 | 7.3892 | 37.78
2021-11-07 05:30 | 44507.2292 | 0 | 7.4213 | 37.78
2021-11-07 06:00 | 44507.25 | 0 | 7.6618 | 37.78
2021-11-07 06:30 | 44507.2708 | 0 | 7.4895 | 37.78
2021-11-07 07:00 | 44507.2917 | 0 | 7.7878 | 37.78
2021-11-07 07:30 | 44507.3125 | 0 | 6.6908 | 37.78
2021-11-07 08:00 | 44507.3333 | 0 | 8.2591 | 37.78
2021-11-07 08:30 | 44507.3542 | 0 | 7.5978 | 37.78
2021-11-07 09:00 | 44507.375 | 0 | 8.3853 | 37.78
2021-11-07 09:30 | 44507.3958 | 0 | 6.8675 | 37.78
2021-11-07 10:00 | 44507.4167 | 0 | 7.5253 | 37.78
2021-11-07 10:30 | 44507.4375 | 0 | 6.6934 | 37.78
2021-11-07 11:00 | 44507.4583 | 0 | 8.6337 | 37.78
2021-11-07 11:30 | 44507.4792 | 0 | 8.6712 | 37.78
2021-11-07 12:00 | 44507.5 | 0 | 8.6183 | 37.78
2021-11-07 12:30 | 44507.5208 | 0 | 7.7693 | 37.78
2021-11-07 13:00 | 44507.5417 | 0 | 9.1621 | 37.78
2021-11-07 13:30 | 44507.5625 | 0 | 8.7184 | 37.78
2021-11-07 14:00 | 44507.5833 | 0 | 7.9723 | 37.78
2021-11-07 14:30 | 44507.6042 | 0 | 8.0429 | 37.78
2021-11-07 15:00 | 44507.625 | 0 | 9.7293 | 37.78
2021-11-07 15:30 | 44507.6458 | 0 | 10.3136 | 37.78
2021-11-07 16:00 | 44507.6667 | 0 | 10.6429 | 37.78
2021-11-07 16:30 | 44507.6875 | 0 | 11.3283 | 37.78
2021-11-07 17:00 | 44507.7083 | 0 | 11.6912 | 37.78
2021-11-07 17:30 | 44507.7292 | 0 | 12.0747 | 37.78
2021-11-07 18:00 | 44507.75 | 0 | 12.69 | 37.78
2021-11-07 18:30 | 44507.7708 | 0 | 12.9656 | 37.78
2021-11-07 19:00 | 44507.7917 | 0 | 12.5653 | 37.78
2021-11-07 19:30 | 44507.8125 | 0 | 12.362 | 37.78
2021-11-07 20:00 | 44507.8333 | 0 | 12.162 | 37.78
2021-11-07 20:30 | 44507.8542 | 0 | 11.6789 | 37.78
2021-11-07 21:00 | 44507.875 | 0 | 11.279 | 37.78
2021-11-07 21:30 | 44507.8958 | 0 | 10.9814 | 37.78
2021-11-07 22:00 | 44507.9167 | 0 | 10.6127 | 37.78
2021-11-07 22:30 | 44507.9375 | 0 | 9.9598 | 37.78
2021-11-07 23:00 | 44507.9583 | 0 | 9.4417 | 37.78
2021-11-07 23:30 | 44507.9792 | 0 | 9.0309 | 37.78
2021-11-08 | 44508 | 0 | 8.6017 | 37.78
2021-11-08 00:30 | 44508.0208 | 0 | 8.4183 | 37.78
2021-11-08 01:00 | 44508.0417 | 0 | 8.3324 | 37.78
2021-11-08 01:30 | 44508.0625 | 0 | 8.1205 | 37.78
2021-11-08 02:00 | 44508.0833 | 0 | 8.0146 | 37.78
2021-11-08 02:30 | 44508.1042 | 0 | 8.0386 | 37.78
2021-11-08 03:00 | 44508.125 | 0 | 7.9235 | 37.78
2021-11-08 03:30 | 44508.1458 | 0 | 8.1233 | 37.78
2021-11-08 04:00 | 44508.1667 | 0 | 8.4354 | 37.78
2021-11-08 04:30 | 44508.1875 | 0 | 8.9773 | 37.78
2021-11-08 05:00 | 44508.2083 | 0 | 9.4688 | 37.78
2021-11-08 05:30 | 44508.2292 | 0 | 10.026 | 37.78
2021-11-08 06:00 | 44508.25 | 0 | 10.9722 | 37.78
2021-11-08 06:30 | 44508.2708 | 0 | 11.5971 | 37.78
2021-11-08 07:00 | 44508.2917 | 0 | 13.0473 | 37.78
2021-11-08 07:30 | 44508.3125 | 0 | 12.4576 | 37.78
2021-11-08 08:00 | 44508.3333 | 0 | 12.4811 | 37.78
2021-11-08 08:30 | 44508.3542 | 0 | 13.1512 | 37.78
2021-11-08 09:00 | 44508.375 | 0 | 12.8673 | 37.78
2021-11-08 09:30 | 44508.3958 | 0 | 13.0656 | 37.78
2021-11-08 10:00 | 44508.4167 | 0 | 10.6149 | 37.78
2021-11-08 10:30 | 44508.4375 | 0 | 11.3903 | 37.78
2021-11-08 11:00 | 44508.4583 | 0 | 14.5443 | 37.78
2021-11-08 11:30 | 44508.4792 | 0 | 12.8805 | 37.78
2021-11-08 12:00 | 44508.5 | 0 | 11.7488 | 37.78
2021-11-08 12:30 | 44508.5208 | 0 | 11.4479 | 37.78
2021-11-08 13:00 | 44508.5417 | 0 | 12.4748 | 37.78
2021-11-08 13:30 | 44508.5625 | 0 | 14.9217 | 37.78
2021-11-08 14:00 | 44508.5833 | 0 | 14.5999 | 37.78
2021-11-08 14:30 | 44508.6042 | 0 | 14.9958 | 37.78
2021-11-08 15:00 | 44508.625 | 0 | 12.1911 | 37.78
2021-11-08 15:30 | 44508.6458 | 0 | 13.6145 | 37.78
2021-11-08 16:00 | 44508.6667 | 0 | 14.4331 | 37.78
2021-11-08 16:30 | 44508.6875 | 0 | 14.6039 | 37.78
2021-11-08 17:00 | 44508.7083 | 0 | 15.182 | 37.78
2021-11-08 17:30 | 44508.7292 | 0 | 15.2898 | 37.78
2021-11-08 18:00 | 44508.75 | 0 | 15.7353 | 37.78
2021-11-08 18:30 | 44508.7708 | 0 | 16.4932 | 37.78
2021-11-08 19:00 | 44508.7917 | 0 | 16.371 | 37.78
2021-11-08 19:30 | 44508.8125 | 0 | 16.1373 | 37.78
2021-11-08 20:00 | 44508.8333 | 0 | 15.5525 | 37.78
2021-11-08 20:30 | 44508.8542 | 0 | 14.6423 | 37.78
2021-11-08 21:00 | 44508.875 | 0 | 14.0459 | 37.78
2021-11-08 21:30 | 44508.8958 | 0 | 13.4398 | 37.78
2021-11-08 22:00 | 44508.9167 | 0 | 12.8397 | 37.78
2021-11-08 22:30 | 44508.9375 | 0 | 11.8745 | 37.78
2021-11-08 23:00 | 44508.9583 | 0 | 11.085 | 37.78
2021-11-08 23:30 | 44508.9792 | 0 | 10.5416 | 37.78
2021-11-09 | 44509 | 0 | 10.0733 | 37.78
2021-11-09 00:30 | 44509.0208 | 0 | 9.5555 | 37.78
2021-11-09 01:00 | 44509.0417 | 0 | 9.4983 | 37.78
2021-11-09 01:30 | 44509.0625 | 0 | 9.1618 | 37.78
2021-11-09 02:00 | 44509.0833 | 0 | 9.1667 | 37.78
2021-11-09 02:30 | 44509.1042 | 0 | 9.0871 | 37.78
2021-11-09 03:00 | 44509.125 | 0 | 8.8192 | 37.78
2021-11-09 03:30 | 44509.1458 | 0 | 9.0046 | 37.78
2021-11-09 04:00 | 44509.1667 | 0 | 9.284 | 37.78
2021-11-09 04:30 | 44509.1875 | 0 | 9.6325 | 37.78
2021-11-09 05:00 | 44509.2083 | 0 | 10.1853 | 37.78
2021-11-09 05:30 | 44509.2292 | 0 | 10.6268 | 37.78
2021-11-09 06:00 | 44509.25 | 0 | 11.3464 | 37.78
2021-11-09 06:30 | 44509.2708 | 0 | 11.5698 | 37.78
2021-11-09 07:00 | 44509.2917 | 0 | 12.1731 | 37.78
2021-11-09 07:30 | 44509.3125 | 0 | 12.3576 | 37.78
2021-11-09 08:00 | 44509.3333 | 0 | 12.2939 | 37.78
2021-11-09 08:30 | 44509.3542 | 0 | 13.1251 | 37.78
2021-11-09 09:00 | 44509.375 | 0 | 13.6481 | 37.78
2021-11-09 09:30 | 44509.3958 | 0 | 12.1629 | 37.78
2021-11-09 10:00 | 44509.4167 | 0 | 12.8407 | 37.78
2021-11-09 10:30 | 44509.4375 | 0 | 14.343 | 37.78
2021-11-09 11:00 | 44509.4583 | 0 | 13.3256 | 37.78
2021-11-09 11:30 | 44509.4792 | 0 | 13.9089 | 37.78
2021-11-09 12:00 | 44509.5 | 0 | 13.8683 | 37.78
2021-11-09 12:30 | 44509.5208 | 0 | 13.1677 | 37.78
2021-11-09 13:00 | 44509.5417 | 0 | 14.0234 | 37.78
2021-11-09 13:30 | 44509.5625 | 0 | 13.4246 | 37.78
2021-11-09 14:00 | 44509.5833 | 0 | 13.4903 | 37.78
2021-11-09 14:30 | 44509.6042 | 0 | 13.616 | 37.78
2021-11-09 15:00 | 44509.625 | 0 | 14.0933 | 37.78
2021-11-09 15:30 | 44509.6458 | 0 | 15.0765 | 37.78
2021-11-09 16:00 | 44509.6667 | 0 | 15.1487 | 37.78
2021-11-09 16:30 | 44509.6875 | 0 | 15.4124 | 37.78
2021-11-09 17:00 | 44509.7083 | 0 | 15.4674 | 37.78
2021-11-09 17:30 | 44509.7292 | 0 | 15.5464 | 37.78
2021-11-09 18:00 | 44509.75 | 0 | 15.4829 | 37.78
2021-11-09 18:30 | 44509.7708 | 0 | 16.0733 | 37.78
2021-11-09 19:00 | 44509.7917 | 0 | 16.3073 | 37.78
2021-11-09 19:30 | 44509.8125 | 0 | 15.7115 | 37.78
2021-11-09 20:00 | 44509.8333 | 0 | 15.4182 | 37.78
2021-11-09 20:30 | 44509.8542 | 0 | 14.9047 | 37.78
2021-11-09 21:00 | 44509.875 | 0 | 14.1706 | 37.78
2021-11-09 21:30 | 44509.8958 | 0 | 13.785 | 37.78
2021-11-09 22:00 | 44509.9167 | 0 | 13.2195 | 37.78
2021-11-09 22:30 | 44509.9375 | 0 | 12.2157 | 37.78
2021-11-09 23:00 | 44509.9583 | 0 | 11.5404 | 37.78
2021-11-09 23:30 | 44509.9792 | 0 | 11.0452 | 37.78
2021-11-10 | 44510 | 0 | 10.4065 | 37.78
2021-11-10 00:30 | 44510.0208 | 0 | 10.0321 | 37.78
2021-11-10 01:00 | 44510.0417 | 0 | 9.7909 | 37.78
2021-11-10 01:30 | 44510.0625 | 0 | 9.7536 | 37.78
2021-11-10 02:00 | 44510.0833 | 0 | 9.5676 | 37.78
2021-11-10 02:30 | 44510.1042 | 0 | 9.4565 | 37.78
2021-11-10 03:00 | 44510.125 | 0 | 9.3483 | 37.78
2021-11-10 03:30 | 44510.1458 | 0 | 9.4444 | 37.78
2021-11-10 04:00 | 44510.1667 | 0 | 9.7929 | 37.78
2021-11-10 04:30 | 44510.1875 | 0 | 10.1333 | 37.78
2021-11-10 05:00 | 44510.2083 | 0 | 10.6896 | 37.78
2021-11-10 05:30 | 44510.2292 | 0 | 11.2345 | 37.78
2021-11-10 06:00 | 44510.25 | 0 | 11.9281 | 37.78
2021-11-10 06:30 | 44510.2708 | 0 | 12.4072 | 37.78
2021-11-10 07:00 | 44510.2917 | 0 | 13.6822 | 37.78
2021-11-10 07:30 | 44510.3125 | 0 | 14.2646 | 37.78
2021-11-10 08:00 | 44510.3333 | 0 | 14.3054 | 37.78
2021-11-10 08:30 | 44510.3542 | 0 | 14.7621 | 37.78
2021-11-10 09:00 | 44510.375 | 0 | 14.6482 | 37.78
2021-11-10 09:30 | 44510.3958 | 0 | 14.0223 | 37.78
2021-11-10 10:00 | 44510.4167 | 0 | 12.503 | 37.78
2021-11-10 10:30 | 44510.4375 | 0 | 13.2135 | 37.78
2021-11-10 11:00 | 44510.4583 | 0 | 14.3627 | 37.78
2021-11-10 11:30 | 44510.4792 | 0 | 13.6456 | 37.78
2021-11-10 12:00 | 44510.5 | 0 | 13.6291 | 37.78
2021-11-10 12:30 | 44510.5208 | 0 | 13.9978 | 37.78
2021-11-10 13:00 | 44510.5417 | 0 | 15.9135 | 37.78
2021-11-10 13:30 | 44510.5625 | 0 | 16.3603 | 37.78
2021-11-10 14:00 | 44510.5833 | 0 | 13.7141 | 37.78
2021-11-10 14:30 | 44510.6042 | 0 | 15.8779 | 37.78
2021-11-10 15:00 | 44510.625 | 0 | 15.239 | 37.78
2021-11-10 15:30 | 44510.6458 | 0 | 16.6605 | 37.78
2021-11-10 16:00 | 44510.6667 | 0 | 16.0007 | 37.78
2021-11-10 16:30 | 44510.6875 | 0 | 17.0324 | 37.78
2021-11-10 17:00 | 44510.7083 | 0 | 17.1629 | 37.78
2021-11-10 17:30 | 44510.7292 | 0 | 17.3879 | 37.78
2021-11-10 18:00 | 44510.75 | 0 | 17.6169 | 37.78
2021-11-10 18:30 | 44510.7708 | 0 | 18.0402 | 37.78
2021-11-10 19:00 | 44510.7917 | 0 | 18.0333 | 37.78
2021-11-10 19:30 | 44510.8125 | 0 | 17.9297 | 37.78
2021-11-10 20:00 | 44510.8333 | 0 | 17.2101 | 37.78
2021-11-10 20:30 | 44510.8542 | 0 | 16.5678 | 37.78
2021-11-10 21:00 | 44510.875 | 0 | 15.7594 | 37.78
2021-11-10 21:30 | 44510.8958 | 0 | 15.1921 | 37.78
2021-11-10 22:00 | 44510.9167 | 0 | 14.4335 | 37.78
2021-11-10 22:30 | 44510.9375 | 0 | 13.456 | 37.78
2021-11-10 23:00 | 44510.9583 | 0 | 12.7659 | 37.78
2021-11-10 23:30 | 44510.9792 | 0 | 11.9001 | 37.78
2021-11-11 | 44511 | 0 | 11.199 | 37.78
2021-11-11 00:30 | 44511.0208 | 0 | 10.8295 | 37.78
2021-11-11 01:00 | 44511.0417 | 0 | 10.6556 | 37.78
2021-11-11 01:30 | 44511.0625 | 0 | 10.4551 | 37.78
2021-11-11 02:00 | 44511.0833 | 0 | 10.2461 | 37.78
2021-11-11 02:30 | 44511.1042 | 0 | 9.9838 | 37.78
2021-11-11 03:00 | 44511.125 | 0 | 9.7949 | 37.78
2021-11-11 03:30 | 44511.1458 | 0 | 9.8292 | 37.78
2021-11-11 04:00 | 44511.1667 | 0 | 10.0485 | 37.78
2021-11-11 04:30 | 44511.1875 | 0 | 10.6139 | 37.78
2021-11-11 05:00 | 44511.2083 | 0 | 11.0014 | 37.78
2021-11-11 05:30 | 44511.2292 | 0 | 11.3805 | 37.78
2021-11-11 06:00 | 44511.25 | 0 | 12.1154 | 37.78
2021-11-11 06:30 | 44511.2708 | 0 | 13.4061 | 37.78
2021-11-11 07:00 | 44511.2917 | 0 | 13.6123 | 37.78
2021-11-11 07:30 | 44511.3125 | 0 | 13.998 | 37.78
2021-11-11 08:00 | 44511.3333 | 0 | 14.5763 | 37.78
2021-11-11 08:30 | 44511.3542 | 0 | 14.6021 | 37.78
2021-11-11 09:00 | 44511.375 | 0 | 15.0756 | 37.78
2021-11-11 09:30 | 44511.3958 | 0 | 16.8185 | 37.78
2021-11-11 10:00 | 44511.4167 | 0 | 16.3684 | 37.78
2021-11-11 10:30 | 44511.4375 | 0 | 17.2097 | 37.78
2021-11-11 11:00 | 44511.4583 | 0 | 17.0319 | 37.78
2021-11-11 11:30 | 44511.4792 | 0 | 16.7203 | 37.78
2021-11-11 12:00 | 44511.5 | 0 | 18.9481 | 37.78
2021-11-11 12:30 | 44511.5208 | 0 | 17.5581 | 37.78
2021-11-11 13:00 | 44511.5417 | 0 | 16.5117 | 37.78
2021-11-11 13:30 | 44511.5625 | 0 | 17.8171 | 37.78
2021-11-11 14:00 | 44511.5833 | 0 | 18.9101 | 37.78
2021-11-11 14:30 | 44511.6042 | 0 | 18.417 | 37.78
2021-11-11 15:00 | 44511.625 | 0 | 17.5116 | 37.78
2021-11-11 15:30 | 44511.6458 | 0 | 16.9578 | 37.78
2021-11-11 16:00 | 44511.6667 | 0 | 16.3599 | 37.78
2021-11-11 16:30 | 44511.6875 | 0 | 16.2464 | 37.78
2021-11-11 17:00 | 44511.7083 | 0 | 16.1937 | 37.78
2021-11-11 17:30 | 44511.7292 | 0 | 16.5969 | 37.78
2021-11-11 18:00 | 44511.75 | 0 | 16.6615 | 37.78
2021-11-11 18:30 | 44511.7708 | 0 | 16.8611 | 37.78
2021-11-11 19:00 | 44511.7917 | 0 | 16.846 | 37.78
2021-11-11 19:30 | 44511.8125 | 0 | 16.663 | 37.78
2021-11-11 20:00 | 44511.8333 | 0 | 16.4138 | 37.78
2021-11-11 20:30 | 44511.8542 | 0 | 15.7393 | 37.78
2021-11-11 21:00 | 44511.875 | 0 | 15.4223 | 37.78
2021-11-11 21:30 | 44511.8958 | 0 | 14.8508 | 37.78
2021-11-11 22:00 | 44511.9167 | 0 | 14.1187 | 37.78
2021-11-11 22:30 | 44511.9375 | 0 | 13.1595 | 37.78
2021-11-11 23:00 | 44511.9583 | 0 | 12.3175 | 37.78
2021-11-11 23:30 | 44511.9792 | 0 | 11.761 | 37.78
2021-11-12 | 44512 | 0 | 11.018 | 37.78
2021-11-12 00:30 | 44512.0208 | 0 | 10.6 | 37.78
2021-11-12 01:00 | 44512.0417 | 0 | 10.5598 | 37.78
2021-11-12 01:30 | 44512.0625 | 0 | 10.2249 | 37.78
2021-11-12 02:00 | 44512.0833 | 0 | 10.1203 | 37.78
2021-11-12 02:30 | 44512.1042 | 0 | 10.1154 | 37.78
2021-11-12 03:00 | 44512.125 | 0 | 9.8803 | 37.78
2021-11-12 03:30 | 44512.1458 | 0 | 9.8795 | 37.78
2021-11-12 04:00 | 44512.1667 | 0 | 10.1151 | 37.78
2021-11-12 04:30 | 44512.1875 | 0 | 10.5089 | 37.78
2021-11-12 05:00 | 44512.2083 | 0 | 11.2162 | 37.78
2021-11-12 05:30 | 44512.2292 | 0 | 11.7149 | 37.78
2021-11-12 06:00 | 44512.25 | 0 | 12.8429 | 37.78
2021-11-12 06:30 | 44512.2708 | 0 | 13.5773 | 37.78
2021-11-12 07:00 | 44512.2917 | 0 | 14.4074 | 37.78
2021-11-12 07:30 | 44512.3125 | 0 | 14.6691 | 37.78
2021-11-12 08:00 | 44512.3333 | 0 | 14.8146 | 37.78
2021-11-12 08:30 | 44512.3542 | 0 | 14.5564 | 37.78
2021-11-12 09:00 | 44512.375 | 0 | 13.9788 | 37.78
2021-11-12 09:30 | 44512.3958 | 0 | 14.5032 | 37.78
2021-11-12 10:00 | 44512.4167 | 0 | 15.497 | 37.78
2021-11-12 10:30 | 44512.4375 | 0 | 14.7779 | 37.78
2021-11-12 11:00 | 44512.4583 | 0 | 14.6034 | 37.78
2021-11-12 11:30 | 44512.4792 | 0 | 15.187 | 37.78
2021-11-12 12:00 | 44512.5 | 0 | 15.1524 | 37.78
2021-11-12 12:30 | 44512.5208 | 0 | 14.7074 | 37.78
2021-11-12 13:00 | 44512.5417 | 0 | 14.3958 | 37.78
2021-11-12 13:30 | 44512.5625 | 0 | 14.1506 | 37.78
2021-11-12 14:00 | 44512.5833 | 0 | 13.7934 | 37.78
2021-11-12 14:30 | 44512.6042 | 0 | 14.4778 | 37.78
2021-11-12 15:00 | 44512.625 | 0 | 14.7351 | 37.78
2021-11-12 15:30 | 44512.6458 | 0 | 15.1034 | 37.78
2021-11-12 16:00 | 44512.6667 | 0 | 15.745 | 37.78
2021-11-12 16:30 | 44512.6875 | 0 | 17.5138 | 37.78
2021-11-12 17:00 | 44512.7083 | 0 | 17.2201 | 37.78
2021-11-12 17:30 | 44512.7292 | 0 | 17.0662 | 37.78
2021-11-12 18:00 | 44512.75 | 0 | 16.8507 | 37.78
2021-11-12 18:30 | 44512.7708 | 0 | 17.3032 | 37.78
2021-11-12 19:00 | 44512.7917 | 0 | 16.9532 | 37.78
2021-11-12 19:30 | 44512.8125 | 0 | 16.5192 | 37.78
2021-11-12 20:00 | 44512.8333 | 0 | 16.119 | 37.78
2021-11-12 20:30 | 44512.8542 | 0 | 15.2924 | 37.78
2021-11-12 21:00 | 44512.875 | 0 | 14.8457 | 37.78
2021-11-12 21:30 | 44512.8958 | 0 | 14.4401 | 37.78
2021-11-12 22:00 | 44512.9167 | 0 | 13.7397 | 37.78
2021-11-12 22:30 | 44512.9375 | 0 | 12.8786 | 37.78
2021-11-12 23:00 | 44512.9583 | 0 | 11.6532 | 37.78
2021-11-12 23:30 | 44512.9792 | 0 | 10.8836 | 37.78
2021-11-13 | 44513 | 0 | 10.0494 | 37.78
2021-11-13 00:30 | 44513.0208 | 0 | 9.5748 | 37.78
2021-11-13 01:00 | 44513.0417 | 0 | 9.078 | 37.78
2021-11-13 01:30 | 44513.0625 | 0 | 8.6333 | 37.78
2021-11-13 02:00 | 44513.0833 | 0 | 8.4315 | 37.78
2021-11-13 02:30 | 44513.1042 | 0 | 8.3131 | 37.78
2021-11-13 03:00 | 44513.125 | 0 | 8.0768 | 37.78
2021-11-13 03:30 | 44513.1458 | 0 | 8.0007 | 37.78
2021-11-13 04:00 | 44513.1667 | 0 | 8.0957 | 37.78
2021-11-13 04:30 | 44513.1875 | 0 | 8.0603 | 37.78
2021-11-13 05:00 | 44513.2083 | 0 | 8.1614 | 37.78
2021-11-13 05:30 | 44513.2292 | 0 | 7.9147 | 37.78
2021-11-13 06:00 | 44513.25 | 0 | 7.7055 | 37.78
2021-11-13 06:30 | 44513.2708 | 0 | 7.3288 | 37.78
2021-11-13 07:00 | 44513.2917 | 0 | 7.0069 | 37.78
2021-11-13 07:30 | 44513.3125 | 0 | 6.7445 | 37.78
2021-11-13 08:00 | 44513.3333 | 0 | 6.56 | 37.78
2021-11-13 08:30 | 44513.3542 | 0 | 6.2114 | 37.78
2021-11-13 09:00 | 44513.375 | 0 | 6.044 | 37.78
2021-11-13 09:30 | 44513.3958 | 0 | 5.9384 | 37.78
2021-11-13 10:00 | 44513.4167 | 0 | 5.7728 | 37.78
2021-11-13 10:30 | 44513.4375 | 0 | 5.6481 | 37.78
2021-11-13 11:00 | 44513.4583 | 0 | 5.4358 | 37.78
2021-11-13 11:30 | 44513.4792 | 0 | 5.48 | 37.78
2021-11-13 12:00 | 44513.5 | 0 | 5.5182 | 37.78
2021-11-13 12:30 | 44513.5208 | 0 | 5.5609 | 37.78
2021-11-13 13:00 | 44513.5417 | 0 | 5.6939 | 37.78
2021-11-13 13:30 | 44513.5625 | 0 | 6.2948 | 37.78
2021-11-13 14:00 | 44513.5833 | 0 | 6.6734 | 37.78
2021-11-13 14:30 | 44513.6042 | 0 | 7.5038 | 37.78
2021-11-13 15:00 | 44513.625 | 0 | 8.116 | 37.78
2021-11-13 15:30 | 44513.6458 | 0 | 8.5506 | 37.78
2021-11-13 16:00 | 44513.6667 | 0 | 9.3956 | 37.78
2021-11-13 16:30 | 44513.6875 | 0 | 10.2933 | 37.78
2021-11-13 17:00 | 44513.7083 | 0 | 10.8558 | 37.78
2021-11-13 17:30 | 44513.7292 | 0 | 11.2373 | 37.78
2021-11-13 18:00 | 44513.75 | 0 | 11.4811 | 37.78
2021-11-13 18:30 | 44513.7708 | 0 | 11.8887 | 37.78
2021-11-13 19:00 | 44513.7917 | 0 | 11.7371 | 37.78
2021-11-13 19:30 | 44513.8125 | 0 | 11.444 | 37.78
2021-11-13 20:00 | 44513.8333 | 0 | 11.0508 | 37.78
2021-11-13 20:30 | 44513.8542 | 0 | 10.6092 | 37.78
2021-11-13 21:00 | 44513.875 | 0 | 10.1976 | 37.78
2021-11-13 21:30 | 44513.8958 | 0 | 10.033 | 37.78
2021-11-13 22:00 | 44513.9167 | 0 | 9.7409 | 37.78
2021-11-13 22:30 | 44513.9375 | 0 | 9.3501 | 37.78
2021-11-13 23:00 | 44513.9583 | 0 | 8.8814 | 37.78
2021-11-13 23:30 | 44513.9792 | 0 | 8.4894 | 37.78
2021-11-14 | 44514 | 0 | 8.0188 | 37.78
2021-11-14 00:30 | 44514.0208 | 0 | 7.6236 | 37.78
2021-11-14 01:00 | 44514.0417 | 0 | 7.465 | 37.78
2021-11-14 01:30 | 44514.0625 | 0 | 7.3063 | 37.78
2021-11-14 02:00 | 44514.0833 | 0 | 7.1597 | 37.78
2021-11-14 02:30 | 44514.1042 | 0 | 6.9227 | 37.78
2021-11-14 03:00 | 44514.125 | 0 | 7.0823 | 37.78
2021-11-14 03:30 | 44514.1458 | 0 | 7.2117 | 37.78
2021-11-14 04:00 | 44514.1667 | 0 | 6.8742 | 37.78
2021-11-14 04:30 | 44514.1875 | 0 | 6.7232 | 37.78
2021-11-14 05:00 | 44514.2083 | 0 | 6.7516 | 37.78
2021-11-14 05:30 | 44514.2292 | 0 | 6.5198 | 37.78
2021-11-14 06:00 | 44514.25 | 0 | 6.1739 | 37.78
2021-11-14 06:30 | 44514.2708 | 0 | 6.2241 | 37.78
2021-11-14 07:00 | 44514.2917 | 0 | 6.2241 | 37.78
2021-11-14 07:30 | 44514.3125 | 0 | 5.9091 | 37.78
2021-11-14 08:00 | 44514.3333 | 0 | 5.8727 | 37.78
2021-11-14 08:30 | 44514.3542 | 0 | 5.798 | 37.78
2021-11-14 09:00 | 44514.375 | 0 | 5.9082 | 37.78
2021-11-14 09:30 | 44514.3958 | 0 | 5.9104 | 37.78
2021-11-14 10:00 | 44514.4167 | 0 | 5.6594 | 37.78
2021-11-14 10:30 | 44514.4375 | 0 | 5.6715 | 37.78
2021-11-14 11:00 | 44514.4583 | 0 | 5.7716 | 37.78
2021-11-14 11:30 | 44514.4792 | 0 | 5.9554 | 37.78
2021-11-14 12:00 | 44514.5 | 0 | 5.9341 | 37.78
2021-11-14 12:30 | 44514.5208 | 0 | 6.1046 | 37.78
2021-11-14 13:00 | 44514.5417 | 0 | 6.2304 | 37.78
2021-11-14 13:30 | 44514.5625 | 0 | 6.7542 | 37.78
2021-11-14 14:00 | 44514.5833 | 0 | 7.3708 | 37.78
2021-11-14 14:30 | 44514.6042 | 0 | 7.3061 | 37.78
2021-11-14 15:00 | 44514.625 | 0 | 8.1961 | 37.78
2021-11-14 15:30 | 44514.6458 | 0 | 8.8873 | 37.78
2021-11-14 16:00 | 44514.6667 | 0 | 9.715 | 37.78
2021-11-14 16:30 | 44514.6875 | 0 | 10.5888 | 37.78
2021-11-14 17:00 | 44514.7083 | 0 | 11.4009 | 37.78
2021-11-14 17:30 | 44514.7292 | 0 | 11.9578 | 37.78
2021-11-14 18:00 | 44514.75 | 0 | 12.1927 | 37.78
2021-11-14 18:30 | 44514.7708 | 0 | 12.6193 | 37.78
2021-11-14 19:00 | 44514.7917 | 0 | 12.3866 | 37.78
2021-11-14 19:30 | 44514.8125 | 0 | 12.1571 | 37.78
2021-11-14 20:00 | 44514.8333 | 0 | 11.8429 | 37.78
2021-11-14 20:30 | 44514.8542 | 0 | 11.2688 | 37.78
2021-11-14 21:00 | 44514.875 | 0 | 10.8906 | 37.78
2021-11-14 21:30 | 44514.8958 | 0 | 10.4259 | 37.78
2021-11-14 22:00 | 44514.9167 | 0 | 9.7675 | 37.78
2021-11-14 22:30 | 44514.9375 | 0 | 9.1198 | 37.78
2021-11-14 23:00 | 44514.9583 | 0 | 8.5276 | 37.78
2021-11-14 23:30 | 44514.9792 | 0 | 8.2745 | 37.78
2021-11-15 | 44515 | 0 | 7.897 | 37.78
2021-11-15 00:30 | 44515.0208 | 0 | 7.6994 | 37.78
2021-11-15 01:00 | 44515.0417 | 0 | 7.5212 | 37.78
2021-11-15 01:30 | 44515.0625 | 0 | 7.3369 | 37.78
2021-11-15 02:00 | 44515.0833 | 0 | 7.3393 | 37.78
2021-11-15 02:30 | 44515.1042 | 0 | 7.2745 | 37.78
2021-11-15 03:00 | 44515.125 | 0 | 7.2088 | 37.78
2021-11-15 03:30 | 44515.1458 | 0 | 7.4805 | 37.78
2021-11-15 04:00 | 44515.1667 | 0 | 7.703 | 37.78
2021-11-15 04:30 | 44515.1875 | 0 | 8.0032 | 37.78
2021-11-15 05:00 | 44515.2083 | 0 | 8.3466 | 37.78
2021-11-15 05:30 | 44515.2292 | 0 | 8.6826 | 37.78
2021-11-15 06:00 | 44515.25 | 0 | 9.0102 | 37.78
2021-11-15 06:30 | 44515.2708 | 0 | 9.2475 | 37.78
2021-11-15 07:00 | 44515.2917 | 0 | 9.6065 | 37.78
2021-11-15 07:30 | 44515.3125 | 0 | 9.5893 | 37.78
2021-11-15 08:00 | 44515.3333 | 0 | 9.3301 | 37.78
2021-11-15 08:30 | 44515.3542 | 0 | 9.0922 | 37.78
2021-11-15 09:00 | 44515.375 | 0 | 9.065 | 37.78
2021-11-15 09:30 | 44515.3958 | 0 | 8.9599 | 37.78
2021-11-15 10:00 | 44515.4167 | 0 | 8.9036 | 37.78
2021-11-15 10:30 | 44515.4375 | 0 | 9.0221 | 37.78
2021-11-15 11:00 | 44515.4583 | 0 | 9.0358 | 37.78
2021-11-15 11:30 | 44515.4792 | 0 | 9.3213 | 37.78
2021-11-15 12:00 | 44515.5 | 0 | 9.3864 | 37.78
2021-11-15 12:30 | 44515.5208 | 0 | 9.6834 | 37.78
2021-11-15 13:00 | 44515.5417 | 0 | 10.2273 | 37.78
2021-11-15 13:30 | 44515.5625 | 0 | 10.7621 | 37.78
2021-11-15 14:00 | 44515.5833 | 0 | 11.1992 | 37.78
2021-11-15 14:30 | 44515.6042 | 0 | 11.8362 | 37.78
2021-11-15 15:00 | 44515.625 | 0 | 12.3824 | 37.78
2021-11-15 15:30 | 44515.6458 | 0 | 13.1183 | 37.78
2021-11-15 16:00 | 44515.6667 | 0 | 13.7388 | 37.78
2021-11-15 16:30 | 44515.6875 | 0 | 14.4991 | 37.78
2021-11-15 17:00 | 44515.7083 | 0 | 14.9934 | 37.78
2021-11-15 17:30 | 44515.7292 | 0 | 15.2707 | 37.78
2021-11-15 18:00 | 44515.75 | 0 | 15.4308 | 37.78
2021-11-15 18:30 | 44515.7708 | 0 | 15.993 | 37.78
2021-11-15 19:00 | 44515.7917 | 0 | 15.6467 | 37.78
2021-11-15 19:30 | 44515.8125 | 0 | 15.0672 | 37.78
2021-11-15 20:00 | 44515.8333 | 0 | 14.5239 | 37.78
2021-11-15 20:30 | 44515.8542 | 0 | 13.9863 | 37.78
2021-11-15 21:00 | 44515.875 | 0 | 13.5917 | 37.78
2021-11-15 21:30 | 44515.8958 | 0 | 12.829 | 37.78
2021-11-15 22:00 | 44515.9167 | 0 | 11.9712 | 37.78
2021-11-15 22:30 | 44515.9375 | 0 | 10.9562 | 37.78
2021-11-15 23:00 | 44515.9583 | 0 | 10.1633 | 37.78
2021-11-15 23:30 | 44515.9792 | 0 | 9.6133 | 37.78
2021-11-16 | 44516 | 0 | 9.0502 | 37.78
2021-11-16 00:30 | 44516.0208 | 0 | 8.5996 | 37.78
2021-11-16 01:00 | 44516.0417 | 0 | 8.5336 | 37.78
2021-11-16 01:30 | 44516.0625 | 0 | 8.4086 | 37.78
2021-11-16 02:00 | 44516.0833 | 0 | 8.2163 | 37.78
2021-11-16 02:30 | 44516.1042 | 0 | 8.1532 | 37.78
2021-11-16 03:00 | 44516.125 | 0 | 7.9342 | 37.78
2021-11-16 03:30 | 44516.1458 | 0 | 8.0922 | 37.78
2021-11-16 04:00 | 44516.1667 | 0 | 8.2352 | 37.78
2021-11-16 04:30 | 44516.1875 | 0 | 8.6575 | 37.78
2021-11-16 05:00 | 44516.2083 | 0 | 8.9521 | 37.78
2021-11-16 05:30 | 44516.2292 | 0 | 9.2553 | 37.78
2021-11-16 06:00 | 44516.25 | 0 | 9.4996 | 37.78
2021-11-16 06:30 | 44516.2708 | 0 | 10.0825 | 37.78
2021-11-16 07:00 | 44516.2917 | 0 | 10.7212 | 37.78
2021-11-16 07:30 | 44516.3125 | 0 | 10.8725 | 37.78
2021-11-16 08:00 | 44516.3333 | 0 | 10.6901 | 37.78
2021-11-16 08:30 | 44516.3542 | 0 | 10.7198 | 37.78
2021-11-16 09:00 | 44516.375 | 0 | 10.7275 | 37.78
2021-11-16 09:30 | 44516.3958 | 0 | 11.1652 | 37.78
2021-11-16 10:00 | 44516.4167 | 0 | 11.3309 | 37.78
2021-11-16 10:30 | 44516.4375 | 0 | 11.7215 | 37.78
2021-11-16 11:00 | 44516.4583 | 0 | 9.9868 | 37.78
2021-11-16 11:30 | 44516.4792 | 0 | 10.9042 | 37.78
2021-11-16 12:00 | 44516.5 | 0 | 10.5899 | 37.78
2021-11-16 12:30 | 44516.5208 | 0 | 11.3984 | 37.78
2021-11-16 13:00 | 44516.5417 | 0 | 11.7316 | 37.78
2021-11-16 13:30 | 44516.5625 | 0 | 11.1751 | 37.78
2021-11-16 14:00 | 44516.5833 | 0 | 11.6013 | 37.78
2021-11-16 14:30 | 44516.6042 | 0 | 12.4784 | 37.78
2021-11-16 15:00 | 44516.625 | 0 | 12.4645 | 37.78
2021-11-16 15:30 | 44516.6458 | 0 | 13.5796 | 37.78
2021-11-16 16:00 | 44516.6667 | 0 | 13.8521 | 37.78
2021-11-16 16:30 | 44516.6875 | 0 | 15.0614 | 37.78
2021-11-16 17:00 | 44516.7083 | 0 | 15.1409 | 37.78
2021-11-16 17:30 | 44516.7292 | 0 | 15.072 | 37.78
2021-11-16 18:00 | 44516.75 | 0 | 15.0579 | 37.78
2021-11-16 18:30 | 44516.7708 | 0 | 15.6427 | 37.78
2021-11-16 19:00 | 44516.7917 | 0 | 15.5763 | 37.78
2021-11-16 19:30 | 44516.8125 | 0 | 15.1186 | 37.78
2021-11-16 20:00 | 44516.8333 | 0 | 14.7031 | 37.78
2021-11-16 20:30 | 44516.8542 | 0 | 14.1996 | 37.78
2021-11-16 21:00 | 44516.875 | 0 | 13.5621 | 37.78
2021-11-16 21:30 | 44516.8958 | 0 | 13.0009 | 37.78
2021-11-16 22:00 | 44516.9167 | 0 | 12.2816 | 37.78
2021-11-16 22:30 | 44516.9375 | 0 | 11.3219 | 37.78
2021-11-16 23:00 | 44516.9583 | 0 | 10.6903 | 37.78
2021-11-16 23:30 | 44516.9792 | 0 | 10.178 | 37.78
2021-11-17 | 44517 | 0 | 9.7313 | 37.78
2021-11-17 00:30 | 44517.0208 | 0 | 9.326 | 37.78
2021-11-17 01:00 | 44517.0417 | 0 | 8.9355 | 37.78
2021-11-17 01:30 | 44517.0625 | 0 | 8.8742 | 37.78
2021-11-17 02:00 | 44517.0833 | 0 | 8.7076 | 37.78
2021-11-17 02:30 | 44517.1042 | 0 | 8.624 | 37.78
2021-11-17 03:00 | 44517.125 | 0 | 8.5729 | 37.78
2021-11-17 03:30 | 44517.1458 | 0 | 8.6688 | 37.78
2021-11-17 04:00 | 44517.1667 | 0 | 8.8762 | 37.78
2021-11-17 04:30 | 44517.1875 | 0 | 9.2098 | 37.78
2021-11-17 05:00 | 44517.2083 | 0 | 9.6033 | 37.78
2021-11-17 05:30 | 44517.2292 | 0 | 10.1107 | 37.78
2021-11-17 06:00 | 44517.25 | 0 | 10.4022 | 37.78
2021-11-17 06:30 | 44517.2708 | 0 | 11.3785 | 37.78
2021-11-17 07:00 | 44517.2917 | 0 | 11.5205 | 37.78
2021-11-17 07:30 | 44517.3125 | 0 | 12.3488 | 37.78
2021-11-17 08:00 | 44517.3333 | 0 | 12.7598 | 37.78
2021-11-17 08:30 | 44517.3542 | 0 | 12.0284 | 37.78
2021-11-17 09:00 | 44517.375 | 0 | 11.5619 | 37.78
2021-11-17 09:30 | 44517.3958 | 0 | 11.9113 | 37.78
2021-11-17 10:00 | 44517.4167 | 0 | 13.3826 | 37.78
2021-11-17 10:30 | 44517.4375 | 0 | 11.4857 | 37.78
2021-11-17 11:00 | 44517.4583 | 0 | 13.521 | 37.78
2021-11-17 11:30 | 44517.4792 | 0 | 14.5294 | 37.78
2021-11-17 12:00 | 44517.5 | 0 | 11.9808 | 37.78
2021-11-17 12:30 | 44517.5208 | 0 | 11.6628 | 37.78
2021-11-17 13:00 | 44517.5417 | 0 | 13.1958 | 37.78
2021-11-17 13:30 | 44517.5625 | 0 | 12.1659 | 37.78
2021-11-17 14:00 | 44517.5833 | 0 | 11.2616 | 37.78
2021-11-17 14:30 | 44517.6042 | 0 | 13.1813 | 37.78
2021-11-17 15:00 | 44517.625 | 0 | 12.8623 | 37.78
2021-11-17 15:30 | 44517.6458 | 0 | 12.6519 | 37.78
2021-11-17 16:00 | 44517.6667 | 0 | 12.9142 | 37.78
2021-11-17 16:30 | 44517.6875 | 0 | 13.6595 | 37.78
2021-11-17 17:00 | 44517.7083 | 0 | 13.1571 | 37.78
2021-11-17 17:30 | 44517.7292 | 0 | 13.6179 | 37.78
2021-11-17 18:00 | 44517.75 | 0 | 13.9018 | 37.78
2021-11-17 18:30 | 44517.7708 | 0 | 14.3592 | 37.78
2021-11-17 19:00 | 44517.7917 | 0 | 14.1087 | 37.78
2021-11-17 19:30 | 44517.8125 | 0 | 13.8459 | 37.78
2021-11-17 20:00 | 44517.8333 | 0 | 13.7052 | 37.78
2021-11-17 20:30 | 44517.8542 | 0 | 12.8942 | 37.78
2021-11-17 21:00 | 44517.875 | 0 | 12.6034 | 37.78
2021-11-17 21:30 | 44517.8958 | 0 | 12.2413 | 37.78
2021-11-17 22:00 | 44517.9167 | 0 | 11.8095 | 37.78
2021-11-17 22:30 | 44517.9375 | 0 | 11.0761 | 37.78
2021-11-17 23:00 | 44517.9583 | 0 | 10.3659 | 37.78
2021-11-17 23:30 | 44517.9792 | 0 | 9.8077 | 37.78
2021-11-18 | 44518 | 0 | 9.2286 | 37.78
2021-11-18 00:30 | 44518.0208 | 0 | 8.9127 | 37.78
2021-11-18 01:00 | 44518.0417 | 0 | 8.7009 | 37.78
2021-11-18 01:30 | 44518.0625 | 0 | 8.5634 | 37.78
2021-11-18 02:00 | 44518.0833 | 0 | 8.471 | 37.78
2021-11-18 02:30 | 44518.1042 | 0 | 8.4556 | 37.78
2021-11-18 03:00 | 44518.125 | 0 | 8.5218 | 37.78
2021-11-18 03:30 | 44518.1458 | 0 | 8.5796 | 37.78
2021-11-18 04:00 | 44518.1667 | 0 | 8.7982 | 37.78
2021-11-18 04:30 | 44518.1875 | 0 | 9.1552 | 37.78
2021-11-18 05:00 | 44518.2083 | 0 | 9.7633 | 37.78
2021-11-18 05:30 | 44518.2292 | 0 | 10.0326 | 37.78
2021-11-18 06:00 | 44518.25 | 0 | 10.4455 | 37.78
2021-11-18 06:30 | 44518.2708 | 0 | 11.6161 | 37.78
2021-11-18 07:00 | 44518.2917 | 0 | 11.9429 | 37.78
2021-11-18 07:30 | 44518.3125 | 0 | 12.7396 | 37.78
2021-11-18 08:00 | 44518.3333 | 0 | 11.9929 | 37.78
2021-11-18 08:30 | 44518.3542 | 0 | 12.1037 | 37.78
2021-11-18 09:00 | 44518.375 | 0 | 11.3536 | 37.78
2021-11-18 09:30 | 44518.3958 | 0 | 10.3067 | 37.78
2021-11-18 10:00 | 44518.4167 | 0 | 10.3181 | 37.78
2021-11-18 10:30 | 44518.4375 | 0 | 10.6332 | 37.78
2021-11-18 11:00 | 44518.4583 | 0 | 11.5297 | 37.78
2021-11-18 11:30 | 44518.4792 | 0 | 10.2244 | 37.78
2021-11-18 12:00 | 44518.5 | 0 | 10.1029 | 37.78
2021-11-18 12:30 | 44518.5208 | 0 | 10.8359 | 37.78
2021-11-18 13:00 | 44518.5417 | 0 | 10.9999 | 37.78
2021-11-18 13:30 | 44518.5625 | 0 | 11.5501 | 37.78
2021-11-18 14:00 | 44518.5833 | 0 | 11.3285 | 37.78
2021-11-18 14:30 | 44518.6042 | 0 | 13.0047 | 37.78
2021-11-18 15:00 | 44518.625 | 0 | 13.1475 | 37.78
2021-11-18 15:30 | 44518.6458 | 0 | 12.737 | 37.78
2021-11-18 16:00 | 44518.6667 | 0 | 11.8311 | 37.78
2021-11-18 16:30 | 44518.6875 | 0 | 12.7524 | 37.78
2021-11-18 17:00 | 44518.7083 | 0 | 13.3904 | 37.78
2021-11-18 17:30 | 44518.7292 | 0 | 14.1255 | 37.78
2021-11-18 18:00 | 44518.75 | 0 | 13.9234 | 37.78
2021-11-18 18:30 | 44518.7708 | 0 | 14.337 | 37.78
2021-11-18 19:00 | 44518.7917 | 0 | 14.2391 | 37.78
2021-11-18 19:30 | 44518.8125 | 0 | 13.8449 | 37.78
2021-11-18 20:00 | 44518.8333 | 0 | 13.4072 | 37.78
2021-11-18 20:30 | 44518.8542 | 0 | 12.9321 | 37.78
2021-11-18 21:00 | 44518.875 | 0 | 12.6062 | 37.78
2021-11-18 21:30 | 44518.8958 | 0 | 12.2216 | 37.78
2021-11-18 22:00 | 44518.9167 | 0 | 11.7088 | 37.78
2021-11-18 22:30 | 44518.9375 | 0 | 10.9525 | 37.78
2021-11-18 23:00 | 44518.9583 | 0 | 10.209 | 37.78
2021-11-18 23:30 | 44518.9792 | 0 | 9.8075 | 37.78
2021-11-19 | 44519 | 0 | 9.2887 | 37.78
2021-11-19 00:30 | 44519.0208 | 0 | 8.7852 | 37.78
2021-11-19 01:00 | 44519.0417 | 0 | 8.5896 | 37.78
2021-11-19 01:30 | 44519.0625 | 0 | 8.4439 | 37.78
2021-11-19 02:00 | 44519.0833 | 0 | 8.3194 | 37.78
2021-11-19 02:30 | 44519.1042 | 0 | 8.3295 | 37.78
2021-11-19 03:00 | 44519.125 | 0 | 8.1904 | 37.78
2021-11-19 03:30 | 44519.1458 | 0 | 8.3083 | 37.78
2021-11-19 04:00 | 44519.1667 | 0 | 8.6015 | 37.78
2021-11-19 04:30 | 44519.1875 | 0 | 8.9775 | 37.78
2021-11-19 05:00 | 44519.2083 | 0 | 9.3048 | 37.78
2021-11-19 05:30 | 44519.2292 | 0 | 9.56 | 37.78
2021-11-19 06:00 | 44519.25 | 0 | 9.7469 | 37.78
2021-11-19 06:30 | 44519.2708 | 0 | 10.0284 | 37.78
2021-11-19 07:00 | 44519.2917 | 0 | 10.6231 | 37.78
2021-11-19 07:30 | 44519.3125 | 0 | 10.5525 | 37.78
2021-11-19 08:00 | 44519.3333 | 0 | 11.4283 | 37.78
2021-11-19 08:30 | 44519.3542 | 0 | 10.9718 | 37.78
2021-11-19 09:00 | 44519.375 | 0 | 10.455 | 37.78
2021-11-19 09:30 | 44519.3958 | 0 | 11.7948 | 37.78
2021-11-19 10:00 | 44519.4167 | 0 | 11.608 | 37.78
2021-11-19 10:30 | 44519.4375 | 0 | 11.3286 | 37.78
2021-11-19 11:00 | 44519.4583 | 0 | 10.6881 | 37.78
2021-11-19 11:30 | 44519.4792 | 0 | 10.6317 | 37.78
2021-11-19 12:00 | 44519.5 | 0 | 10.6421 | 37.78
2021-11-19 12:30 | 44519.5208 | 0 | 10.5377 | 37.78
2021-11-19 13:00 | 44519.5417 | 0 | 10.8815 | 37.78
2021-11-19 13:30 | 44519.5625 | 0 | 11.7217 | 37.78
2021-11-19 14:00 | 44519.5833 | 0 | 11.7635 | 37.78
2021-11-19 14:30 | 44519.6042 | 0 | 12.7989 | 37.78
2021-11-19 15:00 | 44519.625 | 0 | 13.3381 | 37.78
2021-11-19 15:30 | 44519.6458 | 0 | 13.3649 | 37.78
2021-11-19 16:00 | 44519.6667 | 0 | 13.5579 | 37.78
2021-11-19 16:30 | 44519.6875 | 0 | 14.4516 | 37.78
2021-11-19 17:00 | 44519.7083 | 0 | 14.1568 | 37.78
2021-11-19 17:30 | 44519.7292 | 0 | 14.3879 | 37.78
2021-11-19 18:00 | 44519.75 | 0 | 14.2819 | 37.78
2021-11-19 18:30 | 44519.7708 | 0 | 14.5665 | 37.78
2021-11-19 19:00 | 44519.7917 | 0 | 14.4401 | 37.78
2021-11-19 19:30 | 44519.8125 | 0 | 14.0806 | 37.78
2021-11-19 20:00 | 44519.8333 | 0 | 13.6774 | 37.78
2021-11-19 20:30 | 44519.8542 | 0 | 13.4134 | 37.78
2021-11-19 21:00 | 44519.875 | 0 | 12.972 | 37.78
2021-11-19 21:30 | 44519.8958 | 0 | 12.5364 | 37.78
2021-11-19 22:00 | 44519.9167 | 0 | 12.1455 | 37.78
2021-11-19 22:30 | 44519.9375 | 0 | 11.4437 | 37.78
2021-11-19 23:00 | 44519.9583 | 0 | 10.9447 | 37.78
2021-11-19 23:30 | 44519.9792 | 0 | 10.3921 | 37.78
2021-11-20 | 44520 | 0 | 9.742 | 37.78
2021-11-20 00:30 | 44520.0208 | 0 | 9.3476 | 37.78
2021-11-20 01:00 | 44520.0417 | 0 | 9.183 | 37.78
2021-11-20 01:30 | 44520.0625 | 0 | 8.8692 | 37.78
2021-11-20 02:00 | 44520.0833 | 0 | 8.747 | 37.78
2021-11-20 02:30 | 44520.1042 | 0 | 8.7208 | 37.78
2021-11-20 03:00 | 44520.125 | 0 | 8.5613 | 37.78
2021-11-20 03:30 | 44520.1458 | 0 | 8.4474 | 37.78
2021-11-20 04:00 | 44520.1667 | 0 | 8.5678 | 37.78
2021-11-20 04:30 | 44520.1875 | 0 | 8.5382 | 37.78
2021-11-20 05:00 | 44520.2083 | 0 | 8.6543 | 37.78
2021-11-20 05:30 | 44520.2292 | 0 | 8.6535 | 37.78
2021-11-20 06:00 | 44520.25 | 0 | 8.3787 | 37.78
2021-11-20 06:30 | 44520.2708 | 0 | 8.4417 | 37.78
2021-11-20 07:00 | 44520.2917 | 0 | 8.3783 | 37.78
2021-11-20 07:30 | 44520.3125 | 0 | 8.1745 | 37.78
2021-11-20 08:00 | 44520.3333 | 0 | 8.1517 | 37.78
2021-11-20 08:30 | 44520.3542 | 0 | 8.2847 | 37.78
2021-11-20 09:00 | 44520.375 | 0 | 8.5506 | 37.78
2021-11-20 09:30 | 44520.3958 | 0 | 8.6299 | 37.78
2021-11-20 10:00 | 44520.4167 | 0 | 8.5023 | 37.78
2021-11-20 10:30 | 44520.4375 | 0 | 9.11 | 37.78
2021-11-20 11:00 | 44520.4583 | 0 | 9.3063 | 37.78
2021-11-20 11:30 | 44520.4792 | 0 | 9.5661 | 37.78
2021-11-20 12:00 | 44520.5 | 0 | 9.915 | 37.78
2021-11-20 12:30 | 44520.5208 | 0 | 9.9712 | 37.78
2021-11-20 13:00 | 44520.5417 | 0 | 10.3704 | 37.78
2021-11-20 13:30 | 44520.5625 | 0 | 10.7356 | 37.78
2021-11-20 14:00 | 44520.5833 | 0 | 10.8855 | 37.78
2021-11-20 14:30 | 44520.6042 | 0 | 11.5432 | 37.78
2021-11-20 15:00 | 44520.625 | 0 | 12.5738 | 37.78
2021-11-20 15:30 | 44520.6458 | 0 | 13.8422 | 37.78
2021-11-20 16:00 | 44520.6667 | 0 | 14.0079 | 37.78
2021-11-20 16:30 | 44520.6875 | 0 | 13.7984 | 37.78
2021-11-20 17:00 | 44520.7083 | 0 | 13.8118 | 37.78
2021-11-20 17:30 | 44520.7292 | 0 | 13.8763 | 37.78
2021-11-20 18:00 | 44520.75 | 0 | 13.7382 | 37.78
2021-11-20 18:30 | 44520.7708 | 0 | 14.0149 | 37.78
2021-11-20 19:00 | 44520.7917 | 0 | 13.6219 | 37.78
2021-11-20 19:30 | 44520.8125 | 0 | 13.3004 | 37.78
2021-11-20 20:00 | 44520.8333 | 0 | 13.0126 | 37.78
2021-11-20 20:30 | 44520.8542 | 0 | 12.4451 | 37.78
2021-11-20 21:00 | 44520.875 | 0 | 11.989 | 37.78
2021-11-20 21:30 | 44520.8958 | 0 | 11.7441 | 37.78
2021-11-20 22:00 | 44520.9167 | 0 | 11.3676 | 37.78
2021-11-20 22:30 | 44520.9375 | 0 | 10.9074 | 37.78
2021-11-20 23:00 | 44520.9583 | 0 | 10.4198 | 37.78
2021-11-20 23:30 | 44520.9792 | 0 | 9.9189 | 37.78
2021-11-21 | 44521 | 0 | 9.3912 | 37.78
2021-11-21 00:30 | 44521.0208 | 0 | 9.0838 | 37.78
2021-11-21 01:00 | 44521.0417 | 0 | 8.7898 | 37.78
2021-11-21 01:30 | 44521.0625 | 0 | 8.6868 | 37.78
2021-11-21 02:00 | 44521.0833 | 0 | 8.5257 | 37.78
2021-11-21 02:30 | 44521.1042 | 0 | 8.5914 | 37.78
2021-11-21 03:00 | 44521.125 | 0 | 8.363 | 37.78
2021-11-21 03:30 | 44521.1458 | 0 | 8.2536 | 37.78
2021-11-21 04:00 | 44521.1667 | 0 | 8.2556 | 37.78
2021-11-21 04:30 | 44521.1875 | 0 | 8.1468 | 37.78
2021-11-21 05:00 | 44521.2083 | 0 | 8.1979 | 37.78
2021-11-21 05:30 | 44521.2292 | 0 | 8.1032 | 37.78
2021-11-21 06:00 | 44521.25 | 0 | 8.2351 | 37.78
2021-11-21 06:30 | 44521.2708 | 0 | 8.0755 | 37.78
2021-11-21 07:00 | 44521.2917 | 0 | 8.6996 | 37.78
2021-11-21 07:30 | 44521.3125 | 0 | 9.411 | 37.78
2021-11-21 08:00 | 44521.3333 | 0 | 8.8172 | 37.78
2021-11-21 08:30 | 44521.3542 | 0 | 7.5927 | 37.78
2021-11-21 09:00 | 44521.375 | 0 | 7.5104 | 37.78
2021-11-21 09:30 | 44521.3958 | 0 | 8.9197 | 37.78
2021-11-21 10:00 | 44521.4167 | 0 | 11.0635 | 37.78
2021-11-21 10:30 | 44521.4375 | 0 | 10.4484 | 37.78
2021-11-21 11:00 | 44521.4583 | 0 | 8.3209 | 37.78
2021-11-21 11:30 | 44521.4792 | 0 | 10.6994 | 37.78
2021-11-21 12:00 | 44521.5 | 0 | 10.2855 | 37.78
2021-11-21 12:30 | 44521.5208 | 0 | 10.4595 | 37.78
2021-11-21 13:00 | 44521.5417 | 0 | 9.3612 | 37.78
2021-11-21 13:30 | 44521.5625 | 0 | 10.0937 | 37.78
2021-11-21 14:00 | 44521.5833 | 0 | 10.0757 | 37.78
2021-11-21 14:30 | 44521.6042 | 0 | 10.0101 | 37.78
2021-11-21 15:00 | 44521.625 | 0 | 10.6992 | 37.78
2021-11-21 15:30 | 44521.6458 | 0 | 11.8048 | 37.78
2021-11-21 16:00 | 44521.6667 | 0 | 11.4779 | 37.78
2021-11-21 16:30 | 44521.6875 | 0 | 12.4234 | 37.78
2021-11-21 17:00 | 44521.7083 | 0 | 12.2961 | 37.78
2021-11-21 17:30 | 44521.7292 | 0 | 12.71 | 37.78
2021-11-21 18:00 | 44521.75 | 0 | 13.197 | 37.78
2021-11-21 18:30 | 44521.7708 | 0 | 13.7772 | 37.78
2021-11-21 19:00 | 44521.7917 | 0 | 13.655 | 37.78
2021-11-21 19:30 | 44521.8125 | 0 | 13.4027 | 37.78
2021-11-21 20:00 | 44521.8333 | 0 | 13.2817 | 37.78
2021-11-21 20:30 | 44521.8542 | 0 | 12.7538 | 37.78
2021-11-21 21:00 | 44521.875 | 0 | 12.217 | 37.78
2021-11-21 21:30 | 44521.8958 | 0 | 11.6694 | 37.78
2021-11-21 22:00 | 44521.9167 | 0 | 11.0611 | 37.78
2021-11-21 22:30 | 44521.9375 | 0 | 10.3204 | 37.78
2021-11-21 23:00 | 44521.9583 | 0 | 9.7636 | 37.78
2021-11-21 23:30 | 44521.9792 | 0 | 9.4734 | 37.78
2021-11-22 | 44522 | 0 | 9.0834 | 37.78
2021-11-22 00:30 | 44522.0208 | 0 | 8.8137 | 37.78
2021-11-22 01:00 | 44522.0417 | 0 | 8.7254 | 37.78
2021-11-22 01:30 | 44522.0625 | 0 | 8.5398 | 37.78
2021-11-22 02:00 | 44522.0833 | 0 | 8.4595 | 37.78
2021-11-22 02:30 | 44522.1042 | 0 | 8.4145 | 37.78
2021-11-22 03:00 | 44522.125 | 0 | 8.3021 | 37.78
2021-11-22 03:30 | 44522.1458 | 0 | 8.6136 | 37.78
2021-11-22 04:00 | 44522.1667 | 0 | 8.9783 | 37.78
2021-11-22 04:30 | 44522.1875 | 0 | 9.3505 | 37.78
2021-11-22 05:00 | 44522.2083 | 0 | 10.001 | 37.78
2021-11-22 05:30 | 44522.2292 | 0 | 10.7243 | 37.78
2021-11-22 06:00 | 44522.25 | 0 | 11.81 | 37.78
2021-11-22 06:30 | 44522.2708 | 0 | 12.7385 | 37.78
2021-11-22 07:00 | 44522.2917 | 0 | 13.1041 | 37.78
2021-11-22 07:30 | 44522.3125 | 0 | 13.8348 | 37.78
2021-11-22 08:00 | 44522.3333 | 0 | 13.7931 | 37.78
2021-11-22 08:30 | 44522.3542 | 0 | 13.937 | 37.78
2021-11-22 09:00 | 44522.375 | 0 | 14.2696 | 37.78
2021-11-22 09:30 | 44522.3958 | 0 | 14.4592 | 37.78
2021-11-22 10:00 | 44522.4167 | 0 | 14.3542 | 37.78
2021-11-22 10:30 | 44522.4375 | 0 | 13.8628 | 37.78
2021-11-22 11:00 | 44522.4583 | 0 | 12.5271 | 37.78
2021-11-22 11:30 | 44522.4792 | 0 | 11.6782 | 37.78
2021-11-22 12:00 | 44522.5 | 0 | 11.7897 | 37.78
2021-11-22 12:30 | 44522.5208 | 0 | 10.7695 | 37.78
2021-11-22 13:00 | 44522.5417 | 0 | 10.9177 | 37.78
2021-11-22 13:30 | 44522.5625 | 0 | 12.0264 | 37.78
2021-11-22 14:00 | 44522.5833 | 0 | 12.8262 | 37.78
2021-11-22 14:30 | 44522.6042 | 0 | 13.4168 | 37.78
2021-11-22 15:00 | 44522.625 | 0 | 12.3455 | 37.78
2021-11-22 15:30 | 44522.6458 | 0 | 13.0137 | 37.78
2021-11-22 16:00 | 44522.6667 | 0 | 13.0451 | 37.78
2021-11-22 16:30 | 44522.6875 | 0 | 13.3516 | 37.78
2021-11-22 17:00 | 44522.7083 | 0 | 13.7768 | 37.78
2021-11-22 17:30 | 44522.7292 | 0 | 14.0827 | 37.78
2021-11-22 18:00 | 44522.75 | 0 | 14.2682 | 37.78
2021-11-22 18:30 | 44522.7708 | 0 | 14.9378 | 37.78
2021-11-22 19:00 | 44522.7917 | 0 | 14.8793 | 37.78
2021-11-22 19:30 | 44522.8125 | 0 | 14.3807 | 37.78
2021-11-22 20:00 | 44522.8333 | 0 | 13.9841 | 37.78
2021-11-22 20:30 | 44522.8542 | 0 | 13.338 | 37.78
2021-11-22 21:00 | 44522.875 | 0 | 12.7849 | 37.78
2021-11-22 21:30 | 44522.8958 | 0 | 12.3479 | 37.78
2021-11-22 22:00 | 44522.9167 | 0 | 11.746 | 37.78
2021-11-22 22:30 | 44522.9375 | 0 | 10.9824 | 37.78
2021-11-22 23:00 | 44522.9583 | 0 | 10.3409 | 37.78
2021-11-22 23:30 | 44522.9792 | 0 | 9.7144 | 37.78
2021-11-23 | 44523 | 0 | 9.2247 | 37.78
2021-11-23 00:30 | 44523.0208 | 0 | 8.9877 | 37.78
2021-11-23 01:00 | 44523.0417 | 0 | 8.7128 | 37.78
2021-11-23 01:30 | 44523.0625 | 0 | 8.5521 | 37.78
2021-11-23 02:00 | 44523.0833 | 0 | 8.4793 | 37.78
2021-11-23 02:30 | 44523.1042 | 0 | 8.3771 | 37.78
2021-11-23 03:00 | 44523.125 | 0 | 8.3396 | 37.78
2021-11-23 03:30 | 44523.1458 | 0 | 8.4282 | 37.78
2021-11-23 04:00 | 44523.1667 | 0 | 8.8038 | 37.78
2021-11-23 04:30 | 44523.1875 | 0 | 9.043 | 37.78
2021-11-23 05:00 | 44523.2083 | 0 | 9.4647 | 37.78
2021-11-23 05:30 | 44523.2292 | 0 | 10.038 | 37.78
2021-11-23 06:00 | 44523.25 | 0 | 10.827 | 37.78
2021-11-23 06:30 | 44523.2708 | 0 | 10.6167 | 37.78
2021-11-23 07:00 | 44523.2917 | 0 | 11.9875 | 37.78
2021-11-23 07:30 | 44523.3125 | 0 | 12.0004 | 37.78
2021-11-23 08:00 | 44523.3333 | 0 | 12.4882 | 37.78
2021-11-23 08:30 | 44523.3542 | 0 | 11.8457 | 37.78
2021-11-23 09:00 | 44523.375 | 0 | 12.8838 | 37.78
2021-11-23 09:30 | 44523.3958 | 0 | 12.2832 | 37.78
2021-11-23 10:00 | 44523.4167 | 0 | 11.7484 | 37.78
2021-11-23 10:30 | 44523.4375 | 0 | 11.8314 | 37.78
2021-11-23 11:00 | 44523.4583 | 0 | 11.8625 | 37.78
2021-11-23 11:30 | 44523.4792 | 0 | 11.91 | 37.78
2021-11-23 12:00 | 44523.5 | 0 | 11.9894 | 37.78
2021-11-23 12:30 | 44523.5208 | 0 | 13.0091 | 37.78
2021-11-23 13:00 | 44523.5417 | 0 | 12.8842 | 37.78
2021-11-23 13:30 | 44523.5625 | 0 | 13.8564 | 37.78
2021-11-23 14:00 | 44523.5833 | 0 | 14.0238 | 37.78
2021-11-23 14:30 | 44523.6042 | 0 | 14.472 | 37.78
2021-11-23 15:00 | 44523.625 | 0 | 13.0863 | 37.78
2021-11-23 15:30 | 44523.6458 | 0 | 13.7081 | 37.78
2021-11-23 16:00 | 44523.6667 | 0 | 14.5266 | 37.78
2021-11-23 16:30 | 44523.6875 | 0 | 14.8384 | 37.78
2021-11-23 17:00 | 44523.7083 | 0 | 14.5358 | 37.78
2021-11-23 17:30 | 44523.7292 | 0 | 14.8944 | 37.78
2021-11-23 18:00 | 44523.75 | 0 | 14.8884 | 37.78
2021-11-23 18:30 | 44523.7708 | 0 | 15.3232 | 37.78
2021-11-23 19:00 | 44523.7917 | 0 | 14.8661 | 37.78
2021-11-23 19:30 | 44523.8125 | 0 | 14.4568 | 37.78
2021-11-23 20:00 | 44523.8333 | 0 | 14.3624 | 37.78
2021-11-23 20:30 | 44523.8542 | 0 | 13.6488 | 37.78
2021-11-23 21:00 | 44523.875 | 0 | 12.9373 | 37.78
2021-11-23 21:30 | 44523.8958 | 0 | 12.5423 | 37.78
2021-11-23 22:00 | 44523.9167 | 0 | 11.9507 | 37.78
2021-11-23 22:30 | 44523.9375 | 0 | 11.3369 | 37.78
2021-11-23 23:00 | 44523.9583 | 0 | 10.9716 | 37.78
2021-11-23 23:30 | 44523.9792 | 0 | 10.299 | 37.78
2021-11-24 | 44524 | 0 | 9.843 | 37.78
2021-11-24 00:30 | 44524.0208 | 0 | 9.4513 | 37.78
2021-11-24 01:00 | 44524.0417 | 0 | 9.1676 | 37.78
2021-11-24 01:30 | 44524.0625 | 0 | 8.7592 | 37.78
2021-11-24 02:00 | 44524.0833 | 0 | 8.7544 | 37.78
2021-11-24 02:30 | 44524.1042 | 0 | 8.6796 | 37.78
2021-11-24 03:00 | 44524.125 | 0 | 8.6 | 37.78
2021-11-24 03:30 | 44524.1458 | 0 | 8.7209 | 37.78
2021-11-24 04:00 | 44524.1667 | 0 | 9.0508 | 37.78
2021-11-24 04:30 | 44524.1875 | 0 | 9.3726 | 37.78
2021-11-24 05:00 | 44524.2083 | 0 | 9.7805 | 37.78
2021-11-24 05:30 | 44524.2292 | 0 | 10.2172 | 37.78
2021-11-24 06:00 | 44524.25 | 0 | 11.1325 | 37.78
2021-11-24 06:30 | 44524.2708 | 0 | 11.4202 | 37.78
2021-11-24 07:00 | 44524.2917 | 0 | 12.0824 | 37.78
2021-11-24 07:30 | 44524.3125 | 0 | 13.1495 | 37.78
2021-11-24 08:00 | 44524.3333 | 0 | 14.0686 | 37.78
2021-11-24 08:30 | 44524.3542 | 0 | 12.4386 | 37.78
2021-11-24 09:00 | 44524.375 | 0 | 10.7919 | 37.78
2021-11-24 09:30 | 44524.3958 | 0 | 12.3253 | 37.78
2021-11-24 10:00 | 44524.4167 | 0 | 12.0315 | 37.78
2021-11-24 10:30 | 44524.4375 | 0 | 14.0581 | 37.78
2021-11-24 11:00 | 44524.4583 | 0 | 11.0447 | 37.78
2021-11-24 11:30 | 44524.4792 | 0 | 11.5934 | 37.78
2021-11-24 12:00 | 44524.5 | 0 | 11.9355 | 37.78
2021-11-24 12:30 | 44524.5208 | 0 | 13.0537 | 37.78
2021-11-24 13:00 | 44524.5417 | 0 | 13.5859 | 37.78
2021-11-24 13:30 | 44524.5625 | 0 | 12.1151 | 37.78
2021-11-24 14:00 | 44524.5833 | 0 | 14.3999 | 37.78
2021-11-24 14:30 | 44524.6042 | 0 | 14.0755 | 37.78
2021-11-24 15:00 | 44524.625 | 0 | 14.3054 | 37.78
2021-11-24 15:30 | 44524.6458 | 0 | 13.6431 | 37.78
2021-11-24 16:00 | 44524.6667 | 0 | 15.8326 | 37.78
2021-11-24 16:30 | 44524.6875 | 0 | 15.8788 | 37.78
2021-11-24 17:00 | 44524.7083 | 0 | 15.6579 | 37.78
2021-11-24 17:30 | 44524.7292 | 0 | 15.8342 | 37.78
2021-11-24 18:00 | 44524.75 | 0 | 15.8427 | 37.78
2021-11-24 18:30 | 44524.7708 | 0 | 16.2953 | 37.78
2021-11-24 19:00 | 44524.7917 | 0 | 16.248 | 37.78
2021-11-24 19:30 | 44524.8125 | 0 | 16.032 | 37.78
2021-11-24 20:00 | 44524.8333 | 0 | 15.7889 | 37.78
2021-11-24 20:30 | 44524.8542 | 0 | 15.171 | 37.78
2021-11-24 21:00 | 44524.875 | 0 | 14.6619 | 37.78
2021-11-24 21:30 | 44524.8958 | 0 | 14.1467 | 37.78
2021-11-24 22:00 | 44524.9167 | 0 | 13.5346 | 37.78
2021-11-24 22:30 | 44524.9375 | 0 | 12.5446 | 37.78
2021-11-24 23:00 | 44524.9583 | 0 | 11.7471 | 37.78
2021-11-24 23:30 | 44524.9792 | 0 | 11.1878 | 37.78
2021-11-25 | 44525 | 0 | 10.4529 | 37.78
2021-11-25 00:30 | 44525.0208 | 0 | 10.0098 | 37.78
2021-11-25 01:00 | 44525.0417 | 0 | 9.9055 | 37.78
2021-11-25 01:30 | 44525.0625 | 0 | 9.5187 | 37.78
2021-11-25 02:00 | 44525.0833 | 0 | 9.5387 | 37.78
2021-11-25 02:30 | 44525.1042 | 0 | 9.3614 | 37.78
2021-11-25 03:00 | 44525.125 | 0 | 9.2755 | 37.78
2021-11-25 03:30 | 44525.1458 | 0 | 9.356 | 37.78
2021-11-25 04:00 | 44525.1667 | 0 | 9.694 | 37.78
2021-11-25 04:30 | 44525.1875 | 0 | 9.9733 | 37.78
2021-11-25 05:00 | 44525.2083 | 0 | 10.4589 | 37.78
2021-11-25 05:30 | 44525.2292 | 0 | 10.9877 | 37.78
2021-11-25 06:00 | 44525.25 | 0 | 11.7521 | 37.78
2021-11-25 06:30 | 44525.2708 | 0 | 12.9165 | 37.78
2021-11-25 07:00 | 44525.2917 | 0 | 13.7116 | 37.78
2021-11-25 07:30 | 44525.3125 | 0 | 13.6807 | 37.78
2021-11-25 08:00 | 44525.3333 | 0 | 14.5196 | 37.78
2021-11-25 08:30 | 44525.3542 | 0 | 14.2988 | 37.78
2021-11-25 09:00 | 44525.375 | 0 | 13.8363 | 37.78
2021-11-25 09:30 | 44525.3958 | 0 | 13.5953 | 37.78
2021-11-25 10:00 | 44525.4167 | 0 | 14.0612 | 37.78
2021-11-25 10:30 | 44525.4375 | 0 | 14.0412 | 37.78
2021-11-25 11:00 | 44525.4583 | 0 | 15.1026 | 37.78
2021-11-25 11:30 | 44525.4792 | 0 | 14.2852 | 37.78
2021-11-25 12:00 | 44525.5 | 0 | 15.5172 | 37.78
2021-11-25 12:30 | 44525.5208 | 0 | 14.8089 | 37.78
2021-11-25 13:00 | 44525.5417 | 0 | 14.7378 | 37.78
2021-11-25 13:30 | 44525.5625 | 0 | 15.1371 | 37.78
2021-11-25 14:00 | 44525.5833 | 0 | 15.6885 | 37.78
2021-11-25 14:30 | 44525.6042 | 0 | 15.1517 | 37.78
2021-11-25 15:00 | 44525.625 | 0 | 13.4564 | 37.78
2021-11-25 15:30 | 44525.6458 | 0 | 13.9841 | 37.78
2021-11-25 16:00 | 44525.6667 | 0 | 14.4624 | 37.78
2021-11-25 16:30 | 44525.6875 | 0 | 14.2457 | 37.78
2021-11-25 17:00 | 44525.7083 | 0 | 14.7282 | 37.78
2021-11-25 17:30 | 44525.7292 | 0 | 15.3375 | 37.78
2021-11-25 18:00 | 44525.75 | 0 | 15.3263 | 37.78
2021-11-25 18:30 | 44525.7708 | 0 | 15.6283 | 37.78
2021-11-25 19:00 | 44525.7917 | 0 | 15.3612 | 37.78
2021-11-25 19:30 | 44525.8125 | 0 | 15.3364 | 37.78
2021-11-25 20:00 | 44525.8333 | 0 | 15.2092 | 37.78
2021-11-25 20:30 | 44525.8542 | 0 | 14.6925 | 37.78
2021-11-25 21:00 | 44525.875 | 0 | 14.1341 | 37.78
2021-11-25 21:30 | 44525.8958 | 0 | 13.7373 | 37.78
2021-11-25 22:00 | 44525.9167 | 0 | 13.2393 | 37.78
2021-11-25 22:30 | 44525.9375 | 0 | 12.254 | 37.78
2021-11-25 23:00 | 44525.9583 | 0 | 11.6607 | 37.78
2021-11-25 23:30 | 44525.9792 | 0 | 11.1235 | 37.78
2021-11-26 | 44526 | 0 | 10.491 | 37.78
2021-11-26 00:30 | 44526.0208 | 0 | 10.0165 | 37.78
2021-11-26 01:00 | 44526.0417 | 0 | 9.8464 | 37.78
2021-11-26 01:30 | 44526.0625 | 0 | 9.6325 | 37.78
2021-11-26 02:00 | 44526.0833 | 0 | 9.7157 | 37.78
2021-11-26 02:30 | 44526.1042 | 0 | 9.5171 | 37.78
2021-11-26 03:00 | 44526.125 | 0 | 9.3841 | 37.78
2021-11-26 03:30 | 44526.1458 | 0 | 9.5276 | 37.78
2021-11-26 04:00 | 44526.1667 | 0 | 9.8808 | 37.78
2021-11-26 04:30 | 44526.1875 | 0 | 10.1585 | 37.78
2021-11-26 05:00 | 44526.2083 | 0 | 10.4236 | 37.78
2021-11-26 05:30 | 44526.2292 | 0 | 11.0323 | 37.78
2021-11-26 06:00 | 44526.25 | 0 | 11.9561 | 37.78
2021-11-26 06:30 | 44526.2708 | 0 | 12.7303 | 37.78
2021-11-26 07:00 | 44526.2917 | 0 | 13.9522 | 37.78
2021-11-26 07:30 | 44526.3125 | 0 | 14.369 | 37.78
2021-11-26 08:00 | 44526.3333 | 0 | 14.3172 | 37.78
2021-11-26 08:30 | 44526.3542 | 0 | 13.8844 | 37.78
2021-11-26 09:00 | 44526.375 | 0 | 13.4007 | 37.78
2021-11-26 09:30 | 44526.3958 | 0 | 14.6091 | 37.78
2021-11-26 10:00 | 44526.4167 | 0 | 14.211 | 37.78
2021-11-26 10:30 | 44526.4375 | 0 | 13.0401 | 37.78
2021-11-26 11:00 | 44526.4583 | 0 | 13.4335 | 37.78
2021-11-26 11:30 | 44526.4792 | 0 | 12.8832 | 37.78
2021-11-26 12:00 | 44526.5 | 0 | 13.2986 | 37.78
2021-11-26 12:30 | 44526.5208 | 0 | 13.0997 | 37.78
2021-11-26 13:00 | 44526.5417 | 0 | 13.2543 | 37.78
2021-11-26 13:30 | 44526.5625 | 0 | 13.7558 | 37.78
2021-11-26 14:00 | 44526.5833 | 0 | 15.1859 | 37.78
2021-11-26 14:30 | 44526.6042 | 0 | 16.3344 | 37.78
2021-11-26 15:00 | 44526.625 | 0 | 15.254 | 37.78
2021-11-26 15:30 | 44526.6458 | 0 | 16.195 | 37.78
2021-11-26 16:00 | 44526.6667 | 0 | 15.8296 | 37.78
2021-11-26 16:30 | 44526.6875 | 0 | 15.8548 | 37.78
2021-11-26 17:00 | 44526.7083 | 0 | 16.0606 | 37.78
2021-11-26 17:30 | 44526.7292 | 0 | 15.9658 | 37.78
2021-11-26 18:00 | 44526.75 | 0 | 15.9496 | 37.78
2021-11-26 18:30 | 44526.7708 | 0 | 16.2995 | 37.78
2021-11-26 19:00 | 44526.7917 | 0 | 16.1539 | 37.78
2021-11-26 19:30 | 44526.8125 | 0 | 15.9144 | 37.78
2021-11-26 20:00 | 44526.8333 | 0 | 15.7947 | 37.78
2021-11-26 20:30 | 44526.8542 | 0 | 15.175 | 37.78
2021-11-26 21:00 | 44526.875 | 0 | 14.8296 | 37.78
2021-11-26 21:30 | 44526.8958 | 0 | 14.3592 | 37.78
2021-11-26 22:00 | 44526.9167 | 0 | 13.7988 | 37.78
2021-11-26 22:30 | 44526.9375 | 0 | 13.0003 | 37.78
2021-11-26 23:00 | 44526.9583 | 0 | 12.4429 | 37.78
2021-11-26 23:30 | 44526.9792 | 0 | 11.7946 | 37.78
2021-11-27 | 44527 | 0 | 11.1924 | 37.78
2021-11-27 00:30 | 44527.0208 | 0 | 10.8442 | 37.78
2021-11-27 01:00 | 44527.0417 | 0 | 10.4838 | 37.78
2021-11-27 01:30 | 44527.0625 | 0 | 10.1615 | 37.78
2021-11-27 02:00 | 44527.0833 | 0 | 9.801 | 37.78
2021-11-27 02:30 | 44527.1042 | 0 | 9.5953 | 37.78
2021-11-27 03:00 | 44527.125 | 0 | 9.4254 | 37.78
2021-11-27 03:30 | 44527.1458 | 0 | 9.515 | 37.78
2021-11-27 04:00 | 44527.1667 | 0 | 9.5628 | 37.78
2021-11-27 04:30 | 44527.1875 | 0 | 9.4687 | 37.78
2021-11-27 05:00 | 44527.2083 | 0 | 9.4169 | 37.78
2021-11-27 05:30 | 44527.2292 | 0 | 9.5624 | 37.78
2021-11-27 06:00 | 44527.25 | 0 | 9.9343 | 37.78
2021-11-27 06:30 | 44527.2708 | 0 | 10.1362 | 37.78
2021-11-27 07:00 | 44527.2917 | 0 | 10.2659 | 37.78
2021-11-27 07:30 | 44527.3125 | 0 | 9.9914 | 37.78
2021-11-27 08:00 | 44527.3333 | 0 | 9.9258 | 37.78
2021-11-27 08:30 | 44527.3542 | 0 | 10.8044 | 37.78
2021-11-27 09:00 | 44527.375 | 0 | 10.6177 | 37.78
2021-11-27 09:30 | 44527.3958 | 0 | 11.702 | 37.78
2021-11-27 10:00 | 44527.4167 | 0 | 12.4172 | 37.78
2021-11-27 10:30 | 44527.4375 | 0 | 11.3003 | 37.78
2021-11-27 11:00 | 44527.4583 | 0 | 11.351 | 37.78
2021-11-27 11:30 | 44527.4792 | 0 | 11.1994 | 37.78
2021-11-27 12:00 | 44527.5 | 0 | 10.313 | 37.78
2021-11-27 12:30 | 44527.5208 | 0 | 11.4565 | 37.78
2021-11-27 13:00 | 44527.5417 | 0 | 12.1121 | 37.78
2021-11-27 13:30 | 44527.5625 | 0 | 12.0916 | 37.78
2021-11-27 14:00 | 44527.5833 | 0 | 12.9979 | 37.78
2021-11-27 14:30 | 44527.6042 | 0 | 13.1153 | 37.78
2021-11-27 15:00 | 44527.625 | 0 | 13.0646 | 37.78
2021-11-27 15:30 | 44527.6458 | 0 | 13.093 | 37.78
2021-11-27 16:00 | 44527.6667 | 0 | 12.8186 | 37.78
2021-11-27 16:30 | 44527.6875 | 0 | 12.8704 | 37.78
2021-11-27 17:00 | 44527.7083 | 0 | 12.7262 | 37.78
2021-11-27 17:30 | 44527.7292 | 0 | 12.5435 | 37.78
2021-11-27 18:00 | 44527.75 | 0 | 12.464 | 37.78
2021-11-27 18:30 | 44527.7708 | 0 | 12.9201 | 37.78
2021-11-27 19:00 | 44527.7917 | 0 | 12.8521 | 37.78
2021-11-27 19:30 | 44527.8125 | 0 | 12.7154 | 37.78
2021-11-27 20:00 | 44527.8333 | 0 | 12.4674 | 37.78
2021-11-27 20:30 | 44527.8542 | 0 | 11.9808 | 37.78
2021-11-27 21:00 | 44527.875 | 0 | 11.6297 | 37.78
2021-11-27 21:30 | 44527.8958 | 0 | 11.3078 | 37.78
2021-11-27 22:00 | 44527.9167 | 0 | 10.9137 | 37.78
2021-11-27 22:30 | 44527.9375 | 0 | 10.5038 | 37.78
2021-11-27 23:00 | 44527.9583 | 0 | 10.0162 | 37.78
2021-11-27 23:30 | 44527.9792 | 0 | 9.6046 | 37.78
2021-11-28 | 44528 | 0 | 9.1392 | 37.78
2021-11-28 00:30 | 44528.0208 | 0 | 8.6921 | 37.78
2021-11-28 01:00 | 44528.0417 | 0 | 8.5027 | 37.78
2021-11-28 01:30 | 44528.0625 | 0 | 8.3836 | 37.78
2021-11-28 02:00 | 44528.0833 | 0 | 8.178 | 37.78
2021-11-28 02:30 | 44528.1042 | 0 | 8.1822 | 37.78
2021-11-28 03:00 | 44528.125 | 0 | 8.0046 | 37.78
2021-11-28 03:30 | 44528.1458 | 0 | 7.9514 | 37.78
2021-11-28 04:00 | 44528.1667 | 0 | 8.0272 | 37.78
2021-11-28 04:30 | 44528.1875 | 0 | 7.9027 | 37.78
2021-11-28 05:00 | 44528.2083 | 0 | 7.8601 | 37.78
2021-11-28 05:30 | 44528.2292 | 0 | 7.8398 | 37.78
2021-11-28 06:00 | 44528.25 | 0 | 7.763 | 37.78
2021-11-28 06:30 | 44528.2708 | 0 | 7.6861 | 37.78
2021-11-28 07:00 | 44528.2917 | 0 | 7.8915 | 37.78
2021-11-28 07:30 | 44528.3125 | 0 | 7.596 | 37.78
2021-11-28 08:00 | 44528.3333 | 0 | 8.486 | 37.78
2021-11-28 08:30 | 44528.3542 | 0 | 8.4255 | 37.78
2021-11-28 09:00 | 44528.375 | 0 | 8.1147 | 37.78
2021-11-28 09:30 | 44528.3958 | 0 | 7.3261 | 37.78
2021-11-28 10:00 | 44528.4167 | 0 | 7.708 | 37.78
2021-11-28 10:30 | 44528.4375 | 0 | 7.1972 | 37.78
2021-11-28 11:00 | 44528.4583 | 0 | 7.9143 | 37.78
2021-11-28 11:30 | 44528.4792 | 0 | 8.9087 | 37.78
2021-11-28 12:00 | 44528.5 | 0 | 8.7969 | 37.78
2021-11-28 12:30 | 44528.5208 | 0 | 8.3197 | 37.78
2021-11-28 13:00 | 44528.5417 | 0 | 10.7935 | 37.78
2021-11-28 13:30 | 44528.5625 | 0 | 10.7135 | 37.78
2021-11-28 14:00 | 44528.5833 | 0 | 10.1358 | 37.78
2021-11-28 14:30 | 44528.6042 | 0 | 10.1235 | 37.78
2021-11-28 15:00 | 44528.625 | 0 | 10.6055 | 37.78
2021-11-28 15:30 | 44528.6458 | 0 | 11.079 | 37.78
2021-11-28 16:00 | 44528.6667 | 0 | 11.2471 | 37.78
2021-11-28 16:30 | 44528.6875 | 0 | 12.0883 | 37.78
2021-11-28 17:00 | 44528.7083 | 0 | 12.3111 | 37.78
2021-11-28 17:30 | 44528.7292 | 0 | 12.3603 | 37.78
2021-11-28 18:00 | 44528.75 | 0 | 12.8622 | 37.78
2021-11-28 18:30 | 44528.7708 | 0 | 13.1918 | 37.78
2021-11-28 19:00 | 44528.7917 | 0 | 13.0734 | 37.78
2021-11-28 19:30 | 44528.8125 | 0 | 12.7587 | 37.78
2021-11-28 20:00 | 44528.8333 | 0 | 12.413 | 37.78
2021-11-28 20:30 | 44528.8542 | 0 | 11.9561 | 37.78
2021-11-28 21:00 | 44528.875 | 0 | 11.4304 | 37.78
2021-11-28 21:30 | 44528.8958 | 0 | 10.9194 | 37.78
2021-11-28 22:00 | 44528.9167 | 0 | 10.6198 | 37.78
2021-11-28 22:30 | 44528.9375 | 0 | 9.8738 | 37.78
2021-11-28 23:00 | 44528.9583 | 0 | 9.3202 | 37.78
2021-11-28 23:30 | 44528.9792 | 0 | 8.9801 | 37.78
2021-11-29 | 44529 | 0 | 8.6394 | 37.78
2021-11-29 00:30 | 44529.0208 | 0 | 8.416 | 37.78
2021-11-29 01:00 | 44529.0417 | 0 | 8.2675 | 37.78
2021-11-29 01:30 | 44529.0625 | 0 | 8.1832 | 37.78
2021-11-29 02:00 | 44529.0833 | 0 | 8.145 | 37.78
2021-11-29 02:30 | 44529.1042 | 0 | 8.0712 | 37.78
2021-11-29 03:00 | 44529.125 | 0 | 8.1443 | 37.78
2021-11-29 03:30 | 44529.1458 | 0 | 8.4798 | 37.78
2021-11-29 04:00 | 44529.1667 | 0 | 8.773 | 37.78
2021-11-29 04:30 | 44529.1875 | 0 | 8.8325 | 37.78
2021-11-29 05:00 | 44529.2083 | 0 | 9.3779 | 37.78
2021-11-29 05:30 | 44529.2292 | 0 | 10.0477 | 37.78
2021-11-29 06:00 | 44529.25 | 0 | 10.9237 | 37.78
2021-11-29 06:30 | 44529.2708 | 0 | 11.0405 | 37.78
2021-11-29 07:00 | 44529.2917 | 0 | 11.6172 | 37.78
2021-11-29 07:30 | 44529.3125 | 0 | 11.97 | 37.78
2021-11-29 08:00 | 44529.3333 | 0 | 12.4827 | 37.78
2021-11-29 08:30 | 44529.3542 | 0 | 12.4132 | 37.78
2021-11-29 09:00 | 44529.375 | 0 | 12.8834 | 37.78
2021-11-29 09:30 | 44529.3958 | 0 | 13.2751 | 37.78
2021-11-29 10:00 | 44529.4167 | 0 | 13.0224 | 37.78
2021-11-29 10:30 | 44529.4375 | 0 | 12.8862 | 37.78
2021-11-29 11:00 | 44529.4583 | 0 | 11.7005 | 37.78
2021-11-29 11:30 | 44529.4792 | 0 | 11.9081 | 37.78
2021-11-29 12:00 | 44529.5 | 0 | 12.8199 | 37.78
2021-11-29 12:30 | 44529.5208 | 0 | 13.6191 | 37.78
2021-11-29 13:00 | 44529.5417 | 0 | 13.5552 | 37.78
2021-11-29 13:30 | 44529.5625 | 0 | 13.7571 | 37.78
2021-11-29 14:00 | 44529.5833 | 0 | 14.1231 | 37.78
2021-11-29 14:30 | 44529.6042 | 0 | 15.138 | 37.78
2021-11-29 15:00 | 44529.625 | 0 | 14.2024 | 37.78
2021-11-29 15:30 | 44529.6458 | 0 | 14.1484 | 37.78
2021-11-29 16:00 | 44529.6667 | 0 | 14.2696 | 37.78
2021-11-29 16:30 | 44529.6875 | 0 | 14.4898 | 37.78
2021-11-29 17:00 | 44529.7083 | 0 | 14.7155 | 37.78
2021-11-29 17:30 | 44529.7292 | 0 | 15.038 | 37.78
2021-11-29 18:00 | 44529.75 | 0 | 15.4138 | 37.78
2021-11-29 18:30 | 44529.7708 | 0 | 15.9235 | 37.78
2021-11-29 19:00 | 44529.7917 | 0 | 15.8883 | 37.78
2021-11-29 19:30 | 44529.8125 | 0 | 15.7083 | 37.78
2021-11-29 20:00 | 44529.8333 | 0 | 15.5352 | 37.78
2021-11-29 20:30 | 44529.8542 | 0 | 14.723 | 37.78
2021-11-29 21:00 | 44529.875 | 0 | 14.1455 | 37.78
2021-11-29 21:30 | 44529.8958 | 0 | 13.6712 | 37.78
2021-11-29 22:00 | 44529.9167 | 0 | 12.7784 | 37.78
2021-11-29 22:30 | 44529.9375 | 0 | 12.0045 | 37.78
2021-11-29 23:00 | 44529.9583 | 0 | 11.4512 | 37.78
2021-11-29 23:30 | 44529.9792 | 0 | 10.9234 | 37.78
2021-11-30 | 44530 | 0 | 10.2372 | 37.78
2021-11-30 00:30 | 44530.0208 | 0 | 9.825 | 37.78
2021-11-30 01:00 | 44530.0417 | 0 | 9.6559 | 37.78
2021-11-30 01:30 | 44530.0625 | 0 | 9.3997 | 37.78
2021-11-30 02:00 | 44530.0833 | 0 | 9.3198 | 37.78
2021-11-30 02:30 | 44530.1042 | 0 | 9.1926 | 37.78
2021-11-30 03:00 | 44530.125 | 0 | 9.0589 | 37.78
2021-11-30 03:30 | 44530.1458 | 0 | 9.2203 | 37.78
2021-11-30 04:00 | 44530.1667 | 0 | 9.603 | 37.78
2021-11-30 04:30 | 44530.1875 | 0 | 10.0319 | 37.78
2021-11-30 05:00 | 44530.2083 | 0 | 10.5429 | 37.78
2021-11-30 05:30 | 44530.2292 | 0 | 11.0712 | 37.78
2021-11-30 06:00 | 44530.25 | 0 | 12.131 | 37.78
2021-11-30 06:30 | 44530.2708 | 0 | 13.3386 | 37.78
2021-11-30 07:00 | 44530.2917 | 0 | 14.1449 | 37.78
2021-11-30 07:30 | 44530.3125 | 0 | 14.0098 | 37.78
2021-11-30 08:00 | 44530.3333 | 0 | 14.0716 | 37.78
2021-11-30 08:30 | 44530.3542 | 0 | 14.0195 | 37.78
2021-11-30 09:00 | 44530.375 | 0 | 13.4473 | 37.78
2021-11-30 09:30 | 44530.3958 | 0 | 13.5419 | 37.78
2021-11-30 10:00 | 44530.4167 | 0 | 13.8564 | 37.78
2021-11-30 10:30 | 44530.4375 | 0 | 13.5045 | 37.78
2021-11-30 11:00 | 44530.4583 | 0 | 14.0953 | 37.78
2021-11-30 11:30 | 44530.4792 | 0 | 14.2678 | 37.78
2021-11-30 12:00 | 44530.5 | 0 | 14.3048 | 37.78
2021-11-30 12:30 | 44530.5208 | 0 | 14.2787 | 37.78
2021-11-30 13:00 | 44530.5417 | 0 | 14.7079 | 37.78
2021-11-30 13:30 | 44530.5625 | 0 | 14.6883 | 37.78
2021-11-30 14:00 | 44530.5833 | 0 | 14.5179 | 37.78
2021-11-30 14:30 | 44530.6042 | 0 | 14.5406 | 37.78
2021-11-30 15:00 | 44530.625 | 0 | 14.6449 | 37.78
2021-11-30 15:30 | 44530.6458 | 0 | 14.7865 | 37.78
2021-11-30 16:00 | 44530.6667 | 0 | 14.5577 | 37.78
2021-11-30 16:30 | 44530.6875 | 0 | 14.9117 | 37.78
2021-11-30 17:00 | 44530.7083 | 0 | 14.9324 | 37.78
2021-11-30 17:30 | 44530.7292 | 0 | 15.0931 | 37.78
2021-11-30 18:00 | 44530.75 | 0 | 15.4318 | 37.78
2021-11-30 18:30 | 44530.7708 | 0 | 15.7313 | 37.78
2021-11-30 19:00 | 44530.7917 | 0 | 15.462 | 37.78
2021-11-30 19:30 | 44530.8125 | 0 | 15.1499 | 37.78
2021-11-30 20:00 | 44530.8333 | 0 | 14.8344 | 37.78
2021-11-30 20:30 | 44530.8542 | 0 | 14.2256 | 37.78
2021-11-30 21:00 | 44530.875 | 0 | 13.7517 | 37.78
2021-11-30 21:30 | 44530.8958 | 0 | 13.2687 | 37.78
2021-11-30 22:00 | 44530.9167 | 0 | 12.7538 | 37.78
2021-11-30 22:30 | 44530.9375 | 0 | 11.7559 | 37.78
2021-11-30 23:00 | 44530.9583 | 0 | 11.1287 | 37.78
2021-11-30 23:30 | 44530.9792 | 0 | 10.6456 | 37.78
2021-12-01 | 44531 | 0 | 10.0853 | 37.78
2021-12-01 00:30 | 44531.0208 | 0 | 9.6181 | 37.78
2021-12-01 01:00 | 44531.0417 | 0 | 9.4761 | 37.78
2021-12-01 01:30 | 44531.0625 | 0 | 9.2938 | 37.78
2021-12-01 02:00 | 44531.0833 | 0 | 9.1012 | 37.78
2021-12-01 02:30 | 44531.1042 | 0 | 9.0918 | 37.78
2021-12-01 03:00 | 44531.125 | 0 | 8.965 | 37.78
2021-12-01 03:30 | 44531.1458 | 0 | 9.1481 | 37.78
2021-12-01 04:00 | 44531.1667 | 0 | 9.5166 | 37.78
2021-12-01 04:30 | 44531.1875 | 0 | 9.9904 | 37.78
2021-12-01 05:00 | 44531.2083 | 0 | 10.4219 | 37.78
2021-12-01 05:30 | 44531.2292 | 0 | 10.8863 | 37.78
2021-12-01 06:00 | 44531.25 | 0 | 12.4661 | 37.78
2021-12-01 06:30 | 44531.2708 | 0 | 13.2379 | 37.78
2021-12-01 07:00 | 44531.2917 | 0 | 14.2074 | 37.78
2021-12-01 07:30 | 44531.3125 | 0 | 14.1648 | 37.78
2021-12-01 08:00 | 44531.3333 | 0 | 14.3152 | 37.78
2021-12-01 08:30 | 44531.3542 | 0 | 14.2277 | 37.78
2021-12-01 09:00 | 44531.375 | 0 | 13.5677 | 37.78
2021-12-01 09:30 | 44531.3958 | 0 | 13.6794 | 37.78
2021-12-01 10:00 | 44531.4167 | 0 | 13.1875 | 37.78
2021-12-01 10:30 | 44531.4375 | 0 | 14.2855 | 37.78
2021-12-01 11:00 | 44531.4583 | 0 | 15.3201 | 37.78
2021-12-01 11:30 | 44531.4792 | 0 | 15.0979 | 37.78
2021-12-01 12:00 | 44531.5 | 0 | 15.2287 | 37.78
2021-12-01 12:30 | 44531.5208 | 0 | 15.0694 | 37.78
2021-12-01 13:00 | 44531.5417 | 0 | 14.2926 | 37.78
2021-12-01 13:30 | 44531.5625 | 0 | 14.0063 | 37.78
2021-12-01 14:00 | 44531.5833 | 0 | 13.6381 | 37.78
2021-12-01 14:30 | 44531.6042 | 0 | 14.0229 | 37.78
2021-12-01 15:00 | 44531.625 | 0 | 13.1252 | 37.78
2021-12-01 15:30 | 44531.6458 | 0 | 13.4845 | 37.78
2021-12-01 16:00 | 44531.6667 | 0 | 14.089 | 37.78
2021-12-01 16:30 | 44531.6875 | 0 | 14.7941 | 37.78
2021-12-01 17:00 | 44531.7083 | 0 | 15.4752 | 37.78
2021-12-01 17:30 | 44531.7292 | 0 | 15.5889 | 37.78
2021-12-01 18:00 | 44531.75 | 0 | 15.3307 | 37.78
2021-12-01 18:30 | 44531.7708 | 0 | 16.129 | 37.78
2021-12-01 19:00 | 44531.7917 | 0 | 16.2264 | 37.78
2021-12-01 19:30 | 44531.8125 | 0 | 15.8129 | 37.78
2021-12-01 20:00 | 44531.8333 | 0 | 15.3671 | 37.78
2021-12-01 20:30 | 44531.8542 | 0 | 14.6775 | 37.78
2021-12-01 21:00 | 44531.875 | 0 | 14.2036 | 37.78
2021-12-01 21:30 | 44531.8958 | 0 | 13.9028 | 37.78
2021-12-01 22:00 | 44531.9167 | 0 | 13.3534 | 37.78
2021-12-01 22:30 | 44531.9375 | 0 | 12.3732 | 37.78
2021-12-01 23:00 | 44531.9583 | 0 | 11.6902 | 37.78
2021-12-01 23:30 | 44531.9792 | 0 | 11.0662 | 37.78
2021-12-02 | 44532 | 0 | 10.2956 | 37.78
2021-12-02 00:30 | 44532.0208 | 0 | 9.9167 | 37.78
2021-12-02 01:00 | 44532.0417 | 0 | 9.847 | 37.78
2021-12-02 01:30 | 44532.0625 | 0 | 9.6227 | 37.78
2021-12-02 02:00 | 44532.0833 | 0 | 9.3195 | 37.78
2021-12-02 02:30 | 44532.1042 | 0 | 9.2075 | 37.78
2021-12-02 03:00 | 44532.125 | 0 | 9.1296 | 37.78
2021-12-02 03:30 | 44532.1458 | 0 | 9.4132 | 37.78
2021-12-02 04:00 | 44532.1667 | 0 | 9.7436 | 37.78
2021-12-02 04:30 | 44532.1875 | 0 | 10.113 | 37.78
2021-12-02 05:00 | 44532.2083 | 0 | 10.6257 | 37.78
2021-12-02 05:30 | 44532.2292 | 0 | 11.2763 | 37.78
2021-12-02 06:00 | 44532.25 | 0 | 12.1393 | 37.78
2021-12-02 06:30 | 44532.2708 | 0 | 12.6064 | 37.78
2021-12-02 07:00 | 44532.2917 | 0 | 12.9426 | 37.78
2021-12-02 07:30 | 44532.3125 | 0 | 13.341 | 37.78
2021-12-02 08:00 | 44532.3333 | 0 | 13.3052 | 37.78
2021-12-02 08:30 | 44532.3542 | 0 | 12.5671 | 37.78
2021-12-02 09:00 | 44532.375 | 0 | 13.6905 | 37.78
2021-12-02 09:30 | 44532.3958 | 0 | 15.524 | 37.78
2021-12-02 10:00 | 44532.4167 | 0 | 16.4588 | 37.78
2021-12-02 10:30 | 44532.4375 | 0 | 15.5496 | 37.78
2021-12-02 11:00 | 44532.4583 | 0 | 13.4301 | 37.78
2021-12-02 11:30 | 44532.4792 | 0 | 14.8616 | 37.78
2021-12-02 12:00 | 44532.5 | 0 | 14.9886 | 37.78
2021-12-02 12:30 | 44532.5208 | 0 | 14.6169 | 37.78
2021-12-02 13:00 | 44532.5417 | 0 | 15.7193 | 37.78
2021-12-02 13:30 | 44532.5625 | 0 | 15.833 | 37.78
2021-12-02 14:00 | 44532.5833 | 0 | 17.2866 | 37.78
2021-12-02 14:30 | 44532.6042 | 0 | 16.4697 | 37.78
2021-12-02 15:00 | 44532.625 | 0 | 16.5808 | 37.78
2021-12-02 15:30 | 44532.6458 | 0 | 17.0311 | 37.78
2021-12-02 16:00 | 44532.6667 | 0 | 16.6468 | 37.78
2021-12-02 16:30 | 44532.6875 | 0 | 17.0923 | 37.78
2021-12-02 17:00 | 44532.7083 | 0 | 16.9695 | 37.78
2021-12-02 17:30 | 44532.7292 | 0 | 17.2198 | 37.78
2021-12-02 18:00 | 44532.75 | 0 | 16.982 | 37.78
2021-12-02 18:30 | 44532.7708 | 0 | 17.3962 | 37.78
2021-12-02 19:00 | 44532.7917 | 0 | 17.252 | 37.78
2021-12-02 19:30 | 44532.8125 | 0 | 17.0764 | 37.78
2021-12-02 20:00 | 44532.8333 | 0 | 16.5204 | 37.78
2021-12-02 20:30 | 44532.8542 | 0 | 16.0335 | 37.78
2021-12-02 21:00 | 44532.875 | 0 | 15.2853 | 37.78
2021-12-02 21:30 | 44532.8958 | 0 | 14.658 | 37.78
2021-12-02 22:00 | 44532.9167 | 0 | 13.7733 | 37.78
2021-12-02 22:30 | 44532.9375 | 0 | 12.8319 | 37.78
2021-12-02 23:00 | 44532.9583 | 0 | 12.1854 | 37.78
2021-12-02 23:30 | 44532.9792 | 0 | 11.5698 | 37.78
2021-12-03 | 44533 | 0 | 10.6229 | 37.78
2021-12-03 00:30 | 44533.0208 | 0 | 10.3537 | 37.78
2021-12-03 01:00 | 44533.0417 | 0 | 10.1954 | 37.78
2021-12-03 01:30 | 44533.0625 | 0 | 9.8622 | 37.78
2021-12-03 02:00 | 44533.0833 | 0 | 9.7323 | 37.78
2021-12-03 02:30 | 44533.1042 | 0 | 9.6369 | 37.78
2021-12-03 03:00 | 44533.125 | 0 | 9.5381 | 37.78
2021-12-03 03:30 | 44533.1458 | 0 | 9.5019 | 37.78
2021-12-03 04:00 | 44533.1667 | 0 | 9.8486 | 37.78
2021-12-03 04:30 | 44533.1875 | 0 | 10.0811 | 37.78
2021-12-03 05:00 | 44533.2083 | 0 | 10.4848 | 37.78
2021-12-03 05:30 | 44533.2292 | 0 | 10.9467 | 37.78
2021-12-03 06:00 | 44533.25 | 0 | 11.585 | 37.78
2021-12-03 06:30 | 44533.2708 | 0 | 12.3055 | 37.78
2021-12-03 07:00 | 44533.2917 | 0 | 12.8704 | 37.78
2021-12-03 07:30 | 44533.3125 | 0 | 13.0744 | 37.78
2021-12-03 08:00 | 44533.3333 | 0 | 13.0913 | 37.78
2021-12-03 08:30 | 44533.3542 | 0 | 13.3942 | 37.78
2021-12-03 09:00 | 44533.375 | 0 | 14.5997 | 37.78
2021-12-03 09:30 | 44533.3958 | 0 | 15.1154 | 37.78
2021-12-03 10:00 | 44533.4167 | 0 | 15.5517 | 37.78
2021-12-03 10:30 | 44533.4375 | 0 | 15.7669 | 37.78
2021-12-03 11:00 | 44533.4583 | 0 | 15.8736 | 37.78
2021-12-03 11:30 | 44533.4792 | 0 | 16.2049 | 37.78
2021-12-03 12:00 | 44533.5 | 0 | 15.2641 | 37.78
2021-12-03 12:30 | 44533.5208 | 0 | 14.9233 | 37.78
2021-12-03 13:00 | 44533.5417 | 0 | 15.0375 | 37.78
2021-12-03 13:30 | 44533.5625 | 0 | 15.1623 | 37.78
2021-12-03 14:00 | 44533.5833 | 0 | 16.1339 | 37.78
2021-12-03 14:30 | 44533.6042 | 0 | 16.6634 | 37.78
2021-12-03 15:00 | 44533.625 | 0 | 17.7613 | 37.78
2021-12-03 15:30 | 44533.6458 | 0 | 17.3186 | 37.78
2021-12-03 16:00 | 44533.6667 | 0 | 18.1157 | 37.78
2021-12-03 16:30 | 44533.6875 | 0 | 18.8088 | 37.78
2021-12-03 17:00 | 44533.7083 | 0 | 18.5571 | 37.78
2021-12-03 17:30 | 44533.7292 | 0 | 18.5371 | 37.78
2021-12-03 18:00 | 44533.75 | 0 | 17.931 | 37.78
2021-12-03 18:30 | 44533.7708 | 0 | 17.7768 | 37.78
2021-12-03 19:00 | 44533.7917 | 0 | 17.5782 | 37.78
2021-12-03 19:30 | 44533.8125 | 0 | 17.4787 | 37.78
2021-12-03 20:00 | 44533.8333 | 0 | 17.0794 | 37.78
2021-12-03 20:30 | 44533.8542 | 0 | 16.536 | 37.78
2021-12-03 21:00 | 44533.875 | 0 | 16.0468 | 37.78
2021-12-03 21:30 | 44533.8958 | 0 | 15.5742 | 37.78
2021-12-03 22:00 | 44533.9167 | 0 | 14.696 | 37.78
2021-12-03 22:30 | 44533.9375 | 0 | 13.5916 | 37.78
2021-12-03 23:00 | 44533.9583 | 0 | 12.8171 | 37.78
2021-12-03 23:30 | 44533.9792 | 0 | 12.011 | 37.78
2021-12-04 | 44534 | 0 | 11.4704 | 37.78
2021-12-04 00:30 | 44534.0208 | 0 | 10.8117 | 37.78
2021-12-04 01:00 | 44534.0417 | 0 | 10.4454 | 37.78
2021-12-04 01:30 | 44534.0625 | 0 | 10.2642 | 37.78
2021-12-04 02:00 | 44534.0833 | 0 | 10.0335 | 37.78
2021-12-04 02:30 | 44534.1042 | 0 | 9.6182 | 37.78
2021-12-04 03:00 | 44534.125 | 0 | 9.4047 | 37.78
2021-12-04 03:30 | 44534.1458 | 0 | 9.4271 | 37.78
2021-12-04 04:00 | 44534.1667 | 0 | 9.4369 | 37.78
2021-12-04 04:30 | 44534.1875 | 0 | 9.379 | 37.78
2021-12-04 05:00 | 44534.2083 | 0 | 9.4994 | 37.78
2021-12-04 05:30 | 44534.2292 | 0 | 9.4734 | 37.78
2021-12-04 06:00 | 44534.25 | 0 | 9.4897 | 37.78
2021-12-04 06:30 | 44534.2708 | 0 | 9.514 | 37.78
2021-12-04 07:00 | 44534.2917 | 0 | 9.6524 | 37.78
2021-12-04 07:30 | 44534.3125 | 0 | 9.7184 | 37.78
2021-12-04 08:00 | 44534.3333 | 0 | 10.0947 | 37.78
2021-12-04 08:30 | 44534.3542 | 0 | 10.1762 | 37.78
2021-12-04 09:00 | 44534.375 | 0 | 10.2703 | 37.78
2021-12-04 09:30 | 44534.3958 | 0 | 10.7907 | 37.78
2021-12-04 10:00 | 44534.4167 | 0 | 11.0721 | 37.78
2021-12-04 10:30 | 44534.4375 | 0 | 11.3337 | 37.78
2021-12-04 11:00 | 44534.4583 | 0 | 11.4472 | 37.78
2021-12-04 11:30 | 44534.4792 | 0 | 11.5984 | 37.78
2021-12-04 12:00 | 44534.5 | 0 | 11.7622 | 37.78
2021-12-04 12:30 | 44534.5208 | 0 | 11.9869 | 37.78
2021-12-04 13:00 | 44534.5417 | 0 | 12.2966 | 37.78
2021-12-04 13:30 | 44534.5625 | 0 | 12.779 | 37.78
2021-12-04 14:00 | 44534.5833 | 0 | 13.3018 | 37.78
2021-12-04 14:30 | 44534.6042 | 0 | 13.8873 | 37.78
2021-12-04 15:00 | 44534.625 | 0 | 14.4457 | 37.78
2021-12-04 15:30 | 44534.6458 | 0 | 16.2824 | 37.78
2021-12-04 16:00 | 44534.6667 | 0 | 15.8944 | 37.78
2021-12-04 16:30 | 44534.6875 | 0 | 15.9083 | 37.78
2021-12-04 17:00 | 44534.7083 | 0 | 16.0717 | 37.78
2021-12-04 17:30 | 44534.7292 | 0 | 16.047 | 37.78
2021-12-04 18:00 | 44534.75 | 0 | 15.7686 | 37.78
2021-12-04 18:30 | 44534.7708 | 0 | 15.9283 | 37.78
2021-12-04 19:00 | 44534.7917 | 0 | 15.7247 | 37.78
2021-12-04 19:30 | 44534.8125 | 0 | 15.106 | 37.78
2021-12-04 20:00 | 44534.8333 | 0 | 14.0432 | 37.78
2021-12-04 20:30 | 44534.8542 | 0 | 13.261 | 37.78
2021-12-04 21:00 | 44534.875 | 0 | 12.9024 | 37.78
2021-12-04 21:30 | 44534.8958 | 0 | 12.5313 | 37.78
2021-12-04 22:00 | 44534.9167 | 0 | 11.9363 | 37.78
2021-12-04 22:30 | 44534.9375 | 0 | 11.3426 | 37.78
2021-12-04 23:00 | 44534.9583 | 0 | 10.8141 | 37.78
2021-12-04 23:30 | 44534.9792 | 0 | 10.3042 | 37.78
2021-12-05 | 44535 | 0 | 9.8446 | 37.78
2021-12-05 00:30 | 44535.0208 | 0 | 9.516 | 37.78
2021-12-05 01:00 | 44535.0417 | 0 | 9.2343 | 37.78
2021-12-05 01:30 | 44535.0625 | 0 | 9.0214 | 37.78
2021-12-05 02:00 | 44535.0833 | 0 | 8.8286 | 37.78
2021-12-05 02:30 | 44535.1042 | 0 | 8.682 | 37.78
2021-12-05 03:00 | 44535.125 | 0 | 8.6653 | 37.78
2021-12-05 03:30 | 44535.1458 | 0 | 8.4773 | 37.78
2021-12-05 04:00 | 44535.1667 | 0 | 8.4208 | 37.78
2021-12-05 04:30 | 44535.1875 | 0 | 8.1731 | 37.78
2021-12-05 05:00 | 44535.2083 | 0 | 8.144 | 37.78
2021-12-05 05:30 | 44535.2292 | 0 | 8.0658 | 37.78
2021-12-05 06:00 | 44535.25 | 0 | 8.1578 | 37.78
2021-12-05 06:30 | 44535.2708 | 0 | 7.8609 | 37.78
2021-12-05 07:00 | 44535.2917 | 0 | 7.5177 | 37.78
2021-12-05 07:30 | 44535.3125 | 0 | 8.2916 | 37.78
2021-12-05 08:00 | 44535.3333 | 0 | 8.9707 | 37.78
2021-12-05 08:30 | 44535.3542 | 0 | 9.2926 | 37.78
2021-12-05 09:00 | 44535.375 | 0 | 8.8368 | 37.78
2021-12-05 09:30 | 44535.3958 | 0 | 8.1613 | 37.78
2021-12-05 10:00 | 44535.4167 | 0 | 10.4441 | 37.78
2021-12-05 10:30 | 44535.4375 | 0 | 11.4346 | 37.78
2021-12-05 11:00 | 44535.4583 | 0 | 8.3091 | 37.78
2021-12-05 11:30 | 44535.4792 | 0 | 7.7158 | 37.78
2021-12-05 12:00 | 44535.5 | 0 | 7.7528 | 37.78
2021-12-05 12:30 | 44535.5208 | 0 | 8.4678 | 37.78
2021-12-05 13:00 | 44535.5417 | 0 | 8.418 | 37.78
2021-12-05 13:30 | 44535.5625 | 0 | 9.3245 | 37.78
2021-12-05 14:00 | 44535.5833 | 0 | 9.5823 | 37.78
2021-12-05 14:30 | 44535.6042 | 0 | 10.2552 | 37.78
2021-12-05 15:00 | 44535.625 | 0 | 10.7891 | 37.78
2021-12-05 15:30 | 44535.6458 | 0 | 12.0759 | 37.78
2021-12-05 16:00 | 44535.6667 | 0 | 12.9983 | 37.78
2021-12-05 16:30 | 44535.6875 | 0 | 12.8364 | 37.78
2021-12-05 17:00 | 44535.7083 | 0 | 13.285 | 37.78
2021-12-05 17:30 | 44535.7292 | 0 | 13.2815 | 37.78
2021-12-05 18:00 | 44535.75 | 0 | 13.3715 | 37.78
2021-12-05 18:30 | 44535.7708 | 0 | 13.8984 | 37.78
2021-12-05 19:00 | 44535.7917 | 0 | 13.7553 | 37.78
2021-12-05 19:30 | 44535.8125 | 0 | 13.5617 | 37.78
2021-12-05 20:00 | 44535.8333 | 0 | 13.2331 | 37.78
2021-12-05 20:30 | 44535.8542 | 0 | 12.6869 | 37.78
2021-12-05 21:00 | 44535.875 | 0 | 12.196 | 37.78
2021-12-05 21:30 | 44535.8958 | 0 | 11.5856 | 37.78
2021-12-05 22:00 | 44535.9167 | 0 | 11.0965 | 37.78
2021-12-05 22:30 | 44535.9375 | 0 | 10.2558 | 37.78
2021-12-05 23:00 | 44535.9583 | 0 | 9.6873 | 37.78
2021-12-05 23:30 | 44535.9792 | 0 | 9.2585 | 37.78
2021-12-06 | 44536 | 0 | 8.8833 | 37.78
2021-12-06 00:30 | 44536.0208 | 0 | 8.6458 | 37.78
2021-12-06 01:00 | 44536.0417 | 0 | 8.523 | 37.78
2021-12-06 01:30 | 44536.0625 | 0 | 8.3267 | 37.78
2021-12-06 02:00 | 44536.0833 | 0 | 8.3182 | 37.78
2021-12-06 02:30 | 44536.1042 | 0 | 8.213 | 37.78
2021-12-06 03:00 | 44536.125 | 0 | 8.2279 | 37.78
2021-12-06 03:30 | 44536.1458 | 0 | 8.3612 | 37.78
2021-12-06 04:00 | 44536.1667 | 0 | 8.6241 | 37.78
2021-12-06 04:30 | 44536.1875 | 0 | 8.9088 | 37.78
2021-12-06 05:00 | 44536.2083 | 0 | 9.3736 | 37.78
2021-12-06 05:30 | 44536.2292 | 0 | 9.8471 | 37.78
2021-12-06 06:00 | 44536.25 | 0 | 11.153 | 37.78
2021-12-06 06:30 | 44536.2708 | 0 | 11.1921 | 37.78
2021-12-06 07:00 | 44536.2917 | 0 | 11.8528 | 37.78
2021-12-06 07:30 | 44536.3125 | 0 | 12.225 | 37.78
2021-12-06 08:00 | 44536.3333 | 0 | 12.9355 | 37.78
2021-12-06 08:30 | 44536.3542 | 0 | 11.4466 | 37.78
2021-12-06 09:00 | 44536.375 | 0 | 11.2352 | 37.78
2021-12-06 09:30 | 44536.3958 | 0 | 13.0982 | 37.78
2021-12-06 10:00 | 44536.4167 | 0 | 12.1898 | 37.78
2021-12-06 10:30 | 44536.4375 | 0 | 11.627 | 37.78
2021-12-06 11:00 | 44536.4583 | 0 | 12.3024 | 37.78
2021-12-06 11:30 | 44536.4792 | 0 | 11.9161 | 37.78
2021-12-06 12:00 | 44536.5 | 0 | 11.0541 | 37.78
2021-12-06 12:30 | 44536.5208 | 0 | 12.1199 | 37.78
2021-12-06 13:00 | 44536.5417 | 0 | 12.3034 | 37.78
2021-12-06 13:30 | 44536.5625 | 0 | 13.6628 | 37.78
2021-12-06 14:00 | 44536.5833 | 0 | 13.5399 | 37.78
2021-12-06 14:30 | 44536.6042 | 0 | 13.364 | 37.78
2021-12-06 15:00 | 44536.625 | 0 | 14.9004 | 37.78
2021-12-06 15:30 | 44536.6458 | 0 | 14.4812 | 37.78
2021-12-06 16:00 | 44536.6667 | 0 | 15.0042 | 37.78
2021-12-06 16:30 | 44536.6875 | 0 | 15.1114 | 37.78
2021-12-06 17:00 | 44536.7083 | 0 | 15.5132 | 37.78
2021-12-06 17:30 | 44536.7292 | 0 | 15.6071 | 37.78
2021-12-06 18:00 | 44536.75 | 0 | 15.8349 | 37.78
2021-12-06 18:30 | 44536.7708 | 0 | 16.4975 | 37.78
2021-12-06 19:00 | 44536.7917 | 0 | 16.445 | 37.78
2021-12-06 19:30 | 44536.8125 | 0 | 16.1479 | 37.78
2021-12-06 20:00 | 44536.8333 | 0 | 15.5754 | 37.78
2021-12-06 20:30 | 44536.8542 | 0 | 14.9322 | 37.78
2021-12-06 21:00 | 44536.875 | 0 | 14.2949 | 37.78
2021-12-06 21:30 | 44536.8958 | 0 | 13.8074 | 37.78
2021-12-06 22:00 | 44536.9167 | 0 | 13.0699 | 37.78
2021-12-06 22:30 | 44536.9375 | 0 | 11.9029 | 37.78
2021-12-06 23:00 | 44536.9583 | 0 | 11.1854 | 37.78
2021-12-06 23:30 | 44536.9792 | 0 | 10.5566 | 37.78
2021-12-07 | 44537 | 0 | 10.0103 | 37.78
2021-12-07 00:30 | 44537.0208 | 0 | 9.4315 | 37.78
2021-12-07 01:00 | 44537.0417 | 0 | 9.3775 | 37.78
2021-12-07 01:30 | 44537.0625 | 0 | 9.1605 | 37.78
2021-12-07 02:00 | 44537.0833 | 0 | 9.0765 | 37.78
2021-12-07 02:30 | 44537.1042 | 0 | 8.8306 | 37.78
2021-12-07 03:00 | 44537.125 | 0 | 8.9084 | 37.78
2021-12-07 03:30 | 44537.1458 | 0 | 8.9273 | 37.78
2021-12-07 04:00 | 44537.1667 | 0 | 9.3275 | 37.78
2021-12-07 04:30 | 44537.1875 | 0 | 9.4856 | 37.78
2021-12-07 05:00 | 44537.2083 | 0 | 9.9277 | 37.78
2021-12-07 05:30 | 44537.2292 | 0 | 10.3478 | 37.78
2021-12-07 06:00 | 44537.25 | 0 | 11.1921 | 37.78
2021-12-07 06:30 | 44537.2708 | 0 | 11.512 | 37.78
2021-12-07 07:00 | 44537.2917 | 0 | 12.1987 | 37.78
2021-12-07 07:30 | 44537.3125 | 0 | 12.8392 | 37.78
2021-12-07 08:00 | 44537.3333 | 0 | 12.8152 | 37.78
2021-12-07 08:30 | 44537.3542 | 0 | 13.3938 | 37.78
2021-12-07 09:00 | 44537.375 | 0 | 13.17 | 37.78
2021-12-07 09:30 | 44537.3958 | 0 | 13.1506 | 37.78
2021-12-07 10:00 | 44537.4167 | 0 | 13.0998 | 37.78
2021-12-07 10:30 | 44537.4375 | 0 | 12.273 | 37.78
2021-12-07 11:00 | 44537.4583 | 0 | 14.727 | 37.78
2021-12-07 11:30 | 44537.4792 | 0 | 15.0031 | 37.78
2021-12-07 12:00 | 44537.5 | 0 | 16.2956 | 37.78
2021-12-07 12:30 | 44537.5208 | 0 | 14.5785 | 37.78
2021-12-07 13:00 | 44537.5417 | 0 | 14.829 | 37.78
2021-12-07 13:30 | 44537.5625 | 0 | 15.1102 | 37.78
2021-12-07 14:00 | 44537.5833 | 0 | 16.1222 | 37.78
2021-12-07 14:30 | 44537.6042 | 0 | 14.7392 | 37.78
2021-12-07 15:00 | 44537.625 | 0 | 15.5047 | 37.78
2021-12-07 15:30 | 44537.6458 | 0 | 16.6493 | 37.78
2021-12-07 16:00 | 44537.6667 | 0 | 16.2203 | 37.78
2021-12-07 16:30 | 44537.6875 | 0 | 16.8902 | 37.78
2021-12-07 17:00 | 44537.7083 | 0 | 16.2752 | 37.78
2021-12-07 17:30 | 44537.7292 | 0 | 16.553 | 37.78
2021-12-07 18:00 | 44537.75 | 0 | 16.6935 | 37.78
2021-12-07 18:30 | 44537.7708 | 0 | 17.4287 | 37.78
2021-12-07 19:00 | 44537.7917 | 0 | 17.7258 | 37.78
2021-12-07 19:30 | 44537.8125 | 0 | 17.2218 | 37.78
2021-12-07 20:00 | 44537.8333 | 0 | 16.8018 | 37.78
2021-12-07 20:30 | 44537.8542 | 0 | 16.0952 | 37.78
2021-12-07 21:00 | 44537.875 | 0 | 15.5287 | 37.78
2021-12-07 21:30 | 44537.8958 | 0 | 15.0152 | 37.78
2021-12-07 22:00 | 44537.9167 | 0 | 14.0495 | 37.78
2021-12-07 22:30 | 44537.9375 | 0 | 13.1898 | 37.78
2021-12-07 23:00 | 44537.9583 | 0 | 12.4093 | 37.78
2021-12-07 23:30 | 44537.9792 | 0 | 11.7948 | 37.78
2021-12-08 | 44538 | 0 | 11.0995 | 37.78
2021-12-08 00:30 | 44538.0208 | 0 | 10.5683 | 37.78
2021-12-08 01:00 | 44538.0417 | 0 | 10.4476 | 37.78
2021-12-08 01:30 | 44538.0625 | 0 | 10.2117 | 37.78
2021-12-08 02:00 | 44538.0833 | 0 | 10.0342 | 37.78
2021-12-08 02:30 | 44538.1042 | 0 | 9.8979 | 37.78
2021-12-08 03:00 | 44538.125 | 0 | 9.7009 | 37.78
2021-12-08 03:30 | 44538.1458 | 0 | 9.9154 | 37.78
2021-12-08 04:00 | 44538.1667 | 0 | 10.1273 | 37.78
2021-12-08 04:30 | 44538.1875 | 0 | 10.5589 | 37.78
2021-12-08 05:00 | 44538.2083 | 0 | 10.9917 | 37.78
2021-12-08 05:30 | 44538.2292 | 0 | 11.2604 | 37.78
2021-12-08 06:00 | 44538.25 | 0 | 12.3304 | 37.78
2021-12-08 06:30 | 44538.2708 | 0 | 13.1407 | 37.78
2021-12-08 07:00 | 44538.2917 | 0 | 13.3376 | 37.78
2021-12-08 07:30 | 44538.3125 | 0 | 13.7638 | 37.78
2021-12-08 08:00 | 44538.3333 | 0 | 14.8627 | 37.78
2021-12-08 08:30 | 44538.3542 | 0 | 15.6997 | 37.78
2021-12-08 09:00 | 44538.375 | 0 | 15.8004 | 37.78
2021-12-08 09:30 | 44538.3958 | 0 | 15.4483 | 37.78
2021-12-08 10:00 | 44538.4167 | 0 | 14.8329 | 37.78
2021-12-08 10:30 | 44538.4375 | 0 | 14.0615 | 37.78
2021-12-08 11:00 | 44538.4583 | 0 | 13.7901 | 37.78
2021-12-08 11:30 | 44538.4792 | 0 | 15.071 | 37.78
2021-12-08 12:00 | 44538.5 | 0 | 15.6014 | 37.78
2021-12-08 12:30 | 44538.5208 | 0 | 14.5659 | 37.78
2021-12-08 13:00 | 44538.5417 | 0 | 15.8223 | 37.78
2021-12-08 13:30 | 44538.5625 | 0 | 16.2607 | 37.78
2021-12-08 14:00 | 44538.5833 | 0 | 17.4974 | 37.78
2021-12-08 14:30 | 44538.6042 | 0 | 18.8254 | 37.78
2021-12-08 15:00 | 44538.625 | 0 | 17.5857 | 37.78
2021-12-08 15:30 | 44538.6458 | 0 | 16.2406 | 37.78
2021-12-08 16:00 | 44538.6667 | 0 | 15.8638 | 37.78
2021-12-08 16:30 | 44538.6875 | 0 | 15.4713 | 37.78
2021-12-08 17:00 | 44538.7083 | 0 | 15.253 | 37.78
2021-12-08 17:30 | 44538.7292 | 0 | 15.2039 | 37.78
2021-12-08 18:00 | 44538.75 | 0 | 15.081 | 37.78
2021-12-08 18:30 | 44538.7708 | 0 | 15.3262 | 37.78
2021-12-08 19:00 | 44538.7917 | 0 | 15.3059 | 37.78
2021-12-08 19:30 | 44538.8125 | 0 | 15.1278 | 37.78
2021-12-08 20:00 | 44538.8333 | 0 | 14.7962 | 37.78
2021-12-08 20:30 | 44538.8542 | 0 | 14.2947 | 37.78
2021-12-08 21:00 | 44538.875 | 0 | 13.8252 | 37.78
2021-12-08 21:30 | 44538.8958 | 0 | 13.4151 | 37.78
2021-12-08 22:00 | 44538.9167 | 0 | 12.7823 | 37.78
2021-12-08 22:30 | 44538.9375 | 0 | 11.8459 | 37.78
2021-12-08 23:00 | 44538.9583 | 0 | 11.2133 | 37.78
2021-12-08 23:30 | 44538.9792 | 0 | 10.9419 | 37.78
2021-12-09 | 44539 | 0 | 10.3663 | 37.78
2021-12-09 00:30 | 44539.0208 | 0 | 9.9334 | 37.78
2021-12-09 01:00 | 44539.0417 | 0 | 9.7019 | 37.78
2021-12-09 01:30 | 44539.0625 | 0 | 9.4278 | 37.78
2021-12-09 02:00 | 44539.0833 | 0 | 9.3172 | 37.78
2021-12-09 02:30 | 44539.1042 | 0 | 9.0895 | 37.78
2021-12-09 03:00 | 44539.125 | 0 | 8.9876 | 37.78
2021-12-09 03:30 | 44539.1458 | 0 | 9.1801 | 37.78
2021-12-09 04:00 | 44539.1667 | 0 | 9.5162 | 37.78
2021-12-09 04:30 | 44539.1875 | 0 | 9.7685 | 37.78
2021-12-09 05:00 | 44539.2083 | 0 | 10.1519 | 37.78
2021-12-09 05:30 | 44539.2292 | 0 | 10.5056 | 37.78
2021-12-09 06:00 | 44539.25 | 0 | 11.2641 | 37.78
2021-12-09 06:30 | 44539.2708 | 0 | 11.7638 | 37.78
2021-12-09 07:00 | 44539.2917 | 0 | 12.1623 | 37.78
2021-12-09 07:30 | 44539.3125 | 0 | 12.2069 | 37.78
2021-12-09 08:00 | 44539.3333 | 0 | 12.2015 | 37.78
2021-12-09 08:30 | 44539.3542 | 0 | 12.3876 | 37.78
2021-12-09 09:00 | 44539.375 | 0 | 12.2859 | 37.78
2021-12-09 09:30 | 44539.3958 | 0 | 12.4016 | 37.78
2021-12-09 10:00 | 44539.4167 | 0 | 12.5757 | 37.78
2021-12-09 10:30 | 44539.4375 | 0 | 12.9643 | 37.78
2021-12-09 11:00 | 44539.4583 | 0 | 13.3745 | 37.78
2021-12-09 11:30 | 44539.4792 | 0 | 13.9944 | 37.78
2021-12-09 12:00 | 44539.5 | 0 | 14.9513 | 37.78
2021-12-09 12:30 | 44539.5208 | 0 | 16.066 | 37.78
2021-12-09 13:00 | 44539.5417 | 0 | 16.8559 | 37.78
2021-12-09 13:30 | 44539.5625 | 0 | 17.2882 | 37.78
2021-12-09 14:00 | 44539.5833 | 0 | 15.7883 | 37.78
2021-12-09 14:30 | 44539.6042 | 0 | 18.3382 | 37.78
2021-12-09 15:00 | 44539.625 | 0 | 17.7403 | 37.78
2021-12-09 15:30 | 44539.6458 | 0 | 18.1333 | 37.78
2021-12-09 16:00 | 44539.6667 | 0 | 18.6669 | 37.78
2021-12-09 16:30 | 44539.6875 | 0 | 19.0364 | 37.78
2021-12-09 17:00 | 44539.7083 | 0 | 20.2207 | 37.78
2021-12-09 17:30 | 44539.7292 | 0 | 19.5961 | 37.78
2021-12-09 18:00 | 44539.75 | 0 | 19.3493 | 37.78
2021-12-09 18:30 | 44539.7708 | 0 | 19.8149 | 37.78
2021-12-09 19:00 | 44539.7917 | 0 | 18.6189 | 37.78
2021-12-09 19:30 | 44539.8125 | 0 | 17.8386 | 37.78
2021-12-09 20:00 | 44539.8333 | 0 | 16.7749 | 37.78
2021-12-09 20:30 | 44539.8542 | 0 | 15.7742 | 37.78
2021-12-09 21:00 | 44539.875 | 0 | 14.9085 | 37.78
2021-12-09 21:30 | 44539.8958 | 0 | 14.4594 | 37.78
2021-12-09 22:00 | 44539.9167 | 0 | 13.4478 | 37.78
2021-12-09 22:30 | 44539.9375 | 0 | 12.6522 | 37.78
2021-12-09 23:00 | 44539.9583 | 0 | 11.9765 | 37.78
2021-12-09 23:30 | 44539.9792 | 0 | 11.2101 | 37.78
2021-12-10 | 44540 | 0 | 10.5872 | 37.78
2021-12-10 00:30 | 44540.0208 | 0 | 10.2426 | 37.78
2021-12-10 01:00 | 44540.0417 | 0 | 9.8838 | 37.78
2021-12-10 01:30 | 44540.0625 | 0 | 9.6436 | 37.78
2021-12-10 02:00 | 44540.0833 | 0 | 9.5949 | 37.78
2021-12-10 02:30 | 44540.1042 | 0 | 9.5457 | 37.78
2021-12-10 03:00 | 44540.125 | 0 | 9.276 | 37.78
2021-12-10 03:30 | 44540.1458 | 0 | 9.3621 | 37.78
2021-12-10 04:00 | 44540.1667 | 0 | 9.6754 | 37.78
2021-12-10 04:30 | 44540.1875 | 0 | 10.0086 | 37.78
2021-12-10 05:00 | 44540.2083 | 0 | 10.3001 | 37.78
2021-12-10 05:30 | 44540.2292 | 0 | 10.5913 | 37.78
2021-12-10 06:00 | 44540.25 | 0 | 11.3849 | 37.78
2021-12-10 06:30 | 44540.2708 | 0 | 11.8004 | 37.78
2021-12-10 07:00 | 44540.2917 | 0 | 12.1524 | 37.78
2021-12-10 07:30 | 44540.3125 | 0 | 12.624 | 37.78
2021-12-10 08:00 | 44540.3333 | 0 | 12.7788 | 37.78
2021-12-10 08:30 | 44540.3542 | 0 | 13.1864 | 37.78
2021-12-10 09:00 | 44540.375 | 0 | 13.0302 | 37.78
2021-12-10 09:30 | 44540.3958 | 0 | 13.9775 | 37.78
2021-12-10 10:00 | 44540.4167 | 0 | 14.0754 | 37.78
2021-12-10 10:30 | 44540.4375 | 0 | 15.5517 | 37.78
2021-12-10 11:00 | 44540.4583 | 0 | 15.5218 | 37.78
2021-12-10 11:30 | 44540.4792 | 0 | 15.7878 | 37.78
2021-12-10 12:00 | 44540.5 | 0 | 17.1672 | 37.78
2021-12-10 12:30 | 44540.5208 | 0 | 16.3598 | 37.78
2021-12-10 13:00 | 44540.5417 | 0 | 15.632 | 37.78
2021-12-10 13:30 | 44540.5625 | 0 | 15.5961 | 37.78
2021-12-10 14:00 | 44540.5833 | 0 | 15.1905 | 37.78
2021-12-10 14:30 | 44540.6042 | 0 | 15.8539 | 37.78
2021-12-10 15:00 | 44540.625 | 0 | 16.5667 | 37.78
2021-12-10 15:30 | 44540.6458 | 0 | 17.1757 | 37.78
2021-12-10 16:00 | 44540.6667 | 0 | 18.1636 | 37.78
2021-12-10 16:30 | 44540.6875 | 0 | 18.6006 | 37.78
2021-12-10 17:00 | 44540.7083 | 0 | 18.8731 | 37.78
2021-12-10 17:30 | 44540.7292 | 0 | 18.9938 | 37.78
2021-12-10 18:00 | 44540.75 | 0 | 18.4958 | 37.78
2021-12-10 18:30 | 44540.7708 | 0 | 18.1765 | 37.78
2021-12-10 19:00 | 44540.7917 | 0 | 18.0176 | 37.78
2021-12-10 19:30 | 44540.8125 | 0 | 17.5945 | 37.78
2021-12-10 20:00 | 44540.8333 | 0 | 17.3193 | 37.78
2021-12-10 20:30 | 44540.8542 | 0 | 16.5284 | 37.78
2021-12-10 21:00 | 44540.875 | 0 | 15.7381 | 37.78
2021-12-10 21:30 | 44540.8958 | 0 | 14.7461 | 37.78
2021-12-10 22:00 | 44540.9167 | 0 | 13.7056 | 37.78
2021-12-10 22:30 | 44540.9375 | 0 | 12.6062 | 37.78
2021-12-10 23:00 | 44540.9583 | 0 | 11.9219 | 37.78
2021-12-10 23:30 | 44540.9792 | 0 | 11.1177 | 37.78
2021-12-11 | 44541 | 0 | 10.622 | 37.78
2021-12-11 00:30 | 44541.0208 | 0 | 10.1867 | 37.78
2021-12-11 01:00 | 44541.0417 | 0 | 9.8904 | 37.78
2021-12-11 01:30 | 44541.0625 | 0 | 9.516 | 37.78
2021-12-11 02:00 | 44541.0833 | 0 | 9.2702 | 37.78
2021-12-11 02:30 | 44541.1042 | 0 | 9.0008 | 37.78
2021-12-11 03:00 | 44541.125 | 0 | 8.8643 | 37.78
2021-12-11 03:30 | 44541.1458 | 0 | 8.9922 | 37.78
2021-12-11 04:00 | 44541.1667 | 0 | 8.917 | 37.78
2021-12-11 04:30 | 44541.1875 | 0 | 8.8709 | 37.78
2021-12-11 05:00 | 44541.2083 | 0 | 8.8065 | 37.78
2021-12-11 05:30 | 44541.2292 | 0 | 8.7481 | 37.78
2021-12-11 06:00 | 44541.25 | 0 | 8.647 | 37.78
2021-12-11 06:30 | 44541.2708 | 0 | 8.4241 | 37.78
2021-12-11 07:00 | 44541.2917 | 0 | 8.4593 | 37.78
2021-12-11 07:30 | 44541.3125 | 0 | 8.3628 | 37.78
2021-12-11 08:00 | 44541.3333 | 0 | 8.4217 | 37.78
2021-12-11 08:30 | 44541.3542 | 0 | 8.2619 | 37.78
2021-12-11 09:00 | 44541.375 | 0 | 8.3458 | 37.78
2021-12-11 09:30 | 44541.3958 | 0 | 8.4875 | 37.78
2021-12-11 10:00 | 44541.4167 | 0 | 8.6231 | 37.78
2021-12-11 10:30 | 44541.4375 | 0 | 8.7621 | 37.78
2021-12-11 11:00 | 44541.4583 | 0 | 9.1857 | 37.78
2021-12-11 11:30 | 44541.4792 | 0 | 9.3747 | 37.78
2021-12-11 12:00 | 44541.5 | 0 | 9.4645 | 37.78
2021-12-11 12:30 | 44541.5208 | 0 | 9.8411 | 37.78
2021-12-11 13:00 | 44541.5417 | 0 | 10.3702 | 37.78
2021-12-11 13:30 | 44541.5625 | 0 | 11.7603 | 37.78
2021-12-11 14:00 | 44541.5833 | 0 | 13.6279 | 37.78
2021-12-11 14:30 | 44541.6042 | 0 | 12.9813 | 37.78
2021-12-11 15:00 | 44541.625 | 0 | 14.6732 | 37.78
2021-12-11 15:30 | 44541.6458 | 0 | 13.742 | 37.78
2021-12-11 16:00 | 44541.6667 | 0 | 13.6902 | 37.78
2021-12-11 16:30 | 44541.6875 | 0 | 13.9782 | 37.78
2021-12-11 17:00 | 44541.7083 | 0 | 13.8455 | 37.78
2021-12-11 17:30 | 44541.7292 | 0 | 14.0409 | 37.78
2021-12-11 18:00 | 44541.75 | 0 | 14.029 | 37.78
2021-12-11 18:30 | 44541.7708 | 0 | 14.2678 | 37.78
2021-12-11 19:00 | 44541.7917 | 0 | 14.1569 | 37.78
2021-12-11 19:30 | 44541.8125 | 0 | 14.0571 | 37.78
2021-12-11 20:00 | 44541.8333 | 0 | 13.6644 | 37.78
2021-12-11 20:30 | 44541.8542 | 0 | 13.1084 | 37.78
2021-12-11 21:00 | 44541.875 | 0 | 12.9479 | 37.78
2021-12-11 21:30 | 44541.8958 | 0 | 12.5048 | 37.78
2021-12-11 22:00 | 44541.9167 | 0 | 12.0153 | 37.78
2021-12-11 22:30 | 44541.9375 | 0 | 11.3091 | 37.78
2021-12-11 23:00 | 44541.9583 | 0 | 10.744 | 37.78
2021-12-11 23:30 | 44541.9792 | 0 | 10.2831 | 37.78
2021-12-12 | 44542 | 0 | 9.7682 | 37.78
2021-12-12 00:30 | 44542.0208 | 0 | 9.4784 | 37.78
2021-12-12 01:00 | 44542.0417 | 0 | 9.2363 | 37.78
2021-12-12 01:30 | 44542.0625 | 0 | 8.951 | 37.78
2021-12-12 02:00 | 44542.0833 | 0 | 8.7679 | 37.78
2021-12-12 02:30 | 44542.1042 | 0 | 8.626 | 37.78
2021-12-12 03:00 | 44542.125 | 0 | 8.4731 | 37.78
2021-12-12 03:30 | 44542.1458 | 0 | 8.5358 | 37.78
2021-12-12 04:00 | 44542.1667 | 0 | 8.4354 | 37.78
2021-12-12 04:30 | 44542.1875 | 0 | 8.3294 | 37.78
2021-12-12 05:00 | 44542.2083 | 0 | 8.0838 | 37.78
2021-12-12 05:30 | 44542.2292 | 0 | 8.1406 | 37.78
2021-12-12 06:00 | 44542.25 | 0 | 7.9949 | 37.78
2021-12-12 06:30 | 44542.2708 | 0 | 7.5942 | 37.78
2021-12-12 07:00 | 44542.2917 | 0 | 7.7551 | 37.78
2021-12-12 07:30 | 44542.3125 | 0 | 7.5562 | 37.78
2021-12-12 08:00 | 44542.3333 | 0 | 7.6103 | 37.78
2021-12-12 08:30 | 44542.3542 | 0 | 8.7277 | 37.78
2021-12-12 09:00 | 44542.375 | 0 | 8.6396 | 37.78
2021-12-12 09:30 | 44542.3958 | 0 | 8.7731 | 37.78
2021-12-12 10:00 | 44542.4167 | 0 | 8.7952 | 37.78
2021-12-12 10:30 | 44542.4375 | 0 | 10.878 | 37.78
2021-12-12 11:00 | 44542.4583 | 0 | 9.9563 | 37.78
2021-12-12 11:30 | 44542.4792 | 0 | 10.0366 | 37.78
2021-12-12 12:00 | 44542.5 | 0 | 9.7269 | 37.78
2021-12-12 12:30 | 44542.5208 | 0 | 9.0958 | 37.78
2021-12-12 13:00 | 44542.5417 | 0 | 8.9315 | 37.78
2021-12-12 13:30 | 44542.5625 | 0 | 10.6193 | 37.78
2021-12-12 14:00 | 44542.5833 | 0 | 11.6431 | 37.78
2021-12-12 14:30 | 44542.6042 | 0 | 10.5689 | 37.78
2021-12-12 15:00 | 44542.625 | 0 | 11.2726 | 37.78
2021-12-12 15:30 | 44542.6458 | 0 | 13.0941 | 37.78
2021-12-12 16:00 | 44542.6667 | 0 | 12.5799 | 37.78
2021-12-12 16:30 | 44542.6875 | 0 | 13.5902 | 37.78
2021-12-12 17:00 | 44542.7083 | 0 | 13.8235 | 37.78
2021-12-12 17:30 | 44542.7292 | 0 | 13.9746 | 37.78
2021-12-12 18:00 | 44542.75 | 0 | 13.9895 | 37.78
2021-12-12 18:30 | 44542.7708 | 0 | 14.2171 | 37.78
2021-12-12 19:00 | 44542.7917 | 0 | 14.3733 | 37.78
2021-12-12 19:30 | 44542.8125 | 0 | 14.135 | 37.78
2021-12-12 20:00 | 44542.8333 | 0 | 13.8072 | 37.78
2021-12-12 20:30 | 44542.8542 | 0 | 13.1935 | 37.78
2021-12-12 21:00 | 44542.875 | 0 | 12.8063 | 37.78
2021-12-12 21:30 | 44542.8958 | 0 | 12.1122 | 37.78
2021-12-12 22:00 | 44542.9167 | 0 | 11.6036 | 37.78
2021-12-12 22:30 | 44542.9375 | 0 | 10.8306 | 37.78
2021-12-12 23:00 | 44542.9583 | 0 | 10.3256 | 37.78
2021-12-12 23:30 | 44542.9792 | 0 | 10.0971 | 37.78
2021-12-13 | 44543 | 0 | 9.7273 | 37.78
2021-12-13 00:30 | 44543.0208 | 0 | 9.4334 | 37.78
2021-12-13 01:00 | 44543.0417 | 0 | 9.1704 | 37.78
2021-12-13 01:30 | 44543.0625 | 0 | 8.8645 | 37.78
2021-12-13 02:00 | 44543.0833 | 0 | 8.9125 | 37.78
2021-12-13 02:30 | 44543.1042 | 0 | 8.7497 | 37.78
2021-12-13 03:00 | 44543.125 | 0 | 8.5803 | 37.78
2021-12-13 03:30 | 44543.1458 | 0 | 8.8525 | 37.78
2021-12-13 04:00 | 44543.1667 | 0 | 9.053 | 37.78
2021-12-13 04:30 | 44543.1875 | 0 | 9.41 | 37.78
2021-12-13 05:00 | 44543.2083 | 0 | 9.7303 | 37.78
2021-12-13 05:30 | 44543.2292 | 0 | 10.3053 | 37.78
2021-12-13 06:00 | 44543.25 | 0 | 10.8285 | 37.78
2021-12-13 06:30 | 44543.2708 | 0 | 11.2813 | 37.78
2021-12-13 07:00 | 44543.2917 | 0 | 11.6589 | 37.78
2021-12-13 07:30 | 44543.3125 | 0 | 11.6989 | 37.78
2021-12-13 08:00 | 44543.3333 | 0 | 11.6385 | 37.78
2021-12-13 08:30 | 44543.3542 | 0 | 11.8595 | 37.78
2021-12-13 09:00 | 44543.375 | 0 | 12.1603 | 37.78
2021-12-13 09:30 | 44543.3958 | 0 | 13.5514 | 37.78
2021-12-13 10:00 | 44543.4167 | 0 | 13.7903 | 37.78
2021-12-13 10:30 | 44543.4375 | 0 | 12.7865 | 37.78
2021-12-13 11:00 | 44543.4583 | 0 | 11.9447 | 37.78
2021-12-13 11:30 | 44543.4792 | 0 | 13.9572 | 37.78
2021-12-13 12:00 | 44543.5 | 0 | 14.297 | 37.78
2021-12-13 12:30 | 44543.5208 | 0 | 13.7562 | 37.78
2021-12-13 13:00 | 44543.5417 | 0 | 13.4969 | 37.78
2021-12-13 13:30 | 44543.5625 | 0 | 14.6174 | 37.78
2021-12-13 14:00 | 44543.5833 | 0 | 13.3545 | 37.78
2021-12-13 14:30 | 44543.6042 | 0 | 14.2653 | 37.78
2021-12-13 15:00 | 44543.625 | 0 | 14.6271 | 37.78
2021-12-13 15:30 | 44543.6458 | 0 | 15.2186 | 37.78
2021-12-13 16:00 | 44543.6667 | 0 | 15.7549 | 37.78
2021-12-13 16:30 | 44543.6875 | 0 | 15.7371 | 37.78
2021-12-13 17:00 | 44543.7083 | 0 | 15.9956 | 37.78
2021-12-13 17:30 | 44543.7292 | 0 | 16.219 | 37.78
2021-12-13 18:00 | 44543.75 | 0 | 16.0502 | 37.78
2021-12-13 18:30 | 44543.7708 | 0 | 16.3168 | 37.78
2021-12-13 19:00 | 44543.7917 | 0 | 16.2816 | 37.78
2021-12-13 19:30 | 44543.8125 | 0 | 15.9929 | 37.78
2021-12-13 20:00 | 44543.8333 | 0 | 15.6503 | 37.78
2021-12-13 20:30 | 44543.8542 | 0 | 14.8597 | 37.78
2021-12-13 21:00 | 44543.875 | 0 | 14.309 | 37.78
2021-12-13 21:30 | 44543.8958 | 0 | 13.98 | 37.78
2021-12-13 22:00 | 44543.9167 | 0 | 13.1978 | 37.78
2021-12-13 22:30 | 44543.9375 | 0 | 12.3722 | 37.78
2021-12-13 23:00 | 44543.9583 | 0 | 11.6044 | 37.78
2021-12-13 23:30 | 44543.9792 | 0 | 10.8984 | 37.78
2021-12-14 | 44544 | 0 | 10.2446 | 37.78
2021-12-14 00:30 | 44544.0208 | 0 | 9.9231 | 37.78
2021-12-14 01:00 | 44544.0417 | 0 | 9.7082 | 37.78
2021-12-14 01:30 | 44544.0625 | 0 | 9.5116 | 37.78
2021-12-14 02:00 | 44544.0833 | 0 | 9.2933 | 37.78
2021-12-14 02:30 | 44544.1042 | 0 | 9.179 | 37.78
2021-12-14 03:00 | 44544.125 | 0 | 8.8929 | 37.78
2021-12-14 03:30 | 44544.1458 | 0 | 9.0059 | 37.78
2021-12-14 04:00 | 44544.1667 | 0 | 9.203 | 37.78
2021-12-14 04:30 | 44544.1875 | 0 | 9.5207 | 37.78
2021-12-14 05:00 | 44544.2083 | 0 | 9.9903 | 37.78
2021-12-14 05:30 | 44544.2292 | 0 | 10.3227 | 37.78
2021-12-14 06:00 | 44544.25 | 0 | 11.0176 | 37.78
2021-12-14 06:30 | 44544.2708 | 0 | 11.2642 | 37.78
2021-12-14 07:00 | 44544.2917 | 0 | 11.3903 | 37.78
2021-12-14 07:30 | 44544.3125 | 0 | 11.5295 | 37.78
2021-12-14 08:00 | 44544.3333 | 0 | 11.276 | 37.78
2021-12-14 08:30 | 44544.3542 | 0 | 11.156 | 37.78
2021-12-14 09:00 | 44544.375 | 0 | 11.0116 | 37.78
2021-12-14 09:30 | 44544.3958 | 0 | 11.1052 | 37.78
2021-12-14 10:00 | 44544.4167 | 0 | 11.148 | 37.78
2021-12-14 10:30 | 44544.4375 | 0 | 11.278 | 37.78
2021-12-14 11:00 | 44544.4583 | 0 | 11.3172 | 37.78
2021-12-14 11:30 | 44544.4792 | 0 | 11.9395 | 37.78
2021-12-14 12:00 | 44544.5 | 0 | 11.9164 | 37.78
2021-12-14 12:30 | 44544.5208 | 0 | 12.2419 | 37.78
2021-12-14 13:00 | 44544.5417 | 0 | 12.8504 | 37.78
2021-12-14 13:30 | 44544.5625 | 0 | 13.4167 | 37.78
2021-12-14 14:00 | 44544.5833 | 0 | 14.0022 | 37.78
2021-12-14 14:30 | 44544.6042 | 0 | 14.5059 | 37.78
2021-12-14 15:00 | 44544.625 | 0 | 15.1411 | 37.78
2021-12-14 15:30 | 44544.6458 | 0 | 15.6267 | 37.78
2021-12-14 16:00 | 44544.6667 | 0 | 16.2609 | 37.78
2021-12-14 16:30 | 44544.6875 | 0 | 16.8062 | 37.78
2021-12-14 17:00 | 44544.7083 | 0 | 17.1603 | 37.78
2021-12-14 17:30 | 44544.7292 | 0 | 17.2523 | 37.78
2021-12-14 18:00 | 44544.75 | 0 | 17.1828 | 37.78
2021-12-14 18:30 | 44544.7708 | 0 | 17.205 | 37.78
2021-12-14 19:00 | 44544.7917 | 0 | 16.9171 | 37.78
2021-12-14 19:30 | 44544.8125 | 0 | 16.6509 | 37.78
2021-12-14 20:00 | 44544.8333 | 0 | 16.2148 | 37.78
2021-12-14 20:30 | 44544.8542 | 0 | 15.3684 | 37.78
2021-12-14 21:00 | 44544.875 | 0 | 14.6758 | 37.78
2021-12-14 21:30 | 44544.8958 | 0 | 13.9124 | 37.78
2021-12-14 22:00 | 44544.9167 | 0 | 13.1246 | 37.78
2021-12-14 22:30 | 44544.9375 | 0 | 12.3235 | 37.78
2021-12-14 23:00 | 44544.9583 | 0 | 11.6563 | 37.78
2021-12-14 23:30 | 44544.9792 | 0 | 11.0264 | 37.78
2021-12-15 | 44545 | 0 | 10.2127 | 37.78
2021-12-15 00:30 | 44545.0208 | 0 | 9.939 | 37.78
2021-12-15 01:00 | 44545.0417 | 0 | 9.7106 | 37.78
2021-12-15 01:30 | 44545.0625 | 0 | 9.4048 | 37.78
2021-12-15 02:00 | 44545.0833 | 0 | 9.3563 | 37.78
2021-12-15 02:30 | 44545.1042 | 0 | 9.1327 | 37.78
2021-12-15 03:00 | 44545.125 | 0 | 8.9999 | 37.78
2021-12-15 03:30 | 44545.1458 | 0 | 9.1395 | 37.78
2021-12-15 04:00 | 44545.1667 | 0 | 9.3878 | 37.78
2021-12-15 04:30 | 44545.1875 | 0 | 9.5507 | 37.78
2021-12-15 05:00 | 44545.2083 | 0 | 9.8774 | 37.78
2021-12-15 05:30 | 44545.2292 | 0 | 10.3465 | 37.78
2021-12-15 06:00 | 44545.25 | 0 | 10.7613 | 37.78
2021-12-15 06:30 | 44545.2708 | 0 | 11.1336 | 37.78
2021-12-15 07:00 | 44545.2917 | 0 | 11.5072 | 37.78
2021-12-15 07:30 | 44545.3125 | 0 | 11.4203 | 37.78
2021-12-15 08:00 | 44545.3333 | 0 | 11.4894 | 37.78
2021-12-15 08:30 | 44545.3542 | 0 | 11.3139 | 37.78
2021-12-15 09:00 | 44545.375 | 0 | 11.3147 | 37.78
2021-12-15 09:30 | 44545.3958 | 0 | 11.6186 | 37.78
2021-12-15 10:00 | 44545.4167 | 0 | 11.8712 | 37.78
2021-12-15 10:30 | 44545.4375 | 0 | 12.0141 | 37.78
2021-12-15 11:00 | 44545.4583 | 0 | 11.8392 | 37.78
2021-12-15 11:30 | 44545.4792 | 0 | 12.2347 | 37.78
2021-12-15 12:00 | 44545.5 | 0 | 12.6583 | 37.78
2021-12-15 12:30 | 44545.5208 | 0 | 12.8452 | 37.78
2021-12-15 13:00 | 44545.5417 | 0 | 13.4421 | 37.78
2021-12-15 13:30 | 44545.5625 | 0 | 13.7425 | 37.78
2021-12-15 14:00 | 44545.5833 | 0 | 14.5323 | 37.78
2021-12-15 14:30 | 44545.6042 | 0 | 14.9955 | 37.78
2021-12-15 15:00 | 44545.625 | 0 | 15.6353 | 37.78
2021-12-15 15:30 | 44545.6458 | 0 | 16.1715 | 37.78
2021-12-15 16:00 | 44545.6667 | 0 | 16.8432 | 37.78
2021-12-15 16:30 | 44545.6875 | 0 | 17.5195 | 37.78
2021-12-15 17:00 | 44545.7083 | 0 | 17.6978 | 37.78
2021-12-15 17:30 | 44545.7292 | 0 | 17.8855 | 37.78
2021-12-15 18:00 | 44545.75 | 0 | 17.6421 | 37.78
2021-12-15 18:30 | 44545.7708 | 0 | 17.7975 | 37.78
2021-12-15 19:00 | 44545.7917 | 0 | 17.6965 | 37.78
2021-12-15 19:30 | 44545.8125 | 0 | 17.5432 | 37.78
2021-12-15 20:00 | 44545.8333 | 0 | 17.0123 | 37.78
2021-12-15 20:30 | 44545.8542 | 0 | 16.2654 | 37.78
2021-12-15 21:00 | 44545.875 | 0 | 15.5398 | 37.78
2021-12-15 21:30 | 44545.8958 | 0 | 14.8879 | 37.78
2021-12-15 22:00 | 44545.9167 | 0 | 14.0329 | 37.78
2021-12-15 22:30 | 44545.9375 | 0 | 13.023 | 37.78
2021-12-15 23:00 | 44545.9583 | 0 | 12.2297 | 37.78
2021-12-15 23:30 | 44545.9792 | 0 | 11.7647 | 37.78
2021-12-16 | 44546 | 0 | 10.8369 | 37.78
2021-12-16 00:30 | 44546.0208 | 0 | 10.5155 | 37.78
2021-12-16 01:00 | 44546.0417 | 0 | 10.3091 | 37.78
2021-12-16 01:30 | 44546.0625 | 0 | 10.049 | 37.78
2021-12-16 02:00 | 44546.0833 | 0 | 10.1329 | 37.78
2021-12-16 02:30 | 44546.1042 | 0 | 9.9464 | 37.78
2021-12-16 03:00 | 44546.125 | 0 | 9.899 | 37.78
2021-12-16 03:30 | 44546.1458 | 0 | 9.8724 | 37.78
2021-12-16 04:00 | 44546.1667 | 0 | 10.0623 | 37.78
2021-12-16 04:30 | 44546.1875 | 0 | 10.2171 | 37.78
2021-12-16 05:00 | 44546.2083 | 0 | 10.5255 | 37.78
2021-12-16 05:30 | 44546.2292 | 0 | 11.0481 | 37.78
2021-12-16 06:00 | 44546.25 | 0 | 11.373 | 37.78
2021-12-16 06:30 | 44546.2708 | 0 | 11.6667 | 37.78
2021-12-16 07:00 | 44546.2917 | 0 | 12.6405 | 37.78
2021-12-16 07:30 | 44546.3125 | 0 | 12.3443 | 37.78
2021-12-16 08:00 | 44546.3333 | 0 | 12.4316 | 37.78
2021-12-16 08:30 | 44546.3542 | 0 | 12.6014 | 37.78
2021-12-16 09:00 | 44546.375 | 0 | 12.7411 | 37.78
2021-12-16 09:30 | 44546.3958 | 0 | 13.0355 | 37.78
2021-12-16 10:00 | 44546.4167 | 0 | 13.095 | 37.78
2021-12-16 10:30 | 44546.4375 | 0 | 13.4875 | 37.78
2021-12-16 11:00 | 44546.4583 | 0 | 13.8328 | 37.78
2021-12-16 11:30 | 44546.4792 | 0 | 16.4784 | 37.78
2021-12-16 12:00 | 44546.5 | 0 | 15.3533 | 37.78
2021-12-16 12:30 | 44546.5208 | 0 | 14.3778 | 37.78
2021-12-16 13:00 | 44546.5417 | 0 | 15.5137 | 37.78
2021-12-16 13:30 | 44546.5625 | 0 | 15.8748 | 37.78
2021-12-16 14:00 | 44546.5833 | 0 | 16.3213 | 37.78
2021-12-16 14:30 | 44546.6042 | 0 | 19.1966 | 37.78
2021-12-16 15:00 | 44546.625 | 0 | 19.2766 | 37.78
2021-12-16 15:30 | 44546.6458 | 0 | 17.4641 | 37.78
2021-12-16 16:00 | 44546.6667 | 0 | 17.614 | 37.78
2021-12-16 16:30 | 44546.6875 | 0 | 18.39 | 37.78
2021-12-16 17:00 | 44546.7083 | 0 | 18.0939 | 37.78
2021-12-16 17:30 | 44546.7292 | 0 | 18.7296 | 37.78
2021-12-16 18:00 | 44546.75 | 0 | 18.5471 | 37.78
2021-12-16 18:30 | 44546.7708 | 0 | 18.8476 | 37.78
2021-12-16 19:00 | 44546.7917 | 0 | 18.7943 | 37.78
2021-12-16 19:30 | 44546.8125 | 0 | 18.4605 | 37.78
2021-12-16 20:00 | 44546.8333 | 0 | 18.023 | 37.78
2021-12-16 20:30 | 44546.8542 | 0 | 17.4607 | 37.78
2021-12-16 21:00 | 44546.875 | 0 | 16.7614 | 37.78
2021-12-16 21:30 | 44546.8958 | 0 | 16.0059 | 37.78
2021-12-16 22:00 | 44546.9167 | 0 | 14.9489 | 37.78
2021-12-16 22:30 | 44546.9375 | 0 | 14.1239 | 37.78
2021-12-16 23:00 | 44546.9583 | 0 | 13.1915 | 37.78
2021-12-16 23:30 | 44546.9792 | 0 | 12.521 | 37.78
2021-12-17 | 44547 | 0 | 11.7826 | 37.78
2021-12-17 00:30 | 44547.0208 | 0 | 11.2325 | 37.78
2021-12-17 01:00 | 44547.0417 | 0 | 11.0749 | 37.78
2021-12-17 01:30 | 44547.0625 | 0 | 10.6608 | 37.78
2021-12-17 02:00 | 44547.0833 | 0 | 10.5002 | 37.78
2021-12-17 02:30 | 44547.1042 | 0 | 10.3427 | 37.78
2021-12-17 03:00 | 44547.125 | 0 | 10.248 | 37.78
2021-12-17 03:30 | 44547.1458 | 0 | 10.2918 | 37.78
2021-12-17 04:00 | 44547.1667 | 0 | 10.5827 | 37.78
2021-12-17 04:30 | 44547.1875 | 0 | 10.8212 | 37.78
2021-12-17 05:00 | 44547.2083 | 0 | 10.9287 | 37.78
2021-12-17 05:30 | 44547.2292 | 0 | 11.1991 | 37.78
2021-12-17 06:00 | 44547.25 | 0 | 11.9453 | 37.78
2021-12-17 06:30 | 44547.2708 | 0 | 12.6291 | 37.78
2021-12-17 07:00 | 44547.2917 | 0 | 13.5174 | 37.78
2021-12-17 07:30 | 44547.3125 | 0 | 14.3201 | 37.78
2021-12-17 08:00 | 44547.3333 | 0 | 14.8922 | 37.78
2021-12-17 08:30 | 44547.3542 | 0 | 14.6739 | 37.78
2021-12-17 09:00 | 44547.375 | 0 | 14.6309 | 37.78
2021-12-17 09:30 | 44547.3958 | 0 | 13.7998 | 37.78
2021-12-17 10:00 | 44547.4167 | 0 | 13.837 | 37.78
2021-12-17 10:30 | 44547.4375 | 0 | 14.0874 | 37.78
2021-12-17 11:00 | 44547.4583 | 0 | 15.0076 | 37.78
2021-12-17 11:30 | 44547.4792 | 0 | 18.0275 | 37.78
2021-12-17 12:00 | 44547.5 | 0 | 15.3911 | 37.78
2021-12-17 12:30 | 44547.5208 | 0 | 14.2976 | 37.78
2021-12-17 13:00 | 44547.5417 | 0 | 14.5479 | 37.78
2021-12-17 13:30 | 44547.5625 | 0 | 15.667 | 37.78
2021-12-17 14:00 | 44547.5833 | 0 | 17.4592 | 37.78
2021-12-17 14:30 | 44547.6042 | 0 | 18.3601 | 37.78
2021-12-17 15:00 | 44547.625 | 0 | 19.0128 | 37.78
2021-12-17 15:30 | 44547.6458 | 0 | 17.7974 | 37.78
2021-12-17 16:00 | 44547.6667 | 0 | 17.2158 | 37.78
2021-12-17 16:30 | 44547.6875 | 0 | 17.5115 | 37.78
2021-12-17 17:00 | 44547.7083 | 0 | 17.0369 | 37.78
2021-12-17 17:30 | 44547.7292 | 0 | 16.9412 | 37.78
2021-12-17 18:00 | 44547.75 | 0 | 16.6643 | 37.78
2021-12-17 18:30 | 44547.7708 | 0 | 16.8871 | 37.78
2021-12-17 19:00 | 44547.7917 | 0 | 16.4461 | 37.78
2021-12-17 19:30 | 44547.8125 | 0 | 16.3255 | 37.78
2021-12-17 20:00 | 44547.8333 | 0 | 16.0146 | 37.78
2021-12-17 20:30 | 44547.8542 | 0 | 15.5288 | 37.78
2021-12-17 21:00 | 44547.875 | 0 | 14.9254 | 37.78
2021-12-17 21:30 | 44547.8958 | 0 | 14.6726 | 37.78
2021-12-17 22:00 | 44547.9167 | 0 | 14.0078 | 37.78
2021-12-17 22:30 | 44547.9375 | 0 | 13.2729 | 37.78
2021-12-17 23:00 | 44547.9583 | 0 | 12.6328 | 37.78
2021-12-17 23:30 | 44547.9792 | 0 | 11.9857 | 37.78
2021-12-18 | 44548 | 0 | 11.2689 | 37.78
2021-12-18 00:30 | 44548.0208 | 0 | 10.8146 | 37.78
2021-12-18 01:00 | 44548.0417 | 0 | 10.6893 | 37.78
2021-12-18 01:30 | 44548.0625 | 0 | 10.2553 | 37.78
2021-12-18 02:00 | 44548.0833 | 0 | 10.0902 | 37.78
2021-12-18 02:30 | 44548.1042 | 0 | 9.8794 | 37.78
2021-12-18 03:00 | 44548.125 | 0 | 9.6486 | 37.78
2021-12-18 03:30 | 44548.1458 | 0 | 9.5887 | 37.78
2021-12-18 04:00 | 44548.1667 | 0 | 9.6031 | 37.78
2021-12-18 04:30 | 44548.1875 | 0 | 9.4419 | 37.78
2021-12-18 05:00 | 44548.2083 | 0 | 9.4413 | 37.78
2021-12-18 05:30 | 44548.2292 | 0 | 9.4411 | 37.78
2021-12-18 06:00 | 44548.25 | 0 | 9.5009 | 37.78
2021-12-18 06:30 | 44548.2708 | 0 | 9.4411 | 37.78
2021-12-18 07:00 | 44548.2917 | 0 | 10.4647 | 37.78
2021-12-18 07:30 | 44548.3125 | 0 | 10.2843 | 37.78
2021-12-18 08:00 | 44548.3333 | 0 | 9.8491 | 37.78
2021-12-18 08:30 | 44548.3542 | 0 | 11.1723 | 37.78
2021-12-18 09:00 | 44548.375 | 0 | 12.1861 | 37.78
2021-12-18 09:30 | 44548.3958 | 0 | 10.5182 | 37.78
2021-12-18 10:00 | 44548.4167 | 0 | 10.5979 | 37.78
2021-12-18 10:30 | 44548.4375 | 0 | 10.8453 | 37.78
2021-12-18 11:00 | 44548.4583 | 0 | 11.0484 | 37.78
2021-12-18 11:30 | 44548.4792 | 0 | 11.6992 | 37.78
2021-12-18 12:00 | 44548.5 | 0 | 11.4072 | 37.78
2021-12-18 12:30 | 44548.5208 | 0 | 11.8604 | 37.78
2021-12-18 13:00 | 44548.5417 | 0 | 11.61 | 37.78
2021-12-18 13:30 | 44548.5625 | 0 | 12.3646 | 37.78
2021-12-18 14:00 | 44548.5833 | 0 | 12.1532 | 37.78
2021-12-18 14:30 | 44548.6042 | 0 | 13.0577 | 37.78
2021-12-18 15:00 | 44548.625 | 0 | 13.6693 | 37.78
2021-12-18 15:30 | 44548.6458 | 0 | 14.4034 | 37.78
2021-12-18 16:00 | 44548.6667 | 0 | 14.858 | 37.78
2021-12-18 16:30 | 44548.6875 | 0 | 15.1576 | 37.78
2021-12-18 17:00 | 44548.7083 | 0 | 15.4795 | 37.78
2021-12-18 17:30 | 44548.7292 | 0 | 15.7409 | 37.78
2021-12-18 18:00 | 44548.75 | 0 | 15.5191 | 37.78
2021-12-18 18:30 | 44548.7708 | 0 | 15.6293 | 37.78
2021-12-18 19:00 | 44548.7917 | 0 | 15.4497 | 37.78
2021-12-18 19:30 | 44548.8125 | 0 | 15.146 | 37.78
2021-12-18 20:00 | 44548.8333 | 0 | 14.8622 | 37.78
2021-12-18 20:30 | 44548.8542 | 0 | 14.2961 | 37.78
2021-12-18 21:00 | 44548.875 | 0 | 13.9106 | 37.78
2021-12-18 21:30 | 44548.8958 | 0 | 13.3015 | 37.78
2021-12-18 22:00 | 44548.9167 | 0 | 12.7315 | 37.78
2021-12-18 22:30 | 44548.9375 | 0 | 11.8916 | 37.78
2021-12-18 23:00 | 44548.9583 | 0 | 11.1946 | 37.78
2021-12-18 23:30 | 44548.9792 | 0 | 10.6701 | 37.78
2021-12-19 | 44549 | 0 | 10.0809 | 37.78
2021-12-19 00:30 | 44549.0208 | 0 | 9.6971 | 37.78
2021-12-19 01:00 | 44549.0417 | 0 | 9.3386 | 37.78
2021-12-19 01:30 | 44549.0625 | 0 | 9.0076 | 37.78
2021-12-19 02:00 | 44549.0833 | 0 | 8.9521 | 37.78
2021-12-19 02:30 | 44549.1042 | 0 | 8.8071 | 37.78
2021-12-19 03:00 | 44549.125 | 0 | 8.523 | 37.78
2021-12-19 03:30 | 44549.1458 | 0 | 8.4048 | 37.78
2021-12-19 04:00 | 44549.1667 | 0 | 8.4897 | 37.78
2021-12-19 04:30 | 44549.1875 | 0 | 8.3337 | 37.78
2021-12-19 05:00 | 44549.2083 | 0 | 8.1493 | 37.78
2021-12-19 05:30 | 44549.2292 | 0 | 8.1752 | 37.78
2021-12-19 06:00 | 44549.25 | 0 | 8.1118 | 37.78
2021-12-19 06:30 | 44549.2708 | 0 | 7.7962 | 37.78
2021-12-19 07:00 | 44549.2917 | 0 | 7.9007 | 37.78
2021-12-19 07:30 | 44549.3125 | 0 | 8.2981 | 37.78
2021-12-19 08:00 | 44549.3333 | 0 | 8.4816 | 37.78
2021-12-19 08:30 | 44549.3542 | 0 | 8.7626 | 37.78
2021-12-19 09:00 | 44549.375 | 0 | 9.1952 | 37.78
2021-12-19 09:30 | 44549.3958 | 0 | 9.7155 | 37.78
2021-12-19 10:00 | 44549.4167 | 0 | 9.0769 | 37.78
2021-12-19 10:30 | 44549.4375 | 0 | 9.0912 | 37.78
2021-12-19 11:00 | 44549.4583 | 0 | 9.5621 | 37.78
2021-12-19 11:30 | 44549.4792 | 0 | 9.701 | 37.78
2021-12-19 12:00 | 44549.5 | 0 | 9.8963 | 37.78
2021-12-19 12:30 | 44549.5208 | 0 | 10.1608 | 37.78
2021-12-19 13:00 | 44549.5417 | 0 | 10.7316 | 37.78
2021-12-19 13:30 | 44549.5625 | 0 | 11.0682 | 37.78
2021-12-19 14:00 | 44549.5833 | 0 | 11.6097 | 37.78
2021-12-19 14:30 | 44549.6042 | 0 | 12.26 | 37.78
2021-12-19 15:00 | 44549.625 | 0 | 12.8708 | 37.78
2021-12-19 15:30 | 44549.6458 | 0 | 13.4766 | 37.78
2021-12-19 16:00 | 44549.6667 | 0 | 14.09 | 37.78
2021-12-19 16:30 | 44549.6875 | 0 | 14.9156 | 37.78
2021-12-19 17:00 | 44549.7083 | 0 | 15.3995 | 37.78
2021-12-19 17:30 | 44549.7292 | 0 | 15.6001 | 37.78
2021-12-19 18:00 | 44549.75 | 0 | 15.5572 | 37.78
2021-12-19 18:30 | 44549.7708 | 0 | 16.1532 | 37.78
2021-12-19 19:00 | 44549.7917 | 0 | 16.1346 | 37.78
2021-12-19 19:30 | 44549.8125 | 0 | 15.9041 | 37.78
2021-12-19 20:00 | 44549.8333 | 0 | 15.7023 | 37.78
2021-12-19 20:30 | 44549.8542 | 0 | 15.1593 | 37.78
2021-12-19 21:00 | 44549.875 | 0 | 14.7985 | 37.78
2021-12-19 21:30 | 44549.8958 | 0 | 14.0262 | 37.78
2021-12-19 22:00 | 44549.9167 | 0 | 13.2942 | 37.78
2021-12-19 22:30 | 44549.9375 | 0 | 12.3552 | 37.78
2021-12-19 23:00 | 44549.9583 | 0 | 11.6674 | 37.78
2021-12-19 23:30 | 44549.9792 | 0 | 10.9893 | 37.78
2021-12-20 | 44550 | 0 | 10.6914 | 37.78
2021-12-20 00:30 | 44550.0208 | 0 | 10.1122 | 37.78
2021-12-20 01:00 | 44550.0417 | 0 | 9.927 | 37.78
2021-12-20 01:30 | 44550.0625 | 0 | 9.673 | 37.78
2021-12-20 02:00 | 44550.0833 | 0 | 9.6248 | 37.78
2021-12-20 02:30 | 44550.1042 | 0 | 9.4574 | 37.78
2021-12-20 03:00 | 44550.125 | 0 | 9.2919 | 37.78
2021-12-20 03:30 | 44550.1458 | 0 | 9.5289 | 37.78
2021-12-20 04:00 | 44550.1667 | 0 | 9.8603 | 37.78
2021-12-20 04:30 | 44550.1875 | 0 | 10.0628 | 37.78
2021-12-20 05:00 | 44550.2083 | 0 | 10.5323 | 37.78
2021-12-20 05:30 | 44550.2292 | 0 | 10.9727 | 37.78
2021-12-20 06:00 | 44550.25 | 0 | 11.7481 | 37.78
2021-12-20 06:30 | 44550.2708 | 0 | 12.1522 | 37.78
2021-12-20 07:00 | 44550.2917 | 0 | 12.5815 | 37.78
2021-12-20 07:30 | 44550.3125 | 0 | 12.8725 | 37.78
2021-12-20 08:00 | 44550.3333 | 0 | 13.729 | 37.78
2021-12-20 08:30 | 44550.3542 | 0 | 13.6489 | 37.78
2021-12-20 09:00 | 44550.375 | 0 | 13.7982 | 37.78
2021-12-20 09:30 | 44550.3958 | 0 | 14.6386 | 37.78
2021-12-20 10:00 | 44550.4167 | 0 | 14.1538 | 37.78
2021-12-20 10:30 | 44550.4375 | 0 | 14.2975 | 37.78
2021-12-20 11:00 | 44550.4583 | 0 | 14.933 | 37.78
2021-12-20 11:30 | 44550.4792 | 0 | 15.4661 | 37.78
2021-12-20 12:00 | 44550.5 | 0 | 16.2393 | 37.78
2021-12-20 12:30 | 44550.5208 | 0 | 16.7349 | 37.78
2021-12-20 13:00 | 44550.5417 | 0 | 17.5484 | 37.78
2021-12-20 13:30 | 44550.5625 | 0 | 18.052 | 37.78
2021-12-20 14:00 | 44550.5833 | 0 | 18.969 | 37.78
2021-12-20 14:30 | 44550.6042 | 0 | 19.7172 | 37.78
2021-12-20 15:00 | 44550.625 | 0 | 20.5117 | 37.78
2021-12-20 15:30 | 44550.6458 | 0 | 21.3608 | 37.78
2021-12-20 16:00 | 44550.6667 | 0 | 21.0933 | 37.78
2021-12-20 16:30 | 44550.6875 | 0 | 21.7219 | 37.78
2021-12-20 17:00 | 44550.7083 | 0 | 21.7454 | 37.78
2021-12-20 17:30 | 44550.7292 | 0 | 21.7207 | 37.78
2021-12-20 18:00 | 44550.75 | 0 | 21.4974 | 37.78
2021-12-20 18:30 | 44550.7708 | 0 | 21.6129 | 37.78
2021-12-20 19:00 | 44550.7917 | 0 | 21.3929 | 37.78
2021-12-20 19:30 | 44550.8125 | 0 | 20.8585 | 37.78
2021-12-20 20:00 | 44550.8333 | 0 | 20.0562 | 37.78
2021-12-20 20:30 | 44550.8542 | 0 | 19.2398 | 37.78
2021-12-20 21:00 | 44550.875 | 0 | 18.3193 | 37.78
2021-12-20 21:30 | 44550.8958 | 0 | 17.4391 | 37.78
2021-12-20 22:00 | 44550.9167 | 0 | 16.4563 | 37.78
2021-12-20 22:30 | 44550.9375 | 0 | 15.3078 | 37.78
2021-12-20 23:00 | 44550.9583 | 0 | 14.3994 | 37.78
2021-12-20 23:30 | 44550.9792 | 0 | 13.7346 | 37.78
2021-12-21 | 44551 | 0 | 12.8604 | 37.78
2021-12-21 00:30 | 44551.0208 | 0 | 12.2303 | 37.78
2021-12-21 01:00 | 44551.0417 | 0 | 11.9149 | 37.78
2021-12-21 01:30 | 44551.0625 | 0 | 11.5873 | 37.78
2021-12-21 02:00 | 44551.0833 | 0 | 11.2518 | 37.78
2021-12-21 02:30 | 44551.1042 | 0 | 11.1211 | 37.78
2021-12-21 03:00 | 44551.125 | 0 | 10.7331 | 37.78
2021-12-21 03:30 | 44551.1458 | 0 | 10.7836 | 37.78
2021-12-21 04:00 | 44551.1667 | 0 | 10.9608 | 37.78
2021-12-21 04:30 | 44551.1875 | 0 | 11.286 | 37.78
2021-12-21 05:00 | 44551.2083 | 0 | 11.4478 | 37.78
2021-12-21 05:30 | 44551.2292 | 0 | 12.0757 | 37.78
2021-12-21 06:00 | 44551.25 | 0 | 12.5357 | 37.78
2021-12-21 06:30 | 44551.2708 | 0 | 12.9211 | 37.78
2021-12-21 07:00 | 44551.2917 | 0 | 13.2512 | 37.78
2021-12-21 07:30 | 44551.3125 | 0 | 14.614 | 37.78
2021-12-21 08:00 | 44551.3333 | 0 | 14.5587 | 37.78
2021-12-21 08:30 | 44551.3542 | 0 | 14.4229 | 37.78
2021-12-21 09:00 | 44551.375 | 0 | 14.4069 | 37.78
2021-12-21 09:30 | 44551.3958 | 0 | 14.9961 | 37.78
2021-12-21 10:00 | 44551.4167 | 0 | 15.1791 | 37.78
2021-12-21 10:30 | 44551.4375 | 0 | 16.7742 | 37.78
2021-12-21 11:00 | 44551.4583 | 0 | 17.1298 | 37.78
2021-12-21 11:30 | 44551.4792 | 0 | 16.067 | 37.78
2021-12-21 12:00 | 44551.5 | 0 | 16.7509 | 37.78
2021-12-21 12:30 | 44551.5208 | 0 | 18.7293 | 37.78
2021-12-21 13:00 | 44551.5417 | 0 | 18.4103 | 37.78
2021-12-21 13:30 | 44551.5625 | 0 | 17.7376 | 37.78
2021-12-21 14:00 | 44551.5833 | 0 | 18.8258 | 37.78
2021-12-21 14:30 | 44551.6042 | 0 | 19.3672 | 37.78
2021-12-21 15:00 | 44551.625 | 0 | 19.7525 | 37.78
2021-12-21 15:30 | 44551.6458 | 0 | 20.3111 | 37.78
2021-12-21 16:00 | 44551.6667 | 0 | 20.8235 | 37.78
2021-12-21 16:30 | 44551.6875 | 0 | 21.4644 | 37.78
2021-12-21 17:00 | 44551.7083 | 0 | 21.4981 | 37.78
2021-12-21 17:30 | 44551.7292 | 0 | 21.5721 | 37.78
2021-12-21 18:00 | 44551.75 | 0 | 21.2571 | 37.78
2021-12-21 18:30 | 44551.7708 | 0 | 21.0965 | 37.78
2021-12-21 19:00 | 44551.7917 | 0 | 20.6048 | 37.78
2021-12-21 19:30 | 44551.8125 | 0 | 20.5475 | 37.78
2021-12-21 20:00 | 44551.8333 | 0 | 19.7511 | 37.78
2021-12-21 20:30 | 44551.8542 | 0 | 19.0104 | 37.78
2021-12-21 21:00 | 44551.875 | 0 | 18.3273 | 37.78
2021-12-21 21:30 | 44551.8958 | 0 | 17.5287 | 37.78
2021-12-21 22:00 | 44551.9167 | 0 | 16.466 | 37.78
2021-12-21 22:30 | 44551.9375 | 0 | 15.1467 | 37.78
2021-12-21 23:00 | 44551.9583 | 0 | 14.3044 | 37.78
2021-12-21 23:30 | 44551.9792 | 0 | 13.5889 | 37.78
2021-12-22 | 44552 | 0 | 12.7808 | 37.78
2021-12-22 00:30 | 44552.0208 | 0 | 12.2236 | 37.78
2021-12-22 01:00 | 44552.0417 | 0 | 11.5808 | 37.78
2021-12-22 01:30 | 44552.0625 | 0 | 11.1839 | 37.78
2021-12-22 02:00 | 44552.0833 | 0 | 10.9481 | 37.78
2021-12-22 02:30 | 44552.1042 | 0 | 10.7181 | 37.78
2021-12-22 03:00 | 44552.125 | 0 | 10.519 | 37.78
2021-12-22 03:30 | 44552.1458 | 0 | 10.6302 | 37.78
2021-12-22 04:00 | 44552.1667 | 0 | 10.9624 | 37.78
2021-12-22 04:30 | 44552.1875 | 0 | 11.1485 | 37.78
2021-12-22 05:00 | 44552.2083 | 0 | 11.7422 | 37.78
2021-12-22 05:30 | 44552.2292 | 0 | 12.1047 | 37.78
2021-12-22 06:00 | 44552.25 | 0 | 12.7177 | 37.78
2021-12-22 06:30 | 44552.2708 | 0 | 13.2952 | 37.78
2021-12-22 07:00 | 44552.2917 | 0 | 13.8509 | 37.78
2021-12-22 07:30 | 44552.3125 | 0 | 13.8841 | 37.78
2021-12-22 08:00 | 44552.3333 | 0 | 14.2619 | 37.78
2021-12-22 08:30 | 44552.3542 | 0 | 14.5424 | 37.78
2021-12-22 09:00 | 44552.375 | 0 | 14.6925 | 37.78
2021-12-22 09:30 | 44552.3958 | 0 | 14.9647 | 37.78
2021-12-22 10:00 | 44552.4167 | 0 | 15.1316 | 37.78
2021-12-22 10:30 | 44552.4375 | 0 | 15.5697 | 37.78
2021-12-22 11:00 | 44552.4583 | 0 | 15.6579 | 37.78
2021-12-22 11:30 | 44552.4792 | 0 | 15.9299 | 37.78
2021-12-22 12:00 | 44552.5 | 0 | 15.8475 | 37.78
2021-12-22 12:30 | 44552.5208 | 0 | 16.1087 | 37.78
2021-12-22 13:00 | 44552.5417 | 0 | 16.9074 | 37.78
2021-12-22 13:30 | 44552.5625 | 0 | 17.4967 | 37.78
2021-12-22 14:00 | 44552.5833 | 0 | 17.9942 | 37.78
2021-12-22 14:30 | 44552.6042 | 0 | 18.5464 | 37.78
2021-12-22 15:00 | 44552.625 | 0 | 19.2218 | 37.78
2021-12-22 15:30 | 44552.6458 | 0 | 19.2743 | 37.78
2021-12-22 16:00 | 44552.6667 | 0 | 19.7026 | 37.78
2021-12-22 16:30 | 44552.6875 | 0 | 20.4974 | 37.78
2021-12-22 17:00 | 44552.7083 | 0 | 20.3218 | 37.78
2021-12-22 17:30 | 44552.7292 | 0 | 19.798 | 37.78
2021-12-22 18:00 | 44552.75 | 0 | 19.3448 | 37.78
2021-12-22 18:30 | 44552.7708 | 0 | 19.3879 | 37.78
2021-12-22 19:00 | 44552.7917 | 0 | 19.1498 | 37.78
2021-12-22 19:30 | 44552.8125 | 0 | 19.0649 | 37.78
2021-12-22 20:00 | 44552.8333 | 0 | 18.5536 | 37.78
2021-12-22 20:30 | 44552.8542 | 0 | 17.9098 | 37.78
2021-12-22 21:00 | 44552.875 | 0 | 17.3395 | 37.78
2021-12-22 21:30 | 44552.8958 | 0 | 16.4928 | 37.78
2021-12-22 22:00 | 44552.9167 | 0 | 15.6627 | 37.78
2021-12-22 22:30 | 44552.9375 | 0 | 14.4765 | 37.78
2021-12-22 23:00 | 44552.9583 | 0 | 13.846 | 37.78
2021-12-22 23:30 | 44552.9792 | 0 | 13.2137 | 37.78
2021-12-23 | 44553 | 0 | 12.3498 | 37.78
2021-12-23 00:30 | 44553.0208 | 0 | 11.7703 | 37.78
2021-12-23 01:00 | 44553.0417 | 0 | 11.3051 | 37.78
2021-12-23 01:30 | 44553.0625 | 0 | 10.8575 | 37.78
2021-12-23 02:00 | 44553.0833 | 0 | 10.7956 | 37.78
2021-12-23 02:30 | 44553.1042 | 0 | 10.6262 | 37.78
2021-12-23 03:00 | 44553.125 | 0 | 10.3814 | 37.78
2021-12-23 03:30 | 44553.1458 | 0 | 10.4506 | 37.78
2021-12-23 04:00 | 44553.1667 | 0 | 10.7453 | 37.78
2021-12-23 04:30 | 44553.1875 | 0 | 11.0422 | 37.78
2021-12-23 05:00 | 44553.2083 | 0 | 11.2996 | 37.78
2021-12-23 05:30 | 44553.2292 | 0 | 11.704 | 37.78
2021-12-23 06:00 | 44553.25 | 0 | 12.4168 | 37.78
2021-12-23 06:30 | 44553.2708 | 0 | 12.8743 | 37.78
2021-12-23 07:00 | 44553.2917 | 0 | 12.3429 | 37.78
2021-12-23 07:30 | 44553.3125 | 0 | 13.1234 | 37.78
2021-12-23 08:00 | 44553.3333 | 0 | 13.8704 | 37.78
2021-12-23 08:30 | 44553.3542 | 0 | 14.1599 | 37.78
2021-12-23 09:00 | 44553.375 | 0 | 15.098 | 37.78
2021-12-23 09:30 | 44553.3958 | 0 | 16.0759 | 37.78
2021-12-23 10:00 | 44553.4167 | 0 | 16.3433 | 37.78
2021-12-23 10:30 | 44553.4375 | 0 | 15.6575 | 37.78
2021-12-23 11:00 | 44553.4583 | 0 | 15.7139 | 37.78
2021-12-23 11:30 | 44553.4792 | 0 | 16.4118 | 37.78
2021-12-23 12:00 | 44553.5 | 0 | 15.9434 | 37.78
2021-12-23 12:30 | 44553.5208 | 0 | 16.5173 | 37.78
2021-12-23 13:00 | 44553.5417 | 0 | 17.0049 | 37.78
2021-12-23 13:30 | 44553.5625 | 0 | 17.1392 | 37.78
2021-12-23 14:00 | 44553.5833 | 0 | 20.2828 | 37.78
2021-12-23 14:30 | 44553.6042 | 0 | 21.0163 | 37.78
2021-12-23 15:00 | 44553.625 | 0 | 20.7961 | 37.78
2021-12-23 15:30 | 44553.6458 | 0 | 18.8936 | 37.78
2021-12-23 16:00 | 44553.6667 | 0 | 17.9413 | 37.78
2021-12-23 16:30 | 44553.6875 | 0 | 19.1659 | 37.78
2021-12-23 17:00 | 44553.7083 | 0 | 19.0661 | 37.78
2021-12-23 17:30 | 44553.7292 | 0 | 19.349 | 37.78
2021-12-23 18:00 | 44553.75 | 0 | 19.1507 | 37.78
2021-12-23 18:30 | 44553.7708 | 0 | 18.8333 | 37.78
2021-12-23 19:00 | 44553.7917 | 0 | 18.7904 | 37.78
2021-12-23 19:30 | 44553.8125 | 0 | 18.6367 | 37.78
2021-12-23 20:00 | 44553.8333 | 0 | 18.3189 | 37.78
2021-12-23 20:30 | 44553.8542 | 0 | 17.6339 | 37.78
2021-12-23 21:00 | 44553.875 | 0 | 17.0203 | 37.78
2021-12-23 21:30 | 44553.8958 | 0 | 16.653 | 37.78
2021-12-23 22:00 | 44553.9167 | 0 | 15.6256 | 37.78
2021-12-23 22:30 | 44553.9375 | 0 | 14.4412 | 37.78
2021-12-23 23:00 | 44553.9583 | 0 | 13.6905 | 37.78
2021-12-23 23:30 | 44553.9792 | 0 | 12.9882 | 37.78
2021-12-24 | 44554 | 0 | 12.3891 | 37.78
2021-12-24 00:30 | 44554.0208 | 0 | 11.9748 | 37.78
2021-12-24 01:00 | 44554.0417 | 0 | 11.6885 | 37.78
2021-12-24 01:30 | 44554.0625 | 0 | 11.4703 | 37.78
2021-12-24 02:00 | 44554.0833 | 0 | 11.1272 | 37.78
2021-12-24 02:30 | 44554.1042 | 0 | 11.0338 | 37.78
2021-12-24 03:00 | 44554.125 | 0 | 10.9257 | 37.78
2021-12-24 03:30 | 44554.1458 | 0 | 10.865 | 37.78
2021-12-24 04:00 | 44554.1667 | 0 | 10.8989 | 37.78
2021-12-24 04:30 | 44554.1875 | 0 | 11.1015 | 37.78
2021-12-24 05:00 | 44554.2083 | 0 | 11.1574 | 37.78
2021-12-24 05:30 | 44554.2292 | 0 | 11.1675 | 37.78
2021-12-24 06:00 | 44554.25 | 0 | 12.1625 | 37.78
2021-12-24 06:30 | 44554.2708 | 0 | 12.0043 | 37.78
2021-12-24 07:00 | 44554.2917 | 0 | 13.3125 | 37.78
2021-12-24 07:30 | 44554.3125 | 0 | 13.4832 | 37.78
2021-12-24 08:00 | 44554.3333 | 0 | 12.8234 | 37.78
2021-12-24 08:30 | 44554.3542 | 0 | 14.2812 | 37.78
2021-12-24 09:00 | 44554.375 | 0 | 13.9682 | 37.78
2021-12-24 09:30 | 44554.3958 | 0 | 14.2042 | 37.78
2021-12-24 10:00 | 44554.4167 | 0 | 15.505 | 37.78
2021-12-24 10:30 | 44554.4375 | 0 | 15.0572 | 37.78
2021-12-24 11:00 | 44554.4583 | 0 | 16.0017 | 37.78
2021-12-24 11:30 | 44554.4792 | 0 | 18.7789 | 37.78
2021-12-24 12:00 | 44554.5 | 0 | 18.307 | 37.78
2021-12-24 12:30 | 44554.5208 | 0 | 17.2533 | 37.78
2021-12-24 13:00 | 44554.5417 | 0 | 16.066 | 37.78
2021-12-24 13:30 | 44554.5625 | 0 | 18.6448 | 37.78
2021-12-24 14:00 | 44554.5833 | 0 | 18.4241 | 37.78
2021-12-24 14:30 | 44554.6042 | 0 | 18.9374 | 37.78
2021-12-24 15:00 | 44554.625 | 0 | 17.6234 | 37.78
2021-12-24 15:30 | 44554.6458 | 0 | 17.5125 | 37.78
2021-12-24 16:00 | 44554.6667 | 0 | 17.2441 | 37.78
2021-12-24 16:30 | 44554.6875 | 0 | 17.0672 | 37.78
2021-12-24 17:00 | 44554.7083 | 0 | 17.2828 | 37.78
2021-12-24 17:30 | 44554.7292 | 0 | 17.0836 | 37.78
2021-12-24 18:00 | 44554.75 | 0 | 16.7974 | 37.78
2021-12-24 18:30 | 44554.7708 | 0 | 16.9603 | 37.78
2021-12-24 19:00 | 44554.7917 | 0 | 16.8862 | 37.78
2021-12-24 19:30 | 44554.8125 | 0 | 16.493 | 37.78
2021-12-24 20:00 | 44554.8333 | 0 | 16.4029 | 37.78
2021-12-24 20:30 | 44554.8542 | 0 | 15.7625 | 37.78
2021-12-24 21:00 | 44554.875 | 0 | 15.4152 | 37.78
2021-12-24 21:30 | 44554.8958 | 0 | 15.163 | 37.78
2021-12-24 22:00 | 44554.9167 | 0 | 14.372 | 37.78
2021-12-24 22:30 | 44554.9375 | 0 | 13.3149 | 37.78
2021-12-24 23:00 | 44554.9583 | 0 | 12.8076 | 37.78
2021-12-24 23:30 | 44554.9792 | 0 | 12.2349 | 37.78
2021-12-25 | 44555 | 0 | 11.4571 | 37.78
2021-12-25 00:30 | 44555.0208 | 0 | 11.0212 | 37.78
2021-12-25 01:00 | 44555.0417 | 0 | 10.5675 | 37.78
2021-12-25 01:30 | 44555.0625 | 0 | 10.4103 | 37.78
2021-12-25 02:00 | 44555.0833 | 0 | 10.1882 | 37.78
2021-12-25 02:30 | 44555.1042 | 0 | 9.9607 | 37.78
2021-12-25 03:00 | 44555.125 | 0 | 9.6031 | 37.78
2021-12-25 03:30 | 44555.1458 | 0 | 9.6668 | 37.78
2021-12-25 04:00 | 44555.1667 | 0 | 9.6361 | 37.78
2021-12-25 04:30 | 44555.1875 | 0 | 9.6102 | 37.78
2021-12-25 05:00 | 44555.2083 | 0 | 9.439 | 37.78
2021-12-25 05:30 | 44555.2292 | 0 | 9.3863 | 37.78
2021-12-25 06:00 | 44555.25 | 0 | 9.4783 | 37.78
2021-12-25 06:30 | 44555.2708 | 0 | 9.4994 | 37.78
2021-12-25 07:00 | 44555.2917 | 0 | 9.3457 | 37.78
2021-12-25 07:30 | 44555.3125 | 0 | 10.3385 | 37.78
2021-12-25 08:00 | 44555.3333 | 0 | 10.4471 | 37.78
2021-12-25 08:30 | 44555.3542 | 0 | 10.5284 | 37.78
2021-12-25 09:00 | 44555.375 | 0 | 11.0033 | 37.78
2021-12-25 09:30 | 44555.3958 | 0 | 11.5538 | 37.78
2021-12-25 10:00 | 44555.4167 | 0 | 12.3221 | 37.78
2021-12-25 10:30 | 44555.4375 | 0 | 12.6706 | 37.78
2021-12-25 11:00 | 44555.4583 | 0 | 12.7125 | 37.78
2021-12-25 11:30 | 44555.4792 | 0 | 10.3077 | 37.78
2021-12-25 12:00 | 44555.5 | 0 | 12.5509 | 37.78
2021-12-25 12:30 | 44555.5208 | 0 | 13.1348 | 37.78
2021-12-25 13:00 | 44555.5417 | 0 | 12.8955 | 37.78
2021-12-25 13:30 | 44555.5625 | 0 | 12.9999 | 37.78
2021-12-25 14:00 | 44555.5833 | 0 | 13.9692 | 37.78
2021-12-25 14:30 | 44555.6042 | 0 | 13.6846 | 37.78
2021-12-25 15:00 | 44555.625 | 0 | 13.0433 | 37.78
2021-12-25 15:30 | 44555.6458 | 0 | 12.768 | 37.78
2021-12-25 16:00 | 44555.6667 | 0 | 12.5101 | 37.78
2021-12-25 16:30 | 44555.6875 | 0 | 12.4908 | 37.78
2021-12-25 17:00 | 44555.7083 | 0 | 12.3693 | 37.78
2021-12-25 17:30 | 44555.7292 | 0 | 12.0954 | 37.78
2021-12-25 18:00 | 44555.75 | 0 | 12.087 | 37.78
2021-12-25 18:30 | 44555.7708 | 0 | 12.4679 | 37.78
2021-12-25 19:00 | 44555.7917 | 0 | 12.4652 | 37.78
2021-12-25 19:30 | 44555.8125 | 0 | 12.2621 | 37.78
2021-12-25 20:00 | 44555.8333 | 0 | 12.1892 | 37.78
2021-12-25 20:30 | 44555.8542 | 0 | 11.9608 | 37.78
2021-12-25 21:00 | 44555.875 | 0 | 11.8331 | 37.78
2021-12-25 21:30 | 44555.8958 | 0 | 11.6225 | 37.78
2021-12-25 22:00 | 44555.9167 | 0 | 11.2248 | 37.78
2021-12-25 22:30 | 44555.9375 | 0 | 10.5414 | 37.78
2021-12-25 23:00 | 44555.9583 | 0 | 10.1837 | 37.78
2021-12-25 23:30 | 44555.9792 | 0 | 9.8659 | 37.78
2021-12-26 | 44556 | 0 | 9.3812 | 37.78
2021-12-26 00:30 | 44556.0208 | 0 | 9.1648 | 37.78
2021-12-26 01:00 | 44556.0417 | 0 | 8.874 | 37.78
2021-12-26 01:30 | 44556.0625 | 0 | 8.6663 | 37.78
2021-12-26 02:00 | 44556.0833 | 0 | 8.5382 | 37.78
2021-12-26 02:30 | 44556.1042 | 0 | 8.4563 | 37.78
2021-12-26 03:00 | 44556.125 | 0 | 8.3798 | 37.78
2021-12-26 03:30 | 44556.1458 | 0 | 8.1854 | 37.78
2021-12-26 04:00 | 44556.1667 | 0 | 8.2768 | 37.78
2021-12-26 04:30 | 44556.1875 | 0 | 8.0362 | 37.78
2021-12-26 05:00 | 44556.2083 | 0 | 8.1073 | 37.78
2021-12-26 05:30 | 44556.2292 | 0 | 8.2157 | 37.78
2021-12-26 06:00 | 44556.25 | 0 | 8.3134 | 37.78
2021-12-26 06:30 | 44556.2708 | 0 | 8.4691 | 37.78
2021-12-26 07:00 | 44556.2917 | 0 | 8.6526 | 37.78
2021-12-26 07:30 | 44556.3125 | 0 | 8.5033 | 37.78
2021-12-26 08:00 | 44556.3333 | 0 | 7.9794 | 37.78
2021-12-26 08:30 | 44556.3542 | 0 | 8.2195 | 37.78
2021-12-26 09:00 | 44556.375 | 0 | 8.4314 | 37.78
2021-12-26 09:30 | 44556.3958 | 0 | 9.5363 | 37.78
2021-12-26 10:00 | 44556.4167 | 0 | 8.1413 | 37.78
2021-12-26 10:30 | 44556.4375 | 0 | 8.8611 | 37.78
2021-12-26 11:00 | 44556.4583 | 0 | 9.919 | 37.78
2021-12-26 11:30 | 44556.4792 | 0 | 10.1272 | 37.78
2021-12-26 12:00 | 44556.5 | 0 | 10.1683 | 37.78
2021-12-26 12:30 | 44556.5208 | 0 | 8.5235 | 37.78
2021-12-26 13:00 | 44556.5417 | 0 | 8.6249 | 37.78
2021-12-26 13:30 | 44556.5625 | 0 | 9.4741 | 37.78
2021-12-26 14:00 | 44556.5833 | 0 | 10.0287 | 37.78
2021-12-26 14:30 | 44556.6042 | 0 | 10.4772 | 37.78
2021-12-26 15:00 | 44556.625 | 0 | 11.4486 | 37.78
2021-12-26 15:30 | 44556.6458 | 0 | 12.4372 | 37.78
2021-12-26 16:00 | 44556.6667 | 0 | 12.3586 | 37.78
2021-12-26 16:30 | 44556.6875 | 0 | 12.6816 | 37.78
2021-12-26 17:00 | 44556.7083 | 0 | 12.0601 | 37.78
2021-12-26 17:30 | 44556.7292 | 0 | 12.6313 | 37.78
2021-12-26 18:00 | 44556.75 | 0 | 12.6066 | 37.78
2021-12-26 18:30 | 44556.7708 | 0 | 13.0222 | 37.78
2021-12-26 19:00 | 44556.7917 | 0 | 13.1179 | 37.78
2021-12-26 19:30 | 44556.8125 | 0 | 13.0527 | 37.78
2021-12-26 20:00 | 44556.8333 | 0 | 13.1536 | 37.78
2021-12-26 20:30 | 44556.8542 | 0 | 12.579 | 37.78
2021-12-26 21:00 | 44556.875 | 0 | 12.2859 | 37.78
2021-12-26 21:30 | 44556.8958 | 0 | 11.8697 | 37.78
2021-12-26 22:00 | 44556.9167 | 0 | 11.646 | 37.78
2021-12-26 22:30 | 44556.9375 | 0 | 10.8756 | 37.78
2021-12-26 23:00 | 44556.9583 | 0 | 10.2965 | 37.78
2021-12-26 23:30 | 44556.9792 | 0 | 9.9815 | 37.78
2021-12-27 | 44557 | 0 | 9.5091 | 37.78
2021-12-27 00:30 | 44557.0208 | 0 | 9.2689 | 37.78
2021-12-27 01:00 | 44557.0417 | 0 | 9.0195 | 37.78
2021-12-27 01:30 | 44557.0625 | 0 | 8.8187 | 37.78
2021-12-27 02:00 | 44557.0833 | 0 | 8.7842 | 37.78
2021-12-27 02:30 | 44557.1042 | 0 | 8.551 | 37.78
2021-12-27 03:00 | 44557.125 | 0 | 8.4971 | 37.78
2021-12-27 03:30 | 44557.1458 | 0 | 8.6192 | 37.78
2021-12-27 04:00 | 44557.1667 | 0 | 8.555 | 37.78
2021-12-27 04:30 | 44557.1875 | 0 | 8.4298 | 37.78
2021-12-27 05:00 | 44557.2083 | 0 | 8.5751 | 37.78
2021-12-27 05:30 | 44557.2292 | 0 | 8.6168 | 37.78
2021-12-27 06:00 | 44557.25 | 0 | 8.6314 | 37.78
2021-12-27 06:30 | 44557.2708 | 0 | 8.9831 | 37.78
2021-12-27 07:00 | 44557.2917 | 0 | 8.5919 | 37.78
2021-12-27 07:30 | 44557.3125 | 0 | 8.2966 | 37.78
2021-12-27 08:00 | 44557.3333 | 0 | 9.2636 | 37.78
2021-12-27 08:30 | 44557.3542 | 0 | 9.3592 | 37.78
2021-12-27 09:00 | 44557.375 | 0 | 10.3801 | 37.78
2021-12-27 09:30 | 44557.3958 | 0 | 9.1034 | 37.78
2021-12-27 10:00 | 44557.4167 | 0 | 11.8752 | 37.78
2021-12-27 10:30 | 44557.4375 | 0 | 12.1184 | 37.78
2021-12-27 11:00 | 44557.4583 | 0 | 11.3787 | 37.78
2021-12-27 11:30 | 44557.4792 | 0 | 11.9311 | 37.78
2021-12-27 12:00 | 44557.5 | 0 | 13.0331 | 37.78
2021-12-27 12:30 | 44557.5208 | 0 | 12.506 | 37.78
2021-12-27 13:00 | 44557.5417 | 0 | 12.2847 | 37.78
2021-12-27 13:30 | 44557.5625 | 0 | 9.2344 | 37.78
2021-12-27 14:00 | 44557.5833 | 0 | 11.1581 | 37.78
2021-12-27 14:30 | 44557.6042 | 0 | 13.0413 | 37.78
2021-12-27 15:00 | 44557.625 | 0 | 12.6223 | 37.78
2021-12-27 15:30 | 44557.6458 | 0 | 11.924 | 37.78
2021-12-27 16:00 | 44557.6667 | 0 | 12.2846 | 37.78
2021-12-27 16:30 | 44557.6875 | 0 | 11.0762 | 37.78
2021-12-27 17:00 | 44557.7083 | 0 | 11.5657 | 37.78
2021-12-27 17:30 | 44557.7292 | 0 | 12.3114 | 37.78
2021-12-27 18:00 | 44557.75 | 0 | 12.687 | 37.78
2021-12-27 18:30 | 44557.7708 | 0 | 13.0372 | 37.78
2021-12-27 19:00 | 44557.7917 | 0 | 13.1188 | 37.78
2021-12-27 19:30 | 44557.8125 | 0 | 12.9604 | 37.78
2021-12-27 20:00 | 44557.8333 | 0 | 12.7278 | 37.78
2021-12-27 20:30 | 44557.8542 | 0 | 12.2194 | 37.78
2021-12-27 21:00 | 44557.875 | 0 | 11.9447 | 37.78
2021-12-27 21:30 | 44557.8958 | 0 | 11.5808 | 37.78
2021-12-27 22:00 | 44557.9167 | 0 | 11.1946 | 37.78
2021-12-27 22:30 | 44557.9375 | 0 | 10.4356 | 37.78
2021-12-27 23:00 | 44557.9583 | 0 | 10.0395 | 37.78
2021-12-27 23:30 | 44557.9792 | 0 | 9.5827 | 37.78
2021-12-28 | 44558 | 0 | 9.1802 | 37.78
2021-12-28 00:30 | 44558.0208 | 0 | 8.8611 | 37.78
2021-12-28 01:00 | 44558.0417 | 0 | 8.5287 | 37.78
2021-12-28 01:30 | 44558.0625 | 0 | 8.3518 | 37.78
2021-12-28 02:00 | 44558.0833 | 0 | 8.3134 | 37.78
2021-12-28 02:30 | 44558.1042 | 0 | 8.1806 | 37.78
2021-12-28 03:00 | 44558.125 | 0 | 8.1178 | 37.78
2021-12-28 03:30 | 44558.1458 | 0 | 8.2938 | 37.78
2021-12-28 04:00 | 44558.1667 | 0 | 8.0424 | 37.78
2021-12-28 04:30 | 44558.1875 | 0 | 8.3271 | 37.78
2021-12-28 05:00 | 44558.2083 | 0 | 8.3232 | 37.78
2021-12-28 05:30 | 44558.2292 | 0 | 8.4304 | 37.78
2021-12-28 06:00 | 44558.25 | 0 | 8.3024 | 37.78
2021-12-28 06:30 | 44558.2708 | 0 | 8.5343 | 37.78
2021-12-28 07:00 | 44558.2917 | 0 | 8.2526 | 37.78
2021-12-28 07:30 | 44558.3125 | 0 | 7.48 | 37.78
2021-12-28 08:00 | 44558.3333 | 0 | 7.6086 | 37.78
2021-12-28 08:30 | 44558.3542 | 0 | 9.2157 | 37.78
2021-12-28 09:00 | 44558.375 | 0 | 8.5477 | 37.78
2021-12-28 09:30 | 44558.3958 | 0 | 7.9632 | 37.78
2021-12-28 10:00 | 44558.4167 | 0 | 8.2781 | 37.78
2021-12-28 10:30 | 44558.4375 | 0 | 8.9176 | 37.78
2021-12-28 11:00 | 44558.4583 | 0 | 9.4896 | 37.78
2021-12-28 11:30 | 44558.4792 | 0 | 9.2866 | 37.78
2021-12-28 12:00 | 44558.5 | 0 | 7.9086 | 37.78
2021-12-28 12:30 | 44558.5208 | 0 | 7.6045 | 37.78
2021-12-28 13:00 | 44558.5417 | 0 | 7.3765 | 37.78
2021-12-28 13:30 | 44558.5625 | 0 | 7.8261 | 37.78
2021-12-28 14:00 | 44558.5833 | 0 | 8.5953 | 37.78
2021-12-28 14:30 | 44558.6042 | 0 | 8.6451 | 37.78
2021-12-28 15:00 | 44558.625 | 0 | 9.2279 | 37.78
2021-12-28 15:30 | 44558.6458 | 0 | 10.25 | 37.78
2021-12-28 16:00 | 44558.6667 | 0 | 10.4109 | 37.78
2021-12-28 16:30 | 44558.6875 | 0 | 10.0571 | 37.78
2021-12-28 17:00 | 44558.7083 | 0 | 10.085 | 37.78
2021-12-28 17:30 | 44558.7292 | 0 | 10.1624 | 37.78
2021-12-28 18:00 | 44558.75 | 0 | 11.0393 | 37.78
2021-12-28 18:30 | 44558.7708 | 0 | 11.7637 | 37.78
2021-12-28 19:00 | 44558.7917 | 0 | 11.8336 | 37.78
2021-12-28 19:30 | 44558.8125 | 0 | 11.4883 | 37.78
2021-12-28 20:00 | 44558.8333 | 0 | 11.3739 | 37.78
2021-12-28 20:30 | 44558.8542 | 0 | 10.9006 | 37.78
2021-12-28 21:00 | 44558.875 | 0 | 10.4576 | 37.78
2021-12-28 21:30 | 44558.8958 | 0 | 10.2138 | 37.78
2021-12-28 22:00 | 44558.9167 | 0 | 9.9719 | 37.78
2021-12-28 22:30 | 44558.9375 | 0 | 9.341 | 37.78
2021-12-28 23:00 | 44558.9583 | 0 | 9.0382 | 37.78
2021-12-28 23:30 | 44558.9792 | 0 | 8.5426 | 37.78
2021-12-29 | 44559 | 0 | 8.2023 | 37.78
2021-12-29 00:30 | 44559.0208 | 0 | 8.1344 | 37.78
2021-12-29 01:00 | 44559.0417 | 0 | 7.8996 | 37.78
2021-12-29 01:30 | 44559.0625 | 0 | 7.7426 | 37.78
2021-12-29 02:00 | 44559.0833 | 0 | 7.7932 | 37.78
2021-12-29 02:30 | 44559.1042 | 0 | 7.7488 | 37.78
2021-12-29 03:00 | 44559.125 | 0 | 7.8185 | 37.78
2021-12-29 03:30 | 44559.1458 | 0 | 7.9176 | 37.78
2021-12-29 04:00 | 44559.1667 | 0 | 8.0052 | 37.78
2021-12-29 04:30 | 44559.1875 | 0 | 8.3432 | 37.78
2021-12-29 05:00 | 44559.2083 | 0 | 8.62 | 37.78
2021-12-29 05:30 | 44559.2292 | 0 | 8.8559 | 37.78
2021-12-29 06:00 | 44559.25 | 0 | 9.0628 | 37.78
2021-12-29 06:30 | 44559.2708 | 0 | 9.3429 | 37.78
2021-12-29 07:00 | 44559.2917 | 0 | 9.4333 | 37.78
2021-12-29 07:30 | 44559.3125 | 0 | 9.1305 | 37.78
2021-12-29 08:00 | 44559.3333 | 0 | 10.0351 | 37.78
2021-12-29 08:30 | 44559.3542 | 0 | 10.596 | 37.78
2021-12-29 09:00 | 44559.375 | 0 | 10.3836 | 37.78
2021-12-29 09:30 | 44559.3958 | 0 | 10.1094 | 37.78
2021-12-29 10:00 | 44559.4167 | 0 | 10.7338 | 37.78
2021-12-29 10:30 | 44559.4375 | 0 | 9.6489 | 37.78
2021-12-29 11:00 | 44559.4583 | 0 | 8.6181 | 37.78
2021-12-29 11:30 | 44559.4792 | 0 | 9.4393 | 37.78
2021-12-29 12:00 | 44559.5 | 0 | 9.2079 | 37.78
2021-12-29 12:30 | 44559.5208 | 0 | 9.6256 | 37.78
2021-12-29 13:00 | 44559.5417 | 0 | 9.3268 | 37.78
2021-12-29 13:30 | 44559.5625 | 0 | 10.7179 | 37.78
2021-12-29 14:00 | 44559.5833 | 0 | 11.5987 | 37.78
2021-12-29 14:30 | 44559.6042 | 0 | 11.3372 | 37.78
2021-12-29 15:00 | 44559.625 | 0 | 11.3623 | 37.78
2021-12-29 15:30 | 44559.6458 | 0 | 11.5457 | 37.78
2021-12-29 16:00 | 44559.6667 | 0 | 11.8428 | 37.78
2021-12-29 16:30 | 44559.6875 | 0 | 12.6678 | 37.78
2021-12-29 17:00 | 44559.7083 | 0 | 12.9183 | 37.78
2021-12-29 17:30 | 44559.7292 | 0 | 12.8252 | 37.78
2021-12-29 18:00 | 44559.75 | 0 | 12.6459 | 37.78
2021-12-29 18:30 | 44559.7708 | 0 | 13.326 | 37.78
2021-12-29 19:00 | 44559.7917 | 0 | 13.1868 | 37.78
2021-12-29 19:30 | 44559.8125 | 0 | 12.908 | 37.78
2021-12-29 20:00 | 44559.8333 | 0 | 12.6239 | 37.78
2021-12-29 20:30 | 44559.8542 | 0 | 12.3558 | 37.78
2021-12-29 21:00 | 44559.875 | 0 | 11.9334 | 37.78
2021-12-29 21:30 | 44559.8958 | 0 | 11.5026 | 37.78
2021-12-29 22:00 | 44559.9167 | 0 | 11.1377 | 37.78
2021-12-29 22:30 | 44559.9375 | 0 | 10.4502 | 37.78
2021-12-29 23:00 | 44559.9583 | 0 | 10.2005 | 37.78
2021-12-29 23:30 | 44559.9792 | 0 | 9.9199 | 37.78
2021-12-30 | 44560 | 0 | 9.3188 | 37.78
2021-12-30 00:30 | 44560.0208 | 0 | 8.896 | 37.78
2021-12-30 01:00 | 44560.0417 | 0 | 8.6463 | 37.78
2021-12-30 01:30 | 44560.0625 | 0 | 8.4277 | 37.78
2021-12-30 02:00 | 44560.0833 | 0 | 8.3372 | 37.78
2021-12-30 02:30 | 44560.1042 | 0 | 8.1994 | 37.78
2021-12-30 03:00 | 44560.125 | 0 | 8.1374 | 37.78
2021-12-30 03:30 | 44560.1458 | 0 | 8.1818 | 37.78
2021-12-30 04:00 | 44560.1667 | 0 | 8.5577 | 37.78
2021-12-30 04:30 | 44560.1875 | 0 | 8.8908 | 37.78
2021-12-30 05:00 | 44560.2083 | 0 | 9.1488 | 37.78
2021-12-30 05:30 | 44560.2292 | 0 | 8.9916 | 37.78
2021-12-30 06:00 | 44560.25 | 0 | 9.0593 | 37.78
2021-12-30 06:30 | 44560.2708 | 0 | 9.0717 | 37.78
2021-12-30 07:00 | 44560.2917 | 0 | 9.0492 | 37.78
2021-12-30 07:30 | 44560.3125 | 0 | 10.4695 | 37.78
2021-12-30 08:00 | 44560.3333 | 0 | 10.6129 | 37.78
2021-12-30 08:30 | 44560.3542 | 0 | 9.9368 | 37.78
2021-12-30 09:00 | 44560.375 | 0 | 9.3642 | 37.78
2021-12-30 09:30 | 44560.3958 | 0 | 8.9856 | 37.78
2021-12-30 10:00 | 44560.4167 | 0 | 7.7983 | 37.78
2021-12-30 10:30 | 44560.4375 | 0 | 7.901 | 37.78
2021-12-30 11:00 | 44560.4583 | 0 | 8.7312 | 37.78
2021-12-30 11:30 | 44560.4792 | 0 | 9.3001 | 37.78
2021-12-30 12:00 | 44560.5 | 0 | 8.8915 | 37.78
2021-12-30 12:30 | 44560.5208 | 0 | 9.5225 | 37.78
2021-12-30 13:00 | 44560.5417 | 0 | 10.5513 | 37.78
2021-12-30 13:30 | 44560.5625 | 0 | 10.3889 | 37.78
2021-12-30 14:00 | 44560.5833 | 0 | 9.6511 | 37.78
2021-12-30 14:30 | 44560.6042 | 0 | 11.3367 | 37.78
2021-12-30 15:00 | 44560.625 | 0 | 11.2478 | 37.78
2021-12-30 15:30 | 44560.6458 | 0 | 12.3341 | 37.78
2021-12-30 16:00 | 44560.6667 | 0 | 11.8144 | 37.78
2021-12-30 16:30 | 44560.6875 | 0 | 12.6416 | 37.78
2021-12-30 17:00 | 44560.7083 | 0 | 12.7847 | 37.78
2021-12-30 17:30 | 44560.7292 | 0 | 13.0769 | 37.78
2021-12-30 18:00 | 44560.75 | 0 | 13.123 | 37.78
2021-12-30 18:30 | 44560.7708 | 0 | 13.5342 | 37.78
2021-12-30 19:00 | 44560.7917 | 0 | 13.5754 | 37.78
2021-12-30 19:30 | 44560.8125 | 0 | 13.3193 | 37.78
2021-12-30 20:00 | 44560.8333 | 0 | 13.0863 | 37.78
2021-12-30 20:30 | 44560.8542 | 0 | 12.6253 | 37.78
2021-12-30 21:00 | 44560.875 | 0 | 12.3142 | 37.78
2021-12-30 21:30 | 44560.8958 | 0 | 12.1149 | 37.78
2021-12-30 22:00 | 44560.9167 | 0 | 11.453 | 37.78
2021-12-30 22:30 | 44560.9375 | 0 | 10.7563 | 37.78
2021-12-30 23:00 | 44560.9583 | 0 | 10.4005 | 37.78
2021-12-30 23:30 | 44560.9792 | 0 | 9.9918 | 37.78
2021-12-31 | 44561 | 0 | 9.4681 | 37.78
2021-12-31 00:30 | 44561.0208 | 0 | 9.1419 | 37.78
2021-12-31 01:00 | 44561.0417 | 0 | 8.8547 | 37.78
2021-12-31 01:30 | 44561.0625 | 0 | 8.6383 | 37.78
2021-12-31 02:00 | 44561.0833 | 0 | 8.6293 | 37.78
2021-12-31 02:30 | 44561.1042 | 0 | 8.5981 | 37.78
2021-12-31 03:00 | 44561.125 | 0 | 8.5832 | 37.78
2021-12-31 03:30 | 44561.1458 | 0 | 8.6228 | 37.78
2021-12-31 04:00 | 44561.1667 | 0 | 8.7568 | 37.78
2021-12-31 04:30 | 44561.1875 | 0 | 8.9074 | 37.78
2021-12-31 05:00 | 44561.2083 | 0 | 9.1948 | 37.78
2021-12-31 05:30 | 44561.2292 | 0 | 9.1424 | 37.78
2021-12-31 06:00 | 44561.25 | 0 | 9.2293 | 37.78
2021-12-31 06:30 | 44561.2708 | 0 | 9.4723 | 37.78
2021-12-31 07:00 | 44561.2917 | 0 | 9.5699 | 37.78
2021-12-31 07:30 | 44561.3125 | 0 | 10.2106 | 37.78
2021-12-31 08:00 | 44561.3333 | 0 | 9.5705 | 37.78
2021-12-31 08:30 | 44561.3542 | 0 | 11.6712 | 37.78
2021-12-31 09:00 | 44561.375 | 0 | 11.9096 | 37.78
2021-12-31 09:30 | 44561.3958 | 0 | 11.6769 | 37.78
2021-12-31 10:00 | 44561.4167 | 0 | 10.981 | 37.78
2021-12-31 10:30 | 44561.4375 | 0 | 11.8466 | 37.78
2021-12-31 11:00 | 44561.4583 | 0 | 11.0598 | 37.78
2021-12-31 11:30 | 44561.4792 | 0 | 11.0735 | 37.78
2021-12-31 12:00 | 44561.5 | 0 | 12.2755 | 37.78
2021-12-31 12:30 | 44561.5208 | 0 | 11.7762 | 37.78
2021-12-31 13:00 | 44561.5417 | 0 | 11.3589 | 37.78
2021-12-31 13:30 | 44561.5625 | 0 | 10.997 | 37.78
2021-12-31 14:00 | 44561.5833 | 0 | 11.9325 | 37.78
2021-12-31 14:30 | 44561.6042 | 0 | 11.7422 | 37.78
2021-12-31 15:00 | 44561.625 | 0 | 12.4211 | 37.78
2021-12-31 15:30 | 44561.6458 | 0 | 11.7927 | 37.78
2021-12-31 16:00 | 44561.6667 | 0 | 12.405 | 37.78
2021-12-31 16:30 | 44561.6875 | 0 | 13.6431 | 37.78
2021-12-31 17:00 | 44561.7083 | 0 | 13.0884 | 37.78
2021-12-31 17:30 | 44561.7292 | 0 | 13.3711 | 37.78
2021-12-31 18:00 | 44561.75 | 0 | 13.1256 | 37.78
2021-12-31 18:30 | 44561.7708 | 0 | 13.4878 | 37.78
2021-12-31 19:00 | 44561.7917 | 0 | 13.3394 | 37.78
2021-12-31 19:30 | 44561.8125 | 0 | 13.092 | 37.78
2021-12-31 20:00 | 44561.8333 | 0 | 12.8819 | 37.78
2021-12-31 20:30 | 44561.8542 | 0 | 12.4277 | 37.78
2021-12-31 21:00 | 44561.875 | 0 | 12.0238 | 37.78
2021-12-31 21:30 | 44561.8958 | 0 | 11.9334 | 37.78
2021-12-31 22:00 | 44561.9167 | 0 | 11.5602 | 37.78
2021-12-31 22:30 | 44561.9375 | 0 | 11.1925 | 37.78
2021-12-31 23:00 | 44561.9583 | 0 | 10.9603 | 37.78
2021-12-31 23:30 | 44561.9792 | 0 | 10.5028 | 37.78
2022-01-01 | 44562 | 0 | 10.0354 | 37.78
2022-01-01 00:30 | 44562.0208 | 0 | 9.6662 | 37.78
2022-01-01 01:00 | 44562.0417 | 0 | 9.4846 | 37.78
2022-01-01 01:30 | 44562.0625 | 0 | 9.2759 | 37.78
2022-01-01 02:00 | 44562.0833 | 0 | 9.2856 | 37.78
2022-01-01 02:30 | 44562.1042 | 0 | 9.2359 | 37.78
2022-01-01 03:00 | 44562.125 | 0 | 9.0688 | 37.78
2022-01-01 03:30 | 44562.1458 | 0 | 9.0885 | 37.78
2022-01-01 04:00 | 44562.1667 | 0 | 8.9989 | 37.78
2022-01-01 04:30 | 44562.1875 | 0 | 8.8247 | 37.78
2022-01-01 05:00 | 44562.2083 | 0 | 9.0132 | 37.78
2022-01-01 05:30 | 44562.2292 | 0 | 8.7892 | 37.78
2022-01-01 06:00 | 44562.25 | 0 | 8.9658 | 37.78
2022-01-01 06:30 | 44562.2708 | 0 | 8.964 | 37.78
2022-01-01 07:00 | 44562.2917 | 0 | 8.5368 | 37.78
2022-01-01 07:30 | 44562.3125 | 0 | 8.8851 | 37.78
2022-01-01 08:00 | 44562.3333 | 0 | 9.2885 | 37.78
2022-01-01 08:30 | 44562.3542 | 0 | 9.0423 | 37.78
2022-01-01 09:00 | 44562.375 | 0 | 9.9046 | 37.78
2022-01-01 09:30 | 44562.3958 | 0 | 9.8648 | 37.78
2022-01-01 10:00 | 44562.4167 | 0 | 9.0254 | 37.78
2022-01-01 10:30 | 44562.4375 | 0 | 10.1441 | 37.78
2022-01-01 11:00 | 44562.4583 | 0 | 10.7369 | 37.78
2022-01-01 11:30 | 44562.4792 | 0 | 10.9775 | 37.78
2022-01-01 12:00 | 44562.5 | 0 | 9.3774 | 37.78
2022-01-01 12:30 | 44562.5208 | 0 | 9.3571 | 37.78
2022-01-01 13:00 | 44562.5417 | 0 | 8.9857 | 37.78
2022-01-01 13:30 | 44562.5625 | 0 | 9.201 | 37.78
2022-01-01 14:00 | 44562.5833 | 0 | 9.4381 | 37.78
2022-01-01 14:30 | 44562.6042 | 0 | 11.2825 | 37.78
2022-01-01 15:00 | 44562.625 | 0 | 10.9439 | 37.78
2022-01-01 15:30 | 44562.6458 | 0 | 10.4689 | 37.78
2022-01-01 16:00 | 44562.6667 | 0 | 9.7498 | 37.78
2022-01-01 16:30 | 44562.6875 | 0 | 9.8734 | 37.78
2022-01-01 17:00 | 44562.7083 | 0 | 10.5042 | 37.78
2022-01-01 17:30 | 44562.7292 | 0 | 11.1652 | 37.78
2022-01-01 18:00 | 44562.75 | 0 | 11.1505 | 37.78
2022-01-01 18:30 | 44562.7708 | 0 | 11.8981 | 37.78
2022-01-01 19:00 | 44562.7917 | 0 | 12.1148 | 37.78
2022-01-01 19:30 | 44562.8125 | 0 | 12.1149 | 37.78
2022-01-01 20:00 | 44562.8333 | 0 | 11.9215 | 37.78
2022-01-01 20:30 | 44562.8542 | 0 | 11.3952 | 37.78
2022-01-01 21:00 | 44562.875 | 0 | 11.1636 | 37.78
2022-01-01 21:30 | 44562.8958 | 0 | 10.8361 | 37.78
2022-01-01 22:00 | 44562.9167 | 0 | 10.3862 | 37.78
2022-01-01 22:30 | 44562.9375 | 0 | 9.8396 | 37.78
2022-01-01 23:00 | 44562.9583 | 0 | 9.4092 | 37.78
2022-01-01 23:30 | 44562.9792 | 0 | 8.9959 | 37.78
2022-01-02 | 44563 | 0 | 8.5944 | 37.78
2022-01-02 00:30 | 44563.0208 | 0 | 8.3054 | 37.78
2022-01-02 01:00 | 44563.0417 | 0 | 8.1157 | 37.78
2022-01-02 01:30 | 44563.0625 | 0 | 7.9013 | 37.78
2022-01-02 02:00 | 44563.0833 | 0 | 7.777 | 37.78
2022-01-02 02:30 | 44563.1042 | 0 | 7.6672 | 37.78
2022-01-02 03:00 | 44563.125 | 0 | 7.5818 | 37.78
2022-01-02 03:30 | 44563.1458 | 0 | 7.5785 | 37.78
2022-01-02 04:00 | 44563.1667 | 0 | 7.5315 | 37.78
2022-01-02 04:30 | 44563.1875 | 0 | 7.5112 | 37.78
2022-01-02 05:00 | 44563.2083 | 0 | 7.5431 | 37.78
2022-01-02 05:30 | 44563.2292 | 0 | 7.2794 | 37.78
2022-01-02 06:00 | 44563.25 | 0 | 7.3397 | 37.78
2022-01-02 06:30 | 44563.2708 | 0 | 6.9895 | 37.78
2022-01-02 07:00 | 44563.2917 | 0 | 6.6638 | 37.78
2022-01-02 07:30 | 44563.3125 | 0 | 6.489 | 37.78
2022-01-02 08:00 | 44563.3333 | 0 | 6.8877 | 37.78
2022-01-02 08:30 | 44563.3542 | 0 | 7.1143 | 37.78
2022-01-02 09:00 | 44563.375 | 0 | 8.1883 | 37.78
2022-01-02 09:30 | 44563.3958 | 0 | 7.9332 | 37.78
2022-01-02 10:00 | 44563.4167 | 0 | 8.2494 | 37.78
2022-01-02 10:30 | 44563.4375 | 0 | 9.5477 | 37.78
2022-01-02 11:00 | 44563.4583 | 0 | 8.5699 | 37.78
2022-01-02 11:30 | 44563.4792 | 0 | 9.4557 | 37.78
2022-01-02 12:00 | 44563.5 | 0 | 8.8315 | 37.78
2022-01-02 12:30 | 44563.5208 | 0 | 9.6613 | 37.78
2022-01-02 13:00 | 44563.5417 | 0 | 7.8723 | 37.78
2022-01-02 13:30 | 44563.5625 | 0 | 7.9522 | 37.78
2022-01-02 14:00 | 44563.5833 | 0 | 10.959 | 37.78
2022-01-02 14:30 | 44563.6042 | 0 | 9.3598 | 37.78
2022-01-02 15:00 | 44563.625 | 0 | 11.047 | 37.78
2022-01-02 15:30 | 44563.6458 | 0 | 10.9739 | 37.78
2022-01-02 16:00 | 44563.6667 | 0 | 10.2198 | 37.78
2022-01-02 16:30 | 44563.6875 | 0 | 10.8483 | 37.78
2022-01-02 17:00 | 44563.7083 | 0 | 10.902 | 37.78
2022-01-02 17:30 | 44563.7292 | 0 | 11.9628 | 37.78
2022-01-02 18:00 | 44563.75 | 0 | 12.1984 | 37.78
2022-01-02 18:30 | 44563.7708 | 0 | 12.6632 | 37.78
2022-01-02 19:00 | 44563.7917 | 0 | 12.8677 | 37.78
2022-01-02 19:30 | 44563.8125 | 0 | 12.6781 | 37.78
2022-01-02 20:00 | 44563.8333 | 0 | 12.4938 | 37.78
2022-01-02 20:30 | 44563.8542 | 0 | 11.7696 | 37.78
2022-01-02 21:00 | 44563.875 | 0 | 11.2057 | 37.78
2022-01-02 21:30 | 44563.8958 | 0 | 10.8117 | 37.78
2022-01-02 22:00 | 44563.9167 | 0 | 10.3655 | 37.78
2022-01-02 22:30 | 44563.9375 | 0 | 9.7859 | 37.78
2022-01-02 23:00 | 44563.9583 | 0 | 9.3101 | 37.78
2022-01-02 23:30 | 44563.9792 | 0 | 8.7794 | 37.78
2022-01-03 | 44564 | 0 | 8.5194 | 37.78
2022-01-03 00:30 | 44564.0208 | 0 | 8.2253 | 37.78
2022-01-03 01:00 | 44564.0417 | 0 | 8.0639 | 37.78
2022-01-03 01:30 | 44564.0625 | 0 | 7.9108 | 37.78
2022-01-03 02:00 | 44564.0833 | 0 | 7.8909 | 37.78
2022-01-03 02:30 | 44564.1042 | 0 | 7.9745 | 37.78
2022-01-03 03:00 | 44564.125 | 0 | 7.7445 | 37.78
2022-01-03 03:30 | 44564.1458 | 0 | 7.8283 | 37.78
2022-01-03 04:00 | 44564.1667 | 0 | 7.9224 | 37.78
2022-01-03 04:30 | 44564.1875 | 0 | 8.0365 | 37.78
2022-01-03 05:00 | 44564.2083 | 0 | 8.1135 | 37.78
2022-01-03 05:30 | 44564.2292 | 0 | 7.9775 | 37.78
2022-01-03 06:00 | 44564.25 | 0 | 7.9355 | 37.78
2022-01-03 06:30 | 44564.2708 | 0 | 7.8212 | 37.78
2022-01-03 07:00 | 44564.2917 | 0 | 7.7895 | 37.78
2022-01-03 07:30 | 44564.3125 | 0 | 7.5621 | 37.78
2022-01-03 08:00 | 44564.3333 | 0 | 7.8314 | 37.78
2022-01-03 08:30 | 44564.3542 | 0 | 8.0547 | 37.78
2022-01-03 09:00 | 44564.375 | 0 | 7.2483 | 37.78
2022-01-03 09:30 | 44564.3958 | 0 | 7.4197 | 37.78
2022-01-03 10:00 | 44564.4167 | 0 | 7.9124 | 37.78
2022-01-03 10:30 | 44564.4375 | 0 | 7.8391 | 37.78
2022-01-03 11:00 | 44564.4583 | 0 | 9.4987 | 37.78
2022-01-03 11:30 | 44564.4792 | 0 | 10.5186 | 37.78
2022-01-03 12:00 | 44564.5 | 0 | 10.4839 | 37.78
2022-01-03 12:30 | 44564.5208 | 0 | 11.6354 | 37.78
2022-01-03 13:00 | 44564.5417 | 0 | 11.6515 | 37.78
2022-01-03 13:30 | 44564.5625 | 0 | 10.9176 | 37.78
2022-01-03 14:00 | 44564.5833 | 0 | 9.162 | 37.78
2022-01-03 14:30 | 44564.6042 | 0 | 10.9505 | 37.78
2022-01-03 15:00 | 44564.625 | 0 | 10.1867 | 37.78
2022-01-03 15:30 | 44564.6458 | 0 | 12.0175 | 37.78
2022-01-03 16:00 | 44564.6667 | 0 | 11.6313 | 37.78
2022-01-03 16:30 | 44564.6875 | 0 | 12.3078 | 37.78
2022-01-03 17:00 | 44564.7083 | 0 | 13.3502 | 37.78
2022-01-03 17:30 | 44564.7292 | 0 | 14.258 | 37.78
2022-01-03 18:00 | 44564.75 | 0 | 14.6139 | 37.78
2022-01-03 18:30 | 44564.7708 | 0 | 15.1028 | 37.78
2022-01-03 19:00 | 44564.7917 | 0 | 15.2264 | 37.78
2022-01-03 19:30 | 44564.8125 | 0 | 15.1073 | 37.78
2022-01-03 20:00 | 44564.8333 | 0 | 14.9555 | 37.78
2022-01-03 20:30 | 44564.8542 | 0 | 13.889 | 37.78
2022-01-03 21:00 | 44564.875 | 0 | 13.5024 | 37.78
2022-01-03 21:30 | 44564.8958 | 0 | 12.9869 | 37.78
2022-01-03 22:00 | 44564.9167 | 0 | 12.394 | 37.78
2022-01-03 22:30 | 44564.9375 | 0 | 11.317 | 37.78
2022-01-03 23:00 | 44564.9583 | 0 | 10.9311 | 37.78
2022-01-03 23:30 | 44564.9792 | 0 | 10.3267 | 37.78
2022-01-04 | 44565 | 0 | 9.732 | 37.78
2022-01-04 00:30 | 44565.0208 | 0 | 9.4914 | 37.78
2022-01-04 01:00 | 44565.0417 | 0 | 9.1299 | 37.78
2022-01-04 01:30 | 44565.0625 | 0 | 9.0272 | 37.78
2022-01-04 02:00 | 44565.0833 | 0 | 8.9852 | 37.78
2022-01-04 02:30 | 44565.1042 | 0 | 8.853 | 37.78
2022-01-04 03:00 | 44565.125 | 0 | 8.7946 | 37.78
2022-01-04 03:30 | 44565.1458 | 0 | 8.7612 | 37.78
2022-01-04 04:00 | 44565.1667 | 0 | 9.1534 | 37.78
2022-01-04 04:30 | 44565.1875 | 0 | 9.4628 | 37.78
2022-01-04 05:00 | 44565.2083 | 0 | 9.9342 | 37.78
2022-01-04 05:30 | 44565.2292 | 0 | 10.2284 | 37.78
2022-01-04 06:00 | 44565.25 | 0 | 10.8647 | 37.78
2022-01-04 06:30 | 44565.2708 | 0 | 10.9366 | 37.78
2022-01-04 07:00 | 44565.2917 | 0 | 11.194 | 37.78
2022-01-04 07:30 | 44565.3125 | 0 | 11.2893 | 37.78
2022-01-04 08:00 | 44565.3333 | 0 | 11.199 | 37.78
2022-01-04 08:30 | 44565.3542 | 0 | 11.595 | 37.78
2022-01-04 09:00 | 44565.375 | 0 | 12.9674 | 37.78
2022-01-04 09:30 | 44565.3958 | 0 | 14.7328 | 37.78
2022-01-04 10:00 | 44565.4167 | 0 | 14.2645 | 37.78
2022-01-04 10:30 | 44565.4375 | 0 | 13.9196 | 37.78
2022-01-04 11:00 | 44565.4583 | 0 | 14.8987 | 37.78
2022-01-04 11:30 | 44565.4792 | 0 | 14.1717 | 37.78
2022-01-04 12:00 | 44565.5 | 0 | 14.6475 | 37.78
2022-01-04 12:30 | 44565.5208 | 0 | 13.37 | 37.78
2022-01-04 13:00 | 44565.5417 | 0 | 15.5458 | 37.78
2022-01-04 13:30 | 44565.5625 | 0 | 14.3897 | 37.78
2022-01-04 14:00 | 44565.5833 | 0 | 16.668 | 37.78
2022-01-04 14:30 | 44565.6042 | 0 | 15.1038 | 37.78
2022-01-04 15:00 | 44565.625 | 0 | 17.247 | 37.78
2022-01-04 15:30 | 44565.6458 | 0 | 17.8591 | 37.78
2022-01-04 16:00 | 44565.6667 | 0 | 16.9218 | 37.78
2022-01-04 16:30 | 44565.6875 | 0 | 17.3346 | 37.78
2022-01-04 17:00 | 44565.7083 | 0 | 17.8565 | 37.78
2022-01-04 17:30 | 44565.7292 | 0 | 18.5198 | 37.78
2022-01-04 18:00 | 44565.75 | 0 | 18.8124 | 37.78
2022-01-04 18:30 | 44565.7708 | 0 | 19.2425 | 37.78
2022-01-04 19:00 | 44565.7917 | 0 | 19.0792 | 37.78
2022-01-04 19:30 | 44565.8125 | 0 | 18.7499 | 37.78
2022-01-04 20:00 | 44565.8333 | 0 | 18.3439 | 37.78
2022-01-04 20:30 | 44565.8542 | 0 | 17.2056 | 37.78
2022-01-04 21:00 | 44565.875 | 0 | 16.3987 | 37.78
2022-01-04 21:30 | 44565.8958 | 0 | 15.7079 | 37.78
2022-01-04 22:00 | 44565.9167 | 0 | 14.7122 | 37.78
2022-01-04 22:30 | 44565.9375 | 0 | 13.6341 | 37.78
2022-01-04 23:00 | 44565.9583 | 0 | 12.7391 | 37.78
2022-01-04 23:30 | 44565.9792 | 0 | 12.0327 | 37.78
2022-01-05 | 44566 | 0 | 11.5013 | 37.78
2022-01-05 00:30 | 44566.0208 | 0 | 10.9219 | 37.78
2022-01-05 01:00 | 44566.0417 | 0 | 10.8161 | 37.78
2022-01-05 01:30 | 44566.0625 | 0 | 10.5079 | 37.78
2022-01-05 02:00 | 44566.0833 | 0 | 10.3991 | 37.78
2022-01-05 02:30 | 44566.1042 | 0 | 10.2444 | 37.78
2022-01-05 03:00 | 44566.125 | 0 | 10.0363 | 37.78
2022-01-05 03:30 | 44566.1458 | 0 | 9.8874 | 37.78
2022-01-05 04:00 | 44566.1667 | 0 | 10.1532 | 37.78
2022-01-05 04:30 | 44566.1875 | 0 | 10.5685 | 37.78
2022-01-05 05:00 | 44566.2083 | 0 | 10.8014 | 37.78
2022-01-05 05:30 | 44566.2292 | 0 | 11.1261 | 37.78
2022-01-05 06:00 | 44566.25 | 0 | 11.67 | 37.78
2022-01-05 06:30 | 44566.2708 | 0 | 12.0714 | 37.78
2022-01-05 07:00 | 44566.2917 | 0 | 12.4178 | 37.78
2022-01-05 07:30 | 44566.3125 | 0 | 13.1779 | 37.78
2022-01-05 08:00 | 44566.3333 | 0 | 13.7272 | 37.78
2022-01-05 08:30 | 44566.3542 | 0 | 12.7654 | 37.78
2022-01-05 09:00 | 44566.375 | 0 | 14.0539 | 37.78
2022-01-05 09:30 | 44566.3958 | 0 | 14.1199 | 37.78
2022-01-05 10:00 | 44566.4167 | 0 | 13.7827 | 37.78
2022-01-05 10:30 | 44566.4375 | 0 | 14.5514 | 37.78
2022-01-05 11:00 | 44566.4583 | 0 | 13.637 | 37.78
2022-01-05 11:30 | 44566.4792 | 0 | 15.5619 | 37.78
2022-01-05 12:00 | 44566.5 | 0 | 15.885 | 37.78
2022-01-05 12:30 | 44566.5208 | 0 | 15.6276 | 37.78
2022-01-05 13:00 | 44566.5417 | 0 | 16.954 | 37.78
2022-01-05 13:30 | 44566.5625 | 0 | 16.9085 | 37.78
2022-01-05 14:00 | 44566.5833 | 0 | 17.0646 | 37.78
2022-01-05 14:30 | 44566.6042 | 0 | 17.374 | 37.78
2022-01-05 15:00 | 44566.625 | 0 | 18.1183 | 37.78
2022-01-05 15:30 | 44566.6458 | 0 | 17.9881 | 37.78
2022-01-05 16:00 | 44566.6667 | 0 | 17.5178 | 37.78
2022-01-05 16:30 | 44566.6875 | 0 | 18.3014 | 37.78
2022-01-05 17:00 | 44566.7083 | 0 | 18.7071 | 37.78
2022-01-05 17:30 | 44566.7292 | 0 | 18.4434 | 37.78
2022-01-05 18:00 | 44566.75 | 0 | 18.7576 | 37.78
2022-01-05 18:30 | 44566.7708 | 0 | 18.8967 | 37.78
2022-01-05 19:00 | 44566.7917 | 0 | 18.6046 | 37.78
2022-01-05 19:30 | 44566.8125 | 0 | 18.3954 | 37.78
2022-01-05 20:00 | 44566.8333 | 0 | 17.9512 | 37.78
2022-01-05 20:30 | 44566.8542 | 0 | 17.1541 | 37.78
2022-01-05 21:00 | 44566.875 | 0 | 16.4876 | 37.78
2022-01-05 21:30 | 44566.8958 | 0 | 15.8993 | 37.78
2022-01-05 22:00 | 44566.9167 | 0 | 15.1206 | 37.78
2022-01-05 22:30 | 44566.9375 | 0 | 14.077 | 37.78
2022-01-05 23:00 | 44566.9583 | 0 | 13.1884 | 37.78
2022-01-05 23:30 | 44566.9792 | 0 | 12.6401 | 37.78
2022-01-06 | 44567 | 0 | 11.9024 | 37.78
2022-01-06 00:30 | 44567.0208 | 0 | 11.6699 | 37.78
2022-01-06 01:00 | 44567.0417 | 0 | 11.454 | 37.78
2022-01-06 01:30 | 44567.0625 | 0 | 11.2442 | 37.78
2022-01-06 02:00 | 44567.0833 | 0 | 10.8843 | 37.78
2022-01-06 02:30 | 44567.1042 | 0 | 10.7923 | 37.78
2022-01-06 03:00 | 44567.125 | 0 | 10.6775 | 37.78
2022-01-06 03:30 | 44567.1458 | 0 | 10.46 | 37.78
2022-01-06 04:00 | 44567.1667 | 0 | 10.8983 | 37.78
2022-01-06 04:30 | 44567.1875 | 0 | 11.2172 | 37.78
2022-01-06 05:00 | 44567.2083 | 0 | 11.6359 | 37.78
2022-01-06 05:30 | 44567.2292 | 0 | 11.8503 | 37.78
2022-01-06 06:00 | 44567.25 | 0 | 12.3577 | 37.78
2022-01-06 06:30 | 44567.2708 | 0 | 12.2626 | 37.78
2022-01-06 07:00 | 44567.2917 | 0 | 13.5294 | 37.78
2022-01-06 07:30 | 44567.3125 | 0 | 14.0507 | 37.78
2022-01-06 08:00 | 44567.3333 | 0 | 13.5361 | 37.78
2022-01-06 08:30 | 44567.3542 | 0 | 14.7254 | 37.78
2022-01-06 09:00 | 44567.375 | 0 | 15.9218 | 37.78
2022-01-06 09:30 | 44567.3958 | 0 | 15.3172 | 37.78
2022-01-06 10:00 | 44567.4167 | 0 | 14.847 | 37.78
2022-01-06 10:30 | 44567.4375 | 0 | 15.0096 | 37.78
2022-01-06 11:00 | 44567.4583 | 0 | 15.2392 | 37.78
2022-01-06 11:30 | 44567.4792 | 0 | 15.4333 | 37.78
2022-01-06 12:00 | 44567.5 | 0 | 15.5732 | 37.78
2022-01-06 12:30 | 44567.5208 | 0 | 17.5046 | 37.78
2022-01-06 13:00 | 44567.5417 | 0 | 18.3599 | 37.78
2022-01-06 13:30 | 44567.5625 | 0 | 16.3472 | 37.78
2022-01-06 14:00 | 44567.5833 | 0 | 16.088 | 37.78
2022-01-06 14:30 | 44567.6042 | 0 | 16.5294 | 37.78
2022-01-06 15:00 | 44567.625 | 0 | 16.3287 | 37.78
2022-01-06 15:30 | 44567.6458 | 0 | 16.5542 | 37.78
2022-01-06 16:00 | 44567.6667 | 0 | 17.2834 | 37.78
2022-01-06 16:30 | 44567.6875 | 0 | 17.7792 | 37.78
2022-01-06 17:00 | 44567.7083 | 0 | 17.7705 | 37.78
2022-01-06 17:30 | 44567.7292 | 0 | 17.9319 | 37.78
2022-01-06 18:00 | 44567.75 | 0 | 17.6065 | 37.78
2022-01-06 18:30 | 44567.7708 | 0 | 18.0987 | 37.78
2022-01-06 19:00 | 44567.7917 | 0 | 18.0778 | 37.78
2022-01-06 19:30 | 44567.8125 | 0 | 18.0996 | 37.78
2022-01-06 20:00 | 44567.8333 | 0 | 17.8057 | 37.78
2022-01-06 20:30 | 44567.8542 | 0 | 17.2631 | 37.78
2022-01-06 21:00 | 44567.875 | 0 | 16.5652 | 37.78
2022-01-06 21:30 | 44567.8958 | 0 | 15.9131 | 37.78
2022-01-06 22:00 | 44567.9167 | 0 | 15.1631 | 37.78
2022-01-06 22:30 | 44567.9375 | 0 | 14.1516 | 37.78
2022-01-06 23:00 | 44567.9583 | 0 | 13.4597 | 37.78
2022-01-06 23:30 | 44567.9792 | 0 | 12.8432 | 37.78
2022-01-07 | 44568 | 0 | 12.179 | 37.78
2022-01-07 00:30 | 44568.0208 | 0 | 11.8504 | 37.78
2022-01-07 01:00 | 44568.0417 | 0 | 11.5501 | 37.78
2022-01-07 01:30 | 44568.0625 | 0 | 11.3116 | 37.78
2022-01-07 02:00 | 44568.0833 | 0 | 11.1419 | 37.78
2022-01-07 02:30 | 44568.1042 | 0 | 11.1556 | 37.78
2022-01-07 03:00 | 44568.125 | 0 | 11.0395 | 37.78
2022-01-07 03:30 | 44568.1458 | 0 | 11.1913 | 37.78
2022-01-07 04:00 | 44568.1667 | 0 | 11.4898 | 37.78
2022-01-07 04:30 | 44568.1875 | 0 | 11.911 | 37.78
2022-01-07 05:00 | 44568.2083 | 0 | 12.1506 | 37.78
2022-01-07 05:30 | 44568.2292 | 0 | 12.4363 | 37.78
2022-01-07 06:00 | 44568.25 | 0 | 13.2042 | 37.78
2022-01-07 06:30 | 44568.2708 | 0 | 13.683 | 37.78
2022-01-07 07:00 | 44568.2917 | 0 | 13.9196 | 37.78
2022-01-07 07:30 | 44568.3125 | 0 | 13.7686 | 37.78
2022-01-07 08:00 | 44568.3333 | 0 | 14.8723 | 37.78
2022-01-07 08:30 | 44568.3542 | 0 | 15.6709 | 37.78
2022-01-07 09:00 | 44568.375 | 0 | 15.0144 | 37.78
2022-01-07 09:30 | 44568.3958 | 0 | 15.1098 | 37.78
2022-01-07 10:00 | 44568.4167 | 0 | 15.6043 | 37.78
2022-01-07 10:30 | 44568.4375 | 0 | 15.4424 | 37.78
2022-01-07 11:00 | 44568.4583 | 0 | 15.8931 | 37.78
2022-01-07 11:30 | 44568.4792 | 0 | 16.962 | 37.78
2022-01-07 12:00 | 44568.5 | 0 | 17.027 | 37.78
2022-01-07 12:30 | 44568.5208 | 0 | 17.9739 | 37.78
2022-01-07 13:00 | 44568.5417 | 0 | 17.5278 | 37.78
2022-01-07 13:30 | 44568.5625 | 0 | 16.9738 | 37.78
2022-01-07 14:00 | 44568.5833 | 0 | 16.8343 | 37.78
2022-01-07 14:30 | 44568.6042 | 0 | 17.1181 | 37.78
2022-01-07 15:00 | 44568.625 | 0 | 17.0872 | 37.78
2022-01-07 15:30 | 44568.6458 | 0 | 16.8433 | 37.78
2022-01-07 16:00 | 44568.6667 | 0 | 16.414 | 37.78
2022-01-07 16:30 | 44568.6875 | 0 | 16.5762 | 37.78
2022-01-07 17:00 | 44568.7083 | 0 | 16.3746 | 37.78
2022-01-07 17:30 | 44568.7292 | 0 | 16.6795 | 37.78
2022-01-07 18:00 | 44568.75 | 0 | 16.7066 | 37.78
2022-01-07 18:30 | 44568.7708 | 0 | 17.0295 | 37.78
2022-01-07 19:00 | 44568.7917 | 0 | 16.963 | 37.78
2022-01-07 19:30 | 44568.8125 | 0 | 16.8299 | 37.78
2022-01-07 20:00 | 44568.8333 | 0 | 16.5601 | 37.78
2022-01-07 20:30 | 44568.8542 | 0 | 15.9753 | 37.78
2022-01-07 21:00 | 44568.875 | 0 | 15.5775 | 37.78
2022-01-07 21:30 | 44568.8958 | 0 | 15.1893 | 37.78
2022-01-07 22:00 | 44568.9167 | 0 | 14.5007 | 37.78
2022-01-07 22:30 | 44568.9375 | 0 | 13.6266 | 37.78
2022-01-07 23:00 | 44568.9583 | 0 | 13.0841 | 37.78
2022-01-07 23:30 | 44568.9792 | 0 | 12.5795 | 37.78
2022-01-08 | 44569 | 0 | 11.772 | 37.78
2022-01-08 00:30 | 44569.0208 | 0 | 11.4138 | 37.78
2022-01-08 01:00 | 44569.0417 | 0 | 11.0092 | 37.78
2022-01-08 01:30 | 44569.0625 | 0 | 10.6443 | 37.78
2022-01-08 02:00 | 44569.0833 | 0 | 10.4826 | 37.78
2022-01-08 02:30 | 44569.1042 | 0 | 10.4669 | 37.78
2022-01-08 03:00 | 44569.125 | 0 | 10.4517 | 37.78
2022-01-08 03:30 | 44569.1458 | 0 | 10.3734 | 37.78
2022-01-08 04:00 | 44569.1667 | 0 | 10.5005 | 37.78
2022-01-08 04:30 | 44569.1875 | 0 | 10.5931 | 37.78
2022-01-08 05:00 | 44569.2083 | 0 | 10.6062 | 37.78
2022-01-08 05:30 | 44569.2292 | 0 | 10.4401 | 37.78
2022-01-08 06:00 | 44569.25 | 0 | 10.7509 | 37.78
2022-01-08 06:30 | 44569.2708 | 0 | 11.1109 | 37.78
2022-01-08 07:00 | 44569.2917 | 0 | 11.6005 | 37.78
2022-01-08 07:30 | 44569.3125 | 0 | 11.8908 | 37.78
2022-01-08 08:00 | 44569.3333 | 0 | 12.5185 | 37.78
2022-01-08 08:30 | 44569.3542 | 0 | 12.8111 | 37.78
2022-01-08 09:00 | 44569.375 | 0 | 12.9083 | 37.78
2022-01-08 09:30 | 44569.3958 | 0 | 13.0771 | 37.78
2022-01-08 10:00 | 44569.4167 | 0 | 12.5888 | 37.78
2022-01-08 10:30 | 44569.4375 | 0 | 12.9887 | 37.78
2022-01-08 11:00 | 44569.4583 | 0 | 12.4434 | 37.78
2022-01-08 11:30 | 44569.4792 | 0 | 13.9382 | 37.78
2022-01-08 12:00 | 44569.5 | 0 | 14.0546 | 37.78
2022-01-08 12:30 | 44569.5208 | 0 | 13.2775 | 37.78
2022-01-08 13:00 | 44569.5417 | 0 | 12.796 | 37.78
2022-01-08 13:30 | 44569.5625 | 0 | 13.6056 | 37.78
2022-01-08 14:00 | 44569.5833 | 0 | 13.6417 | 37.78
2022-01-08 14:30 | 44569.6042 | 0 | 14.2258 | 37.78
2022-01-08 15:00 | 44569.625 | 0 | 13.9457 | 37.78
2022-01-08 15:30 | 44569.6458 | 0 | 14.1047 | 37.78
2022-01-08 16:00 | 44569.6667 | 0 | 14.5564 | 37.78
2022-01-08 16:30 | 44569.6875 | 0 | 14.4582 | 37.78
2022-01-08 17:00 | 44569.7083 | 0 | 14.5365 | 37.78
2022-01-08 17:30 | 44569.7292 | 0 | 14.2703 | 37.78
2022-01-08 18:00 | 44569.75 | 0 | 14.5886 | 37.78
2022-01-08 18:30 | 44569.7708 | 0 | 14.9556 | 37.78
2022-01-08 19:00 | 44569.7917 | 0 | 15.1001 | 37.78
2022-01-08 19:30 | 44569.8125 | 0 | 15.2556 | 37.78
2022-01-08 20:00 | 44569.8333 | 0 | 14.979 | 37.78
2022-01-08 20:30 | 44569.8542 | 0 | 14.4496 | 37.78
2022-01-08 21:00 | 44569.875 | 0 | 13.9446 | 37.78
2022-01-08 21:30 | 44569.8958 | 0 | 13.5619 | 37.78
2022-01-08 22:00 | 44569.9167 | 0 | 13.0442 | 37.78
2022-01-08 22:30 | 44569.9375 | 0 | 12.2342 | 37.78
2022-01-08 23:00 | 44569.9583 | 0 | 11.8299 | 37.78
2022-01-08 23:30 | 44569.9792 | 0 | 11.2318 | 37.78
2022-01-09 | 44570 | 0 | 10.5624 | 37.78
2022-01-09 00:30 | 44570.0208 | 0 | 10.1652 | 37.78
2022-01-09 01:00 | 44570.0417 | 0 | 9.8103 | 37.78
2022-01-09 01:30 | 44570.0625 | 0 | 9.6227 | 37.78
2022-01-09 02:00 | 44570.0833 | 0 | 9.4488 | 37.78
2022-01-09 02:30 | 44570.1042 | 0 | 9.4366 | 37.78
2022-01-09 03:00 | 44570.125 | 0 | 9.3389 | 37.78
2022-01-09 03:30 | 44570.1458 | 0 | 9.2324 | 37.78
2022-01-09 04:00 | 44570.1667 | 0 | 9.1558 | 37.78
2022-01-09 04:30 | 44570.1875 | 0 | 9.0419 | 37.78
2022-01-09 05:00 | 44570.2083 | 0 | 9.0566 | 37.78
2022-01-09 05:30 | 44570.2292 | 0 | 9.0742 | 37.78
2022-01-09 06:00 | 44570.25 | 0 | 9.2625 | 37.78
2022-01-09 06:30 | 44570.2708 | 0 | 9.3067 | 37.78
2022-01-09 07:00 | 44570.2917 | 0 | 9.3163 | 37.78
2022-01-09 07:30 | 44570.3125 | 0 | 10.6707 | 37.78
2022-01-09 08:00 | 44570.3333 | 0 | 11.3696 | 37.78
2022-01-09 08:30 | 44570.3542 | 0 | 11.1869 | 37.78
2022-01-09 09:00 | 44570.375 | 0 | 10.8707 | 37.78
2022-01-09 09:30 | 44570.3958 | 0 | 11.3556 | 37.78
2022-01-09 10:00 | 44570.4167 | 0 | 12.1848 | 37.78
2022-01-09 10:30 | 44570.4375 | 0 | 12.3873 | 37.78
2022-01-09 11:00 | 44570.4583 | 0 | 10.5236 | 37.78
2022-01-09 11:30 | 44570.4792 | 0 | 10.7782 | 37.78
2022-01-09 12:00 | 44570.5 | 0 | 11.163 | 37.78
2022-01-09 12:30 | 44570.5208 | 0 | 11.4497 | 37.78
2022-01-09 13:00 | 44570.5417 | 0 | 12 | 37.78
2022-01-09 13:30 | 44570.5625 | 0 | 13.452 | 37.78
2022-01-09 14:00 | 44570.5833 | 0 | 14.9132 | 37.78
2022-01-09 14:30 | 44570.6042 | 0 | 14.0877 | 37.78
2022-01-09 15:00 | 44570.625 | 0 | 14.3407 | 37.78
2022-01-09 15:30 | 44570.6458 | 0 | 15.5199 | 37.78
2022-01-09 16:00 | 44570.6667 | 0 | 14.6034 | 37.78
2022-01-09 16:30 | 44570.6875 | 0 | 14.6769 | 37.78
2022-01-09 17:00 | 44570.7083 | 0 | 15.614 | 37.78
2022-01-09 17:30 | 44570.7292 | 0 | 15.7931 | 37.78
2022-01-09 18:00 | 44570.75 | 0 | 16.1511 | 37.78
2022-01-09 18:30 | 44570.7708 | 0 | 16.6527 | 37.78
2022-01-09 19:00 | 44570.7917 | 0 | 16.6259 | 37.78
2022-01-09 19:30 | 44570.8125 | 0 | 16.2368 | 37.78
2022-01-09 20:00 | 44570.8333 | 0 | 15.7972 | 37.78
2022-01-09 20:30 | 44570.8542 | 0 | 15.3321 | 37.78
2022-01-09 21:00 | 44570.875 | 0 | 14.6528 | 37.78
2022-01-09 21:30 | 44570.8958 | 0 | 13.9418 | 37.78
2022-01-09 22:00 | 44570.9167 | 0 | 12.9637 | 37.78
2022-01-09 22:30 | 44570.9375 | 0 | 12.2361 | 37.78
2022-01-09 23:00 | 44570.9583 | 0 | 11.4796 | 37.78
2022-01-09 23:30 | 44570.9792 | 0 | 10.715 | 37.78
2022-01-10 | 44571 | 0 | 10.3178 | 37.78
2022-01-10 00:30 | 44571.0208 | 0 | 9.8523 | 37.78
2022-01-10 01:00 | 44571.0417 | 0 | 9.559 | 37.78
2022-01-10 01:30 | 44571.0625 | 0 | 9.3068 | 37.78
2022-01-10 02:00 | 44571.0833 | 0 | 9.288 | 37.78
2022-01-10 02:30 | 44571.1042 | 0 | 9.2869 | 37.78
2022-01-10 03:00 | 44571.125 | 0 | 9.0691 | 37.78
2022-01-10 03:30 | 44571.1458 | 0 | 9.1847 | 37.78
2022-01-10 04:00 | 44571.1667 | 0 | 9.5396 | 37.78
2022-01-10 04:30 | 44571.1875 | 0 | 9.9026 | 37.78
2022-01-10 05:00 | 44571.2083 | 0 | 10.4002 | 37.78
2022-01-10 05:30 | 44571.2292 | 0 | 10.7099 | 37.78
2022-01-10 06:00 | 44571.25 | 0 | 11.5478 | 37.78
2022-01-10 06:30 | 44571.2708 | 0 | 11.7461 | 37.78
2022-01-10 07:00 | 44571.2917 | 0 | 12.4797 | 37.78
2022-01-10 07:30 | 44571.3125 | 0 | 13.4488 | 37.78
2022-01-10 08:00 | 44571.3333 | 0 | 13.9347 | 37.78
2022-01-10 08:30 | 44571.3542 | 0 | 14.1305 | 37.78
2022-01-10 09:00 | 44571.375 | 0 | 13.9447 | 37.78
2022-01-10 09:30 | 44571.3958 | 0 | 15.2129 | 37.78
2022-01-10 10:00 | 44571.4167 | 0 | 14.3878 | 37.78
2022-01-10 10:30 | 44571.4375 | 0 | 13.0506 | 37.78
2022-01-10 11:00 | 44571.4583 | 0 | 14.0416 | 37.78
2022-01-10 11:30 | 44571.4792 | 0 | 14.3951 | 37.78
2022-01-10 12:00 | 44571.5 | 0 | 15.5491 | 37.78
2022-01-10 12:30 | 44571.5208 | 0 | 14.5825 | 37.78
2022-01-10 13:00 | 44571.5417 | 0 | 14.6994 | 37.78
2022-01-10 13:30 | 44571.5625 | 0 | 15.512 | 37.78
2022-01-10 14:00 | 44571.5833 | 0 | 15.9076 | 37.78
2022-01-10 14:30 | 44571.6042 | 0 | 16.2301 | 37.78
2022-01-10 15:00 | 44571.625 | 0 | 17.4038 | 37.78
2022-01-10 15:30 | 44571.6458 | 0 | 16.943 | 37.78
2022-01-10 16:00 | 44571.6667 | 0 | 17.3263 | 37.78
2022-01-10 16:30 | 44571.6875 | 0 | 18.1501 | 37.78
2022-01-10 17:00 | 44571.7083 | 0 | 18.3023 | 37.78
2022-01-10 17:30 | 44571.7292 | 0 | 18.4353 | 37.78
2022-01-10 18:00 | 44571.75 | 0 | 18.6653 | 37.78
2022-01-10 18:30 | 44571.7708 | 0 | 18.7038 | 37.78
2022-01-10 19:00 | 44571.7917 | 0 | 18.5144 | 37.78
2022-01-10 19:30 | 44571.8125 | 0 | 18.4536 | 37.78
2022-01-10 20:00 | 44571.8333 | 0 | 18.0042 | 37.78
2022-01-10 20:30 | 44571.8542 | 0 | 17.1869 | 37.78
2022-01-10 21:00 | 44571.875 | 0 | 16.5204 | 37.78
2022-01-10 21:30 | 44571.8958 | 0 | 15.7898 | 37.78
2022-01-10 22:00 | 44571.9167 | 0 | 14.9976 | 37.78
2022-01-10 22:30 | 44571.9375 | 0 | 13.9941 | 37.78
2022-01-10 23:00 | 44571.9583 | 0 | 13.2564 | 37.78
2022-01-10 23:30 | 44571.9792 | 0 | 12.4161 | 37.78
2022-01-11 | 44572 | 0 | 11.6034 | 37.78
2022-01-11 00:30 | 44572.0208 | 0 | 11.0162 | 37.78
2022-01-11 01:00 | 44572.0417 | 0 | 10.7715 | 37.78
2022-01-11 01:30 | 44572.0625 | 0 | 10.4642 | 37.78
2022-01-11 02:00 | 44572.0833 | 0 | 10.1789 | 37.78
2022-01-11 02:30 | 44572.1042 | 0 | 10.117 | 37.78
2022-01-11 03:00 | 44572.125 | 0 | 10.0327 | 37.78
2022-01-11 03:30 | 44572.1458 | 0 | 9.9193 | 37.78
2022-01-11 04:00 | 44572.1667 | 0 | 10.0991 | 37.78
2022-01-11 04:30 | 44572.1875 | 0 | 10.5191 | 37.78
2022-01-11 05:00 | 44572.2083 | 0 | 10.8907 | 37.78
2022-01-11 05:30 | 44572.2292 | 0 | 11.2816 | 37.78
2022-01-11 06:00 | 44572.25 | 0 | 11.9187 | 37.78
2022-01-11 06:30 | 44572.2708 | 0 | 12.3206 | 37.78
2022-01-11 07:00 | 44572.2917 | 0 | 13.4363 | 37.78
2022-01-11 07:30 | 44572.3125 | 0 | 12.3544 | 37.78
2022-01-11 08:00 | 44572.3333 | 0 | 13.0689 | 37.78
2022-01-11 08:30 | 44572.3542 | 0 | 14.0012 | 37.78
2022-01-11 09:00 | 44572.375 | 0 | 15.5318 | 37.78
2022-01-11 09:30 | 44572.3958 | 0 | 14.5686 | 37.78
2022-01-11 10:00 | 44572.4167 | 0 | 14.9712 | 37.78
2022-01-11 10:30 | 44572.4375 | 0 | 14.6763 | 37.78
2022-01-11 11:00 | 44572.4583 | 0 | 13.625 | 37.78
2022-01-11 11:30 | 44572.4792 | 0 | 13.2469 | 37.78
2022-01-11 12:00 | 44572.5 | 0 | 15.1749 | 37.78
2022-01-11 12:30 | 44572.5208 | 0 | 14.632 | 37.78
2022-01-11 13:00 | 44572.5417 | 0 | 14.9668 | 37.78
2022-01-11 13:30 | 44572.5625 | 0 | 14.18 | 37.78
2022-01-11 14:00 | 44572.5833 | 0 | 15.5396 | 37.78
2022-01-11 14:30 | 44572.6042 | 0 | 16.0152 | 37.78
2022-01-11 15:00 | 44572.625 | 0 | 15.8555 | 37.78
2022-01-11 15:30 | 44572.6458 | 0 | 16.156 | 37.78
2022-01-11 16:00 | 44572.6667 | 0 | 16.3754 | 37.78
2022-01-11 16:30 | 44572.6875 | 0 | 17.2402 | 37.78
2022-01-11 17:00 | 44572.7083 | 0 | 17.1452 | 37.78
2022-01-11 17:30 | 44572.7292 | 0 | 17.1857 | 37.78
2022-01-11 18:00 | 44572.75 | 0 | 16.8061 | 37.78
2022-01-11 18:30 | 44572.7708 | 0 | 16.8126 | 37.78
2022-01-11 19:00 | 44572.7917 | 0 | 16.8406 | 37.78
2022-01-11 19:30 | 44572.8125 | 0 | 16.4923 | 37.78
2022-01-11 20:00 | 44572.8333 | 0 | 16.0386 | 37.78
2022-01-11 20:30 | 44572.8542 | 0 | 15.343 | 37.78
2022-01-11 21:00 | 44572.875 | 0 | 14.9061 | 37.78
2022-01-11 21:30 | 44572.8958 | 0 | 14.256 | 37.78
2022-01-11 22:00 | 44572.9167 | 0 | 13.5619 | 37.78
2022-01-11 22:30 | 44572.9375 | 0 | 12.6419 | 37.78
2022-01-11 23:00 | 44572.9583 | 0 | 11.7927 | 37.78
2022-01-11 23:30 | 44572.9792 | 0 | 11.1845 | 37.78
2022-01-12 | 44573 | 0 | 10.5465 | 37.78
2022-01-12 00:30 | 44573.0208 | 0 | 9.9779 | 37.78
2022-01-12 01:00 | 44573.0417 | 0 | 9.7671 | 37.78
2022-01-12 01:30 | 44573.0625 | 0 | 9.4738 | 37.78
2022-01-12 02:00 | 44573.0833 | 0 | 9.3556 | 37.78
2022-01-12 02:30 | 44573.1042 | 0 | 9.2849 | 37.78
2022-01-12 03:00 | 44573.125 | 0 | 9.2404 | 37.78
2022-01-12 03:30 | 44573.1458 | 0 | 9.2386 | 37.78
2022-01-12 04:00 | 44573.1667 | 0 | 9.456 | 37.78
2022-01-12 04:30 | 44573.1875 | 0 | 9.8075 | 37.78
2022-01-12 05:00 | 44573.2083 | 0 | 10.282 | 37.78
2022-01-12 05:30 | 44573.2292 | 0 | 10.7372 | 37.78
2022-01-12 06:00 | 44573.25 | 0 | 11.1711 | 37.78
2022-01-12 06:30 | 44573.2708 | 0 | 11.1318 | 37.78
2022-01-12 07:00 | 44573.2917 | 0 | 11.5975 | 37.78
2022-01-12 07:30 | 44573.3125 | 0 | 12.4477 | 37.78
2022-01-12 08:00 | 44573.3333 | 0 | 13.3126 | 37.78
2022-01-12 08:30 | 44573.3542 | 0 | 12.0677 | 37.78
2022-01-12 09:00 | 44573.375 | 0 | 13.4605 | 37.78
2022-01-12 09:30 | 44573.3958 | 0 | 14.4047 | 37.78
2022-01-12 10:00 | 44573.4167 | 0 | 14.1008 | 37.78
2022-01-12 10:30 | 44573.4375 | 0 | 12.9124 | 37.78
2022-01-12 11:00 | 44573.4583 | 0 | 12.0463 | 37.78
2022-01-12 11:30 | 44573.4792 | 0 | 13.1182 | 37.78
2022-01-12 12:00 | 44573.5 | 0 | 14.6357 | 37.78
2022-01-12 12:30 | 44573.5208 | 0 | 14.1035 | 37.78
2022-01-12 13:00 | 44573.5417 | 0 | 14.1122 | 37.78
2022-01-12 13:30 | 44573.5625 | 0 | 13.8074 | 37.78
2022-01-12 14:00 | 44573.5833 | 0 | 14.8768 | 37.78
2022-01-12 14:30 | 44573.6042 | 0 | 15.0552 | 37.78
2022-01-12 15:00 | 44573.625 | 0 | 15.7338 | 37.78
2022-01-12 15:30 | 44573.6458 | 0 | 16.4414 | 37.78
2022-01-12 16:00 | 44573.6667 | 0 | 16.6676 | 37.78
2022-01-12 16:30 | 44573.6875 | 0 | 16.5085 | 37.78
2022-01-12 17:00 | 44573.7083 | 0 | 16.7231 | 37.78
2022-01-12 17:30 | 44573.7292 | 0 | 16.5145 | 37.78
2022-01-12 18:00 | 44573.75 | 0 | 16.4618 | 37.78
2022-01-12 18:30 | 44573.7708 | 0 | 16.9238 | 37.78
2022-01-12 19:00 | 44573.7917 | 0 | 16.9981 | 37.78
2022-01-12 19:30 | 44573.8125 | 0 | 16.62 | 37.78
2022-01-12 20:00 | 44573.8333 | 0 | 16.4121 | 37.78
2022-01-12 20:30 | 44573.8542 | 0 | 15.6367 | 37.78
2022-01-12 21:00 | 44573.875 | 0 | 14.9322 | 37.78
2022-01-12 21:30 | 44573.8958 | 0 | 14.2233 | 37.78
2022-01-12 22:00 | 44573.9167 | 0 | 13.6267 | 37.78
2022-01-12 22:30 | 44573.9375 | 0 | 12.5059 | 37.78
2022-01-12 23:00 | 44573.9583 | 0 | 11.9128 | 37.78
2022-01-12 23:30 | 44573.9792 | 0 | 11.2929 | 37.78
2022-01-13 | 44574 | 0 | 10.6206 | 37.78
2022-01-13 00:30 | 44574.0208 | 0 | 10.2894 | 37.78
2022-01-13 01:00 | 44574.0417 | 0 | 10.1141 | 37.78
2022-01-13 01:30 | 44574.0625 | 0 | 9.9473 | 37.78
2022-01-13 02:00 | 44574.0833 | 0 | 9.7418 | 37.78
2022-01-13 02:30 | 44574.1042 | 0 | 9.7052 | 37.78
2022-01-13 03:00 | 44574.125 | 0 | 9.5465 | 37.78
2022-01-13 03:30 | 44574.1458 | 0 | 9.4469 | 37.78
2022-01-13 04:00 | 44574.1667 | 0 | 9.7842 | 37.78
2022-01-13 04:30 | 44574.1875 | 0 | 10.148 | 37.78
2022-01-13 05:00 | 44574.2083 | 0 | 10.6684 | 37.78
2022-01-13 05:30 | 44574.2292 | 0 | 10.9585 | 37.78
2022-01-13 06:00 | 44574.25 | 0 | 11.3675 | 37.78
2022-01-13 06:30 | 44574.2708 | 0 | 11.4462 | 37.78
2022-01-13 07:00 | 44574.2917 | 0 | 12.706 | 37.78
2022-01-13 07:30 | 44574.3125 | 0 | 11.9614 | 37.78
2022-01-13 08:00 | 44574.3333 | 0 | 12.891 | 37.78
2022-01-13 08:30 | 44574.3542 | 0 | 13.2405 | 37.78
2022-01-13 09:00 | 44574.375 | 0 | 12.6566 | 37.78
2022-01-13 09:30 | 44574.3958 | 0 | 12.72 | 37.78
2022-01-13 10:00 | 44574.4167 | 0 | 13.256 | 37.78
2022-01-13 10:30 | 44574.4375 | 0 | 13.8967 | 37.78
2022-01-13 11:00 | 44574.4583 | 0 | 13.9956 | 37.78
2022-01-13 11:30 | 44574.4792 | 0 | 13.8427 | 37.78
2022-01-13 12:00 | 44574.5 | 0 | 13.2518 | 37.78
2022-01-13 12:30 | 44574.5208 | 0 | 13.3633 | 37.78
2022-01-13 13:00 | 44574.5417 | 0 | 13.5362 | 37.78
2022-01-13 13:30 | 44574.5625 | 0 | 14.6392 | 37.78
2022-01-13 14:00 | 44574.5833 | 0 | 15.1245 | 37.78
2022-01-13 14:30 | 44574.6042 | 0 | 15.2569 | 37.78
2022-01-13 15:00 | 44574.625 | 0 | 16.3212 | 37.78
2022-01-13 15:30 | 44574.6458 | 0 | 16.7944 | 37.78
2022-01-13 16:00 | 44574.6667 | 0 | 17.0615 | 37.78
2022-01-13 16:30 | 44574.6875 | 0 | 17.3444 | 37.78
2022-01-13 17:00 | 44574.7083 | 0 | 17.3224 | 37.78
2022-01-13 17:30 | 44574.7292 | 0 | 17.1614 | 37.78
2022-01-13 18:00 | 44574.75 | 0 | 16.611 | 37.78
2022-01-13 18:30 | 44574.7708 | 0 | 16.8284 | 37.78
2022-01-13 19:00 | 44574.7917 | 0 | 16.8957 | 37.78
2022-01-13 19:30 | 44574.8125 | 0 | 16.3897 | 37.78
2022-01-13 20:00 | 44574.8333 | 0 | 16.0191 | 37.78
2022-01-13 20:30 | 44574.8542 | 0 | 15.4307 | 37.78
2022-01-13 21:00 | 44574.875 | 0 | 14.7698 | 37.78
2022-01-13 21:30 | 44574.8958 | 0 | 14.042 | 37.78
2022-01-13 22:00 | 44574.9167 | 0 | 13.232 | 37.78
2022-01-13 22:30 | 44574.9375 | 0 | 12.1602 | 37.78
2022-01-13 23:00 | 44574.9583 | 0 | 11.6773 | 37.78
2022-01-13 23:30 | 44574.9792 | 0 | 11.0638 | 37.78
2022-01-14 | 44575 | 0 | 10.398 | 37.78
2022-01-14 00:30 | 44575.0208 | 0 | 9.8464 | 37.78
2022-01-14 01:00 | 44575.0417 | 0 | 9.5316 | 37.78
2022-01-14 01:30 | 44575.0625 | 0 | 9.2731 | 37.78
2022-01-14 02:00 | 44575.0833 | 0 | 9.1538 | 37.78
2022-01-14 02:30 | 44575.1042 | 0 | 9.2005 | 37.78
2022-01-14 03:00 | 44575.125 | 0 | 9.0617 | 37.78
2022-01-14 03:30 | 44575.1458 | 0 | 8.9104 | 37.78
2022-01-14 04:00 | 44575.1667 | 0 | 9.2683 | 37.78
2022-01-14 04:30 | 44575.1875 | 0 | 9.6231 | 37.78
2022-01-14 05:00 | 44575.2083 | 0 | 10.1125 | 37.78
2022-01-14 05:30 | 44575.2292 | 0 | 10.2978 | 37.78
2022-01-14 06:00 | 44575.25 | 0 | 10.8507 | 37.78
2022-01-14 06:30 | 44575.2708 | 0 | 11.0094 | 37.78
2022-01-14 07:00 | 44575.2917 | 0 | 11.5765 | 37.78
2022-01-14 07:30 | 44575.3125 | 0 | 11.8831 | 37.78
2022-01-14 08:00 | 44575.3333 | 0 | 12.4615 | 37.78
2022-01-14 08:30 | 44575.3542 | 0 | 13.3356 | 37.78
2022-01-14 09:00 | 44575.375 | 0 | 14.9341 | 37.78
2022-01-14 09:30 | 44575.3958 | 0 | 14.9303 | 37.78
2022-01-14 10:00 | 44575.4167 | 0 | 13.9919 | 37.78
2022-01-14 10:30 | 44575.4375 | 0 | 12.4346 | 37.78
2022-01-14 11:00 | 44575.4583 | 0 | 13.0655 | 37.78
2022-01-14 11:30 | 44575.4792 | 0 | 13.4952 | 37.78
2022-01-14 12:00 | 44575.5 | 0 | 14.4084 | 37.78
2022-01-14 12:30 | 44575.5208 | 0 | 14.0181 | 37.78
2022-01-14 13:00 | 44575.5417 | 0 | 14.0115 | 37.78
2022-01-14 13:30 | 44575.5625 | 0 | 14.2923 | 37.78
2022-01-14 14:00 | 44575.5833 | 0 | 15.7927 | 37.78
2022-01-14 14:30 | 44575.6042 | 0 | 15.8038 | 37.78
2022-01-14 15:00 | 44575.625 | 0 | 15.2528 | 37.78
2022-01-14 15:30 | 44575.6458 | 0 | 16.4667 | 37.78
2022-01-14 16:00 | 44575.6667 | 0 | 16.7403 | 37.78
2022-01-14 16:30 | 44575.6875 | 0 | 16.4103 | 37.78
2022-01-14 17:00 | 44575.7083 | 0 | 16.8358 | 37.78
2022-01-14 17:30 | 44575.7292 | 0 | 16.9231 | 37.78
2022-01-14 18:00 | 44575.75 | 0 | 16.667 | 37.78
2022-01-14 18:30 | 44575.7708 | 0 | 16.86 | 37.78
2022-01-14 19:00 | 44575.7917 | 0 | 16.7432 | 37.78
2022-01-14 19:30 | 44575.8125 | 0 | 16.4127 | 37.78
2022-01-14 20:00 | 44575.8333 | 0 | 16.0872 | 37.78
2022-01-14 20:30 | 44575.8542 | 0 | 15.5796 | 37.78
2022-01-14 21:00 | 44575.875 | 0 | 15.0838 | 37.78
2022-01-14 21:30 | 44575.8958 | 0 | 14.4287 | 37.78
2022-01-14 22:00 | 44575.9167 | 0 | 13.9659 | 37.78
2022-01-14 22:30 | 44575.9375 | 0 | 12.8798 | 37.78
2022-01-14 23:00 | 44575.9583 | 0 | 12.2109 | 37.78
2022-01-14 23:30 | 44575.9792 | 0 | 11.69 | 37.78
2022-01-15 | 44576 | 0 | 10.9775 | 37.78
2022-01-15 00:30 | 44576.0208 | 0 | 10.4183 | 37.78
2022-01-15 01:00 | 44576.0417 | 0 | 10.1801 | 37.78
2022-01-15 01:30 | 44576.0625 | 0 | 9.9353 | 37.78
2022-01-15 02:00 | 44576.0833 | 0 | 9.5934 | 37.78
2022-01-15 02:30 | 44576.1042 | 0 | 9.5616 | 37.78
2022-01-15 03:00 | 44576.125 | 0 | 9.3309 | 37.78
2022-01-15 03:30 | 44576.1458 | 0 | 9.3303 | 37.78
2022-01-15 04:00 | 44576.1667 | 0 | 9.3443 | 37.78
2022-01-15 04:30 | 44576.1875 | 0 | 9.4731 | 37.78
2022-01-15 05:00 | 44576.2083 | 0 | 9.4717 | 37.78
2022-01-15 05:30 | 44576.2292 | 0 | 9.3103 | 37.78
2022-01-15 06:00 | 44576.25 | 0 | 9.6066 | 37.78
2022-01-15 06:30 | 44576.2708 | 0 | 9.4702 | 37.78
2022-01-15 07:00 | 44576.2917 | 0 | 9.752 | 37.78
2022-01-15 07:30 | 44576.3125 | 0 | 9.7707 | 37.78
2022-01-15 08:00 | 44576.3333 | 0 | 10.162 | 37.78
2022-01-15 08:30 | 44576.3542 | 0 | 10.2959 | 37.78
2022-01-15 09:00 | 44576.375 | 0 | 10.4239 | 37.78
2022-01-15 09:30 | 44576.3958 | 0 | 10.9466 | 37.78
2022-01-15 10:00 | 44576.4167 | 0 | 10.3628 | 37.78
2022-01-15 10:30 | 44576.4375 | 0 | 10.6118 | 37.78
2022-01-15 11:00 | 44576.4583 | 0 | 11.4737 | 37.78
2022-01-15 11:30 | 44576.4792 | 0 | 11.1054 | 37.78
2022-01-15 12:00 | 44576.5 | 0 | 10.8659 | 37.78
2022-01-15 12:30 | 44576.5208 | 0 | 11.3852 | 37.78
2022-01-15 13:00 | 44576.5417 | 0 | 11.8503 | 37.78
2022-01-15 13:30 | 44576.5625 | 0 | 12.0584 | 37.78
2022-01-15 14:00 | 44576.5833 | 0 | 12.8096 | 37.78
2022-01-15 14:30 | 44576.6042 | 0 | 13.5089 | 37.78
2022-01-15 15:00 | 44576.625 | 0 | 13.9298 | 37.78
2022-01-15 15:30 | 44576.6458 | 0 | 14.6812 | 37.78
2022-01-15 16:00 | 44576.6667 | 0 | 15.3448 | 37.78
2022-01-15 16:30 | 44576.6875 | 0 | 16.0467 | 37.78
2022-01-15 17:00 | 44576.7083 | 0 | 16.3874 | 37.78
2022-01-15 17:30 | 44576.7292 | 0 | 16.7498 | 37.78
2022-01-15 18:00 | 44576.75 | 0 | 16.8817 | 37.78
2022-01-15 18:30 | 44576.7708 | 0 | 17.0252 | 37.78
2022-01-15 19:00 | 44576.7917 | 0 | 16.9395 | 37.78
2022-01-15 19:30 | 44576.8125 | 0 | 16.8031 | 37.78
2022-01-15 20:00 | 44576.8333 | 0 | 16.5408 | 37.78
2022-01-15 20:30 | 44576.8542 | 0 | 16.1346 | 37.78
2022-01-15 21:00 | 44576.875 | 0 | 15.5118 | 37.78
2022-01-15 21:30 | 44576.8958 | 0 | 14.8728 | 37.78
2022-01-15 22:00 | 44576.9167 | 0 | 14.4775 | 37.78
2022-01-15 22:30 | 44576.9375 | 0 | 13.4092 | 37.78
2022-01-15 23:00 | 44576.9583 | 0 | 12.7122 | 37.78
2022-01-15 23:30 | 44576.9792 | 0 | 12.0988 | 37.78
2022-01-16 | 44577 | 0 | 11.3107 | 37.78
2022-01-16 00:30 | 44577.0208 | 0 | 10.9681 | 37.78
2022-01-16 01:00 | 44577.0417 | 0 | 10.6402 | 37.78
2022-01-16 01:30 | 44577.0625 | 0 | 10.2383 | 37.78
2022-01-16 02:00 | 44577.0833 | 0 | 10.1146 | 37.78
2022-01-16 02:30 | 44577.1042 | 0 | 9.7781 | 37.78
2022-01-16 03:00 | 44577.125 | 0 | 9.377 | 37.78
2022-01-16 03:30 | 44577.1458 | 0 | 9.3321 | 37.78
2022-01-16 04:00 | 44577.1667 | 0 | 9.2867 | 37.78
2022-01-16 04:30 | 44577.1875 | 0 | 9.215 | 37.78
2022-01-16 05:00 | 44577.2083 | 0 | 9.249 | 37.78
2022-01-16 05:30 | 44577.2292 | 0 | 9.1483 | 37.78
2022-01-16 06:00 | 44577.25 | 0 | 9.1099 | 37.78
2022-01-16 06:30 | 44577.2708 | 0 | 8.7888 | 37.78
2022-01-16 07:00 | 44577.2917 | 0 | 8.4078 | 37.78
2022-01-16 07:30 | 44577.3125 | 0 | 8.768 | 37.78
2022-01-16 08:00 | 44577.3333 | 0 | 8.9516 | 37.78
2022-01-16 08:30 | 44577.3542 | 0 | 9.1049 | 37.78
2022-01-16 09:00 | 44577.375 | 0 | 8.1662 | 37.78
2022-01-16 09:30 | 44577.3958 | 0 | 9.6278 | 37.78
2022-01-16 10:00 | 44577.4167 | 0 | 9.5115 | 37.78
2022-01-16 10:30 | 44577.4375 | 0 | 9.3946 | 37.78
2022-01-16 11:00 | 44577.4583 | 0 | 11.2108 | 37.78
2022-01-16 11:30 | 44577.4792 | 0 | 13.2483 | 37.78
2022-01-16 12:00 | 44577.5 | 0 | 13.1731 | 37.78
2022-01-16 12:30 | 44577.5208 | 0 | 11.2322 | 37.78
2022-01-16 13:00 | 44577.5417 | 0 | 11.4326 | 37.78
2022-01-16 13:30 | 44577.5625 | 0 | 12.15 | 37.78
2022-01-16 14:00 | 44577.5833 | 0 | 12.8031 | 37.78
2022-01-16 14:30 | 44577.6042 | 0 | 13.5913 | 37.78
2022-01-16 15:00 | 44577.625 | 0 | 14.3046 | 37.78
2022-01-16 15:30 | 44577.6458 | 0 | 15.1477 | 37.78
2022-01-16 16:00 | 44577.6667 | 0 | 16.0236 | 37.78
2022-01-16 16:30 | 44577.6875 | 0 | 16.7214 | 37.78
2022-01-16 17:00 | 44577.7083 | 0 | 17.7239 | 37.78
2022-01-16 17:30 | 44577.7292 | 0 | 17.8149 | 37.78
2022-01-16 18:00 | 44577.75 | 0 | 17.9352 | 37.78
2022-01-16 18:30 | 44577.7708 | 0 | 18.1737 | 37.78
2022-01-16 19:00 | 44577.7917 | 0 | 18.2398 | 37.78
2022-01-16 19:30 | 44577.8125 | 0 | 18.1159 | 37.78
2022-01-16 20:00 | 44577.8333 | 0 | 17.8399 | 37.78
2022-01-16 20:30 | 44577.8542 | 0 | 16.9646 | 37.78
2022-01-16 21:00 | 44577.875 | 0 | 16.2727 | 37.78
2022-01-16 21:30 | 44577.8958 | 0 | 15.5239 | 37.78
2022-01-16 22:00 | 44577.9167 | 0 | 14.7318 | 37.78
2022-01-16 22:30 | 44577.9375 | 0 | 13.5455 | 37.78
2022-01-16 23:00 | 44577.9583 | 0 | 12.6071 | 37.78
2022-01-16 23:30 | 44577.9792 | 0 | 12.0293 | 37.78
2022-01-17 | 44578 | 0 | 11.7114 | 37.78
2022-01-17 00:30 | 44578.0208 | 0 | 11.2828 | 37.78
2022-01-17 01:00 | 44578.0417 | 0 | 11.0093 | 37.78
2022-01-17 01:30 | 44578.0625 | 0 | 10.7176 | 37.78
2022-01-17 02:00 | 44578.0833 | 0 | 10.5645 | 37.78
2022-01-17 02:30 | 44578.1042 | 0 | 10.5315 | 37.78
2022-01-17 03:00 | 44578.125 | 0 | 10.4011 | 37.78
2022-01-17 03:30 | 44578.1458 | 0 | 10.2846 | 37.78
2022-01-17 04:00 | 44578.1667 | 0 | 10.6397 | 37.78
2022-01-17 04:30 | 44578.1875 | 0 | 11.2126 | 37.78
2022-01-17 05:00 | 44578.2083 | 0 | 11.6163 | 37.78
2022-01-17 05:30 | 44578.2292 | 0 | 12.101 | 37.78
2022-01-17 06:00 | 44578.25 | 0 | 13.0179 | 37.78
2022-01-17 06:30 | 44578.2708 | 0 | 13.646 | 37.78
2022-01-17 07:00 | 44578.2917 | 0 | 14.666 | 37.78
2022-01-17 07:30 | 44578.3125 | 0 | 13.5485 | 37.78
2022-01-17 08:00 | 44578.3333 | 0 | 14.7885 | 37.78
2022-01-17 08:30 | 44578.3542 | 0 | 15.4398 | 37.78
2022-01-17 09:00 | 44578.375 | 0 | 15.7963 | 37.78
2022-01-17 09:30 | 44578.3958 | 0 | 16.5669 | 37.78
2022-01-17 10:00 | 44578.4167 | 0 | 16.9815 | 37.78
2022-01-17 10:30 | 44578.4375 | 0 | 16.4515 | 37.78
2022-01-17 11:00 | 44578.4583 | 0 | 16.8841 | 37.78
2022-01-17 11:30 | 44578.4792 | 0 | 17.1148 | 37.78
2022-01-17 12:00 | 44578.5 | 0 | 17.5928 | 37.78
2022-01-17 12:30 | 44578.5208 | 0 | 17.8143 | 37.78
2022-01-17 13:00 | 44578.5417 | 0 | 19.8726 | 37.78
2022-01-17 13:30 | 44578.5625 | 0 | 20.1583 | 37.78
2022-01-17 14:00 | 44578.5833 | 0 | 20.2517 | 37.78
2022-01-17 14:30 | 44578.6042 | 0 | 19.5477 | 37.78
2022-01-17 15:00 | 44578.625 | 0 | 20.069 | 37.78
2022-01-17 15:30 | 44578.6458 | 0 | 21.1148 | 37.78
2022-01-17 16:00 | 44578.6667 | 0 | 21.8142 | 37.78
2022-01-17 16:30 | 44578.6875 | 0 | 22.2754 | 37.78
2022-01-17 17:00 | 44578.7083 | 0 | 21.5486 | 37.78
2022-01-17 17:30 | 44578.7292 | 0 | 21.6755 | 37.78
2022-01-17 18:00 | 44578.75 | 0 | 21.3086 | 37.78
2022-01-17 18:30 | 44578.7708 | 0 | 21.8316 | 37.78
2022-01-17 19:00 | 44578.7917 | 0 | 21.5153 | 37.78
2022-01-17 19:30 | 44578.8125 | 0 | 21.1349 | 37.78
2022-01-17 20:00 | 44578.8333 | 0 | 20.4953 | 37.78
2022-01-17 20:30 | 44578.8542 | 0 | 19.4808 | 37.78
2022-01-17 21:00 | 44578.875 | 0 | 18.5585 | 37.78
2022-01-17 21:30 | 44578.8958 | 0 | 17.6776 | 37.78
2022-01-17 22:00 | 44578.9167 | 0 | 16.6454 | 37.78
2022-01-17 22:30 | 44578.9375 | 0 | 15.384 | 37.78
2022-01-17 23:00 | 44578.9583 | 0 | 14.407 | 37.78
2022-01-17 23:30 | 44578.9792 | 0 | 13.8186 | 37.78
2022-01-18 | 44579 | 0 | 12.9451 | 37.78
2022-01-18 00:30 | 44579.0208 | 0 | 12.4503 | 37.78
2022-01-18 01:00 | 44579.0417 | 0 | 12.2291 | 37.78
2022-01-18 01:30 | 44579.0625 | 0 | 11.8798 | 37.78
2022-01-18 02:00 | 44579.0833 | 0 | 11.7372 | 37.78
2022-01-18 02:30 | 44579.1042 | 0 | 11.6243 | 37.78
2022-01-18 03:00 | 44579.125 | 0 | 11.5153 | 37.78
2022-01-18 03:30 | 44579.1458 | 0 | 11.4382 | 37.78
2022-01-18 04:00 | 44579.1667 | 0 | 11.7038 | 37.78
2022-01-18 04:30 | 44579.1875 | 0 | 11.8044 | 37.78
2022-01-18 05:00 | 44579.2083 | 0 | 12.067 | 37.78
2022-01-18 05:30 | 44579.2292 | 0 | 12.3741 | 37.78
2022-01-18 06:00 | 44579.25 | 0 | 12.9971 | 37.78
2022-01-18 06:30 | 44579.2708 | 0 | 14.1708 | 37.78
2022-01-18 07:00 | 44579.2917 | 0 | 14.8164 | 37.78
2022-01-18 07:30 | 44579.3125 | 0 | 16.7094 | 37.78
2022-01-18 08:00 | 44579.3333 | 0 | 17.0185 | 37.78
2022-01-18 08:30 | 44579.3542 | 0 | 16.5076 | 37.78
2022-01-18 09:00 | 44579.375 | 0 | 17.4269 | 37.78
2022-01-18 09:30 | 44579.3958 | 0 | 17.5726 | 37.78
2022-01-18 10:00 | 44579.4167 | 0 | 16.5601 | 37.78
2022-01-18 10:30 | 44579.4375 | 0 | 17.4362 | 37.78
2022-01-18 11:00 | 44579.4583 | 0 | 17.6667 | 37.78
2022-01-18 11:30 | 44579.4792 | 0 | 17.2412 | 37.78
2022-01-18 12:00 | 44579.5 | 0 | 17.0797 | 37.78
2022-01-18 12:30 | 44579.5208 | 0 | 17.4451 | 37.78
2022-01-18 13:00 | 44579.5417 | 0 | 17.9989 | 37.78
2022-01-18 13:30 | 44579.5625 | 0 | 17.9507 | 37.78
2022-01-18 14:00 | 44579.5833 | 0 | 18.7411 | 37.78
2022-01-18 14:30 | 44579.6042 | 0 | 20.0871 | 37.78
2022-01-18 15:00 | 44579.625 | 0 | 20.559 | 37.78
2022-01-18 15:30 | 44579.6458 | 0 | 20.8719 | 37.78
2022-01-18 16:00 | 44579.6667 | 0 | 20.7231 | 37.78
2022-01-18 16:30 | 44579.6875 | 0 | 20.9318 | 37.78
2022-01-18 17:00 | 44579.7083 | 0 | 20.293 | 37.78
2022-01-18 17:30 | 44579.7292 | 0 | 20.6419 | 37.78
2022-01-18 18:00 | 44579.75 | 0 | 20.5943 | 37.78
2022-01-18 18:30 | 44579.7708 | 0 | 20.9462 | 37.78
2022-01-18 19:00 | 44579.7917 | 0 | 20.7787 | 37.78
2022-01-18 19:30 | 44579.8125 | 0 | 20.4391 | 37.78
2022-01-18 20:00 | 44579.8333 | 0 | 20.0843 | 37.78
2022-01-18 20:30 | 44579.8542 | 0 | 19.2013 | 37.78
2022-01-18 21:00 | 44579.875 | 0 | 18.3359 | 37.78
2022-01-18 21:30 | 44579.8958 | 0 | 17.3589 | 37.78
2022-01-18 22:00 | 44579.9167 | 0 | 16.4374 | 37.78
2022-01-18 22:30 | 44579.9375 | 0 | 15.2369 | 37.78
2022-01-18 23:00 | 44579.9583 | 0 | 14.323 | 37.78
2022-01-18 23:30 | 44579.9792 | 0 | 13.5994 | 37.78
2022-01-19 | 44580 | 0 | 12.7999 | 37.78
2022-01-19 00:30 | 44580.0208 | 0 | 12.2603 | 37.78
2022-01-19 01:00 | 44580.0417 | 0 | 11.9364 | 37.78
2022-01-19 01:30 | 44580.0625 | 0 | 11.6529 | 37.78
2022-01-19 02:00 | 44580.0833 | 0 | 11.3718 | 37.78
2022-01-19 02:30 | 44580.1042 | 0 | 11.2904 | 37.78
2022-01-19 03:00 | 44580.125 | 0 | 10.9466 | 37.78
2022-01-19 03:30 | 44580.1458 | 0 | 11.0675 | 37.78
2022-01-19 04:00 | 44580.1667 | 0 | 11.2113 | 37.78
2022-01-19 04:30 | 44580.1875 | 0 | 11.586 | 37.78
2022-01-19 05:00 | 44580.2083 | 0 | 11.8685 | 37.78
2022-01-19 05:30 | 44580.2292 | 0 | 12.3555 | 37.78
2022-01-19 06:00 | 44580.25 | 0 | 13.0588 | 37.78
2022-01-19 06:30 | 44580.2708 | 0 | 14.0208 | 37.78
2022-01-19 07:00 | 44580.2917 | 0 | 15.6123 | 37.78
2022-01-19 07:30 | 44580.3125 | 0 | 16.6263 | 37.78
2022-01-19 08:00 | 44580.3333 | 0 | 17.337 | 37.78
2022-01-19 08:30 | 44580.3542 | 0 | 17.3977 | 37.78
2022-01-19 09:00 | 44580.375 | 0 | 17.4284 | 37.78
2022-01-19 09:30 | 44580.3958 | 0 | 15.7647 | 37.78
2022-01-19 10:00 | 44580.4167 | 0 | 15.7121 | 37.78
2022-01-19 10:30 | 44580.4375 | 0 | 17.1545 | 37.78
2022-01-19 11:00 | 44580.4583 | 0 | 17.5507 | 37.78
2022-01-19 11:30 | 44580.4792 | 0 | 17.5643 | 37.78
2022-01-19 12:00 | 44580.5 | 0 | 18.334 | 37.78
2022-01-19 12:30 | 44580.5208 | 0 | 18.9709 | 37.78
2022-01-19 13:00 | 44580.5417 | 0 | 18.6346 | 37.78
2022-01-19 13:30 | 44580.5625 | 0 | 18.7899 | 37.78
2022-01-19 14:00 | 44580.5833 | 0 | 19.5097 | 37.78
2022-01-19 14:30 | 44580.6042 | 0 | 19.6757 | 37.78
2022-01-19 15:00 | 44580.625 | 0 | 20.3524 | 37.78
2022-01-19 15:30 | 44580.6458 | 0 | 22.526 | 37.78
2022-01-19 16:00 | 44580.6667 | 0 | 21.9666 | 37.78
2022-01-19 16:30 | 44580.6875 | 0 | 22.006 | 37.78
2022-01-19 17:00 | 44580.7083 | 0 | 21.3864 | 37.78
2022-01-19 17:30 | 44580.7292 | 0 | 20.9105 | 37.78
2022-01-19 18:00 | 44580.75 | 0 | 20.8352 | 37.78
2022-01-19 18:30 | 44580.7708 | 0 | 21.1454 | 37.78
2022-01-19 19:00 | 44580.7917 | 0 | 21.0549 | 37.78
2022-01-19 19:30 | 44580.8125 | 0 | 20.6823 | 37.78
2022-01-19 20:00 | 44580.8333 | 0 | 20.0691 | 37.78
2022-01-19 20:30 | 44580.8542 | 0 | 18.6859 | 37.78
2022-01-19 21:00 | 44580.875 | 0 | 17.5304 | 37.78
2022-01-19 21:30 | 44580.8958 | 0 | 16.6257 | 37.78
2022-01-19 22:00 | 44580.9167 | 0 | 15.5617 | 37.78
2022-01-19 22:30 | 44580.9375 | 0 | 14.3863 | 37.78
2022-01-19 23:00 | 44580.9583 | 0 | 13.6248 | 37.78
2022-01-19 23:30 | 44580.9792 | 0 | 12.8858 | 37.78
2022-01-20 | 44581 | 0 | 12.1008 | 37.78
2022-01-20 00:30 | 44581.0208 | 0 | 11.677 | 37.78
2022-01-20 01:00 | 44581.0417 | 0 | 11.3903 | 37.78
2022-01-20 01:30 | 44581.0625 | 0 | 11.1154 | 37.78
2022-01-20 02:00 | 44581.0833 | 0 | 11.1199 | 37.78
2022-01-20 02:30 | 44581.1042 | 0 | 11.0079 | 37.78
2022-01-20 03:00 | 44581.125 | 0 | 10.7377 | 37.78
2022-01-20 03:30 | 44581.1458 | 0 | 10.6173 | 37.78
2022-01-20 04:00 | 44581.1667 | 0 | 10.7733 | 37.78
2022-01-20 04:30 | 44581.1875 | 0 | 11.2866 | 37.78
2022-01-20 05:00 | 44581.2083 | 0 | 11.5668 | 37.78
2022-01-20 05:30 | 44581.2292 | 0 | 11.774 | 37.78
2022-01-20 06:00 | 44581.25 | 0 | 12.4901 | 37.78
2022-01-20 06:30 | 44581.2708 | 0 | 13.1284 | 37.78
2022-01-20 07:00 | 44581.2917 | 0 | 13.7638 | 37.78
2022-01-20 07:30 | 44581.3125 | 0 | 14.058 | 37.78
2022-01-20 08:00 | 44581.3333 | 0 | 14.5744 | 37.78
2022-01-20 08:30 | 44581.3542 | 0 | 14.3805 | 37.78
2022-01-20 09:00 | 44581.375 | 0 | 15.4332 | 37.78
2022-01-20 09:30 | 44581.3958 | 0 | 15.1388 | 37.78
2022-01-20 10:00 | 44581.4167 | 0 | 15.2054 | 37.78
2022-01-20 10:30 | 44581.4375 | 0 | 15.1877 | 37.78
2022-01-20 11:00 | 44581.4583 | 0 | 14.785 | 37.78
2022-01-20 11:30 | 44581.4792 | 0 | 14.5276 | 37.78
2022-01-20 12:00 | 44581.5 | 0 | 13.6648 | 37.78
2022-01-20 12:30 | 44581.5208 | 0 | 15.016 | 37.78
2022-01-20 13:00 | 44581.5417 | 0 | 15.5935 | 37.78
2022-01-20 13:30 | 44581.5625 | 0 | 15.2954 | 37.78
2022-01-20 14:00 | 44581.5833 | 0 | 15.4421 | 37.78
2022-01-20 14:30 | 44581.6042 | 0 | 15.38 | 37.78
2022-01-20 15:00 | 44581.625 | 0 | 14.1669 | 37.78
2022-01-20 15:30 | 44581.6458 | 0 | 13.723 | 37.78
2022-01-20 16:00 | 44581.6667 | 0 | 14.5657 | 37.78
2022-01-20 16:30 | 44581.6875 | 0 | 15.3356 | 37.78
2022-01-20 17:00 | 44581.7083 | 0 | 14.8023 | 37.78
2022-01-20 17:30 | 44581.7292 | 0 | 15.5978 | 37.78
2022-01-20 18:00 | 44581.75 | 0 | 15.8589 | 37.78
2022-01-20 18:30 | 44581.7708 | 0 | 15.9479 | 37.78
2022-01-20 19:00 | 44581.7917 | 0 | 15.7198 | 37.78
2022-01-20 19:30 | 44581.8125 | 0 | 15.4121 | 37.78
2022-01-20 20:00 | 44581.8333 | 0 | 15.1472 | 37.78
2022-01-20 20:30 | 44581.8542 | 0 | 14.5612 | 37.78
2022-01-20 21:00 | 44581.875 | 0 | 13.9956 | 37.78
2022-01-20 21:30 | 44581.8958 | 0 | 13.601 | 37.78
2022-01-20 22:00 | 44581.9167 | 0 | 12.6315 | 37.78
2022-01-20 22:30 | 44581.9375 | 0 | 11.9115 | 37.78
2022-01-20 23:00 | 44581.9583 | 0 | 11.3193 | 37.78
2022-01-20 23:30 | 44581.9792 | 0 | 10.6828 | 37.78
2022-01-21 | 44582 | 0 | 10.1551 | 37.78
2022-01-21 00:30 | 44582.0208 | 0 | 9.8056 | 37.78
2022-01-21 01:00 | 44582.0417 | 0 | 9.6334 | 37.78
2022-01-21 01:30 | 44582.0625 | 0 | 9.4911 | 37.78
2022-01-21 02:00 | 44582.0833 | 0 | 9.3109 | 37.78
2022-01-21 02:30 | 44582.1042 | 0 | 9.447 | 37.78
2022-01-21 03:00 | 44582.125 | 0 | 9.2208 | 37.78
2022-01-21 03:30 | 44582.1458 | 0 | 9.0825 | 37.78
2022-01-21 04:00 | 44582.1667 | 0 | 9.5069 | 37.78
2022-01-21 04:30 | 44582.1875 | 0 | 9.7656 | 37.78
2022-01-21 05:00 | 44582.2083 | 0 | 9.9464 | 37.78
2022-01-21 05:30 | 44582.2292 | 0 | 10.0931 | 37.78
2022-01-21 06:00 | 44582.25 | 0 | 10.8317 | 37.78
2022-01-21 06:30 | 44582.2708 | 0 | 11.0581 | 37.78
2022-01-21 07:00 | 44582.2917 | 0 | 11.7002 | 37.78
2022-01-21 07:30 | 44582.3125 | 0 | 11.8482 | 37.78
2022-01-21 08:00 | 44582.3333 | 0 | 12.337 | 37.78
2022-01-21 08:30 | 44582.3542 | 0 | 13.2258 | 37.78
2022-01-21 09:00 | 44582.375 | 0 | 12.5118 | 37.78
2022-01-21 09:30 | 44582.3958 | 0 | 10.8578 | 37.78
2022-01-21 10:00 | 44582.4167 | 0 | 10.9 | 37.78
2022-01-21 10:30 | 44582.4375 | 0 | 11.1947 | 37.78
2022-01-21 11:00 | 44582.4583 | 0 | 10.6127 | 37.78
2022-01-21 11:30 | 44582.4792 | 0 | 11.8813 | 37.78
2022-01-21 12:00 | 44582.5 | 0 | 12.9395 | 37.78
2022-01-21 12:30 | 44582.5208 | 0 | 13.4669 | 37.78
2022-01-21 13:00 | 44582.5417 | 0 | 12.9318 | 37.78
2022-01-21 13:30 | 44582.5625 | 0 | 13.0293 | 37.78
2022-01-21 14:00 | 44582.5833 | 0 | 12.4701 | 37.78
2022-01-21 14:30 | 44582.6042 | 0 | 11.7815 | 37.78
2022-01-21 15:00 | 44582.625 | 0 | 11.4654 | 37.78
2022-01-21 15:30 | 44582.6458 | 0 | 12.9083 | 37.78
2022-01-21 16:00 | 44582.6667 | 0 | 13.1304 | 37.78
2022-01-21 16:30 | 44582.6875 | 0 | 13.3299 | 37.78
2022-01-21 17:00 | 44582.7083 | 0 | 13.7864 | 37.78
2022-01-21 17:30 | 44582.7292 | 0 | 13.9895 | 37.78
2022-01-21 18:00 | 44582.75 | 0 | 14.4224 | 37.78
2022-01-21 18:30 | 44582.7708 | 0 | 14.6475 | 37.78
2022-01-21 19:00 | 44582.7917 | 0 | 14.697 | 37.78
2022-01-21 19:30 | 44582.8125 | 0 | 14.5341 | 37.78
2022-01-21 20:00 | 44582.8333 | 0 | 14.286 | 37.78
2022-01-21 20:30 | 44582.8542 | 0 | 13.827 | 37.78
2022-01-21 21:00 | 44582.875 | 0 | 13.3191 | 37.78
2022-01-21 21:30 | 44582.8958 | 0 | 12.7175 | 37.78
2022-01-21 22:00 | 44582.9167 | 0 | 12.266 | 37.78
2022-01-21 22:30 | 44582.9375 | 0 | 11.5529 | 37.78
2022-01-21 23:00 | 44582.9583 | 0 | 11.0335 | 37.78
2022-01-21 23:30 | 44582.9792 | 0 | 10.3938 | 37.78
2022-01-22 | 44583 | 0 | 9.6898 | 37.78
2022-01-22 00:30 | 44583.0208 | 0 | 9.3123 | 37.78
2022-01-22 01:00 | 44583.0417 | 0 | 9.0949 | 37.78
2022-01-22 01:30 | 44583.0625 | 0 | 8.9527 | 37.78
2022-01-22 02:00 | 44583.0833 | 0 | 8.8366 | 37.78
2022-01-22 02:30 | 44583.1042 | 0 | 8.8655 | 37.78
2022-01-22 03:00 | 44583.125 | 0 | 8.5918 | 37.78
2022-01-22 03:30 | 44583.1458 | 0 | 8.5555 | 37.78
2022-01-22 04:00 | 44583.1667 | 0 | 8.7404 | 37.78
2022-01-22 04:30 | 44583.1875 | 0 | 8.8291 | 37.78
2022-01-22 05:00 | 44583.2083 | 0 | 8.9408 | 37.78
2022-01-22 05:30 | 44583.2292 | 0 | 8.9399 | 37.78
2022-01-22 06:00 | 44583.25 | 0 | 9.1757 | 37.78
2022-01-22 06:30 | 44583.2708 | 0 | 9.287 | 37.78
2022-01-22 07:00 | 44583.2917 | 0 | 9.5025 | 37.78
2022-01-22 07:30 | 44583.3125 | 0 | 9.37 | 37.78
2022-01-22 08:00 | 44583.3333 | 0 | 9.7452 | 37.78
2022-01-22 08:30 | 44583.3542 | 0 | 9.2673 | 37.78
2022-01-22 09:00 | 44583.375 | 0 | 7.5892 | 37.78
2022-01-22 09:30 | 44583.3958 | 0 | 8.9824 | 37.78
2022-01-22 10:00 | 44583.4167 | 0 | 8.575 | 37.78
2022-01-22 10:30 | 44583.4375 | 0 | 8.5259 | 37.78
2022-01-22 11:00 | 44583.4583 | 0 | 9.4653 | 37.78
2022-01-22 11:30 | 44583.4792 | 0 | 10.8849 | 37.78
2022-01-22 12:00 | 44583.5 | 0 | 9.4777 | 37.78
2022-01-22 12:30 | 44583.5208 | 0 | 8.8324 | 37.78
2022-01-22 13:00 | 44583.5417 | 0 | 11.1177 | 37.78
2022-01-22 13:30 | 44583.5625 | 0 | 9.4613 | 37.78
2022-01-22 14:00 | 44583.5833 | 0 | 10.8775 | 37.78
2022-01-22 14:30 | 44583.6042 | 0 | 11.1398 | 37.78
2022-01-22 15:00 | 44583.625 | 0 | 11.4214 | 37.78
2022-01-22 15:30 | 44583.6458 | 0 | 11.5899 | 37.78
2022-01-22 16:00 | 44583.6667 | 0 | 11.5311 | 37.78
2022-01-22 16:30 | 44583.6875 | 0 | 11.3305 | 37.78
2022-01-22 17:00 | 44583.7083 | 0 | 12.1207 | 37.78
2022-01-22 17:30 | 44583.7292 | 0 | 12.3912 | 37.78
2022-01-22 18:00 | 44583.75 | 0 | 12.6379 | 37.78
2022-01-22 18:30 | 44583.7708 | 0 | 12.9262 | 37.78
2022-01-22 19:00 | 44583.7917 | 0 | 12.7976 | 37.78
2022-01-22 19:30 | 44583.8125 | 0 | 12.6852 | 37.78
2022-01-22 20:00 | 44583.8333 | 0 | 12.4247 | 37.78
2022-01-22 20:30 | 44583.8542 | 0 | 11.9376 | 37.78
2022-01-22 21:00 | 44583.875 | 0 | 11.5606 | 37.78
2022-01-22 21:30 | 44583.8958 | 0 | 11.1633 | 37.78
2022-01-22 22:00 | 44583.9167 | 0 | 10.8051 | 37.78
2022-01-22 22:30 | 44583.9375 | 0 | 10.1087 | 37.78
2022-01-22 23:00 | 44583.9583 | 0 | 9.7179 | 37.78
2022-01-22 23:30 | 44583.9792 | 0 | 9.2118 | 37.78
2022-01-23 | 44584 | 0 | 8.7199 | 37.78
2022-01-23 00:30 | 44584.0208 | 0 | 8.4093 | 37.78
2022-01-23 01:00 | 44584.0417 | 0 | 8.3144 | 37.78
2022-01-23 01:30 | 44584.0625 | 0 | 8.1309 | 37.78
2022-01-23 02:00 | 44584.0833 | 0 | 8.0466 | 37.78
2022-01-23 02:30 | 44584.1042 | 0 | 7.9748 | 37.78
2022-01-23 03:00 | 44584.125 | 0 | 7.8903 | 37.78
2022-01-23 03:30 | 44584.1458 | 0 | 7.8909 | 37.78
2022-01-23 04:00 | 44584.1667 | 0 | 7.8501 | 37.78
2022-01-23 04:30 | 44584.1875 | 0 | 7.8685 | 37.78
2022-01-23 05:00 | 44584.2083 | 0 | 7.8444 | 37.78
2022-01-23 05:30 | 44584.2292 | 0 | 7.793 | 37.78
2022-01-23 06:00 | 44584.25 | 0 | 7.929 | 37.78
2022-01-23 06:30 | 44584.2708 | 0 | 7.2572 | 37.78
2022-01-23 07:00 | 44584.2917 | 0 | 7.3391 | 37.78
2022-01-23 07:30 | 44584.3125 | 0 | 7.1494 | 37.78
2022-01-23 08:00 | 44584.3333 | 0 | 7.1057 | 37.78
2022-01-23 08:30 | 44584.3542 | 0 | 7.0927 | 37.78
2022-01-23 09:00 | 44584.375 | 0 | 7.7254 | 37.78
2022-01-23 09:30 | 44584.3958 | 0 | 8.6334 | 37.78
2022-01-23 10:00 | 44584.4167 | 0 | 8.8014 | 37.78
2022-01-23 10:30 | 44584.4375 | 0 | 8.6925 | 37.78
2022-01-23 11:00 | 44584.4583 | 0 | 8.9559 | 37.78
2022-01-23 11:30 | 44584.4792 | 0 | 9.4993 | 37.78
2022-01-23 12:00 | 44584.5 | 0 | 10.383 | 37.78
2022-01-23 12:30 | 44584.5208 | 0 | 9.8543 | 37.78
2022-01-23 13:00 | 44584.5417 | 0 | 11.5726 | 37.78
2022-01-23 13:30 | 44584.5625 | 0 | 10.2646 | 37.78
2022-01-23 14:00 | 44584.5833 | 0 | 10.3803 | 37.78
2022-01-23 14:30 | 44584.6042 | 0 | 9.101 | 37.78
2022-01-23 15:00 | 44584.625 | 0 | 9.4732 | 37.78
2022-01-23 15:30 | 44584.6458 | 0 | 10.9304 | 37.78
2022-01-23 16:00 | 44584.6667 | 0 | 11.1584 | 37.78
2022-01-23 16:30 | 44584.6875 | 0 | 12.2997 | 37.78
2022-01-23 17:00 | 44584.7083 | 0 | 12.5551 | 37.78
2022-01-23 17:30 | 44584.7292 | 0 | 13.0455 | 37.78
2022-01-23 18:00 | 44584.75 | 0 | 13.4801 | 37.78
2022-01-23 18:30 | 44584.7708 | 0 | 13.9987 | 37.78
2022-01-23 19:00 | 44584.7917 | 0 | 14.0958 | 37.78
2022-01-23 19:30 | 44584.8125 | 0 | 13.8034 | 37.78
2022-01-23 20:00 | 44584.8333 | 0 | 13.6896 | 37.78
2022-01-23 20:30 | 44584.8542 | 0 | 13.0619 | 37.78
2022-01-23 21:00 | 44584.875 | 0 | 12.5474 | 37.78
2022-01-23 21:30 | 44584.8958 | 0 | 11.9327 | 37.78
2022-01-23 22:00 | 44584.9167 | 0 | 11.2896 | 37.78
2022-01-23 22:30 | 44584.9375 | 0 | 10.5161 | 37.78
2022-01-23 23:00 | 44584.9583 | 0 | 9.8248 | 37.78
2022-01-23 23:30 | 44584.9792 | 0 | 9.346 | 37.78
2022-01-24 | 44585 | 0 | 8.9402 | 37.78
2022-01-24 00:30 | 44585.0208 | 0 | 8.7029 | 37.78
2022-01-24 01:00 | 44585.0417 | 0 | 8.6427 | 37.78
2022-01-24 01:30 | 44585.0625 | 0 | 8.3795 | 37.78
2022-01-24 02:00 | 44585.0833 | 0 | 8.3765 | 37.78
2022-01-24 02:30 | 44585.1042 | 0 | 8.4584 | 37.78
2022-01-24 03:00 | 44585.125 | 0 | 8.2661 | 37.78
2022-01-24 03:30 | 44585.1458 | 0 | 8.3399 | 37.78
2022-01-24 04:00 | 44585.1667 | 0 | 8.4307 | 37.78
2022-01-24 04:30 | 44585.1875 | 0 | 8.7523 | 37.78
2022-01-24 05:00 | 44585.2083 | 0 | 9.1362 | 37.78
2022-01-24 05:30 | 44585.2292 | 0 | 9.4705 | 37.78
2022-01-24 06:00 | 44585.25 | 0 | 9.882 | 37.78
2022-01-24 06:30 | 44585.2708 | 0 | 10.3031 | 37.78
2022-01-24 07:00 | 44585.2917 | 0 | 10.7209 | 37.78
2022-01-24 07:30 | 44585.3125 | 0 | 10.8923 | 37.78
2022-01-24 08:00 | 44585.3333 | 0 | 10.8869 | 37.78
2022-01-24 08:30 | 44585.3542 | 0 | 10.8246 | 37.78
2022-01-24 09:00 | 44585.375 | 0 | 10.8976 | 37.78
2022-01-24 09:30 | 44585.3958 | 0 | 11.3076 | 37.78
2022-01-24 10:00 | 44585.4167 | 0 | 12.1006 | 37.78
2022-01-24 10:30 | 44585.4375 | 0 | 12.7523 | 37.78
2022-01-24 11:00 | 44585.4583 | 0 | 12.7501 | 37.78
2022-01-24 11:30 | 44585.4792 | 0 | 13.5506 | 37.78
2022-01-24 12:00 | 44585.5 | 0 | 13.5906 | 37.78
2022-01-24 12:30 | 44585.5208 | 0 | 13.3462 | 37.78
2022-01-24 13:00 | 44585.5417 | 0 | 13.3632 | 37.78
2022-01-24 13:30 | 44585.5625 | 0 | 13.0305 | 37.78
2022-01-24 14:00 | 44585.5833 | 0 | 14.2625 | 37.78
2022-01-24 14:30 | 44585.6042 | 0 | 14.0269 | 37.78
2022-01-24 15:00 | 44585.625 | 0 | 15.5092 | 37.78
2022-01-24 15:30 | 44585.6458 | 0 | 15.2569 | 37.78
2022-01-24 16:00 | 44585.6667 | 0 | 14.7699 | 37.78
2022-01-24 16:30 | 44585.6875 | 0 | 14.7687 | 37.78
2022-01-24 17:00 | 44585.7083 | 0 | 14.7151 | 37.78
2022-01-24 17:30 | 44585.7292 | 0 | 15.3946 | 37.78
2022-01-24 18:00 | 44585.75 | 0 | 15.4283 | 37.78
2022-01-24 18:30 | 44585.7708 | 0 | 15.8166 | 37.78
2022-01-24 19:00 | 44585.7917 | 0 | 15.9112 | 37.78
2022-01-24 19:30 | 44585.8125 | 0 | 15.6677 | 37.78
2022-01-24 20:00 | 44585.8333 | 0 | 15.3726 | 37.78
2022-01-24 20:30 | 44585.8542 | 0 | 14.7987 | 37.78
2022-01-24 21:00 | 44585.875 | 0 | 14.0292 | 37.78
2022-01-24 21:30 | 44585.8958 | 0 | 13.5311 | 37.78
2022-01-24 22:00 | 44585.9167 | 0 | 12.8781 | 37.78
2022-01-24 22:30 | 44585.9375 | 0 | 11.7687 | 37.78
2022-01-24 23:00 | 44585.9583 | 0 | 11.1875 | 37.78
2022-01-24 23:30 | 44585.9792 | 0 | 10.5593 | 37.78
2022-01-25 | 44586 | 0 | 10.0834 | 37.78
2022-01-25 00:30 | 44586.0208 | 0 | 9.8404 | 37.78
2022-01-25 01:00 | 44586.0417 | 0 | 9.6436 | 37.78
2022-01-25 01:30 | 44586.0625 | 0 | 9.3942 | 37.78
2022-01-25 02:00 | 44586.0833 | 0 | 9.3376 | 37.78
2022-01-25 02:30 | 44586.1042 | 0 | 9.192 | 37.78
2022-01-25 03:00 | 44586.125 | 0 | 9.1543 | 37.78
2022-01-25 03:30 | 44586.1458 | 0 | 9.037 | 37.78
2022-01-25 04:00 | 44586.1667 | 0 | 9.1665 | 37.78
2022-01-25 04:30 | 44586.1875 | 0 | 9.4143 | 37.78
2022-01-25 05:00 | 44586.2083 | 0 | 9.6027 | 37.78
2022-01-25 05:30 | 44586.2292 | 0 | 10.1006 | 37.78
2022-01-25 06:00 | 44586.25 | 0 | 10.8102 | 37.78
2022-01-25 06:30 | 44586.2708 | 0 | 11.2679 | 37.78
2022-01-25 07:00 | 44586.2917 | 0 | 12.0809 | 37.78
2022-01-25 07:30 | 44586.3125 | 0 | 11.6562 | 37.78
2022-01-25 08:00 | 44586.3333 | 0 | 12.0897 | 37.78
2022-01-25 08:30 | 44586.3542 | 0 | 12.2845 | 37.78
2022-01-25 09:00 | 44586.375 | 0 | 13.0856 | 37.78
2022-01-25 09:30 | 44586.3958 | 0 | 13.8467 | 37.78
2022-01-25 10:00 | 44586.4167 | 0 | 14.6921 | 37.78
2022-01-25 10:30 | 44586.4375 | 0 | 14.909 | 37.78
2022-01-25 11:00 | 44586.4583 | 0 | 14.8649 | 37.78
2022-01-25 11:30 | 44586.4792 | 0 | 14.0501 | 37.78
2022-01-25 12:00 | 44586.5 | 0 | 13.0129 | 37.78
2022-01-25 12:30 | 44586.5208 | 0 | 14.9637 | 37.78
2022-01-25 13:00 | 44586.5417 | 0 | 16.0648 | 37.78
2022-01-25 13:30 | 44586.5625 | 0 | 14.4634 | 37.78
2022-01-25 14:00 | 44586.5833 | 0 | 16.1038 | 37.78
2022-01-25 14:30 | 44586.6042 | 0 | 17.2738 | 37.78
2022-01-25 15:00 | 44586.625 | 0 | 17.2721 | 37.78
2022-01-25 15:30 | 44586.6458 | 0 | 16.8394 | 37.78
2022-01-25 16:00 | 44586.6667 | 0 | 16.4428 | 37.78
2022-01-25 16:30 | 44586.6875 | 0 | 16.1352 | 37.78
2022-01-25 17:00 | 44586.7083 | 0 | 15.8471 | 37.78
2022-01-25 17:30 | 44586.7292 | 0 | 16.3249 | 37.78
2022-01-25 18:00 | 44586.75 | 0 | 16.1405 | 37.78
2022-01-25 18:30 | 44586.7708 | 0 | 16.4583 | 37.78
2022-01-25 19:00 | 44586.7917 | 0 | 16.5297 | 37.78
2022-01-25 19:30 | 44586.8125 | 0 | 16.5804 | 37.78
2022-01-25 20:00 | 44586.8333 | 0 | 16.3782 | 37.78
2022-01-25 20:30 | 44586.8542 | 0 | 15.6321 | 37.78
2022-01-25 21:00 | 44586.875 | 0 | 15.0475 | 37.78
2022-01-25 21:30 | 44586.8958 | 0 | 14.4702 | 37.78
2022-01-25 22:00 | 44586.9167 | 0 | 13.9141 | 37.78
2022-01-25 22:30 | 44586.9375 | 0 | 12.9934 | 37.78
2022-01-25 23:00 | 44586.9583 | 0 | 12.2909 | 37.78
2022-01-25 23:30 | 44586.9792 | 0 | 11.5562 | 37.78
2022-01-26 | 44587 | 0 | 11.2524 | 37.78
2022-01-26 00:30 | 44587.0208 | 0 | 10.5817 | 37.78
2022-01-26 01:00 | 44587.0417 | 0 | 10.301 | 37.78
2022-01-26 01:30 | 44587.0625 | 0 | 10.0309 | 37.78
2022-01-26 02:00 | 44587.0833 | 0 | 9.8589 | 37.78
2022-01-26 02:30 | 44587.1042 | 0 | 9.8012 | 37.78
2022-01-26 03:00 | 44587.125 | 0 | 9.5194 | 37.78
2022-01-26 03:30 | 44587.1458 | 0 | 9.3798 | 37.78
2022-01-26 04:00 | 44587.1667 | 0 | 9.4841 | 37.78
2022-01-26 04:30 | 44587.1875 | 0 | 9.544 | 37.78
2022-01-26 05:00 | 44587.2083 | 0 | 9.7099 | 37.78
2022-01-26 05:30 | 44587.2292 | 0 | 9.6976 | 37.78
2022-01-26 06:00 | 44587.25 | 0 | 10.331 | 37.78
2022-01-26 06:30 | 44587.2708 | 0 | 10.2336 | 37.78
2022-01-26 07:00 | 44587.2917 | 0 | 10.4265 | 37.78
2022-01-26 07:30 | 44587.3125 | 0 | 11.1111 | 37.78
2022-01-26 08:00 | 44587.3333 | 0 | 11.6758 | 37.78
2022-01-26 08:30 | 44587.3542 | 0 | 11.8503 | 37.78
2022-01-26 09:00 | 44587.375 | 0 | 10.2355 | 37.78
2022-01-26 09:30 | 44587.3958 | 0 | 11.6429 | 37.78
2022-01-26 10:00 | 44587.4167 | 0 | 13.0646 | 37.78
2022-01-26 10:30 | 44587.4375 | 0 | 12.4736 | 37.78
2022-01-26 11:00 | 44587.4583 | 0 | 11.5297 | 37.78
2022-01-26 11:30 | 44587.4792 | 0 | 12.597 | 37.78
2022-01-26 12:00 | 44587.5 | 0 | 13.6768 | 37.78
2022-01-26 12:30 | 44587.5208 | 0 | 12.8044 | 37.78
2022-01-26 13:00 | 44587.5417 | 0 | 12.3994 | 37.78
2022-01-26 13:30 | 44587.5625 | 0 | 12.6979 | 37.78
2022-01-26 14:00 | 44587.5833 | 0 | 11.7708 | 37.78
2022-01-26 14:30 | 44587.6042 | 0 | 12.6016 | 37.78
2022-01-26 15:00 | 44587.625 | 0 | 12.9446 | 37.78
2022-01-26 15:30 | 44587.6458 | 0 | 12.3945 | 37.78
2022-01-26 16:00 | 44587.6667 | 0 | 12.2134 | 37.78
2022-01-26 16:30 | 44587.6875 | 0 | 12.5645 | 37.78
2022-01-26 17:00 | 44587.7083 | 0 | 12.6053 | 37.78
2022-01-26 17:30 | 44587.7292 | 0 | 13.1492 | 37.78
2022-01-26 18:00 | 44587.75 | 0 | 13.5781 | 37.78
2022-01-26 18:30 | 44587.7708 | 0 | 13.9233 | 37.78
2022-01-26 19:00 | 44587.7917 | 0 | 13.8381 | 37.78
2022-01-26 19:30 | 44587.8125 | 0 | 13.7073 | 37.78
2022-01-26 20:00 | 44587.8333 | 0 | 13.4133 | 37.78
2022-01-26 20:30 | 44587.8542 | 0 | 12.8081 | 37.78
2022-01-26 21:00 | 44587.875 | 0 | 12.3994 | 37.78
2022-01-26 21:30 | 44587.8958 | 0 | 12.017 | 37.78
2022-01-26 22:00 | 44587.9167 | 0 | 11.5598 | 37.78
2022-01-26 22:30 | 44587.9375 | 0 | 10.8221 | 37.78
2022-01-26 23:00 | 44587.9583 | 0 | 10.2157 | 37.78
2022-01-26 23:30 | 44587.9792 | 0 | 9.7763 | 37.78
2022-01-27 | 44588 | 0 | 9.3482 | 37.78
2022-01-27 00:30 | 44588.0208 | 0 | 9.0598 | 37.78
2022-01-27 01:00 | 44588.0417 | 0 | 8.876 | 37.78
2022-01-27 01:30 | 44588.0625 | 0 | 8.7413 | 37.78
2022-01-27 02:00 | 44588.0833 | 0 | 8.6603 | 37.78
2022-01-27 02:30 | 44588.1042 | 0 | 8.6378 | 37.78
2022-01-27 03:00 | 44588.125 | 0 | 8.5285 | 37.78
2022-01-27 03:30 | 44588.1458 | 0 | 8.695 | 37.78
2022-01-27 04:00 | 44588.1667 | 0 | 8.8993 | 37.78
2022-01-27 04:30 | 44588.1875 | 0 | 9.1447 | 37.78
2022-01-27 05:00 | 44588.2083 | 0 | 9.5934 | 37.78
2022-01-27 05:30 | 44588.2292 | 0 | 9.8418 | 37.78
2022-01-27 06:00 | 44588.25 | 0 | 10.4451 | 37.78
2022-01-27 06:30 | 44588.2708 | 0 | 11.1261 | 37.78
2022-01-27 07:00 | 44588.2917 | 0 | 11.8365 | 37.78
2022-01-27 07:30 | 44588.3125 | 0 | 12.0811 | 37.78
2022-01-27 08:00 | 44588.3333 | 0 | 11.9824 | 37.78
2022-01-27 08:30 | 44588.3542 | 0 | 12.11 | 37.78
2022-01-27 09:00 | 44588.375 | 0 | 11.5432 | 37.78
2022-01-27 09:30 | 44588.3958 | 0 | 11.8927 | 37.78
2022-01-27 10:00 | 44588.4167 | 0 | 12.309 | 37.78
2022-01-27 10:30 | 44588.4375 | 0 | 12.2202 | 37.78
2022-01-27 11:00 | 44588.4583 | 0 | 12.7936 | 37.78
2022-01-27 11:30 | 44588.4792 | 0 | 13.6823 | 37.78
2022-01-27 12:00 | 44588.5 | 0 | 13.9511 | 37.78
2022-01-27 12:30 | 44588.5208 | 0 | 12.8856 | 37.78
2022-01-27 13:00 | 44588.5417 | 0 | 13.971 | 37.78
2022-01-27 13:30 | 44588.5625 | 0 | 14.3301 | 37.78
2022-01-27 14:00 | 44588.5833 | 0 | 13.9069 | 37.78
2022-01-27 14:30 | 44588.6042 | 0 | 14.4982 | 37.78
2022-01-27 15:00 | 44588.625 | 0 | 14.3761 | 37.78
2022-01-27 15:30 | 44588.6458 | 0 | 14.2721 | 37.78
2022-01-27 16:00 | 44588.6667 | 0 | 14.0613 | 37.78
2022-01-27 16:30 | 44588.6875 | 0 | 13.6836 | 37.78
2022-01-27 17:00 | 44588.7083 | 0 | 13.7262 | 37.78
2022-01-27 17:30 | 44588.7292 | 0 | 14.5572 | 37.78
2022-01-27 18:00 | 44588.75 | 0 | 14.7145 | 37.78
2022-01-27 18:30 | 44588.7708 | 0 | 15.3884 | 37.78
2022-01-27 19:00 | 44588.7917 | 0 | 15.3964 | 37.78
2022-01-27 19:30 | 44588.8125 | 0 | 15.2412 | 37.78
2022-01-27 20:00 | 44588.8333 | 0 | 15.0086 | 37.78
2022-01-27 20:30 | 44588.8542 | 0 | 14.3702 | 37.78
2022-01-27 21:00 | 44588.875 | 0 | 13.9064 | 37.78
2022-01-27 21:30 | 44588.8958 | 0 | 13.0335 | 37.78
2022-01-27 22:00 | 44588.9167 | 0 | 12.3093 | 37.78
2022-01-27 22:30 | 44588.9375 | 0 | 11.3052 | 37.78
2022-01-27 23:00 | 44588.9583 | 0 | 10.7003 | 37.78
2022-01-27 23:30 | 44588.9792 | 0 | 10.3096 | 37.78
2022-01-28 | 44589 | 0 | 9.8217 | 37.78
2022-01-28 00:30 | 44589.0208 | 0 | 9.2495 | 37.78
2022-01-28 01:00 | 44589.0417 | 0 | 9.0794 | 37.78
2022-01-28 01:30 | 44589.0625 | 0 | 8.9104 | 37.78
2022-01-28 02:00 | 44589.0833 | 0 | 8.9086 | 37.78
2022-01-28 02:30 | 44589.1042 | 0 | 9.027 | 37.78
2022-01-28 03:00 | 44589.125 | 0 | 8.6966 | 37.78
2022-01-28 03:30 | 44589.1458 | 0 | 8.6633 | 37.78
2022-01-28 04:00 | 44589.1667 | 0 | 9.0081 | 37.78
2022-01-28 04:30 | 44589.1875 | 0 | 9.2067 | 37.78
2022-01-28 05:00 | 44589.2083 | 0 | 9.6261 | 37.78
2022-01-28 05:30 | 44589.2292 | 0 | 10.0903 | 37.78
2022-01-28 06:00 | 44589.25 | 0 | 10.8242 | 37.78
2022-01-28 06:30 | 44589.2708 | 0 | 11.2416 | 37.78
2022-01-28 07:00 | 44589.2917 | 0 | 11.2615 | 37.78
2022-01-28 07:30 | 44589.3125 | 0 | 11.9779 | 37.78
2022-01-28 08:00 | 44589.3333 | 0 | 12.4958 | 37.78
2022-01-28 08:30 | 44589.3542 | 0 | 13.9589 | 37.78
2022-01-28 09:00 | 44589.375 | 0 | 11.9906 | 37.78
2022-01-28 09:30 | 44589.3958 | 0 | 12.3443 | 37.78
2022-01-28 10:00 | 44589.4167 | 0 | 11.5839 | 37.78
2022-01-28 10:30 | 44589.4375 | 0 | 12.2438 | 37.78
2022-01-28 11:00 | 44589.4583 | 0 | 14.0621 | 37.78
2022-01-28 11:30 | 44589.4792 | 0 | 13.7546 | 37.78
2022-01-28 12:00 | 44589.5 | 0 | 13.9624 | 37.78
2022-01-28 12:30 | 44589.5208 | 0 | 13.2742 | 37.78
2022-01-28 13:00 | 44589.5417 | 0 | 12.9995 | 37.78
2022-01-28 13:30 | 44589.5625 | 0 | 13.5186 | 37.78
2022-01-28 14:00 | 44589.5833 | 0 | 14.2937 | 37.78
2022-01-28 14:30 | 44589.6042 | 0 | 14.4148 | 37.78
2022-01-28 15:00 | 44589.625 | 0 | 14.0105 | 37.78
2022-01-28 15:30 | 44589.6458 | 0 | 15.0604 | 37.78
2022-01-28 16:00 | 44589.6667 | 0 | 15.3193 | 37.78
2022-01-28 16:30 | 44589.6875 | 0 | 15.4939 | 37.78
2022-01-28 17:00 | 44589.7083 | 0 | 14.9308 | 37.78
2022-01-28 17:30 | 44589.7292 | 0 | 15.5079 | 37.78
2022-01-28 18:00 | 44589.75 | 0 | 15.1092 | 37.78
2022-01-28 18:30 | 44589.7708 | 0 | 15.4773 | 37.78
2022-01-28 19:00 | 44589.7917 | 0 | 15.4634 | 37.78
2022-01-28 19:30 | 44589.8125 | 0 | 14.9331 | 37.78
2022-01-28 20:00 | 44589.8333 | 0 | 14.6839 | 37.78
2022-01-28 20:30 | 44589.8542 | 0 | 13.9443 | 37.78
2022-01-28 21:00 | 44589.875 | 0 | 13.345 | 37.78
2022-01-28 21:30 | 44589.8958 | 0 | 12.9677 | 37.78
2022-01-28 22:00 | 44589.9167 | 0 | 12.6513 | 37.78
2022-01-28 22:30 | 44589.9375 | 0 | 11.7696 | 37.78
2022-01-28 23:00 | 44589.9583 | 0 | 11.1073 | 37.78
2022-01-28 23:30 | 44589.9792 | 0 | 10.533 | 37.78
2022-01-29 | 44590 | 0 | 10.0463 | 37.78
2022-01-29 00:30 | 44590.0208 | 0 | 9.4833 | 37.78
2022-01-29 01:00 | 44590.0417 | 0 | 9.2196 | 37.78
2022-01-29 01:30 | 44590.0625 | 0 | 9.0991 | 37.78
2022-01-29 02:00 | 44590.0833 | 0 | 8.9877 | 37.78
2022-01-29 02:30 | 44590.1042 | 0 | 8.8506 | 37.78
2022-01-29 03:00 | 44590.125 | 0 | 8.6605 | 37.78
2022-01-29 03:30 | 44590.1458 | 0 | 8.7173 | 37.78
2022-01-29 04:00 | 44590.1667 | 0 | 8.819 | 37.78
2022-01-29 04:30 | 44590.1875 | 0 | 8.7147 | 37.78
2022-01-29 05:00 | 44590.2083 | 0 | 8.8665 | 37.78
2022-01-29 05:30 | 44590.2292 | 0 | 9.0418 | 37.78
2022-01-29 06:00 | 44590.25 | 0 | 9.333 | 37.78
2022-01-29 06:30 | 44590.2708 | 0 | 9.2807 | 37.78
2022-01-29 07:00 | 44590.2917 | 0 | 8.9846 | 37.78
2022-01-29 07:30 | 44590.3125 | 0 | 8.8492 | 37.78
2022-01-29 08:00 | 44590.3333 | 0 | 9.7715 | 37.78
2022-01-29 08:30 | 44590.3542 | 0 | 8.8114 | 37.78
2022-01-29 09:00 | 44590.375 | 0 | 10.7751 | 37.78
2022-01-29 09:30 | 44590.3958 | 0 | 11.0602 | 37.78
2022-01-29 10:00 | 44590.4167 | 0 | 10.8526 | 37.78
2022-01-29 10:30 | 44590.4375 | 0 | 10.6393 | 37.78
2022-01-29 11:00 | 44590.4583 | 0 | 10.6065 | 37.78
2022-01-29 11:30 | 44590.4792 | 0 | 10.127 | 37.78
2022-01-29 12:00 | 44590.5 | 0 | 11.1762 | 37.78
2022-01-29 12:30 | 44590.5208 | 0 | 11.8704 | 37.78
2022-01-29 13:00 | 44590.5417 | 0 | 11.2466 | 37.78
2022-01-29 13:30 | 44590.5625 | 0 | 10.5005 | 37.78
2022-01-29 14:00 | 44590.5833 | 0 | 12.3377 | 37.78
2022-01-29 14:30 | 44590.6042 | 0 | 11.3486 | 37.78
2022-01-29 15:00 | 44590.625 | 0 | 13.6927 | 37.78
2022-01-29 15:30 | 44590.6458 | 0 | 13.4679 | 37.78
2022-01-29 16:00 | 44590.6667 | 0 | 13.372 | 37.78
2022-01-29 16:30 | 44590.6875 | 0 | 14.8894 | 37.78
2022-01-29 17:00 | 44590.7083 | 0 | 14.7023 | 37.78
2022-01-29 17:30 | 44590.7292 | 0 | 14.9044 | 37.78
2022-01-29 18:00 | 44590.75 | 0 | 15.2557 | 37.78
2022-01-29 18:30 | 44590.7708 | 0 | 15.5666 | 37.78
2022-01-29 19:00 | 44590.7917 | 0 | 15.4024 | 37.78
2022-01-29 19:30 | 44590.8125 | 0 | 14.9702 | 37.78
2022-01-29 20:00 | 44590.8333 | 0 | 14.3821 | 37.78
2022-01-29 20:30 | 44590.8542 | 0 | 13.7992 | 37.78
2022-01-29 21:00 | 44590.875 | 0 | 13.545 | 37.78
2022-01-29 21:30 | 44590.8958 | 0 | 12.9996 | 37.78
2022-01-29 22:00 | 44590.9167 | 0 | 12.5345 | 37.78
2022-01-29 22:30 | 44590.9375 | 0 | 11.742 | 37.78
2022-01-29 23:00 | 44590.9583 | 0 | 11.0097 | 37.78
2022-01-29 23:30 | 44590.9792 | 0 | 10.4581 | 37.78
2022-01-30 | 44591 | 0 | 9.7688 | 37.78
2022-01-30 00:30 | 44591.0208 | 0 | 9.2834 | 37.78
2022-01-30 01:00 | 44591.0417 | 0 | 9.0676 | 37.78
2022-01-30 01:30 | 44591.0625 | 0 | 8.8757 | 37.78
2022-01-30 02:00 | 44591.0833 | 0 | 8.7367 | 37.78
2022-01-30 02:30 | 44591.1042 | 0 | 8.5855 | 37.78
2022-01-30 03:00 | 44591.125 | 0 | 8.4386 | 37.78
2022-01-30 03:30 | 44591.1458 | 0 | 8.3328 | 37.78
2022-01-30 04:00 | 44591.1667 | 0 | 8.3025 | 37.78
2022-01-30 04:30 | 44591.1875 | 0 | 8.2455 | 37.78
2022-01-30 05:00 | 44591.2083 | 0 | 8.3521 | 37.78
2022-01-30 05:30 | 44591.2292 | 0 | 8.2407 | 37.78
2022-01-30 06:00 | 44591.25 | 0 | 8.2257 | 37.78
2022-01-30 06:30 | 44591.2708 | 0 | 8.099 | 37.78
2022-01-30 07:00 | 44591.2917 | 0 | 8.1391 | 37.78
2022-01-30 07:30 | 44591.3125 | 0 | 7.9927 | 37.78
2022-01-30 08:00 | 44591.3333 | 0 | 8.4079 | 37.78
2022-01-30 08:30 | 44591.3542 | 0 | 9.1989 | 37.78
2022-01-30 09:00 | 44591.375 | 0 | 9.8426 | 37.78
2022-01-30 09:30 | 44591.3958 | 0 | 10.1308 | 37.78
2022-01-30 10:00 | 44591.4167 | 0 | 11.0956 | 37.78
2022-01-30 10:30 | 44591.4375 | 0 | 11.6883 | 37.78
2022-01-30 11:00 | 44591.4583 | 0 | 11.9863 | 37.78
2022-01-30 11:30 | 44591.4792 | 0 | 11.3119 | 37.78
2022-01-30 12:00 | 44591.5 | 0 | 12.3711 | 37.78
2022-01-30 12:30 | 44591.5208 | 0 | 12.5708 | 37.78
2022-01-30 13:00 | 44591.5417 | 0 | 11.2408 | 37.78
2022-01-30 13:30 | 44591.5625 | 0 | 11.6829 | 37.78
2022-01-30 14:00 | 44591.5833 | 0 | 12.0093 | 37.78
2022-01-30 14:30 | 44591.6042 | 0 | 13.3152 | 37.78
2022-01-30 15:00 | 44591.625 | 0 | 14.4122 | 37.78
2022-01-30 15:30 | 44591.6458 | 0 | 15.2831 | 37.78
2022-01-30 16:00 | 44591.6667 | 0 | 15.4881 | 37.78
2022-01-30 16:30 | 44591.6875 | 0 | 15.6333 | 37.78
2022-01-30 17:00 | 44591.7083 | 0 | 16.4515 | 37.78
2022-01-30 17:30 | 44591.7292 | 0 | 17.1858 | 37.78
2022-01-30 18:00 | 44591.75 | 0 | 17.8238 | 37.78
2022-01-30 18:30 | 44591.7708 | 0 | 17.9328 | 37.78
2022-01-30 19:00 | 44591.7917 | 0 | 17.7788 | 37.78
2022-01-30 19:30 | 44591.8125 | 0 | 17.6903 | 37.78
2022-01-30 20:00 | 44591.8333 | 0 | 17.2751 | 37.78
2022-01-30 20:30 | 44591.8542 | 0 | 16.6843 | 37.78
2022-01-30 21:00 | 44591.875 | 0 | 16.0091 | 37.78
2022-01-30 21:30 | 44591.8958 | 0 | 15.378 | 37.78
2022-01-30 22:00 | 44591.9167 | 0 | 14.4842 | 37.78
2022-01-30 22:30 | 44591.9375 | 0 | 13.3556 | 37.78
2022-01-30 23:00 | 44591.9583 | 0 | 12.673 | 37.78
2022-01-30 23:30 | 44591.9792 | 0 | 11.9503 | 37.78
2022-01-31 | 44592 | 0 | 11.3785 | 37.78
2022-01-31 00:30 | 44592.0208 | 0 | 10.8281 | 37.78
2022-01-31 01:00 | 44592.0417 | 0 | 10.5231 | 37.78
2022-01-31 01:30 | 44592.0625 | 0 | 10.1442 | 37.78
2022-01-31 02:00 | 44592.0833 | 0 | 9.9207 | 37.78
2022-01-31 02:30 | 44592.1042 | 0 | 9.7938 | 37.78
2022-01-31 03:00 | 44592.125 | 0 | 9.7544 | 37.78
2022-01-31 03:30 | 44592.1458 | 0 | 9.7425 | 37.78
2022-01-31 04:00 | 44592.1667 | 0 | 9.926 | 37.78
2022-01-31 04:30 | 44592.1875 | 0 | 10.1981 | 37.78
2022-01-31 05:00 | 44592.2083 | 0 | 10.7651 | 37.78
2022-01-31 05:30 | 44592.2292 | 0 | 11.0678 | 37.78
2022-01-31 06:00 | 44592.25 | 0 | 11.8256 | 37.78
2022-01-31 06:30 | 44592.2708 | 0 | 12.4502 | 37.78
2022-01-31 07:00 | 44592.2917 | 0 | 13.1972 | 37.78
2022-01-31 07:30 | 44592.3125 | 0 | 13.6877 | 37.78
2022-01-31 08:00 | 44592.3333 | 0 | 14.4468 | 37.78
2022-01-31 08:30 | 44592.3542 | 0 | 14.916 | 37.78
2022-01-31 09:00 | 44592.375 | 0 | 15.4989 | 37.78
2022-01-31 09:30 | 44592.3958 | 0 | 16.2483 | 37.78
2022-01-31 10:00 | 44592.4167 | 0 | 16.2919 | 37.78
2022-01-31 10:30 | 44592.4375 | 0 | 16.5474 | 37.78
2022-01-31 11:00 | 44592.4583 | 0 | 16.6043 | 37.78
2022-01-31 11:30 | 44592.4792 | 0 | 18.6076 | 37.78
2022-01-31 12:00 | 44592.5 | 0 | 17.6431 | 37.78
2022-01-31 12:30 | 44592.5208 | 0 | 17.993 | 37.78
2022-01-31 13:00 | 44592.5417 | 0 | 17.97 | 37.78
2022-01-31 13:30 | 44592.5625 | 0 | 18.9345 | 37.78
2022-01-31 14:00 | 44592.5833 | 0 | 19.1193 | 37.78
2022-01-31 14:30 | 44592.6042 | 0 | 19.523 | 37.78
2022-01-31 15:00 | 44592.625 | 0 | 19.9465 | 37.78
2022-01-31 15:30 | 44592.6458 | 0 | 20.4546 | 37.78
2022-01-31 16:00 | 44592.6667 | 0 | 20.8197 | 37.78
2022-01-31 16:30 | 44592.6875 | 0 | 21.5769 | 37.78
2022-01-31 17:00 | 44592.7083 | 0 | 21.8363 | 37.78
2022-01-31 17:30 | 44592.7292 | 0 | 22.0437 | 37.78
2022-01-31 18:00 | 44592.75 | 0 | 22.2055 | 37.78
2022-01-31 18:30 | 44592.7708 | 0 | 22.1828 | 37.78
2022-01-31 19:00 | 44592.7917 | 0 | 21.7669 | 37.78
2022-01-31 19:30 | 44592.8125 | 0 | 21.7365 | 37.78
2022-01-31 20:00 | 44592.8333 | 0 | 20.8702 | 37.78
2022-01-31 20:30 | 44592.8542 | 0 | 20.0221 | 37.78
2022-01-31 21:00 | 44592.875 | 0 | 18.8564 | 37.78
2022-01-31 21:30 | 44592.8958 | 0 | 17.7755 | 37.78
2022-01-31 22:00 | 44592.9167 | 0 | 16.6468 | 37.78
2022-01-31 22:30 | 44592.9375 | 0 | 15.3245 | 37.78
2022-01-31 23:00 | 44592.9583 | 0 | 14.2462 | 37.78
2022-01-31 23:30 | 44592.9792 | 0 | 13.583 | 37.78
2022-02-01 | 44593 | 0 | 12.8362 | 37.78
2022-02-01 00:30 | 44593.0208 | 0 | 12.4168 | 37.78
2022-02-01 01:00 | 44593.0417 | 0 | 12.0841 | 37.78
2022-02-01 01:30 | 44593.0625 | 0 | 11.8085 | 37.78
2022-02-01 02:00 | 44593.0833 | 0 | 11.4735 | 37.78
2022-02-01 02:30 | 44593.1042 | 0 | 11.466 | 37.78
2022-02-01 03:00 | 44593.125 | 0 | 11.3103 | 37.78
2022-02-01 03:30 | 44593.1458 | 0 | 11.283 | 37.78
2022-02-01 04:00 | 44593.1667 | 0 | 11.4999 | 37.78
2022-02-01 04:30 | 44593.1875 | 0 | 12.0911 | 37.78
2022-02-01 05:00 | 44593.2083 | 0 | 12.3157 | 37.78
2022-02-01 05:30 | 44593.2292 | 0 | 12.6085 | 37.78
2022-02-01 06:00 | 44593.25 | 0 | 13.2726 | 37.78
2022-02-01 06:30 | 44593.2708 | 0 | 14.1911 | 37.78
2022-02-01 07:00 | 44593.2917 | 0 | 15.4419 | 37.78
2022-02-01 07:30 | 44593.3125 | 0 | 16.0777 | 37.78
2022-02-01 08:00 | 44593.3333 | 0 | 17.0917 | 37.78
2022-02-01 08:30 | 44593.3542 | 0 | 17.8222 | 37.78
2022-02-01 09:00 | 44593.375 | 0 | 18.8548 | 37.78
2022-02-01 09:30 | 44593.3958 | 0 | 18.9636 | 37.78
2022-02-01 10:00 | 44593.4167 | 0 | 18.6774 | 37.78
2022-02-01 10:30 | 44593.4375 | 0 | 19.6026 | 37.78
2022-02-01 11:00 | 44593.4583 | 0 | 20.2234 | 37.78
2022-02-01 11:30 | 44593.4792 | 0 | 20.9413 | 37.78
2022-02-01 12:00 | 44593.5 | 0 | 21.1776 | 37.78
2022-02-01 12:30 | 44593.5208 | 0 | 21.8063 | 37.78
2022-02-01 13:00 | 44593.5417 | 0 | 22.4334 | 37.78
2022-02-01 13:30 | 44593.5625 | 0 | 24.1307 | 37.78
2022-02-01 14:00 | 44593.5833 | 0 | 24.8011 | 37.78
2022-02-01 14:30 | 44593.6042 | 0 | 24.9238 | 37.78
2022-02-01 15:00 | 44593.625 | 0 | 21.8311 | 37.78
2022-02-01 15:30 | 44593.6458 | 0 | 23.0602 | 37.78
2022-02-01 16:00 | 44593.6667 | 0 | 23.4959 | 37.78
2022-02-01 16:30 | 44593.6875 | 0 | 23.3136 | 37.78
2022-02-01 17:00 | 44593.7083 | 0 | 23.9011 | 37.78
2022-02-01 17:30 | 44593.7292 | 0 | 24.0898 | 37.78
2022-02-01 18:00 | 44593.75 | 0 | 24.2262 | 37.78
2022-02-01 18:30 | 44593.7708 | 0 | 24.3396 | 37.78
2022-02-01 19:00 | 44593.7917 | 0 | 24.0701 | 37.78
2022-02-01 19:30 | 44593.8125 | 0 | 23.9309 | 37.78
2022-02-01 20:00 | 44593.8333 | 0 | 23.0604 | 37.78
2022-02-01 20:30 | 44593.8542 | 0 | 22.5699 | 37.78
2022-02-01 21:00 | 44593.875 | 0 | 22.538 | 37.78
2022-02-01 21:30 | 44593.8958 | 0 | 20.9821 | 37.78
2022-02-01 22:00 | 44593.9167 | 0 | 19.0888 | 37.78
2022-02-01 22:30 | 44593.9375 | 0 | 17.6176 | 37.78
2022-02-01 23:00 | 44593.9583 | 0 | 16.4793 | 37.78
2022-02-01 23:30 | 44593.9792 | 0 | 15.8028 | 37.78
2022-02-02 | 44594 | 0 | 14.9667 | 37.78
2022-02-02 00:30 | 44594.0208 | 0 | 14.1104 | 37.78
2022-02-02 01:00 | 44594.0417 | 0 | 13.7292 | 37.78
2022-02-02 01:30 | 44594.0625 | 0 | 13.2486 | 37.78
2022-02-02 02:00 | 44594.0833 | 0 | 12.8641 | 37.78
2022-02-02 02:30 | 44594.1042 | 0 | 12.8283 | 37.78
2022-02-02 03:00 | 44594.125 | 0 | 12.4234 | 37.78
2022-02-02 03:30 | 44594.1458 | 0 | 12.263 | 37.78
2022-02-02 04:00 | 44594.1667 | 0 | 12.4356 | 37.78
2022-02-02 04:30 | 44594.1875 | 0 | 12.911 | 37.78
2022-02-02 05:00 | 44594.2083 | 0 | 13.5194 | 37.78
2022-02-02 05:30 | 44594.2292 | 0 | 13.9801 | 37.78
2022-02-02 06:00 | 44594.25 | 0 | 14.6829 | 37.78
2022-02-02 06:30 | 44594.2708 | 0 | 15.5144 | 37.78
2022-02-02 07:00 | 44594.2917 | 0 | 16.7496 | 37.78
2022-02-02 07:30 | 44594.3125 | 0 | 17.6084 | 37.78
2022-02-02 08:00 | 44594.3333 | 0 | 18.0694 | 37.78
2022-02-02 08:30 | 44594.3542 | 0 | 19.3969 | 37.78
2022-02-02 09:00 | 44594.375 | 0 | 20.3681 | 37.78
2022-02-02 09:30 | 44594.3958 | 0 | 20.3786 | 37.78
2022-02-02 10:00 | 44594.4167 | 0 | 21.07 | 37.78
2022-02-02 10:30 | 44594.4375 | 0 | 21.9257 | 37.78
2022-02-02 11:00 | 44594.4583 | 0 | 22.9364 | 37.78
2022-02-02 11:30 | 44594.4792 | 0 | 24.7736 | 37.78
2022-02-02 12:00 | 44594.5 | 0 | 25.3598 | 37.78
2022-02-02 12:30 | 44594.5208 | 0 | 26.4855 | 37.78
2022-02-02 13:00 | 44594.5417 | 0 | 25.1037 | 37.78
2022-02-02 13:30 | 44594.5625 | 0 | 24.832 | 37.78
2022-02-02 14:00 | 44594.5833 | 0 | 25.6772 | 37.78
2022-02-02 14:30 | 44594.6042 | 0 | 26.2911 | 37.78
2022-02-02 15:00 | 44594.625 | 0 | 23.4183 | 37.78
2022-02-02 15:30 | 44594.6458 | 0 | 20.8836 | 37.78
2022-02-02 16:00 | 44594.6667 | 0 | 20.0939 | 37.78
2022-02-02 16:30 | 44594.6875 | 0 | 20.3943 | 37.78
2022-02-02 17:00 | 44594.7083 | 0 | 20.0173 | 37.78
2022-02-02 17:30 | 44594.7292 | 0 | 20.3566 | 37.78
2022-02-02 18:00 | 44594.75 | 0 | 20.5386 | 37.78
2022-02-02 18:30 | 44594.7708 | 0 | 20.757 | 37.78
2022-02-02 19:00 | 44594.7917 | 0 | 20.56 | 37.78
2022-02-02 19:30 | 44594.8125 | 0 | 20.1533 | 37.78
2022-02-02 20:00 | 44594.8333 | 0 | 20.0806 | 37.78
2022-02-02 20:30 | 44594.8542 | 0 | 19.6209 | 37.78
2022-02-02 21:00 | 44594.875 | 0 | 18.5359 | 37.78
2022-02-02 21:30 | 44594.8958 | 0 | 17.6502 | 37.78
2022-02-02 22:00 | 44594.9167 | 0 | 16.3836 | 37.78
2022-02-02 22:30 | 44594.9375 | 0 | 15.3237 | 37.78
2022-02-02 23:00 | 44594.9583 | 0 | 14.4832 | 37.78
2022-02-02 23:30 | 44594.9792 | 0 | 13.9074 | 37.78
2022-02-03 | 44595 | 0 | 13.2088 | 37.78
2022-02-03 00:30 | 44595.0208 | 0 | 12.4874 | 37.78
2022-02-03 01:00 | 44595.0417 | 0 | 12.0604 | 37.78
2022-02-03 01:30 | 44595.0625 | 0 | 11.7288 | 37.78
2022-02-03 02:00 | 44595.0833 | 0 | 11.6408 | 37.78
2022-02-03 02:30 | 44595.1042 | 0 | 11.7069 | 37.78
2022-02-03 03:00 | 44595.125 | 0 | 11.5199 | 37.78
2022-02-03 03:30 | 44595.1458 | 0 | 11.3497 | 37.78
2022-02-03 04:00 | 44595.1667 | 0 | 11.6177 | 37.78
2022-02-03 04:30 | 44595.1875 | 0 | 12.2843 | 37.78
2022-02-03 05:00 | 44595.2083 | 0 | 12.8326 | 37.78
2022-02-03 05:30 | 44595.2292 | 0 | 13.162 | 37.78
2022-02-03 06:00 | 44595.25 | 0 | 13.9679 | 37.78
2022-02-03 06:30 | 44595.2708 | 0 | 14.7406 | 37.78
2022-02-03 07:00 | 44595.2917 | 0 | 15.9664 | 37.78
2022-02-03 07:30 | 44595.3125 | 0 | 16.4418 | 37.78
2022-02-03 08:00 | 44595.3333 | 0 | 16.885 | 37.78
2022-02-03 08:30 | 44595.3542 | 0 | 17.7113 | 37.78
2022-02-03 09:00 | 44595.375 | 0 | 17.3173 | 37.78
2022-02-03 09:30 | 44595.3958 | 0 | 17.7061 | 37.78
2022-02-03 10:00 | 44595.4167 | 0 | 18.9812 | 37.78
2022-02-03 10:30 | 44595.4375 | 0 | 21.6686 | 37.78
2022-02-03 11:00 | 44595.4583 | 0 | 21.2863 | 37.78
2022-02-03 11:30 | 44595.4792 | 0 | 19.8203 | 37.78
2022-02-03 12:00 | 44595.5 | 0 | 20.2898 | 37.78
2022-02-03 12:30 | 44595.5208 | 0 | 21.0265 | 37.78
2022-02-03 13:00 | 44595.5417 | 0 | 20.2912 | 37.78
2022-02-03 13:30 | 44595.5625 | 0 | 19.6328 | 37.78
2022-02-03 14:00 | 44595.5833 | 0 | 19.6907 | 37.78
2022-02-03 14:30 | 44595.6042 | 0 | 20.1235 | 37.78
2022-02-03 15:00 | 44595.625 | 0 | 18.9878 | 37.78
2022-02-03 15:30 | 44595.6458 | 0 | 18.4286 | 37.78
2022-02-03 16:00 | 44595.6667 | 0 | 17.3997 | 37.78
2022-02-03 16:30 | 44595.6875 | 0 | 17.019 | 37.78
2022-02-03 17:00 | 44595.7083 | 0 | 16.4771 | 37.78
2022-02-03 17:30 | 44595.7292 | 0 | 16.2827 | 37.78
2022-02-03 18:00 | 44595.75 | 0 | 15.921 | 37.78
2022-02-03 18:30 | 44595.7708 | 0 | 16.1039 | 37.78
2022-02-03 19:00 | 44595.7917 | 0 | 15.9677 | 37.78
2022-02-03 19:30 | 44595.8125 | 0 | 15.6026 | 37.78
2022-02-03 20:00 | 44595.8333 | 0 | 15.0664 | 37.78
2022-02-03 20:30 | 44595.8542 | 0 | 14.5102 | 37.78
2022-02-03 21:00 | 44595.875 | 0 | 13.9275 | 37.78
2022-02-03 21:30 | 44595.8958 | 0 | 13.132 | 37.78
2022-02-03 22:00 | 44595.9167 | 0 | 11.3153 | 37.78
2022-02-03 22:30 | 44595.9375 | 0 | 10.6822 | 37.78
2022-02-03 23:00 | 44595.9583 | 0 | 10.4684 | 37.78
2022-02-03 23:30 | 44595.9792 | 0 | 9.9907 | 37.78
2022-02-04 | 44596 | 0 | 10.2074 | 37.78
2022-02-04 00:30 | 44596.0208 | 0 | 9.7959 | 37.78
2022-02-04 01:00 | 44596.0417 | 0 | 9.5213 | 37.78
2022-02-04 01:30 | 44596.0625 | 0 | 9.256 | 37.78
2022-02-04 02:00 | 44596.0833 | 0 | 9.2427 | 37.78
2022-02-04 02:30 | 44596.1042 | 0 | 9.1064 | 37.78
2022-02-04 03:00 | 44596.125 | 0 | 8.8678 | 37.78
2022-02-04 03:30 | 44596.1458 | 0 | 8.74 | 37.78
2022-02-04 04:00 | 44596.1667 | 0 | 9.0531 | 37.78
2022-02-04 04:30 | 44596.1875 | 0 | 9.5264 | 37.78
2022-02-04 05:00 | 44596.2083 | 0 | 9.9741 | 37.78
2022-02-04 05:30 | 44596.2292 | 0 | 10.5365 | 37.78
2022-02-04 06:00 | 44596.25 | 0 | 10.8498 | 37.78
2022-02-04 06:30 | 44596.2708 | 0 | 11.1939 | 37.78
2022-02-04 07:00 | 44596.2917 | 0 | 11.5417 | 37.78
2022-02-04 07:30 | 44596.3125 | 0 | 11.4416 | 37.78
2022-02-04 08:00 | 44596.3333 | 0 | 11.459 | 37.78
2022-02-04 08:30 | 44596.3542 | 0 | 11.2723 | 37.78
2022-02-04 09:00 | 44596.375 | 0 | 12.026 | 37.78
2022-02-04 09:30 | 44596.3958 | 0 | 12.0664 | 37.78
2022-02-04 10:00 | 44596.4167 | 0 | 13.1908 | 37.78
2022-02-04 10:30 | 44596.4375 | 0 | 13.9081 | 37.78
2022-02-04 11:00 | 44596.4583 | 0 | 14.6245 | 37.78
2022-02-04 11:30 | 44596.4792 | 0 | 11.9508 | 37.78
2022-02-04 12:00 | 44596.5 | 0 | 12.8288 | 37.78
2022-02-04 12:30 | 44596.5208 | 0 | 13.5651 | 37.78
2022-02-04 13:00 | 44596.5417 | 0 | 13.6011 | 37.78
2022-02-04 13:30 | 44596.5625 | 0 | 13.8921 | 37.78
2022-02-04 14:00 | 44596.5833 | 0 | 12.1478 | 37.78
2022-02-04 14:30 | 44596.6042 | 0 | 13.3102 | 37.78
2022-02-04 15:00 | 44596.625 | 0 | 13.4447 | 37.78
2022-02-04 15:30 | 44596.6458 | 0 | 13.6874 | 37.78
2022-02-04 16:00 | 44596.6667 | 0 | 13.402 | 37.78
2022-02-04 16:30 | 44596.6875 | 0 | 14.3288 | 37.78
2022-02-04 17:00 | 44596.7083 | 0 | 13.8565 | 37.78
2022-02-04 17:30 | 44596.7292 | 0 | 13.8165 | 37.78
2022-02-04 18:00 | 44596.75 | 0 | 13.8439 | 37.78
2022-02-04 18:30 | 44596.7708 | 0 | 14.0977 | 37.78
2022-02-04 19:00 | 44596.7917 | 0 | 14.1528 | 37.78
2022-02-04 19:30 | 44596.8125 | 0 | 13.9975 | 37.78
2022-02-04 20:00 | 44596.8333 | 0 | 13.4847 | 37.78
2022-02-04 20:30 | 44596.8542 | 0 | 13.0634 | 37.78
2022-02-04 21:00 | 44596.875 | 0 | 12.4916 | 37.78
2022-02-04 21:30 | 44596.8958 | 0 | 12.0778 | 37.78
2022-02-04 22:00 | 44596.9167 | 0 | 11.6959 | 37.78
2022-02-04 22:30 | 44596.9375 | 0 | 10.9867 | 37.78
2022-02-04 23:00 | 44596.9583 | 0 | 10.5097 | 37.78
2022-02-04 23:30 | 44596.9792 | 0 | 10.0489 | 37.78
2022-02-05 | 44597 | 0 | 9.4853 | 37.78
2022-02-05 00:30 | 44597.0208 | 0 | 9.0269 | 37.78
2022-02-05 01:00 | 44597.0417 | 0 | 8.7419 | 37.78
2022-02-05 01:30 | 44597.0625 | 0 | 8.5906 | 37.78
2022-02-05 02:00 | 44597.0833 | 0 | 8.5281 | 37.78
2022-02-05 02:30 | 44597.1042 | 0 | 8.4698 | 37.78
2022-02-05 03:00 | 44597.125 | 0 | 8.2474 | 37.78
2022-02-05 03:30 | 44597.1458 | 0 | 8.1718 | 37.78
2022-02-05 04:00 | 44597.1667 | 0 | 8.2509 | 37.78
2022-02-05 04:30 | 44597.1875 | 0 | 8.3377 | 37.78
2022-02-05 05:00 | 44597.2083 | 0 | 8.5439 | 37.78
2022-02-05 05:30 | 44597.2292 | 0 | 8.6429 | 37.78
2022-02-05 06:00 | 44597.25 | 0 | 8.5407 | 37.78
2022-02-05 06:30 | 44597.2708 | 0 | 8.3913 | 37.78
2022-02-05 07:00 | 44597.2917 | 0 | 8.2033 | 37.78
2022-02-05 07:30 | 44597.3125 | 0 | 7.9474 | 37.78
2022-02-05 08:00 | 44597.3333 | 0 | 7.6531 | 37.78
2022-02-05 08:30 | 44597.3542 | 0 | 7.5632 | 37.78
2022-02-05 09:00 | 44597.375 | 0 | 7.5476 | 37.78
2022-02-05 09:30 | 44597.3958 | 0 | 9.6823 | 37.78
2022-02-05 10:00 | 44597.4167 | 0 | 8.8991 | 37.78
2022-02-05 10:30 | 44597.4375 | 0 | 8.7863 | 37.78
2022-02-05 11:00 | 44597.4583 | 0 | 9.5922 | 37.78
2022-02-05 11:30 | 44597.4792 | 0 | 9.3572 | 37.78
2022-02-05 12:00 | 44597.5 | 0 | 9.463 | 37.78
2022-02-05 12:30 | 44597.5208 | 0 | 7.5156 | 37.78
2022-02-05 13:00 | 44597.5417 | 0 | 8.7722 | 37.78
2022-02-05 13:30 | 44597.5625 | 0 | 9.584 | 37.78
2022-02-05 14:00 | 44597.5833 | 0 | 7.7669 | 37.78
2022-02-05 14:30 | 44597.6042 | 0 | 10.1328 | 37.78
2022-02-05 15:00 | 44597.625 | 0 | 9.8652 | 37.78
2022-02-05 15:30 | 44597.6458 | 0 | 9.9777 | 37.78
2022-02-05 16:00 | 44597.6667 | 0 | 10.0845 | 37.78
2022-02-05 16:30 | 44597.6875 | 0 | 11.6251 | 37.78
2022-02-05 17:00 | 44597.7083 | 0 | 11.1775 | 37.78
2022-02-05 17:30 | 44597.7292 | 0 | 11.8773 | 37.78
2022-02-05 18:00 | 44597.75 | 0 | 11.7946 | 37.78
2022-02-05 18:30 | 44597.7708 | 0 | 12.2215 | 37.78
2022-02-05 19:00 | 44597.7917 | 0 | 12.2504 | 37.78
2022-02-05 19:30 | 44597.8125 | 0 | 12.0885 | 37.78
2022-02-05 20:00 | 44597.8333 | 0 | 11.7315 | 37.78
2022-02-05 20:30 | 44597.8542 | 0 | 11.4254 | 37.78
2022-02-05 21:00 | 44597.875 | 0 | 11.0737 | 37.78
2022-02-05 21:30 | 44597.8958 | 0 | 10.7023 | 37.78
2022-02-05 22:00 | 44597.9167 | 0 | 10.4429 | 37.78
2022-02-05 22:30 | 44597.9375 | 0 | 9.7597 | 37.78
2022-02-05 23:00 | 44597.9583 | 0 | 9.2532 | 37.78
2022-02-05 23:30 | 44597.9792 | 0 | 8.8306 | 37.78
2022-02-06 | 44598 | 0 | 8.5183 | 37.78
2022-02-06 00:30 | 44598.0208 | 0 | 8.1861 | 37.78
2022-02-06 01:00 | 44598.0417 | 0 | 8.0792 | 37.78
2022-02-06 01:30 | 44598.0625 | 0 | 7.9236 | 37.78
2022-02-06 02:00 | 44598.0833 | 0 | 7.883 | 37.78
2022-02-06 02:30 | 44598.1042 | 0 | 7.8017 | 37.78
2022-02-06 03:00 | 44598.125 | 0 | 7.7838 | 37.78
2022-02-06 03:30 | 44598.1458 | 0 | 7.722 | 37.78
2022-02-06 04:00 | 44598.1667 | 0 | 7.6352 | 37.78
2022-02-06 04:30 | 44598.1875 | 0 | 7.6927 | 37.78
2022-02-06 05:00 | 44598.2083 | 0 | 7.7841 | 37.78
2022-02-06 05:30 | 44598.2292 | 0 | 7.7918 | 37.78
2022-02-06 06:00 | 44598.25 | 0 | 7.8861 | 37.78
2022-02-06 06:30 | 44598.2708 | 0 | 7.5609 | 37.78
2022-02-06 07:00 | 44598.2917 | 0 | 7.2678 | 37.78
2022-02-06 07:30 | 44598.3125 | 0 | 7.0142 | 37.78
2022-02-06 08:00 | 44598.3333 | 0 | 6.965 | 37.78
2022-02-06 08:30 | 44598.3542 | 0 | 8.297 | 37.78
2022-02-06 09:00 | 44598.375 | 0 | 8.0688 | 37.78
2022-02-06 09:30 | 44598.3958 | 0 | 7.5469 | 37.78
2022-02-06 10:00 | 44598.4167 | 0 | 8.8911 | 37.78
2022-02-06 10:30 | 44598.4375 | 0 | 8.1817 | 37.78
2022-02-06 11:00 | 44598.4583 | 0 | 7.204 | 37.78
2022-02-06 11:30 | 44598.4792 | 0 | 8.4249 | 37.78
2022-02-06 12:00 | 44598.5 | 0 | 8.2985 | 37.78
2022-02-06 12:30 | 44598.5208 | 0 | 8.9242 | 37.78
2022-02-06 13:00 | 44598.5417 | 0 | 7.7159 | 37.78
2022-02-06 13:30 | 44598.5625 | 0 | 9.0178 | 37.78
2022-02-06 14:00 | 44598.5833 | 0 | 8.7255 | 37.78
2022-02-06 14:30 | 44598.6042 | 0 | 8.3083 | 37.78
2022-02-06 15:00 | 44598.625 | 0 | 8.1858 | 37.78
2022-02-06 15:30 | 44598.6458 | 0 | 9.4417 | 37.78
2022-02-06 16:00 | 44598.6667 | 0 | 11.2295 | 37.78
2022-02-06 16:30 | 44598.6875 | 0 | 10.6116 | 37.78
2022-02-06 17:00 | 44598.7083 | 0 | 11.4992 | 37.78
2022-02-06 17:30 | 44598.7292 | 0 | 12.3053 | 37.78
2022-02-06 18:00 | 44598.75 | 0 | 12.4421 | 37.78
2022-02-06 18:30 | 44598.7708 | 0 | 12.804 | 37.78
2022-02-06 19:00 | 44598.7917 | 0 | 12.7915 | 37.78
2022-02-06 19:30 | 44598.8125 | 0 | 12.7539 | 37.78
2022-02-06 20:00 | 44598.8333 | 0 | 12.2897 | 37.78
2022-02-06 20:30 | 44598.8542 | 0 | 11.7235 | 37.78
2022-02-06 21:00 | 44598.875 | 0 | 11.1773 | 37.78
2022-02-06 21:30 | 44598.8958 | 0 | 10.7736 | 37.78
2022-02-06 22:00 | 44598.9167 | 0 | 10.2818 | 37.78
2022-02-06 22:30 | 44598.9375 | 0 | 9.4422 | 37.78
2022-02-06 23:00 | 44598.9583 | 0 | 8.9959 | 37.78
2022-02-06 23:30 | 44598.9792 | 0 | 8.5105 | 37.78
2022-02-07 | 44599 | 0 | 8.2432 | 37.78
2022-02-07 00:30 | 44599.0208 | 0 | 8.0543 | 37.78
2022-02-07 01:00 | 44599.0417 | 0 | 7.985 | 37.78
2022-02-07 01:30 | 44599.0625 | 0 | 7.9355 | 37.78
2022-02-07 02:00 | 44599.0833 | 0 | 7.8139 | 37.78
2022-02-07 02:30 | 44599.1042 | 0 | 7.8334 | 37.78
2022-02-07 03:00 | 44599.125 | 0 | 7.655 | 37.78
2022-02-07 03:30 | 44599.1458 | 0 | 7.8518 | 37.78
2022-02-07 04:00 | 44599.1667 | 0 | 8.1206 | 37.78
2022-02-07 04:30 | 44599.1875 | 0 | 8.4991 | 37.78
2022-02-07 05:00 | 44599.2083 | 0 | 9.1269 | 37.78
2022-02-07 05:30 | 44599.2292 | 0 | 9.5667 | 37.78
2022-02-07 06:00 | 44599.25 | 0 | 10.4006 | 37.78
2022-02-07 06:30 | 44599.2708 | 0 | 10.3156 | 37.78
2022-02-07 07:00 | 44599.2917 | 0 | 10.8596 | 37.78
2022-02-07 07:30 | 44599.3125 | 0 | 10.5526 | 37.78
2022-02-07 08:00 | 44599.3333 | 0 | 11.3513 | 37.78
2022-02-07 08:30 | 44599.3542 | 0 | 11.2705 | 37.78
2022-02-07 09:00 | 44599.375 | 0 | 11.2645 | 37.78
2022-02-07 09:30 | 44599.3958 | 0 | 10.8123 | 37.78
2022-02-07 10:00 | 44599.4167 | 0 | 10.4456 | 37.78
2022-02-07 10:30 | 44599.4375 | 0 | 9.7881 | 37.78
2022-02-07 11:00 | 44599.4583 | 0 | 10.2552 | 37.78
2022-02-07 11:30 | 44599.4792 | 0 | 9.8676 | 37.78
2022-02-07 12:00 | 44599.5 | 0 | 10.1825 | 37.78
2022-02-07 12:30 | 44599.5208 | 0 | 10.1708 | 37.78
2022-02-07 13:00 | 44599.5417 | 0 | 11.3146 | 37.78
2022-02-07 13:30 | 44599.5625 | 0 | 11.7432 | 37.78
2022-02-07 14:00 | 44599.5833 | 0 | 11.9642 | 37.78
2022-02-07 14:30 | 44599.6042 | 0 | 11.7078 | 37.78
2022-02-07 15:00 | 44599.625 | 0 | 12.6736 | 37.78
2022-02-07 15:30 | 44599.6458 | 0 | 14.3997 | 37.78
2022-02-07 16:00 | 44599.6667 | 0 | 14.4794 | 37.78
2022-02-07 16:30 | 44599.6875 | 0 | 14.893 | 37.78
2022-02-07 17:00 | 44599.7083 | 0 | 13.8515 | 37.78
2022-02-07 17:30 | 44599.7292 | 0 | 14.1095 | 37.78
2022-02-07 18:00 | 44599.75 | 0 | 14.4826 | 37.78
2022-02-07 18:30 | 44599.7708 | 0 | 14.9809 | 37.78
2022-02-07 19:00 | 44599.7917 | 0 | 14.9821 | 37.78
2022-02-07 19:30 | 44599.8125 | 0 | 14.6123 | 37.78
2022-02-07 20:00 | 44599.8333 | 0 | 13.9049 | 37.78
2022-02-07 20:30 | 44599.8542 | 0 | 13.3106 | 37.78
2022-02-07 21:00 | 44599.875 | 0 | 12.536 | 37.78
2022-02-07 21:30 | 44599.8958 | 0 | 11.9672 | 37.78
2022-02-07 22:00 | 44599.9167 | 0 | 11.3337 | 37.78
2022-02-07 22:30 | 44599.9375 | 0 | 10.5287 | 37.78
2022-02-07 23:00 | 44599.9583 | 0 | 9.7941 | 37.78
2022-02-07 23:30 | 44599.9792 | 0 | 9.4635 | 37.78
2022-02-08 | 44600 | 0 | 8.9293 | 37.78
2022-02-08 00:30 | 44600.0208 | 0 | 8.6247 | 37.78
2022-02-08 01:00 | 44600.0417 | 0 | 8.4319 | 37.78
2022-02-08 01:30 | 44600.0625 | 0 | 8.2753 | 37.78
2022-02-08 02:00 | 44600.0833 | 0 | 8.0447 | 37.78
2022-02-08 02:30 | 44600.1042 | 0 | 8.082 | 37.78
2022-02-08 03:00 | 44600.125 | 0 | 7.9105 | 37.78
2022-02-08 03:30 | 44600.1458 | 0 | 7.9579 | 37.78
2022-02-08 04:00 | 44600.1667 | 0 | 8.3187 | 37.78
2022-02-08 04:30 | 44600.1875 | 0 | 8.7343 | 37.78
2022-02-08 05:00 | 44600.2083 | 0 | 9.1546 | 37.78
2022-02-08 05:30 | 44600.2292 | 0 | 9.6087 | 37.78
2022-02-08 06:00 | 44600.25 | 0 | 10.1512 | 37.78
2022-02-08 06:30 | 44600.2708 | 0 | 10.4404 | 37.78
2022-02-08 07:00 | 44600.2917 | 0 | 10.8282 | 37.78
2022-02-08 07:30 | 44600.3125 | 0 | 10.5471 | 37.78
2022-02-08 08:00 | 44600.3333 | 0 | 10.4066 | 37.78
2022-02-08 08:30 | 44600.3542 | 0 | 10.1771 | 37.78
2022-02-08 09:00 | 44600.375 | 0 | 9.8235 | 37.78
2022-02-08 09:30 | 44600.3958 | 0 | 9.5535 | 37.78
2022-02-08 10:00 | 44600.4167 | 0 | 9.7476 | 37.78
2022-02-08 10:30 | 44600.4375 | 0 | 10.9124 | 37.78
2022-02-08 11:00 | 44600.4583 | 0 | 11.2755 | 37.78
2022-02-08 11:30 | 44600.4792 | 0 | 12.4988 | 37.78
2022-02-08 12:00 | 44600.5 | 0 | 12.2157 | 37.78
2022-02-08 12:30 | 44600.5208 | 0 | 11.7133 | 37.78
2022-02-08 13:00 | 44600.5417 | 0 | 13.5989 | 37.78
2022-02-08 13:30 | 44600.5625 | 0 | 12.8669 | 37.78
2022-02-08 14:00 | 44600.5833 | 0 | 12.8609 | 37.78
2022-02-08 14:30 | 44600.6042 | 0 | 12.3325 | 37.78
2022-02-08 15:00 | 44600.625 | 0 | 12.2514 | 37.78
2022-02-08 15:30 | 44600.6458 | 0 | 13.6767 | 37.78
2022-02-08 16:00 | 44600.6667 | 0 | 13.8348 | 37.78
2022-02-08 16:30 | 44600.6875 | 0 | 14.3659 | 37.78
2022-02-08 17:00 | 44600.7083 | 0 | 14.786 | 37.78
2022-02-08 17:30 | 44600.7292 | 0 | 15.3113 | 37.78
2022-02-08 18:00 | 44600.75 | 0 | 15.5432 | 37.78
2022-02-08 18:30 | 44600.7708 | 0 | 15.8922 | 37.78
2022-02-08 19:00 | 44600.7917 | 0 | 15.8156 | 37.78
2022-02-08 19:30 | 44600.8125 | 0 | 15.3573 | 37.78
2022-02-08 20:00 | 44600.8333 | 0 | 14.8755 | 37.78
2022-02-08 20:30 | 44600.8542 | 0 | 14.0354 | 37.78
2022-02-08 21:00 | 44600.875 | 0 | 13.4443 | 37.78
2022-02-08 21:30 | 44600.8958 | 0 | 12.8815 | 37.78
2022-02-08 22:00 | 44600.9167 | 0 | 12.318 | 37.78
2022-02-08 22:30 | 44600.9375 | 0 | 11.4635 | 37.78
2022-02-08 23:00 | 44600.9583 | 0 | 10.7206 | 37.78
2022-02-08 23:30 | 44600.9792 | 0 | 10.1499 | 37.78
2022-02-09 | 44601 | 0 | 9.6729 | 37.78
2022-02-09 00:30 | 44601.0208 | 0 | 9.3753 | 37.78
2022-02-09 01:00 | 44601.0417 | 0 | 9.1413 | 37.78
2022-02-09 01:30 | 44601.0625 | 0 | 8.9849 | 37.78
2022-02-09 02:00 | 44601.0833 | 0 | 8.8131 | 37.78
2022-02-09 02:30 | 44601.1042 | 0 | 8.8196 | 37.78
2022-02-09 03:00 | 44601.125 | 0 | 8.754 | 37.78
2022-02-09 03:30 | 44601.1458 | 0 | 8.6527 | 37.78
2022-02-09 04:00 | 44601.1667 | 0 | 8.9567 | 37.78
2022-02-09 04:30 | 44601.1875 | 0 | 9.3104 | 37.78
2022-02-09 05:00 | 44601.2083 | 0 | 9.6981 | 37.78
2022-02-09 05:30 | 44601.2292 | 0 | 10.1523 | 37.78
2022-02-09 06:00 | 44601.25 | 0 | 10.8122 | 37.78
2022-02-09 06:30 | 44601.2708 | 0 | 11.2761 | 37.78
2022-02-09 07:00 | 44601.2917 | 0 | 11.6029 | 37.78
2022-02-09 07:30 | 44601.3125 | 0 | 11.5359 | 37.78
2022-02-09 08:00 | 44601.3333 | 0 | 11.3375 | 37.78
2022-02-09 08:30 | 44601.3542 | 0 | 11.1809 | 37.78
2022-02-09 09:00 | 44601.375 | 0 | 11.1964 | 37.78
2022-02-09 09:30 | 44601.3958 | 0 | 11.422 | 37.78
2022-02-09 10:00 | 44601.4167 | 0 | 12.02 | 37.78
2022-02-09 10:30 | 44601.4375 | 0 | 12.6909 | 37.78
2022-02-09 11:00 | 44601.4583 | 0 | 12.7842 | 37.78
2022-02-09 11:30 | 44601.4792 | 0 | 13.1889 | 37.78
2022-02-09 12:00 | 44601.5 | 0 | 13.8429 | 37.78
2022-02-09 12:30 | 44601.5208 | 0 | 13.0224 | 37.78
2022-02-09 13:00 | 44601.5417 | 0 | 14.1093 | 37.78
2022-02-09 13:30 | 44601.5625 | 0 | 15.0304 | 37.78
2022-02-09 14:00 | 44601.5833 | 0 | 14.1025 | 37.78
2022-02-09 14:30 | 44601.6042 | 0 | 13.1711 | 37.78
2022-02-09 15:00 | 44601.625 | 0 | 13.9103 | 37.78
2022-02-09 15:30 | 44601.6458 | 0 | 14.8644 | 37.78
2022-02-09 16:00 | 44601.6667 | 0 | 15.6784 | 37.78
2022-02-09 16:30 | 44601.6875 | 0 | 16.0597 | 37.78
2022-02-09 17:00 | 44601.7083 | 0 | 16.4303 | 37.78
2022-02-09 17:30 | 44601.7292 | 0 | 16.6884 | 37.78
2022-02-09 18:00 | 44601.75 | 0 | 16.5882 | 37.78
2022-02-09 18:30 | 44601.7708 | 0 | 16.9086 | 37.78
2022-02-09 19:00 | 44601.7917 | 0 | 16.9529 | 37.78
2022-02-09 19:30 | 44601.8125 | 0 | 16.5302 | 37.78
2022-02-09 20:00 | 44601.8333 | 0 | 15.9447 | 37.78
2022-02-09 20:30 | 44601.8542 | 0 | 15.2564 | 37.78
2022-02-09 21:00 | 44601.875 | 0 | 14.7038 | 37.78
2022-02-09 21:30 | 44601.8958 | 0 | 13.9841 | 37.78
2022-02-09 22:00 | 44601.9167 | 0 | 13.3331 | 37.78
2022-02-09 22:30 | 44601.9375 | 0 | 12.3293 | 37.78
2022-02-09 23:00 | 44601.9583 | 0 | 11.7089 | 37.78
2022-02-09 23:30 | 44601.9792 | 0 | 11.0509 | 37.78
2022-02-10 | 44602 | 0 | 10.4221 | 37.78
2022-02-10 00:30 | 44602.0208 | 0 | 10.0241 | 37.78
2022-02-10 01:00 | 44602.0417 | 0 | 9.7764 | 37.78
2022-02-10 01:30 | 44602.0625 | 0 | 9.6349 | 37.78
2022-02-10 02:00 | 44602.0833 | 0 | 9.5063 | 37.78
2022-02-10 02:30 | 44602.1042 | 0 | 9.4119 | 37.78
2022-02-10 03:00 | 44602.125 | 0 | 9.2313 | 37.78
2022-02-10 03:30 | 44602.1458 | 0 | 9.2526 | 37.78
2022-02-10 04:00 | 44602.1667 | 0 | 9.3013 | 37.78
2022-02-10 04:30 | 44602.1875 | 0 | 9.8152 | 37.78
2022-02-10 05:00 | 44602.2083 | 0 | 10.2569 | 37.78
2022-02-10 05:30 | 44602.2292 | 0 | 10.6982 | 37.78
2022-02-10 06:00 | 44602.25 | 0 | 11.3203 | 37.78
2022-02-10 06:30 | 44602.2708 | 0 | 11.7076 | 37.78
2022-02-10 07:00 | 44602.2917 | 0 | 11.9782 | 37.78
2022-02-10 07:30 | 44602.3125 | 0 | 11.9401 | 37.78
2022-02-10 08:00 | 44602.3333 | 0 | 11.8988 | 37.78
2022-02-10 08:30 | 44602.3542 | 0 | 11.8412 | 37.78
2022-02-10 09:00 | 44602.375 | 0 | 11.953 | 37.78
2022-02-10 09:30 | 44602.3958 | 0 | 11.8352 | 37.78
2022-02-10 10:00 | 44602.4167 | 0 | 11.6248 | 37.78
2022-02-10 10:30 | 44602.4375 | 0 | 12.1335 | 37.78
2022-02-10 11:00 | 44602.4583 | 0 | 12.0872 | 37.78
2022-02-10 11:30 | 44602.4792 | 0 | 12.0477 | 37.78
2022-02-10 12:00 | 44602.5 | 0 | 12.3983 | 37.78
2022-02-10 12:30 | 44602.5208 | 0 | 12.4948 | 37.78
2022-02-10 13:00 | 44602.5417 | 0 | 13.3833 | 37.78
2022-02-10 13:30 | 44602.5625 | 0 | 14.1488 | 37.78
2022-02-10 14:00 | 44602.5833 | 0 | 15.2647 | 37.78
2022-02-10 14:30 | 44602.6042 | 0 | 15.4088 | 37.78
2022-02-10 15:00 | 44602.625 | 0 | 15.6551 | 37.78
2022-02-10 15:30 | 44602.6458 | 0 | 15.7314 | 37.78
2022-02-10 16:00 | 44602.6667 | 0 | 16.6366 | 37.78
2022-02-10 16:30 | 44602.6875 | 0 | 17.1508 | 37.78
2022-02-10 17:00 | 44602.7083 | 0 | 17.6109 | 37.78
2022-02-10 17:30 | 44602.7292 | 0 | 17.8109 | 37.78
2022-02-10 18:00 | 44602.75 | 0 | 17.5679 | 37.78
2022-02-10 18:30 | 44602.7708 | 0 | 17.628 | 37.78
2022-02-10 19:00 | 44602.7917 | 0 | 17.5541 | 37.78
2022-02-10 19:30 | 44602.8125 | 0 | 17.0769 | 37.78
2022-02-10 20:00 | 44602.8333 | 0 | 16.5843 | 37.78
2022-02-10 20:30 | 44602.8542 | 0 | 15.7931 | 37.78
2022-02-10 21:00 | 44602.875 | 0 | 14.9925 | 37.78
2022-02-10 21:30 | 44602.8958 | 0 | 14.2046 | 37.78
2022-02-10 22:00 | 44602.9167 | 0 | 13.5373 | 37.78
2022-02-10 22:30 | 44602.9375 | 0 | 12.3721 | 37.78
2022-02-10 23:00 | 44602.9583 | 0 | 11.8728 | 37.78
2022-02-10 23:30 | 44602.9792 | 0 | 11.2446 | 37.78
2022-02-11 | 44603 | 0 | 10.5499 | 37.78
2022-02-11 00:30 | 44603.0208 | 0 | 9.9617 | 37.78
2022-02-11 01:00 | 44603.0417 | 0 | 9.871 | 37.78
2022-02-11 01:30 | 44603.0625 | 0 | 9.7315 | 37.78
2022-02-11 02:00 | 44603.0833 | 0 | 9.4213 | 37.78
2022-02-11 02:30 | 44603.1042 | 0 | 9.3767 | 37.78
2022-02-11 03:00 | 44603.125 | 0 | 9.2033 | 37.78
2022-02-11 03:30 | 44603.1458 | 0 | 9.186 | 37.78
2022-02-11 04:00 | 44603.1667 | 0 | 9.446 | 37.78
2022-02-11 04:30 | 44603.1875 | 0 | 9.722 | 37.78
2022-02-11 05:00 | 44603.2083 | 0 | 10.0522 | 37.78
2022-02-11 05:30 | 44603.2292 | 0 | 10.3909 | 37.78
2022-02-11 06:00 | 44603.25 | 0 | 10.989 | 37.78
2022-02-11 06:30 | 44603.2708 | 0 | 11.494 | 37.78
2022-02-11 07:00 | 44603.2917 | 0 | 11.9187 | 37.78
2022-02-11 07:30 | 44603.3125 | 0 | 11.9852 | 37.78
2022-02-11 08:00 | 44603.3333 | 0 | 11.9051 | 37.78
2022-02-11 08:30 | 44603.3542 | 0 | 12.1677 | 37.78
2022-02-11 09:00 | 44603.375 | 0 | 12.8412 | 37.78
2022-02-11 09:30 | 44603.3958 | 0 | 11.7275 | 37.78
2022-02-11 10:00 | 44603.4167 | 0 | 13.1755 | 37.78
2022-02-11 10:30 | 44603.4375 | 0 | 12.4003 | 37.78
2022-02-11 11:00 | 44603.4583 | 0 | 12.5733 | 37.78
2022-02-11 11:30 | 44603.4792 | 0 | 13.1334 | 37.78
2022-02-11 12:00 | 44603.5 | 0 | 14.7058 | 37.78
2022-02-11 12:30 | 44603.5208 | 0 | 13.2665 | 37.78
2022-02-11 13:00 | 44603.5417 | 0 | 13.8637 | 37.78
2022-02-11 13:30 | 44603.5625 | 0 | 14.6655 | 37.78
2022-02-11 14:00 | 44603.5833 | 0 | 16.1924 | 37.78
2022-02-11 14:30 | 44603.6042 | 0 | 16.2564 | 37.78
2022-02-11 15:00 | 44603.625 | 0 | 16.2755 | 37.78
2022-02-11 15:30 | 44603.6458 | 0 | 15.9056 | 37.78
2022-02-11 16:00 | 44603.6667 | 0 | 17.289 | 37.78
2022-02-11 16:30 | 44603.6875 | 0 | 18.0574 | 37.78
2022-02-11 17:00 | 44603.7083 | 0 | 16.9369 | 37.78
2022-02-11 17:30 | 44603.7292 | 0 | 16.8292 | 37.78
2022-02-11 18:00 | 44603.75 | 0 | 16.6251 | 37.78
2022-02-11 18:30 | 44603.7708 | 0 | 16.7026 | 37.78
2022-02-11 19:00 | 44603.7917 | 0 | 16.3042 | 37.78
2022-02-11 19:30 | 44603.8125 | 0 | 16.0263 | 37.78
2022-02-11 20:00 | 44603.8333 | 0 | 15.5106 | 37.78
2022-02-11 20:30 | 44603.8542 | 0 | 14.8792 | 37.78
2022-02-11 21:00 | 44603.875 | 0 | 14.3777 | 37.78
2022-02-11 21:30 | 44603.8958 | 0 | 13.7219 | 37.78
2022-02-11 22:00 | 44603.9167 | 0 | 13.1578 | 37.78
2022-02-11 22:30 | 44603.9375 | 0 | 12.3058 | 37.78
2022-02-11 23:00 | 44603.9583 | 0 | 11.4975 | 37.78
2022-02-11 23:30 | 44603.9792 | 0 | 10.9181 | 37.78
2022-02-12 | 44604 | 0 | 10.174 | 37.78
2022-02-12 00:30 | 44604.0208 | 0 | 9.6766 | 37.78
2022-02-12 01:00 | 44604.0417 | 0 | 9.4019 | 37.78
2022-02-12 01:30 | 44604.0625 | 0 | 9.1562 | 37.78
2022-02-12 02:00 | 44604.0833 | 0 | 9.0051 | 37.78
2022-02-12 02:30 | 44604.1042 | 0 | 9.002 | 37.78
2022-02-12 03:00 | 44604.125 | 0 | 8.8355 | 37.78
2022-02-12 03:30 | 44604.1458 | 0 | 8.6925 | 37.78
2022-02-12 04:00 | 44604.1667 | 0 | 8.7346 | 37.78
2022-02-12 04:30 | 44604.1875 | 0 | 8.7818 | 37.78
2022-02-12 05:00 | 44604.2083 | 0 | 8.8763 | 37.78
2022-02-12 05:30 | 44604.2292 | 0 | 8.9508 | 37.78
2022-02-12 06:00 | 44604.25 | 0 | 8.9752 | 37.78
2022-02-12 06:30 | 44604.2708 | 0 | 8.9825 | 37.78
2022-02-12 07:00 | 44604.2917 | 0 | 9.0298 | 37.78
2022-02-12 07:30 | 44604.3125 | 0 | 8.7937 | 37.78
2022-02-12 08:00 | 44604.3333 | 0 | 8.7814 | 37.78
2022-02-12 08:30 | 44604.3542 | 0 | 8.8182 | 37.78
2022-02-12 09:00 | 44604.375 | 0 | 9.2392 | 37.78
2022-02-12 09:30 | 44604.3958 | 0 | 9.7355 | 37.78
2022-02-12 10:00 | 44604.4167 | 0 | 9.8794 | 37.78
2022-02-12 10:30 | 44604.4375 | 0 | 10.5723 | 37.78
2022-02-12 11:00 | 44604.4583 | 0 | 10.9161 | 37.78
2022-02-12 11:30 | 44604.4792 | 0 | 12.7332 | 37.78
2022-02-12 12:00 | 44604.5 | 0 | 10.9785 | 37.78
2022-02-12 12:30 | 44604.5208 | 0 | 10.2864 | 37.78
2022-02-12 13:00 | 44604.5417 | 0 | 12.2435 | 37.78
2022-02-12 13:30 | 44604.5625 | 0 | 11.8382 | 37.78
2022-02-12 14:00 | 44604.5833 | 0 | 9.8787 | 37.78
2022-02-12 14:30 | 44604.6042 | 0 | 10.7411 | 37.78
2022-02-12 15:00 | 44604.625 | 0 | 11.1495 | 37.78
2022-02-12 15:30 | 44604.6458 | 0 | 10.1423 | 37.78
2022-02-12 16:00 | 44604.6667 | 0 | 12.0418 | 37.78
2022-02-12 16:30 | 44604.6875 | 0 | 12.1016 | 37.78
2022-02-12 17:00 | 44604.7083 | 0 | 12.0568 | 37.78
2022-02-12 17:30 | 44604.7292 | 0 | 12.1494 | 37.78
2022-02-12 18:00 | 44604.75 | 0 | 12.2633 | 37.78
2022-02-12 18:30 | 44604.7708 | 0 | 12.5268 | 37.78
2022-02-12 19:00 | 44604.7917 | 0 | 12.6419 | 37.78
2022-02-12 19:30 | 44604.8125 | 0 | 12.4271 | 37.78
2022-02-12 20:00 | 44604.8333 | 0 | 12.0251 | 37.78
2022-02-12 20:30 | 44604.8542 | 0 | 11.7619 | 37.78
2022-02-12 21:00 | 44604.875 | 0 | 11.6819 | 37.78
2022-02-12 21:30 | 44604.8958 | 0 | 11.2741 | 37.78
2022-02-12 22:00 | 44604.9167 | 0 | 10.9016 | 37.78
2022-02-12 22:30 | 44604.9375 | 0 | 10.1109 | 37.78
2022-02-12 23:00 | 44604.9583 | 0 | 9.6445 | 37.78
2022-02-12 23:30 | 44604.9792 | 0 | 9.1259 | 37.78
2022-02-13 | 44605 | 0 | 8.7555 | 37.78
2022-02-13 00:30 | 44605.0208 | 0 | 8.5427 | 37.78
2022-02-13 01:00 | 44605.0417 | 0 | 8.3001 | 37.78
2022-02-13 01:30 | 44605.0625 | 0 | 8.1062 | 37.78
2022-02-13 02:00 | 44605.0833 | 0 | 7.923 | 37.78
2022-02-13 02:30 | 44605.1042 | 0 | 7.7414 | 37.78
2022-02-13 03:00 | 44605.125 | 0 | 7.5889 | 37.78
2022-02-13 03:30 | 44605.1458 | 0 | 7.5112 | 37.78
2022-02-13 04:00 | 44605.1667 | 0 | 7.4865 | 37.78
2022-02-13 04:30 | 44605.1875 | 0 | 7.4911 | 37.78
2022-02-13 05:00 | 44605.2083 | 0 | 7.5961 | 37.78
2022-02-13 05:30 | 44605.2292 | 0 | 7.6198 | 37.78
2022-02-13 06:00 | 44605.25 | 0 | 7.4938 | 37.78
2022-02-13 06:30 | 44605.2708 | 0 | 7.3522 | 37.78
2022-02-13 07:00 | 44605.2917 | 0 | 7.2204 | 37.78
2022-02-13 07:30 | 44605.3125 | 0 | 6.9185 | 37.78
2022-02-13 08:00 | 44605.3333 | 0 | 6.7988 | 37.78
2022-02-13 08:30 | 44605.3542 | 0 | 6.7305 | 37.78
2022-02-13 09:00 | 44605.375 | 0 | 7.4098 | 37.78
2022-02-13 09:30 | 44605.3958 | 0 | 6.9677 | 37.78
2022-02-13 10:00 | 44605.4167 | 0 | 7.6742 | 37.78
2022-02-13 10:30 | 44605.4375 | 0 | 7.5192 | 37.78
2022-02-13 11:00 | 44605.4583 | 0 | 7.4692 | 37.78
2022-02-13 11:30 | 44605.4792 | 0 | 7.7199 | 37.78
2022-02-13 12:00 | 44605.5 | 0 | 7.4057 | 37.78
2022-02-13 12:30 | 44605.5208 | 0 | 7.9014 | 37.78
2022-02-13 13:00 | 44605.5417 | 0 | 8.0899 | 37.78
2022-02-13 13:30 | 44605.5625 | 0 | 8.3352 | 37.78
2022-02-13 14:00 | 44605.5833 | 0 | 8.3492 | 37.78
2022-02-13 14:30 | 44605.6042 | 0 | 9.5011 | 37.78
2022-02-13 15:00 | 44605.625 | 0 | 9.3968 | 37.78
2022-02-13 15:30 | 44605.6458 | 0 | 11.0747 | 37.78
2022-02-13 16:00 | 44605.6667 | 0 | 11.8468 | 37.78
2022-02-13 16:30 | 44605.6875 | 0 | 12.7373 | 37.78
2022-02-13 17:00 | 44605.7083 | 0 | 13.0488 | 37.78
2022-02-13 17:30 | 44605.7292 | 0 | 13.1453 | 37.78
2022-02-13 18:00 | 44605.75 | 0 | 13.5427 | 37.78
2022-02-13 18:30 | 44605.7708 | 0 | 14.1968 | 37.78
2022-02-13 19:00 | 44605.7917 | 0 | 14.1736 | 37.78
2022-02-13 19:30 | 44605.8125 | 0 | 14.0941 | 37.78
2022-02-13 20:00 | 44605.8333 | 0 | 13.5996 | 37.78
2022-02-13 20:30 | 44605.8542 | 0 | 13.1443 | 37.78
2022-02-13 21:00 | 44605.875 | 0 | 12.4976 | 37.78
2022-02-13 21:30 | 44605.8958 | 0 | 11.8254 | 37.78
2022-02-13 22:00 | 44605.9167 | 0 | 11.304 | 37.78
2022-02-13 22:30 | 44605.9375 | 0 | 10.2725 | 37.78
2022-02-13 23:00 | 44605.9583 | 0 | 9.8259 | 37.78
2022-02-13 23:30 | 44605.9792 | 0 | 9.3613 | 37.78
2022-02-14 | 44606 | 0 | 9.1136 | 37.78
2022-02-14 00:30 | 44606.0208 | 0 | 8.7473 | 37.78
2022-02-14 01:00 | 44606.0417 | 0 | 8.7045 | 37.78
2022-02-14 01:30 | 44606.0625 | 0 | 8.5208 | 37.78
2022-02-14 02:00 | 44606.0833 | 0 | 8.392 | 37.78
2022-02-14 02:30 | 44606.1042 | 0 | 8.3421 | 37.78
2022-02-14 03:00 | 44606.125 | 0 | 8.3551 | 37.78
2022-02-14 03:30 | 44606.1458 | 0 | 8.3674 | 37.78
2022-02-14 04:00 | 44606.1667 | 0 | 8.6334 | 37.78
2022-02-14 04:30 | 44606.1875 | 0 | 8.9807 | 37.78
2022-02-14 05:00 | 44606.2083 | 0 | 9.532 | 37.78
2022-02-14 05:30 | 44606.2292 | 0 | 10.1694 | 37.78
2022-02-14 06:00 | 44606.25 | 0 | 10.6304 | 37.78
2022-02-14 06:30 | 44606.2708 | 0 | 11.2149 | 37.78
2022-02-14 07:00 | 44606.2917 | 0 | 11.714 | 37.78
2022-02-14 07:30 | 44606.3125 | 0 | 11.8053 | 37.78
2022-02-14 08:00 | 44606.3333 | 0 | 12.5323 | 37.78
2022-02-14 08:30 | 44606.3542 | 0 | 12.1369 | 37.78
2022-02-14 09:00 | 44606.375 | 0 | 12.1159 | 37.78
2022-02-14 09:30 | 44606.3958 | 0 | 12.7875 | 37.78
2022-02-14 10:00 | 44606.4167 | 0 | 13.9711 | 37.78
2022-02-14 10:30 | 44606.4375 | 0 | 12.3732 | 37.78
2022-02-14 11:00 | 44606.4583 | 0 | 11.2324 | 37.78
2022-02-14 11:30 | 44606.4792 | 0 | 15.1821 | 37.78
2022-02-14 12:00 | 44606.5 | 0 | 14.313 | 37.78
2022-02-14 12:30 | 44606.5208 | 0 | 13.2381 | 37.78
2022-02-14 13:00 | 44606.5417 | 0 | 13.8261 | 37.78
2022-02-14 13:30 | 44606.5625 | 0 | 15.2415 | 37.78
2022-02-14 14:00 | 44606.5833 | 0 | 14.6376 | 37.78
2022-02-14 14:30 | 44606.6042 | 0 | 14.1173 | 37.78
2022-02-14 15:00 | 44606.625 | 0 | 13.214 | 37.78
2022-02-14 15:30 | 44606.6458 | 0 | 13.0528 | 37.78
2022-02-14 16:00 | 44606.6667 | 0 | 13.2434 | 37.78
2022-02-14 16:30 | 44606.6875 | 0 | 13.9147 | 37.78
2022-02-14 17:00 | 44606.7083 | 0 | 14.245 | 37.78
2022-02-14 17:30 | 44606.7292 | 0 | 14.3276 | 37.78
2022-02-14 18:00 | 44606.75 | 0 | 14.4726 | 37.78
2022-02-14 18:30 | 44606.7708 | 0 | 14.7766 | 37.78
2022-02-14 19:00 | 44606.7917 | 0 | 14.6021 | 37.78
2022-02-14 19:30 | 44606.8125 | 0 | 14.4321 | 37.78
2022-02-14 20:00 | 44606.8333 | 0 | 13.964 | 37.78
2022-02-14 20:30 | 44606.8542 | 0 | 13.4015 | 37.78
2022-02-14 21:00 | 44606.875 | 0 | 12.8456 | 37.78
2022-02-14 21:30 | 44606.8958 | 0 | 12.2944 | 37.78
2022-02-14 22:00 | 44606.9167 | 0 | 11.6493 | 37.78
2022-02-14 22:30 | 44606.9375 | 0 | 10.7491 | 37.78
2022-02-14 23:00 | 44606.9583 | 0 | 10.1525 | 37.78
2022-02-14 23:30 | 44606.9792 | 0 | 9.6147 | 37.78
2022-02-15 | 44607 | 0 | 9.0204 | 37.78
2022-02-15 00:30 | 44607.0208 | 0 | 8.754 | 37.78
2022-02-15 01:00 | 44607.0417 | 0 | 8.606 | 37.78
2022-02-15 01:30 | 44607.0625 | 0 | 8.3299 | 37.78
2022-02-15 02:00 | 44607.0833 | 0 | 8.3174 | 37.78
2022-02-15 02:30 | 44607.1042 | 0 | 8.3875 | 37.78
2022-02-15 03:00 | 44607.125 | 0 | 8.3499 | 37.78
2022-02-15 03:30 | 44607.1458 | 0 | 8.3401 | 37.78
2022-02-15 04:00 | 44607.1667 | 0 | 8.7035 | 37.78
2022-02-15 04:30 | 44607.1875 | 0 | 9.185 | 37.78
2022-02-15 05:00 | 44607.2083 | 0 | 9.7952 | 37.78
2022-02-15 05:30 | 44607.2292 | 0 | 10.3953 | 37.78
2022-02-15 06:00 | 44607.25 | 0 | 10.9549 | 37.78
2022-02-15 06:30 | 44607.2708 | 0 | 11.8311 | 37.78
2022-02-15 07:00 | 44607.2917 | 0 | 12.9272 | 37.78
2022-02-15 07:30 | 44607.3125 | 0 | 12.2238 | 37.78
2022-02-15 08:00 | 44607.3333 | 0 | 12.4242 | 37.78
2022-02-15 08:30 | 44607.3542 | 0 | 12.1844 | 37.78
2022-02-15 09:00 | 44607.375 | 0 | 11.8897 | 37.78
2022-02-15 09:30 | 44607.3958 | 0 | 12.1508 | 37.78
2022-02-15 10:00 | 44607.4167 | 0 | 12.2317 | 37.78
2022-02-15 10:30 | 44607.4375 | 0 | 11.2373 | 37.78
2022-02-15 11:00 | 44607.4583 | 0 | 13.4265 | 37.78
2022-02-15 11:30 | 44607.4792 | 0 | 12.5189 | 37.78
2022-02-15 12:00 | 44607.5 | 0 | 11.6168 | 37.78
2022-02-15 12:30 | 44607.5208 | 0 | 12.2601 | 37.78
2022-02-15 13:00 | 44607.5417 | 0 | 13.429 | 37.78
2022-02-15 13:30 | 44607.5625 | 0 | 14.5605 | 37.78
2022-02-15 14:00 | 44607.5833 | 0 | 14.3967 | 37.78
2022-02-15 14:30 | 44607.6042 | 0 | 14.1378 | 37.78
2022-02-15 15:00 | 44607.625 | 0 | 14.2353 | 37.78
2022-02-15 15:30 | 44607.6458 | 0 | 13.5609 | 37.78
2022-02-15 16:00 | 44607.6667 | 0 | 14.4188 | 37.78
2022-02-15 16:30 | 44607.6875 | 0 | 14.3597 | 37.78
2022-02-15 17:00 | 44607.7083 | 0 | 14.2661 | 37.78
2022-02-15 17:30 | 44607.7292 | 0 | 14.6224 | 37.78
2022-02-15 18:00 | 44607.75 | 0 | 14.7345 | 37.78
2022-02-15 18:30 | 44607.7708 | 0 | 14.9693 | 37.78
2022-02-15 19:00 | 44607.7917 | 0 | 15.245 | 37.78
2022-02-15 19:30 | 44607.8125 | 0 | 14.9076 | 37.78
2022-02-15 20:00 | 44607.8333 | 0 | 14.5342 | 37.78
2022-02-15 20:30 | 44607.8542 | 0 | 14.0459 | 37.78
2022-02-15 21:00 | 44607.875 | 0 | 13.2814 | 37.78
2022-02-15 21:30 | 44607.8958 | 0 | 12.665 | 37.78
2022-02-15 22:00 | 44607.9167 | 0 | 12.3735 | 37.78
2022-02-15 22:30 | 44607.9375 | 0 | 11.2649 | 37.78
2022-02-15 23:00 | 44607.9583 | 0 | 10.6217 | 37.78
2022-02-15 23:30 | 44607.9792 | 0 | 10.1481 | 37.78
2022-02-16 | 44608 | 0 | 9.5823 | 37.78
2022-02-16 00:30 | 44608.0208 | 0 | 9.1434 | 37.78
2022-02-16 01:00 | 44608.0417 | 0 | 8.8215 | 37.78
2022-02-16 01:30 | 44608.0625 | 0 | 8.618 | 37.78
2022-02-16 02:00 | 44608.0833 | 0 | 8.6947 | 37.78
2022-02-16 02:30 | 44608.1042 | 0 | 8.7071 | 37.78
2022-02-16 03:00 | 44608.125 | 0 | 8.5011 | 37.78
2022-02-16 03:30 | 44608.1458 | 0 | 8.5235 | 37.78
2022-02-16 04:00 | 44608.1667 | 0 | 8.8346 | 37.78
2022-02-16 04:30 | 44608.1875 | 0 | 9.148 | 37.78
2022-02-16 05:00 | 44608.2083 | 0 | 9.825 | 37.78
2022-02-16 05:30 | 44608.2292 | 0 | 10.2732 | 37.78
2022-02-16 06:00 | 44608.25 | 0 | 10.9414 | 37.78
2022-02-16 06:30 | 44608.2708 | 0 | 12.052 | 37.78
2022-02-16 07:00 | 44608.2917 | 0 | 12.9277 | 37.78
2022-02-16 07:30 | 44608.3125 | 0 | 12.8682 | 37.78
2022-02-16 08:00 | 44608.3333 | 0 | 11.8426 | 37.78
2022-02-16 08:30 | 44608.3542 | 0 | 10.8564 | 37.78
2022-02-16 09:00 | 44608.375 | 0 | 10.8582 | 37.78
2022-02-16 09:30 | 44608.3958 | 0 | 12.0143 | 37.78
2022-02-16 10:00 | 44608.4167 | 0 | 11.2936 | 37.78
2022-02-16 10:30 | 44608.4375 | 0 | 12.1613 | 37.78
2022-02-16 11:00 | 44608.4583 | 0 | 11.4857 | 37.78
2022-02-16 11:30 | 44608.4792 | 0 | 12.0334 | 37.78
2022-02-16 12:00 | 44608.5 | 0 | 12.2516 | 37.78
2022-02-16 12:30 | 44608.5208 | 0 | 12.0225 | 37.78
2022-02-16 13:00 | 44608.5417 | 0 | 11.708 | 37.78
2022-02-16 13:30 | 44608.5625 | 0 | 11.9194 | 37.78
2022-02-16 14:00 | 44608.5833 | 0 | 12.5384 | 37.78
2022-02-16 14:30 | 44608.6042 | 0 | 12.9726 | 37.78
2022-02-16 15:00 | 44608.625 | 0 | 14.3918 | 37.78
2022-02-16 15:30 | 44608.6458 | 0 | 14.493 | 37.78
2022-02-16 16:00 | 44608.6667 | 0 | 15.3532 | 37.78
2022-02-16 16:30 | 44608.6875 | 0 | 15.6048 | 37.78
2022-02-16 17:00 | 44608.7083 | 0 | 15.29 | 37.78
2022-02-16 17:30 | 44608.7292 | 0 | 15.6608 | 37.78
2022-02-16 18:00 | 44608.75 | 0 | 15.7741 | 37.78
2022-02-16 18:30 | 44608.7708 | 0 | 16.2426 | 37.78
2022-02-16 19:00 | 44608.7917 | 0 | 16.3744 | 37.78
2022-02-16 19:30 | 44608.8125 | 0 | 15.9411 | 37.78
2022-02-16 20:00 | 44608.8333 | 0 | 15.3639 | 37.78
2022-02-16 20:30 | 44608.8542 | 0 | 14.9508 | 37.78
2022-02-16 21:00 | 44608.875 | 0 | 14.3745 | 37.78
2022-02-16 21:30 | 44608.8958 | 0 | 13.7337 | 37.78
2022-02-16 22:00 | 44608.9167 | 0 | 13.0341 | 37.78
2022-02-16 22:30 | 44608.9375 | 0 | 12.0944 | 37.78
2022-02-16 23:00 | 44608.9583 | 0 | 11.2427 | 37.78
2022-02-16 23:30 | 44608.9792 | 0 | 10.6937 | 37.78
2022-02-17 | 44609 | 0 | 10.0673 | 37.78
2022-02-17 00:30 | 44609.0208 | 0 | 9.6395 | 37.78
2022-02-17 01:00 | 44609.0417 | 0 | 9.4064 | 37.78
2022-02-17 01:30 | 44609.0625 | 0 | 9.143 | 37.78
2022-02-17 02:00 | 44609.0833 | 0 | 8.9224 | 37.78
2022-02-17 02:30 | 44609.1042 | 0 | 8.8115 | 37.78
2022-02-17 03:00 | 44609.125 | 0 | 8.7191 | 37.78
2022-02-17 03:30 | 44609.1458 | 0 | 8.723 | 37.78
2022-02-17 04:00 | 44609.1667 | 0 | 9.1498 | 37.78
2022-02-17 04:30 | 44609.1875 | 0 | 9.5326 | 37.78
2022-02-17 05:00 | 44609.2083 | 0 | 10.104 | 37.78
2022-02-17 05:30 | 44609.2292 | 0 | 10.5126 | 37.78
2022-02-17 06:00 | 44609.25 | 0 | 11.2068 | 37.78
2022-02-17 06:30 | 44609.2708 | 0 | 11.5353 | 37.78
2022-02-17 07:00 | 44609.2917 | 0 | 11.8038 | 37.78
2022-02-17 07:30 | 44609.3125 | 0 | 12.0555 | 37.78
2022-02-17 08:00 | 44609.3333 | 0 | 12.0092 | 37.78
2022-02-17 08:30 | 44609.3542 | 0 | 11.8421 | 37.78
2022-02-17 09:00 | 44609.375 | 0 | 12.6747 | 37.78
2022-02-17 09:30 | 44609.3958 | 0 | 12.5361 | 37.78
2022-02-17 10:00 | 44609.4167 | 0 | 12.7491 | 37.78
2022-02-17 10:30 | 44609.4375 | 0 | 13.1242 | 37.78
2022-02-17 11:00 | 44609.4583 | 0 | 14.636 | 37.78
2022-02-17 11:30 | 44609.4792 | 0 | 13.3813 | 37.78
2022-02-17 12:00 | 44609.5 | 0 | 12.5393 | 37.78
2022-02-17 12:30 | 44609.5208 | 0 | 13.3818 | 37.78
2022-02-17 13:00 | 44609.5417 | 0 | 13.6789 | 37.78
2022-02-17 13:30 | 44609.5625 | 0 | 14.1447 | 37.78
2022-02-17 14:00 | 44609.5833 | 0 | 13.4931 | 37.78
2022-02-17 14:30 | 44609.6042 | 0 | 14.0488 | 37.78
2022-02-17 15:00 | 44609.625 | 0 | 14.4131 | 37.78
2022-02-17 15:30 | 44609.6458 | 0 | 15.2208 | 37.78
2022-02-17 16:00 | 44609.6667 | 0 | 16.1328 | 37.78
2022-02-17 16:30 | 44609.6875 | 0 | 16.7481 | 37.78
2022-02-17 17:00 | 44609.7083 | 0 | 17.2914 | 37.78
2022-02-17 17:30 | 44609.7292 | 0 | 17.719 | 37.78
2022-02-17 18:00 | 44609.75 | 0 | 17.5426 | 37.78
2022-02-17 18:30 | 44609.7708 | 0 | 17.7254 | 37.78
2022-02-17 19:00 | 44609.7917 | 0 | 17.8527 | 37.78
2022-02-17 19:30 | 44609.8125 | 0 | 17.3697 | 37.78
2022-02-17 20:00 | 44609.8333 | 0 | 16.9662 | 37.78
2022-02-17 20:30 | 44609.8542 | 0 | 16.4953 | 37.78
2022-02-17 21:00 | 44609.875 | 0 | 15.7109 | 37.78
2022-02-17 21:30 | 44609.8958 | 0 | 14.7113 | 37.78
2022-02-17 22:00 | 44609.9167 | 0 | 13.9992 | 37.78
2022-02-17 22:30 | 44609.9375 | 0 | 13.0158 | 37.78
2022-02-17 23:00 | 44609.9583 | 0 | 12.2251 | 37.78
2022-02-17 23:30 | 44609.9792 | 0 | 11.6631 | 37.78
2022-02-18 | 44610 | 0 | 10.9287 | 37.78
2022-02-18 00:30 | 44610.0208 | 0 | 10.2695 | 37.78
2022-02-18 01:00 | 44610.0417 | 0 | 10.1226 | 37.78
2022-02-18 01:30 | 44610.0625 | 0 | 9.9107 | 37.78
2022-02-18 02:00 | 44610.0833 | 0 | 9.7217 | 37.78
2022-02-18 02:30 | 44610.1042 | 0 | 9.7049 | 37.78
2022-02-18 03:00 | 44610.125 | 0 | 9.6002 | 37.78
2022-02-18 03:30 | 44610.1458 | 0 | 9.3973 | 37.78
2022-02-18 04:00 | 44610.1667 | 0 | 9.7031 | 37.78
2022-02-18 04:30 | 44610.1875 | 0 | 9.9592 | 37.78
2022-02-18 05:00 | 44610.2083 | 0 | 10.6036 | 37.78
2022-02-18 05:30 | 44610.2292 | 0 | 11.1887 | 37.78
2022-02-18 06:00 | 44610.25 | 0 | 11.6349 | 37.78
2022-02-18 06:30 | 44610.2708 | 0 | 12.2292 | 37.78
2022-02-18 07:00 | 44610.2917 | 0 | 12.7795 | 37.78
2022-02-18 07:30 | 44610.3125 | 0 | 12.876 | 37.78
2022-02-18 08:00 | 44610.3333 | 0 | 12.9242 | 37.78
2022-02-18 08:30 | 44610.3542 | 0 | 13.1636 | 37.78
2022-02-18 09:00 | 44610.375 | 0 | 13.1515 | 37.78
2022-02-18 09:30 | 44610.3958 | 0 | 13.1437 | 37.78
2022-02-18 10:00 | 44610.4167 | 0 | 13.1934 | 37.78
2022-02-18 10:30 | 44610.4375 | 0 | 13.6259 | 37.78
2022-02-18 11:00 | 44610.4583 | 0 | 14.0882 | 37.78
2022-02-18 11:30 | 44610.4792 | 0 | 14.5469 | 37.78
2022-02-18 12:00 | 44610.5 | 0 | 14.9517 | 37.78
2022-02-18 12:30 | 44610.5208 | 0 | 15.0323 | 37.78
2022-02-18 13:00 | 44610.5417 | 0 | 15.6961 | 37.78
2022-02-18 13:30 | 44610.5625 | 0 | 16.2739 | 37.78
2022-02-18 14:00 | 44610.5833 | 0 | 16.6965 | 37.78
2022-02-18 14:30 | 44610.6042 | 0 | 17.0273 | 37.78
2022-02-18 15:00 | 44610.625 | 0 | 17.5247 | 37.78
2022-02-18 15:30 | 44610.6458 | 0 | 18.3392 | 37.78
2022-02-18 16:00 | 44610.6667 | 0 | 18.3772 | 37.78
2022-02-18 16:30 | 44610.6875 | 0 | 19.1159 | 37.78
2022-02-18 17:00 | 44610.7083 | 0 | 19.9599 | 37.78
2022-02-18 17:30 | 44610.7292 | 0 | 19.5915 | 37.78
2022-02-18 18:00 | 44610.75 | 0 | 18.4229 | 37.78
2022-02-18 18:30 | 44610.7708 | 0 | 18.4366 | 37.78
2022-02-18 19:00 | 44610.7917 | 0 | 18.0302 | 37.78
2022-02-18 19:30 | 44610.8125 | 0 | 17.6745 | 37.78
2022-02-18 20:00 | 44610.8333 | 0 | 17.1824 | 37.78
2022-02-18 20:30 | 44610.8542 | 0 | 16.4639 | 37.78
2022-02-18 21:00 | 44610.875 | 0 | 15.7263 | 37.78
2022-02-18 21:30 | 44610.8958 | 0 | 14.9047 | 37.78
2022-02-18 22:00 | 44610.9167 | 0 | 14.1335 | 37.78
2022-02-18 22:30 | 44610.9375 | 0 | 13.2266 | 37.78
2022-02-18 23:00 | 44610.9583 | 0 | 12.5898 | 37.78
2022-02-18 23:30 | 44610.9792 | 0 | 12.0589 | 37.78
2022-02-19 | 44611 | 0 | 11.1724 | 37.78
2022-02-19 00:30 | 44611.0208 | 0 | 10.6727 | 37.78
2022-02-19 01:00 | 44611.0417 | 0 | 10.3792 | 37.78
2022-02-19 01:30 | 44611.0625 | 0 | 10.0472 | 37.78
2022-02-19 02:00 | 44611.0833 | 0 | 9.863 | 37.78
2022-02-19 02:30 | 44611.1042 | 0 | 9.7646 | 37.78
2022-02-19 03:00 | 44611.125 | 0 | 9.6095 | 37.78
2022-02-19 03:30 | 44611.1458 | 0 | 9.4119 | 37.78
2022-02-19 04:00 | 44611.1667 | 0 | 9.5088 | 37.78
2022-02-19 04:30 | 44611.1875 | 0 | 9.4619 | 37.78
2022-02-19 05:00 | 44611.2083 | 0 | 9.5755 | 37.78
2022-02-19 05:30 | 44611.2292 | 0 | 9.6205 | 37.78
2022-02-19 06:00 | 44611.25 | 0 | 9.4542 | 37.78
2022-02-19 06:30 | 44611.2708 | 0 | 9.7796 | 37.78
2022-02-19 07:00 | 44611.2917 | 0 | 9.9504 | 37.78
2022-02-19 07:30 | 44611.3125 | 0 | 9.5535 | 37.78
2022-02-19 08:00 | 44611.3333 | 0 | 9.5136 | 37.78
2022-02-19 08:30 | 44611.3542 | 0 | 9.6783 | 37.78
2022-02-19 09:00 | 44611.375 | 0 | 10.4361 | 37.78
2022-02-19 09:30 | 44611.3958 | 0 | 10.5975 | 37.78
2022-02-19 10:00 | 44611.4167 | 0 | 11.0409 | 37.78
2022-02-19 10:30 | 44611.4375 | 0 | 11.9441 | 37.78
2022-02-19 11:00 | 44611.4583 | 0 | 11.5284 | 37.78
2022-02-19 11:30 | 44611.4792 | 0 | 12.6477 | 37.78
2022-02-19 12:00 | 44611.5 | 0 | 13.2114 | 37.78
2022-02-19 12:30 | 44611.5208 | 0 | 12.8021 | 37.78
2022-02-19 13:00 | 44611.5417 | 0 | 14.0403 | 37.78
2022-02-19 13:30 | 44611.5625 | 0 | 14.9868 | 37.78
2022-02-19 14:00 | 44611.5833 | 0 | 16.8951 | 37.78
2022-02-19 14:30 | 44611.6042 | 0 | 15.8696 | 37.78
2022-02-19 15:00 | 44611.625 | 0 | 12.5807 | 37.78
2022-02-19 15:30 | 44611.6458 | 0 | 15.5706 | 37.78
2022-02-19 16:00 | 44611.6667 | 0 | 14.9347 | 37.78
2022-02-19 16:30 | 44611.6875 | 0 | 15.8231 | 37.78
2022-02-19 17:00 | 44611.7083 | 0 | 15.2367 | 37.78
2022-02-19 17:30 | 44611.7292 | 0 | 15.255 | 37.78
2022-02-19 18:00 | 44611.75 | 0 | 15.1971 | 37.78
2022-02-19 18:30 | 44611.7708 | 0 | 15.1198 | 37.78
2022-02-19 19:00 | 44611.7917 | 0 | 14.8922 | 37.78
2022-02-19 19:30 | 44611.8125 | 0 | 14.4861 | 37.78
2022-02-19 20:00 | 44611.8333 | 0 | 14.2844 | 37.78
2022-02-19 20:30 | 44611.8542 | 0 | 13.4548 | 37.78
2022-02-19 21:00 | 44611.875 | 0 | 13.1326 | 37.78
2022-02-19 21:30 | 44611.8958 | 0 | 12.4554 | 37.78
2022-02-19 22:00 | 44611.9167 | 0 | 11.9697 | 37.78
2022-02-19 22:30 | 44611.9375 | 0 | 11.3477 | 37.78
2022-02-19 23:00 | 44611.9583 | 0 | 10.8184 | 37.78
2022-02-19 23:30 | 44611.9792 | 0 | 10.2804 | 37.78
2022-02-20 | 44612 | 0 | 9.9376 | 37.78
2022-02-20 00:30 | 44612.0208 | 0 | 9.5547 | 37.78
2022-02-20 01:00 | 44612.0417 | 0 | 9.3714 | 37.78
2022-02-20 01:30 | 44612.0625 | 0 | 9.1509 | 37.78
2022-02-20 02:00 | 44612.0833 | 0 | 8.7739 | 37.78
2022-02-20 02:30 | 44612.1042 | 0 | 8.7764 | 37.78
2022-02-20 03:00 | 44612.125 | 0 | 8.61 | 37.78
2022-02-20 03:30 | 44612.1458 | 0 | 8.4964 | 37.78
2022-02-20 04:00 | 44612.1667 | 0 | 8.4763 | 37.78
2022-02-20 04:30 | 44612.1875 | 0 | 8.4346 | 37.78
2022-02-20 05:00 | 44612.2083 | 0 | 8.6328 | 37.78
2022-02-20 05:30 | 44612.2292 | 0 | 8.5713 | 37.78
2022-02-20 06:00 | 44612.25 | 0 | 8.6971 | 37.78
2022-02-20 06:30 | 44612.2708 | 0 | 8.7404 | 37.78
2022-02-20 07:00 | 44612.2917 | 0 | 9.0245 | 37.78
2022-02-20 07:30 | 44612.3125 | 0 | 8.4376 | 37.78
2022-02-20 08:00 | 44612.3333 | 0 | 7.6103 | 37.78
2022-02-20 08:30 | 44612.3542 | 0 | 8.2531 | 37.78
2022-02-20 09:00 | 44612.375 | 0 | 10.1265 | 37.78
2022-02-20 09:30 | 44612.3958 | 0 | 10.7763 | 37.78
2022-02-20 10:00 | 44612.4167 | 0 | 11.0475 | 37.78
2022-02-20 10:30 | 44612.4375 | 0 | 11.422 | 37.78
2022-02-20 11:00 | 44612.4583 | 0 | 11.2853 | 37.78
2022-02-20 11:30 | 44612.4792 | 0 | 10.7688 | 37.78
2022-02-20 12:00 | 44612.5 | 0 | 11.4785 | 37.78
2022-02-20 12:30 | 44612.5208 | 0 | 10.3984 | 37.78
2022-02-20 13:00 | 44612.5417 | 0 | 9.7279 | 37.78
2022-02-20 13:30 | 44612.5625 | 0 | 9.8225 | 37.78
2022-02-20 14:00 | 44612.5833 | 0 | 10.2944 | 37.78
2022-02-20 14:30 | 44612.6042 | 0 | 9.332 | 37.78
2022-02-20 15:00 | 44612.625 | 0 | 11.1042 | 37.78
2022-02-20 15:30 | 44612.6458 | 0 | 12.6502 | 37.78
2022-02-20 16:00 | 44612.6667 | 0 | 12.857 | 37.78
2022-02-20 16:30 | 44612.6875 | 0 | 12.8726 | 37.78
2022-02-20 17:00 | 44612.7083 | 0 | 13.1993 | 37.78
2022-02-20 17:30 | 44612.7292 | 0 | 14.2587 | 37.78
2022-02-20 18:00 | 44612.75 | 0 | 14.4132 | 37.78
2022-02-20 18:30 | 44612.7708 | 0 | 14.8951 | 37.78
2022-02-20 19:00 | 44612.7917 | 0 | 14.7012 | 37.78
2022-02-20 19:30 | 44612.8125 | 0 | 14.3295 | 37.78
2022-02-20 20:00 | 44612.8333 | 0 | 13.7891 | 37.78
2022-02-20 20:30 | 44612.8542 | 0 | 13.2489 | 37.78
2022-02-20 21:00 | 44612.875 | 0 | 12.6625 | 37.78
2022-02-20 21:30 | 44612.8958 | 0 | 12.1033 | 37.78
2022-02-20 22:00 | 44612.9167 | 0 | 11.4162 | 37.78
2022-02-20 22:30 | 44612.9375 | 0 | 10.633 | 37.78
2022-02-20 23:00 | 44612.9583 | 0 | 10.0562 | 37.78
2022-02-20 23:30 | 44612.9792 | 0 | 9.5375 | 37.78
2022-02-21 | 44613 | 0 | 9.2353 | 37.78
2022-02-21 00:30 | 44613.0208 | 0 | 8.9857 | 37.78
2022-02-21 01:00 | 44613.0417 | 0 | 8.878 | 37.78
2022-02-21 01:30 | 44613.0625 | 0 | 8.6107 | 37.78
2022-02-21 02:00 | 44613.0833 | 0 | 8.7196 | 37.78
2022-02-21 02:30 | 44613.1042 | 0 | 8.8142 | 37.78
2022-02-21 03:00 | 44613.125 | 0 | 8.697 | 37.78
2022-02-21 03:30 | 44613.1458 | 0 | 8.745 | 37.78
2022-02-21 04:00 | 44613.1667 | 0 | 9.0955 | 37.78
2022-02-21 04:30 | 44613.1875 | 0 | 9.5062 | 37.78
2022-02-21 05:00 | 44613.2083 | 0 | 10.1894 | 37.78
2022-02-21 05:30 | 44613.2292 | 0 | 10.6466 | 37.78
2022-02-21 06:00 | 44613.25 | 0 | 11.3371 | 37.78
2022-02-21 06:30 | 44613.2708 | 0 | 11.9886 | 37.78
2022-02-21 07:00 | 44613.2917 | 0 | 12.8233 | 37.78
2022-02-21 07:30 | 44613.3125 | 0 | 13.0061 | 37.78
2022-02-21 08:00 | 44613.3333 | 0 | 12.9447 | 37.78
2022-02-21 08:30 | 44613.3542 | 0 | 13.3536 | 37.78
2022-02-21 09:00 | 44613.375 | 0 | 14.0829 | 37.78
2022-02-21 09:30 | 44613.3958 | 0 | 14.0994 | 37.78
2022-02-21 10:00 | 44613.4167 | 0 | 14.0959 | 37.78
2022-02-21 10:30 | 44613.4375 | 0 | 14.5026 | 37.78
2022-02-21 11:00 | 44613.4583 | 0 | 12.9677 | 37.78
2022-02-21 11:30 | 44613.4792 | 0 | 13.5162 | 37.78
2022-02-21 12:00 | 44613.5 | 0 | 14.0632 | 37.78
2022-02-21 12:30 | 44613.5208 | 0 | 14.3325 | 37.78
2022-02-21 13:00 | 44613.5417 | 0 | 15.1649 | 37.78
2022-02-21 13:30 | 44613.5625 | 0 | 15.8685 | 37.78
2022-02-21 14:00 | 44613.5833 | 0 | 16.4133 | 37.78
2022-02-21 14:30 | 44613.6042 | 0 | 16.2507 | 37.78
2022-02-21 15:00 | 44613.625 | 0 | 14.949 | 37.78
2022-02-21 15:30 | 44613.6458 | 0 | 15.6818 | 37.78
2022-02-21 16:00 | 44613.6667 | 0 | 16.5974 | 37.78
2022-02-21 16:30 | 44613.6875 | 0 | 17.3751 | 37.78
2022-02-21 17:00 | 44613.7083 | 0 | 17.9281 | 37.78
2022-02-21 17:30 | 44613.7292 | 0 | 18.2958 | 37.78
2022-02-21 18:00 | 44613.75 | 0 | 18.0911 | 37.78
2022-02-21 18:30 | 44613.7708 | 0 | 18.7155 | 37.78
2022-02-21 19:00 | 44613.7917 | 0 | 18.7859 | 37.78
2022-02-21 19:30 | 44613.8125 | 0 | 18.4075 | 37.78
2022-02-21 20:00 | 44613.8333 | 0 | 17.5974 | 37.78
2022-02-21 20:30 | 44613.8542 | 0 | 17.04 | 37.78
2022-02-21 21:00 | 44613.875 | 0 | 16.2639 | 37.78
2022-02-21 21:30 | 44613.8958 | 0 | 15.536 | 37.78
2022-02-21 22:00 | 44613.9167 | 0 | 14.4468 | 37.78
2022-02-21 22:30 | 44613.9375 | 0 | 13.2589 | 37.78
2022-02-21 23:00 | 44613.9583 | 0 | 12.5066 | 37.78
2022-02-21 23:30 | 44613.9792 | 0 | 11.8375 | 37.78
2022-02-22 | 44614 | 0 | 11.2383 | 37.78
2022-02-22 00:30 | 44614.0208 | 0 | 10.7412 | 37.78
2022-02-22 01:00 | 44614.0417 | 0 | 10.5847 | 37.78
2022-02-22 01:30 | 44614.0625 | 0 | 10.3849 | 37.78
2022-02-22 02:00 | 44614.0833 | 0 | 10.1283 | 37.78
2022-02-22 02:30 | 44614.1042 | 0 | 9.857 | 37.78
2022-02-22 03:00 | 44614.125 | 0 | 9.7542 | 37.78
2022-02-22 03:30 | 44614.1458 | 0 | 9.6112 | 37.78
2022-02-22 04:00 | 44614.1667 | 0 | 9.8614 | 37.78
2022-02-22 04:30 | 44614.1875 | 0 | 10.2585 | 37.78
2022-02-22 05:00 | 44614.2083 | 0 | 10.9952 | 37.78
2022-02-22 05:30 | 44614.2292 | 0 | 11.4627 | 37.78
2022-02-22 06:00 | 44614.25 | 0 | 12.115 | 37.78
2022-02-22 06:30 | 44614.2708 | 0 | 12.6479 | 37.78
2022-02-22 07:00 | 44614.2917 | 0 | 13.3438 | 37.78
2022-02-22 07:30 | 44614.3125 | 0 | 13.6124 | 37.78
2022-02-22 08:00 | 44614.3333 | 0 | 14.1036 | 37.78
2022-02-22 08:30 | 44614.3542 | 0 | 15.6725 | 37.78
2022-02-22 09:00 | 44614.375 | 0 | 14.9905 | 37.78
2022-02-22 09:30 | 44614.3958 | 0 | 13.918 | 37.78
2022-02-22 10:00 | 44614.4167 | 0 | 14.5442 | 37.78
2022-02-22 10:30 | 44614.4375 | 0 | 13.967 | 37.78
2022-02-22 11:00 | 44614.4583 | 0 | 14.1885 | 37.78
2022-02-22 11:30 | 44614.4792 | 0 | 14.7208 | 37.78
2022-02-22 12:00 | 44614.5 | 0 | 16.0964 | 37.78
2022-02-22 12:30 | 44614.5208 | 0 | 16.4224 | 37.78
2022-02-22 13:00 | 44614.5417 | 0 | 16.85 | 37.78
2022-02-22 13:30 | 44614.5625 | 0 | 17.349 | 37.78
2022-02-22 14:00 | 44614.5833 | 0 | 17.174 | 37.78
2022-02-22 14:30 | 44614.6042 | 0 | 17.5019 | 37.78
2022-02-22 15:00 | 44614.625 | 0 | 17.2448 | 37.78
2022-02-22 15:30 | 44614.6458 | 0 | 16.2651 | 37.78
2022-02-22 16:00 | 44614.6667 | 0 | 15.9574 | 37.78
2022-02-22 16:30 | 44614.6875 | 0 | 16.0055 | 37.78
2022-02-22 17:00 | 44614.7083 | 0 | 16.0372 | 37.78
2022-02-22 17:30 | 44614.7292 | 0 | 16.3728 | 37.78
2022-02-22 18:00 | 44614.75 | 0 | 16.1907 | 37.78
2022-02-22 18:30 | 44614.7708 | 0 | 16.7889 | 37.78
2022-02-22 19:00 | 44614.7917 | 0 | 16.6893 | 37.78
2022-02-22 19:30 | 44614.8125 | 0 | 16.3868 | 37.78
2022-02-22 20:00 | 44614.8333 | 0 | 15.9998 | 37.78
2022-02-22 20:30 | 44614.8542 | 0 | 15.6578 | 37.78
2022-02-22 21:00 | 44614.875 | 0 | 15.173 | 37.78
2022-02-22 21:30 | 44614.8958 | 0 | 14.6176 | 37.78
2022-02-22 22:00 | 44614.9167 | 0 | 13.9338 | 37.78
2022-02-22 22:30 | 44614.9375 | 0 | 12.8327 | 37.78
2022-02-22 23:00 | 44614.9583 | 0 | 12.2075 | 37.78
2022-02-22 23:30 | 44614.9792 | 0 | 11.7296 | 37.78
2022-02-23 | 44615 | 0 | 11.008 | 37.78
2022-02-23 00:30 | 44615.0208 | 0 | 10.53 | 37.78
2022-02-23 01:00 | 44615.0417 | 0 | 10.3175 | 37.78
2022-02-23 01:30 | 44615.0625 | 0 | 10.1088 | 37.78
2022-02-23 02:00 | 44615.0833 | 0 | 9.8641 | 37.78
2022-02-23 02:30 | 44615.1042 | 0 | 9.9505 | 37.78
2022-02-23 03:00 | 44615.125 | 0 | 9.8652 | 37.78
2022-02-23 03:30 | 44615.1458 | 0 | 9.5777 | 37.78
2022-02-23 04:00 | 44615.1667 | 0 | 9.5097 | 37.78
2022-02-23 04:30 | 44615.1875 | 0 | 10.0351 | 37.78
2022-02-23 05:00 | 44615.2083 | 0 | 10.7088 | 37.78
2022-02-23 05:30 | 44615.2292 | 0 | 11.4464 | 37.78
2022-02-23 06:00 | 44615.25 | 0 | 12.4613 | 37.78
2022-02-23 06:30 | 44615.2708 | 0 | 13.3152 | 37.78
2022-02-23 07:00 | 44615.2917 | 0 | 14.5683 | 37.78
2022-02-23 07:30 | 44615.3125 | 0 | 14.8968 | 37.78
2022-02-23 08:00 | 44615.3333 | 0 | 15.2243 | 37.78
2022-02-23 08:30 | 44615.3542 | 0 | 14.4965 | 37.78
2022-02-23 09:00 | 44615.375 | 0 | 11.8376 | 37.78
2022-02-23 09:30 | 44615.3958 | 0 | 13.7848 | 37.78
2022-02-23 10:00 | 44615.4167 | 0 | 14.4111 | 37.78
2022-02-23 10:30 | 44615.4375 | 0 | 14.8441 | 37.78
2022-02-23 11:00 | 44615.4583 | 0 | 13.4343 | 37.78
2022-02-23 11:30 | 44615.4792 | 0 | 13.5471 | 37.78
2022-02-23 12:00 | 44615.5 | 0 | 13.4929 | 37.78
2022-02-23 12:30 | 44615.5208 | 0 | 14.9243 | 37.78
2022-02-23 13:00 | 44615.5417 | 0 | 14.6602 | 37.78
2022-02-23 13:30 | 44615.5625 | 0 | 15.0803 | 37.78
2022-02-23 14:00 | 44615.5833 | 0 | 14.1788 | 37.78
2022-02-23 14:30 | 44615.6042 | 0 | 14.5807 | 37.78
2022-02-23 15:00 | 44615.625 | 0 | 15.2673 | 37.78
2022-02-23 15:30 | 44615.6458 | 0 | 17.2809 | 37.78
2022-02-23 16:00 | 44615.6667 | 0 | 16.7019 | 37.78
2022-02-23 16:30 | 44615.6875 | 0 | 17.0887 | 37.78
2022-02-23 17:00 | 44615.7083 | 0 | 17.3918 | 37.78
2022-02-23 17:30 | 44615.7292 | 0 | 17.2857 | 37.78
2022-02-23 18:00 | 44615.75 | 0 | 17.5535 | 37.78
2022-02-23 18:30 | 44615.7708 | 0 | 17.9594 | 37.78
2022-02-23 19:00 | 44615.7917 | 0 | 17.9378 | 37.78
2022-02-23 19:30 | 44615.8125 | 0 | 17.505 | 37.78
2022-02-23 20:00 | 44615.8333 | 0 | 16.8311 | 37.78
2022-02-23 20:30 | 44615.8542 | 0 | 16.2614 | 37.78
2022-02-23 21:00 | 44615.875 | 0 | 15.6017 | 37.78
2022-02-23 21:30 | 44615.8958 | 0 | 14.9144 | 37.78
2022-02-23 22:00 | 44615.9167 | 0 | 13.9572 | 37.78
2022-02-23 22:30 | 44615.9375 | 0 | 13.1454 | 37.78
2022-02-23 23:00 | 44615.9583 | 0 | 12.5333 | 37.78
2022-02-23 23:30 | 44615.9792 | 0 | 11.9956 | 37.78
2022-02-24 | 44616 | 0 | 11.1474 | 37.78
2022-02-24 00:30 | 44616.0208 | 0 | 10.6129 | 37.78
2022-02-24 01:00 | 44616.0417 | 0 | 10.4331 | 37.78
2022-02-24 01:30 | 44616.0625 | 0 | 10.3932 | 37.78
2022-02-24 02:00 | 44616.0833 | 0 | 10.1862 | 37.78
2022-02-24 02:30 | 44616.1042 | 0 | 10.2146 | 37.78
2022-02-24 03:00 | 44616.125 | 0 | 10.0373 | 37.78
2022-02-24 03:30 | 44616.1458 | 0 | 10.0994 | 37.78
2022-02-24 04:00 | 44616.1667 | 0 | 10.4577 | 37.78
2022-02-24 04:30 | 44616.1875 | 0 | 10.937 | 37.78
2022-02-24 05:00 | 44616.2083 | 0 | 11.4976 | 37.78
2022-02-24 05:30 | 44616.2292 | 0 | 12.1975 | 37.78
2022-02-24 06:00 | 44616.25 | 0 | 13.3152 | 37.78
2022-02-24 06:30 | 44616.2708 | 0 | 13.7864 | 37.78
2022-02-24 07:00 | 44616.2917 | 0 | 14.5717 | 37.78
2022-02-24 07:30 | 44616.3125 | 0 | 15.0361 | 37.78
2022-02-24 08:00 | 44616.3333 | 0 | 15.2859 | 37.78
2022-02-24 08:30 | 44616.3542 | 0 | 15.08 | 37.78
2022-02-24 09:00 | 44616.375 | 0 | 14.841 | 37.78
2022-02-24 09:30 | 44616.3958 | 0 | 14.4201 | 37.78
2022-02-24 10:00 | 44616.4167 | 0 | 14.3747 | 37.78
2022-02-24 10:30 | 44616.4375 | 0 | 14.1603 | 37.78
2022-02-24 11:00 | 44616.4583 | 0 | 15.6077 | 37.78
2022-02-24 11:30 | 44616.4792 | 0 | 15.538 | 37.78
2022-02-24 12:00 | 44616.5 | 0 | 15.2183 | 37.78
2022-02-24 12:30 | 44616.5208 | 0 | 14.7192 | 37.78
2022-02-24 13:00 | 44616.5417 | 0 | 15.4839 | 37.78
2022-02-24 13:30 | 44616.5625 | 0 | 15.3942 | 37.78
2022-02-24 14:00 | 44616.5833 | 0 | 15.0254 | 37.78
2022-02-24 14:30 | 44616.6042 | 0 | 16.1851 | 37.78
2022-02-24 15:00 | 44616.625 | 0 | 16.3071 | 37.78
2022-02-24 15:30 | 44616.6458 | 0 | 14.5919 | 37.78
2022-02-24 16:00 | 44616.6667 | 0 | 15.3166 | 37.78
2022-02-24 16:30 | 44616.6875 | 0 | 16.0731 | 37.78
2022-02-24 17:00 | 44616.7083 | 0 | 16.2907 | 37.78
2022-02-24 17:30 | 44616.7292 | 0 | 16.6805 | 37.78
2022-02-24 18:00 | 44616.75 | 0 | 17.1046 | 37.78
2022-02-24 18:30 | 44616.7708 | 0 | 17.753 | 37.78
2022-02-24 19:00 | 44616.7917 | 0 | 17.5559 | 37.78
2022-02-24 19:30 | 44616.8125 | 0 | 17.2183 | 37.78
2022-02-24 20:00 | 44616.8333 | 0 | 16.6736 | 37.78
2022-02-24 20:30 | 44616.8542 | 0 | 16.2829 | 37.78
2022-02-24 21:00 | 44616.875 | 0 | 15.5124 | 37.78
2022-02-24 21:30 | 44616.8958 | 0 | 14.7691 | 37.78
2022-02-24 22:00 | 44616.9167 | 0 | 13.9806 | 37.78
2022-02-24 22:30 | 44616.9375 | 0 | 13.1621 | 37.78
2022-02-24 23:00 | 44616.9583 | 0 | 12.4043 | 37.78
2022-02-24 23:30 | 44616.9792 | 0 | 11.7011 | 37.78
2022-02-25 | 44617 | 0 | 11.2442 | 37.78
2022-02-25 00:30 | 44617.0208 | 0 | 10.8475 | 37.78
2022-02-25 01:00 | 44617.0417 | 0 | 10.6477 | 37.78
2022-02-25 01:30 | 44617.0625 | 0 | 10.451 | 37.78
2022-02-25 02:00 | 44617.0833 | 0 | 10.3598 | 37.78
2022-02-25 02:30 | 44617.1042 | 0 | 10.2435 | 37.78
2022-02-25 03:00 | 44617.125 | 0 | 10.3001 | 37.78
2022-02-25 03:30 | 44617.1458 | 0 | 10.1428 | 37.78
2022-02-25 04:00 | 44617.1667 | 0 | 10.5797 | 37.78
2022-02-25 04:30 | 44617.1875 | 0 | 11.0785 | 37.78
2022-02-25 05:00 | 44617.2083 | 0 | 11.4363 | 37.78
2022-02-25 05:30 | 44617.2292 | 0 | 12.0697 | 37.78
2022-02-25 06:00 | 44617.25 | 0 | 13.0498 | 37.78
2022-02-25 06:30 | 44617.2708 | 0 | 14.0067 | 37.78
2022-02-25 07:00 | 44617.2917 | 0 | 15.353 | 37.78
2022-02-25 07:30 | 44617.3125 | 0 | 15.7933 | 37.78
2022-02-25 08:00 | 44617.3333 | 0 | 16.167 | 37.78
2022-02-25 08:30 | 44617.3542 | 0 | 16.372 | 37.78
2022-02-25 09:00 | 44617.375 | 0 | 16.2386 | 37.78
2022-02-25 09:30 | 44617.3958 | 0 | 16.153 | 37.78
2022-02-25 10:00 | 44617.4167 | 0 | 16.2518 | 37.78
2022-02-25 10:30 | 44617.4375 | 0 | 16.3093 | 37.78
2022-02-25 11:00 | 44617.4583 | 0 | 16.11 | 37.78
2022-02-25 11:30 | 44617.4792 | 0 | 15.8561 | 37.78
2022-02-25 12:00 | 44617.5 | 0 | 15.7584 | 37.78
2022-02-25 12:30 | 44617.5208 | 0 | 15.6833 | 37.78
2022-02-25 13:00 | 44617.5417 | 0 | 15.6284 | 37.78
2022-02-25 13:30 | 44617.5625 | 0 | 15.9614 | 37.78
2022-02-25 14:00 | 44617.5833 | 0 | 15.4876 | 37.78
2022-02-25 14:30 | 44617.6042 | 0 | 15.3699 | 37.78
2022-02-25 15:00 | 44617.625 | 0 | 15.4641 | 37.78
2022-02-25 15:30 | 44617.6458 | 0 | 15.4504 | 37.78
2022-02-25 16:00 | 44617.6667 | 0 | 15.4928 | 37.78
2022-02-25 16:30 | 44617.6875 | 0 | 15.6439 | 37.78
2022-02-25 17:00 | 44617.7083 | 0 | 15.212 | 37.78
2022-02-25 17:30 | 44617.7292 | 0 | 15.3575 | 37.78
2022-02-25 18:00 | 44617.75 | 0 | 15.1823 | 37.78
2022-02-25 18:30 | 44617.7708 | 0 | 15.2819 | 37.78
2022-02-25 19:00 | 44617.7917 | 0 | 15.0818 | 37.78
2022-02-25 19:30 | 44617.8125 | 0 | 14.5621 | 37.78
2022-02-25 20:00 | 44617.8333 | 0 | 14.3213 | 37.78
2022-02-25 20:30 | 44617.8542 | 0 | 14.0389 | 37.78
2022-02-25 21:00 | 44617.875 | 0 | 13.5867 | 37.78
2022-02-25 21:30 | 44617.8958 | 0 | 13.3647 | 37.78
2022-02-25 22:00 | 44617.9167 | 0 | 12.6315 | 37.78
2022-02-25 22:30 | 44617.9375 | 0 | 11.9715 | 37.78
2022-02-25 23:00 | 44617.9583 | 0 | 11.5507 | 37.78
2022-02-25 23:30 | 44617.9792 | 0 | 11.1876 | 37.78
2022-02-26 | 44618 | 0 | 10.5481 | 37.78
2022-02-26 00:30 | 44618.0208 | 0 | 10.0074 | 37.78
2022-02-26 01:00 | 44618.0417 | 0 | 9.6581 | 37.78
2022-02-26 01:30 | 44618.0625 | 0 | 9.4863 | 37.78
2022-02-26 02:00 | 44618.0833 | 0 | 9.2148 | 37.78
2022-02-26 02:30 | 44618.1042 | 0 | 9.3983 | 37.78
2022-02-26 03:00 | 44618.125 | 0 | 9.3252 | 37.78
2022-02-26 03:30 | 44618.1458 | 0 | 9.3399 | 37.78
2022-02-26 04:00 | 44618.1667 | 0 | 9.3972 | 37.78
2022-02-26 04:30 | 44618.1875 | 0 | 9.5895 | 37.78
2022-02-26 05:00 | 44618.2083 | 0 | 9.6117 | 37.78
2022-02-26 05:30 | 44618.2292 | 0 | 9.6664 | 37.78
2022-02-26 06:00 | 44618.25 | 0 | 9.8303 | 37.78
2022-02-26 06:30 | 44618.2708 | 0 | 10.257 | 37.78
2022-02-26 07:00 | 44618.2917 | 0 | 10.9052 | 37.78
2022-02-26 07:30 | 44618.3125 | 0 | 11.5037 | 37.78
2022-02-26 08:00 | 44618.3333 | 0 | 11.9968 | 37.78
2022-02-26 08:30 | 44618.3542 | 0 | 12.974 | 37.78
2022-02-26 09:00 | 44618.375 | 0 | 13.118 | 37.78
2022-02-26 09:30 | 44618.3958 | 0 | 13.2508 | 37.78
2022-02-26 10:00 | 44618.4167 | 0 | 13.2559 | 37.78
2022-02-26 10:30 | 44618.4375 | 0 | 13.1452 | 37.78
2022-02-26 11:00 | 44618.4583 | 0 | 13.0076 | 37.78
2022-02-26 11:30 | 44618.4792 | 0 | 13.6267 | 37.78
2022-02-26 12:00 | 44618.5 | 0 | 13.6912 | 37.78
2022-02-26 12:30 | 44618.5208 | 0 | 13.5025 | 37.78
2022-02-26 13:00 | 44618.5417 | 0 | 13.1774 | 37.78
2022-02-26 13:30 | 44618.5625 | 0 | 13.3248 | 37.78
2022-02-26 14:00 | 44618.5833 | 0 | 13.2618 | 37.78
2022-02-26 14:30 | 44618.6042 | 0 | 12.578 | 37.78
2022-02-26 15:00 | 44618.625 | 0 | 12.8161 | 37.78
2022-02-26 15:30 | 44618.6458 | 0 | 12.597 | 37.78
2022-02-26 16:00 | 44618.6667 | 0 | 12.8277 | 37.78
2022-02-26 16:30 | 44618.6875 | 0 | 13.0162 | 37.78
2022-02-26 17:00 | 44618.7083 | 0 | 13.0336 | 37.78
2022-02-26 17:30 | 44618.7292 | 0 | 13.2162 | 37.78
2022-02-26 18:00 | 44618.75 | 0 | 13.4256 | 37.78
2022-02-26 18:30 | 44618.7708 | 0 | 13.541 | 37.78
2022-02-26 19:00 | 44618.7917 | 0 | 13.069 | 37.78
2022-02-26 19:30 | 44618.8125 | 0 | 12.7669 | 37.78
2022-02-26 20:00 | 44618.8333 | 0 | 12.5241 | 37.78
2022-02-26 20:30 | 44618.8542 | 0 | 12.1451 | 37.78
2022-02-26 21:00 | 44618.875 | 0 | 11.9194 | 37.78
2022-02-26 21:30 | 44618.8958 | 0 | 11.4069 | 37.78
2022-02-26 22:00 | 44618.9167 | 0 | 11.1055 | 37.78
2022-02-26 22:30 | 44618.9375 | 0 | 10.3807 | 37.78
2022-02-26 23:00 | 44618.9583 | 0 | 9.7765 | 37.78
2022-02-26 23:30 | 44618.9792 | 0 | 9.459 | 37.78
2022-02-27 | 44619 | 0 | 9.2902 | 37.78
2022-02-27 00:30 | 44619.0208 | 0 | 8.9792 | 37.78
2022-02-27 01:00 | 44619.0417 | 0 | 8.8189 | 37.78
2022-02-27 01:30 | 44619.0625 | 0 | 8.5148 | 37.78
2022-02-27 02:00 | 44619.0833 | 0 | 8.3487 | 37.78
2022-02-27 02:30 | 44619.1042 | 0 | 8.3338 | 37.78
2022-02-27 03:00 | 44619.125 | 0 | 8.155 | 37.78
2022-02-27 03:30 | 44619.1458 | 0 | 8.165 | 37.78
2022-02-27 04:00 | 44619.1667 | 0 | 8.139 | 37.78
2022-02-27 04:30 | 44619.1875 | 0 | 8.0756 | 37.78
2022-02-27 05:00 | 44619.2083 | 0 | 8.0971 | 37.78
2022-02-27 05:30 | 44619.2292 | 0 | 8.4578 | 37.78
2022-02-27 06:00 | 44619.25 | 0 | 8.6147 | 37.78
2022-02-27 06:30 | 44619.2708 | 0 | 8.7991 | 37.78
2022-02-27 07:00 | 44619.2917 | 0 | 9.1851 | 37.78
2022-02-27 07:30 | 44619.3125 | 0 | 9.6639 | 37.78
2022-02-27 08:00 | 44619.3333 | 0 | 10.1442 | 37.78
2022-02-27 08:30 | 44619.3542 | 0 | 10.9034 | 37.78
2022-02-27 09:00 | 44619.375 | 0 | 11.5958 | 37.78
2022-02-27 09:30 | 44619.3958 | 0 | 11.8662 | 37.78
2022-02-27 10:00 | 44619.4167 | 0 | 12.0063 | 37.78
2022-02-27 10:30 | 44619.4375 | 0 | 11.805 | 37.78
2022-02-27 11:00 | 44619.4583 | 0 | 11.3476 | 37.78
2022-02-27 11:30 | 44619.4792 | 0 | 11.8998 | 37.78
2022-02-27 12:00 | 44619.5 | 0 | 12.1477 | 37.78
2022-02-27 12:30 | 44619.5208 | 0 | 12.2978 | 37.78
2022-02-27 13:00 | 44619.5417 | 0 | 12.4717 | 37.78
2022-02-27 13:30 | 44619.5625 | 0 | 12.5881 | 37.78
2022-02-27 14:00 | 44619.5833 | 0 | 12.3648 | 37.78
2022-02-27 14:30 | 44619.6042 | 0 | 12.3699 | 37.78
2022-02-27 15:00 | 44619.625 | 0 | 12.2718 | 37.78
2022-02-27 15:30 | 44619.6458 | 0 | 12.3463 | 37.78
2022-02-27 16:00 | 44619.6667 | 0 | 12.5274 | 37.78
2022-02-27 16:30 | 44619.6875 | 0 | 12.7856 | 37.78
2022-02-27 17:00 | 44619.7083 | 0 | 12.6997 | 37.78
2022-02-27 17:30 | 44619.7292 | 0 | 12.818 | 37.78
2022-02-27 18:00 | 44619.75 | 0 | 12.9069 | 37.78
2022-02-27 18:30 | 44619.7708 | 0 | 12.9404 | 37.78
2022-02-27 19:00 | 44619.7917 | 0 | 12.4883 | 37.78
2022-02-27 19:30 | 44619.8125 | 0 | 12.2506 | 37.78
2022-02-27 20:00 | 44619.8333 | 0 | 11.7044 | 37.78
2022-02-27 20:30 | 44619.8542 | 0 | 11.1426 | 37.78
2022-02-27 21:00 | 44619.875 | 0 | 10.9097 | 37.78
2022-02-27 21:30 | 44619.8958 | 0 | 10.7766 | 37.78
2022-02-27 22:00 | 44619.9167 | 0 | 10.3573 | 37.78
2022-02-27 22:30 | 44619.9375 | 0 | 9.534 | 37.78
2022-02-27 23:00 | 44619.9583 | 0 | 9.1909 | 37.78
2022-02-27 23:30 | 44619.9792 | 0 | 8.712 | 37.78
2022-02-28 | 44620 | 0 | 8.2873 | 37.78
2022-02-28 00:30 | 44620.0208 | 0 | 7.959 | 37.78
2022-02-28 01:00 | 44620.0417 | 0 | 7.8437 | 37.78
2022-02-28 01:30 | 44620.0625 | 0 | 7.6787 | 37.78
2022-02-28 02:00 | 44620.0833 | 0 | 7.7508 | 37.78
2022-02-28 02:30 | 44620.1042 | 0 | 7.8238 | 37.78
2022-02-28 03:00 | 44620.125 | 0 | 7.6577 | 37.78
2022-02-28 03:30 | 44620.1458 | 0 | 7.7743 | 37.78
2022-02-28 04:00 | 44620.1667 | 0 | 7.9766 | 37.78
2022-02-28 04:30 | 44620.1875 | 0 | 8.1516 | 37.78
2022-02-28 05:00 | 44620.2083 | 0 | 8.7555 | 37.78
2022-02-28 05:30 | 44620.2292 | 0 | 9.149 | 37.78
2022-02-28 06:00 | 44620.25 | 0 | 9.4308 | 37.78
2022-02-28 06:30 | 44620.2708 | 0 | 9.9103 | 37.78
2022-02-28 07:00 | 44620.2917 | 0 | 10.5841 | 37.78
2022-02-28 07:30 | 44620.3125 | 0 | 10.284 | 37.78
2022-02-28 08:00 | 44620.3333 | 0 | 9.5834 | 37.78
2022-02-28 08:30 | 44620.3542 | 0 | 10.396 | 37.78
2022-02-28 09:00 | 44620.375 | 0 | 9.9266 | 37.78
2022-02-28 09:30 | 44620.3958 | 0 | 10.6736 | 37.78
2022-02-28 10:00 | 44620.4167 | 0 | 9.7505 | 37.78
2022-02-28 10:30 | 44620.4375 | 0 | 9.3519 | 37.78
2022-02-28 11:00 | 44620.4583 | 0 | 9.8426 | 37.78
2022-02-28 11:30 | 44620.4792 | 0 | 10.8477 | 37.78
2022-02-28 12:00 | 44620.5 | 0 | 11.6264 | 37.78
2022-02-28 12:30 | 44620.5208 | 0 | 12.1979 | 37.78
2022-02-28 13:00 | 44620.5417 | 0 | 13.181 | 37.78
2022-02-28 13:30 | 44620.5625 | 0 | 14.1249 | 37.78
2022-02-28 14:00 | 44620.5833 | 0 | 15.9307 | 37.78
2022-02-28 14:30 | 44620.6042 | 0 | 13.5648 | 37.78
2022-02-28 15:00 | 44620.625 | 0 | 13.3828 | 37.78
2022-02-28 15:30 | 44620.6458 | 0 | 15.2705 | 37.78
2022-02-28 16:00 | 44620.6667 | 0 | 15.7145 | 37.78
2022-02-28 16:30 | 44620.6875 | 0 | 14.2178 | 37.78
2022-02-28 17:00 | 44620.7083 | 0 | 14.7618 | 37.78
2022-02-28 17:30 | 44620.7292 | 0 | 14.7148 | 37.78
2022-02-28 18:00 | 44620.75 | 0 | 15.2892 | 37.78
2022-02-28 18:30 | 44620.7708 | 0 | 16.0446 | 37.78
2022-02-28 19:00 | 44620.7917 | 0 | 15.5448 | 37.78
2022-02-28 19:30 | 44620.8125 | 0 | 15.1229 | 37.78
2022-02-28 20:00 | 44620.8333 | 0 | 14.7243 | 37.78
2022-02-28 20:30 | 44620.8542 | 0 | 14.0274 | 37.78
2022-02-28 21:00 | 44620.875 | 0 | 13.6857 | 37.78
2022-02-28 21:30 | 44620.8958 | 0 | 12.962 | 37.78
2022-02-28 22:00 | 44620.9167 | 0 | 12.4671 | 37.78
2022-02-28 22:30 | 44620.9375 | 0 | 11.4941 | 37.78
2022-02-28 23:00 | 44620.9583 | 0 | 10.8659 | 37.78
2022-02-28 23:30 | 44620.9792 | 0 | 10.5633 | 37.78
2022-03-01 | 44621 | 0 | 9.9511 | 37.78
2022-03-01 00:30 | 44621.0208 | 0 | 9.4507 | 37.78
2022-03-01 01:00 | 44621.0417 | 0 | 9.2667 | 37.78
2022-03-01 01:30 | 44621.0625 | 0 | 9.0447 | 37.78
2022-03-01 02:00 | 44621.0833 | 0 | 8.9329 | 37.78
2022-03-01 02:30 | 44621.1042 | 0 | 8.9516 | 37.78
2022-03-01 03:00 | 44621.125 | 0 | 8.7404 | 37.78
2022-03-01 03:30 | 44621.1458 | 0 | 8.6615 | 37.78
2022-03-01 04:00 | 44621.1667 | 0 | 9.0441 | 37.78
2022-03-01 04:30 | 44621.1875 | 0 | 9.1455 | 37.78
2022-03-01 05:00 | 44621.2083 | 0 | 9.9559 | 37.78
2022-03-01 05:30 | 44621.2292 | 0 | 10.337 | 37.78
2022-03-01 06:00 | 44621.25 | 0 | 10.7324 | 37.78
2022-03-01 06:30 | 44621.2708 | 0 | 11.3349 | 37.78
2022-03-01 07:00 | 44621.2917 | 0 | 11.695 | 37.78
2022-03-01 07:30 | 44621.3125 | 0 | 11.7118 | 37.78
2022-03-01 08:00 | 44621.3333 | 0 | 12.1365 | 37.78
2022-03-01 08:30 | 44621.3542 | 0 | 12.1066 | 37.78
2022-03-01 09:00 | 44621.375 | 0 | 11.6915 | 37.78
2022-03-01 09:30 | 44621.3958 | 0 | 12.7308 | 37.78
2022-03-01 10:00 | 44621.4167 | 0 | 13.8129 | 37.78
2022-03-01 10:30 | 44621.4375 | 0 | 13.5113 | 37.78
2022-03-01 11:00 | 44621.4583 | 0 | 14.51 | 37.78
2022-03-01 11:30 | 44621.4792 | 0 | 14.7764 | 37.78
2022-03-01 12:00 | 44621.5 | 0 | 15.5568 | 37.78
2022-03-01 12:30 | 44621.5208 | 0 | 14.1074 | 37.78
2022-03-01 13:00 | 44621.5417 | 0 | 14.2065 | 37.78
2022-03-01 13:30 | 44621.5625 | 0 | 14.9284 | 37.78
2022-03-01 14:00 | 44621.5833 | 0 | 15.1465 | 37.78
2022-03-01 14:30 | 44621.6042 | 0 | 15.6361 | 37.78
2022-03-01 15:00 | 44621.625 | 0 | 15.5653 | 37.78
2022-03-01 15:30 | 44621.6458 | 0 | 15.6667 | 37.78
2022-03-01 16:00 | 44621.6667 | 0 | 16.862 | 37.78
2022-03-01 16:30 | 44621.6875 | 0 | 17.0663 | 37.78
2022-03-01 17:00 | 44621.7083 | 0 | 17.7465 | 37.78
2022-03-01 17:30 | 44621.7292 | 0 | 18.1355 | 37.78
2022-03-01 18:00 | 44621.75 | 0 | 17.9256 | 37.78
2022-03-01 18:30 | 44621.7708 | 0 | 18.4007 | 37.78
2022-03-01 19:00 | 44621.7917 | 0 | 18.1362 | 37.78
2022-03-01 19:30 | 44621.8125 | 0 | 17.6992 | 37.78
2022-03-01 20:00 | 44621.8333 | 0 | 16.842 | 37.78
2022-03-01 20:30 | 44621.8542 | 0 | 16.3633 | 37.78
2022-03-01 21:00 | 44621.875 | 0 | 15.5183 | 37.78
2022-03-01 21:30 | 44621.8958 | 0 | 15.0036 | 37.78
2022-03-01 22:00 | 44621.9167 | 0 | 13.9957 | 37.78
2022-03-01 22:30 | 44621.9375 | 0 | 13.1626 | 37.78
2022-03-01 23:00 | 44621.9583 | 0 | 12.2438 | 37.78
2022-03-01 23:30 | 44621.9792 | 0 | 11.7839 | 37.78
2022-03-02 | 44622 | 0 | 10.9537 | 37.78
2022-03-02 00:30 | 44622.0208 | 0 | 10.4629 | 37.78
2022-03-02 01:00 | 44622.0417 | 0 | 10.16 | 37.78
2022-03-02 01:30 | 44622.0625 | 0 | 9.9206 | 37.78
2022-03-02 02:00 | 44622.0833 | 0 | 9.7841 | 37.78
2022-03-02 02:30 | 44622.1042 | 0 | 9.8239 | 37.78
2022-03-02 03:00 | 44622.125 | 0 | 9.6531 | 37.78
2022-03-02 03:30 | 44622.1458 | 0 | 9.6193 | 37.78
2022-03-02 04:00 | 44622.1667 | 0 | 9.9995 | 37.78
2022-03-02 04:30 | 44622.1875 | 0 | 10.102 | 37.78
2022-03-02 05:00 | 44622.2083 | 0 | 10.703 | 37.78
2022-03-02 05:30 | 44622.2292 | 0 | 11.0833 | 37.78
2022-03-02 06:00 | 44622.25 | 0 | 11.8056 | 37.78
2022-03-02 06:30 | 44622.2708 | 0 | 12.2585 | 37.78
2022-03-02 07:00 | 44622.2917 | 0 | 13.0228 | 37.78
2022-03-02 07:30 | 44622.3125 | 0 | 13.4285 | 37.78
2022-03-02 08:00 | 44622.3333 | 0 | 13.5757 | 37.78
2022-03-02 08:30 | 44622.3542 | 0 | 13.6465 | 37.78
2022-03-02 09:00 | 44622.375 | 0 | 13.5809 | 37.78
2022-03-02 09:30 | 44622.3958 | 0 | 14.1296 | 37.78
2022-03-02 10:00 | 44622.4167 | 0 | 14.2393 | 37.78
2022-03-02 10:30 | 44622.4375 | 0 | 14.2312 | 37.78
2022-03-02 11:00 | 44622.4583 | 0 | 16.6989 | 37.78
2022-03-02 11:30 | 44622.4792 | 0 | 17.6549 | 37.78
2022-03-02 12:00 | 44622.5 | 0 | 17.8938 | 37.78
2022-03-02 12:30 | 44622.5208 | 0 | 15.9231 | 37.78
2022-03-02 13:00 | 44622.5417 | 0 | 14.8717 | 37.78
2022-03-02 13:30 | 44622.5625 | 0 | 16.6319 | 37.78
2022-03-02 14:00 | 44622.5833 | 0 | 17.6907 | 37.78
2022-03-02 14:30 | 44622.6042 | 0 | 18.2118 | 37.78
2022-03-02 15:00 | 44622.625 | 0 | 18.186 | 37.78
2022-03-02 15:30 | 44622.6458 | 0 | 18.912 | 37.78
2022-03-02 16:00 | 44622.6667 | 0 | 19.5017 | 37.78
2022-03-02 16:30 | 44622.6875 | 0 | 19.9096 | 37.78
2022-03-02 17:00 | 44622.7083 | 0 | 20.1576 | 37.78
2022-03-02 17:30 | 44622.7292 | 0 | 19.6218 | 37.78
2022-03-02 18:00 | 44622.75 | 0 | 19.459 | 37.78
2022-03-02 18:30 | 44622.7708 | 0 | 19.6604 | 37.78
2022-03-02 19:00 | 44622.7917 | 0 | 19.3198 | 37.78
2022-03-02 19:30 | 44622.8125 | 0 | 18.8846 | 37.78
2022-03-02 20:00 | 44622.8333 | 0 | 18.3411 | 37.78
2022-03-02 20:30 | 44622.8542 | 0 | 17.6446 | 37.78
2022-03-02 21:00 | 44622.875 | 0 | 17.218 | 37.78
2022-03-02 21:30 | 44622.8958 | 0 | 16.2478 | 37.78
2022-03-02 22:00 | 44622.9167 | 0 | 15.3139 | 37.78
2022-03-02 22:30 | 44622.9375 | 0 | 14.1943 | 37.78
2022-03-02 23:00 | 44622.9583 | 0 | 13.6189 | 37.78
2022-03-02 23:30 | 44622.9792 | 0 | 13.0559 | 37.78
2022-03-03 | 44623 | 0 | 12.2988 | 37.78
2022-03-03 00:30 | 44623.0208 | 0 | 11.8468 | 37.78
2022-03-03 01:00 | 44623.0417 | 0 | 11.1079 | 37.78
2022-03-03 01:30 | 44623.0625 | 0 | 10.8101 | 37.78
2022-03-03 02:00 | 44623.0833 | 0 | 10.5981 | 37.78
2022-03-03 02:30 | 44623.1042 | 0 | 10.7209 | 37.78
2022-03-03 03:00 | 44623.125 | 0 | 10.5167 | 37.78
2022-03-03 03:30 | 44623.1458 | 0 | 10.484 | 37.78
2022-03-03 04:00 | 44623.1667 | 0 | 10.6736 | 37.78
2022-03-03 04:30 | 44623.1875 | 0 | 11.0163 | 37.78
2022-03-03 05:00 | 44623.2083 | 0 | 11.5355 | 37.78
2022-03-03 05:30 | 44623.2292 | 0 | 12.0702 | 37.78
2022-03-03 06:00 | 44623.25 | 0 | 12.859 | 37.78
2022-03-03 06:30 | 44623.2708 | 0 | 13.6826 | 37.78
2022-03-03 07:00 | 44623.2917 | 0 | 14.6179 | 37.78
2022-03-03 07:30 | 44623.3125 | 0 | 14.6836 | 37.78
2022-03-03 08:00 | 44623.3333 | 0 | 15.1045 | 37.78
2022-03-03 08:30 | 44623.3542 | 0 | 14.9663 | 37.78
2022-03-03 09:00 | 44623.375 | 0 | 14.7874 | 37.78
2022-03-03 09:30 | 44623.3958 | 0 | 14.3204 | 37.78
2022-03-03 10:00 | 44623.4167 | 0 | 13.1662 | 37.78
2022-03-03 10:30 | 44623.4375 | 0 | 14.8282 | 37.78
2022-03-03 11:00 | 44623.4583 | 0 | 15.1614 | 37.78
2022-03-03 11:30 | 44623.4792 | 0 | 15.0221 | 37.78
2022-03-03 12:00 | 44623.5 | 0 | 13.2818 | 37.78
2022-03-03 12:30 | 44623.5208 | 0 | 11.0433 | 37.78
2022-03-03 13:00 | 44623.5417 | 0 | 10.8887 | 37.78
2022-03-03 13:30 | 44623.5625 | 0 | 12.6059 | 37.78
2022-03-03 14:00 | 44623.5833 | 0 | 11.7257 | 37.78
2022-03-03 14:30 | 44623.6042 | 0 | 12.2031 | 37.78
2022-03-03 15:00 | 44623.625 | 0 | 12.7088 | 37.78
2022-03-03 15:30 | 44623.6458 | 0 | 13.3837 | 37.78
2022-03-03 16:00 | 44623.6667 | 0 | 14.2294 | 37.78
2022-03-03 16:30 | 44623.6875 | 0 | 15.8716 | 37.78
2022-03-03 17:00 | 44623.7083 | 0 | 15.6488 | 37.78
2022-03-03 17:30 | 44623.7292 | 0 | 15.7817 | 37.78
2022-03-03 18:00 | 44623.75 | 0 | 15.8587 | 37.78
2022-03-03 18:30 | 44623.7708 | 0 | 16.3832 | 37.78
2022-03-03 19:00 | 44623.7917 | 0 | 16.0386 | 37.78
2022-03-03 19:30 | 44623.8125 | 0 | 15.691 | 37.78
2022-03-03 20:00 | 44623.8333 | 0 | 15.1553 | 37.78
2022-03-03 20:30 | 44623.8542 | 0 | 14.5509 | 37.78
2022-03-03 21:00 | 44623.875 | 0 | 14.1562 | 37.78
2022-03-03 21:30 | 44623.8958 | 0 | 13.6764 | 37.78
2022-03-03 22:00 | 44623.9167 | 0 | 13.0107 | 37.78
2022-03-03 22:30 | 44623.9375 | 0 | 12.3345 | 37.78
2022-03-03 23:00 | 44623.9583 | 0 | 11.6849 | 37.78
2022-03-03 23:30 | 44623.9792 | 0 | 11.0236 | 37.78
2022-03-04 | 44624 | 0 | 10.2658 | 37.78
2022-03-04 00:30 | 44624.0208 | 0 | 9.7343 | 37.78
2022-03-04 01:00 | 44624.0417 | 0 | 9.5546 | 37.78
2022-03-04 01:30 | 44624.0625 | 0 | 9.2914 | 37.78
2022-03-04 02:00 | 44624.0833 | 0 | 9.1229 | 37.78
2022-03-04 02:30 | 44624.1042 | 0 | 9.1861 | 37.78
2022-03-04 03:00 | 44624.125 | 0 | 8.8571 | 37.78
2022-03-04 03:30 | 44624.1458 | 0 | 8.9232 | 37.78
2022-03-04 04:00 | 44624.1667 | 0 | 9.2599 | 37.78
2022-03-04 04:30 | 44624.1875 | 0 | 9.7459 | 37.78
2022-03-04 05:00 | 44624.2083 | 0 | 10.3486 | 37.78
2022-03-04 05:30 | 44624.2292 | 0 | 10.906 | 37.78
2022-03-04 06:00 | 44624.25 | 0 | 11.5847 | 37.78
2022-03-04 06:30 | 44624.2708 | 0 | 11.9959 | 37.78
2022-03-04 07:00 | 44624.2917 | 0 | 12.3413 | 37.78
2022-03-04 07:30 | 44624.3125 | 0 | 12.8406 | 37.78
2022-03-04 08:00 | 44624.3333 | 0 | 13.5961 | 37.78
2022-03-04 08:30 | 44624.3542 | 0 | 13.3571 | 37.78
2022-03-04 09:00 | 44624.375 | 0 | 14.0469 | 37.78
2022-03-04 09:30 | 44624.3958 | 0 | 14.4293 | 37.78
2022-03-04 10:00 | 44624.4167 | 0 | 14.8343 | 37.78
2022-03-04 10:30 | 44624.4375 | 0 | 13.4621 | 37.78
2022-03-04 11:00 | 44624.4583 | 0 | 14.4198 | 37.78
2022-03-04 11:30 | 44624.4792 | 0 | 15.0548 | 37.78
2022-03-04 12:00 | 44624.5 | 0 | 14.0042 | 37.78
2022-03-04 12:30 | 44624.5208 | 0 | 13.5279 | 37.78
2022-03-04 13:00 | 44624.5417 | 0 | 14.8686 | 37.78
2022-03-04 13:30 | 44624.5625 | 0 | 15.9311 | 37.78
2022-03-04 14:00 | 44624.5833 | 0 | 15.8032 | 37.78
2022-03-04 14:30 | 44624.6042 | 0 | 16.3881 | 37.78
2022-03-04 15:00 | 44624.625 | 0 | 16.092 | 37.78
2022-03-04 15:30 | 44624.6458 | 0 | 14.5253 | 37.78
2022-03-04 16:00 | 44624.6667 | 0 | 14.5338 | 37.78
2022-03-04 16:30 | 44624.6875 | 0 | 15.2018 | 37.78
2022-03-04 17:00 | 44624.7083 | 0 | 15.8614 | 37.78
2022-03-04 17:30 | 44624.7292 | 0 | 16.4137 | 37.78
2022-03-04 18:00 | 44624.75 | 0 | 16.1887 | 37.78
2022-03-04 18:30 | 44624.7708 | 0 | 16.7881 | 37.78
2022-03-04 19:00 | 44624.7917 | 0 | 16.5333 | 37.78
2022-03-04 19:30 | 44624.8125 | 0 | 16.1089 | 37.78
2022-03-04 20:00 | 44624.8333 | 0 | 15.5403 | 37.78
2022-03-04 20:30 | 44624.8542 | 0 | 15.1562 | 37.78
2022-03-04 21:00 | 44624.875 | 0 | 14.5832 | 37.78
2022-03-04 21:30 | 44624.8958 | 0 | 14.4193 | 37.78
2022-03-04 22:00 | 44624.9167 | 0 | 13.6942 | 37.78
2022-03-04 22:30 | 44624.9375 | 0 | 12.8656 | 37.78
2022-03-04 23:00 | 44624.9583 | 0 | 12.1053 | 37.78
2022-03-04 23:30 | 44624.9792 | 0 | 11.3123 | 37.78
2022-03-05 | 44625 | 0 | 10.567 | 37.78
2022-03-05 00:30 | 44625.0208 | 0 | 10.1829 | 37.78
2022-03-05 01:00 | 44625.0417 | 0 | 10.0458 | 37.78
2022-03-05 01:30 | 44625.0625 | 0 | 9.7593 | 37.78
2022-03-05 02:00 | 44625.0833 | 0 | 9.4417 | 37.78
2022-03-05 02:30 | 44625.1042 | 0 | 9.4814 | 37.78
2022-03-05 03:00 | 44625.125 | 0 | 9.128 | 37.78
2022-03-05 03:30 | 44625.1458 | 0 | 9.1253 | 37.78
2022-03-05 04:00 | 44625.1667 | 0 | 9.3697 | 37.78
2022-03-05 04:30 | 44625.1875 | 0 | 9.3389 | 37.78
2022-03-05 05:00 | 44625.2083 | 0 | 9.3301 | 37.78
2022-03-05 05:30 | 44625.2292 | 0 | 9.556 | 37.78
2022-03-05 06:00 | 44625.25 | 0 | 9.6106 | 37.78
2022-03-05 06:30 | 44625.2708 | 0 | 9.9156 | 37.78
2022-03-05 07:00 | 44625.2917 | 0 | 10.0509 | 37.78
2022-03-05 07:30 | 44625.3125 | 0 | 9.8449 | 37.78
2022-03-05 08:00 | 44625.3333 | 0 | 9.9131 | 37.78
2022-03-05 08:30 | 44625.3542 | 0 | 9.9654 | 37.78
2022-03-05 09:00 | 44625.375 | 0 | 9.9441 | 37.78
2022-03-05 09:30 | 44625.3958 | 0 | 9.9951 | 37.78
2022-03-05 10:00 | 44625.4167 | 0 | 10.0016 | 37.78
2022-03-05 10:30 | 44625.4375 | 0 | 10.9887 | 37.78
2022-03-05 11:00 | 44625.4583 | 0 | 11.0293 | 37.78
2022-03-05 11:30 | 44625.4792 | 0 | 11.7173 | 37.78
2022-03-05 12:00 | 44625.5 | 0 | 11.6712 | 37.78
2022-03-05 12:30 | 44625.5208 | 0 | 12.0657 | 37.78
2022-03-05 13:00 | 44625.5417 | 0 | 13.2919 | 37.78
2022-03-05 13:30 | 44625.5625 | 0 | 14.4122 | 37.78
2022-03-05 14:00 | 44625.5833 | 0 | 15.9014 | 37.78
2022-03-05 14:30 | 44625.6042 | 0 | 13.5965 | 37.78
2022-03-05 15:00 | 44625.625 | 0 | 14.0674 | 37.78
2022-03-05 15:30 | 44625.6458 | 0 | 15.6024 | 37.78
2022-03-05 16:00 | 44625.6667 | 0 | 15.6607 | 37.78
2022-03-05 16:30 | 44625.6875 | 0 | 16.6281 | 37.78
2022-03-05 17:00 | 44625.7083 | 0 | 17.1542 | 37.78
2022-03-05 17:30 | 44625.7292 | 0 | 17.3437 | 37.78
2022-03-05 18:00 | 44625.75 | 0 | 17.1353 | 37.78
2022-03-05 18:30 | 44625.7708 | 0 | 17.3029 | 37.78
2022-03-05 19:00 | 44625.7917 | 0 | 17.2008 | 37.78
2022-03-05 19:30 | 44625.8125 | 0 | 16.7879 | 37.78
2022-03-05 20:00 | 44625.8333 | 0 | 16.0311 | 37.78
2022-03-05 20:30 | 44625.8542 | 0 | 15.6872 | 37.78
2022-03-05 21:00 | 44625.875 | 0 | 15.1438 | 37.78
2022-03-05 21:30 | 44625.8958 | 0 | 14.7693 | 37.78
2022-03-05 22:00 | 44625.9167 | 0 | 13.972 | 37.78
2022-03-05 22:30 | 44625.9375 | 0 | 13.1552 | 37.78
2022-03-05 23:00 | 44625.9583 | 0 | 12.3483 | 37.78
2022-03-05 23:30 | 44625.9792 | 0 | 11.7652 | 37.78
2022-03-06 | 44626 | 0 | 11.2293 | 37.78
2022-03-06 00:30 | 44626.0208 | 0 | 10.8111 | 37.78
2022-03-06 01:00 | 44626.0417 | 0 | 10.681 | 37.78
2022-03-06 01:30 | 44626.0625 | 0 | 10.296 | 37.78
2022-03-06 02:00 | 44626.0833 | 0 | 10.1194 | 37.78
2022-03-06 02:30 | 44626.1042 | 0 | 10.0707 | 37.78
2022-03-06 03:00 | 44626.125 | 0 | 9.8151 | 37.78
2022-03-06 03:30 | 44626.1458 | 0 | 9.6638 | 37.78
2022-03-06 04:00 | 44626.1667 | 0 | 9.4286 | 37.78
2022-03-06 04:30 | 44626.1875 | 0 | 9.4393 | 37.78
2022-03-06 05:00 | 44626.2083 | 0 | 9.5248 | 37.78
2022-03-06 05:30 | 44626.2292 | 0 | 9.3872 | 37.78
2022-03-06 06:00 | 44626.25 | 0 | 9.3947 | 37.78
2022-03-06 06:30 | 44626.2708 | 0 | 9.5026 | 37.78
2022-03-06 07:00 | 44626.2917 | 0 | 9.3327 | 37.78
2022-03-06 07:30 | 44626.3125 | 0 | 9.4924 | 37.78
2022-03-06 08:00 | 44626.3333 | 0 | 9.7075 | 37.78
2022-03-06 08:30 | 44626.3542 | 0 | 9.9906 | 37.78
2022-03-06 09:00 | 44626.375 | 0 | 10.6022 | 37.78
2022-03-06 09:30 | 44626.3958 | 0 | 11.7022 | 37.78
2022-03-06 10:00 | 44626.4167 | 0 | 12.4585 | 37.78
2022-03-06 10:30 | 44626.4375 | 0 | 13.1936 | 37.78
2022-03-06 11:00 | 44626.4583 | 0 | 13.3773 | 37.78
2022-03-06 11:30 | 44626.4792 | 0 | 14.2962 | 37.78
2022-03-06 12:00 | 44626.5 | 0 | 14.4279 | 37.78
2022-03-06 12:30 | 44626.5208 | 0 | 16.6306 | 37.78
2022-03-06 13:00 | 44626.5417 | 0 | 18.6442 | 37.78
2022-03-06 13:30 | 44626.5625 | 0 | 18.98 | 37.78
2022-03-06 14:00 | 44626.5833 | 0 | 18.9081 | 37.78
2022-03-06 14:30 | 44626.6042 | 0 | 18.9937 | 37.78
2022-03-06 15:00 | 44626.625 | 0 | 17.816 | 37.78
2022-03-06 15:30 | 44626.6458 | 0 | 18.0969 | 37.78
2022-03-06 16:00 | 44626.6667 | 0 | 18.448 | 37.78
2022-03-06 16:30 | 44626.6875 | 0 | 19.2871 | 37.78
2022-03-06 17:00 | 44626.7083 | 0 | 19.4289 | 37.78
2022-03-06 17:30 | 44626.7292 | 0 | 18.4913 | 37.78
2022-03-06 18:00 | 44626.75 | 0 | 17.249 | 37.78
2022-03-06 18:30 | 44626.7708 | 0 | 17.1317 | 37.78
2022-03-06 19:00 | 44626.7917 | 0 | 16.4521 | 37.78
2022-03-06 19:30 | 44626.8125 | 0 | 15.8957 | 37.78
2022-03-06 20:00 | 44626.8333 | 0 | 15.1965 | 37.78
2022-03-06 20:30 | 44626.8542 | 0 | 14.5929 | 37.78
2022-03-06 21:00 | 44626.875 | 0 | 14.0492 | 37.78
2022-03-06 21:30 | 44626.8958 | 0 | 13.3185 | 37.78
2022-03-06 22:00 | 44626.9167 | 0 | 12.4638 | 37.78
2022-03-06 22:30 | 44626.9375 | 0 | 11.507 | 37.78
2022-03-06 23:00 | 44626.9583 | 0 | 10.8982 | 37.78
2022-03-06 23:30 | 44626.9792 | 0 | 10.4017 | 37.78
2022-03-07 | 44627 | 0 | 10.0273 | 37.78
2022-03-07 00:30 | 44627.0208 | 0 | 9.7988 | 37.78
2022-03-07 01:00 | 44627.0417 | 0 | 9.7643 | 37.78
2022-03-07 01:30 | 44627.0625 | 0 | 9.3891 | 37.78
2022-03-07 02:00 | 44627.0833 | 0 | 9.1824 | 37.78
2022-03-07 02:30 | 44627.1042 | 0 | 9.2865 | 37.78
2022-03-07 03:00 | 44627.125 | 0 | 9.0745 | 37.78
2022-03-07 03:30 | 44627.1458 | 0 | 9.0833 | 37.78
2022-03-07 04:00 | 44627.1667 | 0 | 9.3897 | 37.78
2022-03-07 04:30 | 44627.1875 | 0 | 9.7096 | 37.78
2022-03-07 05:00 | 44627.2083 | 0 | 10.4278 | 37.78
2022-03-07 05:30 | 44627.2292 | 0 | 10.9379 | 37.78
2022-03-07 06:00 | 44627.25 | 0 | 11.906 | 37.78
2022-03-07 06:30 | 44627.2708 | 0 | 12.2334 | 37.78
2022-03-07 07:00 | 44627.2917 | 0 | 12.4563 | 37.78
2022-03-07 07:30 | 44627.3125 | 0 | 12.2258 | 37.78
2022-03-07 08:00 | 44627.3333 | 0 | 12.2519 | 37.78
2022-03-07 08:30 | 44627.3542 | 0 | 12.6442 | 37.78
2022-03-07 09:00 | 44627.375 | 0 | 13.2776 | 37.78
2022-03-07 09:30 | 44627.3958 | 0 | 11.606 | 37.78
2022-03-07 10:00 | 44627.4167 | 0 | 11.8401 | 37.78
2022-03-07 10:30 | 44627.4375 | 0 | 12.0185 | 37.78
2022-03-07 11:00 | 44627.4583 | 0 | 13.565 | 37.78
2022-03-07 11:30 | 44627.4792 | 0 | 13.3399 | 37.78
2022-03-07 12:00 | 44627.5 | 0 | 13.2971 | 37.78
2022-03-07 12:30 | 44627.5208 | 0 | 12.5835 | 37.78
2022-03-07 13:00 | 44627.5417 | 0 | 13.1741 | 37.78
2022-03-07 13:30 | 44627.5625 | 0 | 13.7706 | 37.78
2022-03-07 14:00 | 44627.5833 | 0 | 15.9684 | 37.78
2022-03-07 14:30 | 44627.6042 | 0 | 15.9851 | 37.78
2022-03-07 15:00 | 44627.625 | 0 | 17.7074 | 37.78
2022-03-07 15:30 | 44627.6458 | 0 | 16.741 | 37.78
2022-03-07 16:00 | 44627.6667 | 0 | 15.9292 | 37.78
2022-03-07 16:30 | 44627.6875 | 0 | 18.2406 | 37.78
2022-03-07 17:00 | 44627.7083 | 0 | 18.1696 | 37.78
2022-03-07 17:30 | 44627.7292 | 0 | 18.177 | 37.78
2022-03-07 18:00 | 44627.75 | 0 | 18.4129 | 37.78
2022-03-07 18:30 | 44627.7708 | 0 | 19.1723 | 37.78
2022-03-07 19:00 | 44627.7917 | 0 | 18.9435 | 37.78
2022-03-07 19:30 | 44627.8125 | 0 | 18.8313 | 37.78
2022-03-07 20:00 | 44627.8333 | 0 | 18.1112 | 37.78
2022-03-07 20:30 | 44627.8542 | 0 | 17.3626 | 37.78
2022-03-07 21:00 | 44627.875 | 0 | 16.6899 | 37.78
2022-03-07 21:30 | 44627.8958 | 0 | 15.6995 | 37.78
2022-03-07 22:00 | 44627.9167 | 0 | 14.8225 | 37.78
2022-03-07 22:30 | 44627.9375 | 0 | 13.7076 | 37.78
2022-03-07 23:00 | 44627.9583 | 0 | 13.0837 | 37.78
2022-03-07 23:30 | 44627.9792 | 0 | 12.4682 | 37.78
2022-03-08 | 44628 | 0 | 11.7659 | 37.78
2022-03-08 00:30 | 44628.0208 | 0 | 11.1339 | 37.78
2022-03-08 01:00 | 44628.0417 | 0 | 10.9057 | 37.78
2022-03-08 01:30 | 44628.0625 | 0 | 10.8389 | 37.78
2022-03-08 02:00 | 44628.0833 | 0 | 10.7679 | 37.78
2022-03-08 02:30 | 44628.1042 | 0 | 10.5422 | 37.78
2022-03-08 03:00 | 44628.125 | 0 | 10.2027 | 37.78
2022-03-08 03:30 | 44628.1458 | 0 | 10.103 | 37.78
2022-03-08 04:00 | 44628.1667 | 0 | 10.2037 | 37.78
2022-03-08 04:30 | 44628.1875 | 0 | 10.5423 | 37.78
2022-03-08 05:00 | 44628.2083 | 0 | 11.192 | 37.78
2022-03-08 05:30 | 44628.2292 | 0 | 11.8089 | 37.78
2022-03-08 06:00 | 44628.25 | 0 | 12.6339 | 37.78
2022-03-08 06:30 | 44628.2708 | 0 | 13.2412 | 37.78
2022-03-08 07:00 | 44628.2917 | 0 | 13.6974 | 37.78
2022-03-08 07:30 | 44628.3125 | 0 | 13.6253 | 37.78
2022-03-08 08:00 | 44628.3333 | 0 | 13.8301 | 37.78
2022-03-08 08:30 | 44628.3542 | 0 | 13.9846 | 37.78
2022-03-08 09:00 | 44628.375 | 0 | 14.1094 | 37.78
2022-03-08 09:30 | 44628.3958 | 0 | 14.3823 | 37.78
2022-03-08 10:00 | 44628.4167 | 0 | 14.5141 | 37.78
2022-03-08 10:30 | 44628.4375 | 0 | 16.2758 | 37.78
2022-03-08 11:00 | 44628.4583 | 0 | 17.6413 | 37.78
2022-03-08 11:30 | 44628.4792 | 0 | 17.0418 | 37.78
2022-03-08 12:00 | 44628.5 | 0 | 19.0819 | 37.78
2022-03-08 12:30 | 44628.5208 | 0 | 19.6451 | 37.78
2022-03-08 13:00 | 44628.5417 | 0 | 18.1628 | 37.78
2022-03-08 13:30 | 44628.5625 | 0 | 18.9165 | 37.78
2022-03-08 14:00 | 44628.5833 | 0 | 19.8866 | 37.78
2022-03-08 14:30 | 44628.6042 | 0 | 21.4293 | 37.78
2022-03-08 15:00 | 44628.625 | 0 | 21.0387 | 37.78
2022-03-08 15:30 | 44628.6458 | 0 | 22.2253 | 37.78
2022-03-08 16:00 | 44628.6667 | 0 | 22.8474 | 37.78
2022-03-08 16:30 | 44628.6875 | 0 | 23.6714 | 37.78
2022-03-08 17:00 | 44628.7083 | 0 | 23.9097 | 37.78
2022-03-08 17:30 | 44628.7292 | 0 | 24.4166 | 37.78
2022-03-08 18:00 | 44628.75 | 0 | 24.6341 | 37.78
2022-03-08 18:30 | 44628.7708 | 0 | 25.1345 | 37.78
2022-03-08 19:00 | 44628.7917 | 0 | 24.8084 | 37.78
2022-03-08 19:30 | 44628.8125 | 0 | 24.3751 | 37.78
2022-03-08 20:00 | 44628.8333 | 0 | 23.4021 | 37.78
2022-03-08 20:30 | 44628.8542 | 0 | 22.3177 | 37.78
2022-03-08 21:00 | 44628.875 | 0 | 21.0798 | 37.78
2022-03-08 21:30 | 44628.8958 | 0 | 19.9664 | 37.78
2022-03-08 22:00 | 44628.9167 | 0 | 18.4267 | 37.78
2022-03-08 22:30 | 44628.9375 | 0 | 17.2448 | 37.78
2022-03-08 23:00 | 44628.9583 | 0 | 15.9178 | 37.78
2022-03-08 23:30 | 44628.9792 | 0 | 15.2334 | 37.78
2022-03-09 | 44629 | 0 | 14.3256 | 37.78
2022-03-09 00:30 | 44629.0208 | 0 | 13.595 | 37.78
2022-03-09 01:00 | 44629.0417 | 0 | 13.0985 | 37.78
2022-03-09 01:30 | 44629.0625 | 0 | 12.6649 | 37.78
2022-03-09 02:00 | 44629.0833 | 0 | 12.3957 | 37.78
2022-03-09 02:30 | 44629.1042 | 0 | 12.1657 | 37.78
2022-03-09 03:00 | 44629.125 | 0 | 11.8635 | 37.78
2022-03-09 03:30 | 44629.1458 | 0 | 11.7173 | 37.78
2022-03-09 04:00 | 44629.1667 | 0 | 12.0967 | 37.78
2022-03-09 04:30 | 44629.1875 | 0 | 12.4144 | 37.78
2022-03-09 05:00 | 44629.2083 | 0 | 13.1745 | 37.78
2022-03-09 05:30 | 44629.2292 | 0 | 13.2841 | 37.78
2022-03-09 06:00 | 44629.25 | 0 | 13.6554 | 37.78
2022-03-09 06:30 | 44629.2708 | 0 | 14.9685 | 37.78
2022-03-09 07:00 | 44629.2917 | 0 | 15.6548 | 37.78
2022-03-09 07:30 | 44629.3125 | 0 | 15.8435 | 37.78
2022-03-09 08:00 | 44629.3333 | 0 | 15.7841 | 37.78
2022-03-09 08:30 | 44629.3542 | 0 | 17.1116 | 37.78
2022-03-09 09:00 | 44629.375 | 0 | 16.5228 | 37.78
2022-03-09 09:30 | 44629.3958 | 0 | 14.5368 | 37.78
2022-03-09 10:00 | 44629.4167 | 0 | 16.324 | 37.78
2022-03-09 10:30 | 44629.4375 | 0 | 16.7291 | 37.78
2022-03-09 11:00 | 44629.4583 | 0 | 17.7281 | 37.78
2022-03-09 11:30 | 44629.4792 | 0 | 17.6063 | 37.78
2022-03-09 12:00 | 44629.5 | 0 | 15.3044 | 37.78
2022-03-09 12:30 | 44629.5208 | 0 | 17.9186 | 37.78
2022-03-09 13:00 | 44629.5417 | 0 | 17.3852 | 37.78
2022-03-09 13:30 | 44629.5625 | 0 | 17.8835 | 37.78
2022-03-09 14:00 | 44629.5833 | 0 | 19.3457 | 37.78
2022-03-09 14:30 | 44629.6042 | 0 | 20.6297 | 37.78
2022-03-09 15:00 | 44629.625 | 0 | 22.5429 | 37.78
2022-03-09 15:30 | 44629.6458 | 0 | 21.9737 | 37.78
2022-03-09 16:00 | 44629.6667 | 0 | 22.7832 | 37.78
2022-03-09 16:30 | 44629.6875 | 0 | 23.5373 | 37.78
2022-03-09 17:00 | 44629.7083 | 0 | 24.0215 | 37.78
2022-03-09 17:30 | 44629.7292 | 0 | 24.4679 | 37.78
2022-03-09 18:00 | 44629.75 | 0 | 24.3489 | 37.78
2022-03-09 18:30 | 44629.7708 | 0 | 24.6201 | 37.78
2022-03-09 19:00 | 44629.7917 | 0 | 24.031 | 37.78
2022-03-09 19:30 | 44629.8125 | 0 | 23.4943 | 37.78
2022-03-09 20:00 | 44629.8333 | 0 | 22.2916 | 37.78
2022-03-09 20:30 | 44629.8542 | 0 | 21.1904 | 37.78
2022-03-09 21:00 | 44629.875 | 0 | 19.6809 | 37.78
2022-03-09 21:30 | 44629.8958 | 0 | 18.0754 | 37.78
2022-03-09 22:00 | 44629.9167 | 0 | 16.811 | 37.78
2022-03-09 22:30 | 44629.9375 | 0 | 15.5407 | 37.78
2022-03-09 23:00 | 44629.9583 | 0 | 14.7514 | 37.78
2022-03-09 23:30 | 44629.9792 | 0 | 13.9012 | 37.78
2022-03-10 | 44630 | 0 | 12.954 | 37.78
2022-03-10 00:30 | 44630.0208 | 0 | 12.3681 | 37.78
2022-03-10 01:00 | 44630.0417 | 0 | 11.8956 | 37.78
2022-03-10 01:30 | 44630.0625 | 0 | 11.5319 | 37.78
2022-03-10 02:00 | 44630.0833 | 0 | 11.448 | 37.78
2022-03-10 02:30 | 44630.1042 | 0 | 11.4254 | 37.78
2022-03-10 03:00 | 44630.125 | 0 | 11.036 | 37.78
2022-03-10 03:30 | 44630.1458 | 0 | 11.0683 | 37.78
2022-03-10 04:00 | 44630.1667 | 0 | 11.288 | 37.78
2022-03-10 04:30 | 44630.1875 | 0 | 11.5214 | 37.78
2022-03-10 05:00 | 44630.2083 | 0 | 12.067 | 37.78
2022-03-10 05:30 | 44630.2292 | 0 | 12.6725 | 37.78
2022-03-10 06:00 | 44630.25 | 0 | 13.5414 | 37.78
2022-03-10 06:30 | 44630.2708 | 0 | 14.2633 | 37.78
2022-03-10 07:00 | 44630.2917 | 0 | 14.8847 | 37.78
2022-03-10 07:30 | 44630.3125 | 0 | 15.0999 | 37.78
2022-03-10 08:00 | 44630.3333 | 0 | 15.2965 | 37.78
2022-03-10 08:30 | 44630.3542 | 0 | 15.8047 | 37.78
2022-03-10 09:00 | 44630.375 | 0 | 16.0856 | 37.78
2022-03-10 09:30 | 44630.3958 | 0 | 15.9107 | 37.78
2022-03-10 10:00 | 44630.4167 | 0 | 13.7646 | 37.78
2022-03-10 10:30 | 44630.4375 | 0 | 14.9299 | 37.78
2022-03-10 11:00 | 44630.4583 | 0 | 14.8007 | 37.78
2022-03-10 11:30 | 44630.4792 | 0 | 15.5305 | 37.78
2022-03-10 12:00 | 44630.5 | 0 | 15.9384 | 37.78
2022-03-10 12:30 | 44630.5208 | 0 | 15.9114 | 37.78
2022-03-10 13:00 | 44630.5417 | 0 | 16.0796 | 37.78
2022-03-10 13:30 | 44630.5625 | 0 | 14.9943 | 37.78
2022-03-10 14:00 | 44630.5833 | 0 | 16.2034 | 37.78
2022-03-10 14:30 | 44630.6042 | 0 | 15.4326 | 37.78
2022-03-10 15:00 | 44630.625 | 0 | 14.4155 | 37.78
2022-03-10 15:30 | 44630.6458 | 0 | 15.4465 | 37.78
2022-03-10 16:00 | 44630.6667 | 0 | 14.9551 | 37.78
2022-03-10 16:30 | 44630.6875 | 0 | 15.7952 | 37.78
2022-03-10 17:00 | 44630.7083 | 0 | 15.5474 | 37.78
2022-03-10 17:30 | 44630.7292 | 0 | 15.9246 | 37.78
2022-03-10 18:00 | 44630.75 | 0 | 15.9673 | 37.78
2022-03-10 18:30 | 44630.7708 | 0 | 16.6916 | 37.78
2022-03-10 19:00 | 44630.7917 | 0 | 16.3535 | 37.78
2022-03-10 19:30 | 44630.8125 | 0 | 16.1228 | 37.78
2022-03-10 20:00 | 44630.8333 | 0 | 15.731 | 37.78
2022-03-10 20:30 | 44630.8542 | 0 | 15.3213 | 37.78
2022-03-10 21:00 | 44630.875 | 0 | 14.7996 | 37.78
2022-03-10 21:30 | 44630.8958 | 0 | 14.1338 | 37.78
2022-03-10 22:00 | 44630.9167 | 0 | 13.7307 | 37.78
2022-03-10 22:30 | 44630.9375 | 0 | 12.7216 | 37.78
2022-03-10 23:00 | 44630.9583 | 0 | 11.9953 | 37.78
2022-03-10 23:30 | 44630.9792 | 0 | 11.4023 | 37.78
2022-03-11 | 44631 | 0 | 10.698 | 37.78
2022-03-11 00:30 | 44631.0208 | 0 | 10.217 | 37.78
2022-03-11 01:00 | 44631.0417 | 0 | 9.9137 | 37.78
2022-03-11 01:30 | 44631.0625 | 0 | 9.871 | 37.78
2022-03-11 02:00 | 44631.0833 | 0 | 9.8164 | 37.78
2022-03-11 02:30 | 44631.1042 | 0 | 9.7779 | 37.78
2022-03-11 03:00 | 44631.125 | 0 | 9.7036 | 37.78
2022-03-11 03:30 | 44631.1458 | 0 | 9.8192 | 37.78
2022-03-11 04:00 | 44631.1667 | 0 | 9.9666 | 37.78
2022-03-11 04:30 | 44631.1875 | 0 | 10.3829 | 37.78
2022-03-11 05:00 | 44631.2083 | 0 | 10.8122 | 37.78
2022-03-11 05:30 | 44631.2292 | 0 | 11.3715 | 37.78
2022-03-11 06:00 | 44631.25 | 0 | 12.0971 | 37.78
2022-03-11 06:30 | 44631.2708 | 0 | 12.6372 | 37.78
2022-03-11 07:00 | 44631.2917 | 0 | 13.5606 | 37.78
2022-03-11 07:30 | 44631.3125 | 0 | 12.7696 | 37.78
2022-03-11 08:00 | 44631.3333 | 0 | 12.6733 | 37.78
2022-03-11 08:30 | 44631.3542 | 0 | 13.7279 | 37.78
2022-03-11 09:00 | 44631.375 | 0 | 14.3021 | 37.78
2022-03-11 09:30 | 44631.3958 | 0 | 14.3648 | 37.78
2022-03-11 10:00 | 44631.4167 | 0 | 13.6814 | 37.78
2022-03-11 10:30 | 44631.4375 | 0 | 13.4873 | 37.78
2022-03-11 11:00 | 44631.4583 | 0 | 13.3664 | 37.78
2022-03-11 11:30 | 44631.4792 | 0 | 14.1427 | 37.78
2022-03-11 12:00 | 44631.5 | 0 | 13.1646 | 37.78
2022-03-11 12:30 | 44631.5208 | 0 | 14.0097 | 37.78
2022-03-11 13:00 | 44631.5417 | 0 | 14.4019 | 37.78
2022-03-11 13:30 | 44631.5625 | 0 | 12.6359 | 37.78
2022-03-11 14:00 | 44631.5833 | 0 | 14.2126 | 37.78
2022-03-11 14:30 | 44631.6042 | 0 | 14.8643 | 37.78
2022-03-11 15:00 | 44631.625 | 0 | 12.9566 | 37.78
2022-03-11 15:30 | 44631.6458 | 0 | 13.4221 | 37.78
2022-03-11 16:00 | 44631.6667 | 0 | 14.2784 | 37.78
2022-03-11 16:30 | 44631.6875 | 0 | 14.9505 | 37.78
2022-03-11 17:00 | 44631.7083 | 0 | 14.7171 | 37.78
2022-03-11 17:30 | 44631.7292 | 0 | 14.7991 | 37.78
2022-03-11 18:00 | 44631.75 | 0 | 14.7917 | 37.78
2022-03-11 18:30 | 44631.7708 | 0 | 15.1179 | 37.78
2022-03-11 19:00 | 44631.7917 | 0 | 14.7579 | 37.78
2022-03-11 19:30 | 44631.8125 | 0 | 14.418 | 37.78
2022-03-11 20:00 | 44631.8333 | 0 | 14.0508 | 37.78
2022-03-11 20:30 | 44631.8542 | 0 | 13.7247 | 37.78
2022-03-11 21:00 | 44631.875 | 0 | 13.3584 | 37.78
2022-03-11 21:30 | 44631.8958 | 0 | 12.9801 | 37.78
2022-03-11 22:00 | 44631.9167 | 0 | 12.576 | 37.78
2022-03-11 22:30 | 44631.9375 | 0 | 11.8351 | 37.78
2022-03-11 23:00 | 44631.9583 | 0 | 11.243 | 37.78
2022-03-11 23:30 | 44631.9792 | 0 | 10.8539 | 37.78
2022-03-12 | 44632 | 0 | 10.3027 | 37.78
2022-03-12 00:30 | 44632.0208 | 0 | 9.8536 | 37.78
2022-03-12 01:00 | 44632.0417 | 0 | 9.6686 | 37.78
2022-03-12 01:30 | 44632.0625 | 0 | 9.3452 | 37.78
2022-03-12 02:00 | 44632.0833 | 0 | 9.3474 | 37.78
2022-03-12 02:30 | 44632.1042 | 0 | 9.2406 | 37.78
2022-03-12 03:00 | 44632.125 | 0 | 8.9429 | 37.78
2022-03-12 03:30 | 44632.1458 | 0 | 8.9641 | 37.78
2022-03-12 04:00 | 44632.1667 | 0 | 8.9144 | 37.78
2022-03-12 04:30 | 44632.1875 | 0 | 8.9468 | 37.78
2022-03-12 05:00 | 44632.2083 | 0 | 9.2012 | 37.78
2022-03-12 05:30 | 44632.2292 | 0 | 9.3526 | 37.78
2022-03-12 06:00 | 44632.25 | 0 | 9.5521 | 37.78
2022-03-12 06:30 | 44632.2708 | 0 | 9.324 | 37.78
2022-03-12 07:00 | 44632.2917 | 0 | 9.6967 | 37.78
2022-03-12 07:30 | 44632.3125 | 0 | 9.246 | 37.78
2022-03-12 08:00 | 44632.3333 | 0 | 9.1718 | 37.78
2022-03-12 08:30 | 44632.3542 | 0 | 9.0011 | 37.78
2022-03-12 09:00 | 44632.375 | 0 | 8.9665 | 37.78
2022-03-12 09:30 | 44632.3958 | 0 | 8.6932 | 37.78
2022-03-12 10:00 | 44632.4167 | 0 | 10.2199 | 37.78
2022-03-12 10:30 | 44632.4375 | 0 | 10.6924 | 37.78
2022-03-12 11:00 | 44632.4583 | 0 | 11.2193 | 37.78
2022-03-12 11:30 | 44632.4792 | 0 | 10.4123 | 37.78
2022-03-12 12:00 | 44632.5 | 0 | 8.7722 | 37.78
2022-03-12 12:30 | 44632.5208 | 0 | 10.6001 | 37.78
2022-03-12 13:00 | 44632.5417 | 0 | 10.3142 | 37.78
2022-03-12 13:30 | 44632.5625 | 0 | 10.2936 | 37.78
2022-03-12 14:00 | 44632.5833 | 0 | 11.6441 | 37.78
2022-03-12 14:30 | 44632.6042 | 0 | 10.4665 | 37.78
2022-03-12 15:00 | 44632.625 | 0 | 10.4385 | 37.78
2022-03-12 15:30 | 44632.6458 | 0 | 11.0647 | 37.78
2022-03-12 16:00 | 44632.6667 | 0 | 11.2711 | 37.78
2022-03-12 16:30 | 44632.6875 | 0 | 12.0284 | 37.78
2022-03-12 17:00 | 44632.7083 | 0 | 12.6609 | 37.78
2022-03-12 17:30 | 44632.7292 | 0 | 12.7124 | 37.78
2022-03-12 18:00 | 44632.75 | 0 | 12.9977 | 37.78
2022-03-12 18:30 | 44632.7708 | 0 | 13.1589 | 37.78
2022-03-12 19:00 | 44632.7917 | 0 | 12.9068 | 37.78
2022-03-12 19:30 | 44632.8125 | 0 | 12.6229 | 37.78
2022-03-12 20:00 | 44632.8333 | 0 | 12.3287 | 37.78
2022-03-12 20:30 | 44632.8542 | 0 | 11.8883 | 37.78
2022-03-12 21:00 | 44632.875 | 0 | 11.4614 | 37.78
2022-03-12 21:30 | 44632.8958 | 0 | 11.263 | 37.78
2022-03-12 22:00 | 44632.9167 | 0 | 10.8274 | 37.78
2022-03-12 22:30 | 44632.9375 | 0 | 10.2429 | 37.78
2022-03-12 23:00 | 44632.9583 | 0 | 9.8274 | 37.78
2022-03-12 23:30 | 44632.9792 | 0 | 9.3776 | 37.78
2022-03-13 | 44633 | 0 | 8.941 | 37.78
2022-03-13 00:30 | 44633.0208 | 0 | 8.5533 | 37.78
2022-03-13 01:00 | 44633.0417 | 0 | 8.3908 | 37.78
2022-03-13 01:30 | 44633.0625 | 0 | 8.1984 | 37.78
2022-03-13 02:00 | 44633.0833 | 0 | 8.1328 | 37.78
2022-03-13 02:30 | 44633.1042 | 0 | 8.0657 | 37.78
2022-03-13 03:00 | 44633.125 | 0 | 7.892 | 37.78
2022-03-13 03:30 | 44633.1458 | 0 | 7.8337 | 37.78
2022-03-13 04:00 | 44633.1667 | 0 | 7.7946 | 37.78
2022-03-13 04:30 | 44633.1875 | 0 | 7.8326 | 37.78
2022-03-13 05:00 | 44633.2083 | 0 | 7.9219 | 37.78
2022-03-13 05:30 | 44633.2292 | 0 | 7.943 | 37.78
2022-03-13 06:00 | 44633.25 | 0 | 7.9729 | 37.78
2022-03-13 06:30 | 44633.2708 | 0 | 7.9949 | 37.78
2022-03-13 07:00 | 44633.2917 | 0 | 7.9055 | 37.78
2022-03-13 07:30 | 44633.3125 | 0 | 7.3775 | 37.78
2022-03-13 08:00 | 44633.3333 | 0 | 7.3585 | 37.78
2022-03-13 08:30 | 44633.3542 | 0 | 7.3139 | 37.78
2022-03-13 09:00 | 44633.375 | 0 | 7.5573 | 37.78
2022-03-13 09:30 | 44633.3958 | 0 | 7.6639 | 37.78
2022-03-13 10:00 | 44633.4167 | 0 | 7.483 | 37.78
2022-03-13 10:30 | 44633.4375 | 0 | 7.1761 | 37.78
2022-03-13 11:00 | 44633.4583 | 0 | 8.7299 | 37.78
2022-03-13 11:30 | 44633.4792 | 0 | 8.3555 | 37.78
2022-03-13 12:00 | 44633.5 | 0 | 9.0758 | 37.78
2022-03-13 12:30 | 44633.5208 | 0 | 7.6436 | 37.78
2022-03-13 13:00 | 44633.5417 | 0 | 7.9344 | 37.78
2022-03-13 13:30 | 44633.5625 | 0 | 9.6994 | 37.78
2022-03-13 14:00 | 44633.5833 | 0 | 9.851 | 37.78
2022-03-13 14:30 | 44633.6042 | 0 | 9.1874 | 37.78
2022-03-13 15:00 | 44633.625 | 0 | 9.6983 | 37.78
2022-03-13 15:30 | 44633.6458 | 0 | 10.659 | 37.78
2022-03-13 16:00 | 44633.6667 | 0 | 11.3346 | 37.78
2022-03-13 16:30 | 44633.6875 | 0 | 12.2262 | 37.78
2022-03-13 17:00 | 44633.7083 | 0 | 13.1169 | 37.78
2022-03-13 17:30 | 44633.7292 | 0 | 13.3869 | 37.78
2022-03-13 18:00 | 44633.75 | 0 | 13.7272 | 37.78
2022-03-13 18:30 | 44633.7708 | 0 | 14.133 | 37.78
2022-03-13 19:00 | 44633.7917 | 0 | 13.9217 | 37.78
2022-03-13 19:30 | 44633.8125 | 0 | 13.2576 | 37.78
2022-03-13 20:00 | 44633.8333 | 0 | 12.9007 | 37.78
2022-03-13 20:30 | 44633.8542 | 0 | 12.2999 | 37.78
2022-03-13 21:00 | 44633.875 | 0 | 11.8574 | 37.78
2022-03-13 21:30 | 44633.8958 | 0 | 11.341 | 37.78
2022-03-13 22:00 | 44633.9167 | 0 | 10.6835 | 37.78
2022-03-13 22:30 | 44633.9375 | 0 | 9.8424 | 37.78
2022-03-13 23:00 | 44633.9583 | 0 | 9.4353 | 37.78
2022-03-13 23:30 | 44633.9792 | 0 | 9.0681 | 37.78
2022-03-14 | 44634 | 0 | 8.7307 | 37.78
2022-03-14 00:30 | 44634.0208 | 0 | 8.4367 | 37.78
2022-03-14 01:00 | 44634.0417 | 0 | 8.3023 | 37.78
2022-03-14 01:30 | 44634.0625 | 0 | 8.067 | 37.78
2022-03-14 02:00 | 44634.0833 | 0 | 8.0435 | 37.78
2022-03-14 02:30 | 44634.1042 | 0 | 8.3263 | 37.78
2022-03-14 03:00 | 44634.125 | 0 | 8.1316 | 37.78
2022-03-14 03:30 | 44634.1458 | 0 | 8.2782 | 37.78
2022-03-14 04:00 | 44634.1667 | 0 | 8.6638 | 37.78
2022-03-14 04:30 | 44634.1875 | 0 | 8.9978 | 37.78
2022-03-14 05:00 | 44634.2083 | 0 | 9.6229 | 37.78
2022-03-14 05:30 | 44634.2292 | 0 | 10.2027 | 37.78
2022-03-14 06:00 | 44634.25 | 0 | 11.0206 | 37.78
2022-03-14 06:30 | 44634.2708 | 0 | 11.7644 | 37.78
2022-03-14 07:00 | 44634.2917 | 0 | 11.9081 | 37.78
2022-03-14 07:30 | 44634.3125 | 0 | 11.5321 | 37.78
2022-03-14 08:00 | 44634.3333 | 0 | 11.0358 | 37.78
2022-03-14 08:30 | 44634.3542 | 0 | 10.7853 | 37.78
2022-03-14 09:00 | 44634.375 | 0 | 10.7595 | 37.78
2022-03-14 09:30 | 44634.3958 | 0 | 10.87 | 37.78
2022-03-14 10:00 | 44634.4167 | 0 | 11.5825 | 37.78
2022-03-14 10:30 | 44634.4375 | 0 | 11.3262 | 37.78
2022-03-14 11:00 | 44634.4583 | 0 | 11.4693 | 37.78
2022-03-14 11:30 | 44634.4792 | 0 | 11.4093 | 37.78
2022-03-14 12:00 | 44634.5 | 0 | 11.7342 | 37.78
2022-03-14 12:30 | 44634.5208 | 0 | 11.9469 | 37.78
2022-03-14 13:00 | 44634.5417 | 0 | 12.8008 | 37.78
2022-03-14 13:30 | 44634.5625 | 0 | 12.9445 | 37.78
2022-03-14 14:00 | 44634.5833 | 0 | 12.9844 | 37.78
2022-03-14 14:30 | 44634.6042 | 0 | 13.6592 | 37.78
2022-03-14 15:00 | 44634.625 | 0 | 14.2679 | 37.78
2022-03-14 15:30 | 44634.6458 | 0 | 14.3171 | 37.78
2022-03-14 16:00 | 44634.6667 | 0 | 14.2246 | 37.78
2022-03-14 16:30 | 44634.6875 | 0 | 14.7508 | 37.78
2022-03-14 17:00 | 44634.7083 | 0 | 15.551 | 37.78
2022-03-14 17:30 | 44634.7292 | 0 | 15.7901 | 37.78
2022-03-14 18:00 | 44634.75 | 0 | 15.8229 | 37.78
2022-03-14 18:30 | 44634.7708 | 0 | 16.3613 | 37.78
2022-03-14 19:00 | 44634.7917 | 0 | 16.1733 | 37.78
2022-03-14 19:30 | 44634.8125 | 0 | 15.6042 | 37.78
2022-03-14 20:00 | 44634.8333 | 0 | 15.1933 | 37.78
2022-03-14 20:30 | 44634.8542 | 0 | 14.4583 | 37.78
2022-03-14 21:00 | 44634.875 | 0 | 13.953 | 37.78
2022-03-14 21:30 | 44634.8958 | 0 | 13.3623 | 37.78
2022-03-14 22:00 | 44634.9167 | 0 | 12.5497 | 37.78
2022-03-14 22:30 | 44634.9375 | 0 | 11.6123 | 37.78
2022-03-14 23:00 | 44634.9583 | 0 | 10.8993 | 37.78
2022-03-14 23:30 | 44634.9792 | 0 | 10.3399 | 37.78
2022-03-15 | 44635 | 0 | 9.7519 | 37.78
2022-03-15 00:30 | 44635.0208 | 0 | 9.2831 | 37.78
2022-03-15 01:00 | 44635.0417 | 0 | 9.1514 | 37.78
2022-03-15 01:30 | 44635.0625 | 0 | 8.9565 | 37.78
2022-03-15 02:00 | 44635.0833 | 0 | 8.794 | 37.78
2022-03-15 02:30 | 44635.1042 | 0 | 8.8054 | 37.78
2022-03-15 03:00 | 44635.125 | 0 | 8.5912 | 37.78
2022-03-15 03:30 | 44635.1458 | 0 | 8.7099 | 37.78
2022-03-15 04:00 | 44635.1667 | 0 | 8.9436 | 37.78
2022-03-15 04:30 | 44635.1875 | 0 | 9.3166 | 37.78
2022-03-15 05:00 | 44635.2083 | 0 | 10.0316 | 37.78
2022-03-15 05:30 | 44635.2292 | 0 | 10.5833 | 37.78
2022-03-15 06:00 | 44635.25 | 0 | 11.4005 | 37.78
2022-03-15 06:30 | 44635.2708 | 0 | 12.1328 | 37.78
2022-03-15 07:00 | 44635.2917 | 0 | 12.6774 | 37.78
2022-03-15 07:30 | 44635.3125 | 0 | 11.5801 | 37.78
2022-03-15 08:00 | 44635.3333 | 0 | 12.7962 | 37.78
2022-03-15 08:30 | 44635.3542 | 0 | 12.1009 | 37.78
2022-03-15 09:00 | 44635.375 | 0 | 11.0932 | 37.78
2022-03-15 09:30 | 44635.3958 | 0 | 12.2894 | 37.78
2022-03-15 10:00 | 44635.4167 | 0 | 13.9196 | 37.78
2022-03-15 10:30 | 44635.4375 | 0 | 12.1466 | 37.78
2022-03-15 11:00 | 44635.4583 | 0 | 12.2177 | 37.78
2022-03-15 11:30 | 44635.4792 | 0 | 12.7657 | 37.78
2022-03-15 12:00 | 44635.5 | 0 | 12.6353 | 37.78
2022-03-15 12:30 | 44635.5208 | 0 | 11.0401 | 37.78
2022-03-15 13:00 | 44635.5417 | 0 | 12.9665 | 37.78
2022-03-15 13:30 | 44635.5625 | 0 | 12.128 | 37.78
2022-03-15 14:00 | 44635.5833 | 0 | 12.8863 | 37.78
2022-03-15 14:30 | 44635.6042 | 0 | 13.113 | 37.78
2022-03-15 15:00 | 44635.625 | 0 | 13.4976 | 37.78
2022-03-15 15:30 | 44635.6458 | 0 | 14.1723 | 37.78
2022-03-15 16:00 | 44635.6667 | 0 | 14.0065 | 37.78
2022-03-15 16:30 | 44635.6875 | 0 | 14.1834 | 37.78
2022-03-15 17:00 | 44635.7083 | 0 | 14.5425 | 37.78
2022-03-15 17:30 | 44635.7292 | 0 | 14.9865 | 37.78
2022-03-15 18:00 | 44635.75 | 0 | 14.9966 | 37.78
2022-03-15 18:30 | 44635.7708 | 0 | 15.4753 | 37.78
2022-03-15 19:00 | 44635.7917 | 0 | 15.2889 | 37.78
2022-03-15 19:30 | 44635.8125 | 0 | 14.747 | 37.78
2022-03-15 20:00 | 44635.8333 | 0 | 14.3684 | 37.78
2022-03-15 20:30 | 44635.8542 | 0 | 13.7323 | 37.78
2022-03-15 21:00 | 44635.875 | 0 | 13.3062 | 37.78
2022-03-15 21:30 | 44635.8958 | 0 | 12.6946 | 37.78
2022-03-15 22:00 | 44635.9167 | 0 | 12.2425 | 37.78
2022-03-15 22:30 | 44635.9375 | 0 | 11.318 | 37.78
2022-03-15 23:00 | 44635.9583 | 0 | 10.7969 | 37.78
2022-03-15 23:30 | 44635.9792 | 0 | 10.1582 | 37.78
2022-03-16 | 44636 | 0 | 9.6016 | 37.78
2022-03-16 00:30 | 44636.0208 | 0 | 9.2979 | 37.78
2022-03-16 01:00 | 44636.0417 | 0 | 9.0669 | 37.78
2022-03-16 01:30 | 44636.0625 | 0 | 8.8957 | 37.78
2022-03-16 02:00 | 44636.0833 | 0 | 8.7048 | 37.78
2022-03-16 02:30 | 44636.1042 | 0 | 8.6911 | 37.78
2022-03-16 03:00 | 44636.125 | 0 | 8.4809 | 37.78
2022-03-16 03:30 | 44636.1458 | 0 | 8.4866 | 37.78
2022-03-16 04:00 | 44636.1667 | 0 | 8.7533 | 37.78
2022-03-16 04:30 | 44636.1875 | 0 | 9.0752 | 37.78
2022-03-16 05:00 | 44636.2083 | 0 | 9.9587 | 37.78
2022-03-16 05:30 | 44636.2292 | 0 | 10.377 | 37.78
2022-03-16 06:00 | 44636.25 | 0 | 11.0723 | 37.78
2022-03-16 06:30 | 44636.2708 | 0 | 11.8104 | 37.78
2022-03-16 07:00 | 44636.2917 | 0 | 12.3765 | 37.78
2022-03-16 07:30 | 44636.3125 | 0 | 12.1947 | 37.78
2022-03-16 08:00 | 44636.3333 | 0 | 11.7718 | 37.78
2022-03-16 08:30 | 44636.3542 | 0 | 11.1976 | 37.78
2022-03-16 09:00 | 44636.375 | 0 | 11.7753 | 37.78
2022-03-16 09:30 | 44636.3958 | 0 | 10.0874 | 37.78
2022-03-16 10:00 | 44636.4167 | 0 | 11.3552 | 37.78
2022-03-16 10:30 | 44636.4375 | 0 | 12.2802 | 37.78
2022-03-16 11:00 | 44636.4583 | 0 | 11.2088 | 37.78
2022-03-16 11:30 | 44636.4792 | 0 | 11.9445 | 37.78
2022-03-16 12:00 | 44636.5 | 0 | 11.0825 | 37.78
2022-03-16 12:30 | 44636.5208 | 0 | 11.8422 | 37.78
2022-03-16 13:00 | 44636.5417 | 0 | 12.5179 | 37.78
2022-03-16 13:30 | 44636.5625 | 0 | 13.4996 | 37.78
2022-03-16 14:00 | 44636.5833 | 0 | 14.6415 | 37.78
2022-03-16 14:30 | 44636.6042 | 0 | 15.0248 | 37.78
2022-03-16 15:00 | 44636.625 | 0 | 14.3013 | 37.78
2022-03-16 15:30 | 44636.6458 | 0 | 15.0089 | 37.78
2022-03-16 16:00 | 44636.6667 | 0 | 14.6266 | 37.78
2022-03-16 16:30 | 44636.6875 | 0 | 15.0929 | 37.78
2022-03-16 17:00 | 44636.7083 | 0 | 16.0368 | 37.78
2022-03-16 17:30 | 44636.7292 | 0 | 16.0536 | 37.78
2022-03-16 18:00 | 44636.75 | 0 | 16.1192 | 37.78
2022-03-16 18:30 | 44636.7708 | 0 | 16.5659 | 37.78
2022-03-16 19:00 | 44636.7917 | 0 | 16.1215 | 37.78
2022-03-16 19:30 | 44636.8125 | 0 | 15.7382 | 37.78
2022-03-16 20:00 | 44636.8333 | 0 | 15.3333 | 37.78
2022-03-16 20:30 | 44636.8542 | 0 | 14.6191 | 37.78
2022-03-16 21:00 | 44636.875 | 0 | 14.0905 | 37.78
2022-03-16 21:30 | 44636.8958 | 0 | 13.541 | 37.78
2022-03-16 22:00 | 44636.9167 | 0 | 12.8547 | 37.78
2022-03-16 22:30 | 44636.9375 | 0 | 11.9226 | 37.78
2022-03-16 23:00 | 44636.9583 | 0 | 11.3183 | 37.78
2022-03-16 23:30 | 44636.9792 | 0 | 10.6308 | 37.78
2022-03-17 | 44637 | 0 | 9.9267 | 37.78
2022-03-17 00:30 | 44637.0208 | 0 | 9.7552 | 37.78
2022-03-17 01:00 | 44637.0417 | 0 | 9.3733 | 37.78
2022-03-17 01:30 | 44637.0625 | 0 | 8.9974 | 37.78
2022-03-17 02:00 | 44637.0833 | 0 | 8.9492 | 37.78
2022-03-17 02:30 | 44637.1042 | 0 | 8.9032 | 37.78
2022-03-17 03:00 | 44637.125 | 0 | 8.8276 | 37.78
2022-03-17 03:30 | 44637.1458 | 0 | 8.7943 | 37.78
2022-03-17 04:00 | 44637.1667 | 0 | 9.0511 | 37.78
2022-03-17 04:30 | 44637.1875 | 0 | 9.4913 | 37.78
2022-03-17 05:00 | 44637.2083 | 0 | 10.2382 | 37.78
2022-03-17 05:30 | 44637.2292 | 0 | 10.6494 | 37.78
2022-03-17 06:00 | 44637.25 | 0 | 11.3401 | 37.78
2022-03-17 06:30 | 44637.2708 | 0 | 11.5881 | 37.78
2022-03-17 07:00 | 44637.2917 | 0 | 11.8216 | 37.78
2022-03-17 07:30 | 44637.3125 | 0 | 11.7182 | 37.78
2022-03-17 08:00 | 44637.3333 | 0 | 11.5222 | 37.78
2022-03-17 08:30 | 44637.3542 | 0 | 11.1601 | 37.78
2022-03-17 09:00 | 44637.375 | 0 | 11.4694 | 37.78
2022-03-17 09:30 | 44637.3958 | 0 | 11.351 | 37.78
2022-03-17 10:00 | 44637.4167 | 0 | 12.057 | 37.78
2022-03-17 10:30 | 44637.4375 | 0 | 11.9153 | 37.78
2022-03-17 11:00 | 44637.4583 | 0 | 12.042 | 37.78
2022-03-17 11:30 | 44637.4792 | 0 | 12.8476 | 37.78
2022-03-17 12:00 | 44637.5 | 0 | 12.7755 | 37.78
2022-03-17 12:30 | 44637.5208 | 0 | 12.6409 | 37.78
2022-03-17 13:00 | 44637.5417 | 0 | 13.6269 | 37.78
2022-03-17 13:30 | 44637.5625 | 0 | 13.4633 | 37.78
2022-03-17 14:00 | 44637.5833 | 0 | 14.486 | 37.78
2022-03-17 14:30 | 44637.6042 | 0 | 15.6188 | 37.78
2022-03-17 15:00 | 44637.625 | 0 | 14.5469 | 37.78
2022-03-17 15:30 | 44637.6458 | 0 | 15.5049 | 37.78
2022-03-17 16:00 | 44637.6667 | 0 | 16.6303 | 37.78
2022-03-17 16:30 | 44637.6875 | 0 | 16.953 | 37.78
2022-03-17 17:00 | 44637.7083 | 0 | 17.061 | 37.78
2022-03-17 17:30 | 44637.7292 | 0 | 17.1679 | 37.78
2022-03-17 18:00 | 44637.75 | 0 | 17.3747 | 37.78
2022-03-17 18:30 | 44637.7708 | 0 | 17.708 | 37.78
2022-03-17 19:00 | 44637.7917 | 0 | 17.1259 | 37.78
2022-03-17 19:30 | 44637.8125 | 0 | 16.6128 | 37.78
2022-03-17 20:00 | 44637.8333 | 0 | 16.387 | 37.78
2022-03-17 20:30 | 44637.8542 | 0 | 15.743 | 37.78
2022-03-17 21:00 | 44637.875 | 0 | 14.939 | 37.78
2022-03-17 21:30 | 44637.8958 | 0 | 14.4293 | 37.78
2022-03-17 22:00 | 44637.9167 | 0 | 13.5881 | 37.78
2022-03-17 22:30 | 44637.9375 | 0 | 12.5675 | 37.78
2022-03-17 23:00 | 44637.9583 | 0 | 12.0432 | 37.78
2022-03-17 23:30 | 44637.9792 | 0 | 11.3587 | 37.78
2022-03-18 | 44638 | 0 | 10.7856 | 37.78
2022-03-18 00:30 | 44638.0208 | 0 | 10.1779 | 37.78
2022-03-18 01:00 | 44638.0417 | 0 | 10.0893 | 37.78
2022-03-18 01:30 | 44638.0625 | 0 | 9.9379 | 37.78
2022-03-18 02:00 | 44638.0833 | 0 | 9.7705 | 37.78
2022-03-18 02:30 | 44638.1042 | 0 | 9.6849 | 37.78
2022-03-18 03:00 | 44638.125 | 0 | 9.6117 | 37.78
2022-03-18 03:30 | 44638.1458 | 0 | 9.5971 | 37.78
2022-03-18 04:00 | 44638.1667 | 0 | 9.8747 | 37.78
2022-03-18 04:30 | 44638.1875 | 0 | 10.3017 | 37.78
2022-03-18 05:00 | 44638.2083 | 0 | 10.6759 | 37.78
2022-03-18 05:30 | 44638.2292 | 0 | 11.2525 | 37.78
2022-03-18 06:00 | 44638.25 | 0 | 12.0358 | 37.78
2022-03-18 06:30 | 44638.2708 | 0 | 12.2618 | 37.78
2022-03-18 07:00 | 44638.2917 | 0 | 12.4409 | 37.78
2022-03-18 07:30 | 44638.3125 | 0 | 12.4923 | 37.78
2022-03-18 08:00 | 44638.3333 | 0 | 12.5823 | 37.78
2022-03-18 08:30 | 44638.3542 | 0 | 12.4011 | 37.78
2022-03-18 09:00 | 44638.375 | 0 | 12.5631 | 37.78
2022-03-18 09:30 | 44638.3958 | 0 | 13.2733 | 37.78
2022-03-18 10:00 | 44638.4167 | 0 | 13.0063 | 37.78
2022-03-18 10:30 | 44638.4375 | 0 | 13.0637 | 37.78
2022-03-18 11:00 | 44638.4583 | 0 | 13.977 | 37.78
2022-03-18 11:30 | 44638.4792 | 0 | 13.9543 | 37.78
2022-03-18 12:00 | 44638.5 | 0 | 13.2505 | 37.78
2022-03-18 12:30 | 44638.5208 | 0 | 13.2601 | 37.78
2022-03-18 13:00 | 44638.5417 | 0 | 13.3128 | 37.78
2022-03-18 13:30 | 44638.5625 | 0 | 13.3226 | 37.78
2022-03-18 14:00 | 44638.5833 | 0 | 14.1798 | 37.78
2022-03-18 14:30 | 44638.6042 | 0 | 14.0045 | 37.78
2022-03-18 15:00 | 44638.625 | 0 | 14.4354 | 37.78
2022-03-18 15:30 | 44638.6458 | 0 | 16.21 | 37.78
2022-03-18 16:00 | 44638.6667 | 0 | 15.5367 | 37.78
2022-03-18 16:30 | 44638.6875 | 0 | 15.6882 | 37.78
2022-03-18 17:00 | 44638.7083 | 0 | 16.3611 | 37.78
2022-03-18 17:30 | 44638.7292 | 0 | 15.9477 | 37.78
2022-03-18 18:00 | 44638.75 | 0 | 15.8052 | 37.78
2022-03-18 18:30 | 44638.7708 | 0 | 16.042 | 37.78
2022-03-18 19:00 | 44638.7917 | 0 | 15.635 | 37.78
2022-03-18 19:30 | 44638.8125 | 0 | 15.1378 | 37.78
2022-03-18 20:00 | 44638.8333 | 0 | 14.8082 | 37.78
2022-03-18 20:30 | 44638.8542 | 0 | 14.2766 | 37.78
2022-03-18 21:00 | 44638.875 | 0 | 13.9053 | 37.78
2022-03-18 21:30 | 44638.8958 | 0 | 13.5188 | 37.78
2022-03-18 22:00 | 44638.9167 | 0 | 13.1187 | 37.78
2022-03-18 22:30 | 44638.9375 | 0 | 12.2071 | 37.78
2022-03-18 23:00 | 44638.9583 | 0 | 11.757 | 37.78
2022-03-18 23:30 | 44638.9792 | 0 | 11.2397 | 37.78
2022-03-19 | 44639 | 0 | 10.5352 | 37.78
2022-03-19 00:30 | 44639.0208 | 0 | 10.1451 | 37.78
2022-03-19 01:00 | 44639.0417 | 0 | 9.8459 | 37.78
2022-03-19 01:30 | 44639.0625 | 0 | 9.5794 | 37.78
2022-03-19 02:00 | 44639.0833 | 0 | 9.3486 | 37.78
2022-03-19 02:30 | 44639.1042 | 0 | 9.3014 | 37.78
2022-03-19 03:00 | 44639.125 | 0 | 8.9559 | 37.78
2022-03-19 03:30 | 44639.1458 | 0 | 9.0981 | 37.78
2022-03-19 04:00 | 44639.1667 | 0 | 8.9466 | 37.78
2022-03-19 04:30 | 44639.1875 | 0 | 8.9035 | 37.78
2022-03-19 05:00 | 44639.2083 | 0 | 9.1179 | 37.78
2022-03-19 05:30 | 44639.2292 | 0 | 9.221 | 37.78
2022-03-19 06:00 | 44639.25 | 0 | 9.3088 | 37.78
2022-03-19 06:30 | 44639.2708 | 0 | 9.6856 | 37.78
2022-03-19 07:00 | 44639.2917 | 0 | 9.6263 | 37.78
2022-03-19 07:30 | 44639.3125 | 0 | 9.494 | 37.78
2022-03-19 08:00 | 44639.3333 | 0 | 8.6729 | 37.78
2022-03-19 08:30 | 44639.3542 | 0 | 8.865 | 37.78
2022-03-19 09:00 | 44639.375 | 0 | 8.9183 | 37.78
2022-03-19 09:30 | 44639.3958 | 0 | 10.2727 | 37.78
2022-03-19 10:00 | 44639.4167 | 0 | 10.2431 | 37.78
2022-03-19 10:30 | 44639.4375 | 0 | 9.3606 | 37.78
2022-03-19 11:00 | 44639.4583 | 0 | 9.4913 | 37.78
2022-03-19 11:30 | 44639.4792 | 0 | 10.6323 | 37.78
2022-03-19 12:00 | 44639.5 | 0 | 10.1542 | 37.78
2022-03-19 12:30 | 44639.5208 | 0 | 9.502 | 37.78
2022-03-19 13:00 | 44639.5417 | 0 | 9.8439 | 37.78
2022-03-19 13:30 | 44639.5625 | 0 | 10.0337 | 37.78
2022-03-19 14:00 | 44639.5833 | 0 | 9.7869 | 37.78
2022-03-19 14:30 | 44639.6042 | 0 | 10.3093 | 37.78
2022-03-19 15:00 | 44639.625 | 0 | 11.071 | 37.78
2022-03-19 15:30 | 44639.6458 | 0 | 11.6484 | 37.78
2022-03-19 16:00 | 44639.6667 | 0 | 12.3048 | 37.78
2022-03-19 16:30 | 44639.6875 | 0 | 13.0122 | 37.78
2022-03-19 17:00 | 44639.7083 | 0 | 13.7948 | 37.78
2022-03-19 17:30 | 44639.7292 | 0 | 14.0064 | 37.78
2022-03-19 18:00 | 44639.75 | 0 | 13.9306 | 37.78
2022-03-19 18:30 | 44639.7708 | 0 | 14.1046 | 37.78
2022-03-19 19:00 | 44639.7917 | 0 | 13.734 | 37.78
2022-03-19 19:30 | 44639.8125 | 0 | 13.4679 | 37.78
2022-03-19 20:00 | 44639.8333 | 0 | 13.1559 | 37.78
2022-03-19 20:30 | 44639.8542 | 0 | 12.6922 | 37.78
2022-03-19 21:00 | 44639.875 | 0 | 12.1988 | 37.78
2022-03-19 21:30 | 44639.8958 | 0 | 11.7818 | 37.78
2022-03-19 22:00 | 44639.9167 | 0 | 11.5572 | 37.78
2022-03-19 22:30 | 44639.9375 | 0 | 10.9229 | 37.78
2022-03-19 23:00 | 44639.9583 | 0 | 10.5558 | 37.78
2022-03-19 23:30 | 44639.9792 | 0 | 10.0959 | 37.78
2022-03-20 | 44640 | 0 | 9.3911 | 37.78
2022-03-20 00:30 | 44640.0208 | 0 | 9.206 | 37.78
2022-03-20 01:00 | 44640.0417 | 0 | 9.0591 | 37.78
2022-03-20 01:30 | 44640.0625 | 0 | 8.7914 | 37.78
2022-03-20 02:00 | 44640.0833 | 0 | 8.5931 | 37.78
2022-03-20 02:30 | 44640.1042 | 0 | 8.536 | 37.78
2022-03-20 03:00 | 44640.125 | 0 | 8.4174 | 37.78
2022-03-20 03:30 | 44640.1458 | 0 | 8.2197 | 37.78
2022-03-20 04:00 | 44640.1667 | 0 | 8.2482 | 37.78
2022-03-20 04:30 | 44640.1875 | 0 | 8.1613 | 37.78
2022-03-20 05:00 | 44640.2083 | 0 | 8.2433 | 37.78
2022-03-20 05:30 | 44640.2292 | 0 | 8.324 | 37.78
2022-03-20 06:00 | 44640.25 | 0 | 8.3076 | 37.78
2022-03-20 06:30 | 44640.2708 | 0 | 8.2929 | 37.78
2022-03-20 07:00 | 44640.2917 | 0 | 8.1836 | 37.78
2022-03-20 07:30 | 44640.3125 | 0 | 7.8621 | 37.78
2022-03-20 08:00 | 44640.3333 | 0 | 7.6318 | 37.78
2022-03-20 08:30 | 44640.3542 | 0 | 7.5173 | 37.78
2022-03-20 09:00 | 44640.375 | 0 | 7.4395 | 37.78
2022-03-20 09:30 | 44640.3958 | 0 | 8.7072 | 37.78
2022-03-20 10:00 | 44640.4167 | 0 | 8.8646 | 37.78
2022-03-20 10:30 | 44640.4375 | 0 | 7.8127 | 37.78
2022-03-20 11:00 | 44640.4583 | 0 | 7.2397 | 37.78
2022-03-20 11:30 | 44640.4792 | 0 | 8.8364 | 37.78
2022-03-20 12:00 | 44640.5 | 0 | 8.8798 | 37.78
2022-03-20 12:30 | 44640.5208 | 0 | 9.0271 | 37.78
2022-03-20 13:00 | 44640.5417 | 0 | 9.544 | 37.78
2022-03-20 13:30 | 44640.5625 | 0 | 10.7707 | 37.78
2022-03-20 14:00 | 44640.5833 | 0 | 9.9777 | 37.78
2022-03-20 14:30 | 44640.6042 | 0 | 9.8944 | 37.78
2022-03-20 15:00 | 44640.625 | 0 | 10.5783 | 37.78
2022-03-20 15:30 | 44640.6458 | 0 | 10.9271 | 37.78
2022-03-20 16:00 | 44640.6667 | 0 | 11.6542 | 37.78
2022-03-20 16:30 | 44640.6875 | 0 | 12.8376 | 37.78
2022-03-20 17:00 | 44640.7083 | 0 | 13.8666 | 37.78
2022-03-20 17:30 | 44640.7292 | 0 | 14.1946 | 37.78
2022-03-20 18:00 | 44640.75 | 0 | 14.5834 | 37.78
2022-03-20 18:30 | 44640.7708 | 0 | 14.9858 | 37.78
2022-03-20 19:00 | 44640.7917 | 0 | 14.5608 | 37.78
2022-03-20 19:30 | 44640.8125 | 0 | 13.9938 | 37.78
2022-03-20 20:00 | 44640.8333 | 0 | 13.4236 | 37.78
2022-03-20 20:30 | 44640.8542 | 0 | 12.9638 | 37.78
2022-03-20 21:00 | 44640.875 | 0 | 12.2923 | 37.78
2022-03-20 21:30 | 44640.8958 | 0 | 11.6287 | 37.78
2022-03-20 22:00 | 44640.9167 | 0 | 11.0682 | 37.78
2022-03-20 22:30 | 44640.9375 | 0 | 10.1166 | 37.78
2022-03-20 23:00 | 44640.9583 | 0 | 9.6768 | 37.78
2022-03-20 23:30 | 44640.9792 | 0 | 9.2257 | 37.78
2022-03-21 | 44641 | 0 | 8.8654 | 37.78
2022-03-21 00:30 | 44641.0208 | 0 | 8.6762 | 37.78
2022-03-21 01:00 | 44641.0417 | 0 | 8.6365 | 37.78
2022-03-21 01:30 | 44641.0625 | 0 | 8.4044 | 37.78
2022-03-21 02:00 | 44641.0833 | 0 | 8.4003 | 37.78
2022-03-21 02:30 | 44641.1042 | 0 | 8.4047 | 37.78
2022-03-21 03:00 | 44641.125 | 0 | 8.263 | 37.78
2022-03-21 03:30 | 44641.1458 | 0 | 8.3066 | 37.78
2022-03-21 04:00 | 44641.1667 | 0 | 8.5463 | 37.78
2022-03-21 04:30 | 44641.1875 | 0 | 8.9555 | 37.78
2022-03-21 05:00 | 44641.2083 | 0 | 9.5152 | 37.78
2022-03-21 05:30 | 44641.2292 | 0 | 10.2878 | 37.78
2022-03-21 06:00 | 44641.25 | 0 | 10.9032 | 37.78
2022-03-21 06:30 | 44641.2708 | 0 | 11.672 | 37.78
2022-03-21 07:00 | 44641.2917 | 0 | 11.9256 | 37.78
2022-03-21 07:30 | 44641.3125 | 0 | 11.7108 | 37.78
2022-03-21 08:00 | 44641.3333 | 0 | 11.6243 | 37.78
2022-03-21 08:30 | 44641.3542 | 0 | 11.1633 | 37.78
2022-03-21 09:00 | 44641.375 | 0 | 10.7667 | 37.78
2022-03-21 09:30 | 44641.3958 | 0 | 10.7035 | 37.78
2022-03-21 10:00 | 44641.4167 | 0 | 10.5645 | 37.78
2022-03-21 10:30 | 44641.4375 | 0 | 10.5026 | 37.78
2022-03-21 11:00 | 44641.4583 | 0 | 10.6328 | 37.78
2022-03-21 11:30 | 44641.4792 | 0 | 11.3816 | 37.78
2022-03-21 12:00 | 44641.5 | 0 | 11.8239 | 37.78
2022-03-21 12:30 | 44641.5208 | 0 | 12.4005 | 37.78
2022-03-21 13:00 | 44641.5417 | 0 | 12.5715 | 37.78
2022-03-21 13:30 | 44641.5625 | 0 | 13.8516 | 37.78
2022-03-21 14:00 | 44641.5833 | 0 | 14.3983 | 37.78
2022-03-21 14:30 | 44641.6042 | 0 | 14.0745 | 37.78
2022-03-21 15:00 | 44641.625 | 0 | 13.4571 | 37.78
2022-03-21 15:30 | 44641.6458 | 0 | 14.399 | 37.78
2022-03-21 16:00 | 44641.6667 | 0 | 15.2216 | 37.78
2022-03-21 16:30 | 44641.6875 | 0 | 15.8402 | 37.78
2022-03-21 17:00 | 44641.7083 | 0 | 16.464 | 37.78
2022-03-21 17:30 | 44641.7292 | 0 | 16.4977 | 37.78
2022-03-21 18:00 | 44641.75 | 0 | 16.617 | 37.78
2022-03-21 18:30 | 44641.7708 | 0 | 17.2431 | 37.78
2022-03-21 19:00 | 44641.7917 | 0 | 16.801 | 37.78
2022-03-21 19:30 | 44641.8125 | 0 | 16.0955 | 37.78
2022-03-21 20:00 | 44641.8333 | 0 | 15.5157 | 37.78
2022-03-21 20:30 | 44641.8542 | 0 | 14.7948 | 37.78
2022-03-21 21:00 | 44641.875 | 0 | 14.1377 | 37.78
2022-03-21 21:30 | 44641.8958 | 0 | 13.65 | 37.78
2022-03-21 22:00 | 44641.9167 | 0 | 12.8627 | 37.78
2022-03-21 22:30 | 44641.9375 | 0 | 11.844 | 37.78
2022-03-21 23:00 | 44641.9583 | 0 | 11.1493 | 37.78
2022-03-21 23:30 | 44641.9792 | 0 | 10.6082 | 37.78
2022-03-22 | 44642 | 0 | 9.9206 | 37.78
2022-03-22 00:30 | 44642.0208 | 0 | 9.695 | 37.78
2022-03-22 01:00 | 44642.0417 | 0 | 9.5136 | 37.78
2022-03-22 01:30 | 44642.0625 | 0 | 9.2351 | 37.78
2022-03-22 02:00 | 44642.0833 | 0 | 8.8921 | 37.78
2022-03-22 02:30 | 44642.1042 | 0 | 8.8873 | 37.78
2022-03-22 03:00 | 44642.125 | 0 | 8.8102 | 37.78
2022-03-22 03:30 | 44642.1458 | 0 | 8.8104 | 37.78
2022-03-22 04:00 | 44642.1667 | 0 | 9.1813 | 37.78
2022-03-22 04:30 | 44642.1875 | 0 | 9.5615 | 37.78
2022-03-22 05:00 | 44642.2083 | 0 | 10.1288 | 37.78
2022-03-22 05:30 | 44642.2292 | 0 | 10.6283 | 37.78
2022-03-22 06:00 | 44642.25 | 0 | 11.3632 | 37.78
2022-03-22 06:30 | 44642.2708 | 0 | 11.9629 | 37.78
2022-03-22 07:00 | 44642.2917 | 0 | 12.0422 | 37.78
2022-03-22 07:30 | 44642.3125 | 0 | 11.8002 | 37.78
2022-03-22 08:00 | 44642.3333 | 0 | 11.5087 | 37.78
2022-03-22 08:30 | 44642.3542 | 0 | 11.3765 | 37.78
2022-03-22 09:00 | 44642.375 | 0 | 11.0881 | 37.78
2022-03-22 09:30 | 44642.3958 | 0 | 11.0856 | 37.78
2022-03-22 10:00 | 44642.4167 | 0 | 10.8447 | 37.78
2022-03-22 10:30 | 44642.4375 | 0 | 11.0963 | 37.78
2022-03-22 11:00 | 44642.4583 | 0 | 11.3745 | 37.78
2022-03-22 11:30 | 44642.4792 | 0 | 11.588 | 37.78
2022-03-22 12:00 | 44642.5 | 0 | 11.984 | 37.78
2022-03-22 12:30 | 44642.5208 | 0 | 12.6229 | 37.78
2022-03-22 13:00 | 44642.5417 | 0 | 13.1663 | 37.78
2022-03-22 13:30 | 44642.5625 | 0 | 13.2768 | 37.78
2022-03-22 14:00 | 44642.5833 | 0 | 13.3872 | 37.78
2022-03-22 14:30 | 44642.6042 | 0 | 13.7308 | 37.78
2022-03-22 15:00 | 44642.625 | 0 | 13.9284 | 37.78
2022-03-22 15:30 | 44642.6458 | 0 | 14.6822 | 37.78
2022-03-22 16:00 | 44642.6667 | 0 | 15.4775 | 37.78
2022-03-22 16:30 | 44642.6875 | 0 | 15.9961 | 37.78
2022-03-22 17:00 | 44642.7083 | 0 | 16.381 | 37.78
2022-03-22 17:30 | 44642.7292 | 0 | 16.554 | 37.78
2022-03-22 18:00 | 44642.75 | 0 | 16.4917 | 37.78
2022-03-22 18:30 | 44642.7708 | 0 | 17.0085 | 37.78
2022-03-22 19:00 | 44642.7917 | 0 | 16.5045 | 37.78
2022-03-22 19:30 | 44642.8125 | 0 | 15.7705 | 37.78
2022-03-22 20:00 | 44642.8333 | 0 | 15.417 | 37.78
2022-03-22 20:30 | 44642.8542 | 0 | 14.8532 | 37.78
2022-03-22 21:00 | 44642.875 | 0 | 14.273 | 37.78
2022-03-22 21:30 | 44642.8958 | 0 | 13.7691 | 37.78
2022-03-22 22:00 | 44642.9167 | 0 | 12.9345 | 37.78
2022-03-22 22:30 | 44642.9375 | 0 | 12.1478 | 37.78
2022-03-22 23:00 | 44642.9583 | 0 | 11.5497 | 37.78
2022-03-22 23:30 | 44642.9792 | 0 | 10.8028 | 37.78
2022-03-23 | 44643 | 0 | 10.2348 | 37.78
2022-03-23 00:30 | 44643.0208 | 0 | 9.868 | 37.78
2022-03-23 01:00 | 44643.0417 | 0 | 9.5371 | 37.78
2022-03-23 01:30 | 44643.0625 | 0 | 9.2826 | 37.78
2022-03-23 02:00 | 44643.0833 | 0 | 8.9838 | 37.78
2022-03-23 02:30 | 44643.1042 | 0 | 8.9504 | 37.78
2022-03-23 03:00 | 44643.125 | 0 | 8.6898 | 37.78
2022-03-23 03:30 | 44643.1458 | 0 | 8.7719 | 37.78
2022-03-23 04:00 | 44643.1667 | 0 | 9.0399 | 37.78
2022-03-23 04:30 | 44643.1875 | 0 | 9.3468 | 37.78
2022-03-23 05:00 | 44643.2083 | 0 | 9.9321 | 37.78
2022-03-23 05:30 | 44643.2292 | 0 | 10.3952 | 37.78
2022-03-23 06:00 | 44643.25 | 0 | 11.3205 | 37.78
2022-03-23 06:30 | 44643.2708 | 0 | 12.0175 | 37.78
2022-03-23 07:00 | 44643.2917 | 0 | 12.154 | 37.78
2022-03-23 07:30 | 44643.3125 | 0 | 12.016 | 37.78
2022-03-23 08:00 | 44643.3333 | 0 | 11.8511 | 37.78
2022-03-23 08:30 | 44643.3542 | 0 | 11.5744 | 37.78
2022-03-23 09:00 | 44643.375 | 0 | 11.4132 | 37.78
2022-03-23 09:30 | 44643.3958 | 0 | 11.4792 | 37.78
2022-03-23 10:00 | 44643.4167 | 0 | 11.7084 | 37.78
2022-03-23 10:30 | 44643.4375 | 0 | 11.6316 | 37.78
2022-03-23 11:00 | 44643.4583 | 0 | 11.7187 | 37.78
2022-03-23 11:30 | 44643.4792 | 0 | 12.183 | 37.78
2022-03-23 12:00 | 44643.5 | 0 | 12.3789 | 37.78
2022-03-23 12:30 | 44643.5208 | 0 | 12.8849 | 37.78
2022-03-23 13:00 | 44643.5417 | 0 | 13.7747 | 37.78
2022-03-23 13:30 | 44643.5625 | 0 | 14.486 | 37.78
2022-03-23 14:00 | 44643.5833 | 0 | 15.2545 | 37.78
2022-03-23 14:30 | 44643.6042 | 0 | 16.0145 | 37.78
2022-03-23 15:00 | 44643.625 | 0 | 16.6238 | 37.78
2022-03-23 15:30 | 44643.6458 | 0 | 17.4605 | 37.78
2022-03-23 16:00 | 44643.6667 | 0 | 17.8139 | 37.78
2022-03-23 16:30 | 44643.6875 | 0 | 18.1974 | 37.78
2022-03-23 17:00 | 44643.7083 | 0 | 18.2669 | 37.78
2022-03-23 17:30 | 44643.7292 | 0 | 18.6275 | 37.78
2022-03-23 18:00 | 44643.75 | 0 | 18.5983 | 37.78
2022-03-23 18:30 | 44643.7708 | 0 | 18.9268 | 37.78
2022-03-23 19:00 | 44643.7917 | 0 | 18.4257 | 37.78
2022-03-23 19:30 | 44643.8125 | 0 | 18.1018 | 37.78
2022-03-23 20:00 | 44643.8333 | 0 | 17.4784 | 37.78
2022-03-23 20:30 | 44643.8542 | 0 | 16.7693 | 37.78
2022-03-23 21:00 | 44643.875 | 0 | 16.0571 | 37.78
2022-03-23 21:30 | 44643.8958 | 0 | 15.4219 | 37.78
2022-03-23 22:00 | 44643.9167 | 0 | 14.4902 | 37.78
2022-03-23 22:30 | 44643.9375 | 0 | 13.4079 | 37.78
2022-03-23 23:00 | 44643.9583 | 0 | 12.479 | 37.78
2022-03-23 23:30 | 44643.9792 | 0 | 12.0228 | 37.78
2022-03-24 | 44644 | 0 | 11.2704 | 37.78
2022-03-24 00:30 | 44644.0208 | 0 | 10.8871 | 37.78
2022-03-24 01:00 | 44644.0417 | 0 | 10.7108 | 37.78
2022-03-24 01:30 | 44644.0625 | 0 | 10.3352 | 37.78
2022-03-24 02:00 | 44644.0833 | 0 | 10.1099 | 37.78
2022-03-24 02:30 | 44644.1042 | 0 | 10.0213 | 37.78
2022-03-24 03:00 | 44644.125 | 0 | 9.9775 | 37.78
2022-03-24 03:30 | 44644.1458 | 0 | 9.8502 | 37.78
2022-03-24 04:00 | 44644.1667 | 0 | 10.1737 | 37.78
2022-03-24 04:30 | 44644.1875 | 0 | 10.3999 | 37.78
2022-03-24 05:00 | 44644.2083 | 0 | 11.0479 | 37.78
2022-03-24 05:30 | 44644.2292 | 0 | 11.4459 | 37.78
2022-03-24 06:00 | 44644.25 | 0 | 12.1902 | 37.78
2022-03-24 06:30 | 44644.2708 | 0 | 13.0244 | 37.78
2022-03-24 07:00 | 44644.2917 | 0 | 13.5431 | 37.78
2022-03-24 07:30 | 44644.3125 | 0 | 13.1071 | 37.78
2022-03-24 08:00 | 44644.3333 | 0 | 13.2011 | 37.78
2022-03-24 08:30 | 44644.3542 | 0 | 13.2656 | 37.78
2022-03-24 09:00 | 44644.375 | 0 | 13.5931 | 37.78
2022-03-24 09:30 | 44644.3958 | 0 | 14.2187 | 37.78
2022-03-24 10:00 | 44644.4167 | 0 | 14.4082 | 37.78
2022-03-24 10:30 | 44644.4375 | 0 | 14.0859 | 37.78
2022-03-24 11:00 | 44644.4583 | 0 | 14.2221 | 37.78
2022-03-24 11:30 | 44644.4792 | 0 | 13.9903 | 37.78
2022-03-24 12:00 | 44644.5 | 0 | 14.4997 | 37.78
2022-03-24 12:30 | 44644.5208 | 0 | 14.6841 | 37.78
2022-03-24 13:00 | 44644.5417 | 0 | 15.1513 | 37.78
2022-03-24 13:30 | 44644.5625 | 0 | 15.6178 | 37.78
2022-03-24 14:00 | 44644.5833 | 0 | 16.218 | 37.78
2022-03-24 14:30 | 44644.6042 | 0 | 16.5447 | 37.78
2022-03-24 15:00 | 44644.625 | 0 | 17.1538 | 37.78
2022-03-24 15:30 | 44644.6458 | 0 | 17.7336 | 37.78
2022-03-24 16:00 | 44644.6667 | 0 | 18.1162 | 37.78
2022-03-24 16:30 | 44644.6875 | 0 | 18.8171 | 37.78
2022-03-24 17:00 | 44644.7083 | 0 | 18.6761 | 37.78
2022-03-24 17:30 | 44644.7292 | 0 | 18.7254 | 37.78
2022-03-24 18:00 | 44644.75 | 0 | 18.7657 | 37.78
2022-03-24 18:30 | 44644.7708 | 0 | 19.0274 | 37.78
2022-03-24 19:00 | 44644.7917 | 0 | 18.7523 | 37.78
2022-03-24 19:30 | 44644.8125 | 0 | 18.3201 | 37.78
2022-03-24 20:00 | 44644.8333 | 0 | 17.6502 | 37.78
2022-03-24 20:30 | 44644.8542 | 0 | 16.9846 | 37.78
2022-03-24 21:00 | 44644.875 | 0 | 16.4644 | 37.78
2022-03-24 21:30 | 44644.8958 | 0 | 15.8463 | 37.78
2022-03-24 22:00 | 44644.9167 | 0 | 14.9688 | 37.78
2022-03-24 22:30 | 44644.9375 | 0 | 13.9606 | 37.78
2022-03-24 23:00 | 44644.9583 | 0 | 13.0833 | 37.78
2022-03-24 23:30 | 44644.9792 | 0 | 12.3968 | 37.78
2022-03-25 | 44645 | 0 | 11.6777 | 37.78
2022-03-25 00:30 | 44645.0208 | 0 | 10.9826 | 37.78
2022-03-25 01:00 | 44645.0417 | 0 | 10.9291 | 37.78
2022-03-25 01:30 | 44645.0625 | 0 | 10.3336 | 37.78
2022-03-25 02:00 | 44645.0833 | 0 | 10.2234 | 37.78
2022-03-25 02:30 | 44645.1042 | 0 | 10.2296 | 37.78
2022-03-25 03:00 | 44645.125 | 0 | 9.9565 | 37.78
2022-03-25 03:30 | 44645.1458 | 0 | 10.0027 | 37.78
2022-03-25 04:00 | 44645.1667 | 0 | 10.2211 | 37.78
2022-03-25 04:30 | 44645.1875 | 0 | 10.651 | 37.78
2022-03-25 05:00 | 44645.2083 | 0 | 11.3455 | 37.78
2022-03-25 05:30 | 44645.2292 | 0 | 11.8127 | 37.78
2022-03-25 06:00 | 44645.25 | 0 | 12.7342 | 37.78
2022-03-25 06:30 | 44645.2708 | 0 | 13.1292 | 37.78
2022-03-25 07:00 | 44645.2917 | 0 | 13.4261 | 37.78
2022-03-25 07:30 | 44645.3125 | 0 | 13.2806 | 37.78
2022-03-25 08:00 | 44645.3333 | 0 | 13.5258 | 37.78
2022-03-25 08:30 | 44645.3542 | 0 | 14.282 | 37.78
2022-03-25 09:00 | 44645.375 | 0 | 14.2693 | 37.78
2022-03-25 09:30 | 44645.3958 | 0 | 15.3437 | 37.78
2022-03-25 10:00 | 44645.4167 | 0 | 14.4341 | 37.78
2022-03-25 10:30 | 44645.4375 | 0 | 14.6994 | 37.78
2022-03-25 11:00 | 44645.4583 | 0 | 13.8952 | 37.78
2022-03-25 11:30 | 44645.4792 | 0 | 14.7288 | 37.78
2022-03-25 12:00 | 44645.5 | 0 | 15.0478 | 37.78
2022-03-25 12:30 | 44645.5208 | 0 | 14.8665 | 37.78
2022-03-25 13:00 | 44645.5417 | 0 | 14.2532 | 37.78
2022-03-25 13:30 | 44645.5625 | 0 | 14.468 | 37.78
2022-03-25 14:00 | 44645.5833 | 0 | 15.226 | 37.78
2022-03-25 14:30 | 44645.6042 | 0 | 16.1137 | 37.78
2022-03-25 15:00 | 44645.625 | 0 | 15.9099 | 37.78
2022-03-25 15:30 | 44645.6458 | 0 | 16.809 | 37.78
2022-03-25 16:00 | 44645.6667 | 0 | 17.2746 | 37.78
2022-03-25 16:30 | 44645.6875 | 0 | 18.1691 | 37.78
2022-03-25 17:00 | 44645.7083 | 0 | 18.1664 | 37.78
2022-03-25 17:30 | 44645.7292 | 0 | 17.8906 | 37.78
2022-03-25 18:00 | 44645.75 | 0 | 16.548 | 37.78
2022-03-25 18:30 | 44645.7708 | 0 | 16.2579 | 37.78
2022-03-25 19:00 | 44645.7917 | 0 | 15.4778 | 37.78
2022-03-25 19:30 | 44645.8125 | 0 | 15.0012 | 37.78
2022-03-25 20:00 | 44645.8333 | 0 | 14.6128 | 37.78
2022-03-25 20:30 | 44645.8542 | 0 | 13.8506 | 37.78
2022-03-25 21:00 | 44645.875 | 0 | 13.4824 | 37.78
2022-03-25 21:30 | 44645.8958 | 0 | 13.0907 | 37.78
2022-03-25 22:00 | 44645.9167 | 0 | 12.7328 | 37.78
2022-03-25 22:30 | 44645.9375 | 0 | 11.8323 | 37.78
2022-03-25 23:00 | 44645.9583 | 0 | 11.222 | 37.78
2022-03-25 23:30 | 44645.9792 | 0 | 10.7318 | 37.78
2022-03-26 | 44646 | 0 | 9.9949 | 37.78
2022-03-26 00:30 | 44646.0208 | 0 | 9.7865 | 37.78
2022-03-26 01:00 | 44646.0417 | 0 | 9.5172 | 37.78
2022-03-26 01:30 | 44646.0625 | 0 | 9.2219 | 37.78
2022-03-26 02:00 | 44646.0833 | 0 | 8.9963 | 37.78
2022-03-26 02:30 | 44646.1042 | 0 | 9.0087 | 37.78
2022-03-26 03:00 | 44646.125 | 0 | 8.75 | 37.78
2022-03-26 03:30 | 44646.1458 | 0 | 8.7867 | 37.78
2022-03-26 04:00 | 44646.1667 | 0 | 8.8959 | 37.78
2022-03-26 04:30 | 44646.1875 | 0 | 8.8858 | 37.78
2022-03-26 05:00 | 44646.2083 | 0 | 9.1917 | 37.78
2022-03-26 05:30 | 44646.2292 | 0 | 9.2905 | 37.78
2022-03-26 06:00 | 44646.25 | 0 | 9.4653 | 37.78
2022-03-26 06:30 | 44646.2708 | 0 | 9.7258 | 37.78
2022-03-26 07:00 | 44646.2917 | 0 | 10.3754 | 37.78
2022-03-26 07:30 | 44646.3125 | 0 | 10.1954 | 37.78
2022-03-26 08:00 | 44646.3333 | 0 | 9.1279 | 37.78
2022-03-26 08:30 | 44646.3542 | 0 | 9.6804 | 37.78
2022-03-26 09:00 | 44646.375 | 0 | 10.7365 | 37.78
2022-03-26 09:30 | 44646.3958 | 0 | 10.4055 | 37.78
2022-03-26 10:00 | 44646.4167 | 0 | 11.2488 | 37.78
2022-03-26 10:30 | 44646.4375 | 0 | 9.9335 | 37.78
2022-03-26 11:00 | 44646.4583 | 0 | 11.0282 | 37.78
2022-03-26 11:30 | 44646.4792 | 0 | 12.2436 | 37.78
2022-03-26 12:00 | 44646.5 | 0 | 9.6836 | 37.78
2022-03-26 12:30 | 44646.5208 | 0 | 12.6151 | 37.78
2022-03-26 13:00 | 44646.5417 | 0 | 13.3629 | 37.78
2022-03-26 13:30 | 44646.5625 | 0 | 13.62 | 37.78
2022-03-26 14:00 | 44646.5833 | 0 | 13.2411 | 37.78
2022-03-26 14:30 | 44646.6042 | 0 | 12.6043 | 37.78
2022-03-26 15:00 | 44646.625 | 0 | 12.5551 | 37.78
2022-03-26 15:30 | 44646.6458 | 0 | 11.5949 | 37.78
2022-03-26 16:00 | 44646.6667 | 0 | 13.0582 | 37.78
2022-03-26 16:30 | 44646.6875 | 0 | 13.331 | 37.78
2022-03-26 17:00 | 44646.7083 | 0 | 13.3932 | 37.78
2022-03-26 17:30 | 44646.7292 | 0 | 13.5043 | 37.78
2022-03-26 18:00 | 44646.75 | 0 | 14.0807 | 37.78
2022-03-26 18:30 | 44646.7708 | 0 | 14.1037 | 37.78
2022-03-26 19:00 | 44646.7917 | 0 | 13.6497 | 37.78
2022-03-26 19:30 | 44646.8125 | 0 | 13.2166 | 37.78
2022-03-26 20:00 | 44646.8333 | 0 | 12.9217 | 37.78
2022-03-26 20:30 | 44646.8542 | 0 | 12.4472 | 37.78
2022-03-26 21:00 | 44646.875 | 0 | 12.0496 | 37.78
2022-03-26 21:30 | 44646.8958 | 0 | 11.7457 | 37.78
2022-03-26 22:00 | 44646.9167 | 0 | 11.274 | 37.78
2022-03-26 22:30 | 44646.9375 | 0 | 10.7858 | 37.78
2022-03-26 23:00 | 44646.9583 | 0 | 10.2299 | 37.78
2022-03-26 23:30 | 44646.9792 | 0 | 9.8088 | 37.78
2022-03-27 | 44647 | 0 | 9.4456 | 37.78
2022-03-27 00:30 | 44647.0208 | 0 | 9.1117 | 37.78
2022-03-27 01:00 | 44647.0417 | 0 | 8.9605 | 37.78
2022-03-27 01:30 | 44647.0625 | 0 | 8.66 | 37.78
2022-03-27 02:00 | 44647.0833 | 0 | 8.5075 | 37.78
2022-03-27 02:30 | 44647.1042 | 0 | 8.3809 | 37.78
2022-03-27 03:00 | 44647.125 | 0 | 8.2647 | 37.78
2022-03-27 03:30 | 44647.1458 | 0 | 8.1353 | 37.78
2022-03-27 04:00 | 44647.1667 | 0 | 8.1365 | 37.78
2022-03-27 04:30 | 44647.1875 | 0 | 8.1602 | 37.78
2022-03-27 05:00 | 44647.2083 | 0 | 8.3959 | 37.78
2022-03-27 05:30 | 44647.2292 | 0 | 8.4518 | 37.78
2022-03-27 06:00 | 44647.25 | 0 | 8.578 | 37.78
2022-03-27 06:30 | 44647.2708 | 0 | 8.6839 | 37.78
2022-03-27 07:00 | 44647.2917 | 0 | 9.0472 | 37.78
2022-03-27 07:30 | 44647.3125 | 0 | 8.6315 | 37.78
2022-03-27 08:00 | 44647.3333 | 0 | 8.782 | 37.78
2022-03-27 08:30 | 44647.3542 | 0 | 8.2175 | 37.78
2022-03-27 09:00 | 44647.375 | 0 | 7.7915 | 37.78
2022-03-27 09:30 | 44647.3958 | 0 | 8.8556 | 37.78
2022-03-27 10:00 | 44647.4167 | 0 | 9.6312 | 37.78
2022-03-27 10:30 | 44647.4375 | 0 | 11.1879 | 37.78
2022-03-27 11:00 | 44647.4583 | 0 | 8.4905 | 37.78
2022-03-27 11:30 | 44647.4792 | 0 | 7.7749 | 37.78
2022-03-27 12:00 | 44647.5 | 0 | 8.2335 | 37.78
2022-03-27 12:30 | 44647.5208 | 0 | 8.5304 | 37.78
2022-03-27 13:00 | 44647.5417 | 0 | 9.2182 | 37.78
2022-03-27 13:30 | 44647.5625 | 0 | 10.2254 | 37.78
2022-03-27 14:00 | 44647.5833 | 0 | 9.9415 | 37.78
2022-03-27 14:30 | 44647.6042 | 0 | 12.5067 | 37.78
2022-03-27 15:00 | 44647.625 | 0 | 13.2656 | 37.78
2022-03-27 15:30 | 44647.6458 | 0 | 13.0322 | 37.78
2022-03-27 16:00 | 44647.6667 | 0 | 13.0734 | 37.78
2022-03-27 16:30 | 44647.6875 | 0 | 13.4394 | 37.78
2022-03-27 17:00 | 44647.7083 | 0 | 13.8339 | 37.78
2022-03-27 17:30 | 44647.7292 | 0 | 14.2873 | 37.78
2022-03-27 18:00 | 44647.75 | 0 | 14.5027 | 37.78
2022-03-27 18:30 | 44647.7708 | 0 | 14.7398 | 37.78
2022-03-27 19:00 | 44647.7917 | 0 | 14.3191 | 37.78
2022-03-27 19:30 | 44647.8125 | 0 | 13.9572 | 37.78
2022-03-27 20:00 | 44647.8333 | 0 | 13.5309 | 37.78
2022-03-27 20:30 | 44647.8542 | 0 | 12.994 | 37.78
2022-03-27 21:00 | 44647.875 | 0 | 12.6088 | 37.78
2022-03-27 21:30 | 44647.8958 | 0 | 12.0557 | 37.78
2022-03-27 22:00 | 44647.9167 | 0 | 11.4656 | 37.78
2022-03-27 22:30 | 44647.9375 | 0 | 10.7116 | 37.78
2022-03-27 23:00 | 44647.9583 | 0 | 10.0843 | 37.78
2022-03-27 23:30 | 44647.9792 | 0 | 9.822 | 37.78
2022-03-28 | 44648 | 0 | 9.3486 | 37.78
2022-03-28 00:30 | 44648.0208 | 0 | 9.3151 | 37.78
2022-03-28 01:00 | 44648.0417 | 0 | 8.9819 | 37.78
2022-03-28 01:30 | 44648.0625 | 0 | 8.9641 | 37.78
2022-03-28 02:00 | 44648.0833 | 0 | 8.8114 | 37.78
2022-03-28 02:30 | 44648.1042 | 0 | 8.8277 | 37.78
2022-03-28 03:00 | 44648.125 | 0 | 8.9268 | 37.78
2022-03-28 03:30 | 44648.1458 | 0 | 8.7619 | 37.78
2022-03-28 04:00 | 44648.1667 | 0 | 9.0436 | 37.78
2022-03-28 04:30 | 44648.1875 | 0 | 9.5447 | 37.78
2022-03-28 05:00 | 44648.2083 | 0 | 10.1998 | 37.78
2022-03-28 05:30 | 44648.2292 | 0 | 10.8034 | 37.78
2022-03-28 06:00 | 44648.25 | 0 | 11.9224 | 37.78
2022-03-28 06:30 | 44648.2708 | 0 | 12.8023 | 37.78
2022-03-28 07:00 | 44648.2917 | 0 | 14.0042 | 37.78
2022-03-28 07:30 | 44648.3125 | 0 | 14.0674 | 37.78
2022-03-28 08:00 | 44648.3333 | 0 | 14.7253 | 37.78
2022-03-28 08:30 | 44648.3542 | 0 | 15.1715 | 37.78
2022-03-28 09:00 | 44648.375 | 0 | 15.3661 | 37.78
2022-03-28 09:30 | 44648.3958 | 0 | 15.6103 | 37.78
2022-03-28 10:00 | 44648.4167 | 0 | 14.9937 | 37.78
2022-03-28 10:30 | 44648.4375 | 0 | 14.7108 | 37.78
2022-03-28 11:00 | 44648.4583 | 0 | 14.1487 | 37.78
2022-03-28 11:30 | 44648.4792 | 0 | 14.108 | 37.78
2022-03-28 12:00 | 44648.5 | 0 | 13.9156 | 37.78
2022-03-28 12:30 | 44648.5208 | 0 | 14.7026 | 37.78
2022-03-28 13:00 | 44648.5417 | 0 | 14.8721 | 37.78
2022-03-28 13:30 | 44648.5625 | 0 | 14.2623 | 37.78
2022-03-28 14:00 | 44648.5833 | 0 | 14.0623 | 37.78
2022-03-28 14:30 | 44648.6042 | 0 | 13.9639 | 37.78
2022-03-28 15:00 | 44648.625 | 0 | 13.5918 | 37.78
2022-03-28 15:30 | 44648.6458 | 0 | 13.4877 | 37.78
2022-03-28 16:00 | 44648.6667 | 0 | 13.6728 | 37.78
2022-03-28 16:30 | 44648.6875 | 0 | 14.1634 | 37.78
2022-03-28 17:00 | 44648.7083 | 0 | 14.1366 | 37.78
2022-03-28 17:30 | 44648.7292 | 0 | 14.5016 | 37.78
2022-03-28 18:00 | 44648.75 | 0 | 14.7723 | 37.78
2022-03-28 18:30 | 44648.7708 | 0 | 14.8002 | 37.78
2022-03-28 19:00 | 44648.7917 | 0 | 14.341 | 37.78
2022-03-28 19:30 | 44648.8125 | 0 | 14.0073 | 37.78
2022-03-28 20:00 | 44648.8333 | 0 | 13.5271 | 37.78
2022-03-28 20:30 | 44648.8542 | 0 | 13.1118 | 37.78
2022-03-28 21:00 | 44648.875 | 0 | 12.6908 | 37.78
2022-03-28 21:30 | 44648.8958 | 0 | 12.3109 | 37.78
2022-03-28 22:00 | 44648.9167 | 0 | 11.7657 | 37.78
2022-03-28 22:30 | 44648.9375 | 0 | 10.7585 | 37.78
2022-03-28 23:00 | 44648.9583 | 0 | 10.0973 | 37.78
2022-03-28 23:30 | 44648.9792 | 0 | 9.6752 | 37.78
2022-03-29 | 44649 | 0 | 9.2692 | 37.78
2022-03-29 00:30 | 44649.0208 | 0 | 8.9764 | 37.78
2022-03-29 01:00 | 44649.0417 | 0 | 8.7486 | 37.78
2022-03-29 01:30 | 44649.0625 | 0 | 8.598 | 37.78
2022-03-29 02:00 | 44649.0833 | 0 | 8.618 | 37.78
2022-03-29 02:30 | 44649.1042 | 0 | 8.5359 | 37.78
2022-03-29 03:00 | 44649.125 | 0 | 8.325 | 37.78
2022-03-29 03:30 | 44649.1458 | 0 | 8.4531 | 37.78
2022-03-29 04:00 | 44649.1667 | 0 | 8.7434 | 37.78
2022-03-29 04:30 | 44649.1875 | 0 | 9.3069 | 37.78
2022-03-29 05:00 | 44649.2083 | 0 | 9.8523 | 37.78
2022-03-29 05:30 | 44649.2292 | 0 | 10.5199 | 37.78
2022-03-29 06:00 | 44649.25 | 0 | 11.5289 | 37.78
2022-03-29 06:30 | 44649.2708 | 0 | 12.5339 | 37.78
2022-03-29 07:00 | 44649.2917 | 0 | 13.2509 | 37.78
2022-03-29 07:30 | 44649.3125 | 0 | 13.1454 | 37.78
2022-03-29 08:00 | 44649.3333 | 0 | 13.1564 | 37.78
2022-03-29 08:30 | 44649.3542 | 0 | 13.3999 | 37.78
2022-03-29 09:00 | 44649.375 | 0 | 13.742 | 37.78
2022-03-29 09:30 | 44649.3958 | 0 | 13.5843 | 37.78
2022-03-29 10:00 | 44649.4167 | 0 | 13.2929 | 37.78
2022-03-29 10:30 | 44649.4375 | 0 | 13.2714 | 37.78
2022-03-29 11:00 | 44649.4583 | 0 | 12.771 | 37.78
2022-03-29 11:30 | 44649.4792 | 0 | 13.3566 | 37.78
2022-03-29 12:00 | 44649.5 | 0 | 12.2302 | 37.78
2022-03-29 12:30 | 44649.5208 | 0 | 10.7399 | 37.78
2022-03-29 13:00 | 44649.5417 | 0 | 11.7028 | 37.78
2022-03-29 13:30 | 44649.5625 | 0 | 11.0087 | 37.78
2022-03-29 14:00 | 44649.5833 | 0 | 12.7837 | 37.78
2022-03-29 14:30 | 44649.6042 | 0 | 14.4886 | 37.78
2022-03-29 15:00 | 44649.625 | 0 | 14.0308 | 37.78
2022-03-29 15:30 | 44649.6458 | 0 | 14.0115 | 37.78
2022-03-29 16:00 | 44649.6667 | 0 | 13.8261 | 37.78
2022-03-29 16:30 | 44649.6875 | 0 | 14.4121 | 37.78
2022-03-29 17:00 | 44649.7083 | 0 | 14.458 | 37.78
2022-03-29 17:30 | 44649.7292 | 0 | 14.9214 | 37.78
2022-03-29 18:00 | 44649.75 | 0 | 15.1031 | 37.78
2022-03-29 18:30 | 44649.7708 | 0 | 15.299 | 37.78
2022-03-29 19:00 | 44649.7917 | 0 | 14.9291 | 37.78
2022-03-29 19:30 | 44649.8125 | 0 | 14.5603 | 37.78
2022-03-29 20:00 | 44649.8333 | 0 | 14.1302 | 37.78
2022-03-29 20:30 | 44649.8542 | 0 | 13.8722 | 37.78
2022-03-29 21:00 | 44649.875 | 0 | 13.4275 | 37.78
2022-03-29 21:30 | 44649.8958 | 0 | 12.748 | 37.78
2022-03-29 22:00 | 44649.9167 | 0 | 12.135 | 37.78
2022-03-29 22:30 | 44649.9375 | 0 | 11.3117 | 37.78
2022-03-29 23:00 | 44649.9583 | 0 | 10.6648 | 37.78
2022-03-29 23:30 | 44649.9792 | 0 | 10.0874 | 37.78
2022-03-30 | 44650 | 0 | 9.5092 | 37.78
2022-03-30 00:30 | 44650.0208 | 0 | 9.3051 | 37.78
2022-03-30 01:00 | 44650.0417 | 0 | 9.0781 | 37.78
2022-03-30 01:30 | 44650.0625 | 0 | 8.9864 | 37.78
2022-03-30 02:00 | 44650.0833 | 0 | 8.8884 | 37.78
2022-03-30 02:30 | 44650.1042 | 0 | 8.9267 | 37.78
2022-03-30 03:00 | 44650.125 | 0 | 8.6625 | 37.78
2022-03-30 03:30 | 44650.1458 | 0 | 8.8229 | 37.78
2022-03-30 04:00 | 44650.1667 | 0 | 9.2349 | 37.78
2022-03-30 04:30 | 44650.1875 | 0 | 9.4096 | 37.78
2022-03-30 05:00 | 44650.2083 | 0 | 9.9489 | 37.78
2022-03-30 05:30 | 44650.2292 | 0 | 10.4873 | 37.78
2022-03-30 06:00 | 44650.25 | 0 | 11.5446 | 37.78
2022-03-30 06:30 | 44650.2708 | 0 | 12.4016 | 37.78
2022-03-30 07:00 | 44650.2917 | 0 | 13.6333 | 37.78
2022-03-30 07:30 | 44650.3125 | 0 | 13.7219 | 37.78
2022-03-30 08:00 | 44650.3333 | 0 | 13.5272 | 37.78
2022-03-30 08:30 | 44650.3542 | 0 | 12.3926 | 37.78
2022-03-30 09:00 | 44650.375 | 0 | 11.5487 | 37.78
2022-03-30 09:30 | 44650.3958 | 0 | 13.4191 | 37.78
2022-03-30 10:00 | 44650.4167 | 0 | 12.3741 | 37.78
2022-03-30 10:30 | 44650.4375 | 0 | 12.4121 | 37.78
2022-03-30 11:00 | 44650.4583 | 0 | 10.8903 | 37.78
2022-03-30 11:30 | 44650.4792 | 0 | 12.3777 | 37.78
2022-03-30 12:00 | 44650.5 | 0 | 11.0001 | 37.78
2022-03-30 12:30 | 44650.5208 | 0 | 10.8894 | 37.78
2022-03-30 13:00 | 44650.5417 | 0 | 10.7584 | 37.78
2022-03-30 13:30 | 44650.5625 | 0 | 11.4966 | 37.78
2022-03-30 14:00 | 44650.5833 | 0 | 14.0691 | 37.78
2022-03-30 14:30 | 44650.6042 | 0 | 13.9128 | 37.78
2022-03-30 15:00 | 44650.625 | 0 | 13.6101 | 37.78
2022-03-30 15:30 | 44650.6458 | 0 | 14.8797 | 37.78
2022-03-30 16:00 | 44650.6667 | 0 | 14.5153 | 37.78
2022-03-30 16:30 | 44650.6875 | 0 | 15.1228 | 37.78
2022-03-30 17:00 | 44650.7083 | 0 | 15.3226 | 37.78
2022-03-30 17:30 | 44650.7292 | 0 | 15.4675 | 37.78
2022-03-30 18:00 | 44650.75 | 0 | 15.876 | 37.78
2022-03-30 18:30 | 44650.7708 | 0 | 16.0247 | 37.78
2022-03-30 19:00 | 44650.7917 | 0 | 15.7025 | 37.78
2022-03-30 19:30 | 44650.8125 | 0 | 15.2927 | 37.78
2022-03-30 20:00 | 44650.8333 | 0 | 14.8183 | 37.78
2022-03-30 20:30 | 44650.8542 | 0 | 14.4553 | 37.78
2022-03-30 21:00 | 44650.875 | 0 | 13.9316 | 37.78
2022-03-30 21:30 | 44650.8958 | 0 | 13.6614 | 37.78
2022-03-30 22:00 | 44650.9167 | 0 | 12.9173 | 37.78
2022-03-30 22:30 | 44650.9375 | 0 | 11.9108 | 37.78
2022-03-30 23:00 | 44650.9583 | 0 | 11.2607 | 37.78
2022-03-30 23:30 | 44650.9792 | 0 | 10.6678 | 37.78
2022-03-31 | 44651 | 0 | 9.9732 | 37.78
2022-03-31 00:30 | 44651.0208 | 0 | 9.7409 | 37.78
2022-03-31 01:00 | 44651.0417 | 0 | 9.686 | 37.78
2022-03-31 01:30 | 44651.0625 | 0 | 9.5198 | 37.78
2022-03-31 02:00 | 44651.0833 | 0 | 9.3872 | 37.78
2022-03-31 02:30 | 44651.1042 | 0 | 9.3115 | 37.78
2022-03-31 03:00 | 44651.125 | 0 | 9.1085 | 37.78
2022-03-31 03:30 | 44651.1458 | 0 | 9.0349 | 37.78
2022-03-31 04:00 | 44651.1667 | 0 | 9.4802 | 37.78
2022-03-31 04:30 | 44651.1875 | 0 | 9.6506 | 37.78
2022-03-31 05:00 | 44651.2083 | 0 | 10.115 | 37.78
2022-03-31 05:30 | 44651.2292 | 0 | 10.8731 | 37.78
2022-03-31 06:00 | 44651.25 | 0 | 11.7714 | 37.78
2022-03-31 06:30 | 44651.2708 | 0 | 12.9032 | 37.78
2022-03-31 07:00 | 44651.2917 | 0 | 13.697 | 37.78
2022-03-31 07:30 | 44651.3125 | 0 | 13.6017 | 37.78
2022-03-31 08:00 | 44651.3333 | 0 | 13.469 | 37.78
2022-03-31 08:30 | 44651.3542 | 0 | 13.3363 | 37.78
2022-03-31 09:00 | 44651.375 | 0 | 13.097 | 37.78
2022-03-31 09:30 | 44651.3958 | 0 | 14.7724 | 37.78
2022-03-31 10:00 | 44651.4167 | 0 | 14.2314 | 37.78
2022-03-31 10:30 | 44651.4375 | 0 | 13.7206 | 37.78
2022-03-31 11:00 | 44651.4583 | 0 | 14.452 | 37.78
2022-03-31 11:30 | 44651.4792 | 0 | 15.1129 | 37.78
2022-03-31 12:00 | 44651.5 | 0 | 15.1678 | 37.78
2022-03-31 12:30 | 44651.5208 | 0 | 15.6628 | 37.78
2022-03-31 13:00 | 44651.5417 | 0 | 15.7021 | 37.78
2022-03-31 13:30 | 44651.5625 | 0 | 16.7692 | 37.78
2022-03-31 14:00 | 44651.5833 | 0 | 16.2654 | 37.78
2022-03-31 14:30 | 44651.6042 | 0 | 16.1916 | 37.78
2022-03-31 15:00 | 44651.625 | 0 | 15.3651 | 37.78
2022-03-31 15:30 | 44651.6458 | 0 | 14.6098 | 37.78
2022-03-31 16:00 | 44651.6667 | 0 | 14.7057 | 37.78
2022-03-31 16:30 | 44651.6875 | 0 | 14.9032 | 37.78
2022-03-31 17:00 | 44651.7083 | 0 | 15.417 | 37.78
2022-03-31 17:30 | 44651.7292 | 0 | 15.8886 | 37.78
2022-03-31 18:00 | 44651.75 | 0 | 16.0882 | 37.78
2022-03-31 18:30 | 44651.7708 | 0 | 16.1116 | 37.78
2022-03-31 19:00 | 44651.7917 | 0 | 15.8474 | 37.78
2022-03-31 19:30 | 44651.8125 | 0 | 15.5013 | 37.78
2022-03-31 20:00 | 44651.8333 | 0 | 14.9787 | 37.78
2022-03-31 20:30 | 44651.8542 | 0 | 14.4735 | 37.78
2022-03-31 21:00 | 44651.875 | 0 | 13.9192 | 37.78
2022-03-31 21:30 | 44651.8958 | 0 | 13.453 | 37.78
2022-03-31 22:00 | 44651.9167 | 0 | 12.9542 | 37.78
2022-03-31 22:30 | 44651.9375 | 0 | 11.9744 | 37.78
2022-03-31 23:00 | 44651.9583 | 0 | 11.1218 | 37.78
2022-03-31 23:30 | 44651.9792 | 0 | 10.5724 | 37.78
2022-04-01 | 44652 | 0 | 10.088 | 37.78
2022-04-01 00:30 | 44652.0208 | 0 | 9.8063 | 37.78
2022-04-01 01:00 | 44652.0417 | 0 | 9.5433 | 37.78
2022-04-01 01:30 | 44652.0625 | 0 | 9.345 | 37.78
2022-04-01 02:00 | 44652.0833 | 0 | 9.3328 | 37.78
2022-04-01 02:30 | 44652.1042 | 0 | 9.062 | 37.78
2022-04-01 03:00 | 44652.125 | 0 | 8.9813 | 37.78
2022-04-01 03:30 | 44652.1458 | 0 | 8.9654 | 37.78
2022-04-01 04:00 | 44652.1667 | 0 | 9.2805 | 37.78
2022-04-01 04:30 | 44652.1875 | 0 | 9.6528 | 37.78
2022-04-01 05:00 | 44652.2083 | 0 | 9.9073 | 37.78
2022-04-01 05:30 | 44652.2292 | 0 | 10.5033 | 37.78
2022-04-01 06:00 | 44652.25 | 0 | 11.1902 | 37.78
2022-04-01 06:30 | 44652.2708 | 0 | 11.6796 | 37.78
2022-04-01 07:00 | 44652.2917 | 0 | 11.8524 | 37.78
2022-04-01 07:30 | 44652.3125 | 0 | 11.5558 | 37.78
2022-04-01 08:00 | 44652.3333 | 0 | 11.3114 | 37.78
2022-04-01 08:30 | 44652.3542 | 0 | 10.9701 | 37.78
2022-04-01 09:00 | 44652.375 | 0 | 10.6087 | 37.78
2022-04-01 09:30 | 44652.3958 | 0 | 10.3015 | 37.78
2022-04-01 10:00 | 44652.4167 | 0 | 10.1464 | 37.78
2022-04-01 10:30 | 44652.4375 | 0 | 10.0187 | 37.78
2022-04-01 11:00 | 44652.4583 | 0 | 10.0174 | 37.78
2022-04-01 11:30 | 44652.4792 | 0 | 10.0734 | 37.78
2022-04-01 12:00 | 44652.5 | 0 | 10.0012 | 37.78
2022-04-01 12:30 | 44652.5208 | 0 | 9.9554 | 37.78
2022-04-01 13:00 | 44652.5417 | 0 | 10.3476 | 37.78
2022-04-01 13:30 | 44652.5625 | 0 | 10.8773 | 37.78
2022-04-01 14:00 | 44652.5833 | 0 | 11.7772 | 37.78
2022-04-01 14:30 | 44652.6042 | 0 | 13.1262 | 37.78
2022-04-01 15:00 | 44652.625 | 0 | 12.9522 | 37.78
2022-04-01 15:30 | 44652.6458 | 0 | 13.707 | 37.78
2022-04-01 16:00 | 44652.6667 | 0 | 14.1492 | 37.78
2022-04-01 16:30 | 44652.6875 | 0 | 14.6414 | 37.78
2022-04-01 17:00 | 44652.7083 | 0 | 14.7942 | 37.78
2022-04-01 17:30 | 44652.7292 | 0 | 14.8898 | 37.78
2022-04-01 18:00 | 44652.75 | 0 | 14.8746 | 37.78
2022-04-01 18:30 | 44652.7708 | 0 | 14.8686 | 37.78
2022-04-01 19:00 | 44652.7917 | 0 | 14.7111 | 37.78
2022-04-01 19:30 | 44652.8125 | 0 | 14.147 | 37.78
2022-04-01 20:00 | 44652.8333 | 0 | 13.7167 | 37.78
2022-04-01 20:30 | 44652.8542 | 0 | 13.3645 | 37.78
2022-04-01 21:00 | 44652.875 | 0 | 13.238 | 37.78
2022-04-01 21:30 | 44652.8958 | 0 | 12.6325 | 37.78
2022-04-01 22:00 | 44652.9167 | 0 | 12.0863 | 37.78
2022-04-01 22:30 | 44652.9375 | 0 | 11.3791 | 37.78
2022-04-01 23:00 | 44652.9583 | 0 | 10.5842 | 37.78
2022-04-01 23:30 | 44652.9792 | 0 | 10.1676 | 37.78
2022-04-02 | 44653 | 0 | 9.7917 | 37.78
2022-04-02 00:30 | 44653.0208 | 0 | 9.2842 | 37.78
2022-04-02 01:00 | 44653.0417 | 0 | 9.1022 | 37.78
2022-04-02 01:30 | 44653.0625 | 0 | 8.8246 | 37.78
2022-04-02 02:00 | 44653.0833 | 0 | 8.7249 | 37.78
2022-04-02 02:30 | 44653.1042 | 0 | 8.5213 | 37.78
2022-04-02 03:00 | 44653.125 | 0 | 8.5346 | 37.78
2022-04-02 03:30 | 44653.1458 | 0 | 8.4257 | 37.78
2022-04-02 04:00 | 44653.1667 | 0 | 8.539 | 37.78
2022-04-02 04:30 | 44653.1875 | 0 | 8.5632 | 37.78
2022-04-02 05:00 | 44653.2083 | 0 | 8.5392 | 37.78
2022-04-02 05:30 | 44653.2292 | 0 | 8.6597 | 37.78
2022-04-02 06:00 | 44653.25 | 0 | 9.1629 | 37.78
2022-04-02 06:30 | 44653.2708 | 0 | 9.3425 | 37.78
2022-04-02 07:00 | 44653.2917 | 0 | 9.2765 | 37.78
2022-04-02 07:30 | 44653.3125 | 0 | 8.8544 | 37.78
2022-04-02 08:00 | 44653.3333 | 0 | 8.7124 | 37.78
2022-04-02 08:30 | 44653.3542 | 0 | 8.5855 | 37.78
2022-04-02 09:00 | 44653.375 | 0 | 8.4534 | 37.78
2022-04-02 09:30 | 44653.3958 | 0 | 8.261 | 37.78
2022-04-02 10:00 | 44653.4167 | 0 | 7.9266 | 37.78
2022-04-02 10:30 | 44653.4375 | 0 | 8.7736 | 37.78
2022-04-02 11:00 | 44653.4583 | 0 | 9.898 | 37.78
2022-04-02 11:30 | 44653.4792 | 0 | 11.6657 | 37.78
2022-04-02 12:00 | 44653.5 | 0 | 11.333 | 37.78
2022-04-02 12:30 | 44653.5208 | 0 | 10.9362 | 37.78
2022-04-02 13:00 | 44653.5417 | 0 | 9.2554 | 37.78
2022-04-02 13:30 | 44653.5625 | 0 | 10.4994 | 37.78
2022-04-02 14:00 | 44653.5833 | 0 | 9.0565 | 37.78
2022-04-02 14:30 | 44653.6042 | 0 | 10.4476 | 37.78
2022-04-02 15:00 | 44653.625 | 0 | 12.4346 | 37.78
2022-04-02 15:30 | 44653.6458 | 0 | 10.6882 | 37.78
2022-04-02 16:00 | 44653.6667 | 0 | 11.3769 | 37.78
2022-04-02 16:30 | 44653.6875 | 0 | 12.245 | 37.78
2022-04-02 17:00 | 44653.7083 | 0 | 12.9041 | 37.78
2022-04-02 17:30 | 44653.7292 | 0 | 13.094 | 37.78
2022-04-02 18:00 | 44653.75 | 0 | 13.3526 | 37.78
2022-04-02 18:30 | 44653.7708 | 0 | 13.3894 | 37.78
2022-04-02 19:00 | 44653.7917 | 0 | 13.2338 | 37.78
2022-04-02 19:30 | 44653.8125 | 0 | 12.8024 | 37.78
2022-04-02 20:00 | 44653.8333 | 0 | 12.5324 | 37.78
2022-04-02 20:30 | 44653.8542 | 0 | 12.1278 | 37.78
2022-04-02 21:00 | 44653.875 | 0 | 11.851 | 37.78
2022-04-02 21:30 | 44653.8958 | 0 | 11.6676 | 37.78
2022-04-02 22:00 | 44653.9167 | 0 | 11.3244 | 37.78
2022-04-02 22:30 | 44653.9375 | 0 | 10.6596 | 37.78
2022-04-02 23:00 | 44653.9583 | 0 | 9.9803 | 37.78
2022-04-02 23:30 | 44653.9792 | 0 | 9.6254 | 37.78
2022-04-03 | 44654 | 0 | 9.3165 | 37.78
2022-04-03 00:30 | 44654.0208 | 0 | 8.9738 | 37.78
2022-04-03 01:00 | 44654.0417 | 0 | 8.7567 | 37.78
2022-04-03 01:30 | 44654.0625 | 0 | 8.5553 | 37.78
2022-04-03 02:00 | 44654.0833 | 0 | 8.3601 | 37.78
2022-04-03 02:30 | 44654.1042 | 0 | 8.2419 | 37.78
2022-04-03 03:00 | 44654.125 | 0 | 8.0612 | 37.78
2022-04-03 03:30 | 44654.1458 | 0 | 8.128 | 37.78
2022-04-03 04:00 | 44654.1667 | 0 | 7.9876 | 37.78
2022-04-03 04:30 | 44654.1875 | 0 | 7.8825 | 37.78
2022-04-03 05:00 | 44654.2083 | 0 | 7.9999 | 37.78
2022-04-03 05:30 | 44654.2292 | 0 | 8.0856 | 37.78
2022-04-03 06:00 | 44654.25 | 0 | 8.2612 | 37.78
2022-04-03 06:30 | 44654.2708 | 0 | 8.3334 | 37.78
2022-04-03 07:00 | 44654.2917 | 0 | 8.2373 | 37.78
2022-04-03 07:30 | 44654.3125 | 0 | 7.9021 | 37.78
2022-04-03 08:00 | 44654.3333 | 0 | 7.7836 | 37.78
2022-04-03 08:30 | 44654.3542 | 0 | 7.8048 | 37.78
2022-04-03 09:00 | 44654.375 | 0 | 8.7531 | 37.78
2022-04-03 09:30 | 44654.3958 | 0 | 8.9434 | 37.78
2022-04-03 10:00 | 44654.4167 | 0 | 8.3038 | 37.78
2022-04-03 10:30 | 44654.4375 | 0 | 8.5762 | 37.78
2022-04-03 11:00 | 44654.4583 | 0 | 7.3394 | 37.78
2022-04-03 11:30 | 44654.4792 | 0 | 7.7904 | 37.78
2022-04-03 12:00 | 44654.5 | 0 | 7.6732 | 37.78
2022-04-03 12:30 | 44654.5208 | 0 | 7.9169 | 37.78
2022-04-03 13:00 | 44654.5417 | 0 | 8.6497 | 37.78
2022-04-03 13:30 | 44654.5625 | 0 | 9.1697 | 37.78
2022-04-03 14:00 | 44654.5833 | 0 | 9.924 | 37.78
2022-04-03 14:30 | 44654.6042 | 0 | 10.6149 | 37.78
2022-04-03 15:00 | 44654.625 | 0 | 11.2017 | 37.78
2022-04-03 15:30 | 44654.6458 | 0 | 12.2814 | 37.78
2022-04-03 16:00 | 44654.6667 | 0 | 13.2535 | 37.78
2022-04-03 16:30 | 44654.6875 | 0 | 14.1333 | 37.78
2022-04-03 17:00 | 44654.7083 | 0 | 14.5565 | 37.78
2022-04-03 17:30 | 44654.7292 | 0 | 14.4247 | 37.78
2022-04-03 18:00 | 44654.75 | 0 | 14.8662 | 37.78
2022-04-03 18:30 | 44654.7708 | 0 | 14.9052 | 37.78
2022-04-03 19:00 | 44654.7917 | 0 | 14.8591 | 37.78
2022-04-03 19:30 | 44654.8125 | 0 | 14.2627 | 37.78
2022-04-03 20:00 | 44654.8333 | 0 | 13.9246 | 37.78
2022-04-03 20:30 | 44654.8542 | 0 | 13.2872 | 37.78
2022-04-03 21:00 | 44654.875 | 0 | 12.9388 | 37.78
2022-04-03 21:30 | 44654.8958 | 0 | 12.3348 | 37.78
2022-04-03 22:00 | 44654.9167 | 0 | 11.9921 | 37.78
2022-04-03 22:30 | 44654.9375 | 0 | 11.0462 | 37.78
2022-04-03 23:00 | 44654.9583 | 0 | 10.5051 | 37.78
2022-04-03 23:30 | 44654.9792 | 0 | 9.979 | 37.78
2022-04-04 | 44655 | 0 | 9.532 | 37.78
2022-04-04 00:30 | 44655.0208 | 0 | 9.1677 | 37.78
2022-04-04 01:00 | 44655.0417 | 0 | 9.0768 | 37.78
2022-04-04 01:30 | 44655.0625 | 0 | 9.0427 | 37.78
2022-04-04 02:00 | 44655.0833 | 0 | 8.8685 | 37.78
2022-04-04 02:30 | 44655.1042 | 0 | 8.7386 | 37.78
2022-04-04 03:00 | 44655.125 | 0 | 8.7493 | 37.78
2022-04-04 03:30 | 44655.1458 | 0 | 8.7553 | 37.78
2022-04-04 04:00 | 44655.1667 | 0 | 9.0644 | 37.78
2022-04-04 04:30 | 44655.1875 | 0 | 9.3056 | 37.78
2022-04-04 05:00 | 44655.2083 | 0 | 9.8999 | 37.78
2022-04-04 05:30 | 44655.2292 | 0 | 10.573 | 37.78
2022-04-04 06:00 | 44655.25 | 0 | 11.2984 | 37.78
2022-04-04 06:30 | 44655.2708 | 0 | 12.0343 | 37.78
2022-04-04 07:00 | 44655.2917 | 0 | 12.918 | 37.78
2022-04-04 07:30 | 44655.3125 | 0 | 12.8325 | 37.78
2022-04-04 08:00 | 44655.3333 | 0 | 13.7196 | 37.78
2022-04-04 08:30 | 44655.3542 | 0 | 12.8281 | 37.78
2022-04-04 09:00 | 44655.375 | 0 | 12.3999 | 37.78
2022-04-04 09:30 | 44655.3958 | 0 | 12.8036 | 37.78
2022-04-04 10:00 | 44655.4167 | 0 | 11.6699 | 37.78
2022-04-04 10:30 | 44655.4375 | 0 | 12.8764 | 37.78
2022-04-04 11:00 | 44655.4583 | 0 | 12.8362 | 37.78
2022-04-04 11:30 | 44655.4792 | 0 | 12.1191 | 37.78
2022-04-04 12:00 | 44655.5 | 0 | 11.6354 | 37.78
2022-04-04 12:30 | 44655.5208 | 0 | 11.3947 | 37.78
2022-04-04 13:00 | 44655.5417 | 0 | 11.4872 | 37.78
2022-04-04 13:30 | 44655.5625 | 0 | 12.9148 | 37.78
2022-04-04 14:00 | 44655.5833 | 0 | 13.9005 | 37.78
2022-04-04 14:30 | 44655.6042 | 0 | 12.9883 | 37.78
2022-04-04 15:00 | 44655.625 | 0 | 13.5217 | 37.78
2022-04-04 15:30 | 44655.6458 | 0 | 14.5357 | 37.78
2022-04-04 16:00 | 44655.6667 | 0 | 15.1621 | 37.78
2022-04-04 16:30 | 44655.6875 | 0 | 16.0213 | 37.78
2022-04-04 17:00 | 44655.7083 | 0 | 15.9116 | 37.78
2022-04-04 17:30 | 44655.7292 | 0 | 16.0781 | 37.78
2022-04-04 18:00 | 44655.75 | 0 | 16.3957 | 37.78
2022-04-04 18:30 | 44655.7708 | 0 | 16.5587 | 37.78
2022-04-04 19:00 | 44655.7917 | 0 | 16.3333 | 37.78
2022-04-04 19:30 | 44655.8125 | 0 | 15.7857 | 37.78
2022-04-04 20:00 | 44655.8333 | 0 | 15.2387 | 37.78
2022-04-04 20:30 | 44655.8542 | 0 | 14.4632 | 37.78
2022-04-04 21:00 | 44655.875 | 0 | 14.0699 | 37.78
2022-04-04 21:30 | 44655.8958 | 0 | 13.5699 | 37.78
2022-04-04 22:00 | 44655.9167 | 0 | 12.8843 | 37.78
2022-04-04 22:30 | 44655.9375 | 0 | 11.8702 | 37.78
2022-04-04 23:00 | 44655.9583 | 0 | 11.1773 | 37.78
2022-04-04 23:30 | 44655.9792 | 0 | 10.617 | 37.78
2022-04-05 | 44656 | 0 | 9.9713 | 37.78
2022-04-05 00:30 | 44656.0208 | 0 | 9.7966 | 37.78
2022-04-05 01:00 | 44656.0417 | 0 | 9.6198 | 37.78
2022-04-05 01:30 | 44656.0625 | 0 | 9.4689 | 37.78
2022-04-05 02:00 | 44656.0833 | 0 | 9.2148 | 37.78
2022-04-05 02:30 | 44656.1042 | 0 | 9.2367 | 37.78
2022-04-05 03:00 | 44656.125 | 0 | 9.0308 | 37.78
2022-04-05 03:30 | 44656.1458 | 0 | 9.0668 | 37.78
2022-04-05 04:00 | 44656.1667 | 0 | 9.4336 | 37.78
2022-04-05 04:30 | 44656.1875 | 0 | 9.6102 | 37.78
2022-04-05 05:00 | 44656.2083 | 0 | 10.2718 | 37.78
2022-04-05 05:30 | 44656.2292 | 0 | 10.801 | 37.78
2022-04-05 06:00 | 44656.25 | 0 | 11.3201 | 37.78
2022-04-05 06:30 | 44656.2708 | 0 | 11.72 | 37.78
2022-04-05 07:00 | 44656.2917 | 0 | 12.0942 | 37.78
2022-04-05 07:30 | 44656.3125 | 0 | 11.9773 | 37.78
2022-04-05 08:00 | 44656.3333 | 0 | 11.6998 | 37.78
2022-04-05 08:30 | 44656.3542 | 0 | 11.6651 | 37.78
2022-04-05 09:00 | 44656.375 | 0 | 11.3383 | 37.78
2022-04-05 09:30 | 44656.3958 | 0 | 11.3285 | 37.78
2022-04-05 10:00 | 44656.4167 | 0 | 11.2478 | 37.78
2022-04-05 10:30 | 44656.4375 | 0 | 11.2894 | 37.78
2022-04-05 11:00 | 44656.4583 | 0 | 11.2225 | 37.78
2022-04-05 11:30 | 44656.4792 | 0 | 11.452 | 37.78
2022-04-05 12:00 | 44656.5 | 0 | 11.7257 | 37.78
2022-04-05 12:30 | 44656.5208 | 0 | 12.1978 | 37.78
2022-04-05 13:00 | 44656.5417 | 0 | 12.6961 | 37.78
2022-04-05 13:30 | 44656.5625 | 0 | 13.215 | 37.78
2022-04-05 14:00 | 44656.5833 | 0 | 13.9604 | 37.78
2022-04-05 14:30 | 44656.6042 | 0 | 14.3395 | 37.78
2022-04-05 15:00 | 44656.625 | 0 | 14.7217 | 37.78
2022-04-05 15:30 | 44656.6458 | 0 | 15.6029 | 37.78
2022-04-05 16:00 | 44656.6667 | 0 | 15.9754 | 37.78
2022-04-05 16:30 | 44656.6875 | 0 | 16.8567 | 37.78
2022-04-05 17:00 | 44656.7083 | 0 | 16.5921 | 37.78
2022-04-05 17:30 | 44656.7292 | 0 | 16.6159 | 37.78
2022-04-05 18:00 | 44656.75 | 0 | 16.6829 | 37.78
2022-04-05 18:30 | 44656.7708 | 0 | 17.0367 | 37.78
2022-04-05 19:00 | 44656.7917 | 0 | 16.3953 | 37.78
2022-04-05 19:30 | 44656.8125 | 0 | 15.786 | 37.78
2022-04-05 20:00 | 44656.8333 | 0 | 15.2619 | 37.78
2022-04-05 20:30 | 44656.8542 | 0 | 14.9662 | 37.78
2022-04-05 21:00 | 44656.875 | 0 | 14.3743 | 37.78
2022-04-05 21:30 | 44656.8958 | 0 | 13.7846 | 37.78
2022-04-05 22:00 | 44656.9167 | 0 | 13.0534 | 37.78
2022-04-05 22:30 | 44656.9375 | 0 | 12.0546 | 37.78
2022-04-05 23:00 | 44656.9583 | 0 | 11.5642 | 37.78
2022-04-05 23:30 | 44656.9792 | 0 | 11.1319 | 37.78
2022-04-06 | 44657 | 0 | 10.6024 | 37.78
2022-04-06 00:30 | 44657.0208 | 0 | 10.0808 | 37.78
2022-04-06 01:00 | 44657.0417 | 0 | 9.7286 | 37.78
2022-04-06 01:30 | 44657.0625 | 0 | 9.6367 | 37.78
2022-04-06 02:00 | 44657.0833 | 0 | 9.5612 | 37.78
2022-04-06 02:30 | 44657.1042 | 0 | 9.6081 | 37.78
2022-04-06 03:00 | 44657.125 | 0 | 9.4607 | 37.78
2022-04-06 03:30 | 44657.1458 | 0 | 9.4358 | 37.78
2022-04-06 04:00 | 44657.1667 | 0 | 9.7933 | 37.78
2022-04-06 04:30 | 44657.1875 | 0 | 9.9945 | 37.78
2022-04-06 05:00 | 44657.2083 | 0 | 10.5361 | 37.78
2022-04-06 05:30 | 44657.2292 | 0 | 11.1104 | 37.78
2022-04-06 06:00 | 44657.25 | 0 | 11.7379 | 37.78
2022-04-06 06:30 | 44657.2708 | 0 | 12.0116 | 37.78
2022-04-06 07:00 | 44657.2917 | 0 | 12.5967 | 37.78
2022-04-06 07:30 | 44657.3125 | 0 | 13.1024 | 37.78
2022-04-06 08:00 | 44657.3333 | 0 | 12.5843 | 37.78
2022-04-06 08:30 | 44657.3542 | 0 | 12.7149 | 37.78
2022-04-06 09:00 | 44657.375 | 0 | 12.7079 | 37.78
2022-04-06 09:30 | 44657.3958 | 0 | 13.3124 | 37.78
2022-04-06 10:00 | 44657.4167 | 0 | 12.027 | 37.78
2022-04-06 10:30 | 44657.4375 | 0 | 13.8368 | 37.78
2022-04-06 11:00 | 44657.4583 | 0 | 11.9312 | 37.78
2022-04-06 11:30 | 44657.4792 | 0 | 11.899 | 37.78
2022-04-06 12:00 | 44657.5 | 0 | 11.8024 | 37.78
2022-04-06 12:30 | 44657.5208 | 0 | 12.4312 | 37.78
2022-04-06 13:00 | 44657.5417 | 0 | 12.631 | 37.78
2022-04-06 13:30 | 44657.5625 | 0 | 13.6324 | 37.78
2022-04-06 14:00 | 44657.5833 | 0 | 13.5377 | 37.78
2022-04-06 14:30 | 44657.6042 | 0 | 13.6564 | 37.78
2022-04-06 15:00 | 44657.625 | 0 | 14.4675 | 37.78
2022-04-06 15:30 | 44657.6458 | 0 | 14.5965 | 37.78
2022-04-06 16:00 | 44657.6667 | 0 | 15.1627 | 37.78
2022-04-06 16:30 | 44657.6875 | 0 | 15.5318 | 37.78
2022-04-06 17:00 | 44657.7083 | 0 | 15.2967 | 37.78
2022-04-06 17:30 | 44657.7292 | 0 | 15.5111 | 37.78
2022-04-06 18:00 | 44657.75 | 0 | 15.6077 | 37.78
2022-04-06 18:30 | 44657.7708 | 0 | 15.8216 | 37.78
2022-04-06 19:00 | 44657.7917 | 0 | 15.3724 | 37.78
2022-04-06 19:30 | 44657.8125 | 0 | 14.9683 | 37.78
2022-04-06 20:00 | 44657.8333 | 0 | 14.561 | 37.78
2022-04-06 20:30 | 44657.8542 | 0 | 13.8414 | 37.78
2022-04-06 21:00 | 44657.875 | 0 | 13.3618 | 37.78
2022-04-06 21:30 | 44657.8958 | 0 | 13.0074 | 37.78
2022-04-06 22:00 | 44657.9167 | 0 | 12.3802 | 37.78
2022-04-06 22:30 | 44657.9375 | 0 | 11.6526 | 37.78
2022-04-06 23:00 | 44657.9583 | 0 | 11.489 | 37.78
2022-04-06 23:30 | 44657.9792 | 0 | 11.0822 | 37.78
2022-04-07 | 44658 | 0 | 10.5191 | 37.78
2022-04-07 00:30 | 44658.0208 | 0 | 9.9748 | 37.78
2022-04-07 01:00 | 44658.0417 | 0 | 9.8859 | 37.78
2022-04-07 01:30 | 44658.0625 | 0 | 9.2894 | 37.78
2022-04-07 02:00 | 44658.0833 | 0 | 9.1187 | 37.78
2022-04-07 02:30 | 44658.1042 | 0 | 9.1462 | 37.78
2022-04-07 03:00 | 44658.125 | 0 | 8.8852 | 37.78
2022-04-07 03:30 | 44658.1458 | 0 | 8.8818 | 37.78
2022-04-07 04:00 | 44658.1667 | 0 | 9.1882 | 37.78
2022-04-07 04:30 | 44658.1875 | 0 | 9.55 | 37.78
2022-04-07 05:00 | 44658.2083 | 0 | 10.3294 | 37.78
2022-04-07 05:30 | 44658.2292 | 0 | 10.6198 | 37.78
2022-04-07 06:00 | 44658.25 | 0 | 11.4422 | 37.78
2022-04-07 06:30 | 44658.2708 | 0 | 11.5898 | 37.78
2022-04-07 07:00 | 44658.2917 | 0 | 12.2935 | 37.78
2022-04-07 07:30 | 44658.3125 | 0 | 12.2293 | 37.78
2022-04-07 08:00 | 44658.3333 | 0 | 11.4256 | 37.78
2022-04-07 08:30 | 44658.3542 | 0 | 12.5239 | 37.78
2022-04-07 09:00 | 44658.375 | 0 | 11.0322 | 37.78
2022-04-07 09:30 | 44658.3958 | 0 | 10.9171 | 37.78
2022-04-07 10:00 | 44658.4167 | 0 | 10.409 | 37.78
2022-04-07 10:30 | 44658.4375 | 0 | 10.5246 | 37.78
2022-04-07 11:00 | 44658.4583 | 0 | 12.6076 | 37.78
2022-04-07 11:30 | 44658.4792 | 0 | 12.3878 | 37.78
2022-04-07 12:00 | 44658.5 | 0 | 12.1791 | 37.78
2022-04-07 12:30 | 44658.5208 | 0 | 10.6405 | 37.78
2022-04-07 13:00 | 44658.5417 | 0 | 11.6727 | 37.78
2022-04-07 13:30 | 44658.5625 | 0 | 12.297 | 37.78
2022-04-07 14:00 | 44658.5833 | 0 | 12.5267 | 37.78
2022-04-07 14:30 | 44658.6042 | 0 | 12.4737 | 37.78
2022-04-07 15:00 | 44658.625 | 0 | 13.0478 | 37.78
2022-04-07 15:30 | 44658.6458 | 0 | 13.5609 | 37.78
2022-04-07 16:00 | 44658.6667 | 0 | 14.485 | 37.78
2022-04-07 16:30 | 44658.6875 | 0 | 15.1824 | 37.78
2022-04-07 17:00 | 44658.7083 | 0 | 15.29 | 37.78
2022-04-07 17:30 | 44658.7292 | 0 | 15.3374 | 37.78
2022-04-07 18:00 | 44658.75 | 0 | 15.487 | 37.78
2022-04-07 18:30 | 44658.7708 | 0 | 15.5946 | 37.78
2022-04-07 19:00 | 44658.7917 | 0 | 15.3675 | 37.78
2022-04-07 19:30 | 44658.8125 | 0 | 15.08 | 37.78
2022-04-07 20:00 | 44658.8333 | 0 | 14.691 | 37.78
2022-04-07 20:30 | 44658.8542 | 0 | 14.0803 | 37.78
2022-04-07 21:00 | 44658.875 | 0 | 13.4041 | 37.78
2022-04-07 21:30 | 44658.8958 | 0 | 13.1342 | 37.78
2022-04-07 22:00 | 44658.9167 | 0 | 12.6369 | 37.78
2022-04-07 22:30 | 44658.9375 | 0 | 11.7404 | 37.78
2022-04-07 23:00 | 44658.9583 | 0 | 11.1386 | 37.78
2022-04-07 23:30 | 44658.9792 | 0 | 10.7513 | 37.78
2022-04-08 | 44659 | 0 | 10.0994 | 37.78
2022-04-08 00:30 | 44659.0208 | 0 | 9.7272 | 37.78
2022-04-08 01:00 | 44659.0417 | 0 | 9.5481 | 37.78
2022-04-08 01:30 | 44659.0625 | 0 | 9.2888 | 37.78
2022-04-08 02:00 | 44659.0833 | 0 | 9.1089 | 37.78
2022-04-08 02:30 | 44659.1042 | 0 | 9.0799 | 37.78
2022-04-08 03:00 | 44659.125 | 0 | 8.8858 | 37.78
2022-04-08 03:30 | 44659.1458 | 0 | 8.9096 | 37.78
2022-04-08 04:00 | 44659.1667 | 0 | 9.2199 | 37.78
2022-04-08 04:30 | 44659.1875 | 0 | 9.4934 | 37.78
2022-04-08 05:00 | 44659.2083 | 0 | 10.09 | 37.78
2022-04-08 05:30 | 44659.2292 | 0 | 10.5881 | 37.78
2022-04-08 06:00 | 44659.25 | 0 | 11.2518 | 37.78
2022-04-08 06:30 | 44659.2708 | 0 | 11.9783 | 37.78
2022-04-08 07:00 | 44659.2917 | 0 | 12.25 | 37.78
2022-04-08 07:30 | 44659.3125 | 0 | 11.7374 | 37.78
2022-04-08 08:00 | 44659.3333 | 0 | 11.7461 | 37.78
2022-04-08 08:30 | 44659.3542 | 0 | 11.6779 | 37.78
2022-04-08 09:00 | 44659.375 | 0 | 12.9015 | 37.78
2022-04-08 09:30 | 44659.3958 | 0 | 11.0735 | 37.78
2022-04-08 10:00 | 44659.4167 | 0 | 11.394 | 37.78
2022-04-08 10:30 | 44659.4375 | 0 | 10.3282 | 37.78
2022-04-08 11:00 | 44659.4583 | 0 | 10.5991 | 37.78
2022-04-08 11:30 | 44659.4792 | 0 | 11.1278 | 37.78
2022-04-08 12:00 | 44659.5 | 0 | 11.463 | 37.78
2022-04-08 12:30 | 44659.5208 | 0 | 12.0867 | 37.78
2022-04-08 13:00 | 44659.5417 | 0 | 11.7349 | 37.78
2022-04-08 13:30 | 44659.5625 | 0 | 12.1187 | 37.78
2022-04-08 14:00 | 44659.5833 | 0 | 12.0993 | 37.78
2022-04-08 14:30 | 44659.6042 | 0 | 12.1741 | 37.78
2022-04-08 15:00 | 44659.625 | 0 | 13.6942 | 37.78
2022-04-08 15:30 | 44659.6458 | 0 | 13.7321 | 37.78
2022-04-08 16:00 | 44659.6667 | 0 | 13.7554 | 37.78
2022-04-08 16:30 | 44659.6875 | 0 | 14.2796 | 37.78
2022-04-08 17:00 | 44659.7083 | 0 | 14.5304 | 37.78
2022-04-08 17:30 | 44659.7292 | 0 | 14.6058 | 37.78
2022-04-08 18:00 | 44659.75 | 0 | 14.7061 | 37.78
2022-04-08 18:30 | 44659.7708 | 0 | 14.5628 | 37.78
2022-04-08 19:00 | 44659.7917 | 0 | 14.4753 | 37.78
2022-04-08 19:30 | 44659.8125 | 0 | 14.0428 | 37.78
2022-04-08 20:00 | 44659.8333 | 0 | 13.689 | 37.78
2022-04-08 20:30 | 44659.8542 | 0 | 13.2549 | 37.78
2022-04-08 21:00 | 44659.875 | 0 | 13.0182 | 37.78
2022-04-08 21:30 | 44659.8958 | 0 | 12.7319 | 37.78
2022-04-08 22:00 | 44659.9167 | 0 | 12.3097 | 37.78
2022-04-08 22:30 | 44659.9375 | 0 | 11.5955 | 37.78
2022-04-08 23:00 | 44659.9583 | 0 | 11.0255 | 37.78
2022-04-08 23:30 | 44659.9792 | 0 | 10.4836 | 37.78
2022-04-09 | 44660 | 0 | 9.9736 | 37.78
2022-04-09 00:30 | 44660.0208 | 0 | 9.4967 | 37.78
2022-04-09 01:00 | 44660.0417 | 0 | 9.3867 | 37.78
2022-04-09 01:30 | 44660.0625 | 0 | 9.1669 | 37.78
2022-04-09 02:00 | 44660.0833 | 0 | 8.9633 | 37.78
2022-04-09 02:30 | 44660.1042 | 0 | 8.8116 | 37.78
2022-04-09 03:00 | 44660.125 | 0 | 8.6109 | 37.78
2022-04-09 03:30 | 44660.1458 | 0 | 8.5727 | 37.78
2022-04-09 04:00 | 44660.1667 | 0 | 8.7509 | 37.78
2022-04-09 04:30 | 44660.1875 | 0 | 8.7281 | 37.78
2022-04-09 05:00 | 44660.2083 | 0 | 8.7874 | 37.78
2022-04-09 05:30 | 44660.2292 | 0 | 9.0577 | 37.78
2022-04-09 06:00 | 44660.25 | 0 | 9.338 | 37.78
2022-04-09 06:30 | 44660.2708 | 0 | 9.6183 | 37.78
2022-04-09 07:00 | 44660.2917 | 0 | 10.133 | 37.78
2022-04-09 07:30 | 44660.3125 | 0 | 9.5946 | 37.78
2022-04-09 08:00 | 44660.3333 | 0 | 10.0576 | 37.78
2022-04-09 08:30 | 44660.3542 | 0 | 10.9096 | 37.78
2022-04-09 09:00 | 44660.375 | 0 | 10.4512 | 37.78
2022-04-09 09:30 | 44660.3958 | 0 | 9.1716 | 37.78
2022-04-09 10:00 | 44660.4167 | 0 | 9.1314 | 37.78
2022-04-09 10:30 | 44660.4375 | 0 | 9.6606 | 37.78
2022-04-09 11:00 | 44660.4583 | 0 | 9.6807 | 37.78
2022-04-09 11:30 | 44660.4792 | 0 | 9.0753 | 37.78
2022-04-09 12:00 | 44660.5 | 0 | 9.3317 | 37.78
2022-04-09 12:30 | 44660.5208 | 0 | 8.5477 | 37.78
2022-04-09 13:00 | 44660.5417 | 0 | 9.1719 | 37.78
2022-04-09 13:30 | 44660.5625 | 0 | 9.9876 | 37.78
2022-04-09 14:00 | 44660.5833 | 0 | 11.2908 | 37.78
2022-04-09 14:30 | 44660.6042 | 0 | 10.139 | 37.78
2022-04-09 15:00 | 44660.625 | 0 | 11.2408 | 37.78
2022-04-09 15:30 | 44660.6458 | 0 | 11.9017 | 37.78
2022-04-09 16:00 | 44660.6667 | 0 | 11.8547 | 37.78
2022-04-09 16:30 | 44660.6875 | 0 | 12.0573 | 37.78
2022-04-09 17:00 | 44660.7083 | 0 | 12.1017 | 37.78
2022-04-09 17:30 | 44660.7292 | 0 | 12.491 | 37.78
2022-04-09 18:00 | 44660.75 | 0 | 12.7119 | 37.78
2022-04-09 18:30 | 44660.7708 | 0 | 12.7554 | 37.78
2022-04-09 19:00 | 44660.7917 | 0 | 12.3932 | 37.78
2022-04-09 19:30 | 44660.8125 | 0 | 12.0012 | 37.78
2022-04-09 20:00 | 44660.8333 | 0 | 11.6298 | 37.78
2022-04-09 20:30 | 44660.8542 | 0 | 11.1643 | 37.78
2022-04-09 21:00 | 44660.875 | 0 | 10.748 | 37.78
2022-04-09 21:30 | 44660.8958 | 0 | 10.6138 | 37.78
2022-04-09 22:00 | 44660.9167 | 0 | 10.1975 | 37.78
2022-04-09 22:30 | 44660.9375 | 0 | 9.8094 | 37.78
2022-04-09 23:00 | 44660.9583 | 0 | 9.4 | 37.78
2022-04-09 23:30 | 44660.9792 | 0 | 9.0829 | 37.78
2022-04-10 | 44661 | 0 | 8.6591 | 37.78
2022-04-10 00:30 | 44661.0208 | 0 | 8.3899 | 37.78
2022-04-10 01:00 | 44661.0417 | 0 | 8.2489 | 37.78
2022-04-10 01:30 | 44661.0625 | 0 | 8.0339 | 37.78
2022-04-10 02:00 | 44661.0833 | 0 | 8.0233 | 37.78
2022-04-10 02:30 | 44661.1042 | 0 | 7.8732 | 37.78
2022-04-10 03:00 | 44661.125 | 0 | 7.8039 | 37.78
2022-04-10 03:30 | 44661.1458 | 0 | 7.7769 | 37.78
2022-04-10 04:00 | 44661.1667 | 0 | 7.6213 | 37.78
2022-04-10 04:30 | 44661.1875 | 0 | 7.5755 | 37.78
2022-04-10 05:00 | 44661.2083 | 0 | 7.755 | 37.78
2022-04-10 05:30 | 44661.2292 | 0 | 7.838 | 37.78
2022-04-10 06:00 | 44661.25 | 0 | 8.0151 | 37.78
2022-04-10 06:30 | 44661.2708 | 0 | 7.9735 | 37.78
2022-04-10 07:00 | 44661.2917 | 0 | 8.0207 | 37.78
2022-04-10 07:30 | 44661.3125 | 0 | 7.3494 | 37.78
2022-04-10 08:00 | 44661.3333 | 0 | 7.7499 | 37.78
2022-04-10 08:30 | 44661.3542 | 0 | 7.1185 | 37.78
2022-04-10 09:00 | 44661.375 | 0 | 6.8485 | 37.78
2022-04-10 09:30 | 44661.3958 | 0 | 7.7633 | 37.78
2022-04-10 10:00 | 44661.4167 | 0 | 6.9771 | 37.78
2022-04-10 10:30 | 44661.4375 | 0 | 7.3662 | 37.78
2022-04-10 11:00 | 44661.4583 | 0 | 7.8253 | 37.78
2022-04-10 11:30 | 44661.4792 | 0 | 7.4014 | 37.78
2022-04-10 12:00 | 44661.5 | 0 | 7.7279 | 37.78
2022-04-10 12:30 | 44661.5208 | 0 | 8.5892 | 37.78
2022-04-10 13:00 | 44661.5417 | 0 | 9.8867 | 37.78
2022-04-10 13:30 | 44661.5625 | 0 | 8.8243 | 37.78
2022-04-10 14:00 | 44661.5833 | 0 | 8.9833 | 37.78
2022-04-10 14:30 | 44661.6042 | 0 | 9.2313 | 37.78
2022-04-10 15:00 | 44661.625 | 0 | 10.3794 | 37.78
2022-04-10 15:30 | 44661.6458 | 0 | 10.6184 | 37.78
2022-04-10 16:00 | 44661.6667 | 0 | 11.6404 | 37.78
2022-04-10 16:30 | 44661.6875 | 0 | 12.6912 | 37.78
2022-04-10 17:00 | 44661.7083 | 0 | 13.1695 | 37.78
2022-04-10 17:30 | 44661.7292 | 0 | 13.7255 | 37.78
2022-04-10 18:00 | 44661.75 | 0 | 14.3278 | 37.78
2022-04-10 18:30 | 44661.7708 | 0 | 13.5407 | 37.78
2022-04-10 19:00 | 44661.7917 | 0 | 12.8228 | 37.78
2022-04-10 19:30 | 44661.8125 | 0 | 12.3958 | 37.78
2022-04-10 20:00 | 44661.8333 | 0 | 12.1571 | 37.78
2022-04-10 20:30 | 44661.8542 | 0 | 11.3918 | 37.78
2022-04-10 21:00 | 44661.875 | 0 | 11.0382 | 37.78
2022-04-10 21:30 | 44661.8958 | 0 | 10.7925 | 37.78
2022-04-10 22:00 | 44661.9167 | 0 | 10.3313 | 37.78
2022-04-10 22:30 | 44661.9375 | 0 | 9.6438 | 37.78
2022-04-10 23:00 | 44661.9583 | 0 | 9.2632 | 37.78
2022-04-10 23:30 | 44661.9792 | 0 | 8.8926 | 37.78
2022-04-11 | 44662 | 0 | 8.5913 | 37.78
2022-04-11 00:30 | 44662.0208 | 0 | 8.435 | 37.78
2022-04-11 01:00 | 44662.0417 | 0 | 8.3829 | 37.78
2022-04-11 01:30 | 44662.0625 | 0 | 8.211 | 37.78
2022-04-11 02:00 | 44662.0833 | 0 | 8.1184 | 37.78
2022-04-11 02:30 | 44662.1042 | 0 | 8.4019 | 37.78
2022-04-11 03:00 | 44662.125 | 0 | 8.352 | 37.78
2022-04-11 03:30 | 44662.1458 | 0 | 8.7233 | 37.78
2022-04-11 04:00 | 44662.1667 | 0 | 9.1012 | 37.78
2022-04-11 04:30 | 44662.1875 | 0 | 9.2076 | 37.78
2022-04-11 05:00 | 44662.2083 | 0 | 9.3357 | 37.78
2022-04-11 05:30 | 44662.2292 | 0 | 9.8421 | 37.78
2022-04-11 06:00 | 44662.25 | 0 | 10.5277 | 37.78
2022-04-11 06:30 | 44662.2708 | 0 | 11.1044 | 37.78
2022-04-11 07:00 | 44662.2917 | 0 | 11.3263 | 37.78
2022-04-11 07:30 | 44662.3125 | 0 | 11.1313 | 37.78
2022-04-11 08:00 | 44662.3333 | 0 | 11.1193 | 37.78
2022-04-11 08:30 | 44662.3542 | 0 | 10.8193 | 37.78
2022-04-11 09:00 | 44662.375 | 0 | 10.3741 | 37.78
2022-04-11 09:30 | 44662.3958 | 0 | 10.3393 | 37.78
2022-04-11 10:00 | 44662.4167 | 0 | 10.066 | 37.78
2022-04-11 10:30 | 44662.4375 | 0 | 10.2509 | 37.78
2022-04-11 11:00 | 44662.4583 | 0 | 10.9107 | 37.78
2022-04-11 11:30 | 44662.4792 | 0 | 11.8417 | 37.78
2022-04-11 12:00 | 44662.5 | 0 | 11.0111 | 37.78
2022-04-11 12:30 | 44662.5208 | 0 | 11.5769 | 37.78
2022-04-11 13:00 | 44662.5417 | 0 | 11.8572 | 37.78
2022-04-11 13:30 | 44662.5625 | 0 | 12.8946 | 37.78
2022-04-11 14:00 | 44662.5833 | 0 | 13.0902 | 37.78
2022-04-11 14:30 | 44662.6042 | 0 | 13.4782 | 37.78
2022-04-11 15:00 | 44662.625 | 0 | 14.0929 | 37.78
2022-04-11 15:30 | 44662.6458 | 0 | 14.1093 | 37.78
2022-04-11 16:00 | 44662.6667 | 0 | 14.7605 | 37.78
2022-04-11 16:30 | 44662.6875 | 0 | 15.4608 | 37.78
2022-04-11 17:00 | 44662.7083 | 0 | 15.5833 | 37.78
2022-04-11 17:30 | 44662.7292 | 0 | 15.6126 | 37.78
2022-04-11 18:00 | 44662.75 | 0 | 15.8631 | 37.78
2022-04-11 18:30 | 44662.7708 | 0 | 16.0239 | 37.78
2022-04-11 19:00 | 44662.7917 | 0 | 15.516 | 37.78
2022-04-11 19:30 | 44662.8125 | 0 | 14.8259 | 37.78
2022-04-11 20:00 | 44662.8333 | 0 | 14.6439 | 37.78
2022-04-11 20:30 | 44662.8542 | 0 | 13.8621 | 37.78
2022-04-11 21:00 | 44662.875 | 0 | 13.382 | 37.78
2022-04-11 21:30 | 44662.8958 | 0 | 13.031 | 37.78
2022-04-11 22:00 | 44662.9167 | 0 | 12.4746 | 37.78
2022-04-11 22:30 | 44662.9375 | 0 | 11.598 | 37.78
2022-04-11 23:00 | 44662.9583 | 0 | 11.1035 | 37.78
2022-04-11 23:30 | 44662.9792 | 0 | 10.6453 | 37.78
2022-04-12 | 44663 | 0 | 10.0883 | 37.78
2022-04-12 00:30 | 44663.0208 | 0 | 9.6049 | 37.78
2022-04-12 01:00 | 44663.0417 | 0 | 9.48 | 37.78
2022-04-12 01:30 | 44663.0625 | 0 | 9.2925 | 37.78
2022-04-12 02:00 | 44663.0833 | 0 | 9.1054 | 37.78
2022-04-12 02:30 | 44663.1042 | 0 | 9.2203 | 37.78
2022-04-12 03:00 | 44663.125 | 0 | 8.9964 | 37.78
2022-04-12 03:30 | 44663.1458 | 0 | 8.9409 | 37.78
2022-04-12 04:00 | 44663.1667 | 0 | 9.3203 | 37.78
2022-04-12 04:30 | 44663.1875 | 0 | 9.6643 | 37.78
2022-04-12 05:00 | 44663.2083 | 0 | 10.2596 | 37.78
2022-04-12 05:30 | 44663.2292 | 0 | 10.7095 | 37.78
2022-04-12 06:00 | 44663.25 | 0 | 11.5363 | 37.78
2022-04-12 06:30 | 44663.2708 | 0 | 11.9417 | 37.78
2022-04-12 07:00 | 44663.2917 | 0 | 12.0778 | 37.78
2022-04-12 07:30 | 44663.3125 | 0 | 12.2859 | 37.78
2022-04-12 08:00 | 44663.3333 | 0 | 12.1859 | 37.78
2022-04-12 08:30 | 44663.3542 | 0 | 11.7964 | 37.78
2022-04-12 09:00 | 44663.375 | 0 | 11.6619 | 37.78
2022-04-12 09:30 | 44663.3958 | 0 | 11.5382 | 37.78
2022-04-12 10:00 | 44663.4167 | 0 | 11.6174 | 37.78
2022-04-12 10:30 | 44663.4375 | 0 | 12.3934 | 37.78
2022-04-12 11:00 | 44663.4583 | 0 | 12.1987 | 37.78
2022-04-12 11:30 | 44663.4792 | 0 | 12.6836 | 37.78
2022-04-12 12:00 | 44663.5 | 0 | 13.5741 | 37.78
2022-04-12 12:30 | 44663.5208 | 0 | 13.5046 | 37.78
2022-04-12 13:00 | 44663.5417 | 0 | 14.77 | 37.78
2022-04-12 13:30 | 44663.5625 | 0 | 14.2784 | 37.78
2022-04-12 14:00 | 44663.5833 | 0 | 14.6268 | 37.78
2022-04-12 14:30 | 44663.6042 | 0 | 16.1385 | 37.78
2022-04-12 15:00 | 44663.625 | 0 | 14.519 | 37.78
2022-04-12 15:30 | 44663.6458 | 0 | 14.8042 | 37.78
2022-04-12 16:00 | 44663.6667 | 0 | 15.2643 | 37.78
2022-04-12 16:30 | 44663.6875 | 0 | 15.806 | 37.78
2022-04-12 17:00 | 44663.7083 | 0 | 15.4089 | 37.78
2022-04-12 17:30 | 44663.7292 | 0 | 15.5118 | 37.78
2022-04-12 18:00 | 44663.75 | 0 | 15.6058 | 37.78
2022-04-12 18:30 | 44663.7708 | 0 | 15.5361 | 37.78
2022-04-12 19:00 | 44663.7917 | 0 | 15.2036 | 37.78
2022-04-12 19:30 | 44663.8125 | 0 | 14.7823 | 37.78
2022-04-12 20:00 | 44663.8333 | 0 | 14.3092 | 37.78
2022-04-12 20:30 | 44663.8542 | 0 | 13.7489 | 37.78
2022-04-12 21:00 | 44663.875 | 0 | 13.2212 | 37.78
2022-04-12 21:30 | 44663.8958 | 0 | 12.836 | 37.78
2022-04-12 22:00 | 44663.9167 | 0 | 12.0546 | 37.78
2022-04-12 22:30 | 44663.9375 | 0 | 11.4878 | 37.78
2022-04-12 23:00 | 44663.9583 | 0 | 10.7744 | 37.78
2022-04-12 23:30 | 44663.9792 | 0 | 10.1507 | 37.78
2022-04-13 | 44664 | 0 | 9.678 | 37.78
2022-04-13 00:30 | 44664.0208 | 0 | 9.4086 | 37.78
2022-04-13 01:00 | 44664.0417 | 0 | 8.9769 | 37.78
2022-04-13 01:30 | 44664.0625 | 0 | 8.8124 | 37.78
2022-04-13 02:00 | 44664.0833 | 0 | 8.6309 | 37.78
2022-04-13 02:30 | 44664.1042 | 0 | 8.6627 | 37.78
2022-04-13 03:00 | 44664.125 | 0 | 8.435 | 37.78
2022-04-13 03:30 | 44664.1458 | 0 | 8.4704 | 37.78
2022-04-13 04:00 | 44664.1667 | 0 | 8.8662 | 37.78
2022-04-13 04:30 | 44664.1875 | 0 | 9.0307 | 37.78
2022-04-13 05:00 | 44664.2083 | 0 | 9.6157 | 37.78
2022-04-13 05:30 | 44664.2292 | 0 | 10.2187 | 37.78
2022-04-13 06:00 | 44664.25 | 0 | 10.8327 | 37.78
2022-04-13 06:30 | 44664.2708 | 0 | 11.8226 | 37.78
2022-04-13 07:00 | 44664.2917 | 0 | 12.3567 | 37.78
2022-04-13 07:30 | 44664.3125 | 0 | 11.9538 | 37.78
2022-04-13 08:00 | 44664.3333 | 0 | 11.5143 | 37.78
2022-04-13 08:30 | 44664.3542 | 0 | 11.1904 | 37.78
2022-04-13 09:00 | 44664.375 | 0 | 10.9884 | 37.78
2022-04-13 09:30 | 44664.3958 | 0 | 10.932 | 37.78
2022-04-13 10:00 | 44664.4167 | 0 | 11.3068 | 37.78
2022-04-13 10:30 | 44664.4375 | 0 | 11.3428 | 37.78
2022-04-13 11:00 | 44664.4583 | 0 | 12.2405 | 37.78
2022-04-13 11:30 | 44664.4792 | 0 | 11.3165 | 37.78
2022-04-13 12:00 | 44664.5 | 0 | 12.9126 | 37.78
2022-04-13 12:30 | 44664.5208 | 0 | 13.0292 | 37.78
2022-04-13 13:00 | 44664.5417 | 0 | 13.5433 | 37.78
2022-04-13 13:30 | 44664.5625 | 0 | 12.0832 | 37.78
2022-04-13 14:00 | 44664.5833 | 0 | 13.6373 | 37.78
2022-04-13 14:30 | 44664.6042 | 0 | 13.4803 | 37.78
2022-04-13 15:00 | 44664.625 | 0 | 13.9905 | 37.78
2022-04-13 15:30 | 44664.6458 | 0 | 14.0382 | 37.78
2022-04-13 16:00 | 44664.6667 | 0 | 13.86 | 37.78
2022-04-13 16:30 | 44664.6875 | 0 | 13.9993 | 37.78
2022-04-13 17:00 | 44664.7083 | 0 | 13.9379 | 37.78
2022-04-13 17:30 | 44664.7292 | 0 | 14.1114 | 37.78
2022-04-13 18:00 | 44664.75 | 0 | 14.1636 | 37.78
2022-04-13 18:30 | 44664.7708 | 0 | 14.1996 | 37.78
2022-04-13 19:00 | 44664.7917 | 0 | 13.8887 | 37.78
2022-04-13 19:30 | 44664.8125 | 0 | 13.3872 | 37.78
2022-04-13 20:00 | 44664.8333 | 0 | 13.1496 | 37.78
2022-04-13 20:30 | 44664.8542 | 0 | 12.5942 | 37.78
2022-04-13 21:00 | 44664.875 | 0 | 12.2276 | 37.78
2022-04-13 21:30 | 44664.8958 | 0 | 11.8969 | 37.78
2022-04-13 22:00 | 44664.9167 | 0 | 11.4404 | 37.78
2022-04-13 22:30 | 44664.9375 | 0 | 10.6529 | 37.78
2022-04-13 23:00 | 44664.9583 | 0 | 10.1535 | 37.78
2022-04-13 23:30 | 44664.9792 | 0 | 9.885 | 37.78
2022-04-14 | 44665 | 0 | 9.37 | 37.78
2022-04-14 00:30 | 44665.0208 | 0 | 8.7829 | 37.78
2022-04-14 01:00 | 44665.0417 | 0 | 8.656 | 37.78
2022-04-14 01:30 | 44665.0625 | 0 | 8.4179 | 37.78
2022-04-14 02:00 | 44665.0833 | 0 | 8.3708 | 37.78
2022-04-14 02:30 | 44665.1042 | 0 | 8.2108 | 37.78
2022-04-14 03:00 | 44665.125 | 0 | 8.1537 | 37.78
2022-04-14 03:30 | 44665.1458 | 0 | 8.2938 | 37.78
2022-04-14 04:00 | 44665.1667 | 0 | 8.7287 | 37.78
2022-04-14 04:30 | 44665.1875 | 0 | 8.9519 | 37.78
2022-04-14 05:00 | 44665.2083 | 0 | 9.5299 | 37.78
2022-04-14 05:30 | 44665.2292 | 0 | 10.0001 | 37.78
2022-04-14 06:00 | 44665.25 | 0 | 10.6451 | 37.78
2022-04-14 06:30 | 44665.2708 | 0 | 11.1712 | 37.78
2022-04-14 07:00 | 44665.2917 | 0 | 11.75 | 37.78
2022-04-14 07:30 | 44665.3125 | 0 | 10.964 | 37.78
2022-04-14 08:00 | 44665.3333 | 0 | 10.9112 | 37.78
2022-04-14 08:30 | 44665.3542 | 0 | 10.2954 | 37.78
2022-04-14 09:00 | 44665.375 | 0 | 9.7433 | 37.78
2022-04-14 09:30 | 44665.3958 | 0 | 9.5263 | 37.78
2022-04-14 10:00 | 44665.4167 | 0 | 9.235 | 37.78
2022-04-14 10:30 | 44665.4375 | 0 | 10.2012 | 37.78
2022-04-14 11:00 | 44665.4583 | 0 | 10.6629 | 37.78
2022-04-14 11:30 | 44665.4792 | 0 | 10.6515 | 37.78
2022-04-14 12:00 | 44665.5 | 0 | 10.3282 | 37.78
2022-04-14 12:30 | 44665.5208 | 0 | 10.2502 | 37.78
2022-04-14 13:00 | 44665.5417 | 0 | 9.6605 | 37.78
2022-04-14 13:30 | 44665.5625 | 0 | 9.4697 | 37.78
2022-04-14 14:00 | 44665.5833 | 0 | 10.3674 | 37.78
2022-04-14 14:30 | 44665.6042 | 0 | 11.0399 | 37.78
2022-04-14 15:00 | 44665.625 | 0 | 11.5639 | 37.78
2022-04-14 15:30 | 44665.6458 | 0 | 12.1554 | 37.78
2022-04-14 16:00 | 44665.6667 | 0 | 13.4486 | 37.78
2022-04-14 16:30 | 44665.6875 | 0 | 12.9669 | 37.78
2022-04-14 17:00 | 44665.7083 | 0 | 13.0862 | 37.78
2022-04-14 17:30 | 44665.7292 | 0 | 13.4228 | 37.78
2022-04-14 18:00 | 44665.75 | 0 | 13.5194 | 37.78
2022-04-14 18:30 | 44665.7708 | 0 | 13.4184 | 37.78
2022-04-14 19:00 | 44665.7917 | 0 | 13.131 | 37.78
2022-04-14 19:30 | 44665.8125 | 0 | 12.787 | 37.78
2022-04-14 20:00 | 44665.8333 | 0 | 12.4761 | 37.78
2022-04-14 20:30 | 44665.8542 | 0 | 12.027 | 37.78
2022-04-14 21:00 | 44665.875 | 0 | 11.6928 | 37.78
2022-04-14 21:30 | 44665.8958 | 0 | 11.3653 | 37.78
2022-04-14 22:00 | 44665.9167 | 0 | 10.8993 | 37.78
2022-04-14 22:30 | 44665.9375 | 0 | 10.2221 | 37.78
2022-04-14 23:00 | 44665.9583 | 0 | 9.7222 | 37.78
2022-04-14 23:30 | 44665.9792 | 0 | 9.4019 | 37.78
2022-04-15 | 44666 | 0 | 8.8126 | 37.78
2022-04-15 00:30 | 44666.0208 | 0 | 8.4801 | 37.78
2022-04-15 01:00 | 44666.0417 | 0 | 8.3329 | 37.78
2022-04-15 01:30 | 44666.0625 | 0 | 8.1854 | 37.78
2022-04-15 02:00 | 44666.0833 | 0 | 8.0949 | 37.78
2022-04-15 02:30 | 44666.1042 | 0 | 7.9076 | 37.78
2022-04-15 03:00 | 44666.125 | 0 | 7.7976 | 37.78
2022-04-15 03:30 | 44666.1458 | 0 | 7.7025 | 37.78
2022-04-15 04:00 | 44666.1667 | 0 | 7.7918 | 37.78
2022-04-15 04:30 | 44666.1875 | 0 | 7.8169 | 37.78
2022-04-15 05:00 | 44666.2083 | 0 | 7.8274 | 37.78
2022-04-15 05:30 | 44666.2292 | 0 | 8.1175 | 37.78
2022-04-15 06:00 | 44666.25 | 0 | 8.1865 | 37.78
2022-04-15 06:30 | 44666.2708 | 0 | 8.1789 | 37.78
2022-04-15 07:00 | 44666.2917 | 0 | 8.8007 | 37.78
2022-04-15 07:30 | 44666.3125 | 0 | 7.7389 | 37.78
2022-04-15 08:00 | 44666.3333 | 0 | 7.4689 | 37.78
2022-04-15 08:30 | 44666.3542 | 0 | 7.1835 | 37.78
2022-04-15 09:00 | 44666.375 | 0 | 6.9792 | 37.78
2022-04-15 09:30 | 44666.3958 | 0 | 6.7526 | 37.78
2022-04-15 10:00 | 44666.4167 | 0 | 7.1648 | 37.78
2022-04-15 10:30 | 44666.4375 | 0 | 7.1433 | 37.78
2022-04-15 11:00 | 44666.4583 | 0 | 7.5498 | 37.78
2022-04-15 11:30 | 44666.4792 | 0 | 7.1243 | 37.78
2022-04-15 12:00 | 44666.5 | 0 | 6.2753 | 37.78
2022-04-15 12:30 | 44666.5208 | 0 | 7.2673 | 37.78
2022-04-15 13:00 | 44666.5417 | 0 | 6.4675 | 37.78
2022-04-15 13:30 | 44666.5625 | 0 | 8.6198 | 37.78
2022-04-15 14:00 | 44666.5833 | 0 | 9.3797 | 37.78
2022-04-15 14:30 | 44666.6042 | 0 | 8.8717 | 37.78
2022-04-15 15:00 | 44666.625 | 0 | 8.977 | 37.78
2022-04-15 15:30 | 44666.6458 | 0 | 9.8497 | 37.78
2022-04-15 16:00 | 44666.6667 | 0 | 10.1231 | 37.78
2022-04-15 16:30 | 44666.6875 | 0 | 10.9306 | 37.78
2022-04-15 17:00 | 44666.7083 | 0 | 11.0586 | 37.78
2022-04-15 17:30 | 44666.7292 | 0 | 11.4098 | 37.78
2022-04-15 18:00 | 44666.75 | 0 | 11.5102 | 37.78
2022-04-15 18:30 | 44666.7708 | 0 | 11.4434 | 37.78
2022-04-15 19:00 | 44666.7917 | 0 | 10.9012 | 37.78
2022-04-15 19:30 | 44666.8125 | 0 | 10.4928 | 37.78
2022-04-15 20:00 | 44666.8333 | 0 | 10.3927 | 37.78
2022-04-15 20:30 | 44666.8542 | 0 | 9.9286 | 37.78
2022-04-15 21:00 | 44666.875 | 0 | 9.7864 | 37.78
2022-04-15 21:30 | 44666.8958 | 0 | 9.4223 | 37.78
2022-04-15 22:00 | 44666.9167 | 0 | 9.1527 | 37.78
2022-04-15 22:30 | 44666.9375 | 0 | 8.7669 | 37.78
2022-04-15 23:00 | 44666.9583 | 0 | 8.4595 | 37.78
2022-04-15 23:30 | 44666.9792 | 0 | 8.0772 | 37.78
2022-04-16 | 44667 | 0 | 7.7014 | 37.78
2022-04-16 00:30 | 44667.0208 | 0 | 7.4065 | 37.78
2022-04-16 01:00 | 44667.0417 | 0 | 7.3407 | 37.78
2022-04-16 01:30 | 44667.0625 | 0 | 7.1318 | 37.78
2022-04-16 02:00 | 44667.0833 | 0 | 7.1469 | 37.78
2022-04-16 02:30 | 44667.1042 | 0 | 7.0963 | 37.78
2022-04-16 03:00 | 44667.125 | 0 | 7.0634 | 37.78
2022-04-16 03:30 | 44667.1458 | 0 | 7.0725 | 37.78
2022-04-16 04:00 | 44667.1667 | 0 | 7.1735 | 37.78
2022-04-16 04:30 | 44667.1875 | 0 | 7.1743 | 37.78
2022-04-16 05:00 | 44667.2083 | 0 | 7.3228 | 37.78
2022-04-16 05:30 | 44667.2292 | 0 | 7.4905 | 37.78
2022-04-16 06:00 | 44667.25 | 0 | 7.782 | 37.78
2022-04-16 06:30 | 44667.2708 | 0 | 7.8627 | 37.78
2022-04-16 07:00 | 44667.2917 | 0 | 7.9493 | 37.78
2022-04-16 07:30 | 44667.3125 | 0 | 8.0215 | 37.78
2022-04-16 08:00 | 44667.3333 | 0 | 8.0563 | 37.78
2022-04-16 08:30 | 44667.3542 | 0 | 6.8016 | 37.78
2022-04-16 09:00 | 44667.375 | 0 | 6.0637 | 37.78
2022-04-16 09:30 | 44667.3958 | 0 | 5.743 | 37.78
2022-04-16 10:00 | 44667.4167 | 0 | 5.9098 | 37.78
2022-04-16 10:30 | 44667.4375 | 0 | 5.5131 | 37.78
2022-04-16 11:00 | 44667.4583 | 0 | 6.5127 | 37.78
2022-04-16 11:30 | 44667.4792 | 0 | 7.5303 | 37.78
2022-04-16 12:00 | 44667.5 | 0 | 6.7533 | 37.78
2022-04-16 12:30 | 44667.5208 | 0 | 6.3899 | 37.78
2022-04-16 13:00 | 44667.5417 | 0 | 7.3633 | 37.78
2022-04-16 13:30 | 44667.5625 | 0 | 7.623 | 37.78
2022-04-16 14:00 | 44667.5833 | 0 | 8.0108 | 37.78
2022-04-16 14:30 | 44667.6042 | 0 | 8.3381 | 37.78
2022-04-16 15:00 | 44667.625 | 0 | 8.5062 | 37.78
2022-04-16 15:30 | 44667.6458 | 0 | 9.1607 | 37.78
2022-04-16 16:00 | 44667.6667 | 0 | 10.0479 | 37.78
2022-04-16 16:30 | 44667.6875 | 0 | 10.4396 | 37.78
2022-04-16 17:00 | 44667.7083 | 0 | 10.7531 | 37.78
2022-04-16 17:30 | 44667.7292 | 0 | 11.1763 | 37.78
2022-04-16 18:00 | 44667.75 | 0 | 11.0828 | 37.78
2022-04-16 18:30 | 44667.7708 | 0 | 10.9782 | 37.78
2022-04-16 19:00 | 44667.7917 | 0 | 10.676 | 37.78
2022-04-16 19:30 | 44667.8125 | 0 | 10.5277 | 37.78
2022-04-16 20:00 | 44667.8333 | 0 | 10.3058 | 37.78
2022-04-16 20:30 | 44667.8542 | 0 | 9.9704 | 37.78
2022-04-16 21:00 | 44667.875 | 0 | 9.7481 | 37.78
2022-04-16 21:30 | 44667.8958 | 0 | 9.5286 | 37.78
2022-04-16 22:00 | 44667.9167 | 0 | 9.3004 | 37.78
2022-04-16 22:30 | 44667.9375 | 0 | 8.7099 | 37.78
2022-04-16 23:00 | 44667.9583 | 0 | 8.4597 | 37.78
2022-04-16 23:30 | 44667.9792 | 0 | 8.1263 | 37.78
2022-04-17 | 44668 | 0 | 7.6881 | 37.78
2022-04-17 00:30 | 44668.0208 | 0 | 7.421 | 37.78
2022-04-17 01:00 | 44668.0417 | 0 | 7.4753 | 37.78
2022-04-17 01:30 | 44668.0625 | 0 | 7.193 | 37.78
2022-04-17 02:00 | 44668.0833 | 0 | 7.1911 | 37.78
2022-04-17 02:30 | 44668.1042 | 0 | 6.9669 | 37.78
2022-04-17 03:00 | 44668.125 | 0 | 7.0587 | 37.78
2022-04-17 03:30 | 44668.1458 | 0 | 7.0857 | 37.78
2022-04-17 04:00 | 44668.1667 | 0 | 7.0297 | 37.78
2022-04-17 04:30 | 44668.1875 | 0 | 6.9725 | 37.78
2022-04-17 05:00 | 44668.2083 | 0 | 7.0713 | 37.78
2022-04-17 05:30 | 44668.2292 | 0 | 7.2166 | 37.78
2022-04-17 06:00 | 44668.25 | 0 | 7.4882 | 37.78
2022-04-17 06:30 | 44668.2708 | 0 | 7.5426 | 37.78
2022-04-17 07:00 | 44668.2917 | 0 | 7.2065 | 37.78
2022-04-17 07:30 | 44668.3125 | 0 | 7.2303 | 37.78
2022-04-17 08:00 | 44668.3333 | 0 | 7.8994 | 37.78
2022-04-17 08:30 | 44668.3542 | 0 | 7.6706 | 37.78
2022-04-17 09:00 | 44668.375 | 0 | 6.3806 | 37.78
2022-04-17 09:30 | 44668.3958 | 0 | 6.7779 | 37.78
2022-04-17 10:00 | 44668.4167 | 0 | 5.9217 | 37.78
2022-04-17 10:30 | 44668.4375 | 0 | 6.8574 | 37.78
2022-04-17 11:00 | 44668.4583 | 0 | 6.3944 | 37.78
2022-04-17 11:30 | 44668.4792 | 0 | 5.3212 | 37.78
2022-04-17 12:00 | 44668.5 | 0 | 7.6756 | 37.78
2022-04-17 12:30 | 44668.5208 | 0 | 7.3709 | 37.78
2022-04-17 13:00 | 44668.5417 | 0 | 7.5738 | 37.78
2022-04-17 13:30 | 44668.5625 | 0 | 6.2679 | 37.78
2022-04-17 14:00 | 44668.5833 | 0 | 7.4149 | 37.78
2022-04-17 14:30 | 44668.6042 | 0 | 8.1587 | 37.78
2022-04-17 15:00 | 44668.625 | 0 | 9.6948 | 37.78
2022-04-17 15:30 | 44668.6458 | 0 | 9.3769 | 37.78
2022-04-17 16:00 | 44668.6667 | 0 | 9.4937 | 37.78
2022-04-17 16:30 | 44668.6875 | 0 | 9.7733 | 37.78
2022-04-17 17:00 | 44668.7083 | 0 | 10.3467 | 37.78
2022-04-17 17:30 | 44668.7292 | 0 | 10.6756 | 37.78
2022-04-17 18:00 | 44668.75 | 0 | 10.8897 | 37.78
2022-04-17 18:30 | 44668.7708 | 0 | 10.8716 | 37.78
2022-04-17 19:00 | 44668.7917 | 0 | 10.6878 | 37.78
2022-04-17 19:30 | 44668.8125 | 0 | 10.4087 | 37.78
2022-04-17 20:00 | 44668.8333 | 0 | 10.2174 | 37.78
2022-04-17 20:30 | 44668.8542 | 0 | 9.9292 | 37.78
2022-04-17 21:00 | 44668.875 | 0 | 9.606 | 37.78
2022-04-17 21:30 | 44668.8958 | 0 | 9.476 | 37.78
2022-04-17 22:00 | 44668.9167 | 0 | 9.098 | 37.78
2022-04-17 22:30 | 44668.9375 | 0 | 8.5541 | 37.78
2022-04-17 23:00 | 44668.9583 | 0 | 8.4001 | 37.78
2022-04-17 23:30 | 44668.9792 | 0 | 8.0585 | 37.78
2022-04-18 | 44669 | 0 | 7.6893 | 37.78
2022-04-18 00:30 | 44669.0208 | 0 | 7.5152 | 37.78
2022-04-18 01:00 | 44669.0417 | 0 | 7.5021 | 37.78
2022-04-18 01:30 | 44669.0625 | 0 | 7.2623 | 37.78
2022-04-18 02:00 | 44669.0833 | 0 | 7.2146 | 37.78
2022-04-18 02:30 | 44669.1042 | 0 | 7.3172 | 37.78
2022-04-18 03:00 | 44669.125 | 0 | 7.0697 | 37.78
2022-04-18 03:30 | 44669.1458 | 0 | 7.0771 | 37.78
2022-04-18 04:00 | 44669.1667 | 0 | 7.2025 | 37.78
2022-04-18 04:30 | 44669.1875 | 0 | 7.3256 | 37.78
2022-04-18 05:00 | 44669.2083 | 0 | 7.4835 | 37.78
2022-04-18 05:30 | 44669.2292 | 0 | 7.7891 | 37.78
2022-04-18 06:00 | 44669.25 | 0 | 8.0437 | 37.78
2022-04-18 06:30 | 44669.2708 | 0 | 8.2628 | 37.78
2022-04-18 07:00 | 44669.2917 | 0 | 8.3512 | 37.78
2022-04-18 07:30 | 44669.3125 | 0 | 8.2626 | 37.78
2022-04-18 08:00 | 44669.3333 | 0 | 8.6823 | 37.78
2022-04-18 08:30 | 44669.3542 | 0 | 7.4135 | 37.78
2022-04-18 09:00 | 44669.375 | 0 | 7.3642 | 37.78
2022-04-18 09:30 | 44669.3958 | 0 | 7.9417 | 37.78
2022-04-18 10:00 | 44669.4167 | 0 | 7.728 | 37.78
2022-04-18 10:30 | 44669.4375 | 0 | 6.875 | 37.78
2022-04-18 11:00 | 44669.4583 | 0 | 7.4283 | 37.78
2022-04-18 11:30 | 44669.4792 | 0 | 6.9829 | 37.78
2022-04-18 12:00 | 44669.5 | 0 | 8.8276 | 37.78
2022-04-18 12:30 | 44669.5208 | 0 | 7.1496 | 37.78
2022-04-18 13:00 | 44669.5417 | 0 | 9.1321 | 37.78
2022-04-18 13:30 | 44669.5625 | 0 | 8.3699 | 37.78
2022-04-18 14:00 | 44669.5833 | 0 | 9.995 | 37.78
2022-04-18 14:30 | 44669.6042 | 0 | 9.9446 | 37.78
2022-04-18 15:00 | 44669.625 | 0 | 8.9294 | 37.78
2022-04-18 15:30 | 44669.6458 | 0 | 10.5802 | 37.78
2022-04-18 16:00 | 44669.6667 | 0 | 10.9347 | 37.78
2022-04-18 16:30 | 44669.6875 | 0 | 11.5524 | 37.78
2022-04-18 17:00 | 44669.7083 | 0 | 12.2761 | 37.78
2022-04-18 17:30 | 44669.7292 | 0 | 12.6452 | 37.78
2022-04-18 18:00 | 44669.75 | 0 | 12.8318 | 37.78
2022-04-18 18:30 | 44669.7708 | 0 | 12.8957 | 37.78
2022-04-18 19:00 | 44669.7917 | 0 | 12.5434 | 37.78
2022-04-18 19:30 | 44669.8125 | 0 | 11.9607 | 37.78
2022-04-18 20:00 | 44669.8333 | 0 | 11.5332 | 37.78
2022-04-18 20:30 | 44669.8542 | 0 | 11.0526 | 37.78
2022-04-18 21:00 | 44669.875 | 0 | 10.6054 | 37.78
2022-04-18 21:30 | 44669.8958 | 0 | 10.1856 | 37.78
2022-04-18 22:00 | 44669.9167 | 0 | 9.7437 | 37.78
2022-04-18 22:30 | 44669.9375 | 0 | 8.9737 | 37.78
2022-04-18 23:00 | 44669.9583 | 0 | 8.5109 | 37.78
2022-04-18 23:30 | 44669.9792 | 0 | 8.2505 | 37.78
2022-04-19 | 44670 | 0 | 7.81 | 37.78
2022-04-19 00:30 | 44670.0208 | 0 | 7.6755 | 37.78
2022-04-19 01:00 | 44670.0417 | 0 | 7.611 | 37.78
2022-04-19 01:30 | 44670.0625 | 0 | 7.4787 | 37.78
2022-04-19 02:00 | 44670.0833 | 0 | 7.4728 | 37.78
2022-04-19 02:30 | 44670.1042 | 0 | 7.4505 | 37.78
2022-04-19 03:00 | 44670.125 | 0 | 7.501 | 37.78
2022-04-19 03:30 | 44670.1458 | 0 | 7.6152 | 37.78
2022-04-19 04:00 | 44670.1667 | 0 | 7.8841 | 37.78
2022-04-19 04:30 | 44670.1875 | 0 | 8.3314 | 37.78
2022-04-19 05:00 | 44670.2083 | 0 | 8.8495 | 37.78
2022-04-19 05:30 | 44670.2292 | 0 | 9.4941 | 37.78
2022-04-19 06:00 | 44670.25 | 0 | 10.5172 | 37.78
2022-04-19 06:30 | 44670.2708 | 0 | 11.2896 | 37.78
2022-04-19 07:00 | 44670.2917 | 0 | 11.4009 | 37.78
2022-04-19 07:30 | 44670.3125 | 0 | 10.9412 | 37.78
2022-04-19 08:00 | 44670.3333 | 0 | 10.4555 | 37.78
2022-04-19 08:30 | 44670.3542 | 0 | 9.9778 | 37.78
2022-04-19 09:00 | 44670.375 | 0 | 9.7628 | 37.78
2022-04-19 09:30 | 44670.3958 | 0 | 9.7198 | 37.78
2022-04-19 10:00 | 44670.4167 | 0 | 9.4842 | 37.78
2022-04-19 10:30 | 44670.4375 | 0 | 9.3143 | 37.78
2022-04-19 11:00 | 44670.4583 | 0 | 9.3397 | 37.78
2022-04-19 11:30 | 44670.4792 | 0 | 10.1383 | 37.78
2022-04-19 12:00 | 44670.5 | 0 | 10.3731 | 37.78
2022-04-19 12:30 | 44670.5208 | 0 | 10.5893 | 37.78
2022-04-19 13:00 | 44670.5417 | 0 | 11.0868 | 37.78
2022-04-19 13:30 | 44670.5625 | 0 | 11.4576 | 37.78
2022-04-19 14:00 | 44670.5833 | 0 | 11.8356 | 37.78
2022-04-19 14:30 | 44670.6042 | 0 | 11.3354 | 37.78
2022-04-19 15:00 | 44670.625 | 0 | 11.9628 | 37.78
2022-04-19 15:30 | 44670.6458 | 0 | 12.7086 | 37.78
2022-04-19 16:00 | 44670.6667 | 0 | 13.2892 | 37.78
2022-04-19 16:30 | 44670.6875 | 0 | 14.1884 | 37.78
2022-04-19 17:00 | 44670.7083 | 0 | 14.0049 | 37.78
2022-04-19 17:30 | 44670.7292 | 0 | 14.5855 | 37.78
2022-04-19 18:00 | 44670.75 | 0 | 14.7568 | 37.78
2022-04-19 18:30 | 44670.7708 | 0 | 14.7601 | 37.78
2022-04-19 19:00 | 44670.7917 | 0 | 14.1126 | 37.78
2022-04-19 19:30 | 44670.8125 | 0 | 13.8039 | 37.78
2022-04-19 20:00 | 44670.8333 | 0 | 13.562 | 37.78
2022-04-19 20:30 | 44670.8542 | 0 | 12.9926 | 37.78
2022-04-19 21:00 | 44670.875 | 0 | 12.4145 | 37.78
2022-04-19 21:30 | 44670.8958 | 0 | 11.952 | 37.78
2022-04-19 22:00 | 44670.9167 | 0 | 11.4463 | 37.78
2022-04-19 22:30 | 44670.9375 | 0 | 10.5655 | 37.78
2022-04-19 23:00 | 44670.9583 | 0 | 10.1761 | 37.78
2022-04-19 23:30 | 44670.9792 | 0 | 9.7849 | 37.78
2022-04-20 | 44671 | 0 | 9.2552 | 37.78
2022-04-20 00:30 | 44671.0208 | 0 | 8.9059 | 37.78
2022-04-20 01:00 | 44671.0417 | 0 | 8.7525 | 37.78
2022-04-20 01:30 | 44671.0625 | 0 | 8.5732 | 37.78
2022-04-20 02:00 | 44671.0833 | 0 | 8.472 | 37.78
2022-04-20 02:30 | 44671.1042 | 0 | 8.358 | 37.78
2022-04-20 03:00 | 44671.125 | 0 | 8.3387 | 37.78
2022-04-20 03:30 | 44671.1458 | 0 | 8.3466 | 37.78
2022-04-20 04:00 | 44671.1667 | 0 | 8.5892 | 37.78
2022-04-20 04:30 | 44671.1875 | 0 | 8.8651 | 37.78
2022-04-20 05:00 | 44671.2083 | 0 | 9.2148 | 37.78
2022-04-20 05:30 | 44671.2292 | 0 | 10.0417 | 37.78
2022-04-20 06:00 | 44671.25 | 0 | 10.848 | 37.78
2022-04-20 06:30 | 44671.2708 | 0 | 11.5419 | 37.78
2022-04-20 07:00 | 44671.2917 | 0 | 11.9621 | 37.78
2022-04-20 07:30 | 44671.3125 | 0 | 11.7217 | 37.78
2022-04-20 08:00 | 44671.3333 | 0 | 11.4951 | 37.78
2022-04-20 08:30 | 44671.3542 | 0 | 11.1334 | 37.78
2022-04-20 09:00 | 44671.375 | 0 | 10.9453 | 37.78
2022-04-20 09:30 | 44671.3958 | 0 | 10.6626 | 37.78
2022-04-20 10:00 | 44671.4167 | 0 | 10.5242 | 37.78
2022-04-20 10:30 | 44671.4375 | 0 | 10.8001 | 37.78
2022-04-20 11:00 | 44671.4583 | 0 | 10.6997 | 37.78
2022-04-20 11:30 | 44671.4792 | 0 | 10.8878 | 37.78
2022-04-20 12:00 | 44671.5 | 0 | 10.8688 | 37.78
2022-04-20 12:30 | 44671.5208 | 0 | 11.1486 | 37.78
2022-04-20 13:00 | 44671.5417 | 0 | 11.8616 | 37.78
2022-04-20 13:30 | 44671.5625 | 0 | 12.5316 | 37.78
2022-04-20 14:00 | 44671.5833 | 0 | 13.0089 | 37.78
2022-04-20 14:30 | 44671.6042 | 0 | 13.957 | 37.78
2022-04-20 15:00 | 44671.625 | 0 | 14.5292 | 37.78
2022-04-20 15:30 | 44671.6458 | 0 | 15.1639 | 37.78
2022-04-20 16:00 | 44671.6667 | 0 | 15.8782 | 37.78
2022-04-20 16:30 | 44671.6875 | 0 | 16.2939 | 37.78
2022-04-20 17:00 | 44671.7083 | 0 | 16.3349 | 37.78
2022-04-20 17:30 | 44671.7292 | 0 | 16.5655 | 37.78
2022-04-20 18:00 | 44671.75 | 0 | 16.6492 | 37.78
2022-04-20 18:30 | 44671.7708 | 0 | 16.9121 | 37.78
2022-04-20 19:00 | 44671.7917 | 0 | 16.4888 | 37.78
2022-04-20 19:30 | 44671.8125 | 0 | 16.0122 | 37.78
2022-04-20 20:00 | 44671.8333 | 0 | 15.6512 | 37.78
2022-04-20 20:30 | 44671.8542 | 0 | 14.7728 | 37.78
2022-04-20 21:00 | 44671.875 | 0 | 14.1766 | 37.78
2022-04-20 21:30 | 44671.8958 | 0 | 13.4004 | 37.78
2022-04-20 22:00 | 44671.9167 | 0 | 12.7894 | 37.78
2022-04-20 22:30 | 44671.9375 | 0 | 11.6145 | 37.78
2022-04-20 23:00 | 44671.9583 | 0 | 11.0758 | 37.78
2022-04-20 23:30 | 44671.9792 | 0 | 10.4657 | 37.78
2022-04-21 | 44672 | 0 | 9.7929 | 37.78
2022-04-21 00:30 | 44672.0208 | 0 | 9.4023 | 37.78
2022-04-21 01:00 | 44672.0417 | 0 | 9.1743 | 37.78
2022-04-21 01:30 | 44672.0625 | 0 | 9.0068 | 37.78
2022-04-21 02:00 | 44672.0833 | 0 | 8.8868 | 37.78
2022-04-21 02:30 | 44672.1042 | 0 | 8.7951 | 37.78
2022-04-21 03:00 | 44672.125 | 0 | 8.6572 | 37.78
2022-04-21 03:30 | 44672.1458 | 0 | 8.5906 | 37.78
2022-04-21 04:00 | 44672.1667 | 0 | 8.8182 | 37.78
2022-04-21 04:30 | 44672.1875 | 0 | 9.1601 | 37.78
2022-04-21 05:00 | 44672.2083 | 0 | 9.7419 | 37.78
2022-04-21 05:30 | 44672.2292 | 0 | 10.3275 | 37.78
2022-04-21 06:00 | 44672.25 | 0 | 11.1565 | 37.78
2022-04-21 06:30 | 44672.2708 | 0 | 11.7452 | 37.78
2022-04-21 07:00 | 44672.2917 | 0 | 12.1576 | 37.78
2022-04-21 07:30 | 44672.3125 | 0 | 11.6075 | 37.78
2022-04-21 08:00 | 44672.3333 | 0 | 11.4266 | 37.78
2022-04-21 08:30 | 44672.3542 | 0 | 11.2234 | 37.78
2022-04-21 09:00 | 44672.375 | 0 | 10.8615 | 37.78
2022-04-21 09:30 | 44672.3958 | 0 | 12.3315 | 37.78
2022-04-21 10:00 | 44672.4167 | 0 | 11.4768 | 37.78
2022-04-21 10:30 | 44672.4375 | 0 | 10.9697 | 37.78
2022-04-21 11:00 | 44672.4583 | 0 | 10.334 | 37.78
2022-04-21 11:30 | 44672.4792 | 0 | 11.5176 | 37.78
2022-04-21 12:00 | 44672.5 | 0 | 13.2864 | 37.78
2022-04-21 12:30 | 44672.5208 | 0 | 13.245 | 37.78
2022-04-21 13:00 | 44672.5417 | 0 | 12.3469 | 37.78
2022-04-21 13:30 | 44672.5625 | 0 | 13.6037 | 37.78
2022-04-21 14:00 | 44672.5833 | 0 | 13.4989 | 37.78
2022-04-21 14:30 | 44672.6042 | 0 | 13.6799 | 37.78
2022-04-21 15:00 | 44672.625 | 0 | 13.8356 | 37.78
2022-04-21 15:30 | 44672.6458 | 0 | 13.4255 | 37.78
2022-04-21 16:00 | 44672.6667 | 0 | 13.9502 | 37.78
2022-04-21 16:30 | 44672.6875 | 0 | 14.3373 | 37.78
2022-04-21 17:00 | 44672.7083 | 0 | 14.5072 | 37.78
2022-04-21 17:30 | 44672.7292 | 0 | 14.7447 | 37.78
2022-04-21 18:00 | 44672.75 | 0 | 14.8563 | 37.78
2022-04-21 18:30 | 44672.7708 | 0 | 14.6902 | 37.78
2022-04-21 19:00 | 44672.7917 | 0 | 14.3856 | 37.78
2022-04-21 19:30 | 44672.8125 | 0 | 14.1125 | 37.78
2022-04-21 20:00 | 44672.8333 | 0 | 13.6257 | 37.78
2022-04-21 20:30 | 44672.8542 | 0 | 13.2631 | 37.78
2022-04-21 21:00 | 44672.875 | 0 | 12.9316 | 37.78
2022-04-21 21:30 | 44672.8958 | 0 | 12.5705 | 37.78
2022-04-21 22:00 | 44672.9167 | 0 | 11.8853 | 37.78
2022-04-21 22:30 | 44672.9375 | 0 | 10.9036 | 37.78
2022-04-21 23:00 | 44672.9583 | 0 | 10.4123 | 37.78
2022-04-21 23:30 | 44672.9792 | 0 | 10.0095 | 37.78
2022-04-22 | 44673 | 0 | 9.3898 | 37.78
2022-04-22 00:30 | 44673.0208 | 0 | 9.0055 | 37.78
2022-04-22 01:00 | 44673.0417 | 0 | 8.7633 | 37.78
2022-04-22 01:30 | 44673.0625 | 0 | 8.5478 | 37.78
2022-04-22 02:00 | 44673.0833 | 0 | 8.5001 | 37.78
2022-04-22 02:30 | 44673.1042 | 0 | 8.5825 | 37.78
2022-04-22 03:00 | 44673.125 | 0 | 8.5667 | 37.78
2022-04-22 03:30 | 44673.1458 | 0 | 8.4647 | 37.78
2022-04-22 04:00 | 44673.1667 | 0 | 8.851 | 37.78
2022-04-22 04:30 | 44673.1875 | 0 | 8.9468 | 37.78
2022-04-22 05:00 | 44673.2083 | 0 | 9.6552 | 37.78
2022-04-22 05:30 | 44673.2292 | 0 | 10.066 | 37.78
2022-04-22 06:00 | 44673.25 | 0 | 10.9354 | 37.78
2022-04-22 06:30 | 44673.2708 | 0 | 11.9135 | 37.78
2022-04-22 07:00 | 44673.2917 | 0 | 12.6135 | 37.78
2022-04-22 07:30 | 44673.3125 | 0 | 13.0121 | 37.78
2022-04-22 08:00 | 44673.3333 | 0 | 12.8861 | 37.78
2022-04-22 08:30 | 44673.3542 | 0 | 13.224 | 37.78
2022-04-22 09:00 | 44673.375 | 0 | 12.5696 | 37.78
2022-04-22 09:30 | 44673.3958 | 0 | 10.8607 | 37.78
2022-04-22 10:00 | 44673.4167 | 0 | 11.2279 | 37.78
2022-04-22 10:30 | 44673.4375 | 0 | 11.6888 | 37.78
2022-04-22 11:00 | 44673.4583 | 0 | 10.9886 | 37.78
2022-04-22 11:30 | 44673.4792 | 0 | 9.9444 | 37.78
2022-04-22 12:00 | 44673.5 | 0 | 9.8542 | 37.78
2022-04-22 12:30 | 44673.5208 | 0 | 10.8 | 37.78
2022-04-22 13:00 | 44673.5417 | 0 | 11.4874 | 37.78
2022-04-22 13:30 | 44673.5625 | 0 | 10.547 | 37.78
2022-04-22 14:00 | 44673.5833 | 0 | 11.3869 | 37.78
2022-04-22 14:30 | 44673.6042 | 0 | 11.8077 | 37.78
2022-04-22 15:00 | 44673.625 | 0 | 12.216 | 37.78
2022-04-22 15:30 | 44673.6458 | 0 | 12.886 | 37.78
2022-04-22 16:00 | 44673.6667 | 0 | 13.323 | 37.78
2022-04-22 16:30 | 44673.6875 | 0 | 13.5861 | 37.78
2022-04-22 17:00 | 44673.7083 | 0 | 13.6657 | 37.78
2022-04-22 17:30 | 44673.7292 | 0 | 14.0229 | 37.78
2022-04-22 18:00 | 44673.75 | 0 | 13.9402 | 37.78
2022-04-22 18:30 | 44673.7708 | 0 | 14.0237 | 37.78
2022-04-22 19:00 | 44673.7917 | 0 | 13.6368 | 37.78
2022-04-22 19:30 | 44673.8125 | 0 | 13.2491 | 37.78
2022-04-22 20:00 | 44673.8333 | 0 | 13.0469 | 37.78
2022-04-22 20:30 | 44673.8542 | 0 | 12.6458 | 37.78
2022-04-22 21:00 | 44673.875 | 0 | 12.3576 | 37.78
2022-04-22 21:30 | 44673.8958 | 0 | 12.0534 | 37.78
2022-04-22 22:00 | 44673.9167 | 0 | 11.7073 | 37.78
2022-04-22 22:30 | 44673.9375 | 0 | 11.0186 | 37.78
2022-04-22 23:00 | 44673.9583 | 0 | 10.4355 | 37.78
2022-04-22 23:30 | 44673.9792 | 0 | 9.859 | 37.78
2022-04-23 | 44674 | 0 | 9.2032 | 37.78
2022-04-23 00:30 | 44674.0208 | 0 | 8.9142 | 37.78
2022-04-23 01:00 | 44674.0417 | 0 | 8.744 | 37.78
2022-04-23 01:30 | 44674.0625 | 0 | 8.6254 | 37.78
2022-04-23 02:00 | 44674.0833 | 0 | 8.4527 | 37.78
2022-04-23 02:30 | 44674.1042 | 0 | 8.3696 | 37.78
2022-04-23 03:00 | 44674.125 | 0 | 8.3504 | 37.78
2022-04-23 03:30 | 44674.1458 | 0 | 8.2459 | 37.78
2022-04-23 04:00 | 44674.1667 | 0 | 8.3431 | 37.78
2022-04-23 04:30 | 44674.1875 | 0 | 8.492 | 37.78
2022-04-23 05:00 | 44674.2083 | 0 | 8.6239 | 37.78
2022-04-23 05:30 | 44674.2292 | 0 | 8.8028 | 37.78
2022-04-23 06:00 | 44674.25 | 0 | 9.3046 | 37.78
2022-04-23 06:30 | 44674.2708 | 0 | 9.3565 | 37.78
2022-04-23 07:00 | 44674.2917 | 0 | 9.2508 | 37.78
2022-04-23 07:30 | 44674.3125 | 0 | 9.0308 | 37.78
2022-04-23 08:00 | 44674.3333 | 0 | 9.435 | 37.78
2022-04-23 08:30 | 44674.3542 | 0 | 10.0102 | 37.78
2022-04-23 09:00 | 44674.375 | 0 | 8.6102 | 37.78
2022-04-23 09:30 | 44674.3958 | 0 | 9.5064 | 37.78
2022-04-23 10:00 | 44674.4167 | 0 | 7.1907 | 37.78
2022-04-23 10:30 | 44674.4375 | 0 | 9.3486 | 37.78
2022-04-23 11:00 | 44674.4583 | 0 | 8.7967 | 37.78
2022-04-23 11:30 | 44674.4792 | 0 | 8.2469 | 37.78
2022-04-23 12:00 | 44674.5 | 0 | 9.1735 | 37.78
2022-04-23 12:30 | 44674.5208 | 0 | 8.7186 | 37.78
2022-04-23 13:00 | 44674.5417 | 0 | 9.1184 | 37.78
2022-04-23 13:30 | 44674.5625 | 0 | 7.7716 | 37.78
2022-04-23 14:00 | 44674.5833 | 0 | 8.8969 | 37.78
2022-04-23 14:30 | 44674.6042 | 0 | 9.4556 | 37.78
2022-04-23 15:00 | 44674.625 | 0 | 10.6749 | 37.78
2022-04-23 15:30 | 44674.6458 | 0 | 10.1948 | 37.78
2022-04-23 16:00 | 44674.6667 | 0 | 10.2598 | 37.78
2022-04-23 16:30 | 44674.6875 | 0 | 11.0972 | 37.78
2022-04-23 17:00 | 44674.7083 | 0 | 11.4047 | 37.78
2022-04-23 17:30 | 44674.7292 | 0 | 11.6578 | 37.78
2022-04-23 18:00 | 44674.75 | 0 | 11.8137 | 37.78
2022-04-23 18:30 | 44674.7708 | 0 | 11.8156 | 37.78
2022-04-23 19:00 | 44674.7917 | 0 | 11.6689 | 37.78
2022-04-23 19:30 | 44674.8125 | 0 | 11.1568 | 37.78
2022-04-23 20:00 | 44674.8333 | 0 | 10.9977 | 37.78
2022-04-23 20:30 | 44674.8542 | 0 | 10.6835 | 37.78
2022-04-23 21:00 | 44674.875 | 0 | 10.2372 | 37.78
2022-04-23 21:30 | 44674.8958 | 0 | 9.9325 | 37.78
2022-04-23 22:00 | 44674.9167 | 0 | 9.6452 | 37.78
2022-04-23 22:30 | 44674.9375 | 0 | 9.1915 | 37.78
2022-04-23 23:00 | 44674.9583 | 0 | 8.889 | 37.78
2022-04-23 23:30 | 44674.9792 | 0 | 8.466 | 37.78
2022-04-24 | 44675 | 0 | 8.0678 | 37.78
2022-04-24 00:30 | 44675.0208 | 0 | 7.8109 | 37.78
2022-04-24 01:00 | 44675.0417 | 0 | 7.738 | 37.78
2022-04-24 01:30 | 44675.0625 | 0 | 7.5985 | 37.78
2022-04-24 02:00 | 44675.0833 | 0 | 7.4341 | 37.78
2022-04-24 02:30 | 44675.1042 | 0 | 7.3835 | 37.78
2022-04-24 03:00 | 44675.125 | 0 | 7.3693 | 37.78
2022-04-24 03:30 | 44675.1458 | 0 | 7.2632 | 37.78
2022-04-24 04:00 | 44675.1667 | 0 | 7.2209 | 37.78
2022-04-24 04:30 | 44675.1875 | 0 | 7.3091 | 37.78
2022-04-24 05:00 | 44675.2083 | 0 | 7.3835 | 37.78
2022-04-24 05:30 | 44675.2292 | 0 | 7.4807 | 37.78
2022-04-24 06:00 | 44675.25 | 0 | 7.7129 | 37.78
2022-04-24 06:30 | 44675.2708 | 0 | 7.9779 | 37.78
2022-04-24 07:00 | 44675.2917 | 0 | 7.3769 | 37.78
2022-04-24 07:30 | 44675.3125 | 0 | 8.1681 | 37.78
2022-04-24 08:00 | 44675.3333 | 0 | 8.8241 | 37.78
2022-04-24 08:30 | 44675.3542 | 0 | 8.8913 | 37.78
2022-04-24 09:00 | 44675.375 | 0 | 7.5328 | 37.78
2022-04-24 09:30 | 44675.3958 | 0 | 7.6968 | 37.78
2022-04-24 10:00 | 44675.4167 | 0 | 7.8076 | 37.78
2022-04-24 10:30 | 44675.4375 | 0 | 7.7112 | 37.78
2022-04-24 11:00 | 44675.4583 | 0 | 6.6447 | 37.78
2022-04-24 11:30 | 44675.4792 | 0 | 6.7739 | 37.78
2022-04-24 12:00 | 44675.5 | 0 | 8.0313 | 37.78
2022-04-24 12:30 | 44675.5208 | 0 | 8.0068 | 37.78
2022-04-24 13:00 | 44675.5417 | 0 | 7.1392 | 37.78
2022-04-24 13:30 | 44675.5625 | 0 | 7.2124 | 37.78
2022-04-24 14:00 | 44675.5833 | 0 | 7.9944 | 37.78
2022-04-24 14:30 | 44675.6042 | 0 | 8.8579 | 37.78
2022-04-24 15:00 | 44675.625 | 0 | 8.1762 | 37.78
2022-04-24 15:30 | 44675.6458 | 0 | 8.9423 | 37.78
2022-04-24 16:00 | 44675.6667 | 0 | 9.6225 | 37.78
2022-04-24 16:30 | 44675.6875 | 0 | 10.226 | 37.78
2022-04-24 17:00 | 44675.7083 | 0 | 11.0488 | 37.78
2022-04-24 17:30 | 44675.7292 | 0 | 11.5062 | 37.78
2022-04-24 18:00 | 44675.75 | 0 | 11.6979 | 37.78
2022-04-24 18:30 | 44675.7708 | 0 | 11.6467 | 37.78
2022-04-24 19:00 | 44675.7917 | 0 | 11.2051 | 37.78
2022-04-24 19:30 | 44675.8125 | 0 | 10.7055 | 37.78
2022-04-24 20:00 | 44675.8333 | 0 | 10.5208 | 37.78
2022-04-24 20:30 | 44675.8542 | 0 | 10.2137 | 37.78
2022-04-24 21:00 | 44675.875 | 0 | 9.9055 | 37.78
2022-04-24 21:30 | 44675.8958 | 0 | 9.5419 | 37.78
2022-04-24 22:00 | 44675.9167 | 0 | 9.3616 | 37.78
2022-04-24 22:30 | 44675.9375 | 0 | 8.7272 | 37.78
2022-04-24 23:00 | 44675.9583 | 0 | 8.3945 | 37.78
2022-04-24 23:30 | 44675.9792 | 0 | 8.0898 | 37.78
2022-04-25 | 44676 | 0 | 7.7395 | 37.78
2022-04-25 00:30 | 44676.0208 | 0 | 7.5719 | 37.78
2022-04-25 01:00 | 44676.0417 | 0 | 7.4857 | 37.78
2022-04-25 01:30 | 44676.0625 | 0 | 7.2772 | 37.78
2022-04-25 02:00 | 44676.0833 | 0 | 7.1825 | 37.78
2022-04-25 02:30 | 44676.1042 | 0 | 7.2843 | 37.78
2022-04-25 03:00 | 44676.125 | 0 | 7.1409 | 37.78
2022-04-25 03:30 | 44676.1458 | 0 | 7.0634 | 37.78
2022-04-25 04:00 | 44676.1667 | 0 | 7.2202 | 37.78
2022-04-25 04:30 | 44676.1875 | 0 | 7.3993 | 37.78
2022-04-25 05:00 | 44676.2083 | 0 | 7.5649 | 37.78
2022-04-25 05:30 | 44676.2292 | 0 | 7.7852 | 37.78
2022-04-25 06:00 | 44676.25 | 0 | 8.1586 | 37.78
2022-04-25 06:30 | 44676.2708 | 0 | 8.5879 | 37.78
2022-04-25 07:00 | 44676.2917 | 0 | 8.6003 | 37.78
2022-04-25 07:30 | 44676.3125 | 0 | 8.8744 | 37.78
2022-04-25 08:00 | 44676.3333 | 0 | 9.0605 | 37.78
2022-04-25 08:30 | 44676.3542 | 0 | 8.2839 | 37.78
2022-04-25 09:00 | 44676.375 | 0 | 8.4471 | 37.78
2022-04-25 09:30 | 44676.3958 | 0 | 8.6932 | 37.78
2022-04-25 10:00 | 44676.4167 | 0 | 10.2176 | 37.78
2022-04-25 10:30 | 44676.4375 | 0 | 8.9619 | 37.78
2022-04-25 11:00 | 44676.4583 | 0 | 9.0863 | 37.78
2022-04-25 11:30 | 44676.4792 | 0 | 10.2327 | 37.78
2022-04-25 12:00 | 44676.5 | 0 | 8.1261 | 37.78
2022-04-25 12:30 | 44676.5208 | 0 | 8.7442 | 37.78
2022-04-25 13:00 | 44676.5417 | 0 | 9.1806 | 37.78
2022-04-25 13:30 | 44676.5625 | 0 | 8.8866 | 37.78
2022-04-25 14:00 | 44676.5833 | 0 | 9.644 | 37.78
2022-04-25 14:30 | 44676.6042 | 0 | 9.3167 | 37.78
2022-04-25 15:00 | 44676.625 | 0 | 9.6279 | 37.78
2022-04-25 15:30 | 44676.6458 | 0 | 9.898 | 37.78
2022-04-25 16:00 | 44676.6667 | 0 | 10.5623 | 37.78
2022-04-25 16:30 | 44676.6875 | 0 | 11.3256 | 37.78
2022-04-25 17:00 | 44676.7083 | 0 | 11.9646 | 37.78
2022-04-25 17:30 | 44676.7292 | 0 | 12.4272 | 37.78
2022-04-25 18:00 | 44676.75 | 0 | 12.2467 | 37.78
2022-04-25 18:30 | 44676.7708 | 0 | 12.1638 | 37.78
2022-04-25 19:00 | 44676.7917 | 0 | 11.919 | 37.78
2022-04-25 19:30 | 44676.8125 | 0 | 11.4997 | 37.78
2022-04-25 20:00 | 44676.8333 | 0 | 11.3374 | 37.78
2022-04-25 20:30 | 44676.8542 | 0 | 10.6951 | 37.78
2022-04-25 21:00 | 44676.875 | 0 | 10.24 | 37.78
2022-04-25 21:30 | 44676.8958 | 0 | 9.7476 | 37.78
2022-04-25 22:00 | 44676.9167 | 0 | 9.5044 | 37.78
2022-04-25 22:30 | 44676.9375 | 0 | 8.4921 | 37.78
2022-04-25 23:00 | 44676.9583 | 0 | 8.2677 | 37.78
2022-04-25 23:30 | 44676.9792 | 0 | 7.9558 | 37.78
2022-04-26 | 44677 | 0 | 7.6092 | 37.78
2022-04-26 00:30 | 44677.0208 | 0 | 7.5003 | 37.78
2022-04-26 01:00 | 44677.0417 | 0 | 7.3905 | 37.78
2022-04-26 01:30 | 44677.0625 | 0 | 7.2698 | 37.78
2022-04-26 02:00 | 44677.0833 | 0 | 7.2821 | 37.78
2022-04-26 02:30 | 44677.1042 | 0 | 7.2456 | 37.78
2022-04-26 03:00 | 44677.125 | 0 | 7.2981 | 37.78
2022-04-26 03:30 | 44677.1458 | 0 | 7.4326 | 37.78
2022-04-26 04:00 | 44677.1667 | 0 | 7.8675 | 37.78
2022-04-26 04:30 | 44677.1875 | 0 | 8.3249 | 37.78
2022-04-26 05:00 | 44677.2083 | 0 | 8.7977 | 37.78
2022-04-26 05:30 | 44677.2292 | 0 | 9.5412 | 37.78
2022-04-26 06:00 | 44677.25 | 0 | 10.5544 | 37.78
2022-04-26 06:30 | 44677.2708 | 0 | 11.5259 | 37.78
2022-04-26 07:00 | 44677.2917 | 0 | 12.0649 | 37.78
2022-04-26 07:30 | 44677.3125 | 0 | 12.4053 | 37.78
2022-04-26 08:00 | 44677.3333 | 0 | 12.3183 | 37.78
2022-04-26 08:30 | 44677.3542 | 0 | 12.6165 | 37.78
2022-04-26 09:00 | 44677.375 | 0 | 12.711 | 37.78
2022-04-26 09:30 | 44677.3958 | 0 | 12.3605 | 37.78
2022-04-26 10:00 | 44677.4167 | 0 | 12.2295 | 37.78
2022-04-26 10:30 | 44677.4375 | 0 | 12.1443 | 37.78
2022-04-26 11:00 | 44677.4583 | 0 | 12.2004 | 37.78
2022-04-26 11:30 | 44677.4792 | 0 | 11.934 | 37.78
2022-04-26 12:00 | 44677.5 | 0 | 12.297 | 37.78
2022-04-26 12:30 | 44677.5208 | 0 | 12.1308 | 37.78
2022-04-26 13:00 | 44677.5417 | 0 | 12.0303 | 37.78
2022-04-26 13:30 | 44677.5625 | 0 | 11.7914 | 37.78
2022-04-26 14:00 | 44677.5833 | 0 | 11.8595 | 37.78
2022-04-26 14:30 | 44677.6042 | 0 | 12.4566 | 37.78
2022-04-26 15:00 | 44677.625 | 0 | 12.1749 | 37.78
2022-04-26 15:30 | 44677.6458 | 0 | 12.4706 | 37.78
2022-04-26 16:00 | 44677.6667 | 0 | 13.0036 | 37.78
2022-04-26 16:30 | 44677.6875 | 0 | 13.2137 | 37.78
2022-04-26 17:00 | 44677.7083 | 0 | 13.7269 | 37.78
2022-04-26 17:30 | 44677.7292 | 0 | 14.0035 | 37.78
2022-04-26 18:00 | 44677.75 | 0 | 14.1275 | 37.78
2022-04-26 18:30 | 44677.7708 | 0 | 14.3432 | 37.78
2022-04-26 19:00 | 44677.7917 | 0 | 13.9686 | 37.78
2022-04-26 19:30 | 44677.8125 | 0 | 13.5689 | 37.78
2022-04-26 20:00 | 44677.8333 | 0 | 13.2381 | 37.78
2022-04-26 20:30 | 44677.8542 | 0 | 12.6394 | 37.78
2022-04-26 21:00 | 44677.875 | 0 | 12.1409 | 37.78
2022-04-26 21:30 | 44677.8958 | 0 | 11.5893 | 37.78
2022-04-26 22:00 | 44677.9167 | 0 | 11.1069 | 37.78
2022-04-26 22:30 | 44677.9375 | 0 | 10.3305 | 37.78
2022-04-26 23:00 | 44677.9583 | 0 | 9.809 | 37.78
2022-04-26 23:30 | 44677.9792 | 0 | 9.3557 | 37.78
2022-04-27 | 44678 | 0 | 8.7793 | 37.78
2022-04-27 00:30 | 44678.0208 | 0 | 8.5124 | 37.78
2022-04-27 01:00 | 44678.0417 | 0 | 8.3701 | 37.78
2022-04-27 01:30 | 44678.0625 | 0 | 8.0607 | 37.78
2022-04-27 02:00 | 44678.0833 | 0 | 8.0386 | 37.78
2022-04-27 02:30 | 44678.1042 | 0 | 7.9183 | 37.78
2022-04-27 03:00 | 44678.125 | 0 | 7.8167 | 37.78
2022-04-27 03:30 | 44678.1458 | 0 | 7.8734 | 37.78
2022-04-27 04:00 | 44678.1667 | 0 | 8.1158 | 37.78
2022-04-27 04:30 | 44678.1875 | 0 | 8.4892 | 37.78
2022-04-27 05:00 | 44678.2083 | 0 | 8.9805 | 37.78
2022-04-27 05:30 | 44678.2292 | 0 | 9.7377 | 37.78
2022-04-27 06:00 | 44678.25 | 0 | 10.7371 | 37.78
2022-04-27 06:30 | 44678.2708 | 0 | 11.8163 | 37.78
2022-04-27 07:00 | 44678.2917 | 0 | 12.5595 | 37.78
2022-04-27 07:30 | 44678.3125 | 0 | 12.1973 | 37.78
2022-04-27 08:00 | 44678.3333 | 0 | 11.3116 | 37.78
2022-04-27 08:30 | 44678.3542 | 0 | 11.9757 | 37.78
2022-04-27 09:00 | 44678.375 | 0 | 11.7586 | 37.78
2022-04-27 09:30 | 44678.3958 | 0 | 10.965 | 37.78
2022-04-27 10:00 | 44678.4167 | 0 | 10.975 | 37.78
2022-04-27 10:30 | 44678.4375 | 0 | 12.2994 | 37.78
2022-04-27 11:00 | 44678.4583 | 0 | 12.2308 | 37.78
2022-04-27 11:30 | 44678.4792 | 0 | 11.9802 | 37.78
2022-04-27 12:00 | 44678.5 | 0 | 9.933 | 37.78
2022-04-27 12:30 | 44678.5208 | 0 | 9.4462 | 37.78
2022-04-27 13:00 | 44678.5417 | 0 | 10.4882 | 37.78
2022-04-27 13:30 | 44678.5625 | 0 | 10.8413 | 37.78
2022-04-27 14:00 | 44678.5833 | 0 | 10.5685 | 37.78
2022-04-27 14:30 | 44678.6042 | 0 | 11.4352 | 37.78
2022-04-27 15:00 | 44678.625 | 0 | 12.1618 | 37.78
2022-04-27 15:30 | 44678.6458 | 0 | 12.9538 | 37.78
2022-04-27 16:00 | 44678.6667 | 0 | 13.1386 | 37.78
2022-04-27 16:30 | 44678.6875 | 0 | 13.3504 | 37.78
2022-04-27 17:00 | 44678.7083 | 0 | 13.6574 | 37.78
2022-04-27 17:30 | 44678.7292 | 0 | 13.9295 | 37.78
2022-04-27 18:00 | 44678.75 | 0 | 14.2576 | 37.78
2022-04-27 18:30 | 44678.7708 | 0 | 14.3536 | 37.78
2022-04-27 19:00 | 44678.7917 | 0 | 13.8524 | 37.78
2022-04-27 19:30 | 44678.8125 | 0 | 13.6104 | 37.78
2022-04-27 20:00 | 44678.8333 | 0 | 13.3472 | 37.78
2022-04-27 20:30 | 44678.8542 | 0 | 13.0669 | 37.78
2022-04-27 21:00 | 44678.875 | 0 | 12.3829 | 37.78
2022-04-27 21:30 | 44678.8958 | 0 | 11.8328 | 37.78
2022-04-27 22:00 | 44678.9167 | 0 | 11.3266 | 37.78
2022-04-27 22:30 | 44678.9375 | 0 | 10.6532 | 37.78
2022-04-27 23:00 | 44678.9583 | 0 | 10.1953 | 37.78
2022-04-27 23:30 | 44678.9792 | 0 | 9.7922 | 37.78
2022-04-28 | 44679 | 0 | 9.0458 | 37.78
2022-04-28 00:30 | 44679.0208 | 0 | 8.5458 | 37.78
2022-04-28 01:00 | 44679.0417 | 0 | 8.6099 | 37.78
2022-04-28 01:30 | 44679.0625 | 0 | 8.3875 | 37.78
2022-04-28 02:00 | 44679.0833 | 0 | 8.3034 | 37.78
2022-04-28 02:30 | 44679.1042 | 0 | 8.2564 | 37.78
2022-04-28 03:00 | 44679.125 | 0 | 8.2103 | 37.78
2022-04-28 03:30 | 44679.1458 | 0 | 8.3568 | 37.78
2022-04-28 04:00 | 44679.1667 | 0 | 8.7773 | 37.78
2022-04-28 04:30 | 44679.1875 | 0 | 8.9296 | 37.78
2022-04-28 05:00 | 44679.2083 | 0 | 9.5308 | 37.78
2022-04-28 05:30 | 44679.2292 | 0 | 10.1534 | 37.78
2022-04-28 06:00 | 44679.25 | 0 | 11.1564 | 37.78
2022-04-28 06:30 | 44679.2708 | 0 | 12.0649 | 37.78
2022-04-28 07:00 | 44679.2917 | 0 | 12.5702 | 37.78
2022-04-28 07:30 | 44679.3125 | 0 | 12.5081 | 37.78
2022-04-28 08:00 | 44679.3333 | 0 | 12.9855 | 37.78
2022-04-28 08:30 | 44679.3542 | 0 | 12.01 | 37.78
2022-04-28 09:00 | 44679.375 | 0 | 12.1485 | 37.78
2022-04-28 09:30 | 44679.3958 | 0 | 12.2265 | 37.78
2022-04-28 10:00 | 44679.4167 | 0 | 11.3784 | 37.78
2022-04-28 10:30 | 44679.4375 | 0 | 12.013 | 37.78
2022-04-28 11:00 | 44679.4583 | 0 | 11.453 | 37.78
2022-04-28 11:30 | 44679.4792 | 0 | 10.5994 | 37.78
2022-04-28 12:00 | 44679.5 | 0 | 11.1181 | 37.78
2022-04-28 12:30 | 44679.5208 | 0 | 11.3448 | 37.78
2022-04-28 13:00 | 44679.5417 | 0 | 12.3629 | 37.78
2022-04-28 13:30 | 44679.5625 | 0 | 12.0653 | 37.78
2022-04-28 14:00 | 44679.5833 | 0 | 12.4473 | 37.78
2022-04-28 14:30 | 44679.6042 | 0 | 12.43 | 37.78
2022-04-28 15:00 | 44679.625 | 0 | 12.1733 | 37.78
2022-04-28 15:30 | 44679.6458 | 0 | 12.9473 | 37.78
2022-04-28 16:00 | 44679.6667 | 0 | 13.7015 | 37.78
2022-04-28 16:30 | 44679.6875 | 0 | 14.0845 | 37.78
2022-04-28 17:00 | 44679.7083 | 0 | 14.115 | 37.78
2022-04-28 17:30 | 44679.7292 | 0 | 14.455 | 37.78
2022-04-28 18:00 | 44679.75 | 0 | 14.5374 | 37.78
2022-04-28 18:30 | 44679.7708 | 0 | 14.5937 | 37.78
2022-04-28 19:00 | 44679.7917 | 0 | 14.2654 | 37.78
2022-04-28 19:30 | 44679.8125 | 0 | 13.9181 | 37.78
2022-04-28 20:00 | 44679.8333 | 0 | 13.6183 | 37.78
2022-04-28 20:30 | 44679.8542 | 0 | 13.1769 | 37.78
2022-04-28 21:00 | 44679.875 | 0 | 12.7483 | 37.78
2022-04-28 21:30 | 44679.8958 | 0 | 12.2202 | 37.78
2022-04-28 22:00 | 44679.9167 | 0 | 11.6862 | 37.78
2022-04-28 22:30 | 44679.9375 | 0 | 10.829 | 37.78
2022-04-28 23:00 | 44679.9583 | 0 | 10.2169 | 37.78
2022-04-28 23:30 | 44679.9792 | 0 | 9.9013 | 37.78
2022-04-29 | 44680 | 0 | 9.269 | 37.78
2022-04-29 00:30 | 44680.0208 | 0 | 8.8912 | 37.78
2022-04-29 01:00 | 44680.0417 | 0 | 8.7677 | 37.78
2022-04-29 01:30 | 44680.0625 | 0 | 8.6772 | 37.78
2022-04-29 02:00 | 44680.0833 | 0 | 8.5588 | 37.78
2022-04-29 02:30 | 44680.1042 | 0 | 8.5315 | 37.78
2022-04-29 03:00 | 44680.125 | 0 | 8.4206 | 37.78
2022-04-29 03:30 | 44680.1458 | 0 | 8.5939 | 37.78
2022-04-29 04:00 | 44680.1667 | 0 | 8.8853 | 37.78
2022-04-29 04:30 | 44680.1875 | 0 | 9.0252 | 37.78
2022-04-29 05:00 | 44680.2083 | 0 | 9.6589 | 37.78
2022-04-29 05:30 | 44680.2292 | 0 | 10.1956 | 37.78
2022-04-29 06:00 | 44680.25 | 0 | 10.9905 | 37.78
2022-04-29 06:30 | 44680.2708 | 0 | 11.7694 | 37.78
2022-04-29 07:00 | 44680.2917 | 0 | 12.199 | 37.78
2022-04-29 07:30 | 44680.3125 | 0 | 11.6632 | 37.78
2022-04-29 08:00 | 44680.3333 | 0 | 11.6242 | 37.78
2022-04-29 08:30 | 44680.3542 | 0 | 11.1145 | 37.78
2022-04-29 09:00 | 44680.375 | 0 | 11.7099 | 37.78
2022-04-29 09:30 | 44680.3958 | 0 | 12.2043 | 37.78
2022-04-29 10:00 | 44680.4167 | 0 | 10.7149 | 37.78
2022-04-29 10:30 | 44680.4375 | 0 | 10.9448 | 37.78
2022-04-29 11:00 | 44680.4583 | 0 | 12.0741 | 37.78
2022-04-29 11:30 | 44680.4792 | 0 | 12.7485 | 37.78
2022-04-29 12:00 | 44680.5 | 0 | 10.7438 | 37.78
2022-04-29 12:30 | 44680.5208 | 0 | 10.5918 | 37.78
2022-04-29 13:00 | 44680.5417 | 0 | 11.7852 | 37.78
2022-04-29 13:30 | 44680.5625 | 0 | 12.0396 | 37.78
2022-04-29 14:00 | 44680.5833 | 0 | 11.6511 | 37.78
2022-04-29 14:30 | 44680.6042 | 0 | 12.3162 | 37.78
2022-04-29 15:00 | 44680.625 | 0 | 13.1737 | 37.78
2022-04-29 15:30 | 44680.6458 | 0 | 13.3194 | 37.78
2022-04-29 16:00 | 44680.6667 | 0 | 13.9419 | 37.78
2022-04-29 16:30 | 44680.6875 | 0 | 14.1019 | 37.78
2022-04-29 17:00 | 44680.7083 | 0 | 14.2291 | 37.78
2022-04-29 17:30 | 44680.7292 | 0 | 14.3798 | 37.78
2022-04-29 18:00 | 44680.75 | 0 | 14.3276 | 37.78
2022-04-29 18:30 | 44680.7708 | 0 | 14.1201 | 37.78
2022-04-29 19:00 | 44680.7917 | 0 | 13.86 | 37.78
2022-04-29 19:30 | 44680.8125 | 0 | 13.5911 | 37.78
2022-04-29 20:00 | 44680.8333 | 0 | 13.4766 | 37.78
2022-04-29 20:30 | 44680.8542 | 0 | 12.9384 | 37.78
2022-04-29 21:00 | 44680.875 | 0 | 12.373 | 37.78
2022-04-29 21:30 | 44680.8958 | 0 | 12.098 | 37.78
2022-04-29 22:00 | 44680.9167 | 0 | 11.6871 | 37.78
2022-04-29 22:30 | 44680.9375 | 0 | 10.8153 | 37.78
2022-04-29 23:00 | 44680.9583 | 0 | 10.4017 | 37.78
2022-04-29 23:30 | 44680.9792 | 0 | 9.9768 | 37.78
2022-04-30 | 44681 | 0 | 9.3588 | 37.78
2022-04-30 00:30 | 44681.0208 | 0 | 9.001 | 37.78
2022-04-30 01:00 | 44681.0417 | 0 | 8.9428 | 37.78
2022-04-30 01:30 | 44681.0625 | 0 | 8.7316 | 37.78
2022-04-30 02:00 | 44681.0833 | 0 | 8.5886 | 37.78
2022-04-30 02:30 | 44681.1042 | 0 | 8.5362 | 37.78
2022-04-30 03:00 | 44681.125 | 0 | 8.3168 | 37.78
2022-04-30 03:30 | 44681.1458 | 0 | 8.476 | 37.78
2022-04-30 04:00 | 44681.1667 | 0 | 8.5852 | 37.78
2022-04-30 04:30 | 44681.1875 | 0 | 8.5392 | 37.78
2022-04-30 05:00 | 44681.2083 | 0 | 8.8068 | 37.78
2022-04-30 05:30 | 44681.2292 | 0 | 8.6557 | 37.78
2022-04-30 06:00 | 44681.25 | 0 | 9.2995 | 37.78
2022-04-30 06:30 | 44681.2708 | 0 | 9.5339 | 37.78
2022-04-30 07:00 | 44681.2917 | 0 | 9.902 | 37.78
2022-04-30 07:30 | 44681.3125 | 0 | 9.6458 | 37.78
2022-04-30 08:00 | 44681.3333 | 0 | 9.454 | 37.78
2022-04-30 08:30 | 44681.3542 | 0 | 8.8405 | 37.78
2022-04-30 09:00 | 44681.375 | 0 | 8.7502 | 37.78
2022-04-30 09:30 | 44681.3958 | 0 | 9.3082 | 37.78
2022-04-30 10:00 | 44681.4167 | 0 | 9.6558 | 37.78
2022-04-30 10:30 | 44681.4375 | 0 | 8.2233 | 37.78
2022-04-30 11:00 | 44681.4583 | 0 | 8.0102 | 37.78
2022-04-30 11:30 | 44681.4792 | 0 | 7.9879 | 37.78
2022-04-30 12:00 | 44681.5 | 0 | 7.881 | 37.78
2022-04-30 12:30 | 44681.5208 | 0 | 8.0008 | 37.78
2022-04-30 13:00 | 44681.5417 | 0 | 9.0713 | 37.78
2022-04-30 13:30 | 44681.5625 | 0 | 9.5572 | 37.78
2022-04-30 14:00 | 44681.5833 | 0 | 10.3403 | 37.78
2022-04-30 14:30 | 44681.6042 | 0 | 10.7467 | 37.78
2022-04-30 15:00 | 44681.625 | 0 | 10.5912 | 37.78
2022-04-30 15:30 | 44681.6458 | 0 | 11.163 | 37.78
2022-04-30 16:00 | 44681.6667 | 0 | 11.323 | 37.78
2022-04-30 16:30 | 44681.6875 | 0 | 11.88 | 37.78
2022-04-30 17:00 | 44681.7083 | 0 | 12.2838 | 37.78
2022-04-30 17:30 | 44681.7292 | 0 | 12.55 | 37.78
2022-04-30 18:00 | 44681.75 | 0 | 12.6057 | 37.78
2022-04-30 18:30 | 44681.7708 | 0 | 12.4962 | 37.78
2022-04-30 19:00 | 44681.7917 | 0 | 12.3667 | 37.78
2022-04-30 19:30 | 44681.8125 | 0 | 11.9091 | 37.78
2022-04-30 20:00 | 44681.8333 | 0 | 11.8474 | 37.78
2022-04-30 20:30 | 44681.8542 | 0 | 11.3134 | 37.78
2022-04-30 21:00 | 44681.875 | 0 | 10.8539 | 37.78
2022-04-30 21:30 | 44681.8958 | 0 | 10.5503 | 37.78
2022-04-30 22:00 | 44681.9167 | 0 | 10.4094 | 37.78
2022-04-30 22:30 | 44681.9375 | 0 | 9.8803 | 37.78
2022-04-30 23:00 | 44681.9583 | 0 | 9.3926 | 37.78
2022-04-30 23:30 | 44681.9792 | 0 | 9.0379 | 37.78
2022-05-01 | 44682 | 0 | 8.5465 | 39.95
2022-05-01 00:30 | 44682.0208 | 0 | 8.1457 | 39.95
2022-05-01 01:00 | 44682.0417 | 0 | 8.0519 | 39.95
2022-05-01 01:30 | 44682.0625 | 0 | 7.9511 | 39.95
2022-05-01 02:00 | 44682.0833 | 0 | 7.9418 | 39.95
2022-05-01 02:30 | 44682.1042 | 0 | 7.7376 | 39.95
2022-05-01 03:00 | 44682.125 | 0 | 7.6756 | 39.95
2022-05-01 03:30 | 44682.1458 | 0 | 7.6943 | 39.95
2022-05-01 04:00 | 44682.1667 | 0 | 7.6099 | 39.95
2022-05-01 04:30 | 44682.1875 | 0 | 7.5808 | 39.95
2022-05-01 05:00 | 44682.2083 | 0 | 7.6927 | 39.95
2022-05-01 05:30 | 44682.2292 | 0 | 7.7985 | 39.95
2022-05-01 06:00 | 44682.25 | 0 | 8.1455 | 39.95
2022-05-01 06:30 | 44682.2708 | 0 | 8.2844 | 39.95
2022-05-01 07:00 | 44682.2917 | 0 | 8.7378 | 39.95
2022-05-01 07:30 | 44682.3125 | 0 | 8.3593 | 39.95
2022-05-01 08:00 | 44682.3333 | 0 | 9.0378 | 39.95
2022-05-01 08:30 | 44682.3542 | 0 | 9.3774 | 39.95
2022-05-01 09:00 | 44682.375 | 0 | 9.1987 | 39.95
2022-05-01 09:30 | 44682.3958 | 0 | 8.4531 | 39.95
2022-05-01 10:00 | 44682.4167 | 0 | 8.7982 | 39.95
2022-05-01 10:30 | 44682.4375 | 0 | 8.8027 | 39.95
2022-05-01 11:00 | 44682.4583 | 0 | 9.1324 | 39.95
2022-05-01 11:30 | 44682.4792 | 0 | 8.2784 | 39.95
2022-05-01 12:00 | 44682.5 | 0 | 8.4966 | 39.95
2022-05-01 12:30 | 44682.5208 | 0 | 8.8566 | 39.95
2022-05-01 13:00 | 44682.5417 | 0 | 9.2326 | 39.95
2022-05-01 13:30 | 44682.5625 | 0 | 9.9145 | 39.95
2022-05-01 14:00 | 44682.5833 | 0 | 9.4042 | 39.95
2022-05-01 14:30 | 44682.6042 | 0 | 9.8489 | 39.95
2022-05-01 15:00 | 44682.625 | 0 | 9.8354 | 39.95
2022-05-01 15:30 | 44682.6458 | 0 | 9.871 | 39.95
2022-05-01 16:00 | 44682.6667 | 0 | 10.1964 | 39.95
2022-05-01 16:30 | 44682.6875 | 0 | 10.4656 | 39.95
2022-05-01 17:00 | 44682.7083 | 0 | 11.1903 | 39.95
2022-05-01 17:30 | 44682.7292 | 0 | 11.4305 | 39.95
2022-05-01 18:00 | 44682.75 | 0 | 11.7446 | 39.95
2022-05-01 18:30 | 44682.7708 | 0 | 11.5039 | 39.95
2022-05-01 19:00 | 44682.7917 | 0 | 11.1263 | 39.95
2022-05-01 19:30 | 44682.8125 | 0 | 10.8976 | 39.95
2022-05-01 20:00 | 44682.8333 | 0 | 10.7904 | 39.95
2022-05-01 20:30 | 44682.8542 | 0 | 10.3542 | 39.95
2022-05-01 21:00 | 44682.875 | 0 | 10.0061 | 39.95
2022-05-01 21:30 | 44682.8958 | 0 | 9.6612 | 39.95
2022-05-01 22:00 | 44682.9167 | 0 | 9.4207 | 39.95
2022-05-01 22:30 | 44682.9375 | 0 | 8.8631 | 39.95
2022-05-01 23:00 | 44682.9583 | 0 | 8.4822 | 39.95
2022-05-01 23:30 | 44682.9792 | 0 | 8.1819 | 39.95
2022-05-02 | 44683 | 0 | 7.8614 | 39.95
2022-05-02 00:30 | 44683.0208 | 0 | 7.6341 | 39.95
2022-05-02 01:00 | 44683.0417 | 0 | 7.6173 | 39.95
2022-05-02 01:30 | 44683.0625 | 0 | 7.427 | 39.95
2022-05-02 02:00 | 44683.0833 | 0 | 7.343 | 39.95
2022-05-02 02:30 | 44683.1042 | 0 | 7.4219 | 39.95
2022-05-02 03:00 | 44683.125 | 0 | 7.2249 | 39.95
2022-05-02 03:30 | 44683.1458 | 0 | 7.2742 | 39.95
2022-05-02 04:00 | 44683.1667 | 0 | 7.4074 | 39.95
2022-05-02 04:30 | 44683.1875 | 0 | 7.5654 | 39.95
2022-05-02 05:00 | 44683.2083 | 0 | 7.8071 | 39.95
2022-05-02 05:30 | 44683.2292 | 0 | 8.0377 | 39.95
2022-05-02 06:00 | 44683.25 | 0 | 8.3384 | 39.95
2022-05-02 06:30 | 44683.2708 | 0 | 8.4492 | 39.95
2022-05-02 07:00 | 44683.2917 | 0 | 8.4392 | 39.95
2022-05-02 07:30 | 44683.3125 | 0 | 8.1807 | 39.95
2022-05-02 08:00 | 44683.3333 | 0 | 7.9033 | 39.95
2022-05-02 08:30 | 44683.3542 | 0 | 8.035 | 39.95
2022-05-02 09:00 | 44683.375 | 0 | 8.2089 | 39.95
2022-05-02 09:30 | 44683.3958 | 0 | 7.4203 | 39.95
2022-05-02 10:00 | 44683.4167 | 0 | 7.2224 | 39.95
2022-05-02 10:30 | 44683.4375 | 0 | 7.8048 | 39.95
2022-05-02 11:00 | 44683.4583 | 0 | 7.4625 | 39.95
2022-05-02 11:30 | 44683.4792 | 0 | 7.3603 | 39.95
2022-05-02 12:00 | 44683.5 | 0 | 7.9906 | 39.95
2022-05-02 12:30 | 44683.5208 | 0 | 8.6099 | 39.95
2022-05-02 13:00 | 44683.5417 | 0 | 9.097 | 39.95
2022-05-02 13:30 | 44683.5625 | 0 | 9.5681 | 39.95
2022-05-02 14:00 | 44683.5833 | 0 | 9.1673 | 39.95
2022-05-02 14:30 | 44683.6042 | 0 | 8.4848 | 39.95
2022-05-02 15:00 | 44683.625 | 0 | 9.8214 | 39.95
2022-05-02 15:30 | 44683.6458 | 0 | 10.4796 | 39.95
2022-05-02 16:00 | 44683.6667 | 0 | 11.0789 | 39.95
2022-05-02 16:30 | 44683.6875 | 0 | 11.6603 | 39.95
2022-05-02 17:00 | 44683.7083 | 0 | 12.0754 | 39.95
2022-05-02 17:30 | 44683.7292 | 0 | 12.4895 | 39.95
2022-05-02 18:00 | 44683.75 | 0 | 12.6066 | 39.95
2022-05-02 18:30 | 44683.7708 | 0 | 12.3616 | 39.95
2022-05-02 19:00 | 44683.7917 | 0 | 12.184 | 39.95
2022-05-02 19:30 | 44683.8125 | 0 | 11.7439 | 39.95
2022-05-02 20:00 | 44683.8333 | 0 | 11.5802 | 39.95
2022-05-02 20:30 | 44683.8542 | 0 | 10.8983 | 39.95
2022-05-02 21:00 | 44683.875 | 0 | 10.4494 | 39.95
2022-05-02 21:30 | 44683.8958 | 0 | 10.1267 | 39.95
2022-05-02 22:00 | 44683.9167 | 0 | 9.5909 | 39.95
2022-05-02 22:30 | 44683.9375 | 0 | 8.8391 | 39.95
2022-05-02 23:00 | 44683.9583 | 0 | 8.3933 | 39.95
2022-05-02 23:30 | 44683.9792 | 0 | 8.1063 | 39.95
2022-05-03 | 44684 | 0 | 7.6032 | 39.95
2022-05-03 00:30 | 44684.0208 | 0 | 7.4735 | 39.95
2022-05-03 01:00 | 44684.0417 | 0 | 7.3442 | 39.95
2022-05-03 01:30 | 44684.0625 | 0 | 7.3393 | 39.95
2022-05-03 02:00 | 44684.0833 | 0 | 7.2004 | 39.95
2022-05-03 02:30 | 44684.1042 | 0 | 7.2734 | 39.95
2022-05-03 03:00 | 44684.125 | 0 | 7.1193 | 39.95
2022-05-03 03:30 | 44684.1458 | 0 | 7.2536 | 39.95
2022-05-03 04:00 | 44684.1667 | 0 | 7.6622 | 39.95
2022-05-03 04:30 | 44684.1875 | 0 | 8.1196 | 39.95
2022-05-03 05:00 | 44684.2083 | 0 | 8.683 | 39.95
2022-05-03 05:30 | 44684.2292 | 0 | 9.3026 | 39.95
2022-05-03 06:00 | 44684.25 | 0 | 10.5329 | 39.95
2022-05-03 06:30 | 44684.2708 | 0 | 11.51 | 39.95
2022-05-03 07:00 | 44684.2917 | 0 | 11.7521 | 39.95
2022-05-03 07:30 | 44684.3125 | 0 | 11.1659 | 39.95
2022-05-03 08:00 | 44684.3333 | 0 | 10.739 | 39.95
2022-05-03 08:30 | 44684.3542 | 0 | 10.3086 | 39.95
2022-05-03 09:00 | 44684.375 | 0 | 9.4365 | 39.95
2022-05-03 09:30 | 44684.3958 | 0 | 9.1216 | 39.95
2022-05-03 10:00 | 44684.4167 | 0 | 8.6644 | 39.95
2022-05-03 10:30 | 44684.4375 | 0 | 10.2932 | 39.95
2022-05-03 11:00 | 44684.4583 | 0 | 10.3681 | 39.95
2022-05-03 11:30 | 44684.4792 | 0 | 10.3774 | 39.95
2022-05-03 12:00 | 44684.5 | 0 | 10.3177 | 39.95
2022-05-03 12:30 | 44684.5208 | 0 | 11.2492 | 39.95
2022-05-03 13:00 | 44684.5417 | 0 | 11.1645 | 39.95
2022-05-03 13:30 | 44684.5625 | 0 | 11.931 | 39.95
2022-05-03 14:00 | 44684.5833 | 0 | 10.5009 | 39.95
2022-05-03 14:30 | 44684.6042 | 0 | 11.6583 | 39.95
2022-05-03 15:00 | 44684.625 | 0 | 12.0514 | 39.95
2022-05-03 15:30 | 44684.6458 | 0 | 12.8333 | 39.95
2022-05-03 16:00 | 44684.6667 | 0 | 12.6503 | 39.95
2022-05-03 16:30 | 44684.6875 | 0 | 13.4284 | 39.95
2022-05-03 17:00 | 44684.7083 | 0 | 13.5257 | 39.95
2022-05-03 17:30 | 44684.7292 | 0 | 14.196 | 39.95
2022-05-03 18:00 | 44684.75 | 0 | 14.2441 | 39.95
2022-05-03 18:30 | 44684.7708 | 0 | 14.2296 | 39.95
2022-05-03 19:00 | 44684.7917 | 0 | 13.6823 | 39.95
2022-05-03 19:30 | 44684.8125 | 0 | 13.5587 | 39.95
2022-05-03 20:00 | 44684.8333 | 0 | 13.1857 | 39.95
2022-05-03 20:30 | 44684.8542 | 0 | 12.7203 | 39.95
2022-05-03 21:00 | 44684.875 | 0 | 12.0739 | 39.95
2022-05-03 21:30 | 44684.8958 | 0 | 11.6595 | 39.95
2022-05-03 22:00 | 44684.9167 | 0 | 10.9762 | 39.95
2022-05-03 22:30 | 44684.9375 | 0 | 10.302 | 39.95
2022-05-03 23:00 | 44684.9583 | 0 | 9.7678 | 39.95
2022-05-03 23:30 | 44684.9792 | 0 | 9.3796 | 39.95
2022-05-04 | 44685 | 0 | 8.8471 | 39.95
2022-05-04 00:30 | 44685.0208 | 0 | 8.5199 | 39.95
2022-05-04 01:00 | 44685.0417 | 0 | 8.3301 | 39.95
2022-05-04 01:30 | 44685.0625 | 0 | 8.1207 | 39.95
2022-05-04 02:00 | 44685.0833 | 0 | 7.9716 | 39.95
2022-05-04 02:30 | 44685.1042 | 0 | 8.0134 | 39.95
2022-05-04 03:00 | 44685.125 | 0 | 7.8533 | 39.95
2022-05-04 03:30 | 44685.1458 | 0 | 7.9043 | 39.95
2022-05-04 04:00 | 44685.1667 | 0 | 8.2117 | 39.95
2022-05-04 04:30 | 44685.1875 | 0 | 8.6768 | 39.95
2022-05-04 05:00 | 44685.2083 | 0 | 9.3418 | 39.95
2022-05-04 05:30 | 44685.2292 | 0 | 9.8151 | 39.95
2022-05-04 06:00 | 44685.25 | 0 | 10.7634 | 39.95
2022-05-04 06:30 | 44685.2708 | 0 | 11.702 | 39.95
2022-05-04 07:00 | 44685.2917 | 0 | 12.1541 | 39.95
2022-05-04 07:30 | 44685.3125 | 0 | 11.304 | 39.95
2022-05-04 08:00 | 44685.3333 | 0 | 10.8707 | 39.95
2022-05-04 08:30 | 44685.3542 | 0 | 10.6968 | 39.95
2022-05-04 09:00 | 44685.375 | 0 | 10.5588 | 39.95
2022-05-04 09:30 | 44685.3958 | 0 | 10.7167 | 39.95
2022-05-04 10:00 | 44685.4167 | 0 | 10.005 | 39.95
2022-05-04 10:30 | 44685.4375 | 0 | 11.0316 | 39.95
2022-05-04 11:00 | 44685.4583 | 0 | 10.9423 | 39.95
2022-05-04 11:30 | 44685.4792 | 0 | 9.257 | 39.95
2022-05-04 12:00 | 44685.5 | 0 | 10.3741 | 39.95
2022-05-04 12:30 | 44685.5208 | 0 | 12.0231 | 39.95
2022-05-04 13:00 | 44685.5417 | 0 | 12.7784 | 39.95
2022-05-04 13:30 | 44685.5625 | 0 | 13.097 | 39.95
2022-05-04 14:00 | 44685.5833 | 0 | 12.9668 | 39.95
2022-05-04 14:30 | 44685.6042 | 0 | 12.1598 | 39.95
2022-05-04 15:00 | 44685.625 | 0 | 11.9986 | 39.95
2022-05-04 15:30 | 44685.6458 | 0 | 12.6098 | 39.95
2022-05-04 16:00 | 44685.6667 | 0 | 13.1253 | 39.95
2022-05-04 16:30 | 44685.6875 | 0 | 13.698 | 39.95
2022-05-04 17:00 | 44685.7083 | 0 | 13.9595 | 39.95
2022-05-04 17:30 | 44685.7292 | 0 | 14.4679 | 39.95
2022-05-04 18:00 | 44685.75 | 0 | 14.4845 | 39.95
2022-05-04 18:30 | 44685.7708 | 0 | 14.4884 | 39.95
2022-05-04 19:00 | 44685.7917 | 0 | 14.2338 | 39.95
2022-05-04 19:30 | 44685.8125 | 0 | 13.6925 | 39.95
2022-05-04 20:00 | 44685.8333 | 0 | 13.3096 | 39.95
2022-05-04 20:30 | 44685.8542 | 0 | 12.8047 | 39.95
2022-05-04 21:00 | 44685.875 | 0 | 12.3435 | 39.95
2022-05-04 21:30 | 44685.8958 | 0 | 11.913 | 39.95
2022-05-04 22:00 | 44685.9167 | 0 | 11.3065 | 39.95
2022-05-04 22:30 | 44685.9375 | 0 | 10.6372 | 39.95
2022-05-04 23:00 | 44685.9583 | 0 | 10.2556 | 39.95
2022-05-04 23:30 | 44685.9792 | 0 | 9.6874 | 39.95
2022-05-05 | 44686 | 0 | 9.2608 | 39.95
2022-05-05 00:30 | 44686.0208 | 0 | 8.9103 | 39.95
2022-05-05 01:00 | 44686.0417 | 0 | 8.7417 | 39.95
2022-05-05 01:30 | 44686.0625 | 0 | 8.448 | 39.95
2022-05-05 02:00 | 44686.0833 | 0 | 8.4217 | 39.95
2022-05-05 02:30 | 44686.1042 | 0 | 8.4143 | 39.95
2022-05-05 03:00 | 44686.125 | 0 | 8.3171 | 39.95
2022-05-05 03:30 | 44686.1458 | 0 | 8.4105 | 39.95
2022-05-05 04:00 | 44686.1667 | 0 | 8.6432 | 39.95
2022-05-05 04:30 | 44686.1875 | 0 | 8.9266 | 39.95
2022-05-05 05:00 | 44686.2083 | 0 | 9.6039 | 39.95
2022-05-05 05:30 | 44686.2292 | 0 | 10.0417 | 39.95
2022-05-05 06:00 | 44686.25 | 0 | 11.0405 | 39.95
2022-05-05 06:30 | 44686.2708 | 0 | 11.9337 | 39.95
2022-05-05 07:00 | 44686.2917 | 0 | 12.4013 | 39.95
2022-05-05 07:30 | 44686.3125 | 0 | 12.3684 | 39.95
2022-05-05 08:00 | 44686.3333 | 0 | 12.5228 | 39.95
2022-05-05 08:30 | 44686.3542 | 0 | 11.2927 | 39.95
2022-05-05 09:00 | 44686.375 | 0 | 10.5775 | 39.95
2022-05-05 09:30 | 44686.3958 | 0 | 11.0639 | 39.95
2022-05-05 10:00 | 44686.4167 | 0 | 11.0682 | 39.95
2022-05-05 10:30 | 44686.4375 | 0 | 11.4491 | 39.95
2022-05-05 11:00 | 44686.4583 | 0 | 11.7385 | 39.95
2022-05-05 11:30 | 44686.4792 | 0 | 12.1969 | 39.95
2022-05-05 12:00 | 44686.5 | 0 | 12.4132 | 39.95
2022-05-05 12:30 | 44686.5208 | 0 | 12.2912 | 39.95
2022-05-05 13:00 | 44686.5417 | 0 | 12.0375 | 39.95
2022-05-05 13:30 | 44686.5625 | 0 | 11.9002 | 39.95
2022-05-05 14:00 | 44686.5833 | 0 | 12.1346 | 39.95
2022-05-05 14:30 | 44686.6042 | 0 | 12.7746 | 39.95
2022-05-05 15:00 | 44686.625 | 0 | 13.1562 | 39.95
2022-05-05 15:30 | 44686.6458 | 0 | 13.8912 | 39.95
2022-05-05 16:00 | 44686.6667 | 0 | 14.3057 | 39.95
2022-05-05 16:30 | 44686.6875 | 0 | 14.8184 | 39.95
2022-05-05 17:00 | 44686.7083 | 0 | 14.9312 | 39.95
2022-05-05 17:30 | 44686.7292 | 0 | 15.3749 | 39.95
2022-05-05 18:00 | 44686.75 | 0 | 15.3676 | 39.95
2022-05-05 18:30 | 44686.7708 | 0 | 15.3018 | 39.95
2022-05-05 19:00 | 44686.7917 | 0 | 15.1999 | 39.95
2022-05-05 19:30 | 44686.8125 | 0 | 14.7749 | 39.95
2022-05-05 20:00 | 44686.8333 | 0 | 14.4016 | 39.95
2022-05-05 20:30 | 44686.8542 | 0 | 13.864 | 39.95
2022-05-05 21:00 | 44686.875 | 0 | 13.3432 | 39.95
2022-05-05 21:30 | 44686.8958 | 0 | 12.9685 | 39.95
2022-05-05 22:00 | 44686.9167 | 0 | 12.3355 | 39.95
2022-05-05 22:30 | 44686.9375 | 0 | 11.5916 | 39.95
2022-05-05 23:00 | 44686.9583 | 0 | 10.932 | 39.95
2022-05-05 23:30 | 44686.9792 | 0 | 10.5261 | 39.95
2022-05-06 | 44687 | 0 | 9.8027 | 39.95
2022-05-06 00:30 | 44687.0208 | 0 | 9.4086 | 39.95
2022-05-06 01:00 | 44687.0417 | 0 | 9.1273 | 39.95
2022-05-06 01:30 | 44687.0625 | 0 | 9.0541 | 39.95
2022-05-06 02:00 | 44687.0833 | 0 | 9.0177 | 39.95
2022-05-06 02:30 | 44687.1042 | 0 | 9.0001 | 39.95
2022-05-06 03:00 | 44687.125 | 0 | 8.9452 | 39.95
2022-05-06 03:30 | 44687.1458 | 0 | 9.0244 | 39.95
2022-05-06 04:00 | 44687.1667 | 0 | 9.1662 | 39.95
2022-05-06 04:30 | 44687.1875 | 0 | 9.5367 | 39.95
2022-05-06 05:00 | 44687.2083 | 0 | 10.1316 | 39.95
2022-05-06 05:30 | 44687.2292 | 0 | 10.6193 | 39.95
2022-05-06 06:00 | 44687.25 | 0 | 11.6154 | 39.95
2022-05-06 06:30 | 44687.2708 | 0 | 12.5715 | 39.95
2022-05-06 07:00 | 44687.2917 | 0 | 13.2246 | 39.95
2022-05-06 07:30 | 44687.3125 | 0 | 13.734 | 39.95
2022-05-06 08:00 | 44687.3333 | 0 | 14.2827 | 39.95
2022-05-06 08:30 | 44687.3542 | 0 | 13.76 | 39.95
2022-05-06 09:00 | 44687.375 | 0 | 13.1007 | 39.95
2022-05-06 09:30 | 44687.3958 | 0 | 12.86 | 39.95
2022-05-06 10:00 | 44687.4167 | 0 | 11.7219 | 39.95
2022-05-06 10:30 | 44687.4375 | 0 | 11.2997 | 39.95
2022-05-06 11:00 | 44687.4583 | 0 | 11.6679 | 39.95
2022-05-06 11:30 | 44687.4792 | 0 | 11.4547 | 39.95
2022-05-06 12:00 | 44687.5 | 0 | 11.667 | 39.95
2022-05-06 12:30 | 44687.5208 | 0 | 12.1879 | 39.95
2022-05-06 13:00 | 44687.5417 | 0 | 12.1052 | 39.95
2022-05-06 13:30 | 44687.5625 | 0 | 12.6765 | 39.95
2022-05-06 14:00 | 44687.5833 | 0 | 12.6556 | 39.95
2022-05-06 14:30 | 44687.6042 | 0 | 14.0236 | 39.95
2022-05-06 15:00 | 44687.625 | 0 | 14.1365 | 39.95
2022-05-06 15:30 | 44687.6458 | 0 | 14.8022 | 39.95
2022-05-06 16:00 | 44687.6667 | 0 | 14.6184 | 39.95
2022-05-06 16:30 | 44687.6875 | 0 | 14.7867 | 39.95
2022-05-06 17:00 | 44687.7083 | 0 | 15.0103 | 39.95
2022-05-06 17:30 | 44687.7292 | 0 | 15.1415 | 39.95
2022-05-06 18:00 | 44687.75 | 0 | 14.864 | 39.95
2022-05-06 18:30 | 44687.7708 | 0 | 14.8638 | 39.95
2022-05-06 19:00 | 44687.7917 | 0 | 14.6278 | 39.95
2022-05-06 19:30 | 44687.8125 | 0 | 14.1625 | 39.95
2022-05-06 20:00 | 44687.8333 | 0 | 13.9279 | 39.95
2022-05-06 20:30 | 44687.8542 | 0 | 13.5311 | 39.95
2022-05-06 21:00 | 44687.875 | 0 | 13.025 | 39.95
2022-05-06 21:30 | 44687.8958 | 0 | 12.6857 | 39.95
2022-05-06 22:00 | 44687.9167 | 0 | 12.2203 | 39.95
2022-05-06 22:30 | 44687.9375 | 0 | 11.3324 | 39.95
2022-05-06 23:00 | 44687.9583 | 0 | 10.8807 | 39.95
2022-05-06 23:30 | 44687.9792 | 0 | 10.3349 | 39.95
2022-05-07 | 44688 | 0 | 9.7339 | 39.95
2022-05-07 00:30 | 44688.0208 | 0 | 9.3518 | 39.95
2022-05-07 01:00 | 44688.0417 | 0 | 9.2462 | 39.95
2022-05-07 01:30 | 44688.0625 | 0 | 8.9722 | 39.95
2022-05-07 02:00 | 44688.0833 | 0 | 8.7065 | 39.95
2022-05-07 02:30 | 44688.1042 | 0 | 8.673 | 39.95
2022-05-07 03:00 | 44688.125 | 0 | 8.533 | 39.95
2022-05-07 03:30 | 44688.1458 | 0 | 8.5162 | 39.95
2022-05-07 04:00 | 44688.1667 | 0 | 8.5671 | 39.95
2022-05-07 04:30 | 44688.1875 | 0 | 8.6678 | 39.95
2022-05-07 05:00 | 44688.2083 | 0 | 8.7721 | 39.95
2022-05-07 05:30 | 44688.2292 | 0 | 9.0096 | 39.95
2022-05-07 06:00 | 44688.25 | 0 | 9.3609 | 39.95
2022-05-07 06:30 | 44688.2708 | 0 | 9.5293 | 39.95
2022-05-07 07:00 | 44688.2917 | 0 | 9.8879 | 39.95
2022-05-07 07:30 | 44688.3125 | 0 | 9.9621 | 39.95
2022-05-07 08:00 | 44688.3333 | 0 | 10.2075 | 39.95
2022-05-07 08:30 | 44688.3542 | 0 | 9.8562 | 39.95
2022-05-07 09:00 | 44688.375 | 0 | 10.5038 | 39.95
2022-05-07 09:30 | 44688.3958 | 0 | 10.4301 | 39.95
2022-05-07 10:00 | 44688.4167 | 0 | 9.4263 | 39.95
2022-05-07 10:30 | 44688.4375 | 0 | 9.4823 | 39.95
2022-05-07 11:00 | 44688.4583 | 0 | 8.8416 | 39.95
2022-05-07 11:30 | 44688.4792 | 0 | 9.0593 | 39.95
2022-05-07 12:00 | 44688.5 | 0 | 8.601 | 39.95
2022-05-07 12:30 | 44688.5208 | 0 | 9.3059 | 39.95
2022-05-07 13:00 | 44688.5417 | 0 | 10.9482 | 39.95
2022-05-07 13:30 | 44688.5625 | 0 | 11.4229 | 39.95
2022-05-07 14:00 | 44688.5833 | 0 | 11.7001 | 39.95
2022-05-07 14:30 | 44688.6042 | 0 | 12.0352 | 39.95
2022-05-07 15:00 | 44688.625 | 0 | 11.9069 | 39.95
2022-05-07 15:30 | 44688.6458 | 0 | 11.8204 | 39.95
2022-05-07 16:00 | 44688.6667 | 0 | 12.0194 | 39.95
2022-05-07 16:30 | 44688.6875 | 0 | 12.316 | 39.95
2022-05-07 17:00 | 44688.7083 | 0 | 12.5914 | 39.95
2022-05-07 17:30 | 44688.7292 | 0 | 12.7384 | 39.95
2022-05-07 18:00 | 44688.75 | 0 | 12.429 | 39.95
2022-05-07 18:30 | 44688.7708 | 0 | 12.2739 | 39.95
2022-05-07 19:00 | 44688.7917 | 0 | 12.1399 | 39.95
2022-05-07 19:30 | 44688.8125 | 0 | 11.8931 | 39.95
2022-05-07 20:00 | 44688.8333 | 0 | 11.6474 | 39.95
2022-05-07 20:30 | 44688.8542 | 0 | 11.2669 | 39.95
2022-05-07 21:00 | 44688.875 | 0 | 10.8288 | 39.95
2022-05-07 21:30 | 44688.8958 | 0 | 10.4858 | 39.95
2022-05-07 22:00 | 44688.9167 | 0 | 10.1729 | 39.95
2022-05-07 22:30 | 44688.9375 | 0 | 9.6415 | 39.95
2022-05-07 23:00 | 44688.9583 | 0 | 9.2413 | 39.95
2022-05-07 23:30 | 44688.9792 | 0 | 8.7672 | 39.95
2022-05-08 | 44689 | 0 | 8.3061 | 39.95
2022-05-08 00:30 | 44689.0208 | 0 | 7.9528 | 39.95
2022-05-08 01:00 | 44689.0417 | 0 | 7.9481 | 39.95
2022-05-08 01:30 | 44689.0625 | 0 | 7.5936 | 39.95
2022-05-08 02:00 | 44689.0833 | 0 | 7.4225 | 39.95
2022-05-08 02:30 | 44689.1042 | 0 | 7.3984 | 39.95
2022-05-08 03:00 | 44689.125 | 0 | 7.3779 | 39.95
2022-05-08 03:30 | 44689.1458 | 0 | 7.2734 | 39.95
2022-05-08 04:00 | 44689.1667 | 0 | 7.2679 | 39.95
2022-05-08 04:30 | 44689.1875 | 0 | 7.1186 | 39.95
2022-05-08 05:00 | 44689.2083 | 0 | 7.2441 | 39.95
2022-05-08 05:30 | 44689.2292 | 0 | 7.4196 | 39.95
2022-05-08 06:00 | 44689.25 | 0 | 7.6712 | 39.95
2022-05-08 06:30 | 44689.2708 | 0 | 8.0503 | 39.95
2022-05-08 07:00 | 44689.2917 | 0 | 7.8497 | 39.95
2022-05-08 07:30 | 44689.3125 | 0 | 8.7497 | 39.95
2022-05-08 08:00 | 44689.3333 | 0 | 8.6685 | 39.95
2022-05-08 08:30 | 44689.3542 | 0 | 9.5628 | 39.95
2022-05-08 09:00 | 44689.375 | 0 | 9.8191 | 39.95
2022-05-08 09:30 | 44689.3958 | 0 | 9.4921 | 39.95
2022-05-08 10:00 | 44689.4167 | 0 | 10.5797 | 39.95
2022-05-08 10:30 | 44689.4375 | 0 | 10.319 | 39.95
2022-05-08 11:00 | 44689.4583 | 0 | 8.695 | 39.95
2022-05-08 11:30 | 44689.4792 | 0 | 7.651 | 39.95
2022-05-08 12:00 | 44689.5 | 0 | 7.6674 | 39.95
2022-05-08 12:30 | 44689.5208 | 0 | 8.2592 | 39.95
2022-05-08 13:00 | 44689.5417 | 0 | 9.4232 | 39.95
2022-05-08 13:30 | 44689.5625 | 0 | 9.8827 | 39.95
2022-05-08 14:00 | 44689.5833 | 0 | 9.1273 | 39.95
2022-05-08 14:30 | 44689.6042 | 0 | 8.6607 | 39.95
2022-05-08 15:00 | 44689.625 | 0 | 9.5576 | 39.95
2022-05-08 15:30 | 44689.6458 | 0 | 10.3195 | 39.95
2022-05-08 16:00 | 44689.6667 | 0 | 10.6436 | 39.95
2022-05-08 16:30 | 44689.6875 | 0 | 10.9862 | 39.95
2022-05-08 17:00 | 44689.7083 | 0 | 11.3627 | 39.95
2022-05-08 17:30 | 44689.7292 | 0 | 12.0043 | 39.95
2022-05-08 18:00 | 44689.75 | 0 | 12.0717 | 39.95
2022-05-08 18:30 | 44689.7708 | 0 | 11.9703 | 39.95
2022-05-08 19:00 | 44689.7917 | 0 | 11.7784 | 39.95
2022-05-08 19:30 | 44689.8125 | 0 | 11.334 | 39.95
2022-05-08 20:00 | 44689.8333 | 0 | 11.2159 | 39.95
2022-05-08 20:30 | 44689.8542 | 0 | 10.7382 | 39.95
2022-05-08 21:00 | 44689.875 | 0 | 10.3162 | 39.95
2022-05-08 21:30 | 44689.8958 | 0 | 9.9909 | 39.95
2022-05-08 22:00 | 44689.9167 | 0 | 9.5093 | 39.95
2022-05-08 22:30 | 44689.9375 | 0 | 8.927 | 39.95
2022-05-08 23:00 | 44689.9583 | 0 | 8.5274 | 39.95
2022-05-08 23:30 | 44689.9792 | 0 | 8.0583 | 39.95
2022-05-09 | 44690 | 0 | 7.8402 | 39.95
2022-05-09 00:30 | 44690.0208 | 0 | 7.6017 | 39.95
2022-05-09 01:00 | 44690.0417 | 0 | 7.6142 | 39.95
2022-05-09 01:30 | 44690.0625 | 0 | 7.4149 | 39.95
2022-05-09 02:00 | 44690.0833 | 0 | 7.3149 | 39.95
2022-05-09 02:30 | 44690.1042 | 0 | 7.5528 | 39.95
2022-05-09 03:00 | 44690.125 | 0 | 7.2356 | 39.95
2022-05-09 03:30 | 44690.1458 | 0 | 7.4193 | 39.95
2022-05-09 04:00 | 44690.1667 | 0 | 7.6716 | 39.95
2022-05-09 04:30 | 44690.1875 | 0 | 8.1774 | 39.95
2022-05-09 05:00 | 44690.2083 | 0 | 8.9788 | 39.95
2022-05-09 05:30 | 44690.2292 | 0 | 9.7217 | 39.95
2022-05-09 06:00 | 44690.25 | 0 | 10.6696 | 39.95
2022-05-09 06:30 | 44690.2708 | 0 | 11.7585 | 39.95
2022-05-09 07:00 | 44690.2917 | 0 | 12.7956 | 39.95
2022-05-09 07:30 | 44690.3125 | 0 | 12.7244 | 39.95
2022-05-09 08:00 | 44690.3333 | 0 | 13.1268 | 39.95
2022-05-09 08:30 | 44690.3542 | 0 | 13.5548 | 39.95
2022-05-09 09:00 | 44690.375 | 0 | 13.7235 | 39.95
2022-05-09 09:30 | 44690.3958 | 0 | 13.2855 | 39.95
2022-05-09 10:00 | 44690.4167 | 0 | 13.3367 | 39.95
2022-05-09 10:30 | 44690.4375 | 0 | 13.5294 | 39.95
2022-05-09 11:00 | 44690.4583 | 0 | 13.2242 | 39.95
2022-05-09 11:30 | 44690.4792 | 0 | 12.6899 | 39.95
2022-05-09 12:00 | 44690.5 | 0 | 12.3288 | 39.95
2022-05-09 12:30 | 44690.5208 | 0 | 12.4159 | 39.95
2022-05-09 13:00 | 44690.5417 | 0 | 13.2155 | 39.95
2022-05-09 13:30 | 44690.5625 | 0 | 13.072 | 39.95
2022-05-09 14:00 | 44690.5833 | 0 | 13.3268 | 39.95
2022-05-09 14:30 | 44690.6042 | 0 | 13.1437 | 39.95
2022-05-09 15:00 | 44690.625 | 0 | 12.9544 | 39.95
2022-05-09 15:30 | 44690.6458 | 0 | 12.9032 | 39.95
2022-05-09 16:00 | 44690.6667 | 0 | 12.9617 | 39.95
2022-05-09 16:30 | 44690.6875 | 0 | 13.5665 | 39.95
2022-05-09 17:00 | 44690.7083 | 0 | 14.2255 | 39.95
2022-05-09 17:30 | 44690.7292 | 0 | 14.733 | 39.95
2022-05-09 18:00 | 44690.75 | 0 | 14.9264 | 39.95
2022-05-09 18:30 | 44690.7708 | 0 | 14.8003 | 39.95
2022-05-09 19:00 | 44690.7917 | 0 | 14.3413 | 39.95
2022-05-09 19:30 | 44690.8125 | 0 | 13.7916 | 39.95
2022-05-09 20:00 | 44690.8333 | 0 | 13.5627 | 39.95
2022-05-09 20:30 | 44690.8542 | 0 | 12.8258 | 39.95
2022-05-09 21:00 | 44690.875 | 0 | 12.4146 | 39.95
2022-05-09 21:30 | 44690.8958 | 0 | 11.8012 | 39.95
2022-05-09 22:00 | 44690.9167 | 0 | 11.0204 | 39.95
2022-05-09 22:30 | 44690.9375 | 0 | 10.2768 | 39.95
2022-05-09 23:00 | 44690.9583 | 0 | 9.7534 | 39.95
2022-05-09 23:30 | 44690.9792 | 0 | 9.3325 | 39.95
2022-05-10 | 44691 | 0 | 8.678 | 39.95
2022-05-10 00:30 | 44691.0208 | 0 | 8.2838 | 39.95
2022-05-10 01:00 | 44691.0417 | 0 | 8.1679 | 39.95
2022-05-10 01:30 | 44691.0625 | 0 | 8.1122 | 39.95
2022-05-10 02:00 | 44691.0833 | 0 | 8.0339 | 39.95
2022-05-10 02:30 | 44691.1042 | 0 | 7.9358 | 39.95
2022-05-10 03:00 | 44691.125 | 0 | 7.9395 | 39.95
2022-05-10 03:30 | 44691.1458 | 0 | 7.9834 | 39.95
2022-05-10 04:00 | 44691.1667 | 0 | 8.2972 | 39.95
2022-05-10 04:30 | 44691.1875 | 0 | 8.5611 | 39.95
2022-05-10 05:00 | 44691.2083 | 0 | 9.2572 | 39.95
2022-05-10 05:30 | 44691.2292 | 0 | 9.8693 | 39.95
2022-05-10 06:00 | 44691.25 | 0 | 10.9747 | 39.95
2022-05-10 06:30 | 44691.2708 | 0 | 12.1267 | 39.95
2022-05-10 07:00 | 44691.2917 | 0 | 12.968 | 39.95
2022-05-10 07:30 | 44691.3125 | 0 | 12.9744 | 39.95
2022-05-10 08:00 | 44691.3333 | 0 | 12.9043 | 39.95
2022-05-10 08:30 | 44691.3542 | 0 | 12.8604 | 39.95
2022-05-10 09:00 | 44691.375 | 0 | 12.3387 | 39.95
2022-05-10 09:30 | 44691.3958 | 0 | 12.1945 | 39.95
2022-05-10 10:00 | 44691.4167 | 0 | 11.595 | 39.95
2022-05-10 10:30 | 44691.4375 | 0 | 11.7973 | 39.95
2022-05-10 11:00 | 44691.4583 | 0 | 12.3492 | 39.95
2022-05-10 11:30 | 44691.4792 | 0 | 12.3455 | 39.95
2022-05-10 12:00 | 44691.5 | 0 | 11.1061 | 39.95
2022-05-10 12:30 | 44691.5208 | 0 | 11.8349 | 39.95
2022-05-10 13:00 | 44691.5417 | 0 | 12.2641 | 39.95
2022-05-10 13:30 | 44691.5625 | 0 | 13.0278 | 39.95
2022-05-10 14:00 | 44691.5833 | 0 | 12.9621 | 39.95
2022-05-10 14:30 | 44691.6042 | 0 | 12.5657 | 39.95
2022-05-10 15:00 | 44691.625 | 0 | 12.5409 | 39.95
2022-05-10 15:30 | 44691.6458 | 0 | 12.962 | 39.95
2022-05-10 16:00 | 44691.6667 | 0 | 13.2046 | 39.95
2022-05-10 16:30 | 44691.6875 | 0 | 13.6205 | 39.95
2022-05-10 17:00 | 44691.7083 | 0 | 14.2047 | 39.95
2022-05-10 17:30 | 44691.7292 | 0 | 14.556 | 39.95
2022-05-10 18:00 | 44691.75 | 0 | 14.6456 | 39.95
2022-05-10 18:30 | 44691.7708 | 0 | 14.5039 | 39.95
2022-05-10 19:00 | 44691.7917 | 0 | 14.1106 | 39.95
2022-05-10 19:30 | 44691.8125 | 0 | 13.8465 | 39.95
2022-05-10 20:00 | 44691.8333 | 0 | 13.6651 | 39.95
2022-05-10 20:30 | 44691.8542 | 0 | 13.0074 | 39.95
2022-05-10 21:00 | 44691.875 | 0 | 12.5622 | 39.95
2022-05-10 21:30 | 44691.8958 | 0 | 12.1046 | 39.95
2022-05-10 22:00 | 44691.9167 | 0 | 11.4623 | 39.95
2022-05-10 22:30 | 44691.9375 | 0 | 10.6347 | 39.95
2022-05-10 23:00 | 44691.9583 | 0 | 10.1435 | 39.95
2022-05-10 23:30 | 44691.9792 | 0 | 9.8426 | 39.95
2022-05-11 | 44692 | 0 | 9.2016 | 39.95
2022-05-11 00:30 | 44692.0208 | 0 | 8.738 | 39.95
2022-05-11 01:00 | 44692.0417 | 0 | 8.522 | 39.95
2022-05-11 01:30 | 44692.0625 | 0 | 8.3747 | 39.95
2022-05-11 02:00 | 44692.0833 | 0 | 8.3927 | 39.95
2022-05-11 02:30 | 44692.1042 | 0 | 8.3473 | 39.95
2022-05-11 03:00 | 44692.125 | 0 | 8.1783 | 39.95
2022-05-11 03:30 | 44692.1458 | 0 | 8.3 | 39.95
2022-05-11 04:00 | 44692.1667 | 0 | 8.7011 | 39.95
2022-05-11 04:30 | 44692.1875 | 0 | 9.0271 | 39.95
2022-05-11 05:00 | 44692.2083 | 0 | 9.5888 | 39.95
2022-05-11 05:30 | 44692.2292 | 0 | 10.2691 | 39.95
2022-05-11 06:00 | 44692.25 | 0 | 11.4929 | 39.95
2022-05-11 06:30 | 44692.2708 | 0 | 12.34 | 39.95
2022-05-11 07:00 | 44692.2917 | 0 | 13.172 | 39.95
2022-05-11 07:30 | 44692.3125 | 0 | 13.3716 | 39.95
2022-05-11 08:00 | 44692.3333 | 0 | 13.788 | 39.95
2022-05-11 08:30 | 44692.3542 | 0 | 13.7416 | 39.95
2022-05-11 09:00 | 44692.375 | 0 | 13.8487 | 39.95
2022-05-11 09:30 | 44692.3958 | 0 | 13.1942 | 39.95
2022-05-11 10:00 | 44692.4167 | 0 | 13.5085 | 39.95
2022-05-11 10:30 | 44692.4375 | 0 | 13.4457 | 39.95
2022-05-11 11:00 | 44692.4583 | 0 | 13.1599 | 39.95
2022-05-11 11:30 | 44692.4792 | 0 | 12.9929 | 39.95
2022-05-11 12:00 | 44692.5 | 0 | 13.4377 | 39.95
2022-05-11 12:30 | 44692.5208 | 0 | 13.0774 | 39.95
2022-05-11 13:00 | 44692.5417 | 0 | 13.2193 | 39.95
2022-05-11 13:30 | 44692.5625 | 0 | 13.6622 | 39.95
2022-05-11 14:00 | 44692.5833 | 0 | 13.9435 | 39.95
2022-05-11 14:30 | 44692.6042 | 0 | 13.7861 | 39.95
2022-05-11 15:00 | 44692.625 | 0 | 13.6306 | 39.95
2022-05-11 15:30 | 44692.6458 | 0 | 13.8848 | 39.95
2022-05-11 16:00 | 44692.6667 | 0 | 14.0723 | 39.95
2022-05-11 16:30 | 44692.6875 | 0 | 14.3079 | 39.95
2022-05-11 17:00 | 44692.7083 | 0 | 14.8059 | 39.95
2022-05-11 17:30 | 44692.7292 | 0 | 15.2698 | 39.95
2022-05-11 18:00 | 44692.75 | 0 | 14.7227 | 39.95
2022-05-11 18:30 | 44692.7708 | 0 | 14.5483 | 39.95
2022-05-11 19:00 | 44692.7917 | 0 | 14.0882 | 39.95
2022-05-11 19:30 | 44692.8125 | 0 | 13.8325 | 39.95
2022-05-11 20:00 | 44692.8333 | 0 | 13.452 | 39.95
2022-05-11 20:30 | 44692.8542 | 0 | 12.8932 | 39.95
2022-05-11 21:00 | 44692.875 | 0 | 12.2299 | 39.95
2022-05-11 21:30 | 44692.8958 | 0 | 11.8335 | 39.95
2022-05-11 22:00 | 44692.9167 | 0 | 11.4554 | 39.95
2022-05-11 22:30 | 44692.9375 | 0 | 10.6089 | 39.95
2022-05-11 23:00 | 44692.9583 | 0 | 10.0718 | 39.95
2022-05-11 23:30 | 44692.9792 | 0 | 9.6182 | 39.95
2022-05-12 | 44693 | 0 | 9.2084 | 39.95
2022-05-12 00:30 | 44693.0208 | 0 | 8.7891 | 39.95
2022-05-12 01:00 | 44693.0417 | 0 | 8.5414 | 39.95
2022-05-12 01:30 | 44693.0625 | 0 | 8.3115 | 39.95
2022-05-12 02:00 | 44693.0833 | 0 | 8.3442 | 39.95
2022-05-12 02:30 | 44693.1042 | 0 | 8.2575 | 39.95
2022-05-12 03:00 | 44693.125 | 0 | 8.1968 | 39.95
2022-05-12 03:30 | 44693.1458 | 0 | 8.2805 | 39.95
2022-05-12 04:00 | 44693.1667 | 0 | 8.6304 | 39.95
2022-05-12 04:30 | 44693.1875 | 0 | 8.8566 | 39.95
2022-05-12 05:00 | 44693.2083 | 0 | 9.5063 | 39.95
2022-05-12 05:30 | 44693.2292 | 0 | 10.0829 | 39.95
2022-05-12 06:00 | 44693.25 | 0 | 11.0676 | 39.95
2022-05-12 06:30 | 44693.2708 | 0 | 12.1966 | 39.95
2022-05-12 07:00 | 44693.2917 | 0 | 13.2002 | 39.95
2022-05-12 07:30 | 44693.3125 | 0 | 13.4577 | 39.95
2022-05-12 08:00 | 44693.3333 | 0 | 13.4975 | 39.95
2022-05-12 08:30 | 44693.3542 | 0 | 13.824 | 39.95
2022-05-12 09:00 | 44693.375 | 0 | 13.8141 | 39.95
2022-05-12 09:30 | 44693.3958 | 0 | 13.6577 | 39.95
2022-05-12 10:00 | 44693.4167 | 0 | 13.2406 | 39.95
2022-05-12 10:30 | 44693.4375 | 0 | 13.8885 | 39.95
2022-05-12 11:00 | 44693.4583 | 0 | 14.3158 | 39.95
2022-05-12 11:30 | 44693.4792 | 0 | 13.8554 | 39.95
2022-05-12 12:00 | 44693.5 | 0 | 12.8674 | 39.95
2022-05-12 12:30 | 44693.5208 | 0 | 12.92 | 39.95
2022-05-12 13:00 | 44693.5417 | 0 | 12.6052 | 39.95
2022-05-12 13:30 | 44693.5625 | 0 | 13.7833 | 39.95
2022-05-12 14:00 | 44693.5833 | 0 | 13.9413 | 39.95
2022-05-12 14:30 | 44693.6042 | 0 | 13.1127 | 39.95
2022-05-12 15:00 | 44693.625 | 0 | 13.8417 | 39.95
2022-05-12 15:30 | 44693.6458 | 0 | 14.1238 | 39.95
2022-05-12 16:00 | 44693.6667 | 0 | 14.1492 | 39.95
2022-05-12 16:30 | 44693.6875 | 0 | 13.8937 | 39.95
2022-05-12 17:00 | 44693.7083 | 0 | 14.1566 | 39.95
2022-05-12 17:30 | 44693.7292 | 0 | 14.8368 | 39.95
2022-05-12 18:00 | 44693.75 | 0 | 14.7026 | 39.95
2022-05-12 18:30 | 44693.7708 | 0 | 14.6542 | 39.95
2022-05-12 19:00 | 44693.7917 | 0 | 14.1827 | 39.95
2022-05-12 19:30 | 44693.8125 | 0 | 13.8618 | 39.95
2022-05-12 20:00 | 44693.8333 | 0 | 13.6381 | 39.95
2022-05-12 20:30 | 44693.8542 | 0 | 13.2197 | 39.95
2022-05-12 21:00 | 44693.875 | 0 | 12.6907 | 39.95
2022-05-12 21:30 | 44693.8958 | 0 | 12.4777 | 39.95
2022-05-12 22:00 | 44693.9167 | 0 | 11.7773 | 39.95
2022-05-12 22:30 | 44693.9375 | 0 | 11.0344 | 39.95
2022-05-12 23:00 | 44693.9583 | 0 | 10.5209 | 39.95
2022-05-12 23:30 | 44693.9792 | 0 | 10.1472 | 39.95
2022-05-13 | 44694 | 0 | 9.6504 | 39.95
2022-05-13 00:30 | 44694.0208 | 0 | 9.2857 | 39.95
2022-05-13 01:00 | 44694.0417 | 0 | 9.0192 | 39.95
2022-05-13 01:30 | 44694.0625 | 0 | 8.8496 | 39.95
2022-05-13 02:00 | 44694.0833 | 0 | 8.707 | 39.95
2022-05-13 02:30 | 44694.1042 | 0 | 8.7728 | 39.95
2022-05-13 03:00 | 44694.125 | 0 | 8.6392 | 39.95
2022-05-13 03:30 | 44694.1458 | 0 | 8.6601 | 39.95
2022-05-13 04:00 | 44694.1667 | 0 | 8.9309 | 39.95
2022-05-13 04:30 | 44694.1875 | 0 | 9.3348 | 39.95
2022-05-13 05:00 | 44694.2083 | 0 | 9.9425 | 39.95
2022-05-13 05:30 | 44694.2292 | 0 | 10.4254 | 39.95
2022-05-13 06:00 | 44694.25 | 0 | 11.5393 | 39.95
2022-05-13 06:30 | 44694.2708 | 0 | 12.5367 | 39.95
2022-05-13 07:00 | 44694.2917 | 0 | 13.5647 | 39.95
2022-05-13 07:30 | 44694.3125 | 0 | 13.8831 | 39.95
2022-05-13 08:00 | 44694.3333 | 0 | 14.2049 | 39.95
2022-05-13 08:30 | 44694.3542 | 0 | 14.5823 | 39.95
2022-05-13 09:00 | 44694.375 | 0 | 14.4374 | 39.95
2022-05-13 09:30 | 44694.3958 | 0 | 14.4876 | 39.95
2022-05-13 10:00 | 44694.4167 | 0 | 14.1821 | 39.95
2022-05-13 10:30 | 44694.4375 | 0 | 13.4426 | 39.95
2022-05-13 11:00 | 44694.4583 | 0 | 13.6954 | 39.95
2022-05-13 11:30 | 44694.4792 | 0 | 13.9498 | 39.95
2022-05-13 12:00 | 44694.5 | 0 | 13.7493 | 39.95
2022-05-13 12:30 | 44694.5208 | 0 | 14.1937 | 39.95
2022-05-13 13:00 | 44694.5417 | 0 | 13.8056 | 39.95
2022-05-13 13:30 | 44694.5625 | 0 | 13.8726 | 39.95
2022-05-13 14:00 | 44694.5833 | 0 | 13.64 | 39.95
2022-05-13 14:30 | 44694.6042 | 0 | 13.3692 | 39.95
2022-05-13 15:00 | 44694.625 | 0 | 13.2892 | 39.95
2022-05-13 15:30 | 44694.6458 | 0 | 13.4401 | 39.95
2022-05-13 16:00 | 44694.6667 | 0 | 13.8532 | 39.95
2022-05-13 16:30 | 44694.6875 | 0 | 14.0751 | 39.95
2022-05-13 17:00 | 44694.7083 | 0 | 14.2208 | 39.95
2022-05-13 17:30 | 44694.7292 | 0 | 14.4208 | 39.95
2022-05-13 18:00 | 44694.75 | 0 | 14.3021 | 39.95
2022-05-13 18:30 | 44694.7708 | 0 | 13.8109 | 39.95
2022-05-13 19:00 | 44694.7917 | 0 | 13.8531 | 39.95
2022-05-13 19:30 | 44694.8125 | 0 | 13.4624 | 39.95
2022-05-13 20:00 | 44694.8333 | 0 | 13.3308 | 39.95
2022-05-13 20:30 | 44694.8542 | 0 | 12.9744 | 39.95
2022-05-13 21:00 | 44694.875 | 0 | 12.5257 | 39.95
2022-05-13 21:30 | 44694.8958 | 0 | 12.068 | 39.95
2022-05-13 22:00 | 44694.9167 | 0 | 11.5747 | 39.95
2022-05-13 22:30 | 44694.9375 | 0 | 10.9878 | 39.95
2022-05-13 23:00 | 44694.9583 | 0 | 10.448 | 39.95
2022-05-13 23:30 | 44694.9792 | 0 | 9.9486 | 39.95
2022-05-14 | 44695 | 0 | 9.3808 | 39.95
2022-05-14 00:30 | 44695.0208 | 0 | 9.0889 | 39.95
2022-05-14 01:00 | 44695.0417 | 0 | 8.7894 | 39.95
2022-05-14 01:30 | 44695.0625 | 0 | 8.6683 | 39.95
2022-05-14 02:00 | 44695.0833 | 0 | 8.442 | 39.95
2022-05-14 02:30 | 44695.1042 | 0 | 8.328 | 39.95
2022-05-14 03:00 | 44695.125 | 0 | 8.3305 | 39.95
2022-05-14 03:30 | 44695.1458 | 0 | 8.3791 | 39.95
2022-05-14 04:00 | 44695.1667 | 0 | 8.2587 | 39.95
2022-05-14 04:30 | 44695.1875 | 0 | 8.3207 | 39.95
2022-05-14 05:00 | 44695.2083 | 0 | 8.5657 | 39.95
2022-05-14 05:30 | 44695.2292 | 0 | 8.6576 | 39.95
2022-05-14 06:00 | 44695.25 | 0 | 8.9976 | 39.95
2022-05-14 06:30 | 44695.2708 | 0 | 9.4031 | 39.95
2022-05-14 07:00 | 44695.2917 | 0 | 10.1592 | 39.95
2022-05-14 07:30 | 44695.3125 | 0 | 10.3211 | 39.95
2022-05-14 08:00 | 44695.3333 | 0 | 11.0977 | 39.95
2022-05-14 08:30 | 44695.3542 | 0 | 11.2957 | 39.95
2022-05-14 09:00 | 44695.375 | 0 | 11.3548 | 39.95
2022-05-14 09:30 | 44695.3958 | 0 | 11.151 | 39.95
2022-05-14 10:00 | 44695.4167 | 0 | 10.9362 | 39.95
2022-05-14 10:30 | 44695.4375 | 0 | 10.8608 | 39.95
2022-05-14 11:00 | 44695.4583 | 0 | 11.5278 | 39.95
2022-05-14 11:30 | 44695.4792 | 0 | 11.5486 | 39.95
2022-05-14 12:00 | 44695.5 | 0 | 11.1666 | 39.95
2022-05-14 12:30 | 44695.5208 | 0 | 11.3078 | 39.95
2022-05-14 13:00 | 44695.5417 | 0 | 11.1726 | 39.95
2022-05-14 13:30 | 44695.5625 | 0 | 11.3575 | 39.95
2022-05-14 14:00 | 44695.5833 | 0 | 11.5669 | 39.95
2022-05-14 14:30 | 44695.6042 | 0 | 11.5632 | 39.95
2022-05-14 15:00 | 44695.625 | 0 | 11.7176 | 39.95
2022-05-14 15:30 | 44695.6458 | 0 | 11.6948 | 39.95
2022-05-14 16:00 | 44695.6667 | 0 | 12.071 | 39.95
2022-05-14 16:30 | 44695.6875 | 0 | 12.2873 | 39.95
2022-05-14 17:00 | 44695.7083 | 0 | 12.6879 | 39.95
2022-05-14 17:30 | 44695.7292 | 0 | 12.9233 | 39.95
2022-05-14 18:00 | 44695.75 | 0 | 12.9485 | 39.95
2022-05-14 18:30 | 44695.7708 | 0 | 12.7934 | 39.95
2022-05-14 19:00 | 44695.7917 | 0 | 12.4501 | 39.95
2022-05-14 19:30 | 44695.8125 | 0 | 12.1357 | 39.95
2022-05-14 20:00 | 44695.8333 | 0 | 12.0878 | 39.95
2022-05-14 20:30 | 44695.8542 | 0 | 11.5562 | 39.95
2022-05-14 21:00 | 44695.875 | 0 | 11.2869 | 39.95
2022-05-14 21:30 | 44695.8958 | 0 | 10.9621 | 39.95
2022-05-14 22:00 | 44695.9167 | 0 | 10.707 | 39.95
2022-05-14 22:30 | 44695.9375 | 0 | 10.1888 | 39.95
2022-05-14 23:00 | 44695.9583 | 0 | 9.8576 | 39.95
2022-05-14 23:30 | 44695.9792 | 0 | 9.3803 | 39.95
2022-05-15 | 44696 | 0 | 8.8533 | 39.95
2022-05-15 00:30 | 44696.0208 | 0 | 8.5506 | 39.95
2022-05-15 01:00 | 44696.0417 | 0 | 8.3308 | 39.95
2022-05-15 01:30 | 44696.0625 | 0 | 8.2603 | 39.95
2022-05-15 02:00 | 44696.0833 | 0 | 8.1596 | 39.95
2022-05-15 02:30 | 44696.1042 | 0 | 8.0379 | 39.95
2022-05-15 03:00 | 44696.125 | 0 | 7.6266 | 39.95
2022-05-15 03:30 | 44696.1458 | 0 | 7.982 | 39.95
2022-05-15 04:00 | 44696.1667 | 0 | 7.975 | 39.95
2022-05-15 04:30 | 44696.1875 | 0 | 7.8469 | 39.95
2022-05-15 05:00 | 44696.2083 | 0 | 7.9928 | 39.95
2022-05-15 05:30 | 44696.2292 | 0 | 8.0641 | 39.95
2022-05-15 06:00 | 44696.25 | 0 | 8.5154 | 39.95
2022-05-15 06:30 | 44696.2708 | 0 | 8.7302 | 39.95
2022-05-15 07:00 | 44696.2917 | 0 | 9.225 | 39.95
2022-05-15 07:30 | 44696.3125 | 0 | 9.2876 | 39.95
2022-05-15 08:00 | 44696.3333 | 0 | 9.6825 | 39.95
2022-05-15 08:30 | 44696.3542 | 0 | 9.9185 | 39.95
2022-05-15 09:00 | 44696.375 | 0 | 10.4806 | 39.95
2022-05-15 09:30 | 44696.3958 | 0 | 11.0189 | 39.95
2022-05-15 10:00 | 44696.4167 | 0 | 10.824 | 39.95
2022-05-15 10:30 | 44696.4375 | 0 | 10.4371 | 39.95
2022-05-15 11:00 | 44696.4583 | 0 | 10.1892 | 39.95
2022-05-15 11:30 | 44696.4792 | 0 | 9.7392 | 39.95
2022-05-15 12:00 | 44696.5 | 0 | 9.2059 | 39.95
2022-05-15 12:30 | 44696.5208 | 0 | 10.1837 | 39.95
2022-05-15 13:00 | 44696.5417 | 0 | 10.4636 | 39.95
2022-05-15 13:30 | 44696.5625 | 0 | 11.2973 | 39.95
2022-05-15 14:00 | 44696.5833 | 0 | 11.0945 | 39.95
2022-05-15 14:30 | 44696.6042 | 0 | 11.3268 | 39.95
2022-05-15 15:00 | 44696.625 | 0 | 12.0698 | 39.95
2022-05-15 15:30 | 44696.6458 | 0 | 12.9648 | 39.95
2022-05-15 16:00 | 44696.6667 | 0 | 12.7371 | 39.95
2022-05-15 16:30 | 44696.6875 | 0 | 13.6091 | 39.95
2022-05-15 17:00 | 44696.7083 | 0 | 14.096 | 39.95
2022-05-15 17:30 | 44696.7292 | 0 | 14.4814 | 39.95
2022-05-15 18:00 | 44696.75 | 0 | 14.5353 | 39.95
2022-05-15 18:30 | 44696.7708 | 0 | 14.2834 | 39.95
2022-05-15 19:00 | 44696.7917 | 0 | 13.7725 | 39.95
2022-05-15 19:30 | 44696.8125 | 0 | 13.4042 | 39.95
2022-05-15 20:00 | 44696.8333 | 0 | 13.0899 | 39.95
2022-05-15 20:30 | 44696.8542 | 0 | 12.4049 | 39.95
2022-05-15 21:00 | 44696.875 | 0 | 11.9799 | 39.95
2022-05-15 21:30 | 44696.8958 | 0 | 11.4589 | 39.95
2022-05-15 22:00 | 44696.9167 | 0 | 10.9098 | 39.95
2022-05-15 22:30 | 44696.9375 | 0 | 10.266 | 39.95
2022-05-15 23:00 | 44696.9583 | 0 | 9.8113 | 39.95
2022-05-15 23:30 | 44696.9792 | 0 | 9.4465 | 39.95
2022-05-16 | 44697 | 0 | 9.0038 | 39.95
2022-05-16 00:30 | 44697.0208 | 0 | 8.7394 | 39.95
2022-05-16 01:00 | 44697.0417 | 0 | 8.5694 | 39.95
2022-05-16 01:30 | 44697.0625 | 0 | 8.4676 | 39.95
2022-05-16 02:00 | 44697.0833 | 0 | 8.3829 | 39.95
2022-05-16 02:30 | 44697.1042 | 0 | 8.4527 | 39.95
2022-05-16 03:00 | 44697.125 | 0 | 8.3815 | 39.95
2022-05-16 03:30 | 44697.1458 | 0 | 8.4461 | 39.95
2022-05-16 04:00 | 44697.1667 | 0 | 8.8513 | 39.95
2022-05-16 04:30 | 44697.1875 | 0 | 9.2751 | 39.95
2022-05-16 05:00 | 44697.2083 | 0 | 9.8676 | 39.95
2022-05-16 05:30 | 44697.2292 | 0 | 10.5236 | 39.95
2022-05-16 06:00 | 44697.25 | 0 | 11.6121 | 39.95
2022-05-16 06:30 | 44697.2708 | 0 | 12.5297 | 39.95
2022-05-16 07:00 | 44697.2917 | 0 | 13.4026 | 39.95
2022-05-16 07:30 | 44697.3125 | 0 | 13.6123 | 39.95
2022-05-16 08:00 | 44697.3333 | 0 | 13.2698 | 39.95
2022-05-16 08:30 | 44697.3542 | 0 | 13.0254 | 39.95
2022-05-16 09:00 | 44697.375 | 0 | 13.9395 | 39.95
2022-05-16 09:30 | 44697.3958 | 0 | 13.5853 | 39.95
2022-05-16 10:00 | 44697.4167 | 0 | 14.0006 | 39.95
2022-05-16 10:30 | 44697.4375 | 0 | 13.2828 | 39.95
2022-05-16 11:00 | 44697.4583 | 0 | 12.6173 | 39.95
2022-05-16 11:30 | 44697.4792 | 0 | 13.5371 | 39.95
2022-05-16 12:00 | 44697.5 | 0 | 14.6239 | 39.95
2022-05-16 12:30 | 44697.5208 | 0 | 14.427 | 39.95
2022-05-16 13:00 | 44697.5417 | 0 | 14.8415 | 39.95
2022-05-16 13:30 | 44697.5625 | 0 | 14.8554 | 39.95
2022-05-16 14:00 | 44697.5833 | 0 | 15.3453 | 39.95
2022-05-16 14:30 | 44697.6042 | 0 | 15.8345 | 39.95
2022-05-16 15:00 | 44697.625 | 0 | 14.5075 | 39.95
2022-05-16 15:30 | 44697.6458 | 0 | 14.5301 | 39.95
2022-05-16 16:00 | 44697.6667 | 0 | 15.1566 | 39.95
2022-05-16 16:30 | 44697.6875 | 0 | 15.4735 | 39.95
2022-05-16 17:00 | 44697.7083 | 0 | 15.7826 | 39.95
2022-05-16 17:30 | 44697.7292 | 0 | 16.3839 | 39.95
2022-05-16 18:00 | 44697.75 | 0 | 16.4124 | 39.95
2022-05-16 18:30 | 44697.7708 | 0 | 16.3217 | 39.95
2022-05-16 19:00 | 44697.7917 | 0 | 15.9705 | 39.95
2022-05-16 19:30 | 44697.8125 | 0 | 15.4466 | 39.95
2022-05-16 20:00 | 44697.8333 | 0 | 15.1622 | 39.95
2022-05-16 20:30 | 44697.8542 | 0 | 14.3242 | 39.95
2022-05-16 21:00 | 44697.875 | 0 | 13.8188 | 39.95
2022-05-16 21:30 | 44697.8958 | 0 | 13.2479 | 39.95
2022-05-16 22:00 | 44697.9167 | 0 | 12.6512 | 39.95
2022-05-16 22:30 | 44697.9375 | 0 | 11.6961 | 39.95
2022-05-16 23:00 | 44697.9583 | 0 | 10.921 | 39.95
2022-05-16 23:30 | 44697.9792 | 0 | 10.3649 | 39.95
2022-05-17 | 44698 | 0 | 9.8329 | 39.95
2022-05-17 00:30 | 44698.0208 | 0 | 9.5434 | 39.95
2022-05-17 01:00 | 44698.0417 | 0 | 9.3961 | 39.95
2022-05-17 01:30 | 44698.0625 | 0 | 9.192 | 39.95
2022-05-17 02:00 | 44698.0833 | 0 | 9.1273 | 39.95
2022-05-17 02:30 | 44698.1042 | 0 | 9.0057 | 39.95
2022-05-17 03:00 | 44698.125 | 0 | 8.8837 | 39.95
2022-05-17 03:30 | 44698.1458 | 0 | 9.0154 | 39.95
2022-05-17 04:00 | 44698.1667 | 0 | 9.0514 | 39.95
2022-05-17 04:30 | 44698.1875 | 0 | 9.393 | 39.95
2022-05-17 05:00 | 44698.2083 | 0 | 9.7711 | 39.95
2022-05-17 05:30 | 44698.2292 | 0 | 10.5036 | 39.95
2022-05-17 06:00 | 44698.25 | 0 | 11.8235 | 39.95
2022-05-17 06:30 | 44698.2708 | 0 | 12.9298 | 39.95
2022-05-17 07:00 | 44698.2917 | 0 | 13.537 | 39.95
2022-05-17 07:30 | 44698.3125 | 0 | 13.2373 | 39.95
2022-05-17 08:00 | 44698.3333 | 0 | 13.9358 | 39.95
2022-05-17 08:30 | 44698.3542 | 0 | 14.2783 | 39.95
2022-05-17 09:00 | 44698.375 | 0 | 13.8848 | 39.95
2022-05-17 09:30 | 44698.3958 | 0 | 14.3503 | 39.95
2022-05-17 10:00 | 44698.4167 | 0 | 13.8099 | 39.95
2022-05-17 10:30 | 44698.4375 | 0 | 13.3066 | 39.95
2022-05-17 11:00 | 44698.4583 | 0 | 12.4672 | 39.95
2022-05-17 11:30 | 44698.4792 | 0 | 12.9991 | 39.95
2022-05-17 12:00 | 44698.5 | 0 | 14.5727 | 39.95
2022-05-17 12:30 | 44698.5208 | 0 | 13.3965 | 39.95
2022-05-17 13:00 | 44698.5417 | 0 | 14.0579 | 39.95
2022-05-17 13:30 | 44698.5625 | 0 | 15.1269 | 39.95
2022-05-17 14:00 | 44698.5833 | 0 | 15.5257 | 39.95
2022-05-17 14:30 | 44698.6042 | 0 | 15.4554 | 39.95
2022-05-17 15:00 | 44698.625 | 0 | 14.7967 | 39.95
2022-05-17 15:30 | 44698.6458 | 0 | 14.4256 | 39.95
2022-05-17 16:00 | 44698.6667 | 0 | 14.3105 | 39.95
2022-05-17 16:30 | 44698.6875 | 0 | 14.6594 | 39.95
2022-05-17 17:00 | 44698.7083 | 0 | 14.7575 | 39.95
2022-05-17 17:30 | 44698.7292 | 0 | 15.1731 | 39.95
2022-05-17 18:00 | 44698.75 | 0 | 15.219 | 39.95
2022-05-17 18:30 | 44698.7708 | 0 | 15.1995 | 39.95
2022-05-17 19:00 | 44698.7917 | 0 | 14.9066 | 39.95
2022-05-17 19:30 | 44698.8125 | 0 | 14.4957 | 39.95
2022-05-17 20:00 | 44698.8333 | 0 | 14.2727 | 39.95
2022-05-17 20:30 | 44698.8542 | 0 | 13.597 | 39.95
2022-05-17 21:00 | 44698.875 | 0 | 13.2223 | 39.95
2022-05-17 21:30 | 44698.8958 | 0 | 12.5931 | 39.95
2022-05-17 22:00 | 44698.9167 | 0 | 12.0066 | 39.95
2022-05-17 22:30 | 44698.9375 | 0 | 11.3057 | 39.95
2022-05-17 23:00 | 44698.9583 | 0 | 10.7773 | 39.95
2022-05-17 23:30 | 44698.9792 | 0 | 10.3668 | 39.95
2022-05-18 | 44699 | 0 | 9.6953 | 39.95
2022-05-18 00:30 | 44699.0208 | 0 | 9.3564 | 39.95
2022-05-18 01:00 | 44699.0417 | 0 | 9.2606 | 39.95
2022-05-18 01:30 | 44699.0625 | 0 | 8.9363 | 39.95
2022-05-18 02:00 | 44699.0833 | 0 | 8.8479 | 39.95
2022-05-18 02:30 | 44699.1042 | 0 | 8.767 | 39.95
2022-05-18 03:00 | 44699.125 | 0 | 8.7688 | 39.95
2022-05-18 03:30 | 44699.1458 | 0 | 8.7325 | 39.95
2022-05-18 04:00 | 44699.1667 | 0 | 8.9402 | 39.95
2022-05-18 04:30 | 44699.1875 | 0 | 9.2774 | 39.95
2022-05-18 05:00 | 44699.2083 | 0 | 9.7824 | 39.95
2022-05-18 05:30 | 44699.2292 | 0 | 10.418 | 39.95
2022-05-18 06:00 | 44699.25 | 0 | 11.3375 | 39.95
2022-05-18 06:30 | 44699.2708 | 0 | 12.4396 | 39.95
2022-05-18 07:00 | 44699.2917 | 0 | 13.4442 | 39.95
2022-05-18 07:30 | 44699.3125 | 0 | 13.6966 | 39.95
2022-05-18 08:00 | 44699.3333 | 0 | 14.0231 | 39.95
2022-05-18 08:30 | 44699.3542 | 0 | 13.5794 | 39.95
2022-05-18 09:00 | 44699.375 | 0 | 12.6175 | 39.95
2022-05-18 09:30 | 44699.3958 | 0 | 11.2372 | 39.95
2022-05-18 10:00 | 44699.4167 | 0 | 10.5452 | 39.95
2022-05-18 10:30 | 44699.4375 | 0 | 11.1504 | 39.95
2022-05-18 11:00 | 44699.4583 | 0 | 13.3367 | 39.95
2022-05-18 11:30 | 44699.4792 | 0 | 13.8749 | 39.95
2022-05-18 12:00 | 44699.5 | 0 | 12.5676 | 39.95
2022-05-18 12:30 | 44699.5208 | 0 | 12.8624 | 39.95
2022-05-18 13:00 | 44699.5417 | 0 | 11.7913 | 39.95
2022-05-18 13:30 | 44699.5625 | 0 | 12.059 | 39.95
2022-05-18 14:00 | 44699.5833 | 0 | 13.2548 | 39.95
2022-05-18 14:30 | 44699.6042 | 0 | 13.2017 | 39.95
2022-05-18 15:00 | 44699.625 | 0 | 13.766 | 39.95
2022-05-18 15:30 | 44699.6458 | 0 | 14.3082 | 39.95
2022-05-18 16:00 | 44699.6667 | 0 | 14.3005 | 39.95
2022-05-18 16:30 | 44699.6875 | 0 | 14.6186 | 39.95
2022-05-18 17:00 | 44699.7083 | 0 | 14.9384 | 39.95
2022-05-18 17:30 | 44699.7292 | 0 | 15.2118 | 39.95
2022-05-18 18:00 | 44699.75 | 0 | 15.2065 | 39.95
2022-05-18 18:30 | 44699.7708 | 0 | 15.1823 | 39.95
2022-05-18 19:00 | 44699.7917 | 0 | 14.9179 | 39.95
2022-05-18 19:30 | 44699.8125 | 0 | 14.3955 | 39.95
2022-05-18 20:00 | 44699.8333 | 0 | 14.1557 | 39.95
2022-05-18 20:30 | 44699.8542 | 0 | 13.5097 | 39.95
2022-05-18 21:00 | 44699.875 | 0 | 13.1866 | 39.95
2022-05-18 21:30 | 44699.8958 | 0 | 12.6277 | 39.95
2022-05-18 22:00 | 44699.9167 | 0 | 11.9857 | 39.95
2022-05-18 22:30 | 44699.9375 | 0 | 11.3219 | 39.95
2022-05-18 23:00 | 44699.9583 | 0 | 10.7818 | 39.95
2022-05-18 23:30 | 44699.9792 | 0 | 10.1772 | 39.95
2022-05-19 | 44700 | 0 | 9.5795 | 39.95
2022-05-19 00:30 | 44700.0208 | 0 | 9.1471 | 39.95
2022-05-19 01:00 | 44700.0417 | 0 | 9.0552 | 39.95
2022-05-19 01:30 | 44700.0625 | 0 | 8.7786 | 39.95
2022-05-19 02:00 | 44700.0833 | 0 | 8.7772 | 39.95
2022-05-19 02:30 | 44700.1042 | 0 | 8.7877 | 39.95
2022-05-19 03:00 | 44700.125 | 0 | 8.6144 | 39.95
2022-05-19 03:30 | 44700.1458 | 0 | 8.5641 | 39.95
2022-05-19 04:00 | 44700.1667 | 0 | 8.843 | 39.95
2022-05-19 04:30 | 44700.1875 | 0 | 9.1142 | 39.95
2022-05-19 05:00 | 44700.2083 | 0 | 9.6405 | 39.95
2022-05-19 05:30 | 44700.2292 | 0 | 10.3563 | 39.95
2022-05-19 06:00 | 44700.25 | 0 | 11.4929 | 39.95
2022-05-19 06:30 | 44700.2708 | 0 | 12.3875 | 39.95
2022-05-19 07:00 | 44700.2917 | 0 | 13.0555 | 39.95
2022-05-19 07:30 | 44700.3125 | 0 | 12.9207 | 39.95
2022-05-19 08:00 | 44700.3333 | 0 | 12.6639 | 39.95
2022-05-19 08:30 | 44700.3542 | 0 | 13.5135 | 39.95
2022-05-19 09:00 | 44700.375 | 0 | 13.6813 | 39.95
2022-05-19 09:30 | 44700.3958 | 0 | 12.5839 | 39.95
2022-05-19 10:00 | 44700.4167 | 0 | 12.7588 | 39.95
2022-05-19 10:30 | 44700.4375 | 0 | 12.7672 | 39.95
2022-05-19 11:00 | 44700.4583 | 0 | 11.838 | 39.95
2022-05-19 11:30 | 44700.4792 | 0 | 12.8409 | 39.95
2022-05-19 12:00 | 44700.5 | 0 | 11.7861 | 39.95
2022-05-19 12:30 | 44700.5208 | 0 | 12.347 | 39.95
2022-05-19 13:00 | 44700.5417 | 0 | 12.5916 | 39.95
2022-05-19 13:30 | 44700.5625 | 0 | 12.4667 | 39.95
2022-05-19 14:00 | 44700.5833 | 0 | 12.6858 | 39.95
2022-05-19 14:30 | 44700.6042 | 0 | 12.4447 | 39.95
2022-05-19 15:00 | 44700.625 | 0 | 12.3707 | 39.95
2022-05-19 15:30 | 44700.6458 | 0 | 12.9659 | 39.95
2022-05-19 16:00 | 44700.6667 | 0 | 12.8476 | 39.95
2022-05-19 16:30 | 44700.6875 | 0 | 13.5369 | 39.95
2022-05-19 17:00 | 44700.7083 | 0 | 13.893 | 39.95
2022-05-19 17:30 | 44700.7292 | 0 | 14.2985 | 39.95
2022-05-19 18:00 | 44700.75 | 0 | 14.3148 | 39.95
2022-05-19 18:30 | 44700.7708 | 0 | 14.3238 | 39.95
2022-05-19 19:00 | 44700.7917 | 0 | 13.915 | 39.95
2022-05-19 19:30 | 44700.8125 | 0 | 13.6241 | 39.95
2022-05-19 20:00 | 44700.8333 | 0 | 13.4241 | 39.95
2022-05-19 20:30 | 44700.8542 | 0 | 12.9732 | 39.95
2022-05-19 21:00 | 44700.875 | 0 | 12.3609 | 39.95
2022-05-19 21:30 | 44700.8958 | 0 | 11.9109 | 39.95
2022-05-19 22:00 | 44700.9167 | 0 | 11.3467 | 39.95
2022-05-19 22:30 | 44700.9375 | 0 | 10.7939 | 39.95
2022-05-19 23:00 | 44700.9583 | 0 | 10.3385 | 39.95
2022-05-19 23:30 | 44700.9792 | 0 | 9.763 | 39.95
2022-05-20 | 44701 | 0 | 9.1123 | 39.95
2022-05-20 00:30 | 44701.0208 | 0 | 8.6779 | 39.95
2022-05-20 01:00 | 44701.0417 | 0 | 8.5483 | 39.95
2022-05-20 01:30 | 44701.0625 | 0 | 8.342 | 39.95
2022-05-20 02:00 | 44701.0833 | 0 | 8.3485 | 39.95
2022-05-20 02:30 | 44701.1042 | 0 | 8.3564 | 39.95
2022-05-20 03:00 | 44701.125 | 0 | 8.2564 | 39.95
2022-05-20 03:30 | 44701.1458 | 0 | 8.3991 | 39.95
2022-05-20 04:00 | 44701.1667 | 0 | 8.5108 | 39.95
2022-05-20 04:30 | 44701.1875 | 0 | 8.834 | 39.95
2022-05-20 05:00 | 44701.2083 | 0 | 9.299 | 39.95
2022-05-20 05:30 | 44701.2292 | 0 | 10.058 | 39.95
2022-05-20 06:00 | 44701.25 | 0 | 11.0484 | 39.95
2022-05-20 06:30 | 44701.2708 | 0 | 12.0581 | 39.95
2022-05-20 07:00 | 44701.2917 | 0 | 13.0079 | 39.95
2022-05-20 07:30 | 44701.3125 | 0 | 13.0258 | 39.95
2022-05-20 08:00 | 44701.3333 | 0 | 12.6736 | 39.95
2022-05-20 08:30 | 44701.3542 | 0 | 12.3476 | 39.95
2022-05-20 09:00 | 44701.375 | 0 | 12.7384 | 39.95
2022-05-20 09:30 | 44701.3958 | 0 | 13.3788 | 39.95
2022-05-20 10:00 | 44701.4167 | 0 | 12.6872 | 39.95
2022-05-20 10:30 | 44701.4375 | 0 | 12.5047 | 39.95
2022-05-20 11:00 | 44701.4583 | 0 | 11.6298 | 39.95
2022-05-20 11:30 | 44701.4792 | 0 | 11.3632 | 39.95
2022-05-20 12:00 | 44701.5 | 0 | 12.8679 | 39.95
2022-05-20 12:30 | 44701.5208 | 0 | 12.2396 | 39.95
2022-05-20 13:00 | 44701.5417 | 0 | 12.8005 | 39.95
2022-05-20 13:30 | 44701.5625 | 0 | 12.8222 | 39.95
2022-05-20 14:00 | 44701.5833 | 0 | 12.6407 | 39.95
2022-05-20 14:30 | 44701.6042 | 0 | 12.7414 | 39.95
2022-05-20 15:00 | 44701.625 | 0 | 12.5108 | 39.95
2022-05-20 15:30 | 44701.6458 | 0 | 12.9866 | 39.95
2022-05-20 16:00 | 44701.6667 | 0 | 13.16 | 39.95
2022-05-20 16:30 | 44701.6875 | 0 | 13.3116 | 39.95
2022-05-20 17:00 | 44701.7083 | 0 | 13.6689 | 39.95
2022-05-20 17:30 | 44701.7292 | 0 | 13.8534 | 39.95
2022-05-20 18:00 | 44701.75 | 0 | 13.7549 | 39.95
2022-05-20 18:30 | 44701.7708 | 0 | 13.7307 | 39.95
2022-05-20 19:00 | 44701.7917 | 0 | 13.6224 | 39.95
2022-05-20 19:30 | 44701.8125 | 0 | 13.0434 | 39.95
2022-05-20 20:00 | 44701.8333 | 0 | 12.9665 | 39.95
2022-05-20 20:30 | 44701.8542 | 0 | 12.3056 | 39.95
2022-05-20 21:00 | 44701.875 | 0 | 11.8981 | 39.95
2022-05-20 21:30 | 44701.8958 | 0 | 11.5839 | 39.95
2022-05-20 22:00 | 44701.9167 | 0 | 11.2323 | 39.95
2022-05-20 22:30 | 44701.9375 | 0 | 10.4872 | 39.95
2022-05-20 23:00 | 44701.9583 | 0 | 10.0814 | 39.95
2022-05-20 23:30 | 44701.9792 | 0 | 9.5007 | 39.95
2022-05-21 | 44702 | 0 | 8.9356 | 39.95
2022-05-21 00:30 | 44702.0208 | 0 | 8.67 | 39.95
2022-05-21 01:00 | 44702.0417 | 0 | 8.3473 | 39.95
2022-05-21 01:30 | 44702.0625 | 0 | 8.1819 | 39.95
2022-05-21 02:00 | 44702.0833 | 0 | 8.0856 | 39.95
2022-05-21 02:30 | 44702.1042 | 0 | 7.9888 | 39.95
2022-05-21 03:00 | 44702.125 | 0 | 7.899 | 39.95
2022-05-21 03:30 | 44702.1458 | 0 | 8.0395 | 39.95
2022-05-21 04:00 | 44702.1667 | 0 | 7.93 | 39.95
2022-05-21 04:30 | 44702.1875 | 0 | 7.9939 | 39.95
2022-05-21 05:00 | 44702.2083 | 0 | 8.1746 | 39.95
2022-05-21 05:30 | 44702.2292 | 0 | 8.3866 | 39.95
2022-05-21 06:00 | 44702.25 | 0 | 8.6686 | 39.95
2022-05-21 06:30 | 44702.2708 | 0 | 9.1445 | 39.95
2022-05-21 07:00 | 44702.2917 | 0 | 9.9411 | 39.95
2022-05-21 07:30 | 44702.3125 | 0 | 10.4793 | 39.95
2022-05-21 08:00 | 44702.3333 | 0 | 10.9626 | 39.95
2022-05-21 08:30 | 44702.3542 | 0 | 11.4094 | 39.95
2022-05-21 09:00 | 44702.375 | 0 | 11.6699 | 39.95
2022-05-21 09:30 | 44702.3958 | 0 | 11.9449 | 39.95
2022-05-21 10:00 | 44702.4167 | 0 | 11.5137 | 39.95
2022-05-21 10:30 | 44702.4375 | 0 | 11.5038 | 39.95
2022-05-21 11:00 | 44702.4583 | 0 | 12.002 | 39.95
2022-05-21 11:30 | 44702.4792 | 0 | 11.854 | 39.95
2022-05-21 12:00 | 44702.5 | 0 | 11.5251 | 39.95
2022-05-21 12:30 | 44702.5208 | 0 | 11.5534 | 39.95
2022-05-21 13:00 | 44702.5417 | 0 | 11.6183 | 39.95
2022-05-21 13:30 | 44702.5625 | 0 | 11.5028 | 39.95
2022-05-21 14:00 | 44702.5833 | 0 | 11.6132 | 39.95
2022-05-21 14:30 | 44702.6042 | 0 | 11.7109 | 39.95
2022-05-21 15:00 | 44702.625 | 0 | 11.8321 | 39.95
2022-05-21 15:30 | 44702.6458 | 0 | 12.0985 | 39.95
2022-05-21 16:00 | 44702.6667 | 0 | 12.2838 | 39.95
2022-05-21 16:30 | 44702.6875 | 0 | 12.4632 | 39.95
2022-05-21 17:00 | 44702.7083 | 0 | 12.8385 | 39.95
2022-05-21 17:30 | 44702.7292 | 0 | 12.8659 | 39.95
2022-05-21 18:00 | 44702.75 | 0 | 12.7527 | 39.95
2022-05-21 18:30 | 44702.7708 | 0 | 12.447 | 39.95
2022-05-21 19:00 | 44702.7917 | 0 | 12.3635 | 39.95
2022-05-21 19:30 | 44702.8125 | 0 | 11.9924 | 39.95
2022-05-21 20:00 | 44702.8333 | 0 | 11.68 | 39.95
2022-05-21 20:30 | 44702.8542 | 0 | 11.2691 | 39.95
2022-05-21 21:00 | 44702.875 | 0 | 11.0091 | 39.95
2022-05-21 21:30 | 44702.8958 | 0 | 10.6078 | 39.95
2022-05-21 22:00 | 44702.9167 | 0 | 10.2819 | 39.95
2022-05-21 22:30 | 44702.9375 | 0 | 9.734 | 39.95
2022-05-21 23:00 | 44702.9583 | 0 | 9.2144 | 39.95
2022-05-21 23:30 | 44702.9792 | 0 | 8.8177 | 39.95
2022-05-22 | 44703 | 0 | 8.2247 | 39.95
2022-05-22 00:30 | 44703.0208 | 0 | 7.9316 | 39.95
2022-05-22 01:00 | 44703.0417 | 0 | 7.8355 | 39.95
2022-05-22 01:30 | 44703.0625 | 0 | 7.5633 | 39.95
2022-05-22 02:00 | 44703.0833 | 0 | 7.4987 | 39.95
2022-05-22 02:30 | 44703.1042 | 0 | 7.3619 | 39.95
2022-05-22 03:00 | 44703.125 | 0 | 7.3023 | 39.95
2022-05-22 03:30 | 44703.1458 | 0 | 7.2609 | 39.95
2022-05-22 04:00 | 44703.1667 | 0 | 7.2444 | 39.95
2022-05-22 04:30 | 44703.1875 | 0 | 7.1797 | 39.95
2022-05-22 05:00 | 44703.2083 | 0 | 7.4177 | 39.95
2022-05-22 05:30 | 44703.2292 | 0 | 7.4882 | 39.95
2022-05-22 06:00 | 44703.25 | 0 | 7.8087 | 39.95
2022-05-22 06:30 | 44703.2708 | 0 | 8.0454 | 39.95
2022-05-22 07:00 | 44703.2917 | 0 | 8.6417 | 39.95
2022-05-22 07:30 | 44703.3125 | 0 | 8.7554 | 39.95
2022-05-22 08:00 | 44703.3333 | 0 | 9.6091 | 39.95
2022-05-22 08:30 | 44703.3542 | 0 | 9.814 | 39.95
2022-05-22 09:00 | 44703.375 | 0 | 10.8767 | 39.95
2022-05-22 09:30 | 44703.3958 | 0 | 10.7234 | 39.95
2022-05-22 10:00 | 44703.4167 | 0 | 10.2457 | 39.95
2022-05-22 10:30 | 44703.4375 | 0 | 8.9579 | 39.95
2022-05-22 11:00 | 44703.4583 | 0 | 10.6438 | 39.95
2022-05-22 11:30 | 44703.4792 | 0 | 10.5512 | 39.95
2022-05-22 12:00 | 44703.5 | 0 | 9.8996 | 39.95
2022-05-22 12:30 | 44703.5208 | 0 | 9.9185 | 39.95
2022-05-22 13:00 | 44703.5417 | 0 | 10.2537 | 39.95
2022-05-22 13:30 | 44703.5625 | 0 | 9.6723 | 39.95
2022-05-22 14:00 | 44703.5833 | 0 | 9.2553 | 39.95
2022-05-22 14:30 | 44703.6042 | 0 | 10.0849 | 39.95
2022-05-22 15:00 | 44703.625 | 0 | 10.9536 | 39.95
2022-05-22 15:30 | 44703.6458 | 0 | 11.6778 | 39.95
2022-05-22 16:00 | 44703.6667 | 0 | 11.7032 | 39.95
2022-05-22 16:30 | 44703.6875 | 0 | 11.9242 | 39.95
2022-05-22 17:00 | 44703.7083 | 0 | 12.5887 | 39.95
2022-05-22 17:30 | 44703.7292 | 0 | 13.0868 | 39.95
2022-05-22 18:00 | 44703.75 | 0 | 13.2328 | 39.95
2022-05-22 18:30 | 44703.7708 | 0 | 13.2259 | 39.95
2022-05-22 19:00 | 44703.7917 | 0 | 12.776 | 39.95
2022-05-22 19:30 | 44703.8125 | 0 | 12.1488 | 39.95
2022-05-22 20:00 | 44703.8333 | 0 | 12.0217 | 39.95
2022-05-22 20:30 | 44703.8542 | 0 | 11.532 | 39.95
2022-05-22 21:00 | 44703.875 | 0 | 10.8822 | 39.95
2022-05-22 21:30 | 44703.8958 | 0 | 10.3955 | 39.95
2022-05-22 22:00 | 44703.9167 | 0 | 9.6509 | 39.95
2022-05-22 22:30 | 44703.9375 | 0 | 8.9603 | 39.95
2022-05-22 23:00 | 44703.9583 | 0 | 8.4323 | 39.95
2022-05-22 23:30 | 44703.9792 | 0 | 8.074 | 39.95
2022-05-23 | 44704 | 0 | 7.6515 | 39.95
2022-05-23 00:30 | 44704.0208 | 0 | 7.5426 | 39.95
2022-05-23 01:00 | 44704.0417 | 0 | 7.5143 | 39.95
2022-05-23 01:30 | 44704.0625 | 0 | 7.3168 | 39.95
2022-05-23 02:00 | 44704.0833 | 0 | 7.3412 | 39.95
2022-05-23 02:30 | 44704.1042 | 0 | 7.5077 | 39.95
2022-05-23 03:00 | 44704.125 | 0 | 7.3074 | 39.95
2022-05-23 03:30 | 44704.1458 | 0 | 7.6337 | 39.95
2022-05-23 04:00 | 44704.1667 | 0 | 7.7718 | 39.95
2022-05-23 04:30 | 44704.1875 | 0 | 8.1811 | 39.95
2022-05-23 05:00 | 44704.2083 | 0 | 8.8426 | 39.95
2022-05-23 05:30 | 44704.2292 | 0 | 9.3749 | 39.95
2022-05-23 06:00 | 44704.25 | 0 | 10.6321 | 39.95
2022-05-23 06:30 | 44704.2708 | 0 | 11.991 | 39.95
2022-05-23 07:00 | 44704.2917 | 0 | 12.7775 | 39.95
2022-05-23 07:30 | 44704.3125 | 0 | 13.2728 | 39.95
2022-05-23 08:00 | 44704.3333 | 0 | 11.9706 | 39.95
2022-05-23 08:30 | 44704.3542 | 0 | 12.5034 | 39.95
2022-05-23 09:00 | 44704.375 | 0 | 13.3381 | 39.95
2022-05-23 09:30 | 44704.3958 | 0 | 12.1077 | 39.95
2022-05-23 10:00 | 44704.4167 | 0 | 11.3682 | 39.95
2022-05-23 10:30 | 44704.4375 | 0 | 9.8029 | 39.95
2022-05-23 11:00 | 44704.4583 | 0 | 10.7496 | 39.95
2022-05-23 11:30 | 44704.4792 | 0 | 10.5726 | 39.95
2022-05-23 12:00 | 44704.5 | 0 | 11.4031 | 39.95
2022-05-23 12:30 | 44704.5208 | 0 | 9.937 | 39.95
2022-05-23 13:00 | 44704.5417 | 0 | 11.6602 | 39.95
2022-05-23 13:30 | 44704.5625 | 0 | 12.2766 | 39.95
2022-05-23 14:00 | 44704.5833 | 0 | 12.4804 | 39.95
2022-05-23 14:30 | 44704.6042 | 0 | 12.3788 | 39.95
2022-05-23 15:00 | 44704.625 | 0 | 13.0157 | 39.95
2022-05-23 15:30 | 44704.6458 | 0 | 13.2547 | 39.95
2022-05-23 16:00 | 44704.6667 | 0 | 13.3242 | 39.95
2022-05-23 16:30 | 44704.6875 | 0 | 13.7529 | 39.95
2022-05-23 17:00 | 44704.7083 | 0 | 14.4114 | 39.95
2022-05-23 17:30 | 44704.7292 | 0 | 14.9052 | 39.95
2022-05-23 18:00 | 44704.75 | 0 | 15.0058 | 39.95
2022-05-23 18:30 | 44704.7708 | 0 | 14.9587 | 39.95
2022-05-23 19:00 | 44704.7917 | 0 | 14.3708 | 39.95
2022-05-23 19:30 | 44704.8125 | 0 | 13.9729 | 39.95
2022-05-23 20:00 | 44704.8333 | 0 | 13.7608 | 39.95
2022-05-23 20:30 | 44704.8542 | 0 | 13.0916 | 39.95
2022-05-23 21:00 | 44704.875 | 0 | 12.4346 | 39.95
2022-05-23 21:30 | 44704.8958 | 0 | 11.8407 | 39.95
2022-05-23 22:00 | 44704.9167 | 0 | 11.1071 | 39.95
2022-05-23 22:30 | 44704.9375 | 0 | 10.3141 | 39.95
2022-05-23 23:00 | 44704.9583 | 0 | 9.9336 | 39.95
2022-05-23 23:30 | 44704.9792 | 0 | 9.4776 | 39.95
2022-05-24 | 44705 | 0 | 8.8841 | 39.95
2022-05-24 00:30 | 44705.0208 | 0 | 8.4971 | 39.95
2022-05-24 01:00 | 44705.0417 | 0 | 8.0689 | 39.95
2022-05-24 01:30 | 44705.0625 | 0 | 7.9464 | 39.95
2022-05-24 02:00 | 44705.0833 | 0 | 7.9063 | 39.95
2022-05-24 02:30 | 44705.1042 | 0 | 8.0151 | 39.95
2022-05-24 03:00 | 44705.125 | 0 | 7.8273 | 39.95
2022-05-24 03:30 | 44705.1458 | 0 | 8.001 | 39.95
2022-05-24 04:00 | 44705.1667 | 0 | 8.4946 | 39.95
2022-05-24 04:30 | 44705.1875 | 0 | 8.712 | 39.95
2022-05-24 05:00 | 44705.2083 | 0 | 9.275 | 39.95
2022-05-24 05:30 | 44705.2292 | 0 | 10.0692 | 39.95
2022-05-24 06:00 | 44705.25 | 0 | 11.2372 | 39.95
2022-05-24 06:30 | 44705.2708 | 0 | 12.6564 | 39.95
2022-05-24 07:00 | 44705.2917 | 0 | 13.5262 | 39.95
2022-05-24 07:30 | 44705.3125 | 0 | 13.4317 | 39.95
2022-05-24 08:00 | 44705.3333 | 0 | 13.432 | 39.95
2022-05-24 08:30 | 44705.3542 | 0 | 12.2881 | 39.95
2022-05-24 09:00 | 44705.375 | 0 | 11.6345 | 39.95
2022-05-24 09:30 | 44705.3958 | 0 | 11.6603 | 39.95
2022-05-24 10:00 | 44705.4167 | 0 | 10.0819 | 39.95
2022-05-24 10:30 | 44705.4375 | 0 | 9.2731 | 39.95
2022-05-24 11:00 | 44705.4583 | 0 | 9.1815 | 39.95
2022-05-24 11:30 | 44705.4792 | 0 | 9.0392 | 39.95
2022-05-24 12:00 | 44705.5 | 0 | 9.0525 | 39.95
2022-05-24 12:30 | 44705.5208 | 0 | 8.8169 | 39.95
2022-05-24 13:00 | 44705.5417 | 0 | 9.688 | 39.95
2022-05-24 13:30 | 44705.5625 | 0 | 9.8102 | 39.95
2022-05-24 14:00 | 44705.5833 | 0 | 10.7752 | 39.95
2022-05-24 14:30 | 44705.6042 | 0 | 10.7945 | 39.95
2022-05-24 15:00 | 44705.625 | 0 | 11.2902 | 39.95
2022-05-24 15:30 | 44705.6458 | 0 | 11.9106 | 39.95
2022-05-24 16:00 | 44705.6667 | 0 | 12.5454 | 39.95
2022-05-24 16:30 | 44705.6875 | 0 | 13.0778 | 39.95
2022-05-24 17:00 | 44705.7083 | 0 | 13.6027 | 39.95
2022-05-24 17:30 | 44705.7292 | 0 | 14.459 | 39.95
2022-05-24 18:00 | 44705.75 | 0 | 14.6478 | 39.95
2022-05-24 18:30 | 44705.7708 | 0 | 14.5189 | 39.95
2022-05-24 19:00 | 44705.7917 | 0 | 14.2346 | 39.95
2022-05-24 19:30 | 44705.8125 | 0 | 13.8957 | 39.95
2022-05-24 20:00 | 44705.8333 | 0 | 13.4785 | 39.95
2022-05-24 20:30 | 44705.8542 | 0 | 12.9722 | 39.95
2022-05-24 21:00 | 44705.875 | 0 | 12.3789 | 39.95
2022-05-24 21:30 | 44705.8958 | 0 | 11.8068 | 39.95
2022-05-24 22:00 | 44705.9167 | 0 | 11.2201 | 39.95
2022-05-24 22:30 | 44705.9375 | 0 | 10.4816 | 39.95
2022-05-24 23:00 | 44705.9583 | 0 | 10.0248 | 39.95
2022-05-24 23:30 | 44705.9792 | 0 | 9.4707 | 39.95
2022-05-25 | 44706 | 0 | 8.9392 | 39.95
2022-05-25 00:30 | 44706.0208 | 0 | 8.5728 | 39.95
2022-05-25 01:00 | 44706.0417 | 0 | 8.4136 | 39.95
2022-05-25 01:30 | 44706.0625 | 0 | 8.3144 | 39.95
2022-05-25 02:00 | 44706.0833 | 0 | 8.0277 | 39.95
2022-05-25 02:30 | 44706.1042 | 0 | 8.1388 | 39.95
2022-05-25 03:00 | 44706.125 | 0 | 8.1114 | 39.95
2022-05-25 03:30 | 44706.1458 | 0 | 8.2596 | 39.95
2022-05-25 04:00 | 44706.1667 | 0 | 8.2369 | 39.95
2022-05-25 04:30 | 44706.1875 | 0 | 8.5163 | 39.95
2022-05-25 05:00 | 44706.2083 | 0 | 9.0277 | 39.95
2022-05-25 05:30 | 44706.2292 | 0 | 10.0431 | 39.95
2022-05-25 06:00 | 44706.25 | 0 | 11.1352 | 39.95
2022-05-25 06:30 | 44706.2708 | 0 | 12.2276 | 39.95
2022-05-25 07:00 | 44706.2917 | 0 | 12.886 | 39.95
2022-05-25 07:30 | 44706.3125 | 0 | 13.0525 | 39.95
2022-05-25 08:00 | 44706.3333 | 0 | 12.3407 | 39.95
2022-05-25 08:30 | 44706.3542 | 0 | 11.0199 | 39.95
2022-05-25 09:00 | 44706.375 | 0 | 10.4238 | 39.95
2022-05-25 09:30 | 44706.3958 | 0 | 11.4541 | 39.95
2022-05-25 10:00 | 44706.4167 | 0 | 10.5961 | 39.95
2022-05-25 10:30 | 44706.4375 | 0 | 11.6172 | 39.95
2022-05-25 11:00 | 44706.4583 | 0 | 11.4326 | 39.95
2022-05-25 11:30 | 44706.4792 | 0 | 10.5349 | 39.95
2022-05-25 12:00 | 44706.5 | 0 | 9.6844 | 39.95
2022-05-25 12:30 | 44706.5208 | 0 | 11.9294 | 39.95
2022-05-25 13:00 | 44706.5417 | 0 | 12.9564 | 39.95
2022-05-25 13:30 | 44706.5625 | 0 | 12.432 | 39.95
2022-05-25 14:00 | 44706.5833 | 0 | 12.6512 | 39.95
2022-05-25 14:30 | 44706.6042 | 0 | 12.8189 | 39.95
2022-05-25 15:00 | 44706.625 | 0 | 12.451 | 39.95
2022-05-25 15:30 | 44706.6458 | 0 | 12.1195 | 39.95
2022-05-25 16:00 | 44706.6667 | 0 | 12.9984 | 39.95
2022-05-25 16:30 | 44706.6875 | 0 | 13.4925 | 39.95
2022-05-25 17:00 | 44706.7083 | 0 | 14.1268 | 39.95
2022-05-25 17:30 | 44706.7292 | 0 | 14.7343 | 39.95
2022-05-25 18:00 | 44706.75 | 0 | 14.7224 | 39.95
2022-05-25 18:30 | 44706.7708 | 0 | 14.6989 | 39.95
2022-05-25 19:00 | 44706.7917 | 0 | 14.4128 | 39.95
2022-05-25 19:30 | 44706.8125 | 0 | 13.8886 | 39.95
2022-05-25 20:00 | 44706.8333 | 0 | 13.6605 | 39.95
2022-05-25 20:30 | 44706.8542 | 0 | 13.0637 | 39.95
2022-05-25 21:00 | 44706.875 | 0 | 12.46 | 39.95
2022-05-25 21:30 | 44706.8958 | 0 | 12.0893 | 39.95
2022-05-25 22:00 | 44706.9167 | 0 | 11.4281 | 39.95
2022-05-25 22:30 | 44706.9375 | 0 | 10.6579 | 39.95
2022-05-25 23:00 | 44706.9583 | 0 | 10.0691 | 39.95
2022-05-25 23:30 | 44706.9792 | 0 | 9.747 | 39.95
2022-05-26 | 44707 | 0 | 9.1111 | 39.95
2022-05-26 00:30 | 44707.0208 | 0 | 8.6117 | 39.95
2022-05-26 01:00 | 44707.0417 | 0 | 8.3815 | 39.95
2022-05-26 01:30 | 44707.0625 | 0 | 8.2269 | 39.95
2022-05-26 02:00 | 44707.0833 | 0 | 8.0546 | 39.95
2022-05-26 02:30 | 44707.1042 | 0 | 8.0919 | 39.95
2022-05-26 03:00 | 44707.125 | 0 | 7.9991 | 39.95
2022-05-26 03:30 | 44707.1458 | 0 | 8.0478 | 39.95
2022-05-26 04:00 | 44707.1667 | 0 | 8.2672 | 39.95
2022-05-26 04:30 | 44707.1875 | 0 | 8.7328 | 39.95
2022-05-26 05:00 | 44707.2083 | 0 | 9.4317 | 39.95
2022-05-26 05:30 | 44707.2292 | 0 | 10.2434 | 39.95
2022-05-26 06:00 | 44707.25 | 0 | 11.2736 | 39.95
2022-05-26 06:30 | 44707.2708 | 0 | 12.4727 | 39.95
2022-05-26 07:00 | 44707.2917 | 0 | 13.208 | 39.95
2022-05-26 07:30 | 44707.3125 | 0 | 13.1877 | 39.95
2022-05-26 08:00 | 44707.3333 | 0 | 13.0233 | 39.95
2022-05-26 08:30 | 44707.3542 | 0 | 11.4095 | 39.95
2022-05-26 09:00 | 44707.375 | 0 | 10.2529 | 39.95
2022-05-26 09:30 | 44707.3958 | 0 | 10.2585 | 39.95
2022-05-26 10:00 | 44707.4167 | 0 | 9.9727 | 39.95
2022-05-26 10:30 | 44707.4375 | 0 | 10.2474 | 39.95
2022-05-26 11:00 | 44707.4583 | 0 | 9.0672 | 39.95
2022-05-26 11:30 | 44707.4792 | 0 | 9.4285 | 39.95
2022-05-26 12:00 | 44707.5 | 0 | 10.9732 | 39.95
2022-05-26 12:30 | 44707.5208 | 0 | 10.5223 | 39.95
2022-05-26 13:00 | 44707.5417 | 0 | 10.9577 | 39.95
2022-05-26 13:30 | 44707.5625 | 0 | 9.6431 | 39.95
2022-05-26 14:00 | 44707.5833 | 0 | 10.8302 | 39.95
2022-05-26 14:30 | 44707.6042 | 0 | 10.7815 | 39.95
2022-05-26 15:00 | 44707.625 | 0 | 11.0176 | 39.95
2022-05-26 15:30 | 44707.6458 | 0 | 11.9091 | 39.95
2022-05-26 16:00 | 44707.6667 | 0 | 12.5012 | 39.95
2022-05-26 16:30 | 44707.6875 | 0 | 13.1901 | 39.95
2022-05-26 17:00 | 44707.7083 | 0 | 13.6526 | 39.95
2022-05-26 17:30 | 44707.7292 | 0 | 14.1178 | 39.95
2022-05-26 18:00 | 44707.75 | 0 | 14.1771 | 39.95
2022-05-26 18:30 | 44707.7708 | 0 | 14.0139 | 39.95
2022-05-26 19:00 | 44707.7917 | 0 | 13.8066 | 39.95
2022-05-26 19:30 | 44707.8125 | 0 | 13.5501 | 39.95
2022-05-26 20:00 | 44707.8333 | 0 | 13.2364 | 39.95
2022-05-26 20:30 | 44707.8542 | 0 | 12.7821 | 39.95
2022-05-26 21:00 | 44707.875 | 0 | 12.5014 | 39.95
2022-05-26 21:30 | 44707.8958 | 0 | 11.8274 | 39.95
2022-05-26 22:00 | 44707.9167 | 0 | 11.216 | 39.95
2022-05-26 22:30 | 44707.9375 | 0 | 10.4722 | 39.95
2022-05-26 23:00 | 44707.9583 | 0 | 9.9723 | 39.95
2022-05-26 23:30 | 44707.9792 | 0 | 9.565 | 39.95
2022-05-27 | 44708 | 0 | 8.9672 | 39.95
2022-05-27 00:30 | 44708.0208 | 0 | 8.5511 | 39.95
2022-05-27 01:00 | 44708.0417 | 0 | 8.3796 | 39.95
2022-05-27 01:30 | 44708.0625 | 0 | 8.1766 | 39.95
2022-05-27 02:00 | 44708.0833 | 0 | 8.1612 | 39.95
2022-05-27 02:30 | 44708.1042 | 0 | 8.188 | 39.95
2022-05-27 03:00 | 44708.125 | 0 | 8.0169 | 39.95
2022-05-27 03:30 | 44708.1458 | 0 | 8.1709 | 39.95
2022-05-27 04:00 | 44708.1667 | 0 | 8.4597 | 39.95
2022-05-27 04:30 | 44708.1875 | 0 | 8.8107 | 39.95
2022-05-27 05:00 | 44708.2083 | 0 | 9.2705 | 39.95
2022-05-27 05:30 | 44708.2292 | 0 | 10.1275 | 39.95
2022-05-27 06:00 | 44708.25 | 0 | 11.3259 | 39.95
2022-05-27 06:30 | 44708.2708 | 0 | 12.4171 | 39.95
2022-05-27 07:00 | 44708.2917 | 0 | 13.0446 | 39.95
2022-05-27 07:30 | 44708.3125 | 0 | 12.4903 | 39.95
2022-05-27 08:00 | 44708.3333 | 0 | 11.8648 | 39.95
2022-05-27 08:30 | 44708.3542 | 0 | 11.1776 | 39.95
2022-05-27 09:00 | 44708.375 | 0 | 10.511 | 39.95
2022-05-27 09:30 | 44708.3958 | 0 | 10.0216 | 39.95
2022-05-27 10:00 | 44708.4167 | 0 | 9.4741 | 39.95
2022-05-27 10:30 | 44708.4375 | 0 | 9.2449 | 39.95
2022-05-27 11:00 | 44708.4583 | 0 | 9.5377 | 39.95
2022-05-27 11:30 | 44708.4792 | 0 | 10.9081 | 39.95
2022-05-27 12:00 | 44708.5 | 0 | 11.3171 | 39.95
2022-05-27 12:30 | 44708.5208 | 0 | 9.7545 | 39.95
2022-05-27 13:00 | 44708.5417 | 0 | 9.2694 | 39.95
2022-05-27 13:30 | 44708.5625 | 0 | 9.768 | 39.95
2022-05-27 14:00 | 44708.5833 | 0 | 10.2781 | 39.95
2022-05-27 14:30 | 44708.6042 | 0 | 11.2608 | 39.95
2022-05-27 15:00 | 44708.625 | 0 | 11.5794 | 39.95
2022-05-27 15:30 | 44708.6458 | 0 | 12.0116 | 39.95
2022-05-27 16:00 | 44708.6667 | 0 | 12.5196 | 39.95
2022-05-27 16:30 | 44708.6875 | 0 | 13.1081 | 39.95
2022-05-27 17:00 | 44708.7083 | 0 | 13.3814 | 39.95
2022-05-27 17:30 | 44708.7292 | 0 | 13.7166 | 39.95
2022-05-27 18:00 | 44708.75 | 0 | 13.5649 | 39.95
2022-05-27 18:30 | 44708.7708 | 0 | 13.3702 | 39.95
2022-05-27 19:00 | 44708.7917 | 0 | 12.9488 | 39.95
2022-05-27 19:30 | 44708.8125 | 0 | 12.8831 | 39.95
2022-05-27 20:00 | 44708.8333 | 0 | 12.6066 | 39.95
2022-05-27 20:30 | 44708.8542 | 0 | 12.166 | 39.95
2022-05-27 21:00 | 44708.875 | 0 | 11.894 | 39.95
2022-05-27 21:30 | 44708.8958 | 0 | 11.3688 | 39.95
2022-05-27 22:00 | 44708.9167 | 0 | 11.0109 | 39.95
2022-05-27 22:30 | 44708.9375 | 0 | 10.3874 | 39.95
2022-05-27 23:00 | 44708.9583 | 0 | 9.8582 | 39.95
2022-05-27 23:30 | 44708.9792 | 0 | 9.4299 | 39.95
2022-05-28 | 44709 | 0 | 8.8868 | 39.95
2022-05-28 00:30 | 44709.0208 | 0 | 8.5153 | 39.95
2022-05-28 01:00 | 44709.0417 | 0 | 8.3197 | 39.95
2022-05-28 01:30 | 44709.0625 | 0 | 8.1233 | 39.95
2022-05-28 02:00 | 44709.0833 | 0 | 8.0317 | 39.95
2022-05-28 02:30 | 44709.1042 | 0 | 7.9292 | 39.95
2022-05-28 03:00 | 44709.125 | 0 | 7.868 | 39.95
2022-05-28 03:30 | 44709.1458 | 0 | 7.8988 | 39.95
2022-05-28 04:00 | 44709.1667 | 0 | 7.9946 | 39.95
2022-05-28 04:30 | 44709.1875 | 0 | 8.0782 | 39.95
2022-05-28 05:00 | 44709.2083 | 0 | 8.4028 | 39.95
2022-05-28 05:30 | 44709.2292 | 0 | 8.64 | 39.95
2022-05-28 06:00 | 44709.25 | 0 | 9.0945 | 39.95
2022-05-28 06:30 | 44709.2708 | 0 | 9.5842 | 39.95
2022-05-28 07:00 | 44709.2917 | 0 | 9.8297 | 39.95
2022-05-28 07:30 | 44709.3125 | 0 | 9.5353 | 39.95
2022-05-28 08:00 | 44709.3333 | 0 | 9.5709 | 39.95
2022-05-28 08:30 | 44709.3542 | 0 | 8.8173 | 39.95
2022-05-28 09:00 | 44709.375 | 0 | 8.5071 | 39.95
2022-05-28 09:30 | 44709.3958 | 0 | 7.9101 | 39.95
2022-05-28 10:00 | 44709.4167 | 0 | 7.4595 | 39.95
2022-05-28 10:30 | 44709.4375 | 0 | 7.1242 | 39.95
2022-05-28 11:00 | 44709.4583 | 0 | 6.8962 | 39.95
2022-05-28 11:30 | 44709.4792 | 0 | 6.7948 | 39.95
2022-05-28 12:00 | 44709.5 | 0 | 6.5858 | 39.95
2022-05-28 12:30 | 44709.5208 | 0 | 6.7479 | 39.95
2022-05-28 13:00 | 44709.5417 | 0 | 6.8769 | 39.95
2022-05-28 13:30 | 44709.5625 | 0 | 7.3407 | 39.95
2022-05-28 14:00 | 44709.5833 | 0 | 7.7445 | 39.95
2022-05-28 14:30 | 44709.6042 | 0 | 8.479 | 39.95
2022-05-28 15:00 | 44709.625 | 0 | 9.0122 | 39.95
2022-05-28 15:30 | 44709.6458 | 0 | 9.7973 | 39.95
2022-05-28 16:00 | 44709.6667 | 0 | 10.6392 | 39.95
2022-05-28 16:30 | 44709.6875 | 0 | 11.0499 | 39.95
2022-05-28 17:00 | 44709.7083 | 0 | 11.6227 | 39.95
2022-05-28 17:30 | 44709.7292 | 0 | 11.8859 | 39.95
2022-05-28 18:00 | 44709.75 | 0 | 11.9432 | 39.95
2022-05-28 18:30 | 44709.7708 | 0 | 11.6972 | 39.95
2022-05-28 19:00 | 44709.7917 | 0 | 11.4397 | 39.95
2022-05-28 19:30 | 44709.8125 | 0 | 11.2517 | 39.95
2022-05-28 20:00 | 44709.8333 | 0 | 11.0522 | 39.95
2022-05-28 20:30 | 44709.8542 | 0 | 10.5823 | 39.95
2022-05-28 21:00 | 44709.875 | 0 | 10.3409 | 39.95
2022-05-28 21:30 | 44709.8958 | 0 | 10.0703 | 39.95
2022-05-28 22:00 | 44709.9167 | 0 | 9.864 | 39.95
2022-05-28 22:30 | 44709.9375 | 0 | 9.3769 | 39.95
2022-05-28 23:00 | 44709.9583 | 0 | 8.993 | 39.95
2022-05-28 23:30 | 44709.9792 | 0 | 8.4321 | 39.95
2022-05-29 | 44710 | 0 | 7.9782 | 39.95
2022-05-29 00:30 | 44710.0208 | 0 | 7.6498 | 39.95
2022-05-29 01:00 | 44710.0417 | 0 | 7.5667 | 39.95
2022-05-29 01:30 | 44710.0625 | 0 | 7.3554 | 39.95
2022-05-29 02:00 | 44710.0833 | 0 | 7.3495 | 39.95
2022-05-29 02:30 | 44710.1042 | 0 | 7.1059 | 39.95
2022-05-29 03:00 | 44710.125 | 0 | 7.1539 | 39.95
2022-05-29 03:30 | 44710.1458 | 0 | 7.1453 | 39.95
2022-05-29 04:00 | 44710.1667 | 0 | 7.1504 | 39.95
2022-05-29 04:30 | 44710.1875 | 0 | 7.1178 | 39.95
2022-05-29 05:00 | 44710.2083 | 0 | 7.2604 | 39.95
2022-05-29 05:30 | 44710.2292 | 0 | 7.3155 | 39.95
2022-05-29 06:00 | 44710.25 | 0 | 7.7518 | 39.95
2022-05-29 06:30 | 44710.2708 | 0 | 8.1427 | 39.95
2022-05-29 07:00 | 44710.2917 | 0 | 8.4383 | 39.95
2022-05-29 07:30 | 44710.3125 | 0 | 8.0848 | 39.95
2022-05-29 08:00 | 44710.3333 | 0 | 7.8333 | 39.95
2022-05-29 08:30 | 44710.3542 | 0 | 7.6474 | 39.95
2022-05-29 09:00 | 44710.375 | 0 | 7.2813 | 39.95
2022-05-29 09:30 | 44710.3958 | 0 | 6.8468 | 39.95
2022-05-29 10:00 | 44710.4167 | 0 | 6.327 | 39.95
2022-05-29 10:30 | 44710.4375 | 0 | 6.0401 | 39.95
2022-05-29 11:00 | 44710.4583 | 0 | 5.796 | 39.95
2022-05-29 11:30 | 44710.4792 | 0 | 5.5963 | 39.95
2022-05-29 12:00 | 44710.5 | 0 | 5.9037 | 39.95
2022-05-29 12:30 | 44710.5208 | 0 | 6.2525 | 39.95
2022-05-29 13:00 | 44710.5417 | 0 | 6.7466 | 39.95
2022-05-29 13:30 | 44710.5625 | 0 | 6.3317 | 39.95
2022-05-29 14:00 | 44710.5833 | 0 | 6.9609 | 39.95
2022-05-29 14:30 | 44710.6042 | 0 | 7.5581 | 39.95
2022-05-29 15:00 | 44710.625 | 0 | 8.2134 | 39.95
2022-05-29 15:30 | 44710.6458 | 0 | 9.0551 | 39.95
2022-05-29 16:00 | 44710.6667 | 0 | 10.0028 | 39.95
2022-05-29 16:30 | 44710.6875 | 0 | 10.8457 | 39.95
2022-05-29 17:00 | 44710.7083 | 0 | 11.7132 | 39.95
2022-05-29 17:30 | 44710.7292 | 0 | 12.2816 | 39.95
2022-05-29 18:00 | 44710.75 | 0 | 12.5107 | 39.95
2022-05-29 18:30 | 44710.7708 | 0 | 12.3517 | 39.95
2022-05-29 19:00 | 44710.7917 | 0 | 12.1879 | 39.95
2022-05-29 19:30 | 44710.8125 | 0 | 11.8259 | 39.95
2022-05-29 20:00 | 44710.8333 | 0 | 11.4016 | 39.95
2022-05-29 20:30 | 44710.8542 | 0 | 11.1231 | 39.95
2022-05-29 21:00 | 44710.875 | 0 | 10.5189 | 39.95
2022-05-29 21:30 | 44710.8958 | 0 | 10.1091 | 39.95
2022-05-29 22:00 | 44710.9167 | 0 | 9.5713 | 39.95
2022-05-29 22:30 | 44710.9375 | 0 | 8.9504 | 39.95
2022-05-29 23:00 | 44710.9583 | 0 | 8.4734 | 39.95
2022-05-29 23:30 | 44710.9792 | 0 | 7.8941 | 39.95
2022-05-30 | 44711 | 0 | 7.585 | 39.95
2022-05-30 00:30 | 44711.0208 | 0 | 7.4304 | 39.95
2022-05-30 01:00 | 44711.0417 | 0 | 7.1986 | 39.95
2022-05-30 01:30 | 44711.0625 | 0 | 7.1269 | 39.95
2022-05-30 02:00 | 44711.0833 | 0 | 7.1837 | 39.95
2022-05-30 02:30 | 44711.1042 | 0 | 7.2077 | 39.95
2022-05-30 03:00 | 44711.125 | 0 | 7.0978 | 39.95
2022-05-30 03:30 | 44711.1458 | 0 | 7.2605 | 39.95
2022-05-30 04:00 | 44711.1667 | 0 | 7.6356 | 39.95
2022-05-30 04:30 | 44711.1875 | 0 | 8.1709 | 39.95
2022-05-30 05:00 | 44711.2083 | 0 | 8.8445 | 39.95
2022-05-30 05:30 | 44711.2292 | 0 | 9.5165 | 39.95
2022-05-30 06:00 | 44711.25 | 0 | 20.1639 | 39.95
2022-05-30 06:30 | 44711.2708 | 0 | 23.5673 | 39.95
2022-05-30 07:00 | 44711.2917 | 0 | 25.5081 | 39.95
2022-05-30 07:30 | 44711.3125 | 0 | 25.979 | 39.95
2022-05-30 08:00 | 44711.3333 | 0 | 25.4194 | 39.95
2022-05-30 08:30 | 44711.3542 | 0 | 25.204 | 39.95
2022-05-30 09:00 | 44711.375 | 0 | 24.6699 | 39.95
2022-05-30 09:30 | 44711.3958 | 0 | 24.4258 | 39.95
2022-05-30 10:00 | 44711.4167 | 0 | 21.632 | 39.95
2022-05-30 10:30 | 44711.4375 | 0 | 23.427 | 39.95
2022-05-30 11:00 | 44711.4583 | 0 | 23.7992 | 39.95
2022-05-30 11:30 | 44711.4792 | 0 | 21.0328 | 39.95
2022-05-30 12:00 | 44711.5 | 0 | 21.4773 | 39.95
2022-05-30 12:30 | 44711.5208 | 0 | 19.0441 | 39.95
2022-05-30 13:00 | 44711.5417 | 0 | 22.8123 | 39.95
2022-05-30 13:30 | 44711.5625 | 0 | 23.721 | 39.95
2022-05-30 14:00 | 44711.5833 | 0 | 23.4064 | 39.95
2022-05-30 14:30 | 44711.6042 | 0 | 24.1337 | 39.95
2022-05-30 15:00 | 44711.625 | 0 | 24.775 | 39.95
2022-05-30 15:30 | 44711.6458 | 0 | 25.3176 | 39.95
2022-05-30 16:00 | 44711.6667 | 0 | 25.8637 | 39.95
2022-05-30 16:30 | 44711.6875 | 0 | 26.7049 | 39.95
2022-05-30 17:00 | 44711.7083 | 0 | 28.2429 | 39.95
2022-05-30 17:30 | 44711.7292 | 0 | 29.0957 | 39.95
2022-05-30 18:00 | 44711.75 | 0 | 29.2226 | 39.95
2022-05-30 18:30 | 44711.7708 | 0 | 29.0958 | 39.95
2022-05-30 19:00 | 44711.7917 | 0 | 28.1533 | 39.95
2022-05-30 19:30 | 44711.8125 | 0 | 27.5389 | 39.95
2022-05-30 20:00 | 44711.8333 | 0 | 26.9554 | 39.95
2022-05-30 20:30 | 44711.8542 | 0 | 25.3906 | 39.95
2022-05-30 21:00 | 44711.875 | 0 | 23.8326 | 39.95
2022-05-30 21:30 | 44711.8958 | 0 | 22.8903 | 39.95
2022-05-30 22:00 | 44711.9167 | 0 | 21.9423 | 39.95
2022-05-30 22:30 | 44711.9375 | 0 | 20.6259 | 39.95
2022-05-30 23:00 | 44711.9583 | 0 | 19.2889 | 39.95
2022-05-30 23:30 | 44711.9792 | 0 | 18.146 | 39.95
2022-05-31 | 44712 | 0 | 17.0624 | 39.95
2022-05-31 00:30 | 44712.0208 | 0 | 16.5372 | 39.95
2022-05-31 01:00 | 44712.0417 | 0 | 16.1533 | 39.95
2022-05-31 01:30 | 44712.0625 | 0 | 15.8577 | 39.95
2022-05-31 02:00 | 44712.0833 | 0 | 15.748 | 39.95
2022-05-31 02:30 | 44712.1042 | 0 | 15.7583 | 39.95
2022-05-31 03:00 | 44712.125 | 0 | 15.5911 | 39.95
2022-05-31 03:30 | 44712.1458 | 0 | 15.6356 | 39.95
2022-05-31 04:00 | 44712.1667 | 0 | 16.2973 | 39.95
2022-05-31 04:30 | 44712.1875 | 0 | 17.345 | 39.95
2022-05-31 05:00 | 44712.2083 | 0 | 18.2828 | 39.95
2022-05-31 05:30 | 44712.2292 | 0 | 19.9561 | 39.95
2022-05-31 06:00 | 44712.25 | 0 | 22.691 | 39.95
2022-05-31 06:30 | 44712.2708 | 0 | 25.5751 | 39.95
2022-05-31 07:00 | 44712.2917 | 0 | 26.5962 | 39.95
2022-05-31 07:30 | 44712.3125 | 0 | 25.3269 | 39.95
2022-05-31 08:00 | 44712.3333 | 0 | 23.5971 | 39.95
2022-05-31 08:30 | 44712.3542 | 0 | 21.8475 | 39.95
2022-05-31 09:00 | 44712.375 | 0 | 19.7671 | 39.95
2022-05-31 09:30 | 44712.3958 | 0 | 18.5478 | 39.95
2022-05-31 10:00 | 44712.4167 | 0 | 17.3717 | 39.95
2022-05-31 10:30 | 44712.4375 | 0 | 16.3995 | 39.95
2022-05-31 11:00 | 44712.4583 | 0 | 15.8955 | 39.95
2022-05-31 11:30 | 44712.4792 | 0 | 15.6655 | 39.95
2022-05-31 12:00 | 44712.5 | 0 | 15.2487 | 39.95
2022-05-31 12:30 | 44712.5208 | 0 | 15.335 | 39.95
2022-05-31 13:00 | 44712.5417 | 0 | 15.5467 | 39.95
2022-05-31 13:30 | 44712.5625 | 0 | 16.5757 | 39.95
2022-05-31 14:00 | 44712.5833 | 0 | 20.5076 | 39.95
2022-05-31 14:30 | 44712.6042 | 0 | 20.602 | 39.95
2022-05-31 15:00 | 44712.625 | 0 | 21.8741 | 39.95
2022-05-31 15:30 | 44712.6458 | 0 | 21.9383 | 39.95
2022-05-31 16:00 | 44712.6667 | 0 | 23.4982 | 39.95
2022-05-31 16:30 | 44712.6875 | 0 | 25.6123 | 39.95
2022-05-31 17:00 | 44712.7083 | 0 | 27.1733 | 39.95
2022-05-31 17:30 | 44712.7292 | 0 | 28.505 | 39.95
2022-05-31 18:00 | 44712.75 | 0 | 28.5235 | 39.95
2022-05-31 18:30 | 44712.7708 | 0 | 28.9863 | 39.95
2022-05-31 19:00 | 44712.7917 | 0 | 28.1955 | 39.95
2022-05-31 19:30 | 44712.8125 | 0 | 27.6025 | 39.95
2022-05-31 20:00 | 44712.8333 | 0 | 26.8175 | 39.95
2022-05-31 20:30 | 44712.8542 | 0 | 25.9214 | 39.95
2022-05-31 21:00 | 44712.875 | 0 | 24.2761 | 39.95
2022-05-31 21:30 | 44712.8958 | 0 | 23.2983 | 39.95
2022-05-31 22:00 | 44712.9167 | 0 | 22.0936 | 39.95
2022-05-31 22:30 | 44712.9375 | 0 | 20.474 | 39.95
2022-05-31 23:00 | 44712.9583 | 0 | 19.2972 | 39.95
2022-05-31 23:30 | 44712.9792 | 0 | 18.4175 | 39.95
2022-06-01 | 44713 | 0 | 16.9996 | 39.95
2022-06-01 00:30 | 44713.0208 | 0 | 16.4928 | 39.95
2022-06-01 01:00 | 44713.0417 | 0 | 16.0017 | 39.95
2022-06-01 01:30 | 44713.0625 | 0 | 15.6008 | 39.95
2022-06-01 02:00 | 44713.0833 | 0 | 15.6072 | 39.95
2022-06-01 02:30 | 44713.1042 | 0 | 15.7141 | 39.95
2022-06-01 03:00 | 44713.125 | 0 | 15.5979 | 39.95
2022-06-01 03:30 | 44713.1458 | 0 | 15.7239 | 39.95
2022-06-01 04:00 | 44713.1667 | 0 | 16.0032 | 39.95
2022-06-01 04:30 | 44713.1875 | 0 | 16.3933 | 39.95
2022-06-01 05:00 | 44713.2083 | 0 | 17.4507 | 39.95
2022-06-01 05:30 | 44713.2292 | 0 | 19.4049 | 39.95
2022-06-01 06:00 | 44713.25 | 0 | 22.5075 | 39.95
2022-06-01 06:30 | 44713.2708 | 0 | 24.7199 | 39.95
2022-06-01 07:00 | 44713.2917 | 0 | 25.9885 | 39.95
2022-06-01 07:30 | 44713.3125 | 0 | 24.4265 | 39.95
2022-06-01 08:00 | 44713.3333 | 0 | 22.9609 | 39.95
2022-06-01 08:30 | 44713.3542 | 0 | 21.0028 | 39.95
2022-06-01 09:00 | 44713.375 | 0 | 19.5412 | 39.95
2022-06-01 09:30 | 44713.3958 | 0 | 17.9901 | 39.95
2022-06-01 10:00 | 44713.4167 | 0 | 16.9564 | 39.95
2022-06-01 10:30 | 44713.4375 | 0 | 16.1368 | 39.95
2022-06-01 11:00 | 44713.4583 | 0 | 15.8333 | 39.95
2022-06-01 11:30 | 44713.4792 | 0 | 15.5063 | 39.95
2022-06-01 12:00 | 44713.5 | 0 | 15.0814 | 39.95
2022-06-01 12:30 | 44713.5208 | 0 | 15.4744 | 39.95
2022-06-01 13:00 | 44713.5417 | 0 | 15.9668 | 39.95
2022-06-01 13:30 | 44713.5625 | 0 | 16.9252 | 39.95
2022-06-01 14:00 | 44713.5833 | 0 | 18.1201 | 39.95
2022-06-01 14:30 | 44713.6042 | 0 | 19.1062 | 39.95
2022-06-01 15:00 | 44713.625 | 0 | 20.3406 | 39.95
2022-06-01 15:30 | 44713.6458 | 0 | 22.0315 | 39.95
2022-06-01 16:00 | 44713.6667 | 0 | 24.5778 | 39.95
2022-06-01 16:30 | 44713.6875 | 0 | 25.7057 | 39.95
2022-06-01 17:00 | 44713.7083 | 0 | 27.7289 | 39.95
2022-06-01 17:30 | 44713.7292 | 0 | 28.7724 | 39.95
2022-06-01 18:00 | 44713.75 | 0 | 29.2794 | 39.95
2022-06-01 18:30 | 44713.7708 | 0 | 29.5469 | 39.95
2022-06-01 19:00 | 44713.7917 | 0 | 28.7015 | 39.95
2022-06-01 19:30 | 44713.8125 | 0 | 28.6386 | 39.95
2022-06-01 20:00 | 44713.8333 | 0 | 27.8404 | 39.95
2022-06-01 20:30 | 44713.8542 | 0 | 26.5801 | 39.95
2022-06-01 21:00 | 44713.875 | 0 | 25.2342 | 39.95
2022-06-01 21:30 | 44713.8958 | 0 | 24.1489 | 39.95
2022-06-01 22:00 | 44713.9167 | 0 | 22.8642 | 39.95
2022-06-01 22:30 | 44713.9375 | 0 | 20.8423 | 39.95
2022-06-01 23:00 | 44713.9583 | 0 | 19.4232 | 39.95
2022-06-01 23:30 | 44713.9792 | 0 | 18.37 | 39.95
2022-06-02 | 44714 | 0 | 17.1401 | 39.95
2022-06-02 00:30 | 44714.0208 | 0 | 16.3973 | 39.95
2022-06-02 01:00 | 44714.0417 | 0 | 16.3772 | 39.95
2022-06-02 01:30 | 44714.0625 | 0 | 15.9884 | 39.95
2022-06-02 02:00 | 44714.0833 | 0 | 15.8374 | 39.95
2022-06-02 02:30 | 44714.1042 | 0 | 15.8086 | 39.95
2022-06-02 03:00 | 44714.125 | 0 | 15.5957 | 39.95
2022-06-02 03:30 | 44714.1458 | 0 | 16.2072 | 39.95
2022-06-02 04:00 | 44714.1667 | 0 | 16.7091 | 39.95
2022-06-02 04:30 | 44714.1875 | 0 | 17.5832 | 39.95
2022-06-02 05:00 | 44714.2083 | 0 | 18.9147 | 39.95
2022-06-02 05:30 | 44714.2292 | 0 | 20.9863 | 39.95
2022-06-02 06:00 | 44714.25 | 0 | 23.8041 | 39.95
2022-06-02 06:30 | 44714.2708 | 0 | 26.6813 | 39.95
2022-06-02 07:00 | 44714.2917 | 0 | 27.834 | 39.95
2022-06-02 07:30 | 44714.3125 | 0 | 28.0054 | 39.95
2022-06-02 08:00 | 44714.3333 | 0 | 25.7034 | 39.95
2022-06-02 08:30 | 44714.3542 | 0 | 24.3469 | 39.95
2022-06-02 09:00 | 44714.375 | 0 | 21.0051 | 39.95
2022-06-02 09:30 | 44714.3958 | 0 | 22.5772 | 39.95
2022-06-02 10:00 | 44714.4167 | 0 | 18.613 | 39.95
2022-06-02 10:30 | 44714.4375 | 0 | 18.0729 | 39.95
2022-06-02 11:00 | 44714.4583 | 0 | 16.6476 | 39.95
2022-06-02 11:30 | 44714.4792 | 0 | 16.5557 | 39.95
2022-06-02 12:00 | 44714.5 | 0 | 16.0373 | 39.95
2022-06-02 12:30 | 44714.5208 | 0 | 16.1939 | 39.95
2022-06-02 13:00 | 44714.5417 | 0 | 16.7932 | 39.95
2022-06-02 13:30 | 44714.5625 | 0 | 17.5708 | 39.95
2022-06-02 14:00 | 44714.5833 | 0 | 18.3205 | 39.95
2022-06-02 14:30 | 44714.6042 | 0 | 19.3552 | 39.95
2022-06-02 15:00 | 44714.625 | 0 | 20.7501 | 39.95
2022-06-02 15:30 | 44714.6458 | 0 | 22.4419 | 39.95
2022-06-02 16:00 | 44714.6667 | 0 | 24.1904 | 39.95
2022-06-02 16:30 | 44714.6875 | 0 | 25.7624 | 39.95
2022-06-02 17:00 | 44714.7083 | 0 | 27.6631 | 39.95
2022-06-02 17:30 | 44714.7292 | 0 | 29.3945 | 39.95
2022-06-02 18:00 | 44714.75 | 0 | 29.8422 | 39.95
2022-06-02 18:30 | 44714.7708 | 0 | 30.3073 | 39.95
2022-06-02 19:00 | 44714.7917 | 0 | 29.6184 | 39.95
2022-06-02 19:30 | 44714.8125 | 0 | 29.3777 | 39.95
2022-06-02 20:00 | 44714.8333 | 0 | 28.3657 | 39.95
2022-06-02 20:30 | 44714.8542 | 0 | 27.5839 | 39.95
2022-06-02 21:00 | 44714.875 | 0 | 26.2969 | 39.95
2022-06-02 21:30 | 44714.8958 | 0 | 24.9654 | 39.95
2022-06-02 22:00 | 44714.9167 | 0 | 23.5951 | 39.95
2022-06-02 22:30 | 44714.9375 | 0 | 21.3114 | 39.95
2022-06-02 23:00 | 44714.9583 | 0 | 20.1832 | 39.95
2022-06-02 23:30 | 44714.9792 | 0 | 19.0561 | 39.95
2022-06-03 | 44715 | 0 | 17.9493 | 39.95
2022-06-03 00:30 | 44715.0208 | 0 | 17.2516 | 39.95
2022-06-03 01:00 | 44715.0417 | 0 | 16.9401 | 39.95
2022-06-03 01:30 | 44715.0625 | 0 | 16.5026 | 39.95
2022-06-03 02:00 | 44715.0833 | 0 | 16.2823 | 39.95
2022-06-03 02:30 | 44715.1042 | 0 | 16.4763 | 39.95
2022-06-03 03:00 | 44715.125 | 0 | 16.0692 | 39.95
2022-06-03 03:30 | 44715.1458 | 0 | 16.1919 | 39.95
2022-06-03 04:00 | 44715.1667 | 0 | 16.7645 | 39.95
2022-06-03 04:30 | 44715.1875 | 0 | 17.6084 | 39.95
2022-06-03 05:00 | 44715.2083 | 0 | 19.1794 | 39.95
2022-06-03 05:30 | 44715.2292 | 0 | 20.7423 | 39.95
2022-06-03 06:00 | 44715.25 | 0 | 23.9325 | 39.95
2022-06-03 06:30 | 44715.2708 | 0 | 27.1539 | 39.95
2022-06-03 07:00 | 44715.2917 | 0 | 28.5067 | 39.95
2022-06-03 07:30 | 44715.3125 | 0 | 27.4167 | 39.95
2022-06-03 08:00 | 44715.3333 | 0 | 25.8178 | 39.95
2022-06-03 08:30 | 44715.3542 | 0 | 23.6969 | 39.95
2022-06-03 09:00 | 44715.375 | 0 | 21.5561 | 39.95
2022-06-03 09:30 | 44715.3958 | 0 | 20.2396 | 39.95
2022-06-03 10:00 | 44715.4167 | 0 | 20.6825 | 39.95
2022-06-03 10:30 | 44715.4375 | 0 | 22.0779 | 39.95
2022-06-03 11:00 | 44715.4583 | 0 | 21.9394 | 39.95
2022-06-03 11:30 | 44715.4792 | 0 | 18.8073 | 39.95
2022-06-03 12:00 | 44715.5 | 0 | 20.2813 | 39.95
2022-06-03 12:30 | 44715.5208 | 0 | 18.2102 | 39.95
2022-06-03 13:00 | 44715.5417 | 0 | 18.3016 | 39.95
2022-06-03 13:30 | 44715.5625 | 0 | 17.2848 | 39.95
2022-06-03 14:00 | 44715.5833 | 0 | 18.7024 | 39.95
2022-06-03 14:30 | 44715.6042 | 0 | 21.9231 | 39.95
2022-06-03 15:00 | 44715.625 | 0 | 22.8665 | 39.95
2022-06-03 15:30 | 44715.6458 | 0 | 23.41 | 39.95
2022-06-03 16:00 | 44715.6667 | 0 | 24.5246 | 39.95
2022-06-03 16:30 | 44715.6875 | 0 | 26.0902 | 39.95
2022-06-03 17:00 | 44715.7083 | 0 | 26.8602 | 39.95
2022-06-03 17:30 | 44715.7292 | 0 | 27.4978 | 39.95
2022-06-03 18:00 | 44715.75 | 0 | 27.1141 | 39.95
2022-06-03 18:30 | 44715.7708 | 0 | 27.1701 | 39.95
2022-06-03 19:00 | 44715.7917 | 0 | 26.7302 | 39.95
2022-06-03 19:30 | 44715.8125 | 0 | 26.3257 | 39.95
2022-06-03 20:00 | 44715.8333 | 0 | 25.6742 | 39.95
2022-06-03 20:30 | 44715.8542 | 0 | 24.8047 | 39.95
2022-06-03 21:00 | 44715.875 | 0 | 23.7797 | 39.95
2022-06-03 21:30 | 44715.8958 | 0 | 23.0248 | 39.95
2022-06-03 22:00 | 44715.9167 | 0 | 22.2642 | 39.95
2022-06-03 22:30 | 44715.9375 | 0 | 20.5037 | 39.95
2022-06-03 23:00 | 44715.9583 | 0 | 19.7055 | 39.95
2022-06-03 23:30 | 44715.9792 | 0 | 18.6116 | 39.95
2022-06-04 | 44716 | 0 | 17.3148 | 39.95
2022-06-04 00:30 | 44716.0208 | 0 | 16.6227 | 39.95
2022-06-04 01:00 | 44716.0417 | 0 | 16.2995 | 39.95
2022-06-04 01:30 | 44716.0625 | 0 | 15.7857 | 39.95
2022-06-04 02:00 | 44716.0833 | 0 | 15.6063 | 39.95
2022-06-04 02:30 | 44716.1042 | 0 | 15.3684 | 39.95
2022-06-04 03:00 | 44716.125 | 0 | 15.2903 | 39.95
2022-06-04 03:30 | 44716.1458 | 0 | 15.2373 | 39.95
2022-06-04 04:00 | 44716.1667 | 0 | 15.575 | 39.95
2022-06-04 04:30 | 44716.1875 | 0 | 15.5213 | 39.95
2022-06-04 05:00 | 44716.2083 | 0 | 16.1736 | 39.95
2022-06-04 05:30 | 44716.2292 | 0 | 16.6653 | 39.95
2022-06-04 06:00 | 44716.25 | 0 | 17.0913 | 39.95
2022-06-04 06:30 | 44716.2708 | 0 | 18.3203 | 39.95
2022-06-04 07:00 | 44716.2917 | 0 | 19.0342 | 39.95
2022-06-04 07:30 | 44716.3125 | 0 | 20.2491 | 39.95
2022-06-04 08:00 | 44716.3333 | 0 | 18.7927 | 39.95
2022-06-04 08:30 | 44716.3542 | 0 | 18.4494 | 39.95
2022-06-04 09:00 | 44716.375 | 0 | 17.2157 | 39.95
2022-06-04 09:30 | 44716.3958 | 0 | 19.22 | 39.95
2022-06-04 10:00 | 44716.4167 | 0 | 17.5891 | 39.95
2022-06-04 10:30 | 44716.4375 | 0 | 15.7073 | 39.95
2022-06-04 11:00 | 44716.4583 | 0 | 14.1782 | 39.95
2022-06-04 11:30 | 44716.4792 | 0 | 12.1723 | 39.95
2022-06-04 12:00 | 44716.5 | 0 | 11.9266 | 39.95
2022-06-04 12:30 | 44716.5208 | 0 | 11.7983 | 39.95
2022-06-04 13:00 | 44716.5417 | 0 | 12.2004 | 39.95
2022-06-04 13:30 | 44716.5625 | 0 | 13.0801 | 39.95
2022-06-04 14:00 | 44716.5833 | 0 | 14.2396 | 39.95
2022-06-04 14:30 | 44716.6042 | 0 | 15.1076 | 39.95
2022-06-04 15:00 | 44716.625 | 0 | 16.5181 | 39.95
2022-06-04 15:30 | 44716.6458 | 0 | 18.1167 | 39.95
2022-06-04 16:00 | 44716.6667 | 0 | 19.9661 | 39.95
2022-06-04 16:30 | 44716.6875 | 0 | 21.6907 | 39.95
2022-06-04 17:00 | 44716.7083 | 0 | 23.1533 | 39.95
2022-06-04 17:30 | 44716.7292 | 0 | 24.0761 | 39.95
2022-06-04 18:00 | 44716.75 | 0 | 24.1773 | 39.95
2022-06-04 18:30 | 44716.7708 | 0 | 24.4711 | 39.95
2022-06-04 19:00 | 44716.7917 | 0 | 24.1694 | 39.95
2022-06-04 19:30 | 44716.8125 | 0 | 23.6788 | 39.95
2022-06-04 20:00 | 44716.8333 | 0 | 23.1851 | 39.95
2022-06-04 20:30 | 44716.8542 | 0 | 22.2931 | 39.95
2022-06-04 21:00 | 44716.875 | 0 | 21.3952 | 39.95
2022-06-04 21:30 | 44716.8958 | 0 | 20.8176 | 39.95
2022-06-04 22:00 | 44716.9167 | 0 | 20.3254 | 39.95
2022-06-04 22:30 | 44716.9375 | 0 | 18.8074 | 39.95
2022-06-04 23:00 | 44716.9583 | 0 | 17.9406 | 39.95
2022-06-04 23:30 | 44716.9792 | 0 | 17.1155 | 39.95
2022-06-05 | 44717 | 0 | 16.0349 | 39.95
2022-06-05 00:30 | 44717.0208 | 0 | 9.632 | 39.95
2022-06-05 01:00 | 44717.0417 | 0 | 7.8393 | 39.95
2022-06-05 01:30 | 44717.0625 | 0 | 7.566 | 39.95
2022-06-05 02:00 | 44717.0833 | 0 | 7.4397 | 39.95
2022-06-05 02:30 | 44717.1042 | 0 | 7.3979 | 39.95
2022-06-05 03:00 | 44717.125 | 0 | 7.4156 | 39.95
2022-06-05 03:30 | 44717.1458 | 0 | 7.4396 | 39.95
2022-06-05 04:00 | 44717.1667 | 0 | 7.3177 | 39.95
2022-06-05 04:30 | 44717.1875 | 0 | 7.4644 | 39.95
2022-06-05 05:00 | 44717.2083 | 0 | 7.6138 | 39.95
2022-06-05 05:30 | 44717.2292 | 0 | 7.8763 | 39.95
2022-06-05 06:00 | 44717.25 | 0 | 8.1647 | 39.95
2022-06-05 06:30 | 44717.2708 | 0 | 8.664 | 39.95
2022-06-05 07:00 | 44717.2917 | 0 | 9.2318 | 39.95
2022-06-05 07:30 | 44717.3125 | 0 | 8.9192 | 39.95
2022-06-05 08:00 | 44717.3333 | 0 | 8.7802 | 39.95
2022-06-05 08:30 | 44717.3542 | 0 | 8.5138 | 39.95
2022-06-05 09:00 | 44717.375 | 0 | 8.0335 | 39.95
2022-06-05 09:30 | 44717.3958 | 0 | 7.3857 | 39.95
2022-06-05 10:00 | 44717.4167 | 0 | 7.0272 | 39.95
2022-06-05 10:30 | 44717.4375 | 0 | 6.5404 | 39.95
2022-06-05 11:00 | 44717.4583 | 0 | 6.0759 | 39.95
2022-06-05 11:30 | 44717.4792 | 0 | 5.9513 | 39.95
2022-06-05 12:00 | 44717.5 | 0 | 5.7458 | 39.95
2022-06-05 12:30 | 44717.5208 | 0 | 5.7876 | 39.95
2022-06-05 13:00 | 44717.5417 | 0 | 5.9131 | 39.95
2022-06-05 13:30 | 44717.5625 | 0 | 6.1985 | 39.95
2022-06-05 14:00 | 44717.5833 | 0 | 6.8008 | 39.95
2022-06-05 14:30 | 44717.6042 | 0 | 7.4794 | 39.95
2022-06-05 15:00 | 44717.625 | 0 | 8.3038 | 39.95
2022-06-05 15:30 | 44717.6458 | 0 | 9.2383 | 39.95
2022-06-05 16:00 | 44717.6667 | 0 | 10.3258 | 39.95
2022-06-05 16:30 | 44717.6875 | 0 | 11.5032 | 39.95
2022-06-05 17:00 | 44717.7083 | 0 | 12.4899 | 39.95
2022-06-05 17:30 | 44717.7292 | 0 | 13.2458 | 39.95
2022-06-05 18:00 | 44717.75 | 0 | 13.4117 | 39.95
2022-06-05 18:30 | 44717.7708 | 0 | 13.3503 | 39.95
2022-06-05 19:00 | 44717.7917 | 0 | 12.7976 | 39.95
2022-06-05 19:30 | 44717.8125 | 0 | 12.5426 | 39.95
2022-06-05 20:00 | 44717.8333 | 0 | 12.1684 | 39.95
2022-06-05 20:30 | 44717.8542 | 0 | 11.5818 | 39.95
2022-06-05 21:00 | 44717.875 | 0 | 10.8893 | 39.95
2022-06-05 21:30 | 44717.8958 | 0 | 10.2292 | 39.95
2022-06-05 22:00 | 44717.9167 | 0 | 9.9352 | 39.95
2022-06-05 22:30 | 44717.9375 | 0 | 9.1369 | 39.95
2022-06-05 23:00 | 44717.9583 | 0 | 8.657 | 39.95
2022-06-05 23:30 | 44717.9792 | 0 | 8.1965 | 39.95
2022-06-06 | 44718 | 0 | 7.8186 | 39.95
2022-06-06 00:30 | 44718.0208 | 0 | 7.5408 | 39.95
2022-06-06 01:00 | 44718.0417 | 0 | 7.5181 | 39.95
2022-06-06 01:30 | 44718.0625 | 0 | 7.3622 | 39.95
2022-06-06 02:00 | 44718.0833 | 0 | 7.2765 | 39.95
2022-06-06 02:30 | 44718.1042 | 0 | 7.4116 | 39.95
2022-06-06 03:00 | 44718.125 | 0 | 7.3264 | 39.95
2022-06-06 03:30 | 44718.1458 | 0 | 7.6097 | 39.95
2022-06-06 04:00 | 44718.1667 | 0 | 7.9677 | 39.95
2022-06-06 04:30 | 44718.1875 | 0 | 8.3945 | 39.95
2022-06-06 05:00 | 44718.2083 | 0 | 8.9443 | 39.95
2022-06-06 05:30 | 44718.2292 | 0 | 9.897 | 39.95
2022-06-06 06:00 | 44718.25 | 0 | 11.222 | 39.95
2022-06-06 06:30 | 44718.2708 | 0 | 12.2904 | 39.95
2022-06-06 07:00 | 44718.2917 | 0 | 13.2059 | 39.95
2022-06-06 07:30 | 44718.3125 | 0 | 13.3996 | 39.95
2022-06-06 08:00 | 44718.3333 | 0 | 13.8267 | 39.95
2022-06-06 08:30 | 44718.3542 | 0 | 13.3186 | 39.95
2022-06-06 09:00 | 44718.375 | 0 | 12.8582 | 39.95
2022-06-06 09:30 | 44718.3958 | 0 | 12.33 | 39.95
2022-06-06 10:00 | 44718.4167 | 0 | 12.8282 | 39.95
2022-06-06 10:30 | 44718.4375 | 0 | 12.3555 | 39.95
2022-06-06 11:00 | 44718.4583 | 0 | 11.8867 | 39.95
2022-06-06 11:30 | 44718.4792 | 0 | 11.3729 | 39.95
2022-06-06 12:00 | 44718.5 | 0 | 9.3277 | 39.95
2022-06-06 12:30 | 44718.5208 | 0 | 10.4313 | 39.95
2022-06-06 13:00 | 44718.5417 | 0 | 10.067 | 39.95
2022-06-06 13:30 | 44718.5625 | 0 | 8.9887 | 39.95
2022-06-06 14:00 | 44718.5833 | 0 | 11.1032 | 39.95
2022-06-06 14:30 | 44718.6042 | 0 | 11.3751 | 39.95
2022-06-06 15:00 | 44718.625 | 0 | 11.2595 | 39.95
2022-06-06 15:30 | 44718.6458 | 0 | 11.3252 | 39.95
2022-06-06 16:00 | 44718.6667 | 0 | 12.1444 | 39.95
2022-06-06 16:30 | 44718.6875 | 0 | 12.9992 | 39.95
2022-06-06 17:00 | 44718.7083 | 0 | 14.2288 | 39.95
2022-06-06 17:30 | 44718.7292 | 0 | 15.1631 | 39.95
2022-06-06 18:00 | 44718.75 | 0 | 15.3093 | 39.95
2022-06-06 18:30 | 44718.7708 | 0 | 15.4981 | 39.95
2022-06-06 19:00 | 44718.7917 | 0 | 15.0703 | 39.95
2022-06-06 19:30 | 44718.8125 | 0 | 14.6436 | 39.95
2022-06-06 20:00 | 44718.8333 | 0 | 14.3477 | 39.95
2022-06-06 20:30 | 44718.8542 | 0 | 13.6818 | 39.95
2022-06-06 21:00 | 44718.875 | 0 | 12.9029 | 39.95
2022-06-06 21:30 | 44718.8958 | 0 | 12.3464 | 39.95
2022-06-06 22:00 | 44718.9167 | 0 | 11.7363 | 39.95
2022-06-06 22:30 | 44718.9375 | 0 | 10.7301 | 39.95
2022-06-06 23:00 | 44718.9583 | 0 | 10.0633 | 39.95
2022-06-06 23:30 | 44718.9792 | 0 | 9.5271 | 39.95
2022-06-07 | 44719 | 0 | 8.9747 | 39.95
2022-06-07 00:30 | 44719.0208 | 0 | 8.5482 | 39.95
2022-06-07 01:00 | 44719.0417 | 0 | 8.3665 | 39.95
2022-06-07 01:30 | 44719.0625 | 0 | 8.0952 | 39.95
2022-06-07 02:00 | 44719.0833 | 0 | 7.9985 | 39.95
2022-06-07 02:30 | 44719.1042 | 0 | 8.0878 | 39.95
2022-06-07 03:00 | 44719.125 | 0 | 7.8233 | 39.95
2022-06-07 03:30 | 44719.1458 | 0 | 8.0708 | 39.95
2022-06-07 04:00 | 44719.1667 | 0 | 8.5146 | 39.95
2022-06-07 04:30 | 44719.1875 | 0 | 8.9132 | 39.95
2022-06-07 05:00 | 44719.2083 | 0 | 9.6676 | 39.95
2022-06-07 05:30 | 44719.2292 | 0 | 10.674 | 39.95
2022-06-07 06:00 | 44719.25 | 0 | 12.4739 | 39.95
2022-06-07 06:30 | 44719.2708 | 0 | 13.9632 | 39.95
2022-06-07 07:00 | 44719.2917 | 0 | 15.0497 | 39.95
2022-06-07 07:30 | 44719.3125 | 0 | 14.9656 | 39.95
2022-06-07 08:00 | 44719.3333 | 0 | 14.8023 | 39.95
2022-06-07 08:30 | 44719.3542 | 0 | 13.9001 | 39.95
2022-06-07 09:00 | 44719.375 | 0 | 13.4546 | 39.95
2022-06-07 09:30 | 44719.3958 | 0 | 13.4241 | 39.95
2022-06-07 10:00 | 44719.4167 | 0 | 13.3363 | 39.95
2022-06-07 10:30 | 44719.4375 | 0 | 13.3595 | 39.95
2022-06-07 11:00 | 44719.4583 | 0 | 13.2848 | 39.95
2022-06-07 11:30 | 44719.4792 | 0 | 13.0651 | 39.95
2022-06-07 12:00 | 44719.5 | 0 | 12.2422 | 39.95
2022-06-07 12:30 | 44719.5208 | 0 | 11.322 | 39.95
2022-06-07 13:00 | 44719.5417 | 0 | 11.6389 | 39.95
2022-06-07 13:30 | 44719.5625 | 0 | 12.416 | 39.95
2022-06-07 14:00 | 44719.5833 | 0 | 13.0472 | 39.95
2022-06-07 14:30 | 44719.6042 | 0 | 13.3498 | 39.95
2022-06-07 15:00 | 44719.625 | 0 | 13.54 | 39.95
2022-06-07 15:30 | 44719.6458 | 0 | 14.1188 | 39.95
2022-06-07 16:00 | 44719.6667 | 0 | 14.5939 | 39.95
2022-06-07 16:30 | 44719.6875 | 0 | 15.4365 | 39.95
2022-06-07 17:00 | 44719.7083 | 0 | 16.5579 | 39.95
2022-06-07 17:30 | 44719.7292 | 0 | 17.342 | 39.95
2022-06-07 18:00 | 44719.75 | 0 | 17.709 | 39.95
2022-06-07 18:30 | 44719.7708 | 0 | 17.5909 | 39.95
2022-06-07 19:00 | 44719.7917 | 0 | 17.33 | 39.95
2022-06-07 19:30 | 44719.8125 | 0 | 16.7782 | 39.95
2022-06-07 20:00 | 44719.8333 | 0 | 16.0413 | 39.95
2022-06-07 20:30 | 44719.8542 | 0 | 15.347 | 39.95
2022-06-07 21:00 | 44719.875 | 0 | 14.444 | 39.95
2022-06-07 21:30 | 44719.8958 | 0 | 13.5105 | 39.95
2022-06-07 22:00 | 44719.9167 | 0 | 12.5643 | 39.95
2022-06-07 22:30 | 44719.9375 | 0 | 11.405 | 39.95
2022-06-07 23:00 | 44719.9583 | 0 | 10.6835 | 39.95
2022-06-07 23:30 | 44719.9792 | 0 | 10.2572 | 39.95
2022-06-08 | 44720 | 0 | 9.4382 | 39.95
2022-06-08 00:30 | 44720.0208 | 0 | 8.9666 | 39.95
2022-06-08 01:00 | 44720.0417 | 0 | 8.8258 | 39.95
2022-06-08 01:30 | 44720.0625 | 0 | 8.578 | 39.95
2022-06-08 02:00 | 44720.0833 | 0 | 8.5196 | 39.95
2022-06-08 02:30 | 44720.1042 | 0 | 8.4411 | 39.95
2022-06-08 03:00 | 44720.125 | 0 | 8.3725 | 39.95
2022-06-08 03:30 | 44720.1458 | 0 | 8.5311 | 39.95
2022-06-08 04:00 | 44720.1667 | 0 | 8.7677 | 39.95
2022-06-08 04:30 | 44720.1875 | 0 | 9.2227 | 39.95
2022-06-08 05:00 | 44720.2083 | 0 | 10.2489 | 39.95
2022-06-08 05:30 | 44720.2292 | 0 | 11.3062 | 39.95
2022-06-08 06:00 | 44720.25 | 0 | 13.2269 | 39.95
2022-06-08 06:30 | 44720.2708 | 0 | 15.2569 | 39.95
2022-06-08 07:00 | 44720.2917 | 0 | 16.5398 | 39.95
2022-06-08 07:30 | 44720.3125 | 0 | 15.5463 | 39.95
2022-06-08 08:00 | 44720.3333 | 0 | 14.3923 | 39.95
2022-06-08 08:30 | 44720.3542 | 0 | 13.11 | 39.95
2022-06-08 09:00 | 44720.375 | 0 | 11.9147 | 39.95
2022-06-08 09:30 | 44720.3958 | 0 | 10.8137 | 39.95
2022-06-08 10:00 | 44720.4167 | 0 | 10.0341 | 39.95
2022-06-08 10:30 | 44720.4375 | 0 | 9.5303 | 39.95
2022-06-08 11:00 | 44720.4583 | 0 | 9.1226 | 39.95
2022-06-08 11:30 | 44720.4792 | 0 | 8.839 | 39.95
2022-06-08 12:00 | 44720.5 | 0 | 8.57 | 39.95
2022-06-08 12:30 | 44720.5208 | 0 | 8.4574 | 39.95
2022-06-08 13:00 | 44720.5417 | 0 | 8.7888 | 39.95
2022-06-08 13:30 | 44720.5625 | 0 | 9.2343 | 39.95
2022-06-08 14:00 | 44720.5833 | 0 | 9.6584 | 39.95
2022-06-08 14:30 | 44720.6042 | 0 | 10.2428 | 39.95
2022-06-08 15:00 | 44720.625 | 0 | 10.8802 | 39.95
2022-06-08 15:30 | 44720.6458 | 0 | 11.7992 | 39.95
2022-06-08 16:00 | 44720.6667 | 0 | 12.766 | 39.95
2022-06-08 16:30 | 44720.6875 | 0 | 13.9407 | 39.95
2022-06-08 17:00 | 44720.7083 | 0 | 15.0403 | 39.95
2022-06-08 17:30 | 44720.7292 | 0 | 16.1559 | 39.95
2022-06-08 18:00 | 44720.75 | 0 | 16.7272 | 39.95
2022-06-08 18:30 | 44720.7708 | 0 | 16.9419 | 39.95
2022-06-08 19:00 | 44720.7917 | 0 | 16.6957 | 39.95
2022-06-08 19:30 | 44720.8125 | 0 | 16.5489 | 39.95
2022-06-08 20:00 | 44720.8333 | 0 | 16.0464 | 39.95
2022-06-08 20:30 | 44720.8542 | 0 | 15.5817 | 39.95
2022-06-08 21:00 | 44720.875 | 0 | 14.9281 | 39.95
2022-06-08 21:30 | 44720.8958 | 0 | 14.1702 | 39.95
2022-06-08 22:00 | 44720.9167 | 0 | 13.2378 | 39.95
2022-06-08 22:30 | 44720.9375 | 0 | 12.2772 | 39.95
2022-06-08 23:00 | 44720.9583 | 0 | 11.2733 | 39.95
2022-06-08 23:30 | 44720.9792 | 0 | 10.5384 | 39.95
2022-06-09 | 44721 | 0 | 9.7918 | 39.95
2022-06-09 00:30 | 44721.0208 | 0 | 9.4444 | 39.95
2022-06-09 01:00 | 44721.0417 | 0 | 9.245 | 39.95
2022-06-09 01:30 | 44721.0625 | 0 | 8.8342 | 39.95
2022-06-09 02:00 | 44721.0833 | 0 | 8.8277 | 39.95
2022-06-09 02:30 | 44721.1042 | 0 | 8.803 | 39.95
2022-06-09 03:00 | 44721.125 | 0 | 8.6118 | 39.95
2022-06-09 03:30 | 44721.1458 | 0 | 8.7883 | 39.95
2022-06-09 04:00 | 44721.1667 | 0 | 9.1376 | 39.95
2022-06-09 04:30 | 44721.1875 | 0 | 9.6318 | 39.95
2022-06-09 05:00 | 44721.2083 | 0 | 10.7121 | 39.95
2022-06-09 05:30 | 44721.2292 | 0 | 11.8117 | 39.95
2022-06-09 06:00 | 44721.25 | 0 | 13.7775 | 39.95
2022-06-09 06:30 | 44721.2708 | 0 | 15.8349 | 39.95
2022-06-09 07:00 | 44721.2917 | 0 | 16.9782 | 39.95
2022-06-09 07:30 | 44721.3125 | 0 | 16.3526 | 39.95
2022-06-09 08:00 | 44721.3333 | 0 | 15.1887 | 39.95
2022-06-09 08:30 | 44721.3542 | 0 | 13.9393 | 39.95
2022-06-09 09:00 | 44721.375 | 0 | 12.8927 | 39.95
2022-06-09 09:30 | 44721.3958 | 0 | 11.9561 | 39.95
2022-06-09 10:00 | 44721.4167 | 0 | 10.9658 | 39.95
2022-06-09 10:30 | 44721.4375 | 0 | 10.2517 | 39.95
2022-06-09 11:00 | 44721.4583 | 0 | 9.8554 | 39.95
2022-06-09 11:30 | 44721.4792 | 0 | 9.5104 | 39.95
2022-06-09 12:00 | 44721.5 | 0 | 9.2668 | 39.95
2022-06-09 12:30 | 44721.5208 | 0 | 8.9659 | 39.95
2022-06-09 13:00 | 44721.5417 | 0 | 9.0106 | 39.95
2022-06-09 13:30 | 44721.5625 | 0 | 9.4228 | 39.95
2022-06-09 14:00 | 44721.5833 | 0 | 10.2191 | 39.95
2022-06-09 14:30 | 44721.6042 | 0 | 10.5413 | 39.95
2022-06-09 15:00 | 44721.625 | 0 | 11.2807 | 39.95
2022-06-09 15:30 | 44721.6458 | 0 | 12.3662 | 39.95
2022-06-09 16:00 | 44721.6667 | 0 | 13.2701 | 39.95
2022-06-09 16:30 | 44721.6875 | 0 | 14.6299 | 39.95
2022-06-09 17:00 | 44721.7083 | 0 | 16.1461 | 39.95
2022-06-09 17:30 | 44721.7292 | 0 | 17.4801 | 39.95
2022-06-09 18:00 | 44721.75 | 0 | 17.8759 | 39.95
2022-06-09 18:30 | 44721.7708 | 0 | 18.2787 | 39.95
2022-06-09 19:00 | 44721.7917 | 0 | 18.2202 | 39.95
2022-06-09 19:30 | 44721.8125 | 0 | 18.0435 | 39.95
2022-06-09 20:00 | 44721.8333 | 0 | 17.488 | 39.95
2022-06-09 20:30 | 44721.8542 | 0 | 16.7178 | 39.95
2022-06-09 21:00 | 44721.875 | 0 | 15.6702 | 39.95
2022-06-09 21:30 | 44721.8958 | 0 | 14.7384 | 39.95
2022-06-09 22:00 | 44721.9167 | 0 | 13.6917 | 39.95
2022-06-09 22:30 | 44721.9375 | 0 | 12.4753 | 39.95
2022-06-09 23:00 | 44721.9583 | 0 | 11.6138 | 39.95
2022-06-09 23:30 | 44721.9792 | 0 | 10.9301 | 39.95
2022-06-10 | 44722 | 0 | 10.2394 | 39.95
2022-06-10 00:30 | 44722.0208 | 0 | 9.7834 | 39.95
2022-06-10 01:00 | 44722.0417 | 0 | 9.4532 | 39.95
2022-06-10 01:30 | 44722.0625 | 0 | 9.2118 | 39.95
2022-06-10 02:00 | 44722.0833 | 0 | 9.0235 | 39.95
2022-06-10 02:30 | 44722.1042 | 0 | 9.1369 | 39.95
2022-06-10 03:00 | 44722.125 | 0 | 9.11 | 39.95
2022-06-10 03:30 | 44722.1458 | 0 | 9.1782 | 39.95
2022-06-10 04:00 | 44722.1667 | 0 | 9.5963 | 39.95
2022-06-10 04:30 | 44722.1875 | 0 | 10.0435 | 39.95
2022-06-10 05:00 | 44722.2083 | 0 | 11.1675 | 39.95
2022-06-10 05:30 | 44722.2292 | 0 | 12.185 | 39.95
2022-06-10 06:00 | 44722.25 | 0 | 14.1807 | 39.95
2022-06-10 06:30 | 44722.2708 | 0 | 16.4656 | 39.95
2022-06-10 07:00 | 44722.2917 | 0 | 17.7077 | 39.95
2022-06-10 07:30 | 44722.3125 | 0 | 16.9546 | 39.95
2022-06-10 08:00 | 44722.3333 | 0 | 16.0311 | 39.95
2022-06-10 08:30 | 44722.3542 | 0 | 14.6894 | 39.95
2022-06-10 09:00 | 44722.375 | 0 | 13.5707 | 39.95
2022-06-10 09:30 | 44722.3958 | 0 | 12.5388 | 39.95
2022-06-10 10:00 | 44722.4167 | 0 | 11.6966 | 39.95
2022-06-10 10:30 | 44722.4375 | 0 | 11.0256 | 39.95
2022-06-10 11:00 | 44722.4583 | 0 | 10.3121 | 39.95
2022-06-10 11:30 | 44722.4792 | 0 | 9.8727 | 39.95
2022-06-10 12:00 | 44722.5 | 0 | 9.4405 | 39.95
2022-06-10 12:30 | 44722.5208 | 0 | 9.39 | 39.95
2022-06-10 13:00 | 44722.5417 | 0 | 9.5236 | 39.95
2022-06-10 13:30 | 44722.5625 | 0 | 9.8414 | 39.95
2022-06-10 14:00 | 44722.5833 | 0 | 10.2454 | 39.95
2022-06-10 14:30 | 44722.6042 | 0 | 10.6877 | 39.95
2022-06-10 15:00 | 44722.625 | 0 | 11.2947 | 39.95
2022-06-10 15:30 | 44722.6458 | 0 | 12.3903 | 39.95
2022-06-10 16:00 | 44722.6667 | 0 | 13.5731 | 39.95
2022-06-10 16:30 | 44722.6875 | 0 | 14.7355 | 39.95
2022-06-10 17:00 | 44722.7083 | 0 | 16.1826 | 39.95
2022-06-10 17:30 | 44722.7292 | 0 | 17.1131 | 39.95
2022-06-10 18:00 | 44722.75 | 0 | 17.4068 | 39.95
2022-06-10 18:30 | 44722.7708 | 0 | 17.5143 | 39.95
2022-06-10 19:00 | 44722.7917 | 0 | 17.4238 | 39.95
2022-06-10 19:30 | 44722.8125 | 0 | 16.9481 | 39.95
2022-06-10 20:00 | 44722.8333 | 0 | 16.6445 | 39.95
2022-06-10 20:30 | 44722.8542 | 0 | 16.1859 | 39.95
2022-06-10 21:00 | 44722.875 | 0 | 15.6266 | 39.95
2022-06-10 21:30 | 44722.8958 | 0 | 14.7404 | 39.95
2022-06-10 22:00 | 44722.9167 | 0 | 13.9434 | 39.95
2022-06-10 22:30 | 44722.9375 | 0 | 12.7136 | 39.95
2022-06-10 23:00 | 44722.9583 | 0 | 11.8302 | 39.95
2022-06-10 23:30 | 44722.9792 | 0 | 11.2815 | 39.95
2022-06-11 | 44723 | 0 | 10.5283 | 39.95
2022-06-11 00:30 | 44723.0208 | 0 | 9.9242 | 39.95
2022-06-11 01:00 | 44723.0417 | 0 | 9.5486 | 39.95
2022-06-11 01:30 | 44723.0625 | 0 | 9.2944 | 39.95
2022-06-11 02:00 | 44723.0833 | 0 | 9.0478 | 39.95
2022-06-11 02:30 | 44723.1042 | 0 | 9.0699 | 39.95
2022-06-11 03:00 | 44723.125 | 0 | 8.9271 | 39.95
2022-06-11 03:30 | 44723.1458 | 0 | 8.9148 | 39.95
2022-06-11 04:00 | 44723.1667 | 0 | 9.1427 | 39.95
2022-06-11 04:30 | 44723.1875 | 0 | 9.1324 | 39.95
2022-06-11 05:00 | 44723.2083 | 0 | 9.4776 | 39.95
2022-06-11 05:30 | 44723.2292 | 0 | 9.9738 | 39.95
2022-06-11 06:00 | 44723.25 | 0 | 10.8953 | 39.95
2022-06-11 06:30 | 44723.2708 | 0 | 12.0994 | 39.95
2022-06-11 07:00 | 44723.2917 | 0 | 13.0271 | 39.95
2022-06-11 07:30 | 44723.3125 | 0 | 12.9099 | 39.95
2022-06-11 08:00 | 44723.3333 | 0 | 12.5867 | 39.95
2022-06-11 08:30 | 44723.3542 | 0 | 11.8079 | 39.95
2022-06-11 09:00 | 44723.375 | 0 | 10.7271 | 39.95
2022-06-11 09:30 | 44723.3958 | 0 | 9.8874 | 39.95
2022-06-11 10:00 | 44723.4167 | 0 | 9.1049 | 39.95
2022-06-11 10:30 | 44723.4375 | 0 | 8.298 | 39.95
2022-06-11 11:00 | 44723.4583 | 0 | 7.6697 | 39.95
2022-06-11 11:30 | 44723.4792 | 0 | 7.3403 | 39.95
2022-06-11 12:00 | 44723.5 | 0 | 7.0411 | 39.95
2022-06-11 12:30 | 44723.5208 | 0 | 6.9417 | 39.95
2022-06-11 13:00 | 44723.5417 | 0 | 7.107 | 39.95
2022-06-11 13:30 | 44723.5625 | 0 | 7.4273 | 39.95
2022-06-11 14:00 | 44723.5833 | 0 | 7.807 | 39.95
2022-06-11 14:30 | 44723.6042 | 0 | 8.4429 | 39.95
2022-06-11 15:00 | 44723.625 | 0 | 9.155 | 39.95
2022-06-11 15:30 | 44723.6458 | 0 | 10.2922 | 39.95
2022-06-11 16:00 | 44723.6667 | 0 | 11.275 | 39.95
2022-06-11 16:30 | 44723.6875 | 0 | 12.4656 | 39.95
2022-06-11 17:00 | 44723.7083 | 0 | 13.5713 | 39.95
2022-06-11 17:30 | 44723.7292 | 0 | 14.3704 | 39.95
2022-06-11 18:00 | 44723.75 | 0 | 14.5138 | 39.95
2022-06-11 18:30 | 44723.7708 | 0 | 14.5701 | 39.95
2022-06-11 19:00 | 44723.7917 | 0 | 14.5757 | 39.95
2022-06-11 19:30 | 44723.8125 | 0 | 14.2997 | 39.95
2022-06-11 20:00 | 44723.8333 | 0 | 13.8475 | 39.95
2022-06-11 20:30 | 44723.8542 | 0 | 13.3821 | 39.95
2022-06-11 21:00 | 44723.875 | 0 | 12.8807 | 39.95
2022-06-11 21:30 | 44723.8958 | 0 | 12.3777 | 39.95
2022-06-11 22:00 | 44723.9167 | 0 | 11.7855 | 39.95
2022-06-11 22:30 | 44723.9375 | 0 | 10.9931 | 39.95
2022-06-11 23:00 | 44723.9583 | 0 | 10.3815 | 39.95
2022-06-11 23:30 | 44723.9792 | 0 | 9.7952 | 39.95
2022-06-12 | 44724 | 0 | 9.2188 | 39.95
2022-06-12 00:30 | 44724.0208 | 0 | 8.7422 | 39.95
2022-06-12 01:00 | 44724.0417 | 0 | 8.3971 | 39.95
2022-06-12 01:30 | 44724.0625 | 0 | 8.3172 | 39.95
2022-06-12 02:00 | 44724.0833 | 0 | 8.0953 | 39.95
2022-06-12 02:30 | 44724.1042 | 0 | 8.0295 | 39.95
2022-06-12 03:00 | 44724.125 | 0 | 8.1079 | 39.95
2022-06-12 03:30 | 44724.1458 | 0 | 8.1245 | 39.95
2022-06-12 04:00 | 44724.1667 | 0 | 8.0581 | 39.95
2022-06-12 04:30 | 44724.1875 | 0 | 8.0489 | 39.95
2022-06-12 05:00 | 44724.2083 | 0 | 8.3485 | 39.95
2022-06-12 05:30 | 44724.2292 | 0 | 8.9039 | 39.95
2022-06-12 06:00 | 44724.25 | 0 | 9.4373 | 39.95
2022-06-12 06:30 | 44724.2708 | 0 | 10.177 | 39.95
2022-06-12 07:00 | 44724.2917 | 0 | 10.8586 | 39.95
2022-06-12 07:30 | 44724.3125 | 0 | 11.5185 | 39.95
2022-06-12 08:00 | 44724.3333 | 0 | 12.0377 | 39.95
2022-06-12 08:30 | 44724.3542 | 0 | 11.8946 | 39.95
2022-06-12 09:00 | 44724.375 | 0 | 11.3275 | 39.95
2022-06-12 09:30 | 44724.3958 | 0 | 11.5809 | 39.95
2022-06-12 10:00 | 44724.4167 | 0 | 11.7349 | 39.95
2022-06-12 10:30 | 44724.4375 | 0 | 11.5422 | 39.95
2022-06-12 11:00 | 44724.4583 | 0 | 9.6988 | 39.95
2022-06-12 11:30 | 44724.4792 | 0 | 8.7832 | 39.95
2022-06-12 12:00 | 44724.5 | 0 | 9.2973 | 39.95
2022-06-12 12:30 | 44724.5208 | 0 | 7.3206 | 39.95
2022-06-12 13:00 | 44724.5417 | 0 | 7.2486 | 39.95
2022-06-12 13:30 | 44724.5625 | 0 | 7.5078 | 39.95
2022-06-12 14:00 | 44724.5833 | 0 | 8.0566 | 39.95
2022-06-12 14:30 | 44724.6042 | 0 | 8.6025 | 39.95
2022-06-12 15:00 | 44724.625 | 0 | 9.2864 | 39.95
2022-06-12 15:30 | 44724.6458 | 0 | 10.5359 | 39.95
2022-06-12 16:00 | 44724.6667 | 0 | 11.7773 | 39.95
2022-06-12 16:30 | 44724.6875 | 0 | 12.8975 | 39.95
2022-06-12 17:00 | 44724.7083 | 0 | 14.2792 | 39.95
2022-06-12 17:30 | 44724.7292 | 0 | 15.0626 | 39.95
2022-06-12 18:00 | 44724.75 | 0 | 15.5086 | 39.95
2022-06-12 18:30 | 44724.7708 | 0 | 15.4689 | 39.95
2022-06-12 19:00 | 44724.7917 | 0 | 14.9664 | 39.95
2022-06-12 19:30 | 44724.8125 | 0 | 14.5288 | 39.95
2022-06-12 20:00 | 44724.8333 | 0 | 14.0918 | 39.95
2022-06-12 20:30 | 44724.8542 | 0 | 13.4875 | 39.95
2022-06-12 21:00 | 44724.875 | 0 | 12.6986 | 39.95
2022-06-12 21:30 | 44724.8958 | 0 | 12.1121 | 39.95
2022-06-12 22:00 | 44724.9167 | 0 | 11.3145 | 39.95
2022-06-12 22:30 | 44724.9375 | 0 | 10.2316 | 39.95
2022-06-12 23:00 | 44724.9583 | 0 | 9.6189 | 39.95
2022-06-12 23:30 | 44724.9792 | 0 | 9.0991 | 39.95
2022-06-13 | 44725 | 0 | 8.6558 | 39.95
2022-06-13 00:30 | 44725.0208 | 0 | 8.4414 | 39.95
2022-06-13 01:00 | 44725.0417 | 0 | 8.2906 | 39.95
2022-06-13 01:30 | 44725.0625 | 0 | 8.0317 | 39.95
2022-06-13 02:00 | 44725.0833 | 0 | 7.9802 | 39.95
2022-06-13 02:30 | 44725.1042 | 0 | 8.1193 | 39.95
2022-06-13 03:00 | 44725.125 | 0 | 8.0655 | 39.95
2022-06-13 03:30 | 44725.1458 | 0 | 8.1778 | 39.95
2022-06-13 04:00 | 44725.1667 | 0 | 8.5013 | 39.95
2022-06-13 04:30 | 44725.1875 | 0 | 9.1652 | 39.95
2022-06-13 05:00 | 44725.2083 | 0 | 10.0747 | 39.95
2022-06-13 05:30 | 44725.2292 | 0 | 11.1196 | 39.95
2022-06-13 06:00 | 44725.25 | 0 | 13.0048 | 39.95
2022-06-13 06:30 | 44725.2708 | 0 | 14.9843 | 39.95
2022-06-13 07:00 | 44725.2917 | 0 | 16.7093 | 39.95
2022-06-13 07:30 | 44725.3125 | 0 | 16.8069 | 39.95
2022-06-13 08:00 | 44725.3333 | 0 | 15.4729 | 39.95
2022-06-13 08:30 | 44725.3542 | 0 | 14.4868 | 39.95
2022-06-13 09:00 | 44725.375 | 0 | 14.2684 | 39.95
2022-06-13 09:30 | 44725.3958 | 0 | 13.4832 | 39.95
2022-06-13 10:00 | 44725.4167 | 0 | 11.4807 | 39.95
2022-06-13 10:30 | 44725.4375 | 0 | 12.1425 | 39.95
2022-06-13 11:00 | 44725.4583 | 0 | 9.9524 | 39.95
2022-06-13 11:30 | 44725.4792 | 0 | 9.4524 | 39.95
2022-06-13 12:00 | 44725.5 | 0 | 9.1288 | 39.95
2022-06-13 12:30 | 44725.5208 | 0 | 9.0329 | 39.95
2022-06-13 13:00 | 44725.5417 | 0 | 9.6174 | 39.95
2022-06-13 13:30 | 44725.5625 | 0 | 9.9556 | 39.95
2022-06-13 14:00 | 44725.5833 | 0 | 10.2118 | 39.95
2022-06-13 14:30 | 44725.6042 | 0 | 10.5108 | 39.95
2022-06-13 15:00 | 44725.625 | 0 | 11.5273 | 39.95
2022-06-13 15:30 | 44725.6458 | 0 | 12.4013 | 39.95
2022-06-13 16:00 | 44725.6667 | 0 | 12.8108 | 39.95
2022-06-13 16:30 | 44725.6875 | 0 | 13.424 | 39.95
2022-06-13 17:00 | 44725.7083 | 0 | 14.6118 | 39.95
2022-06-13 17:30 | 44725.7292 | 0 | 15.6804 | 39.95
2022-06-13 18:00 | 44725.75 | 0 | 16.0554 | 39.95
2022-06-13 18:30 | 44725.7708 | 0 | 15.9467 | 39.95
2022-06-13 19:00 | 44725.7917 | 0 | 15.5289 | 39.95
2022-06-13 19:30 | 44725.8125 | 0 | 14.9633 | 39.95
2022-06-13 20:00 | 44725.8333 | 0 | 15.0407 | 39.95
2022-06-13 20:30 | 44725.8542 | 0 | 14.7984 | 39.95
2022-06-13 21:00 | 44725.875 | 0 | 13.7703 | 39.95
2022-06-13 21:30 | 44725.8958 | 0 | 13.5594 | 39.95
2022-06-13 22:00 | 44725.9167 | 0 | 12.382 | 39.95
2022-06-13 22:30 | 44725.9375 | 0 | 11.3488 | 39.95
2022-06-13 23:00 | 44725.9583 | 0 | 10.6915 | 39.95
2022-06-13 23:30 | 44725.9792 | 0 | 10.2857 | 39.95
2022-06-14 | 44726 | 0 | 9.6783 | 39.95
2022-06-14 00:30 | 44726.0208 | 0 | 9.327 | 39.95
2022-06-14 01:00 | 44726.0417 | 0 | 9.0268 | 39.95
2022-06-14 01:30 | 44726.0625 | 0 | 8.6838 | 39.95
2022-06-14 02:00 | 44726.0833 | 0 | 8.4222 | 39.95
2022-06-14 02:30 | 44726.1042 | 0 | 8.472 | 39.95
2022-06-14 03:00 | 44726.125 | 0 | 8.3782 | 39.95
2022-06-14 03:30 | 44726.1458 | 0 | 8.3931 | 39.95
2022-06-14 04:00 | 44726.1667 | 0 | 8.8555 | 39.95
2022-06-14 04:30 | 44726.1875 | 0 | 9.359 | 39.95
2022-06-14 05:00 | 44726.2083 | 0 | 10.2184 | 39.95
2022-06-14 05:30 | 44726.2292 | 0 | 11.1094 | 39.95
2022-06-14 06:00 | 44726.25 | 0 | 12.8112 | 39.95
2022-06-14 06:30 | 44726.2708 | 0 | 14.3415 | 39.95
2022-06-14 07:00 | 44726.2917 | 0 | 15.2432 | 39.95
2022-06-14 07:30 | 44726.3125 | 0 | 14.6731 | 39.95
2022-06-14 08:00 | 44726.3333 | 0 | 13.2346 | 39.95
2022-06-14 08:30 | 44726.3542 | 0 | 12.423 | 39.95
2022-06-14 09:00 | 44726.375 | 0 | 11.7353 | 39.95
2022-06-14 09:30 | 44726.3958 | 0 | 11.4354 | 39.95
2022-06-14 10:00 | 44726.4167 | 0 | 11.9896 | 39.95
2022-06-14 10:30 | 44726.4375 | 0 | 10.659 | 39.95
2022-06-14 11:00 | 44726.4583 | 0 | 9.7924 | 39.95
2022-06-14 11:30 | 44726.4792 | 0 | 9.9393 | 39.95
2022-06-14 12:00 | 44726.5 | 0 | 10.5079 | 39.95
2022-06-14 12:30 | 44726.5208 | 0 | 12.0963 | 39.95
2022-06-14 13:00 | 44726.5417 | 0 | 10.9633 | 39.95
2022-06-14 13:30 | 44726.5625 | 0 | 10.3671 | 39.95
2022-06-14 14:00 | 44726.5833 | 0 | 11.2394 | 39.95
2022-06-14 14:30 | 44726.6042 | 0 | 11.722 | 39.95
2022-06-14 15:00 | 44726.625 | 0 | 11.5034 | 39.95
2022-06-14 15:30 | 44726.6458 | 0 | 12.0119 | 39.95
2022-06-14 16:00 | 44726.6667 | 0 | 12.4181 | 39.95
2022-06-14 16:30 | 44726.6875 | 0 | 13.0768 | 39.95
2022-06-14 17:00 | 44726.7083 | 0 | 13.9656 | 39.95
2022-06-14 17:30 | 44726.7292 | 0 | 15.148 | 39.95
2022-06-14 18:00 | 44726.75 | 0 | 15.4061 | 39.95
2022-06-14 18:30 | 44726.7708 | 0 | 15.2874 | 39.95
2022-06-14 19:00 | 44726.7917 | 0 | 14.7366 | 39.95
2022-06-14 19:30 | 44726.8125 | 0 | 14.2493 | 39.95
2022-06-14 20:00 | 44726.8333 | 0 | 14.4346 | 39.95
2022-06-14 20:30 | 44726.8542 | 0 | 13.5677 | 39.95
2022-06-14 21:00 | 44726.875 | 0 | 12.8717 | 39.95
2022-06-14 21:30 | 44726.8958 | 0 | 12.0261 | 39.95
2022-06-14 22:00 | 44726.9167 | 0 | 12.3464 | 39.95
2022-06-14 22:30 | 44726.9375 | 0 | 11.4911 | 39.95
2022-06-14 23:00 | 44726.9583 | 0 | 10.9388 | 39.95
2022-06-14 23:30 | 44726.9792 | 0 | 10.1312 | 39.95
2022-06-15 | 44727 | 0 | 9.5955 | 39.95
2022-06-15 00:30 | 44727.0208 | 0 | 9.1191 | 39.95
2022-06-15 01:00 | 44727.0417 | 0 | 8.9662 | 39.95
2022-06-15 01:30 | 44727.0625 | 0 | 8.6075 | 39.95
2022-06-15 02:00 | 44727.0833 | 0 | 8.4056 | 39.95
2022-06-15 02:30 | 44727.1042 | 0 | 8.388 | 39.95
2022-06-15 03:00 | 44727.125 | 0 | 8.3736 | 39.95
2022-06-15 03:30 | 44727.1458 | 0 | 8.321 | 39.95
2022-06-15 04:00 | 44727.1667 | 0 | 8.6847 | 39.95
2022-06-15 04:30 | 44727.1875 | 0 | 9.2619 | 39.95
2022-06-15 05:00 | 44727.2083 | 0 | 9.9287 | 39.95
2022-06-15 05:30 | 44727.2292 | 0 | 11.0026 | 39.95
2022-06-15 06:00 | 44727.25 | 0 | 12.5014 | 39.95
2022-06-15 06:30 | 44727.2708 | 0 | 13.9214 | 39.95
2022-06-15 07:00 | 44727.2917 | 0 | 14.8597 | 39.95
2022-06-15 07:30 | 44727.3125 | 0 | 14.7439 | 39.95
2022-06-15 08:00 | 44727.3333 | 0 | 14.1289 | 39.95
2022-06-15 08:30 | 44727.3542 | 0 | 12.2354 | 39.95
2022-06-15 09:00 | 44727.375 | 0 | 11.3235 | 39.95
2022-06-15 09:30 | 44727.3958 | 0 | 10.4022 | 39.95
2022-06-15 10:00 | 44727.4167 | 0 | 9.7834 | 39.95
2022-06-15 10:30 | 44727.4375 | 0 | 9.1914 | 39.95
2022-06-15 11:00 | 44727.4583 | 0 | 9.1219 | 39.95
2022-06-15 11:30 | 44727.4792 | 0 | 8.8912 | 39.95
2022-06-15 12:00 | 44727.5 | 0 | 8.6431 | 39.95
2022-06-15 12:30 | 44727.5208 | 0 | 8.9809 | 39.95
2022-06-15 13:00 | 44727.5417 | 0 | 9.0572 | 39.95
2022-06-15 13:30 | 44727.5625 | 0 | 9.9769 | 39.95
2022-06-15 14:00 | 44727.5833 | 0 | 11.4301 | 39.95
2022-06-15 14:30 | 44727.6042 | 0 | 11.5073 | 39.95
2022-06-15 15:00 | 44727.625 | 0 | 10.8248 | 39.95
2022-06-15 15:30 | 44727.6458 | 0 | 11.7601 | 39.95
2022-06-15 16:00 | 44727.6667 | 0 | 12.2144 | 39.95
2022-06-15 16:30 | 44727.6875 | 0 | 12.778 | 39.95
2022-06-15 17:00 | 44727.7083 | 0 | 13.6183 | 39.95
2022-06-15 17:30 | 44727.7292 | 0 | 14.5348 | 39.95
2022-06-15 18:00 | 44727.75 | 0 | 14.3707 | 39.95
2022-06-15 18:30 | 44727.7708 | 0 | 14.121 | 39.95
2022-06-15 19:00 | 44727.7917 | 0 | 13.8152 | 39.95
2022-06-15 19:30 | 44727.8125 | 0 | 13.4263 | 39.95
2022-06-15 20:00 | 44727.8333 | 0 | 12.8468 | 39.95
2022-06-15 20:30 | 44727.8542 | 0 | 12.2806 | 39.95
2022-06-15 21:00 | 44727.875 | 0 | 12.7795 | 39.95
2022-06-15 21:30 | 44727.8958 | 0 | 12.4976 | 39.95
2022-06-15 22:00 | 44727.9167 | 0 | 11.2042 | 39.95
2022-06-15 22:30 | 44727.9375 | 0 | 11.2768 | 39.95
2022-06-15 23:00 | 44727.9583 | 0 | 10.6056 | 39.95
2022-06-15 23:30 | 44727.9792 | 0 | 10.1641 | 39.95
2022-06-16 | 44728 | 0 | 9.5434 | 39.95
2022-06-16 00:30 | 44728.0208 | 0 | 9.1383 | 39.95
2022-06-16 01:00 | 44728.0417 | 0 | 8.8688 | 39.95
2022-06-16 01:30 | 44728.0625 | 0 | 8.4909 | 39.95
2022-06-16 02:00 | 44728.0833 | 0 | 8.3192 | 39.95
2022-06-16 02:30 | 44728.1042 | 0 | 8.2741 | 39.95
2022-06-16 03:00 | 44728.125 | 0 | 8.1709 | 39.95
2022-06-16 03:30 | 44728.1458 | 0 | 8.3233 | 39.95
2022-06-16 04:00 | 44728.1667 | 0 | 8.6546 | 39.95
2022-06-16 04:30 | 44728.1875 | 0 | 9.1026 | 39.95
2022-06-16 05:00 | 44728.2083 | 0 | 9.8314 | 39.95
2022-06-16 05:30 | 44728.2292 | 0 | 10.7049 | 39.95
2022-06-16 06:00 | 44728.25 | 0 | 11.969 | 39.95
2022-06-16 06:30 | 44728.2708 | 0 | 13.5432 | 39.95
2022-06-16 07:00 | 44728.2917 | 0 | 14.4504 | 39.95
2022-06-16 07:30 | 44728.3125 | 0 | 13.8942 | 39.95
2022-06-16 08:00 | 44728.3333 | 0 | 13.207 | 39.95
2022-06-16 08:30 | 44728.3542 | 0 | 11.7151 | 39.95
2022-06-16 09:00 | 44728.375 | 0 | 10.6734 | 39.95
2022-06-16 09:30 | 44728.3958 | 0 | 9.876 | 39.95
2022-06-16 10:00 | 44728.4167 | 0 | 9.3906 | 39.95
2022-06-16 10:30 | 44728.4375 | 0 | 8.6767 | 39.95
2022-06-16 11:00 | 44728.4583 | 0 | 8.3185 | 39.95
2022-06-16 11:30 | 44728.4792 | 0 | 8.4159 | 39.95
2022-06-16 12:00 | 44728.5 | 0 | 8.2591 | 39.95
2022-06-16 12:30 | 44728.5208 | 0 | 8.2986 | 39.95
2022-06-16 13:00 | 44728.5417 | 0 | 8.6056 | 39.95
2022-06-16 13:30 | 44728.5625 | 0 | 8.9543 | 39.95
2022-06-16 14:00 | 44728.5833 | 0 | 9.3588 | 39.95
2022-06-16 14:30 | 44728.6042 | 0 | 10.0635 | 39.95
2022-06-16 15:00 | 44728.625 | 0 | 10.6603 | 39.95
2022-06-16 15:30 | 44728.6458 | 0 | 11.6734 | 39.95
2022-06-16 16:00 | 44728.6667 | 0 | 12.3033 | 39.95
2022-06-16 16:30 | 44728.6875 | 0 | 12.8749 | 39.95
2022-06-16 17:00 | 44728.7083 | 0 | 13.6044 | 39.95
2022-06-16 17:30 | 44728.7292 | 0 | 14.1594 | 39.95
2022-06-16 18:00 | 44728.75 | 0 | 14.3025 | 39.95
2022-06-16 18:30 | 44728.7708 | 0 | 14.3456 | 39.95
2022-06-16 19:00 | 44728.7917 | 0 | 14.2395 | 39.95
2022-06-16 19:30 | 44728.8125 | 0 | 14.1388 | 39.95
2022-06-16 20:00 | 44728.8333 | 0 | 13.7785 | 39.95
2022-06-16 20:30 | 44728.8542 | 0 | 13.4218 | 39.95
2022-06-16 21:00 | 44728.875 | 0 | 12.8941 | 39.95
2022-06-16 21:30 | 44728.8958 | 0 | 12.3855 | 39.95
2022-06-16 22:00 | 44728.9167 | 0 | 11.901 | 39.95
2022-06-16 22:30 | 44728.9375 | 0 | 11.0105 | 39.95
2022-06-16 23:00 | 44728.9583 | 0 | 10.3498 | 39.95
2022-06-16 23:30 | 44728.9792 | 0 | 9.7968 | 39.95
2022-06-17 | 44729 | 0 | 9.0863 | 39.95
2022-06-17 00:30 | 44729.0208 | 0 | 8.6443 | 39.95
2022-06-17 01:00 | 44729.0417 | 0 | 8.4611 | 39.95
2022-06-17 01:30 | 44729.0625 | 0 | 8.208 | 39.95
2022-06-17 02:00 | 44729.0833 | 0 | 8.1519 | 39.95
2022-06-17 02:30 | 44729.1042 | 0 | 8.1732 | 39.95
2022-06-17 03:00 | 44729.125 | 0 | 8.1107 | 39.95
2022-06-17 03:30 | 44729.1458 | 0 | 8.147 | 39.95
2022-06-17 04:00 | 44729.1667 | 0 | 8.6445 | 39.95
2022-06-17 04:30 | 44729.1875 | 0 | 9.1183 | 39.95
2022-06-17 05:00 | 44729.2083 | 0 | 9.8209 | 39.95
2022-06-17 05:30 | 44729.2292 | 0 | 10.8767 | 39.95
2022-06-17 06:00 | 44729.25 | 0 | 12.2877 | 39.95
2022-06-17 06:30 | 44729.2708 | 0 | 13.8663 | 39.95
2022-06-17 07:00 | 44729.2917 | 0 | 15.0219 | 39.95
2022-06-17 07:30 | 44729.3125 | 0 | 14.4565 | 39.95
2022-06-17 08:00 | 44729.3333 | 0 | 13.6722 | 39.95
2022-06-17 08:30 | 44729.3542 | 0 | 12.2571 | 39.95
2022-06-17 09:00 | 44729.375 | 0 | 10.6159 | 39.95
2022-06-17 09:30 | 44729.3958 | 0 | 9.8509 | 39.95
2022-06-17 10:00 | 44729.4167 | 0 | 9.3495 | 39.95
2022-06-17 10:30 | 44729.4375 | 0 | 8.7784 | 39.95
2022-06-17 11:00 | 44729.4583 | 0 | 8.461 | 39.95
2022-06-17 11:30 | 44729.4792 | 0 | 8.1839 | 39.95
2022-06-17 12:00 | 44729.5 | 0 | 7.8062 | 39.95
2022-06-17 12:30 | 44729.5208 | 0 | 7.9985 | 39.95
2022-06-17 13:00 | 44729.5417 | 0 | 8.198 | 39.95
2022-06-17 13:30 | 44729.5625 | 0 | 8.7265 | 39.95
2022-06-17 14:00 | 44729.5833 | 0 | 9.33 | 39.95
2022-06-17 14:30 | 44729.6042 | 0 | 9.7638 | 39.95
2022-06-17 15:00 | 44729.625 | 0 | 10.3382 | 39.95
2022-06-17 15:30 | 44729.6458 | 0 | 11.3585 | 39.95
2022-06-17 16:00 | 44729.6667 | 0 | 12.064 | 39.95
2022-06-17 16:30 | 44729.6875 | 0 | 12.6441 | 39.95
2022-06-17 17:00 | 44729.7083 | 0 | 13.4714 | 39.95
2022-06-17 17:30 | 44729.7292 | 0 | 14.2263 | 39.95
2022-06-17 18:00 | 44729.75 | 0 | 14.3494 | 39.95
2022-06-17 18:30 | 44729.7708 | 0 | 14.3376 | 39.95
2022-06-17 19:00 | 44729.7917 | 0 | 14.4399 | 39.95
2022-06-17 19:30 | 44729.8125 | 0 | 14.1904 | 39.95
2022-06-17 20:00 | 44729.8333 | 0 | 14.101 | 39.95
2022-06-17 20:30 | 44729.8542 | 0 | 13.5868 | 39.95
2022-06-17 21:00 | 44729.875 | 0 | 13.0511 | 39.95
2022-06-17 21:30 | 44729.8958 | 0 | 12.6763 | 39.95
2022-06-17 22:00 | 44729.9167 | 0 | 12.2118 | 39.95
2022-06-17 22:30 | 44729.9375 | 0 | 11.3559 | 39.95
2022-06-17 23:00 | 44729.9583 | 0 | 10.7864 | 39.95
2022-06-17 23:30 | 44729.9792 | 0 | 10.1414 | 39.95
2022-06-18 | 44730 | 0 | 9.397 | 39.95
2022-06-18 00:30 | 44730.0208 | 0 | 9.0437 | 39.95
2022-06-18 01:00 | 44730.0417 | 0 | 8.6054 | 39.95
2022-06-18 01:30 | 44730.0625 | 0 | 8.3369 | 39.95
2022-06-18 02:00 | 44730.0833 | 0 | 8.3043 | 39.95
2022-06-18 02:30 | 44730.1042 | 0 | 8.1822 | 39.95
2022-06-18 03:00 | 44730.125 | 0 | 8.0976 | 39.95
2022-06-18 03:30 | 44730.1458 | 0 | 8.1858 | 39.95
2022-06-18 04:00 | 44730.1667 | 0 | 8.3375 | 39.95
2022-06-18 04:30 | 44730.1875 | 0 | 8.3393 | 39.95
2022-06-18 05:00 | 44730.2083 | 0 | 8.7778 | 39.95
2022-06-18 05:30 | 44730.2292 | 0 | 9.261 | 39.95
2022-06-18 06:00 | 44730.25 | 0 | 9.5769 | 39.95
2022-06-18 06:30 | 44730.2708 | 0 | 10.4382 | 39.95
2022-06-18 07:00 | 44730.2917 | 0 | 11.1949 | 39.95
2022-06-18 07:30 | 44730.3125 | 0 | 11.1422 | 39.95
2022-06-18 08:00 | 44730.3333 | 0 | 10.8209 | 39.95
2022-06-18 08:30 | 44730.3542 | 0 | 10.1038 | 39.95
2022-06-18 09:00 | 44730.375 | 0 | 9.2481 | 39.95
2022-06-18 09:30 | 44730.3958 | 0 | 8.4754 | 39.95
2022-06-18 10:00 | 44730.4167 | 0 | 8.0092 | 39.95
2022-06-18 10:30 | 44730.4375 | 0 | 7.2222 | 39.95
2022-06-18 11:00 | 44730.4583 | 0 | 6.7129 | 39.95
2022-06-18 11:30 | 44730.4792 | 0 | 6.6931 | 39.95
2022-06-18 12:00 | 44730.5 | 0 | 6.1168 | 39.95
2022-06-18 12:30 | 44730.5208 | 0 | 6.6085 | 39.95
2022-06-18 13:00 | 44730.5417 | 0 | 8.2733 | 39.95
2022-06-18 13:30 | 44730.5625 | 0 | 8.9883 | 39.95
2022-06-18 14:00 | 44730.5833 | 0 | 8.7262 | 39.95
2022-06-18 14:30 | 44730.6042 | 0 | 8.6406 | 39.95
2022-06-18 15:00 | 44730.625 | 0 | 9.6007 | 39.95
2022-06-18 15:30 | 44730.6458 | 0 | 9.7267 | 39.95
2022-06-18 16:00 | 44730.6667 | 0 | 10.5699 | 39.95
2022-06-18 16:30 | 44730.6875 | 0 | 11.3446 | 39.95
2022-06-18 17:00 | 44730.7083 | 0 | 12.114 | 39.95
2022-06-18 17:30 | 44730.7292 | 0 | 12.4143 | 39.95
2022-06-18 18:00 | 44730.75 | 0 | 12.6405 | 39.95
2022-06-18 18:30 | 44730.7708 | 0 | 12.6718 | 39.95
2022-06-18 19:00 | 44730.7917 | 0 | 12.4276 | 39.95
2022-06-18 19:30 | 44730.8125 | 0 | 12.3161 | 39.95
2022-06-18 20:00 | 44730.8333 | 0 | 12.0309 | 39.95
2022-06-18 20:30 | 44730.8542 | 0 | 11.67 | 39.95
2022-06-18 21:00 | 44730.875 | 0 | 11.2202 | 39.95
2022-06-18 21:30 | 44730.8958 | 0 | 10.8874 | 39.95
2022-06-18 22:00 | 44730.9167 | 0 | 10.538 | 39.95
2022-06-18 22:30 | 44730.9375 | 0 | 9.8268 | 39.95
2022-06-18 23:00 | 44730.9583 | 0 | 9.4038 | 39.95
2022-06-18 23:30 | 44730.9792 | 0 | 8.7963 | 39.95
2022-06-19 | 44731 | 0 | 8.3545 | 39.95
2022-06-19 00:30 | 44731.0208 | 0 | 7.9081 | 39.95
2022-06-19 01:00 | 44731.0417 | 0 | 7.8204 | 39.95
2022-06-19 01:30 | 44731.0625 | 0 | 7.6555 | 39.95
2022-06-19 02:00 | 44731.0833 | 0 | 7.5197 | 39.95
2022-06-19 02:30 | 44731.1042 | 0 | 7.3674 | 39.95
2022-06-19 03:00 | 44731.125 | 0 | 7.3617 | 39.95
2022-06-19 03:30 | 44731.1458 | 0 | 7.3188 | 39.95
2022-06-19 04:00 | 44731.1667 | 0 | 7.3612 | 39.95
2022-06-19 04:30 | 44731.1875 | 0 | 7.3681 | 39.95
2022-06-19 05:00 | 44731.2083 | 0 | 7.5898 | 39.95
2022-06-19 05:30 | 44731.2292 | 0 | 7.8899 | 39.95
2022-06-19 06:00 | 44731.25 | 0 | 8.2684 | 39.95
2022-06-19 06:30 | 44731.2708 | 0 | 8.9226 | 39.95
2022-06-19 07:00 | 44731.2917 | 0 | 9.5241 | 39.95
2022-06-19 07:30 | 44731.3125 | 0 | 9.4036 | 39.95
2022-06-19 08:00 | 44731.3333 | 0 | 9.296 | 39.95
2022-06-19 08:30 | 44731.3542 | 0 | 8.7884 | 39.95
2022-06-19 09:00 | 44731.375 | 0 | 8.4303 | 39.95
2022-06-19 09:30 | 44731.3958 | 0 | 8.0368 | 39.95
2022-06-19 10:00 | 44731.4167 | 0 | 7.4094 | 39.95
2022-06-19 10:30 | 44731.4375 | 0 | 6.5251 | 39.95
2022-06-19 11:00 | 44731.4583 | 0 | 7.1649 | 39.95
2022-06-19 11:30 | 44731.4792 | 0 | 7.7855 | 39.95
2022-06-19 12:00 | 44731.5 | 0 | 7.5203 | 39.95
2022-06-19 12:30 | 44731.5208 | 0 | 9.2675 | 39.95
2022-06-19 13:00 | 44731.5417 | 0 | 7.0674 | 39.95
2022-06-19 13:30 | 44731.5625 | 0 | 6.934 | 39.95
2022-06-19 14:00 | 44731.5833 | 0 | 7.8468 | 39.95
2022-06-19 14:30 | 44731.6042 | 0 | 8.1688 | 39.95
2022-06-19 15:00 | 44731.625 | 0 | 8.6818 | 39.95
2022-06-19 15:30 | 44731.6458 | 0 | 10.5666 | 39.95
2022-06-19 16:00 | 44731.6667 | 0 | 10.8651 | 39.95
2022-06-19 16:30 | 44731.6875 | 0 | 11.1909 | 39.95
2022-06-19 17:00 | 44731.7083 | 0 | 12.1129 | 39.95
2022-06-19 17:30 | 44731.7292 | 0 | 12.8089 | 39.95
2022-06-19 18:00 | 44731.75 | 0 | 12.8916 | 39.95
2022-06-19 18:30 | 44731.7708 | 0 | 12.8916 | 39.95
2022-06-19 19:00 | 44731.7917 | 0 | 12.6226 | 39.95
2022-06-19 19:30 | 44731.8125 | 0 | 12.2926 | 39.95
2022-06-19 20:00 | 44731.8333 | 0 | 11.9634 | 39.95
2022-06-19 20:30 | 44731.8542 | 0 | 11.5926 | 39.95
2022-06-19 21:00 | 44731.875 | 0 | 11.0661 | 39.95
2022-06-19 21:30 | 44731.8958 | 0 | 10.4927 | 39.95
2022-06-19 22:00 | 44731.9167 | 0 | 9.9945 | 39.95
2022-06-19 22:30 | 44731.9375 | 0 | 9.3297 | 39.95
2022-06-19 23:00 | 44731.9583 | 0 | 8.7672 | 39.95
2022-06-19 23:30 | 44731.9792 | 0 | 8.2868 | 39.95
2022-06-20 | 44732 | 0 | 7.897 | 39.95
2022-06-20 00:30 | 44732.0208 | 0 | 7.6887 | 39.95
2022-06-20 01:00 | 44732.0417 | 0 | 7.6222 | 39.95
2022-06-20 01:30 | 44732.0625 | 0 | 7.3753 | 39.95
2022-06-20 02:00 | 44732.0833 | 0 | 7.2879 | 39.95
2022-06-20 02:30 | 44732.1042 | 0 | 7.4012 | 39.95
2022-06-20 03:00 | 44732.125 | 0 | 7.2908 | 39.95
2022-06-20 03:30 | 44732.1458 | 0 | 7.4036 | 39.95
2022-06-20 04:00 | 44732.1667 | 0 | 7.8577 | 39.95
2022-06-20 04:30 | 44732.1875 | 0 | 8.3177 | 39.95
2022-06-20 05:00 | 44732.2083 | 0 | 9.3258 | 39.95
2022-06-20 05:30 | 44732.2292 | 0 | 10.0769 | 39.95
2022-06-20 06:00 | 44732.25 | 0 | 11.2728 | 39.95
2022-06-20 06:30 | 44732.2708 | 0 | 12.5528 | 39.95
2022-06-20 07:00 | 44732.2917 | 0 | 13.3649 | 39.95
2022-06-20 07:30 | 44732.3125 | 0 | 13.3034 | 39.95
2022-06-20 08:00 | 44732.3333 | 0 | 13.186 | 39.95
2022-06-20 08:30 | 44732.3542 | 0 | 12.6462 | 39.95
2022-06-20 09:00 | 44732.375 | 0 | 11.1787 | 39.95
2022-06-20 09:30 | 44732.3958 | 0 | 10.5515 | 39.95
2022-06-20 10:00 | 44732.4167 | 0 | 10.5733 | 39.95
2022-06-20 10:30 | 44732.4375 | 0 | 9.8156 | 39.95
2022-06-20 11:00 | 44732.4583 | 0 | 8.929 | 39.95
2022-06-20 11:30 | 44732.4792 | 0 | 8.471 | 39.95
2022-06-20 12:00 | 44732.5 | 0 | 9.7563 | 39.95
2022-06-20 12:30 | 44732.5208 | 0 | 9.707 | 39.95
2022-06-20 13:00 | 44732.5417 | 0 | 9.6432 | 39.95
2022-06-20 13:30 | 44732.5625 | 0 | 10.1751 | 39.95
2022-06-20 14:00 | 44732.5833 | 0 | 11.1145 | 39.95
2022-06-20 14:30 | 44732.6042 | 0 | 10.783 | 39.95
2022-06-20 15:00 | 44732.625 | 0 | 11.8329 | 39.95
2022-06-20 15:30 | 44732.6458 | 0 | 12.2284 | 39.95
2022-06-20 16:00 | 44732.6667 | 0 | 12.4864 | 39.95
2022-06-20 16:30 | 44732.6875 | 0 | 13.1264 | 39.95
2022-06-20 17:00 | 44732.7083 | 0 | 13.9505 | 39.95
2022-06-20 17:30 | 44732.7292 | 0 | 14.7963 | 39.95
2022-06-20 18:00 | 44732.75 | 0 | 14.7583 | 39.95
2022-06-20 18:30 | 44732.7708 | 0 | 14.7775 | 39.95
2022-06-20 19:00 | 44732.7917 | 0 | 14.6312 | 39.95
2022-06-20 19:30 | 44732.8125 | 0 | 14.3651 | 39.95
2022-06-20 20:00 | 44732.8333 | 0 | 14.0733 | 39.95
2022-06-20 20:30 | 44732.8542 | 0 | 13.4721 | 39.95
2022-06-20 21:00 | 44732.875 | 0 | 12.8378 | 39.95
2022-06-20 21:30 | 44732.8958 | 0 | 12.2146 | 39.95
2022-06-20 22:00 | 44732.9167 | 0 | 11.5222 | 39.95
2022-06-20 22:30 | 44732.9375 | 0 | 10.4737 | 39.95
2022-06-20 23:00 | 44732.9583 | 0 | 9.9328 | 39.95
2022-06-20 23:30 | 44732.9792 | 0 | 9.5131 | 39.95
2022-06-21 | 44733 | 0 | 8.8689 | 39.95
2022-06-21 00:30 | 44733.0208 | 0 | 8.6633 | 39.95
2022-06-21 01:00 | 44733.0417 | 0 | 8.3862 | 39.95
2022-06-21 01:30 | 44733.0625 | 0 | 8.283 | 39.95
2022-06-21 02:00 | 44733.0833 | 0 | 8.1481 | 39.95
2022-06-21 02:30 | 44733.1042 | 0 | 8.1692 | 39.95
2022-06-21 03:00 | 44733.125 | 0 | 8.0181 | 39.95
2022-06-21 03:30 | 44733.1458 | 0 | 8.1441 | 39.95
2022-06-21 04:00 | 44733.1667 | 0 | 8.4832 | 39.95
2022-06-21 04:30 | 44733.1875 | 0 | 9.0342 | 39.95
2022-06-21 05:00 | 44733.2083 | 0 | 9.7365 | 39.95
2022-06-21 05:30 | 44733.2292 | 0 | 10.7912 | 39.95
2022-06-21 06:00 | 44733.25 | 0 | 12.1498 | 39.95
2022-06-21 06:30 | 44733.2708 | 0 | 13.5668 | 39.95
2022-06-21 07:00 | 44733.2917 | 0 | 14.5409 | 39.95
2022-06-21 07:30 | 44733.3125 | 0 | 14.2273 | 39.95
2022-06-21 08:00 | 44733.3333 | 0 | 13.2928 | 39.95
2022-06-21 08:30 | 44733.3542 | 0 | 12.221 | 39.95
2022-06-21 09:00 | 44733.375 | 0 | 11.2382 | 39.95
2022-06-21 09:30 | 44733.3958 | 0 | 10.3369 | 39.95
2022-06-21 10:00 | 44733.4167 | 0 | 9.6227 | 39.95
2022-06-21 10:30 | 44733.4375 | 0 | 9.2015 | 39.95
2022-06-21 11:00 | 44733.4583 | 0 | 8.6924 | 39.95
2022-06-21 11:30 | 44733.4792 | 0 | 8.6255 | 39.95
2022-06-21 12:00 | 44733.5 | 0 | 8.3054 | 39.95
2022-06-21 12:30 | 44733.5208 | 0 | 8.5065 | 39.95
2022-06-21 13:00 | 44733.5417 | 0 | 8.8888 | 39.95
2022-06-21 13:30 | 44733.5625 | 0 | 9.2576 | 39.95
2022-06-21 14:00 | 44733.5833 | 0 | 9.7079 | 39.95
2022-06-21 14:30 | 44733.6042 | 0 | 10.7465 | 39.95
2022-06-21 15:00 | 44733.625 | 0 | 11.0593 | 39.95
2022-06-21 15:30 | 44733.6458 | 0 | 11.9229 | 39.95
2022-06-21 16:00 | 44733.6667 | 0 | 12.0996 | 39.95
2022-06-21 16:30 | 44733.6875 | 0 | 12.7899 | 39.95
2022-06-21 17:00 | 44733.7083 | 0 | 13.8119 | 39.95
2022-06-21 17:30 | 44733.7292 | 0 | 14.7224 | 39.95
2022-06-21 18:00 | 44733.75 | 0 | 14.9245 | 39.95
2022-06-21 18:30 | 44733.7708 | 0 | 15.1282 | 39.95
2022-06-21 19:00 | 44733.7917 | 0 | 14.6614 | 39.95
2022-06-21 19:30 | 44733.8125 | 0 | 14.4234 | 39.95
2022-06-21 20:00 | 44733.8333 | 0 | 14.1182 | 39.95
2022-06-21 20:30 | 44733.8542 | 0 | 13.7304 | 39.95
2022-06-21 21:00 | 44733.875 | 0 | 13.0684 | 39.95
2022-06-21 21:30 | 44733.8958 | 0 | 12.4879 | 39.95
2022-06-21 22:00 | 44733.9167 | 0 | 11.7741 | 39.95
2022-06-21 22:30 | 44733.9375 | 0 | 10.797 | 39.95
2022-06-21 23:00 | 44733.9583 | 0 | 10.2024 | 39.95
2022-06-21 23:30 | 44733.9792 | 0 | 9.6825 | 39.95
2022-06-22 | 44734 | 0 | 9.1638 | 39.95
2022-06-22 00:30 | 44734.0208 | 0 | 8.7429 | 39.95
2022-06-22 01:00 | 44734.0417 | 0 | 8.5007 | 39.95
2022-06-22 01:30 | 44734.0625 | 0 | 8.3347 | 39.95
2022-06-22 02:00 | 44734.0833 | 0 | 8.2791 | 39.95
2022-06-22 02:30 | 44734.1042 | 0 | 8.2814 | 39.95
2022-06-22 03:00 | 44734.125 | 0 | 8.3083 | 39.95
2022-06-22 03:30 | 44734.1458 | 0 | 8.4442 | 39.95
2022-06-22 04:00 | 44734.1667 | 0 | 8.7398 | 39.95
2022-06-22 04:30 | 44734.1875 | 0 | 9.0392 | 39.95
2022-06-22 05:00 | 44734.2083 | 0 | 9.9416 | 39.95
2022-06-22 05:30 | 44734.2292 | 0 | 11.068 | 39.95
2022-06-22 06:00 | 44734.25 | 0 | 12.3665 | 39.95
2022-06-22 06:30 | 44734.2708 | 0 | 13.6615 | 39.95
2022-06-22 07:00 | 44734.2917 | 0 | 14.7147 | 39.95
2022-06-22 07:30 | 44734.3125 | 0 | 14.6168 | 39.95
2022-06-22 08:00 | 44734.3333 | 0 | 13.7513 | 39.95
2022-06-22 08:30 | 44734.3542 | 0 | 12.5803 | 39.95
2022-06-22 09:00 | 44734.375 | 0 | 11.6636 | 39.95
2022-06-22 09:30 | 44734.3958 | 0 | 10.7312 | 39.95
2022-06-22 10:00 | 44734.4167 | 0 | 9.7881 | 39.95
2022-06-22 10:30 | 44734.4375 | 0 | 9.1419 | 39.95
2022-06-22 11:00 | 44734.4583 | 0 | 8.5125 | 39.95
2022-06-22 11:30 | 44734.4792 | 0 | 8.3196 | 39.95
2022-06-22 12:00 | 44734.5 | 0 | 7.9928 | 39.95
2022-06-22 12:30 | 44734.5208 | 0 | 8.0817 | 39.95
2022-06-22 13:00 | 44734.5417 | 0 | 8.4539 | 39.95
2022-06-22 13:30 | 44734.5625 | 0 | 8.8518 | 39.95
2022-06-22 14:00 | 44734.5833 | 0 | 9.6702 | 39.95
2022-06-22 14:30 | 44734.6042 | 0 | 10.1046 | 39.95
2022-06-22 15:00 | 44734.625 | 0 | 10.8162 | 39.95
2022-06-22 15:30 | 44734.6458 | 0 | 11.5593 | 39.95
2022-06-22 16:00 | 44734.6667 | 0 | 12.2614 | 39.95
2022-06-22 16:30 | 44734.6875 | 0 | 12.9585 | 39.95
2022-06-22 17:00 | 44734.7083 | 0 | 13.7307 | 39.95
2022-06-22 17:30 | 44734.7292 | 0 | 14.732 | 39.95
2022-06-22 18:00 | 44734.75 | 0 | 14.7762 | 39.95
2022-06-22 18:30 | 44734.7708 | 0 | 14.9221 | 39.95
2022-06-22 19:00 | 44734.7917 | 0 | 14.623 | 39.95
2022-06-22 19:30 | 44734.8125 | 0 | 14.2413 | 39.95
2022-06-22 20:00 | 44734.8333 | 0 | 13.8522 | 39.95
2022-06-22 20:30 | 44734.8542 | 0 | 13.3803 | 39.95
2022-06-22 21:00 | 44734.875 | 0 | 13.0477 | 39.95
2022-06-22 21:30 | 44734.8958 | 0 | 12.4257 | 39.95
2022-06-22 22:00 | 44734.9167 | 0 | 11.5962 | 39.95
2022-06-22 22:30 | 44734.9375 | 0 | 10.7319 | 39.95
2022-06-22 23:00 | 44734.9583 | 0 | 10.1139 | 39.95
2022-06-22 23:30 | 44734.9792 | 0 | 9.6451 | 39.95
2022-06-23 | 44735 | 0 | 8.9857 | 39.95
2022-06-23 00:30 | 44735.0208 | 0 | 8.6707 | 39.95
2022-06-23 01:00 | 44735.0417 | 0 | 8.4972 | 39.95
2022-06-23 01:30 | 44735.0625 | 0 | 8.2247 | 39.95
2022-06-23 02:00 | 44735.0833 | 0 | 8.2527 | 39.95
2022-06-23 02:30 | 44735.1042 | 0 | 8.1778 | 39.95
2022-06-23 03:00 | 44735.125 | 0 | 8.2391 | 39.95
2022-06-23 03:30 | 44735.1458 | 0 | 8.297 | 39.95
2022-06-23 04:00 | 44735.1667 | 0 | 8.6153 | 39.95
2022-06-23 04:30 | 44735.1875 | 0 | 9.105 | 39.95
2022-06-23 05:00 | 44735.2083 | 0 | 9.9467 | 39.95
2022-06-23 05:30 | 44735.2292 | 0 | 10.7403 | 39.95
2022-06-23 06:00 | 44735.25 | 0 | 12.2484 | 39.95
2022-06-23 06:30 | 44735.2708 | 0 | 13.456 | 39.95
2022-06-23 07:00 | 44735.2917 | 0 | 14.4754 | 39.95
2022-06-23 07:30 | 44735.3125 | 0 | 14.1474 | 39.95
2022-06-23 08:00 | 44735.3333 | 0 | 13.3892 | 39.95
2022-06-23 08:30 | 44735.3542 | 0 | 12.0151 | 39.95
2022-06-23 09:00 | 44735.375 | 0 | 11.1797 | 39.95
2022-06-23 09:30 | 44735.3958 | 0 | 10.6387 | 39.95
2022-06-23 10:00 | 44735.4167 | 0 | 9.7884 | 39.95
2022-06-23 10:30 | 44735.4375 | 0 | 9.2467 | 39.95
2022-06-23 11:00 | 44735.4583 | 0 | 8.8745 | 39.95
2022-06-23 11:30 | 44735.4792 | 0 | 8.6083 | 39.95
2022-06-23 12:00 | 44735.5 | 0 | 8.4972 | 39.95
2022-06-23 12:30 | 44735.5208 | 0 | 8.5472 | 39.95
2022-06-23 13:00 | 44735.5417 | 0 | 8.9224 | 39.95
2022-06-23 13:30 | 44735.5625 | 0 | 9.8035 | 39.95
2022-06-23 14:00 | 44735.5833 | 0 | 10.1941 | 39.95
2022-06-23 14:30 | 44735.6042 | 0 | 11.06 | 39.95
2022-06-23 15:00 | 44735.625 | 0 | 10.7422 | 39.95
2022-06-23 15:30 | 44735.6458 | 0 | 11.5056 | 39.95
2022-06-23 16:00 | 44735.6667 | 0 | 12.0738 | 39.95
2022-06-23 16:30 | 44735.6875 | 0 | 12.7615 | 39.95
2022-06-23 17:00 | 44735.7083 | 0 | 13.5455 | 39.95
2022-06-23 17:30 | 44735.7292 | 0 | 14.3341 | 39.95
2022-06-23 18:00 | 44735.75 | 0 | 14.635 | 39.95
2022-06-23 18:30 | 44735.7708 | 0 | 14.5053 | 39.95
2022-06-23 19:00 | 44735.7917 | 0 | 14.3872 | 39.95
2022-06-23 19:30 | 44735.8125 | 0 | 14.0203 | 39.95
2022-06-23 20:00 | 44735.8333 | 0 | 13.9493 | 39.95
2022-06-23 20:30 | 44735.8542 | 0 | 13.5667 | 39.95
2022-06-23 21:00 | 44735.875 | 0 | 12.9687 | 39.95
2022-06-23 21:30 | 44735.8958 | 0 | 12.3445 | 39.95
2022-06-23 22:00 | 44735.9167 | 0 | 11.764 | 39.95
2022-06-23 22:30 | 44735.9375 | 0 | 10.9099 | 39.95
2022-06-23 23:00 | 44735.9583 | 0 | 10.2598 | 39.95
2022-06-23 23:30 | 44735.9792 | 0 | 10.0203 | 39.95
2022-06-24 | 44736 | 0 | 9.2941 | 39.95
2022-06-24 00:30 | 44736.0208 | 0 | 8.8265 | 39.95
2022-06-24 01:00 | 44736.0417 | 0 | 8.7617 | 39.95
2022-06-24 01:30 | 44736.0625 | 0 | 8.5442 | 39.95
2022-06-24 02:00 | 44736.0833 | 0 | 8.4154 | 39.95
2022-06-24 02:30 | 44736.1042 | 0 | 8.4337 | 39.95
2022-06-24 03:00 | 44736.125 | 0 | 8.245 | 39.95
2022-06-24 03:30 | 44736.1458 | 0 | 8.4636 | 39.95
2022-06-24 04:00 | 44736.1667 | 0 | 8.6589 | 39.95
2022-06-24 04:30 | 44736.1875 | 0 | 9.0796 | 39.95
2022-06-24 05:00 | 44736.2083 | 0 | 10.0152 | 39.95
2022-06-24 05:30 | 44736.2292 | 0 | 10.7813 | 39.95
2022-06-24 06:00 | 44736.25 | 0 | 11.9691 | 39.95
2022-06-24 06:30 | 44736.2708 | 0 | 13.4405 | 39.95
2022-06-24 07:00 | 44736.2917 | 0 | 14.4176 | 39.95
2022-06-24 07:30 | 44736.3125 | 0 | 14.188 | 39.95
2022-06-24 08:00 | 44736.3333 | 0 | 13.5862 | 39.95
2022-06-24 08:30 | 44736.3542 | 0 | 12.3415 | 39.95
2022-06-24 09:00 | 44736.375 | 0 | 11.3179 | 39.95
2022-06-24 09:30 | 44736.3958 | 0 | 10.4919 | 39.95
2022-06-24 10:00 | 44736.4167 | 0 | 10.0701 | 39.95
2022-06-24 10:30 | 44736.4375 | 0 | 9.2515 | 39.95
2022-06-24 11:00 | 44736.4583 | 0 | 8.8523 | 39.95
2022-06-24 11:30 | 44736.4792 | 0 | 8.6041 | 39.95
2022-06-24 12:00 | 44736.5 | 0 | 8.1795 | 39.95
2022-06-24 12:30 | 44736.5208 | 0 | 8.1914 | 39.95
2022-06-24 13:00 | 44736.5417 | 0 | 8.2146 | 39.95
2022-06-24 13:30 | 44736.5625 | 0 | 8.5193 | 39.95
2022-06-24 14:00 | 44736.5833 | 0 | 9.0351 | 39.95
2022-06-24 14:30 | 44736.6042 | 0 | 9.5474 | 39.95
2022-06-24 15:00 | 44736.625 | 0 | 10.3505 | 39.95
2022-06-24 15:30 | 44736.6458 | 0 | 11.2195 | 39.95
2022-06-24 16:00 | 44736.6667 | 0 | 11.9403 | 39.95
2022-06-24 16:30 | 44736.6875 | 0 | 12.7598 | 39.95
2022-06-24 17:00 | 44736.7083 | 0 | 13.5096 | 39.95
2022-06-24 17:30 | 44736.7292 | 0 | 14.0773 | 39.95
2022-06-24 18:00 | 44736.75 | 0 | 14.1348 | 39.95
2022-06-24 18:30 | 44736.7708 | 0 | 14.0472 | 39.95
2022-06-24 19:00 | 44736.7917 | 0 | 13.8288 | 39.95
2022-06-24 19:30 | 44736.8125 | 0 | 13.6201 | 39.95
2022-06-24 20:00 | 44736.8333 | 0 | 13.6062 | 39.95
2022-06-24 20:30 | 44736.8542 | 0 | 13.1769 | 39.95
2022-06-24 21:00 | 44736.875 | 0 | 12.7455 | 39.95
2022-06-24 21:30 | 44736.8958 | 0 | 12.1695 | 39.95
2022-06-24 22:00 | 44736.9167 | 0 | 11.6959 | 39.95
2022-06-24 22:30 | 44736.9375 | 0 | 10.938 | 39.95
2022-06-24 23:00 | 44736.9583 | 0 | 10.5095 | 39.95
2022-06-24 23:30 | 44736.9792 | 0 | 9.9175 | 39.95
2022-06-25 | 44737 | 0 | 9.2662 | 39.95
2022-06-25 00:30 | 44737.0208 | 0 | 8.9116 | 39.95
2022-06-25 01:00 | 44737.0417 | 0 | 8.7034 | 39.95
2022-06-25 01:30 | 44737.0625 | 0 | 8.5573 | 39.95
2022-06-25 02:00 | 44737.0833 | 0 | 8.4383 | 39.95
2022-06-25 02:30 | 44737.1042 | 0 | 8.4435 | 39.95
2022-06-25 03:00 | 44737.125 | 0 | 8.2917 | 39.95
2022-06-25 03:30 | 44737.1458 | 0 | 8.2974 | 39.95
2022-06-25 04:00 | 44737.1667 | 0 | 8.2328 | 39.95
2022-06-25 04:30 | 44737.1875 | 0 | 8.3898 | 39.95
2022-06-25 05:00 | 44737.2083 | 0 | 8.9171 | 39.95
2022-06-25 05:30 | 44737.2292 | 0 | 9.4382 | 39.95
2022-06-25 06:00 | 44737.25 | 0 | 10.0585 | 39.95
2022-06-25 06:30 | 44737.2708 | 0 | 10.9537 | 39.95
2022-06-25 07:00 | 44737.2917 | 0 | 11.6361 | 39.95
2022-06-25 07:30 | 44737.3125 | 0 | 11.4373 | 39.95
2022-06-25 08:00 | 44737.3333 | 0 | 11.102 | 39.95
2022-06-25 08:30 | 44737.3542 | 0 | 10.2665 | 39.95
2022-06-25 09:00 | 44737.375 | 0 | 9.5708 | 39.95
2022-06-25 09:30 | 44737.3958 | 0 | 8.7961 | 39.95
2022-06-25 10:00 | 44737.4167 | 0 | 8.0405 | 39.95
2022-06-25 10:30 | 44737.4375 | 0 | 7.3037 | 39.95
2022-06-25 11:00 | 44737.4583 | 0 | 6.7587 | 39.95
2022-06-25 11:30 | 44737.4792 | 0 | 6.5822 | 39.95
2022-06-25 12:00 | 44737.5 | 0 | 6.2152 | 39.95
2022-06-25 12:30 | 44737.5208 | 0 | 6.0946 | 39.95
2022-06-25 13:00 | 44737.5417 | 0 | 6.268 | 39.95
2022-06-25 13:30 | 44737.5625 | 0 | 6.5812 | 39.95
2022-06-25 14:00 | 44737.5833 | 0 | 6.9605 | 39.95
2022-06-25 14:30 | 44737.6042 | 0 | 7.5046 | 39.95
2022-06-25 15:00 | 44737.625 | 0 | 8.1309 | 39.95
2022-06-25 15:30 | 44737.6458 | 0 | 9.1122 | 39.95
2022-06-25 16:00 | 44737.6667 | 0 | 10.062 | 39.95
2022-06-25 16:30 | 44737.6875 | 0 | 10.8264 | 39.95
2022-06-25 17:00 | 44737.7083 | 0 | 11.7854 | 39.95
2022-06-25 17:30 | 44737.7292 | 0 | 12.2109 | 39.95
2022-06-25 18:00 | 44737.75 | 0 | 12.441 | 39.95
2022-06-25 18:30 | 44737.7708 | 0 | 12.65 | 39.95
2022-06-25 19:00 | 44737.7917 | 0 | 12.6562 | 39.95
2022-06-25 19:30 | 44737.8125 | 0 | 12.3453 | 39.95
2022-06-25 20:00 | 44737.8333 | 0 | 12.3723 | 39.95
2022-06-25 20:30 | 44737.8542 | 0 | 12.0275 | 39.95
2022-06-25 21:00 | 44737.875 | 0 | 11.4651 | 39.95
2022-06-25 21:30 | 44737.8958 | 0 | 11.1364 | 39.95
2022-06-25 22:00 | 44737.9167 | 0 | 10.746 | 39.95
2022-06-25 22:30 | 44737.9375 | 0 | 10.0502 | 39.95
2022-06-25 23:00 | 44737.9583 | 0 | 9.5782 | 39.95
2022-06-25 23:30 | 44737.9792 | 0 | 9.0888 | 39.95
2022-06-26 | 44738 | 0 | 8.636 | 39.95
2022-06-26 00:30 | 44738.0208 | 0 | 8.2315 | 39.95
2022-06-26 01:00 | 44738.0417 | 0 | 8.1141 | 39.95
2022-06-26 01:30 | 44738.0625 | 0 | 7.8553 | 39.95
2022-06-26 02:00 | 44738.0833 | 0 | 7.8078 | 39.95
2022-06-26 02:30 | 44738.1042 | 0 | 7.8181 | 39.95
2022-06-26 03:00 | 44738.125 | 0 | 7.7729 | 39.95
2022-06-26 03:30 | 44738.1458 | 0 | 7.7225 | 39.95
2022-06-26 04:00 | 44738.1667 | 0 | 7.7003 | 39.95
2022-06-26 04:30 | 44738.1875 | 0 | 7.7288 | 39.95
2022-06-26 05:00 | 44738.2083 | 0 | 7.7884 | 39.95
2022-06-26 05:30 | 44738.2292 | 0 | 8.0124 | 39.95
2022-06-26 06:00 | 44738.25 | 0 | 8.5466 | 39.95
2022-06-26 06:30 | 44738.2708 | 0 | 9.1721 | 39.95
2022-06-26 07:00 | 44738.2917 | 0 | 9.8196 | 39.95
2022-06-26 07:30 | 44738.3125 | 0 | 9.717 | 39.95
2022-06-26 08:00 | 44738.3333 | 0 | 9.8447 | 39.95
2022-06-26 08:30 | 44738.3542 | 0 | 9.6277 | 39.95
2022-06-26 09:00 | 44738.375 | 0 | 9.1987 | 39.95
2022-06-26 09:30 | 44738.3958 | 0 | 8.1854 | 39.95
2022-06-26 10:00 | 44738.4167 | 0 | 7.9309 | 39.95
2022-06-26 10:30 | 44738.4375 | 0 | 7.3696 | 39.95
2022-06-26 11:00 | 44738.4583 | 0 | 6.3422 | 39.95
2022-06-26 11:30 | 44738.4792 | 0 | 6.4235 | 39.95
2022-06-26 12:00 | 44738.5 | 0 | 5.9619 | 39.95
2022-06-26 12:30 | 44738.5208 | 0 | 6.3823 | 39.95
2022-06-26 13:00 | 44738.5417 | 0 | 6.0293 | 39.95
2022-06-26 13:30 | 44738.5625 | 0 | 6.3386 | 39.95
2022-06-26 14:00 | 44738.5833 | 0 | 6.8778 | 39.95
2022-06-26 14:30 | 44738.6042 | 0 | 7.4872 | 39.95
2022-06-26 15:00 | 44738.625 | 0 | 8.0501 | 39.95
2022-06-26 15:30 | 44738.6458 | 0 | 9.1328 | 39.95
2022-06-26 16:00 | 44738.6667 | 0 | 10.1116 | 39.95
2022-06-26 16:30 | 44738.6875 | 0 | 11.0165 | 39.95
2022-06-26 17:00 | 44738.7083 | 0 | 12.0463 | 39.95
2022-06-26 17:30 | 44738.7292 | 0 | 12.8152 | 39.95
2022-06-26 18:00 | 44738.75 | 0 | 12.9677 | 39.95
2022-06-26 18:30 | 44738.7708 | 0 | 12.9839 | 39.95
2022-06-26 19:00 | 44738.7917 | 0 | 12.9817 | 39.95
2022-06-26 19:30 | 44738.8125 | 0 | 12.5848 | 39.95
2022-06-26 20:00 | 44738.8333 | 0 | 12.5205 | 39.95
2022-06-26 20:30 | 44738.8542 | 0 | 11.9107 | 39.95
2022-06-26 21:00 | 44738.875 | 0 | 11.5613 | 39.95
2022-06-26 21:30 | 44738.8958 | 0 | 11.0061 | 39.95
2022-06-26 22:00 | 44738.9167 | 0 | 10.4381 | 39.95
2022-06-26 22:30 | 44738.9375 | 0 | 9.8173 | 39.95
2022-06-26 23:00 | 44738.9583 | 0 | 9.0939 | 39.95
2022-06-26 23:30 | 44738.9792 | 0 | 8.5996 | 39.95
2022-06-27 | 44739 | 0 | 8.3211 | 39.95
2022-06-27 00:30 | 44739.0208 | 0 | 7.9205 | 39.95
2022-06-27 01:00 | 44739.0417 | 0 | 7.8354 | 39.95
2022-06-27 01:30 | 44739.0625 | 0 | 7.6755 | 39.95
2022-06-27 02:00 | 44739.0833 | 0 | 7.6133 | 39.95
2022-06-27 02:30 | 44739.1042 | 0 | 7.6343 | 39.95
2022-06-27 03:00 | 44739.125 | 0 | 7.6951 | 39.95
2022-06-27 03:30 | 44739.1458 | 0 | 7.8405 | 39.95
2022-06-27 04:00 | 44739.1667 | 0 | 8.1802 | 39.95
2022-06-27 04:30 | 44739.1875 | 0 | 8.5954 | 39.95
2022-06-27 05:00 | 44739.2083 | 0 | 9.3531 | 39.95
2022-06-27 05:30 | 44739.2292 | 0 | 10.2382 | 39.95
2022-06-27 06:00 | 44739.25 | 0 | 11.3847 | 39.95
2022-06-27 06:30 | 44739.2708 | 0 | 12.9725 | 39.95
2022-06-27 07:00 | 44739.2917 | 0 | 21.8247 | 39.95
2022-06-27 07:30 | 44739.3125 | 0 | 26.8357 | 39.95
2022-06-27 08:00 | 44739.3333 | 0 | 25.483 | 39.95
2022-06-27 08:30 | 44739.3542 | 0 | 23.2086 | 39.95
2022-06-27 09:00 | 44739.375 | 0 | 22.1112 | 39.95
2022-06-27 09:30 | 44739.3958 | 0 | 22.4006 | 39.95
2022-06-27 10:00 | 44739.4167 | 0 | 19.2742 | 39.95
2022-06-27 10:30 | 44739.4375 | 0 | 19.079 | 39.95
2022-06-27 11:00 | 44739.4583 | 0 | 18.562 | 39.95
2022-06-27 11:30 | 44739.4792 | 0 | 17.1787 | 39.95
2022-06-27 12:00 | 44739.5 | 0 | 15.9419 | 39.95
2022-06-27 12:30 | 44739.5208 | 0 | 15.9938 | 39.95
2022-06-27 13:00 | 44739.5417 | 0 | 16.3349 | 39.95
2022-06-27 13:30 | 44739.5625 | 0 | 17.2679 | 39.95
2022-06-27 14:00 | 44739.5833 | 0 | 17.8219 | 39.95
2022-06-27 14:30 | 44739.6042 | 0 | 18.963 | 39.95
2022-06-27 15:00 | 44739.625 | 0 | 20.1277 | 39.95
2022-06-27 15:30 | 44739.6458 | 0 | 21.5892 | 39.95
2022-06-27 16:00 | 44739.6667 | 0 | 22.9604 | 39.95
2022-06-27 16:30 | 44739.6875 | 0 | 24.5692 | 39.95
2022-06-27 17:00 | 44739.7083 | 0 | 26.5932 | 39.95
2022-06-27 17:30 | 44739.7292 | 0 | 28.2226 | 39.95
2022-06-27 18:00 | 44739.75 | 0 | 28.6412 | 39.95
2022-06-27 18:30 | 44739.7708 | 0 | 29.1598 | 39.95
2022-06-27 19:00 | 44739.7917 | 0 | 29.0242 | 39.95
2022-06-27 19:30 | 44739.8125 | 0 | 28.2638 | 39.95
2022-06-27 20:00 | 44739.8333 | 0 | 27.5633 | 39.95
2022-06-27 20:30 | 44739.8542 | 0 | 26.62 | 39.95
2022-06-27 21:00 | 44739.875 | 0 | 24.9582 | 39.95
2022-06-27 21:30 | 44739.8958 | 0 | 23.9178 | 39.95
2022-06-27 22:00 | 44739.9167 | 0 | 22.6154 | 39.95
2022-06-27 22:30 | 44739.9375 | 0 | 20.9951 | 39.95
2022-06-27 23:00 | 44739.9583 | 0 | 19.7647 | 39.95
2022-06-27 23:30 | 44739.9792 | 0 | 18.5137 | 39.95
2022-06-28 | 44740 | 0 | 17.2894 | 39.95
2022-06-28 00:30 | 44740.0208 | 0 | 16.7559 | 39.95
2022-06-28 01:00 | 44740.0417 | 0 | 16.2201 | 39.95
2022-06-28 01:30 | 44740.0625 | 0 | 15.8436 | 39.95
2022-06-28 02:00 | 44740.0833 | 0 | 15.6821 | 39.95
2022-06-28 02:30 | 44740.1042 | 0 | 15.6421 | 39.95
2022-06-28 03:00 | 44740.125 | 0 | 15.4805 | 39.95
2022-06-28 03:30 | 44740.1458 | 0 | 15.6543 | 39.95
2022-06-28 04:00 | 44740.1667 | 0 | 16.4668 | 39.95
2022-06-28 04:30 | 44740.1875 | 0 | 17.4565 | 39.95
2022-06-28 05:00 | 44740.2083 | 0 | 19.3829 | 39.95
2022-06-28 05:30 | 44740.2292 | 0 | 20.6926 | 39.95
2022-06-28 06:00 | 44740.25 | 0 | 23.221 | 39.95
2022-06-28 06:30 | 44740.2708 | 0 | 25.6209 | 39.95
2022-06-28 07:00 | 44740.2917 | 0 | 27.5517 | 39.95
2022-06-28 07:30 | 44740.3125 | 0 | 27.0772 | 39.95
2022-06-28 08:00 | 44740.3333 | 0 | 25.8161 | 39.95
2022-06-28 08:30 | 44740.3542 | 0 | 23.4379 | 39.95
2022-06-28 09:00 | 44740.375 | 0 | 21.3795 | 39.95
2022-06-28 09:30 | 44740.3958 | 0 | 19.9151 | 39.95
2022-06-28 10:00 | 44740.4167 | 0 | 18.7298 | 39.95
2022-06-28 10:30 | 44740.4375 | 0 | 19.0669 | 39.95
2022-06-28 11:00 | 44740.4583 | 0 | 17.2678 | 39.95
2022-06-28 11:30 | 44740.4792 | 0 | 19.133 | 39.95
2022-06-28 12:00 | 44740.5 | 0 | 18.6698 | 39.95
2022-06-28 12:30 | 44740.5208 | 0 | 20.6182 | 39.95
2022-06-28 13:00 | 44740.5417 | 0 | 20.2723 | 39.95
2022-06-28 13:30 | 44740.5625 | 0 | 20.2326 | 39.95
2022-06-28 14:00 | 44740.5833 | 0 | 19.218 | 39.95
2022-06-28 14:30 | 44740.6042 | 0 | 21.3947 | 39.95
2022-06-28 15:00 | 44740.625 | 0 | 21.8432 | 39.95
2022-06-28 15:30 | 44740.6458 | 0 | 21.9904 | 39.95
2022-06-28 16:00 | 44740.6667 | 0 | 23.6554 | 39.95
2022-06-28 16:30 | 44740.6875 | 0 | 25.3935 | 39.95
2022-06-28 17:00 | 44740.7083 | 0 | 27.6772 | 39.95
2022-06-28 17:30 | 44740.7292 | 0 | 29.4883 | 39.95
2022-06-28 18:00 | 44740.75 | 0 | 30.0587 | 39.95
2022-06-28 18:30 | 44740.7708 | 0 | 29.9667 | 39.95
2022-06-28 19:00 | 44740.7917 | 0 | 29.4949 | 39.95
2022-06-28 19:30 | 44740.8125 | 0 | 28.973 | 39.95
2022-06-28 20:00 | 44740.8333 | 0 | 28.322 | 39.95
2022-06-28 20:30 | 44740.8542 | 0 | 26.8735 | 39.95
2022-06-28 21:00 | 44740.875 | 0 | 25.4822 | 39.95
2022-06-28 21:30 | 44740.8958 | 0 | 24.446 | 39.95
2022-06-28 22:00 | 44740.9167 | 0 | 22.941 | 39.95
2022-06-28 22:30 | 44740.9375 | 0 | 21.1262 | 39.95
2022-06-28 23:00 | 44740.9583 | 0 | 19.7274 | 39.95
2022-06-28 23:30 | 44740.9792 | 0 | 18.7874 | 39.95
2022-06-29 | 44741 | 0 | 17.6036 | 39.95
2022-06-29 00:30 | 44741.0208 | 0 | 17.0002 | 39.95
2022-06-29 01:00 | 44741.0417 | 0 | 16.5405 | 39.95
2022-06-29 01:30 | 44741.0625 | 0 | 16.1 | 39.95
2022-06-29 02:00 | 44741.0833 | 0 | 16.1242 | 39.95
2022-06-29 02:30 | 44741.1042 | 0 | 16.0411 | 39.95
2022-06-29 03:00 | 44741.125 | 0 | 15.9047 | 39.95
2022-06-29 03:30 | 44741.1458 | 0 | 15.8506 | 39.95
2022-06-29 04:00 | 44741.1667 | 0 | 16.7013 | 39.95
2022-06-29 04:30 | 44741.1875 | 0 | 17.1475 | 39.95
2022-06-29 05:00 | 44741.2083 | 0 | 18.5882 | 39.95
2022-06-29 05:30 | 44741.2292 | 0 | 20.0846 | 39.95
2022-06-29 06:00 | 44741.25 | 0 | 22.6441 | 39.95
2022-06-29 06:30 | 44741.2708 | 0 | 24.9654 | 39.95
2022-06-29 07:00 | 44741.2917 | 0 | 26.8807 | 39.95
2022-06-29 07:30 | 44741.3125 | 0 | 27.1112 | 39.95
2022-06-29 08:00 | 44741.3333 | 0 | 27.2385 | 39.95
2022-06-29 08:30 | 44741.3542 | 0 | 27.3393 | 39.95
2022-06-29 09:00 | 44741.375 | 0 | 25.8974 | 39.95
2022-06-29 09:30 | 44741.3958 | 0 | 24.7954 | 39.95
2022-06-29 10:00 | 44741.4167 | 0 | 24.4783 | 39.95
2022-06-29 10:30 | 44741.4375 | 0 | 18.9642 | 39.95
2022-06-29 11:00 | 44741.4583 | 0 | 19.8175 | 39.95
2022-06-29 11:30 | 44741.4792 | 0 | 21.929 | 39.95
2022-06-29 12:00 | 44741.5 | 0 | 22.6911 | 39.95
2022-06-29 12:30 | 44741.5208 | 0 | 19.288 | 39.95
2022-06-29 13:00 | 44741.5417 | 0 | 21.8403 | 39.95
2022-06-29 13:30 | 44741.5625 | 0 | 23.8525 | 39.95
2022-06-29 14:00 | 44741.5833 | 0 | 24.2446 | 39.95
2022-06-29 14:30 | 44741.6042 | 0 | 22.9682 | 39.95
2022-06-29 15:00 | 44741.625 | 0 | 23.23 | 39.95
2022-06-29 15:30 | 44741.6458 | 0 | 24.5024 | 39.95
2022-06-29 16:00 | 44741.6667 | 0 | 24.6127 | 39.95
2022-06-29 16:30 | 44741.6875 | 0 | 27.0653 | 39.95
2022-06-29 17:00 | 44741.7083 | 0 | 28.8315 | 39.95
2022-06-29 17:30 | 44741.7292 | 0 | 30.1963 | 39.95
2022-06-29 18:00 | 44741.75 | 0 | 30.5915 | 39.95
2022-06-29 18:30 | 44741.7708 | 0 | 30.5631 | 39.95
2022-06-29 19:00 | 44741.7917 | 0 | 30.3506 | 39.95
2022-06-29 19:30 | 44741.8125 | 0 | 29.5764 | 39.95
2022-06-29 20:00 | 44741.8333 | 0 | 28.8602 | 39.95
2022-06-29 20:30 | 44741.8542 | 0 | 27.5249 | 39.95
2022-06-29 21:00 | 44741.875 | 0 | 26.0738 | 39.95
2022-06-29 21:30 | 44741.8958 | 0 | 24.6825 | 39.95
2022-06-29 22:00 | 44741.9167 | 0 | 23.0662 | 39.95
2022-06-29 22:30 | 44741.9375 | 0 | 21.3275 | 39.95
2022-06-29 23:00 | 44741.9583 | 0 | 20.0802 | 39.95
2022-06-29 23:30 | 44741.9792 | 0 | 18.8499 | 39.95
2022-06-30 | 44742 | 0 | 17.7138 | 39.95
2022-06-30 00:30 | 44742.0208 | 0 | 17.0672 | 39.95
2022-06-30 01:00 | 44742.0417 | 0 | 16.7073 | 39.95
2022-06-30 01:30 | 44742.0625 | 0 | 16.0919 | 39.95
2022-06-30 02:00 | 44742.0833 | 0 | 15.8873 | 39.95
2022-06-30 02:30 | 44742.1042 | 0 | 15.9599 | 39.95
2022-06-30 03:00 | 44742.125 | 0 | 15.8962 | 39.95
2022-06-30 03:30 | 44742.1458 | 0 | 15.7475 | 39.95
2022-06-30 04:00 | 44742.1667 | 0 | 16.5107 | 39.95
2022-06-30 04:30 | 44742.1875 | 0 | 17.6818 | 39.95
2022-06-30 05:00 | 44742.2083 | 0 | 18.6983 | 39.95
2022-06-30 05:30 | 44742.2292 | 0 | 20.2013 | 39.95
2022-06-30 06:00 | 44742.25 | 0 | 22.5605 | 39.95
2022-06-30 06:30 | 44742.2708 | 0 | 25.0029 | 39.95
2022-06-30 07:00 | 44742.2917 | 0 | 26.6084 | 39.95
2022-06-30 07:30 | 44742.3125 | 0 | 26.313 | 39.95
2022-06-30 08:00 | 44742.3333 | 0 | 25.5613 | 39.95
2022-06-30 08:30 | 44742.3542 | 0 | 24.9499 | 39.95
2022-06-30 09:00 | 44742.375 | 0 | 24.5918 | 39.95
2022-06-30 09:30 | 44742.3958 | 0 | 22.7708 | 39.95
2022-06-30 10:00 | 44742.4167 | 0 | 21.873 | 39.95
2022-06-30 10:30 | 44742.4375 | 0 | 22.4872 | 39.95
2022-06-30 11:00 | 44742.4583 | 0 | 20.1371 | 39.95
2022-06-30 11:30 | 44742.4792 | 0 | 21.0898 | 39.95
2022-06-30 12:00 | 44742.5 | 0 | 21.543 | 39.95
2022-06-30 12:30 | 44742.5208 | 0 | 22.4414 | 39.95
2022-06-30 13:00 | 44742.5417 | 0 | 20.8059 | 39.95
2022-06-30 13:30 | 44742.5625 | 0 | 20.8074 | 39.95
2022-06-30 14:00 | 44742.5833 | 0 | 21.8836 | 39.95
2022-06-30 14:30 | 44742.6042 | 0 | 13.048 | 39.95
2022-06-30 15:00 | 44742.625 | 0 | 12.1724 | 39.95
2022-06-30 15:30 | 44742.6458 | 0 | 12.6966 | 39.95
2022-06-30 16:00 | 44742.6667 | 0 | 13.0744 | 39.95
2022-06-30 16:30 | 44742.6875 | 0 | 13.4828 | 39.95
2022-06-30 17:00 | 44742.7083 | 0 | 14.1487 | 39.95
2022-06-30 17:30 | 44742.7292 | 0 | 14.6759 | 39.95
2022-06-30 18:00 | 44742.75 | 0 | 14.846 | 39.95
2022-06-30 18:30 | 44742.7708 | 0 | 14.7618 | 39.95
2022-06-30 19:00 | 44742.7917 | 0 | 14.3409 | 39.95
2022-06-30 19:30 | 44742.8125 | 0 | 14.0106 | 39.95
2022-06-30 20:00 | 44742.8333 | 0 | 13.7453 | 39.95
2022-06-30 20:30 | 44742.8542 | 0 | 13.3463 | 39.95
2022-06-30 21:00 | 44742.875 | 0 | 12.7803 | 39.95
2022-06-30 21:30 | 44742.8958 | 0 | 12.3055 | 39.95
2022-06-30 22:00 | 44742.9167 | 0 | 11.6502 | 39.95
2022-06-30 22:30 | 44742.9375 | 0 | 10.8358 | 39.95
2022-06-30 23:00 | 44742.9583 | 0 | 10.2763 | 39.95
2022-06-30 23:30 | 44742.9792 | 0 | 9.6779 | 39.95
2022-07-01 | 44743 | 0 | 9.0125 | 39.95
2022-07-01 00:30 | 44743.0208 | 0 | 8.7412 | 39.95
2022-07-01 01:00 | 44743.0417 | 0 | 8.5418 | 39.95
2022-07-01 01:30 | 44743.0625 | 0 | 8.2538 | 39.95
2022-07-01 02:00 | 44743.0833 | 0 | 8.1875 | 39.95
2022-07-01 02:30 | 44743.1042 | 0 | 8.1433 | 39.95
2022-07-01 03:00 | 44743.125 | 0 | 8.136 | 39.95
2022-07-01 03:30 | 44743.1458 | 0 | 8.2437 | 39.95
2022-07-01 04:00 | 44743.1667 | 0 | 8.4877 | 39.95
2022-07-01 04:30 | 44743.1875 | 0 | 8.7717 | 39.95
2022-07-01 05:00 | 44743.2083 | 0 | 9.4662 | 39.95
2022-07-01 05:30 | 44743.2292 | 0 | 10.2371 | 39.95
2022-07-01 06:00 | 44743.25 | 0 | 11.0765 | 39.95
2022-07-01 06:30 | 44743.2708 | 0 | 12.0604 | 39.95
2022-07-01 07:00 | 44743.2917 | 0 | 13.2013 | 39.95
2022-07-01 07:30 | 44743.3125 | 0 | 13.6396 | 39.95
2022-07-01 08:00 | 44743.3333 | 0 | 14.0468 | 39.95
2022-07-01 08:30 | 44743.3542 | 0 | 14.3931 | 39.95
2022-07-01 09:00 | 44743.375 | 0 | 14.3324 | 39.95
2022-07-01 09:30 | 44743.3958 | 0 | 14.2225 | 39.95
2022-07-01 10:00 | 44743.4167 | 0 | 13.5965 | 39.95
2022-07-01 10:30 | 44743.4375 | 0 | 13.5679 | 39.95
2022-07-01 11:00 | 44743.4583 | 0 | 13.4782 | 39.95
2022-07-01 11:30 | 44743.4792 | 0 | 13.4872 | 39.95
2022-07-01 12:00 | 44743.5 | 0 | 13.2632 | 39.95
2022-07-01 12:30 | 44743.5208 | 0 | 13.1401 | 39.95
2022-07-01 13:00 | 44743.5417 | 0 | 13.0225 | 39.95
2022-07-01 13:30 | 44743.5625 | 0 | 13.6553 | 39.95
2022-07-01 14:00 | 44743.5833 | 0 | 13.9859 | 39.95
2022-07-01 14:30 | 44743.6042 | 0 | 13.8072 | 39.95
2022-07-01 15:00 | 44743.625 | 0 | 13.7994 | 39.95
2022-07-01 15:30 | 44743.6458 | 0 | 14.0508 | 39.95
2022-07-01 16:00 | 44743.6667 | 0 | 14.3787 | 39.95
2022-07-01 16:30 | 44743.6875 | 0 | 14.8124 | 39.95
2022-07-01 17:00 | 44743.7083 | 0 | 15.3752 | 39.95
2022-07-01 17:30 | 44743.7292 | 0 | 15.6272 | 39.95
2022-07-01 18:00 | 44743.75 | 0 | 15.4552 | 39.95
2022-07-01 18:30 | 44743.7708 | 0 | 15.2698 | 39.95
2022-07-01 19:00 | 44743.7917 | 0 | 14.915 | 39.95
2022-07-01 19:30 | 44743.8125 | 0 | 14.846 | 39.95
2022-07-01 20:00 | 44743.8333 | 0 | 14.4795 | 39.95
2022-07-01 20:30 | 44743.8542 | 0 | 13.9096 | 39.95
2022-07-01 21:00 | 44743.875 | 0 | 13.4427 | 39.95
2022-07-01 21:30 | 44743.8958 | 0 | 12.7052 | 39.95
2022-07-01 22:00 | 44743.9167 | 0 | 12.0221 | 39.95
2022-07-01 22:30 | 44743.9375 | 0 | 11.1657 | 39.95
2022-07-01 23:00 | 44743.9583 | 0 | 10.6904 | 39.95
2022-07-01 23:30 | 44743.9792 | 0 | 10.1705 | 39.95
2022-07-02 | 44744 | 0 | 9.464 | 39.95
2022-07-02 00:30 | 44744.0208 | 0 | 9.0394 | 39.95
2022-07-02 01:00 | 44744.0417 | 0 | 8.7624 | 39.95
2022-07-02 01:30 | 44744.0625 | 0 | 8.5444 | 39.95
2022-07-02 02:00 | 44744.0833 | 0 | 8.3581 | 39.95
2022-07-02 02:30 | 44744.1042 | 0 | 8.2952 | 39.95
2022-07-02 03:00 | 44744.125 | 0 | 8.2264 | 39.95
2022-07-02 03:30 | 44744.1458 | 0 | 8.1532 | 39.95
2022-07-02 04:00 | 44744.1667 | 0 | 8.2975 | 39.95
2022-07-02 04:30 | 44744.1875 | 0 | 8.2934 | 39.95
2022-07-02 05:00 | 44744.2083 | 0 | 8.5037 | 39.95
2022-07-02 05:30 | 44744.2292 | 0 | 8.7333 | 39.95
2022-07-02 06:00 | 44744.25 | 0 | 9.2108 | 39.95
2022-07-02 06:30 | 44744.2708 | 0 | 9.698 | 39.95
2022-07-02 07:00 | 44744.2917 | 0 | 10.291 | 39.95
2022-07-02 07:30 | 44744.3125 | 0 | 10.7024 | 39.95
2022-07-02 08:00 | 44744.3333 | 0 | 11.4063 | 39.95
2022-07-02 08:30 | 44744.3542 | 0 | 11.5165 | 39.95
2022-07-02 09:00 | 44744.375 | 0 | 12.0012 | 39.95
2022-07-02 09:30 | 44744.3958 | 0 | 11.9352 | 39.95
2022-07-02 10:00 | 44744.4167 | 0 | 11.7879 | 39.95
2022-07-02 10:30 | 44744.4375 | 0 | 12.1059 | 39.95
2022-07-02 11:00 | 44744.4583 | 0 | 11.7308 | 39.95
2022-07-02 11:30 | 44744.4792 | 0 | 11.5999 | 39.95
2022-07-02 12:00 | 44744.5 | 0 | 11.4863 | 39.95
2022-07-02 12:30 | 44744.5208 | 0 | 11.2341 | 39.95
2022-07-02 13:00 | 44744.5417 | 0 | 11.3982 | 39.95
2022-07-02 13:30 | 44744.5625 | 0 | 11.638 | 39.95
2022-07-02 14:00 | 44744.5833 | 0 | 11.2034 | 39.95
2022-07-02 14:30 | 44744.6042 | 0 | 11.4094 | 39.95
2022-07-02 15:00 | 44744.625 | 0 | 12.0945 | 39.95
2022-07-02 15:30 | 44744.6458 | 0 | 12.2354 | 39.95
2022-07-02 16:00 | 44744.6667 | 0 | 12.0007 | 39.95
2022-07-02 16:30 | 44744.6875 | 0 | 12.7078 | 39.95
2022-07-02 17:00 | 44744.7083 | 0 | 13.3106 | 39.95
2022-07-02 17:30 | 44744.7292 | 0 | 13.4627 | 39.95
2022-07-02 18:00 | 44744.75 | 0 | 13.4028 | 39.95
2022-07-02 18:30 | 44744.7708 | 0 | 13.2781 | 39.95
2022-07-02 19:00 | 44744.7917 | 0 | 12.9037 | 39.95
2022-07-02 19:30 | 44744.8125 | 0 | 12.5457 | 39.95
2022-07-02 20:00 | 44744.8333 | 0 | 12.2228 | 39.95
2022-07-02 20:30 | 44744.8542 | 0 | 11.9146 | 39.95
2022-07-02 21:00 | 44744.875 | 0 | 11.4687 | 39.95
2022-07-02 21:30 | 44744.8958 | 0 | 10.9979 | 39.95
2022-07-02 22:00 | 44744.9167 | 0 | 10.6027 | 39.95
2022-07-02 22:30 | 44744.9375 | 0 | 9.8172 | 39.95
2022-07-02 23:00 | 44744.9583 | 0 | 9.3437 | 39.95
2022-07-02 23:30 | 44744.9792 | 0 | 8.8917 | 39.95
2022-07-03 | 44745 | 0 | 8.331 | 39.95
2022-07-03 00:30 | 44745.0208 | 0 | 7.9247 | 39.95
2022-07-03 01:00 | 44745.0417 | 0 | 7.7402 | 39.95
2022-07-03 01:30 | 44745.0625 | 0 | 7.5513 | 39.95
2022-07-03 02:00 | 44745.0833 | 0 | 7.5822 | 39.95
2022-07-03 02:30 | 44745.1042 | 0 | 7.4098 | 39.95
2022-07-03 03:00 | 44745.125 | 0 | 7.3812 | 39.95
2022-07-03 03:30 | 44745.1458 | 0 | 7.3102 | 39.95
2022-07-03 04:00 | 44745.1667 | 0 | 7.395 | 39.95
2022-07-03 04:30 | 44745.1875 | 0 | 7.3714 | 39.95
2022-07-03 05:00 | 44745.2083 | 0 | 7.45 | 39.95
2022-07-03 05:30 | 44745.2292 | 0 | 7.6419 | 39.95
2022-07-03 06:00 | 44745.25 | 0 | 7.9437 | 39.95
2022-07-03 06:30 | 44745.2708 | 0 | 8.4218 | 39.95
2022-07-03 07:00 | 44745.2917 | 0 | 9.017 | 39.95
2022-07-03 07:30 | 44745.3125 | 0 | 8.7875 | 39.95
2022-07-03 08:00 | 44745.3333 | 0 | 9.2797 | 39.95
2022-07-03 08:30 | 44745.3542 | 0 | 9.0073 | 39.95
2022-07-03 09:00 | 44745.375 | 0 | 9.366 | 39.95
2022-07-03 09:30 | 44745.3958 | 0 | 7.8948 | 39.95
2022-07-03 10:00 | 44745.4167 | 0 | 7.2092 | 39.95
2022-07-03 10:30 | 44745.4375 | 0 | 6.6949 | 39.95
2022-07-03 11:00 | 44745.4583 | 0 | 6.2162 | 39.95
2022-07-03 11:30 | 44745.4792 | 0 | 6.3323 | 39.95
2022-07-03 12:00 | 44745.5 | 0 | 5.7926 | 39.95
2022-07-03 12:30 | 44745.5208 | 0 | 5.7645 | 39.95
2022-07-03 13:00 | 44745.5417 | 0 | 5.9784 | 39.95
2022-07-03 13:30 | 44745.5625 | 0 | 8.4541 | 39.95
2022-07-03 14:00 | 44745.5833 | 0 | 9.2514 | 39.95
2022-07-03 14:30 | 44745.6042 | 0 | 9.4245 | 39.95
2022-07-03 15:00 | 44745.625 | 0 | 10.1156 | 39.95
2022-07-03 15:30 | 44745.6458 | 0 | 10.7658 | 39.95
2022-07-03 16:00 | 44745.6667 | 0 | 11.412 | 39.95
2022-07-03 16:30 | 44745.6875 | 0 | 12.3319 | 39.95
2022-07-03 17:00 | 44745.7083 | 0 | 13.3127 | 39.95
2022-07-03 17:30 | 44745.7292 | 0 | 14.1154 | 39.95
2022-07-03 18:00 | 44745.75 | 0 | 14.4703 | 39.95
2022-07-03 18:30 | 44745.7708 | 0 | 14.2328 | 39.95
2022-07-03 19:00 | 44745.7917 | 0 | 13.9194 | 39.95
2022-07-03 19:30 | 44745.8125 | 0 | 13.6814 | 39.95
2022-07-03 20:00 | 44745.8333 | 0 | 13.4001 | 39.95
2022-07-03 20:30 | 44745.8542 | 0 | 12.7844 | 39.95
2022-07-03 21:00 | 44745.875 | 0 | 12.0434 | 39.95
2022-07-03 21:30 | 44745.8958 | 0 | 11.3952 | 39.95
2022-07-03 22:00 | 44745.9167 | 0 | 10.7408 | 39.95
2022-07-03 22:30 | 44745.9375 | 0 | 9.8975 | 39.95
2022-07-03 23:00 | 44745.9583 | 0 | 9.1122 | 39.95
2022-07-03 23:30 | 44745.9792 | 0 | 8.6145 | 39.95
2022-07-04 | 44746 | 0 | 8.2842 | 39.95
2022-07-04 00:30 | 44746.0208 | 0 | 8.0093 | 39.95
2022-07-04 01:00 | 44746.0417 | 0 | 7.8076 | 39.95
2022-07-04 01:30 | 44746.0625 | 0 | 7.7019 | 39.95
2022-07-04 02:00 | 44746.0833 | 0 | 7.6011 | 39.95
2022-07-04 02:30 | 44746.1042 | 0 | 7.5587 | 39.95
2022-07-04 03:00 | 44746.125 | 0 | 7.6172 | 39.95
2022-07-04 03:30 | 44746.1458 | 0 | 7.7484 | 39.95
2022-07-04 04:00 | 44746.1667 | 0 | 8.0524 | 39.95
2022-07-04 04:30 | 44746.1875 | 0 | 8.5009 | 39.95
2022-07-04 05:00 | 44746.2083 | 0 | 9.251 | 39.95
2022-07-04 05:30 | 44746.2292 | 0 | 10.06 | 39.95
2022-07-04 06:00 | 44746.25 | 0 | 11.1623 | 39.95
2022-07-04 06:30 | 44746.2708 | 0 | 12.6679 | 39.95
2022-07-04 07:00 | 44746.2917 | 0 | 14.1325 | 39.95
2022-07-04 07:30 | 44746.3125 | 0 | 14.6212 | 39.95
2022-07-04 08:00 | 44746.3333 | 0 | 15.3682 | 39.95
2022-07-04 08:30 | 44746.3542 | 0 | 15.6547 | 39.95
2022-07-04 09:00 | 44746.375 | 0 | 14.8719 | 39.95
2022-07-04 09:30 | 44746.3958 | 0 | 13.6844 | 39.95
2022-07-04 10:00 | 44746.4167 | 0 | 14.0035 | 39.95
2022-07-04 10:30 | 44746.4375 | 0 | 14.6558 | 39.95
2022-07-04 11:00 | 44746.4583 | 0 | 14.4641 | 39.95
2022-07-04 11:30 | 44746.4792 | 0 | 14.5815 | 39.95
2022-07-04 12:00 | 44746.5 | 0 | 14.5523 | 39.95
2022-07-04 12:30 | 44746.5208 | 0 | 14.915 | 39.95
2022-07-04 13:00 | 44746.5417 | 0 | 15.0596 | 39.95
2022-07-04 13:30 | 44746.5625 | 0 | 15.4032 | 39.95
2022-07-04 14:00 | 44746.5833 | 0 | 15.103 | 39.95
2022-07-04 14:30 | 44746.6042 | 0 | 15.1292 | 39.95
2022-07-04 15:00 | 44746.625 | 0 | 15.6095 | 39.95
2022-07-04 15:30 | 44746.6458 | 0 | 15.9911 | 39.95
2022-07-04 16:00 | 44746.6667 | 0 | 16.4181 | 39.95
2022-07-04 16:30 | 44746.6875 | 0 | 17.2572 | 39.95
2022-07-04 17:00 | 44746.7083 | 0 | 18.0168 | 39.95
2022-07-04 17:30 | 44746.7292 | 0 | 18.9369 | 39.95
2022-07-04 18:00 | 44746.75 | 0 | 18.7652 | 39.95
2022-07-04 18:30 | 44746.7708 | 0 | 18.8418 | 39.95
2022-07-04 19:00 | 44746.7917 | 0 | 18.4551 | 39.95
2022-07-04 19:30 | 44746.8125 | 0 | 17.9662 | 39.95
2022-07-04 20:00 | 44746.8333 | 0 | 17.3709 | 39.95
2022-07-04 20:30 | 44746.8542 | 0 | 16.3401 | 39.95
2022-07-04 21:00 | 44746.875 | 0 | 15.4249 | 39.95
2022-07-04 21:30 | 44746.8958 | 0 | 14.3758 | 39.95
2022-07-04 22:00 | 44746.9167 | 0 | 13.2388 | 39.95
2022-07-04 22:30 | 44746.9375 | 0 | 12.0581 | 39.95
2022-07-04 23:00 | 44746.9583 | 0 | 11.4456 | 39.95
2022-07-04 23:30 | 44746.9792 | 0 | 10.6184 | 39.95
2022-07-05 | 44747 | 0 | 9.8462 | 39.95
2022-07-05 00:30 | 44747.0208 | 0 | 9.3662 | 39.95
2022-07-05 01:00 | 44747.0417 | 0 | 9.106 | 39.95
2022-07-05 01:30 | 44747.0625 | 0 | 8.8385 | 39.95
2022-07-05 02:00 | 44747.0833 | 0 | 8.7223 | 39.95
2022-07-05 02:30 | 44747.1042 | 0 | 8.6341 | 39.95
2022-07-05 03:00 | 44747.125 | 0 | 8.5041 | 39.95
2022-07-05 03:30 | 44747.1458 | 0 | 8.5793 | 39.95
2022-07-05 04:00 | 44747.1667 | 0 | 8.9136 | 39.95
2022-07-05 04:30 | 44747.1875 | 0 | 9.5603 | 39.95
2022-07-05 05:00 | 44747.2083 | 0 | 10.3815 | 39.95
2022-07-05 05:30 | 44747.2292 | 0 | 10.969 | 39.95
2022-07-05 06:00 | 44747.25 | 0 | 12.5881 | 39.95
2022-07-05 06:30 | 44747.2708 | 0 | 14.0905 | 39.95
2022-07-05 07:00 | 44747.2917 | 0 | 15.7386 | 39.95
2022-07-05 07:30 | 44747.3125 | 0 | 16.6962 | 39.95
2022-07-05 08:00 | 44747.3333 | 0 | 17.0752 | 39.95
2022-07-05 08:30 | 44747.3542 | 0 | 17.1611 | 39.95
2022-07-05 09:00 | 44747.375 | 0 | 16.7266 | 39.95
2022-07-05 09:30 | 44747.3958 | 0 | 17.1058 | 39.95
2022-07-05 10:00 | 44747.4167 | 0 | 16.9583 | 39.95
2022-07-05 10:30 | 44747.4375 | 0 | 16.6393 | 39.95
2022-07-05 11:00 | 44747.4583 | 0 | 16.8302 | 39.95
2022-07-05 11:30 | 44747.4792 | 0 | 16.9235 | 39.95
2022-07-05 12:00 | 44747.5 | 0 | 16.4756 | 39.95
2022-07-05 12:30 | 44747.5208 | 0 | 16.4198 | 39.95
2022-07-05 13:00 | 44747.5417 | 0 | 16.779 | 39.95
2022-07-05 13:30 | 44747.5625 | 0 | 17.2516 | 39.95
2022-07-05 14:00 | 44747.5833 | 0 | 17.3541 | 39.95
2022-07-05 14:30 | 44747.6042 | 0 | 17.5461 | 39.95
2022-07-05 15:00 | 44747.625 | 0 | 17.4934 | 39.95
2022-07-05 15:30 | 44747.6458 | 0 | 17.7832 | 39.95
2022-07-05 16:00 | 44747.6667 | 0 | 17.8799 | 39.95
2022-07-05 16:30 | 44747.6875 | 0 | 18.4955 | 39.95
2022-07-05 17:00 | 44747.7083 | 0 | 19.342 | 39.95
2022-07-05 17:30 | 44747.7292 | 0 | 19.646 | 39.95
2022-07-05 18:00 | 44747.75 | 0 | 19.7929 | 39.95
2022-07-05 18:30 | 44747.7708 | 0 | 19.6589 | 39.95
2022-07-05 19:00 | 44747.7917 | 0 | 19.3586 | 39.95
2022-07-05 19:30 | 44747.8125 | 0 | 18.8348 | 39.95
2022-07-05 20:00 | 44747.8333 | 0 | 18.2243 | 39.95
2022-07-05 20:30 | 44747.8542 | 0 | 17.207 | 39.95
2022-07-05 21:00 | 44747.875 | 0 | 16.0891 | 39.95
2022-07-05 21:30 | 44747.8958 | 0 | 15.0499 | 39.95
2022-07-05 22:00 | 44747.9167 | 0 | 13.8656 | 39.95
2022-07-05 22:30 | 44747.9375 | 0 | 12.4866 | 39.95
2022-07-05 23:00 | 44747.9583 | 0 | 11.5914 | 39.95
2022-07-05 23:30 | 44747.9792 | 0 | 10.9163 | 39.95
2022-07-06 | 44748 | 0 | 10.2281 | 39.95
2022-07-06 00:30 | 44748.0208 | 0 | 9.6355 | 39.95
2022-07-06 01:00 | 44748.0417 | 0 | 9.3677 | 39.95
2022-07-06 01:30 | 44748.0625 | 0 | 9.1786 | 39.95
2022-07-06 02:00 | 44748.0833 | 0 | 8.9278 | 39.95
2022-07-06 02:30 | 44748.1042 | 0 | 8.8237 | 39.95
2022-07-06 03:00 | 44748.125 | 0 | 8.9022 | 39.95
2022-07-06 03:30 | 44748.1458 | 0 | 8.8707 | 39.95
2022-07-06 04:00 | 44748.1667 | 0 | 9.0976 | 39.95
2022-07-06 04:30 | 44748.1875 | 0 | 9.586 | 39.95
2022-07-06 05:00 | 44748.2083 | 0 | 10.2598 | 39.95
2022-07-06 05:30 | 44748.2292 | 0 | 10.9611 | 39.95
2022-07-06 06:00 | 44748.25 | 0 | 12.4262 | 39.95
2022-07-06 06:30 | 44748.2708 | 0 | 13.8828 | 39.95
2022-07-06 07:00 | 44748.2917 | 0 | 14.8259 | 39.95
2022-07-06 07:30 | 44748.3125 | 0 | 15.4855 | 39.95
2022-07-06 08:00 | 44748.3333 | 0 | 16.1714 | 39.95
2022-07-06 08:30 | 44748.3542 | 0 | 15.4317 | 39.95
2022-07-06 09:00 | 44748.375 | 0 | 14.3244 | 39.95
2022-07-06 09:30 | 44748.3958 | 0 | 13.3314 | 39.95
2022-07-06 10:00 | 44748.4167 | 0 | 10.958 | 39.95
2022-07-06 10:30 | 44748.4375 | 0 | 10.2121 | 39.95
2022-07-06 11:00 | 44748.4583 | 0 | 10.8464 | 39.95
2022-07-06 11:30 | 44748.4792 | 0 | 10.6632 | 39.95
2022-07-06 12:00 | 44748.5 | 0 | 9.7772 | 39.95
2022-07-06 12:30 | 44748.5208 | 0 | 8.825 | 39.95
2022-07-06 13:00 | 44748.5417 | 0 | 10.2514 | 39.95
2022-07-06 13:30 | 44748.5625 | 0 | 12.42 | 39.95
2022-07-06 14:00 | 44748.5833 | 0 | 12.4612 | 39.95
2022-07-06 14:30 | 44748.6042 | 0 | 12.4218 | 39.95
2022-07-06 15:00 | 44748.625 | 0 | 12.0606 | 39.95
2022-07-06 15:30 | 44748.6458 | 0 | 13.2818 | 39.95
2022-07-06 16:00 | 44748.6667 | 0 | 13.5721 | 39.95
2022-07-06 16:30 | 44748.6875 | 0 | 14.3382 | 39.95
2022-07-06 17:00 | 44748.7083 | 0 | 15.4457 | 39.95
2022-07-06 17:30 | 44748.7292 | 0 | 16.629 | 39.95
2022-07-06 18:00 | 44748.75 | 0 | 16.9157 | 39.95
2022-07-06 18:30 | 44748.7708 | 0 | 17.3142 | 39.95
2022-07-06 19:00 | 44748.7917 | 0 | 17.336 | 39.95
2022-07-06 19:30 | 44748.8125 | 0 | 16.8966 | 39.95
2022-07-06 20:00 | 44748.8333 | 0 | 16.3579 | 39.95
2022-07-06 20:30 | 44748.8542 | 0 | 15.8822 | 39.95
2022-07-06 21:00 | 44748.875 | 0 | 15.1851 | 39.95
2022-07-06 21:30 | 44748.8958 | 0 | 14.4209 | 39.95
2022-07-06 22:00 | 44748.9167 | 0 | 13.4992 | 39.95
2022-07-06 22:30 | 44748.9375 | 0 | 12.3544 | 39.95
2022-07-06 23:00 | 44748.9583 | 0 | 11.5318 | 39.95
2022-07-06 23:30 | 44748.9792 | 0 | 10.7519 | 39.95
2022-07-07 | 44749 | 0 | 9.9419 | 39.95
2022-07-07 00:30 | 44749.0208 | 0 | 9.44 | 39.95
2022-07-07 01:00 | 44749.0417 | 0 | 9.2801 | 39.95
2022-07-07 01:30 | 44749.0625 | 0 | 8.9785 | 39.95
2022-07-07 02:00 | 44749.0833 | 0 | 9.0218 | 39.95
2022-07-07 02:30 | 44749.1042 | 0 | 8.7556 | 39.95
2022-07-07 03:00 | 44749.125 | 0 | 8.7835 | 39.95
2022-07-07 03:30 | 44749.1458 | 0 | 8.695 | 39.95
2022-07-07 04:00 | 44749.1667 | 0 | 9.1176 | 39.95
2022-07-07 04:30 | 44749.1875 | 0 | 9.4647 | 39.95
2022-07-07 05:00 | 44749.2083 | 0 | 10.2452 | 39.95
2022-07-07 05:30 | 44749.2292 | 0 | 10.9769 | 39.95
2022-07-07 06:00 | 44749.25 | 0 | 12.3081 | 39.95
2022-07-07 06:30 | 44749.2708 | 0 | 13.5105 | 39.95
2022-07-07 07:00 | 44749.2917 | 0 | 14.4399 | 39.95
2022-07-07 07:30 | 44749.3125 | 0 | 14.1306 | 39.95
2022-07-07 08:00 | 44749.3333 | 0 | 13.2752 | 39.95
2022-07-07 08:30 | 44749.3542 | 0 | 12.302 | 39.95
2022-07-07 09:00 | 44749.375 | 0 | 11.3922 | 39.95
2022-07-07 09:30 | 44749.3958 | 0 | 10.6641 | 39.95
2022-07-07 10:00 | 44749.4167 | 0 | 9.984 | 39.95
2022-07-07 10:30 | 44749.4375 | 0 | 9.2635 | 39.95
2022-07-07 11:00 | 44749.4583 | 0 | 8.7928 | 39.95
2022-07-07 11:30 | 44749.4792 | 0 | 8.6392 | 39.95
2022-07-07 12:00 | 44749.5 | 0 | 8.8122 | 39.95
2022-07-07 12:30 | 44749.5208 | 0 | 8.4171 | 39.95
2022-07-07 13:00 | 44749.5417 | 0 | 8.5266 | 39.95
2022-07-07 13:30 | 44749.5625 | 0 | 8.8032 | 39.95
2022-07-07 14:00 | 44749.5833 | 0 | 9.2916 | 39.95
2022-07-07 14:30 | 44749.6042 | 0 | 9.9135 | 39.95
2022-07-07 15:00 | 44749.625 | 0 | 10.4392 | 39.95
2022-07-07 15:30 | 44749.6458 | 0 | 11.3364 | 39.95
2022-07-07 16:00 | 44749.6667 | 0 | 12.0069 | 39.95
2022-07-07 16:30 | 44749.6875 | 0 | 12.91 | 39.95
2022-07-07 17:00 | 44749.7083 | 0 | 13.766 | 39.95
2022-07-07 17:30 | 44749.7292 | 0 | 14.5895 | 39.95
2022-07-07 18:00 | 44749.75 | 0 | 15.0401 | 39.95
2022-07-07 18:30 | 44749.7708 | 0 | 15.1822 | 39.95
2022-07-07 19:00 | 44749.7917 | 0 | 15.0642 | 39.95
2022-07-07 19:30 | 44749.8125 | 0 | 14.7898 | 39.95
2022-07-07 20:00 | 44749.8333 | 0 | 14.5012 | 39.95
2022-07-07 20:30 | 44749.8542 | 0 | 13.8187 | 39.95
2022-07-07 21:00 | 44749.875 | 0 | 13.3495 | 39.95
2022-07-07 21:30 | 44749.8958 | 0 | 12.8532 | 39.95
2022-07-07 22:00 | 44749.9167 | 0 | 12.3097 | 39.95
2022-07-07 22:30 | 44749.9375 | 0 | 11.4613 | 39.95
2022-07-07 23:00 | 44749.9583 | 0 | 10.8163 | 39.95
2022-07-07 23:30 | 44749.9792 | 0 | 10.175 | 39.95
2022-07-08 | 44750 | 0 | 9.442 | 39.95
2022-07-08 00:30 | 44750.0208 | 0 | 8.9532 | 39.95
2022-07-08 01:00 | 44750.0417 | 0 | 8.8671 | 39.95
2022-07-08 01:30 | 44750.0625 | 0 | 8.5648 | 39.95
2022-07-08 02:00 | 44750.0833 | 0 | 8.4933 | 39.95
2022-07-08 02:30 | 44750.1042 | 0 | 8.4681 | 39.95
2022-07-08 03:00 | 44750.125 | 0 | 8.4652 | 39.95
2022-07-08 03:30 | 44750.1458 | 0 | 8.4831 | 39.95
2022-07-08 04:00 | 44750.1667 | 0 | 8.8938 | 39.95
2022-07-08 04:30 | 44750.1875 | 0 | 9.2965 | 39.95
2022-07-08 05:00 | 44750.2083 | 0 | 9.9738 | 39.95
2022-07-08 05:30 | 44750.2292 | 0 | 10.6278 | 39.95
2022-07-08 06:00 | 44750.25 | 0 | 11.9102 | 39.95
2022-07-08 06:30 | 44750.2708 | 0 | 13.1874 | 39.95
2022-07-08 07:00 | 44750.2917 | 0 | 14.0677 | 39.95
2022-07-08 07:30 | 44750.3125 | 0 | 13.9838 | 39.95
2022-07-08 08:00 | 44750.3333 | 0 | 13.437 | 39.95
2022-07-08 08:30 | 44750.3542 | 0 | 12.6562 | 39.95
2022-07-08 09:00 | 44750.375 | 0 | 11.4157 | 39.95
2022-07-08 09:30 | 44750.3958 | 0 | 10.6198 | 39.95
2022-07-08 10:00 | 44750.4167 | 0 | 9.731 | 39.95
2022-07-08 10:30 | 44750.4375 | 0 | 9.2914 | 39.95
2022-07-08 11:00 | 44750.4583 | 0 | 8.7287 | 39.95
2022-07-08 11:30 | 44750.4792 | 0 | 8.5098 | 39.95
2022-07-08 12:00 | 44750.5 | 0 | 8.2236 | 39.95
2022-07-08 12:30 | 44750.5208 | 0 | 8.1319 | 39.95
2022-07-08 13:00 | 44750.5417 | 0 | 8.2346 | 39.95
2022-07-08 13:30 | 44750.5625 | 0 | 8.4309 | 39.95
2022-07-08 14:00 | 44750.5833 | 0 | 8.9087 | 39.95
2022-07-08 14:30 | 44750.6042 | 0 | 9.4187 | 39.95
2022-07-08 15:00 | 44750.625 | 0 | 10.1504 | 39.95
2022-07-08 15:30 | 44750.6458 | 0 | 11.0557 | 39.95
2022-07-08 16:00 | 44750.6667 | 0 | 11.9527 | 39.95
2022-07-08 16:30 | 44750.6875 | 0 | 13.2001 | 39.95
2022-07-08 17:00 | 44750.7083 | 0 | 14.3983 | 39.95
2022-07-08 17:30 | 44750.7292 | 0 | 15.3659 | 39.95
2022-07-08 18:00 | 44750.75 | 0 | 15.788 | 39.95
2022-07-08 18:30 | 44750.7708 | 0 | 15.8848 | 39.95
2022-07-08 19:00 | 44750.7917 | 0 | 15.7993 | 39.95
2022-07-08 19:30 | 44750.8125 | 0 | 15.6255 | 39.95
2022-07-08 20:00 | 44750.8333 | 0 | 15.4993 | 39.95
2022-07-08 20:30 | 44750.8542 | 0 | 14.9137 | 39.95
2022-07-08 21:00 | 44750.875 | 0 | 14.3571 | 39.95
2022-07-08 21:30 | 44750.8958 | 0 | 13.6683 | 39.95
2022-07-08 22:00 | 44750.9167 | 0 | 12.9737 | 39.95
2022-07-08 22:30 | 44750.9375 | 0 | 11.9567 | 39.95
2022-07-08 23:00 | 44750.9583 | 0 | 11.4606 | 39.95
2022-07-08 23:30 | 44750.9792 | 0 | 10.8993 | 39.95
2022-07-09 | 44751 | 0 | 10.0907 | 39.95
2022-07-09 00:30 | 44751.0208 | 0 | 9.5633 | 39.95
2022-07-09 01:00 | 44751.0417 | 0 | 9.3224 | 39.95
2022-07-09 01:30 | 44751.0625 | 0 | 8.969 | 39.95
2022-07-09 02:00 | 44751.0833 | 0 | 8.7865 | 39.95
2022-07-09 02:30 | 44751.1042 | 0 | 8.7927 | 39.95
2022-07-09 03:00 | 44751.125 | 0 | 8.5878 | 39.95
2022-07-09 03:30 | 44751.1458 | 0 | 8.68 | 39.95
2022-07-09 04:00 | 44751.1667 | 0 | 8.7618 | 39.95
2022-07-09 04:30 | 44751.1875 | 0 | 8.8863 | 39.95
2022-07-09 05:00 | 44751.2083 | 0 | 9.3328 | 39.95
2022-07-09 05:30 | 44751.2292 | 0 | 9.6203 | 39.95
2022-07-09 06:00 | 44751.25 | 0 | 10.1091 | 39.95
2022-07-09 06:30 | 44751.2708 | 0 | 10.8568 | 39.95
2022-07-09 07:00 | 44751.2917 | 0 | 11.4824 | 39.95
2022-07-09 07:30 | 44751.3125 | 0 | 11.4824 | 39.95
2022-07-09 08:00 | 44751.3333 | 0 | 11.2733 | 39.95
2022-07-09 08:30 | 44751.3542 | 0 | 10.6141 | 39.95
2022-07-09 09:00 | 44751.375 | 0 | 10.0021 | 39.95
2022-07-09 09:30 | 44751.3958 | 0 | 9.2063 | 39.95
2022-07-09 10:00 | 44751.4167 | 0 | 8.2515 | 39.95
2022-07-09 10:30 | 44751.4375 | 0 | 7.6032 | 39.95
2022-07-09 11:00 | 44751.4583 | 0 | 7.1189 | 39.95
2022-07-09 11:30 | 44751.4792 | 0 | 6.7588 | 39.95
2022-07-09 12:00 | 44751.5 | 0 | 6.6356 | 39.95
2022-07-09 12:30 | 44751.5208 | 0 | 6.3803 | 39.95
2022-07-09 13:00 | 44751.5417 | 0 | 6.4933 | 39.95
2022-07-09 13:30 | 44751.5625 | 0 | 6.7903 | 39.95
2022-07-09 14:00 | 44751.5833 | 0 | 7.2911 | 39.95
2022-07-09 14:30 | 44751.6042 | 0 | 7.939 | 39.95
2022-07-09 15:00 | 44751.625 | 0 | 8.588 | 39.95
2022-07-09 15:30 | 44751.6458 | 0 | 9.5671 | 39.95
2022-07-09 16:00 | 44751.6667 | 0 | 10.626 | 39.95
2022-07-09 16:30 | 44751.6875 | 0 | 11.7277 | 39.95
2022-07-09 17:00 | 44751.7083 | 0 | 12.8772 | 39.95
2022-07-09 17:30 | 44751.7292 | 0 | 13.8688 | 39.95
2022-07-09 18:00 | 44751.75 | 0 | 14.428 | 39.95
2022-07-09 18:30 | 44751.7708 | 0 | 14.6669 | 39.95
2022-07-09 19:00 | 44751.7917 | 0 | 14.578 | 39.95
2022-07-09 19:30 | 44751.8125 | 0 | 14.3501 | 39.95
2022-07-09 20:00 | 44751.8333 | 0 | 14.2378 | 39.95
2022-07-09 20:30 | 44751.8542 | 0 | 13.6237 | 39.95
2022-07-09 21:00 | 44751.875 | 0 | 13.1718 | 39.95
2022-07-09 21:30 | 44751.8958 | 0 | 12.7227 | 39.95
2022-07-09 22:00 | 44751.9167 | 0 | 12.3526 | 39.95
2022-07-09 22:30 | 44751.9375 | 0 | 11.4921 | 39.95
2022-07-09 23:00 | 44751.9583 | 0 | 10.9428 | 39.95
2022-07-09 23:30 | 44751.9792 | 0 | 10.2343 | 39.95
2022-07-10 | 44752 | 0 | 9.7138 | 39.95
2022-07-10 00:30 | 44752.0208 | 0 | 9.1431 | 39.95
2022-07-10 01:00 | 44752.0417 | 0 | 8.826 | 39.95
2022-07-10 01:30 | 44752.0625 | 0 | 8.6232 | 39.95
2022-07-10 02:00 | 44752.0833 | 0 | 8.5334 | 39.95
2022-07-10 02:30 | 44752.1042 | 0 | 8.3533 | 39.95
2022-07-10 03:00 | 44752.125 | 0 | 8.1858 | 39.95
2022-07-10 03:30 | 44752.1458 | 0 | 8.172 | 39.95
2022-07-10 04:00 | 44752.1667 | 0 | 8.1755 | 39.95
2022-07-10 04:30 | 44752.1875 | 0 | 8.1658 | 39.95
2022-07-10 05:00 | 44752.2083 | 0 | 8.4217 | 39.95
2022-07-10 05:30 | 44752.2292 | 0 | 8.6611 | 39.95
2022-07-10 06:00 | 44752.25 | 0 | 9.1789 | 39.95
2022-07-10 06:30 | 44752.2708 | 0 | 9.9648 | 39.95
2022-07-10 07:00 | 44752.2917 | 0 | 10.5973 | 39.95
2022-07-10 07:30 | 44752.3125 | 0 | 11.1052 | 39.95
2022-07-10 08:00 | 44752.3333 | 0 | 11.1397 | 39.95
2022-07-10 08:30 | 44752.3542 | 0 | 10.3401 | 39.95
2022-07-10 09:00 | 44752.375 | 0 | 9.9179 | 39.95
2022-07-10 09:30 | 44752.3958 | 0 | 9.1196 | 39.95
2022-07-10 10:00 | 44752.4167 | 0 | 8.356 | 39.95
2022-07-10 10:30 | 44752.4375 | 0 | 7.71 | 39.95
2022-07-10 11:00 | 44752.4583 | 0 | 7.0795 | 39.95
2022-07-10 11:30 | 44752.4792 | 0 | 6.6619 | 39.95
2022-07-10 12:00 | 44752.5 | 0 | 6.2924 | 39.95
2022-07-10 12:30 | 44752.5208 | 0 | 6.1081 | 39.95
2022-07-10 13:00 | 44752.5417 | 0 | 6.8174 | 39.95
2022-07-10 13:30 | 44752.5625 | 0 | 8.5095 | 39.95
2022-07-10 14:00 | 44752.5833 | 0 | 8.4109 | 39.95
2022-07-10 14:30 | 44752.6042 | 0 | 10.0133 | 39.95
2022-07-10 15:00 | 44752.625 | 0 | 9.9859 | 39.95
2022-07-10 15:30 | 44752.6458 | 0 | 10.1943 | 39.95
2022-07-10 16:00 | 44752.6667 | 0 | 11.8646 | 39.95
2022-07-10 16:30 | 44752.6875 | 0 | 12.9475 | 39.95
2022-07-10 17:00 | 44752.7083 | 0 | 13.8365 | 39.95
2022-07-10 17:30 | 44752.7292 | 0 | 14.6129 | 39.95
2022-07-10 18:00 | 44752.75 | 0 | 15.1546 | 39.95
2022-07-10 18:30 | 44752.7708 | 0 | 15.2782 | 39.95
2022-07-10 19:00 | 44752.7917 | 0 | 15.0344 | 39.95
2022-07-10 19:30 | 44752.8125 | 0 | 14.7909 | 39.95
2022-07-10 20:00 | 44752.8333 | 0 | 14.3462 | 39.95
2022-07-10 20:30 | 44752.8542 | 0 | 13.7469 | 39.95
2022-07-10 21:00 | 44752.875 | 0 | 13.1191 | 39.95
2022-07-10 21:30 | 44752.8958 | 0 | 12.3314 | 39.95
2022-07-10 22:00 | 44752.9167 | 0 | 11.3589 | 39.95
2022-07-10 22:30 | 44752.9375 | 0 | 10.5489 | 39.95
2022-07-10 23:00 | 44752.9583 | 0 | 10.0058 | 39.95
2022-07-10 23:30 | 44752.9792 | 0 | 9.415 | 39.95
2022-07-11 | 44753 | 0 | 9.0669 | 39.95
2022-07-11 00:30 | 44753.0208 | 0 | 8.6495 | 39.95
2022-07-11 01:00 | 44753.0417 | 0 | 8.4215 | 39.95
2022-07-11 01:30 | 44753.0625 | 0 | 8.3203 | 39.95
2022-07-11 02:00 | 44753.0833 | 0 | 8.3604 | 39.95
2022-07-11 02:30 | 44753.1042 | 0 | 8.412 | 39.95
2022-07-11 03:00 | 44753.125 | 0 | 8.2591 | 39.95
2022-07-11 03:30 | 44753.1458 | 0 | 8.4086 | 39.95
2022-07-11 04:00 | 44753.1667 | 0 | 8.7445 | 39.95
2022-07-11 04:30 | 44753.1875 | 0 | 9.2163 | 39.95
2022-07-11 05:00 | 44753.2083 | 0 | 10.257 | 39.95
2022-07-11 05:30 | 44753.2292 | 0 | 11.6211 | 39.95
2022-07-11 06:00 | 44753.25 | 0 | 13.5093 | 39.95
2022-07-11 06:30 | 44753.2708 | 0 | 15.6554 | 39.95
2022-07-11 07:00 | 44753.2917 | 0 | 17.2434 | 39.95
2022-07-11 07:30 | 44753.3125 | 0 | 16.8041 | 39.95
2022-07-11 08:00 | 44753.3333 | 0 | 15.6468 | 39.95
2022-07-11 08:30 | 44753.3542 | 0 | 14.2703 | 39.95
2022-07-11 09:00 | 44753.375 | 0 | 12.706 | 39.95
2022-07-11 09:30 | 44753.3958 | 0 | 11.7778 | 39.95
2022-07-11 10:00 | 44753.4167 | 0 | 10.8449 | 39.95
2022-07-11 10:30 | 44753.4375 | 0 | 10.123 | 39.95
2022-07-11 11:00 | 44753.4583 | 0 | 10.5383 | 39.95
2022-07-11 11:30 | 44753.4792 | 0 | 11.2101 | 39.95
2022-07-11 12:00 | 44753.5 | 0 | 9.7202 | 39.95
2022-07-11 12:30 | 44753.5208 | 0 | 9.6181 | 39.95
2022-07-11 13:00 | 44753.5417 | 0 | 11.1379 | 39.95
2022-07-11 13:30 | 44753.5625 | 0 | 11.5126 | 39.95
2022-07-11 14:00 | 44753.5833 | 0 | 12.9389 | 39.95
2022-07-11 14:30 | 44753.6042 | 0 | 12.1062 | 39.95
2022-07-11 15:00 | 44753.625 | 0 | 12.6366 | 39.95
2022-07-11 15:30 | 44753.6458 | 0 | 13.202 | 39.95
2022-07-11 16:00 | 44753.6667 | 0 | 13.2962 | 39.95
2022-07-11 16:30 | 44753.6875 | 0 | 14.3937 | 39.95
2022-07-11 17:00 | 44753.7083 | 0 | 15.4529 | 39.95
2022-07-11 17:30 | 44753.7292 | 0 | 16.3925 | 39.95
2022-07-11 18:00 | 44753.75 | 0 | 16.8268 | 39.95
2022-07-11 18:30 | 44753.7708 | 0 | 16.6875 | 39.95
2022-07-11 19:00 | 44753.7917 | 0 | 16.3276 | 39.95
2022-07-11 19:30 | 44753.8125 | 0 | 16.1636 | 39.95
2022-07-11 20:00 | 44753.8333 | 0 | 15.7208 | 39.95
2022-07-11 20:30 | 44753.8542 | 0 | 15.0728 | 39.95
2022-07-11 21:00 | 44753.875 | 0 | 13.9698 | 39.95
2022-07-11 21:30 | 44753.8958 | 0 | 13.2416 | 39.95
2022-07-11 22:00 | 44753.9167 | 0 | 12.4165 | 39.95
2022-07-11 22:30 | 44753.9375 | 0 | 11.3248 | 39.95
2022-07-11 23:00 | 44753.9583 | 0 | 10.8229 | 39.95
2022-07-11 23:30 | 44753.9792 | 0 | 10.0124 | 39.95
2022-07-12 | 44754 | 0 | 9.3973 | 39.95
2022-07-12 00:30 | 44754.0208 | 0 | 8.9856 | 39.95
2022-07-12 01:00 | 44754.0417 | 0 | 8.6887 | 39.95
2022-07-12 01:30 | 44754.0625 | 0 | 8.5316 | 39.95
2022-07-12 02:00 | 44754.0833 | 0 | 8.3942 | 39.95
2022-07-12 02:30 | 44754.1042 | 0 | 8.4572 | 39.95
2022-07-12 03:00 | 44754.125 | 0 | 8.3858 | 39.95
2022-07-12 03:30 | 44754.1458 | 0 | 8.5132 | 39.95
2022-07-12 04:00 | 44754.1667 | 0 | 8.7821 | 39.95
2022-07-12 04:30 | 44754.1875 | 0 | 9.3346 | 39.95
2022-07-12 05:00 | 44754.2083 | 0 | 10.304 | 39.95
2022-07-12 05:30 | 44754.2292 | 0 | 11.2191 | 39.95
2022-07-12 06:00 | 44754.25 | 0 | 12.9642 | 39.95
2022-07-12 06:30 | 44754.2708 | 0 | 14.9319 | 39.95
2022-07-12 07:00 | 44754.2917 | 0 | 16.2075 | 39.95
2022-07-12 07:30 | 44754.3125 | 0 | 15.4612 | 39.95
2022-07-12 08:00 | 44754.3333 | 0 | 14.6312 | 39.95
2022-07-12 08:30 | 44754.3542 | 0 | 14.3187 | 39.95
2022-07-12 09:00 | 44754.375 | 0 | 13.7581 | 39.95
2022-07-12 09:30 | 44754.3958 | 0 | 13.2052 | 39.95
2022-07-12 10:00 | 44754.4167 | 0 | 12.1403 | 39.95
2022-07-12 10:30 | 44754.4375 | 0 | 12.1585 | 39.95
2022-07-12 11:00 | 44754.4583 | 0 | 9.0817 | 39.95
2022-07-12 11:30 | 44754.4792 | 0 | 9.5 | 39.95
2022-07-12 12:00 | 44754.5 | 0 | 11.8016 | 39.95
2022-07-12 12:30 | 44754.5208 | 0 | 11.9318 | 39.95
2022-07-12 13:00 | 44754.5417 | 0 | 12.2475 | 39.95
2022-07-12 13:30 | 44754.5625 | 0 | 13.14 | 39.95
2022-07-12 14:00 | 44754.5833 | 0 | 13.0636 | 39.95
2022-07-12 14:30 | 44754.6042 | 0 | 13.5515 | 39.95
2022-07-12 15:00 | 44754.625 | 0 | 13.7304 | 39.95
2022-07-12 15:30 | 44754.6458 | 0 | 14.2897 | 39.95
2022-07-12 16:00 | 44754.6667 | 0 | 14.9713 | 39.95
2022-07-12 16:30 | 44754.6875 | 0 | 15.8869 | 39.95
2022-07-12 17:00 | 44754.7083 | 0 | 17.1071 | 39.95
2022-07-12 17:30 | 44754.7292 | 0 | 18.0578 | 39.95
2022-07-12 18:00 | 44754.75 | 0 | 18.1987 | 39.95
2022-07-12 18:30 | 44754.7708 | 0 | 18.0638 | 39.95
2022-07-12 19:00 | 44754.7917 | 0 | 17.9532 | 39.95
2022-07-12 19:30 | 44754.8125 | 0 | 17.4783 | 39.95
2022-07-12 20:00 | 44754.8333 | 0 | 16.7496 | 39.95
2022-07-12 20:30 | 44754.8542 | 0 | 15.958 | 39.95
2022-07-12 21:00 | 44754.875 | 0 | 14.977 | 39.95
2022-07-12 21:30 | 44754.8958 | 0 | 13.9423 | 39.95
2022-07-12 22:00 | 44754.9167 | 0 | 12.9654 | 39.95
2022-07-12 22:30 | 44754.9375 | 0 | 11.9758 | 39.95
2022-07-12 23:00 | 44754.9583 | 0 | 11.2184 | 39.95
2022-07-12 23:30 | 44754.9792 | 0 | 10.5664 | 39.95
2022-07-13 | 44755 | 0 | 9.8448 | 39.95
2022-07-13 00:30 | 44755.0208 | 0 | 9.4104 | 39.95
2022-07-13 01:00 | 44755.0417 | 0 | 9.245 | 39.95
2022-07-13 01:30 | 44755.0625 | 0 | 8.8998 | 39.95
2022-07-13 02:00 | 44755.0833 | 0 | 8.8047 | 39.95
2022-07-13 02:30 | 44755.1042 | 0 | 8.7526 | 39.95
2022-07-13 03:00 | 44755.125 | 0 | 8.5569 | 39.95
2022-07-13 03:30 | 44755.1458 | 0 | 8.6835 | 39.95
2022-07-13 04:00 | 44755.1667 | 0 | 9.0644 | 39.95
2022-07-13 04:30 | 44755.1875 | 0 | 9.4183 | 39.95
2022-07-13 05:00 | 44755.2083 | 0 | 10.3979 | 39.95
2022-07-13 05:30 | 44755.2292 | 0 | 11.741 | 39.95
2022-07-13 06:00 | 44755.25 | 0 | 13.4291 | 39.95
2022-07-13 06:30 | 44755.2708 | 0 | 15.4871 | 39.95
2022-07-13 07:00 | 44755.2917 | 0 | 16.6529 | 39.95
2022-07-13 07:30 | 44755.3125 | 0 | 16.1369 | 39.95
2022-07-13 08:00 | 44755.3333 | 0 | 15.0167 | 39.95
2022-07-13 08:30 | 44755.3542 | 0 | 13.2967 | 39.95
2022-07-13 09:00 | 44755.375 | 0 | 12.0293 | 39.95
2022-07-13 09:30 | 44755.3958 | 0 | 11.0589 | 39.95
2022-07-13 10:00 | 44755.4167 | 0 | 10.1724 | 39.95
2022-07-13 10:30 | 44755.4375 | 0 | 9.519 | 39.95
2022-07-13 11:00 | 44755.4583 | 0 | 8.8459 | 39.95
2022-07-13 11:30 | 44755.4792 | 0 | 8.5803 | 39.95
2022-07-13 12:00 | 44755.5 | 0 | 8.5828 | 39.95
2022-07-13 12:30 | 44755.5208 | 0 | 8.7536 | 39.95
2022-07-13 13:00 | 44755.5417 | 0 | 8.7272 | 39.95
2022-07-13 13:30 | 44755.5625 | 0 | 9.1954 | 39.95
2022-07-13 14:00 | 44755.5833 | 0 | 9.7281 | 39.95
2022-07-13 14:30 | 44755.6042 | 0 | 11.6248 | 39.95
2022-07-13 15:00 | 44755.625 | 0 | 10.9191 | 39.95
2022-07-13 15:30 | 44755.6458 | 0 | 12.1125 | 39.95
2022-07-13 16:00 | 44755.6667 | 0 | 13.1354 | 39.95
2022-07-13 16:30 | 44755.6875 | 0 | 14.4675 | 39.95
2022-07-13 17:00 | 44755.7083 | 0 | 15.9363 | 39.95
2022-07-13 17:30 | 44755.7292 | 0 | 17.2878 | 39.95
2022-07-13 18:00 | 44755.75 | 0 | 17.8011 | 39.95
2022-07-13 18:30 | 44755.7708 | 0 | 17.9261 | 39.95
2022-07-13 19:00 | 44755.7917 | 0 | 18.0813 | 39.95
2022-07-13 19:30 | 44755.8125 | 0 | 17.8804 | 39.95
2022-07-13 20:00 | 44755.8333 | 0 | 17.5277 | 39.95
2022-07-13 20:30 | 44755.8542 | 0 | 16.4683 | 39.95
2022-07-13 21:00 | 44755.875 | 0 | 15.8273 | 39.95
2022-07-13 21:30 | 44755.8958 | 0 | 14.9827 | 39.95
2022-07-13 22:00 | 44755.9167 | 0 | 14.1413 | 39.95
2022-07-13 22:30 | 44755.9375 | 0 | 12.8305 | 39.95
2022-07-13 23:00 | 44755.9583 | 0 | 11.8318 | 39.95
2022-07-13 23:30 | 44755.9792 | 0 | 10.9736 | 39.95
2022-07-14 | 44756 | 0 | 10.3784 | 39.95
2022-07-14 00:30 | 44756.0208 | 0 | 9.7482 | 39.95
2022-07-14 01:00 | 44756.0417 | 0 | 9.3649 | 39.95
2022-07-14 01:30 | 44756.0625 | 0 | 9.1171 | 39.95
2022-07-14 02:00 | 44756.0833 | 0 | 8.8961 | 39.95
2022-07-14 02:30 | 44756.1042 | 0 | 8.8721 | 39.95
2022-07-14 03:00 | 44756.125 | 0 | 8.7934 | 39.95
2022-07-14 03:30 | 44756.1458 | 0 | 9.0301 | 39.95
2022-07-14 04:00 | 44756.1667 | 0 | 9.3395 | 39.95
2022-07-14 04:30 | 44756.1875 | 0 | 9.9436 | 39.95
2022-07-14 05:00 | 44756.2083 | 0 | 10.807 | 39.95
2022-07-14 05:30 | 44756.2292 | 0 | 11.8264 | 39.95
2022-07-14 06:00 | 44756.25 | 0 | 13.6801 | 39.95
2022-07-14 06:30 | 44756.2708 | 0 | 15.5827 | 39.95
2022-07-14 07:00 | 44756.2917 | 0 | 17.063 | 39.95
2022-07-14 07:30 | 44756.3125 | 0 | 16.8427 | 39.95
2022-07-14 08:00 | 44756.3333 | 0 | 15.5243 | 39.95
2022-07-14 08:30 | 44756.3542 | 0 | 14.05 | 39.95
2022-07-14 09:00 | 44756.375 | 0 | 12.905 | 39.95
2022-07-14 09:30 | 44756.3958 | 0 | 11.6017 | 39.95
2022-07-14 10:00 | 44756.4167 | 0 | 10.8689 | 39.95
2022-07-14 10:30 | 44756.4375 | 0 | 10.1012 | 39.95
2022-07-14 11:00 | 44756.4583 | 0 | 9.6463 | 39.95
2022-07-14 11:30 | 44756.4792 | 0 | 9.2318 | 39.95
2022-07-14 12:00 | 44756.5 | 0 | 8.8848 | 39.95
2022-07-14 12:30 | 44756.5208 | 0 | 8.7179 | 39.95
2022-07-14 13:00 | 44756.5417 | 0 | 8.985 | 39.95
2022-07-14 13:30 | 44756.5625 | 0 | 8.9736 | 39.95
2022-07-14 14:00 | 44756.5833 | 0 | 9.7141 | 39.95
2022-07-14 14:30 | 44756.6042 | 0 | 9.9656 | 39.95
2022-07-14 15:00 | 44756.625 | 0 | 10.6239 | 39.95
2022-07-14 15:30 | 44756.6458 | 0 | 11.5015 | 39.95
2022-07-14 16:00 | 44756.6667 | 0 | 12.3752 | 39.95
2022-07-14 16:30 | 44756.6875 | 0 | 13.5026 | 39.95
2022-07-14 17:00 | 44756.7083 | 0 | 14.8375 | 39.95
2022-07-14 17:30 | 44756.7292 | 0 | 16.1217 | 39.95
2022-07-14 18:00 | 44756.75 | 0 | 16.6166 | 39.95
2022-07-14 18:30 | 44756.7708 | 0 | 16.9281 | 39.95
2022-07-14 19:00 | 44756.7917 | 0 | 16.8604 | 39.95
2022-07-14 19:30 | 44756.8125 | 0 | 16.7406 | 39.95
2022-07-14 20:00 | 44756.8333 | 0 | 16.1652 | 39.95
2022-07-14 20:30 | 44756.8542 | 0 | 15.736 | 39.95
2022-07-14 21:00 | 44756.875 | 0 | 14.9216 | 39.95
2022-07-14 21:30 | 44756.8958 | 0 | 14.0308 | 39.95
2022-07-14 22:00 | 44756.9167 | 0 | 13.2796 | 39.95
2022-07-14 22:30 | 44756.9375 | 0 | 12.2891 | 39.95
2022-07-14 23:00 | 44756.9583 | 0 | 11.6253 | 39.95
2022-07-14 23:30 | 44756.9792 | 0 | 10.9735 | 39.95
2022-07-15 | 44757 | 0 | 10.1379 | 39.95
2022-07-15 00:30 | 44757.0208 | 0 | 9.586 | 39.95
2022-07-15 01:00 | 44757.0417 | 0 | 9.1859 | 39.95
2022-07-15 01:30 | 44757.0625 | 0 | 9.0443 | 39.95
2022-07-15 02:00 | 44757.0833 | 0 | 9.0511 | 39.95
2022-07-15 02:30 | 44757.1042 | 0 | 8.8668 | 39.95
2022-07-15 03:00 | 44757.125 | 0 | 8.9334 | 39.95
2022-07-15 03:30 | 44757.1458 | 0 | 9.0534 | 39.95
2022-07-15 04:00 | 44757.1667 | 0 | 9.4135 | 39.95
2022-07-15 04:30 | 44757.1875 | 0 | 9.7848 | 39.95
2022-07-15 05:00 | 44757.2083 | 0 | 10.747 | 39.95
2022-07-15 05:30 | 44757.2292 | 0 | 11.6842 | 39.95
2022-07-15 06:00 | 44757.25 | 0 | 13.0997 | 39.95
2022-07-15 06:30 | 44757.2708 | 0 | 15.8332 | 39.95
2022-07-15 07:00 | 44757.2917 | 0 | 17.3346 | 39.95
2022-07-15 07:30 | 44757.3125 | 0 | 16.7124 | 39.95
2022-07-15 08:00 | 44757.3333 | 0 | 15.6095 | 39.95
2022-07-15 08:30 | 44757.3542 | 0 | 14.1258 | 39.95
2022-07-15 09:00 | 44757.375 | 0 | 12.8597 | 39.95
2022-07-15 09:30 | 44757.3958 | 0 | 11.6291 | 39.95
2022-07-15 10:00 | 44757.4167 | 0 | 10.0671 | 39.95
2022-07-15 10:30 | 44757.4375 | 0 | 9.5268 | 39.95
2022-07-15 11:00 | 44757.4583 | 0 | 8.8456 | 39.95
2022-07-15 11:30 | 44757.4792 | 0 | 8.4732 | 39.95
2022-07-15 12:00 | 44757.5 | 0 | 8.0534 | 39.95
2022-07-15 12:30 | 44757.5208 | 0 | 8.017 | 39.95
2022-07-15 13:00 | 44757.5417 | 0 | 7.9526 | 39.95
2022-07-15 13:30 | 44757.5625 | 0 | 8.8634 | 39.95
2022-07-15 14:00 | 44757.5833 | 0 | 9.7035 | 39.95
2022-07-15 14:30 | 44757.6042 | 0 | 10.4463 | 39.95
2022-07-15 15:00 | 44757.625 | 0 | 11.0471 | 39.95
2022-07-15 15:30 | 44757.6458 | 0 | 11.1834 | 39.95
2022-07-15 16:00 | 44757.6667 | 0 | 11.6664 | 39.95
2022-07-15 16:30 | 44757.6875 | 0 | 12.4847 | 39.95
2022-07-15 17:00 | 44757.7083 | 0 | 13.5661 | 39.95
2022-07-15 17:30 | 44757.7292 | 0 | 14.6172 | 39.95
2022-07-15 18:00 | 44757.75 | 0 | 15.1196 | 39.95
2022-07-15 18:30 | 44757.7708 | 0 | 15.2602 | 39.95
2022-07-15 19:00 | 44757.7917 | 0 | 15.1634 | 39.95
2022-07-15 19:30 | 44757.8125 | 0 | 15.0076 | 39.95
2022-07-15 20:00 | 44757.8333 | 0 | 14.8427 | 39.95
2022-07-15 20:30 | 44757.8542 | 0 | 14.5956 | 39.95
2022-07-15 21:00 | 44757.875 | 0 | 13.9853 | 39.95
2022-07-15 21:30 | 44757.8958 | 0 | 13.3019 | 39.95
2022-07-15 22:00 | 44757.9167 | 0 | 12.8936 | 39.95
2022-07-15 22:30 | 44757.9375 | 0 | 11.8811 | 39.95
2022-07-15 23:00 | 44757.9583 | 0 | 11.1847 | 39.95
2022-07-15 23:30 | 44757.9792 | 0 | 10.5154 | 39.95
2022-07-16 | 44758 | 0 | 9.9124 | 39.95
2022-07-16 00:30 | 44758.0208 | 0 | 9.1789 | 39.95
2022-07-16 01:00 | 44758.0417 | 0 | 9.1922 | 39.95
2022-07-16 01:30 | 44758.0625 | 0 | 8.9496 | 39.95
2022-07-16 02:00 | 44758.0833 | 0 | 8.8424 | 39.95
2022-07-16 02:30 | 44758.1042 | 0 | 8.6645 | 39.95
2022-07-16 03:00 | 44758.125 | 0 | 8.5836 | 39.95
2022-07-16 03:30 | 44758.1458 | 0 | 8.5237 | 39.95
2022-07-16 04:00 | 44758.1667 | 0 | 8.6435 | 39.95
2022-07-16 04:30 | 44758.1875 | 0 | 8.7696 | 39.95
2022-07-16 05:00 | 44758.2083 | 0 | 9.139 | 39.95
2022-07-16 05:30 | 44758.2292 | 0 | 9.5313 | 39.95
2022-07-16 06:00 | 44758.25 | 0 | 10.3859 | 39.95
2022-07-16 06:30 | 44758.2708 | 0 | 11.1362 | 39.95
2022-07-16 07:00 | 44758.2917 | 0 | 11.9681 | 39.95
2022-07-16 07:30 | 44758.3125 | 0 | 11.872 | 39.95
2022-07-16 08:00 | 44758.3333 | 0 | 11.6025 | 39.95
2022-07-16 08:30 | 44758.3542 | 0 | 10.9179 | 39.95
2022-07-16 09:00 | 44758.375 | 0 | 9.8955 | 39.95
2022-07-16 09:30 | 44758.3958 | 0 | 9.1173 | 39.95
2022-07-16 10:00 | 44758.4167 | 0 | 8.2539 | 39.95
2022-07-16 10:30 | 44758.4375 | 0 | 7.6012 | 39.95
2022-07-16 11:00 | 44758.4583 | 0 | 7.0088 | 39.95
2022-07-16 11:30 | 44758.4792 | 0 | 6.6256 | 39.95
2022-07-16 12:00 | 44758.5 | 0 | 6.4658 | 39.95
2022-07-16 12:30 | 44758.5208 | 0 | 6.2169 | 39.95
2022-07-16 13:00 | 44758.5417 | 0 | 6.2688 | 39.95
2022-07-16 13:30 | 44758.5625 | 0 | 6.6683 | 39.95
2022-07-16 14:00 | 44758.5833 | 0 | 7.8108 | 39.95
2022-07-16 14:30 | 44758.6042 | 0 | 7.6388 | 39.95
2022-07-16 15:00 | 44758.625 | 0 | 8.28 | 39.95
2022-07-16 15:30 | 44758.6458 | 0 | 9.0319 | 39.95
2022-07-16 16:00 | 44758.6667 | 0 | 10.0712 | 39.95
2022-07-16 16:30 | 44758.6875 | 0 | 11.0894 | 39.95
2022-07-16 17:00 | 44758.7083 | 0 | 12.0014 | 39.95
2022-07-16 17:30 | 44758.7292 | 0 | 12.8261 | 39.95
2022-07-16 18:00 | 44758.75 | 0 | 13.1532 | 39.95
2022-07-16 18:30 | 44758.7708 | 0 | 13.3858 | 39.95
2022-07-16 19:00 | 44758.7917 | 0 | 13.2637 | 39.95
2022-07-16 19:30 | 44758.8125 | 0 | 13.0118 | 39.95
2022-07-16 20:00 | 44758.8333 | 0 | 12.7037 | 39.95
2022-07-16 20:30 | 44758.8542 | 0 | 12.2743 | 39.95
2022-07-16 21:00 | 44758.875 | 0 | 11.863 | 39.95
2022-07-16 21:30 | 44758.8958 | 0 | 11.3671 | 39.95
2022-07-16 22:00 | 44758.9167 | 0 | 10.9551 | 39.95
2022-07-16 22:30 | 44758.9375 | 0 | 10.2387 | 39.95
2022-07-16 23:00 | 44758.9583 | 0 | 9.639 | 39.95
2022-07-16 23:30 | 44758.9792 | 0 | 9.1519 | 39.95
2022-07-17 | 44759 | 0 | 8.4548 | 39.95
2022-07-17 00:30 | 44759.0208 | 0 | 8.1279 | 39.95
2022-07-17 01:00 | 44759.0417 | 0 | 7.8967 | 39.95
2022-07-17 01:30 | 44759.0625 | 0 | 7.6401 | 39.95
2022-07-17 02:00 | 44759.0833 | 0 | 7.5262 | 39.95
2022-07-17 02:30 | 44759.1042 | 0 | 7.4515 | 39.95
2022-07-17 03:00 | 44759.125 | 0 | 7.429 | 39.95
2022-07-17 03:30 | 44759.1458 | 0 | 7.4286 | 39.95
2022-07-17 04:00 | 44759.1667 | 0 | 7.3182 | 39.95
2022-07-17 04:30 | 44759.1875 | 0 | 7.3629 | 39.95
2022-07-17 05:00 | 44759.2083 | 0 | 7.5937 | 39.95
2022-07-17 05:30 | 44759.2292 | 0 | 7.8062 | 39.95
2022-07-17 06:00 | 44759.25 | 0 | 8.2579 | 39.95
2022-07-17 06:30 | 44759.2708 | 0 | 8.8476 | 39.95
2022-07-17 07:00 | 44759.2917 | 0 | 9.0894 | 39.95
2022-07-17 07:30 | 44759.3125 | 0 | 8.8487 | 39.95
2022-07-17 08:00 | 44759.3333 | 0 | 9.3145 | 39.95
2022-07-17 08:30 | 44759.3542 | 0 | 8.9593 | 39.95
2022-07-17 09:00 | 44759.375 | 0 | 8.0772 | 39.95
2022-07-17 09:30 | 44759.3958 | 0 | 7.6375 | 39.95
2022-07-17 10:00 | 44759.4167 | 0 | 7.373 | 39.95
2022-07-17 10:30 | 44759.4375 | 0 | 6.9792 | 39.95
2022-07-17 11:00 | 44759.4583 | 0 | 6.7553 | 39.95
2022-07-17 11:30 | 44759.4792 | 0 | 7.058 | 39.95
2022-07-17 12:00 | 44759.5 | 0 | 6.5856 | 39.95
2022-07-17 12:30 | 44759.5208 | 0 | 6.3034 | 39.95
2022-07-17 13:00 | 44759.5417 | 0 | 8.5723 | 39.95
2022-07-17 13:30 | 44759.5625 | 0 | 6.6675 | 39.95
2022-07-17 14:00 | 44759.5833 | 0 | 6.8433 | 39.95
2022-07-17 14:30 | 44759.6042 | 0 | 7.5915 | 39.95
2022-07-17 15:00 | 44759.625 | 0 | 8.0495 | 39.95
2022-07-17 15:30 | 44759.6458 | 0 | 9.586 | 39.95
2022-07-17 16:00 | 44759.6667 | 0 | 10.445 | 39.95
2022-07-17 16:30 | 44759.6875 | 0 | 11.427 | 39.95
2022-07-17 17:00 | 44759.7083 | 0 | 12.3083 | 39.95
2022-07-17 17:30 | 44759.7292 | 0 | 12.9614 | 39.95
2022-07-17 18:00 | 44759.75 | 0 | 13.3773 | 39.95
2022-07-17 18:30 | 44759.7708 | 0 | 13.4093 | 39.95
2022-07-17 19:00 | 44759.7917 | 0 | 13.0769 | 39.95
2022-07-17 19:30 | 44759.8125 | 0 | 12.715 | 39.95
2022-07-17 20:00 | 44759.8333 | 0 | 12.2291 | 39.95
2022-07-17 20:30 | 44759.8542 | 0 | 11.786 | 39.95
2022-07-17 21:00 | 44759.875 | 0 | 11.1575 | 39.95
2022-07-17 21:30 | 44759.8958 | 0 | 10.591 | 39.95
2022-07-17 22:00 | 44759.9167 | 0 | 10.0884 | 39.95
2022-07-17 22:30 | 44759.9375 | 0 | 9.3406 | 39.95
2022-07-17 23:00 | 44759.9583 | 0 | 8.72 | 39.95
2022-07-17 23:30 | 44759.9792 | 0 | 8.302 | 39.95
2022-07-18 | 44760 | 0 | 7.9719 | 39.95
2022-07-18 00:30 | 44760.0208 | 0 | 7.6367 | 39.95
2022-07-18 01:00 | 44760.0417 | 0 | 7.5813 | 39.95
2022-07-18 01:30 | 44760.0625 | 0 | 7.3841 | 39.95
2022-07-18 02:00 | 44760.0833 | 0 | 7.4069 | 39.95
2022-07-18 02:30 | 44760.1042 | 0 | 7.4585 | 39.95
2022-07-18 03:00 | 44760.125 | 0 | 7.259 | 39.95
2022-07-18 03:30 | 44760.1458 | 0 | 7.4683 | 39.95
2022-07-18 04:00 | 44760.1667 | 0 | 7.8904 | 39.95
2022-07-18 04:30 | 44760.1875 | 0 | 8.2725 | 39.95
2022-07-18 05:00 | 44760.2083 | 0 | 8.9773 | 39.95
2022-07-18 05:30 | 44760.2292 | 0 | 9.8373 | 39.95
2022-07-18 06:00 | 44760.25 | 0 | 11.2555 | 39.95
2022-07-18 06:30 | 44760.2708 | 0 | 12.5397 | 39.95
2022-07-18 07:00 | 44760.2917 | 0 | 13.3101 | 39.95
2022-07-18 07:30 | 44760.3125 | 0 | 12.9018 | 39.95
2022-07-18 08:00 | 44760.3333 | 0 | 12.0608 | 39.95
2022-07-18 08:30 | 44760.3542 | 0 | 11.1438 | 39.95
2022-07-18 09:00 | 44760.375 | 0 | 10.1806 | 39.95
2022-07-18 09:30 | 44760.3958 | 0 | 9.4001 | 39.95
2022-07-18 10:00 | 44760.4167 | 0 | 8.9268 | 39.95
2022-07-18 10:30 | 44760.4375 | 0 | 8.6113 | 39.95
2022-07-18 11:00 | 44760.4583 | 0 | 8.1005 | 39.95
2022-07-18 11:30 | 44760.4792 | 0 | 8.0828 | 39.95
2022-07-18 12:00 | 44760.5 | 0 | 7.8672 | 39.95
2022-07-18 12:30 | 44760.5208 | 0 | 8.4008 | 39.95
2022-07-18 13:00 | 44760.5417 | 0 | 9.4046 | 39.95
2022-07-18 13:30 | 44760.5625 | 0 | 8.6364 | 39.95
2022-07-18 14:00 | 44760.5833 | 0 | 9.3092 | 39.95
2022-07-18 14:30 | 44760.6042 | 0 | 10.1256 | 39.95
2022-07-18 15:00 | 44760.625 | 0 | 10.9334 | 39.95
2022-07-18 15:30 | 44760.6458 | 0 | 11.6693 | 39.95
2022-07-18 16:00 | 44760.6667 | 0 | 11.2835 | 39.95
2022-07-18 16:30 | 44760.6875 | 0 | 12.1315 | 39.95
2022-07-18 17:00 | 44760.7083 | 0 | 12.8625 | 39.95
2022-07-18 17:30 | 44760.7292 | 0 | 13.9308 | 39.95
2022-07-18 18:00 | 44760.75 | 0 | 14.2708 | 39.95
2022-07-18 18:30 | 44760.7708 | 0 | 14.5085 | 39.95
2022-07-18 19:00 | 44760.7917 | 0 | 14.3723 | 39.95
2022-07-18 19:30 | 44760.8125 | 0 | 13.7862 | 39.95
2022-07-18 20:00 | 44760.8333 | 0 | 13.6069 | 39.95
2022-07-18 20:30 | 44760.8542 | 0 | 13.1421 | 39.95
2022-07-18 21:00 | 44760.875 | 0 | 12.6803 | 39.95
2022-07-18 21:30 | 44760.8958 | 0 | 11.9669 | 39.95
2022-07-18 22:00 | 44760.9167 | 0 | 11.3263 | 39.95
2022-07-18 22:30 | 44760.9375 | 0 | 10.4508 | 39.95
2022-07-18 23:00 | 44760.9583 | 0 | 9.8743 | 39.95
2022-07-18 23:30 | 44760.9792 | 0 | 9.3912 | 39.95
2022-07-19 | 44761 | 0 | 8.8132 | 39.95
2022-07-19 00:30 | 44761.0208 | 0 | 8.5303 | 39.95
2022-07-19 01:00 | 44761.0417 | 0 | 8.4337 | 39.95
2022-07-19 01:30 | 44761.0625 | 0 | 8.2223 | 39.95
2022-07-19 02:00 | 44761.0833 | 0 | 8.1591 | 39.95
2022-07-19 02:30 | 44761.1042 | 0 | 8.1357 | 39.95
2022-07-19 03:00 | 44761.125 | 0 | 7.9883 | 39.95
2022-07-19 03:30 | 44761.1458 | 0 | 8.219 | 39.95
2022-07-19 04:00 | 44761.1667 | 0 | 8.4136 | 39.95
2022-07-19 04:30 | 44761.1875 | 0 | 8.896 | 39.95
2022-07-19 05:00 | 44761.2083 | 0 | 9.5808 | 39.95
2022-07-19 05:30 | 44761.2292 | 0 | 10.6076 | 39.95
2022-07-19 06:00 | 44761.25 | 0 | 12.0229 | 39.95
2022-07-19 06:30 | 44761.2708 | 0 | 13.8484 | 39.95
2022-07-19 07:00 | 44761.2917 | 0 | 14.6487 | 39.95
2022-07-19 07:30 | 44761.3125 | 0 | 13.7936 | 39.95
2022-07-19 08:00 | 44761.3333 | 0 | 13.1589 | 39.95
2022-07-19 08:30 | 44761.3542 | 0 | 11.8812 | 39.95
2022-07-19 09:00 | 44761.375 | 0 | 10.6851 | 39.95
2022-07-19 09:30 | 44761.3958 | 0 | 9.9125 | 39.95
2022-07-19 10:00 | 44761.4167 | 0 | 9.5809 | 39.95
2022-07-19 10:30 | 44761.4375 | 0 | 9.6831 | 39.95
2022-07-19 11:00 | 44761.4583 | 0 | 9.7999 | 39.95
2022-07-19 11:30 | 44761.4792 | 0 | 7.8421 | 39.95
2022-07-19 12:00 | 44761.5 | 0 | 8.2242 | 39.95
2022-07-19 12:30 | 44761.5208 | 0 | 7.88 | 39.95
2022-07-19 13:00 | 44761.5417 | 0 | 9.2287 | 39.95
2022-07-19 13:30 | 44761.5625 | 0 | 9.9923 | 39.95
2022-07-19 14:00 | 44761.5833 | 0 | 9.9598 | 39.95
2022-07-19 14:30 | 44761.6042 | 0 | 10.6819 | 39.95
2022-07-19 15:00 | 44761.625 | 0 | 10.6267 | 39.95
2022-07-19 15:30 | 44761.6458 | 0 | 11.6947 | 39.95
2022-07-19 16:00 | 44761.6667 | 0 | 12.6714 | 39.95
2022-07-19 16:30 | 44761.6875 | 0 | 13.552 | 39.95
2022-07-19 17:00 | 44761.7083 | 0 | 14.5463 | 39.95
2022-07-19 17:30 | 44761.7292 | 0 | 15.5513 | 39.95
2022-07-19 18:00 | 44761.75 | 0 | 15.6923 | 39.95
2022-07-19 18:30 | 44761.7708 | 0 | 15.8171 | 39.95
2022-07-19 19:00 | 44761.7917 | 0 | 15.4679 | 39.95
2022-07-19 19:30 | 44761.8125 | 0 | 15.3869 | 39.95
2022-07-19 20:00 | 44761.8333 | 0 | 15.0195 | 39.95
2022-07-19 20:30 | 44761.8542 | 0 | 14.39 | 39.95
2022-07-19 21:00 | 44761.875 | 0 | 13.5853 | 39.95
2022-07-19 21:30 | 44761.8958 | 0 | 12.9882 | 39.95
2022-07-19 22:00 | 44761.9167 | 0 | 12.1675 | 39.95
2022-07-19 22:30 | 44761.9375 | 0 | 11.3764 | 39.95
2022-07-19 23:00 | 44761.9583 | 0 | 10.6929 | 39.95
2022-07-19 23:30 | 44761.9792 | 0 | 10.0531 | 39.95
2022-07-20 | 44762 | 0 | 9.37 | 39.95
2022-07-20 00:30 | 44762.0208 | 0 | 8.9618 | 39.95
2022-07-20 01:00 | 44762.0417 | 0 | 8.7342 | 39.95
2022-07-20 01:30 | 44762.0625 | 0 | 8.4121 | 39.95
2022-07-20 02:00 | 44762.0833 | 0 | 8.4151 | 39.95
2022-07-20 02:30 | 44762.1042 | 0 | 8.3377 | 39.95
2022-07-20 03:00 | 44762.125 | 0 | 8.3893 | 39.95
2022-07-20 03:30 | 44762.1458 | 0 | 8.3824 | 39.95
2022-07-20 04:00 | 44762.1667 | 0 | 8.6124 | 39.95
2022-07-20 04:30 | 44762.1875 | 0 | 9.1688 | 39.95
2022-07-20 05:00 | 44762.2083 | 0 | 9.8409 | 39.95
2022-07-20 05:30 | 44762.2292 | 0 | 10.7979 | 39.95
2022-07-20 06:00 | 44762.25 | 0 | 12.0118 | 39.95
2022-07-20 06:30 | 44762.2708 | 0 | 13.5047 | 39.95
2022-07-20 07:00 | 44762.2917 | 0 | 14.6289 | 39.95
2022-07-20 07:30 | 44762.3125 | 0 | 14.3859 | 39.95
2022-07-20 08:00 | 44762.3333 | 0 | 13.8545 | 39.95
2022-07-20 08:30 | 44762.3542 | 0 | 13.0053 | 39.95
2022-07-20 09:00 | 44762.375 | 0 | 13.2312 | 39.95
2022-07-20 09:30 | 44762.3958 | 0 | 12.2273 | 39.95
2022-07-20 10:00 | 44762.4167 | 0 | 11.2682 | 39.95
2022-07-20 10:30 | 44762.4375 | 0 | 9.1696 | 39.95
2022-07-20 11:00 | 44762.4583 | 0 | 11.1791 | 39.95
2022-07-20 11:30 | 44762.4792 | 0 | 10.4954 | 39.95
2022-07-20 12:00 | 44762.5 | 0 | 11.0376 | 39.95
2022-07-20 12:30 | 44762.5208 | 0 | 11.568 | 39.95
2022-07-20 13:00 | 44762.5417 | 0 | 11.2247 | 39.95
2022-07-20 13:30 | 44762.5625 | 0 | 12.1324 | 39.95
2022-07-20 14:00 | 44762.5833 | 0 | 12.4058 | 39.95
2022-07-20 14:30 | 44762.6042 | 0 | 12.0301 | 39.95
2022-07-20 15:00 | 44762.625 | 0 | 13.0349 | 39.95
2022-07-20 15:30 | 44762.6458 | 0 | 13.1461 | 39.95
2022-07-20 16:00 | 44762.6667 | 0 | 13.2107 | 39.95
2022-07-20 16:30 | 44762.6875 | 0 | 14.4053 | 39.95
2022-07-20 17:00 | 44762.7083 | 0 | 15.1558 | 39.95
2022-07-20 17:30 | 44762.7292 | 0 | 16.2014 | 39.95
2022-07-20 18:00 | 44762.75 | 0 | 16.7494 | 39.95
2022-07-20 18:30 | 44762.7708 | 0 | 16.928 | 39.95
2022-07-20 19:00 | 44762.7917 | 0 | 16.5364 | 39.95
2022-07-20 19:30 | 44762.8125 | 0 | 16.1981 | 39.95
2022-07-20 20:00 | 44762.8333 | 0 | 15.805 | 39.95
2022-07-20 20:30 | 44762.8542 | 0 | 15.0062 | 39.95
2022-07-20 21:00 | 44762.875 | 0 | 14.3205 | 39.95
2022-07-20 21:30 | 44762.8958 | 0 | 13.7127 | 39.95
2022-07-20 22:00 | 44762.9167 | 0 | 12.706 | 39.95
2022-07-20 22:30 | 44762.9375 | 0 | 11.6184 | 39.95
2022-07-20 23:00 | 44762.9583 | 0 | 10.8459 | 39.95
2022-07-20 23:30 | 44762.9792 | 0 | 10.2695 | 39.95
2022-07-21 | 44763 | 0 | 9.6649 | 39.95
2022-07-21 00:30 | 44763.0208 | 0 | 9.1904 | 39.95
2022-07-21 01:00 | 44763.0417 | 0 | 9.0297 | 39.95
2022-07-21 01:30 | 44763.0625 | 0 | 8.7994 | 39.95
2022-07-21 02:00 | 44763.0833 | 0 | 8.7693 | 39.95
2022-07-21 02:30 | 44763.1042 | 0 | 8.6356 | 39.95
2022-07-21 03:00 | 44763.125 | 0 | 8.4493 | 39.95
2022-07-21 03:30 | 44763.1458 | 0 | 8.6054 | 39.95
2022-07-21 04:00 | 44763.1667 | 0 | 8.9324 | 39.95
2022-07-21 04:30 | 44763.1875 | 0 | 9.4559 | 39.95
2022-07-21 05:00 | 44763.2083 | 0 | 10.0871 | 39.95
2022-07-21 05:30 | 44763.2292 | 0 | 10.8922 | 39.95
2022-07-21 06:00 | 44763.25 | 0 | 12.3789 | 39.95
2022-07-21 06:30 | 44763.2708 | 0 | 14.1422 | 39.95
2022-07-21 07:00 | 44763.2917 | 0 | 15.1699 | 39.95
2022-07-21 07:30 | 44763.3125 | 0 | 15.5286 | 39.95
2022-07-21 08:00 | 44763.3333 | 0 | 15.4023 | 39.95
2022-07-21 08:30 | 44763.3542 | 0 | 15.1786 | 39.95
2022-07-21 09:00 | 44763.375 | 0 | 15.0525 | 39.95
2022-07-21 09:30 | 44763.3958 | 0 | 14.1623 | 39.95
2022-07-21 10:00 | 44763.4167 | 0 | 13.7868 | 39.95
2022-07-21 10:30 | 44763.4375 | 0 | 14.678 | 39.95
2022-07-21 11:00 | 44763.4583 | 0 | 13.1722 | 39.95
2022-07-21 11:30 | 44763.4792 | 0 | 12.9404 | 39.95
2022-07-21 12:00 | 44763.5 | 0 | 13.8406 | 39.95
2022-07-21 12:30 | 44763.5208 | 0 | 13.5349 | 39.95
2022-07-21 13:00 | 44763.5417 | 0 | 13.3756 | 39.95
2022-07-21 13:30 | 44763.5625 | 0 | 13.564 | 39.95
2022-07-21 14:00 | 44763.5833 | 0 | 13.2503 | 39.95
2022-07-21 14:30 | 44763.6042 | 0 | 13.3623 | 39.95
2022-07-21 15:00 | 44763.625 | 0 | 13.7894 | 39.95
2022-07-21 15:30 | 44763.6458 | 0 | 14.218 | 39.95
2022-07-21 16:00 | 44763.6667 | 0 | 14.4848 | 39.95
2022-07-21 16:30 | 44763.6875 | 0 | 15.2701 | 39.95
2022-07-21 17:00 | 44763.7083 | 0 | 16.0273 | 39.95
2022-07-21 17:30 | 44763.7292 | 0 | 16.7163 | 39.95
2022-07-21 18:00 | 44763.75 | 0 | 16.9731 | 39.95
2022-07-21 18:30 | 44763.7708 | 0 | 16.7943 | 39.95
2022-07-21 19:00 | 44763.7917 | 0 | 16.5412 | 39.95
2022-07-21 19:30 | 44763.8125 | 0 | 16.1754 | 39.95
2022-07-21 20:00 | 44763.8333 | 0 | 15.5646 | 39.95
2022-07-21 20:30 | 44763.8542 | 0 | 15.0427 | 39.95
2022-07-21 21:00 | 44763.875 | 0 | 14.1601 | 39.95
2022-07-21 21:30 | 44763.8958 | 0 | 13.2999 | 39.95
2022-07-21 22:00 | 44763.9167 | 0 | 12.6512 | 39.95
2022-07-21 22:30 | 44763.9375 | 0 | 11.5531 | 39.95
2022-07-21 23:00 | 44763.9583 | 0 | 10.9063 | 39.95
2022-07-21 23:30 | 44763.9792 | 0 | 10.4496 | 39.95
2022-07-22 | 44764 | 0 | 9.9069 | 39.95
2022-07-22 00:30 | 44764.0208 | 0 | 9.2367 | 39.95
2022-07-22 01:00 | 44764.0417 | 0 | 9.1191 | 39.95
2022-07-22 01:30 | 44764.0625 | 0 | 8.7996 | 39.95
2022-07-22 02:00 | 44764.0833 | 0 | 8.7395 | 39.95
2022-07-22 02:30 | 44764.1042 | 0 | 8.6056 | 39.95
2022-07-22 03:00 | 44764.125 | 0 | 8.5348 | 39.95
2022-07-22 03:30 | 44764.1458 | 0 | 8.6203 | 39.95
2022-07-22 04:00 | 44764.1667 | 0 | 8.7874 | 39.95
2022-07-22 04:30 | 44764.1875 | 0 | 9.379 | 39.95
2022-07-22 05:00 | 44764.2083 | 0 | 10.0848 | 39.95
2022-07-22 05:30 | 44764.2292 | 0 | 10.737 | 39.95
2022-07-22 06:00 | 44764.25 | 0 | 12.0998 | 39.95
2022-07-22 06:30 | 44764.2708 | 0 | 13.2328 | 39.95
2022-07-22 07:00 | 44764.2917 | 0 | 14.4248 | 39.95
2022-07-22 07:30 | 44764.3125 | 0 | 14.9482 | 39.95
2022-07-22 08:00 | 44764.3333 | 0 | 15.3721 | 39.95
2022-07-22 08:30 | 44764.3542 | 0 | 15.3802 | 39.95
2022-07-22 09:00 | 44764.375 | 0 | 15.1298 | 39.95
2022-07-22 09:30 | 44764.3958 | 0 | 15.3053 | 39.95
2022-07-22 10:00 | 44764.4167 | 0 | 14.3573 | 39.95
2022-07-22 10:30 | 44764.4375 | 0 | 14.6022 | 39.95
2022-07-22 11:00 | 44764.4583 | 0 | 14.5694 | 39.95
2022-07-22 11:30 | 44764.4792 | 0 | 14.6314 | 39.95
2022-07-22 12:00 | 44764.5 | 0 | 13.9476 | 39.95
2022-07-22 12:30 | 44764.5208 | 0 | 13.8147 | 39.95
2022-07-22 13:00 | 44764.5417 | 0 | 13.4221 | 39.95
2022-07-22 13:30 | 44764.5625 | 0 | 13.313 | 39.95
2022-07-22 14:00 | 44764.5833 | 0 | 13.2299 | 39.95
2022-07-22 14:30 | 44764.6042 | 0 | 13.2667 | 39.95
2022-07-22 15:00 | 44764.625 | 0 | 13.8033 | 39.95
2022-07-22 15:30 | 44764.6458 | 0 | 14.0596 | 39.95
2022-07-22 16:00 | 44764.6667 | 0 | 14.1664 | 39.95
2022-07-22 16:30 | 44764.6875 | 0 | 14.5395 | 39.95
2022-07-22 17:00 | 44764.7083 | 0 | 15.3488 | 39.95
2022-07-22 17:30 | 44764.7292 | 0 | 16.3099 | 39.95
2022-07-22 18:00 | 44764.75 | 0 | 16.4071 | 39.95
2022-07-22 18:30 | 44764.7708 | 0 | 16.236 | 39.95
2022-07-22 19:00 | 44764.7917 | 0 | 15.8322 | 39.95
2022-07-22 19:30 | 44764.8125 | 0 | 15.5437 | 39.95
2022-07-22 20:00 | 44764.8333 | 0 | 15.2705 | 39.95
2022-07-22 20:30 | 44764.8542 | 0 | 14.6284 | 39.95
2022-07-22 21:00 | 44764.875 | 0 | 14.1591 | 39.95
2022-07-22 21:30 | 44764.8958 | 0 | 13.4727 | 39.95
2022-07-22 22:00 | 44764.9167 | 0 | 12.9213 | 39.95
2022-07-22 22:30 | 44764.9375 | 0 | 11.7963 | 39.95
2022-07-22 23:00 | 44764.9583 | 0 | 11.1592 | 39.95
2022-07-22 23:30 | 44764.9792 | 0 | 10.6245 | 39.95
2022-07-23 | 44765 | 0 | 9.9316 | 39.95
2022-07-23 00:30 | 44765.0208 | 0 | 9.3735 | 39.95
2022-07-23 01:00 | 44765.0417 | 0 | 8.9816 | 39.95
2022-07-23 01:30 | 44765.0625 | 0 | 8.695 | 39.95
2022-07-23 02:00 | 44765.0833 | 0 | 8.6575 | 39.95
2022-07-23 02:30 | 44765.1042 | 0 | 8.5611 | 39.95
2022-07-23 03:00 | 44765.125 | 0 | 8.4271 | 39.95
2022-07-23 03:30 | 44765.1458 | 0 | 8.4043 | 39.95
2022-07-23 04:00 | 44765.1667 | 0 | 8.5609 | 39.95
2022-07-23 04:30 | 44765.1875 | 0 | 8.5013 | 39.95
2022-07-23 05:00 | 44765.2083 | 0 | 8.6646 | 39.95
2022-07-23 05:30 | 44765.2292 | 0 | 8.9478 | 39.95
2022-07-23 06:00 | 44765.25 | 0 | 9.3306 | 39.95
2022-07-23 06:30 | 44765.2708 | 0 | 9.9549 | 39.95
2022-07-23 07:00 | 44765.2917 | 0 | 10.5446 | 39.95
2022-07-23 07:30 | 44765.3125 | 0 | 10.7944 | 39.95
2022-07-23 08:00 | 44765.3333 | 0 | 10.2583 | 39.95
2022-07-23 08:30 | 44765.3542 | 0 | 9.4686 | 39.95
2022-07-23 09:00 | 44765.375 | 0 | 10.1782 | 39.95
2022-07-23 09:30 | 44765.3958 | 0 | 9.544 | 39.95
2022-07-23 10:00 | 44765.4167 | 0 | 9.205 | 39.95
2022-07-23 10:30 | 44765.4375 | 0 | 9.2477 | 39.95
2022-07-23 11:00 | 44765.4583 | 0 | 8.8903 | 39.95
2022-07-23 11:30 | 44765.4792 | 0 | 8.493 | 39.95
2022-07-23 12:00 | 44765.5 | 0 | 8.7623 | 39.95
2022-07-23 12:30 | 44765.5208 | 0 | 8.0902 | 39.95
2022-07-23 13:00 | 44765.5417 | 0 | 8.6832 | 39.95
2022-07-23 13:30 | 44765.5625 | 0 | 8.9272 | 39.95
2022-07-23 14:00 | 44765.5833 | 0 | 9.1049 | 39.95
2022-07-23 14:30 | 44765.6042 | 0 | 9.7339 | 39.95
2022-07-23 15:00 | 44765.625 | 0 | 9.3461 | 39.95
2022-07-23 15:30 | 44765.6458 | 0 | 9.6604 | 39.95
2022-07-23 16:00 | 44765.6667 | 0 | 10.0381 | 39.95
2022-07-23 16:30 | 44765.6875 | 0 | 10.8771 | 39.95
2022-07-23 17:00 | 44765.7083 | 0 | 11.8508 | 39.95
2022-07-23 17:30 | 44765.7292 | 0 | 12.5793 | 39.95
2022-07-23 18:00 | 44765.75 | 0 | 12.938 | 39.95
2022-07-23 18:30 | 44765.7708 | 0 | 12.8786 | 39.95
2022-07-23 19:00 | 44765.7917 | 0 | 12.7076 | 39.95
2022-07-23 19:30 | 44765.8125 | 0 | 12.4764 | 39.95
2022-07-23 20:00 | 44765.8333 | 0 | 12.2307 | 39.95
2022-07-23 20:30 | 44765.8542 | 0 | 11.7803 | 39.95
2022-07-23 21:00 | 44765.875 | 0 | 11.3377 | 39.95
2022-07-23 21:30 | 44765.8958 | 0 | 11.0402 | 39.95
2022-07-23 22:00 | 44765.9167 | 0 | 10.8787 | 39.95
2022-07-23 22:30 | 44765.9375 | 0 | 10.1566 | 39.95
2022-07-23 23:00 | 44765.9583 | 0 | 9.7225 | 39.95
2022-07-23 23:30 | 44765.9792 | 0 | 9.3012 | 39.95
2022-07-24 | 44766 | 0 | 8.6149 | 39.95
2022-07-24 00:30 | 44766.0208 | 0 | 8.308 | 39.95
2022-07-24 01:00 | 44766.0417 | 0 | 8.1078 | 39.95
2022-07-24 01:30 | 44766.0625 | 0 | 8.0099 | 39.95
2022-07-24 02:00 | 44766.0833 | 0 | 7.9729 | 39.95
2022-07-24 02:30 | 44766.1042 | 0 | 7.72 | 39.95
2022-07-24 03:00 | 44766.125 | 0 | 7.6898 | 39.95
2022-07-24 03:30 | 44766.1458 | 0 | 7.7196 | 39.95
2022-07-24 04:00 | 44766.1667 | 0 | 7.4817 | 39.95
2022-07-24 04:30 | 44766.1875 | 0 | 7.5409 | 39.95
2022-07-24 05:00 | 44766.2083 | 0 | 7.5854 | 39.95
2022-07-24 05:30 | 44766.2292 | 0 | 7.8683 | 39.95
2022-07-24 06:00 | 44766.25 | 0 | 8.2701 | 39.95
2022-07-24 06:30 | 44766.2708 | 0 | 8.7986 | 39.95
2022-07-24 07:00 | 44766.2917 | 0 | 9.1748 | 39.95
2022-07-24 07:30 | 44766.3125 | 0 | 8.977 | 39.95
2022-07-24 08:00 | 44766.3333 | 0 | 8.6429 | 39.95
2022-07-24 08:30 | 44766.3542 | 0 | 8.2648 | 39.95
2022-07-24 09:00 | 44766.375 | 0 | 7.8986 | 39.95
2022-07-24 09:30 | 44766.3958 | 0 | 7.3133 | 39.95
2022-07-24 10:00 | 44766.4167 | 0 | 6.5452 | 39.95
2022-07-24 10:30 | 44766.4375 | 0 | 6.176 | 39.95
2022-07-24 11:00 | 44766.4583 | 0 | 5.8067 | 39.95
2022-07-24 11:30 | 44766.4792 | 0 | 5.7173 | 39.95
2022-07-24 12:00 | 44766.5 | 0 | 5.9398 | 39.95
2022-07-24 12:30 | 44766.5208 | 0 | 6.4323 | 39.95
2022-07-24 13:00 | 44766.5417 | 0 | 6.5551 | 39.95
2022-07-24 13:30 | 44766.5625 | 0 | 6.4422 | 39.95
2022-07-24 14:00 | 44766.5833 | 0 | 7.184 | 39.95
2022-07-24 14:30 | 44766.6042 | 0 | 7.7536 | 39.95
2022-07-24 15:00 | 44766.625 | 0 | 8.5369 | 39.95
2022-07-24 15:30 | 44766.6458 | 0 | 9.0131 | 39.95
2022-07-24 16:00 | 44766.6667 | 0 | 9.5874 | 39.95
2022-07-24 16:30 | 44766.6875 | 0 | 10.43 | 39.95
2022-07-24 17:00 | 44766.7083 | 0 | 11.5824 | 39.95
2022-07-24 17:30 | 44766.7292 | 0 | 12.5646 | 39.95
2022-07-24 18:00 | 44766.75 | 0 | 13.0495 | 39.95
2022-07-24 18:30 | 44766.7708 | 0 | 13.0793 | 39.95
2022-07-24 19:00 | 44766.7917 | 0 | 12.7451 | 39.95
2022-07-24 19:30 | 44766.8125 | 0 | 12.5062 | 39.95
2022-07-24 20:00 | 44766.8333 | 0 | 12.1947 | 39.95
2022-07-24 20:30 | 44766.8542 | 0 | 11.7755 | 39.95
2022-07-24 21:00 | 44766.875 | 0 | 11.3527 | 39.95
2022-07-24 21:30 | 44766.8958 | 0 | 10.7596 | 39.95
2022-07-24 22:00 | 44766.9167 | 0 | 10.3569 | 39.95
2022-07-24 22:30 | 44766.9375 | 0 | 9.4279 | 39.95
2022-07-24 23:00 | 44766.9583 | 0 | 8.8832 | 39.95
2022-07-24 23:30 | 44766.9792 | 0 | 8.5016 | 39.95
2022-07-25 | 44767 | 0 | 8.1912 | 39.95
2022-07-25 00:30 | 44767.0208 | 0 | 7.9059 | 39.95
2022-07-25 01:00 | 44767.0417 | 0 | 7.8313 | 39.95
2022-07-25 01:30 | 44767.0625 | 0 | 7.5859 | 39.95
2022-07-25 02:00 | 44767.0833 | 0 | 7.608 | 39.95
2022-07-25 02:30 | 44767.1042 | 0 | 7.6527 | 39.95
2022-07-25 03:00 | 44767.125 | 0 | 7.4741 | 39.95
2022-07-25 03:30 | 44767.1458 | 0 | 7.7043 | 39.95
2022-07-25 04:00 | 44767.1667 | 0 | 8.0022 | 39.95
2022-07-25 04:30 | 44767.1875 | 0 | 8.5971 | 39.95
2022-07-25 05:00 | 44767.2083 | 0 | 9.5317 | 39.95
2022-07-25 05:30 | 44767.2292 | 0 | 10.3761 | 39.95
2022-07-25 06:00 | 44767.25 | 0 | 12.0287 | 39.95
2022-07-25 06:30 | 44767.2708 | 0 | 13.5403 | 39.95
2022-07-25 07:00 | 44767.2917 | 0 | 14.6847 | 39.95
2022-07-25 07:30 | 44767.3125 | 0 | 14.0953 | 39.95
2022-07-25 08:00 | 44767.3333 | 0 | 13.1853 | 39.95
2022-07-25 08:30 | 44767.3542 | 0 | 11.857 | 39.95
2022-07-25 09:00 | 44767.375 | 0 | 10.7168 | 39.95
2022-07-25 09:30 | 44767.3958 | 0 | 9.8738 | 39.95
2022-07-25 10:00 | 44767.4167 | 0 | 9.1494 | 39.95
2022-07-25 10:30 | 44767.4375 | 0 | 8.9311 | 39.95
2022-07-25 11:00 | 44767.4583 | 0 | 9.0843 | 39.95
2022-07-25 11:30 | 44767.4792 | 0 | 7.9429 | 39.95
2022-07-25 12:00 | 44767.5 | 0 | 7.8611 | 39.95
2022-07-25 12:30 | 44767.5208 | 0 | 7.9208 | 39.95
2022-07-25 13:00 | 44767.5417 | 0 | 8.768 | 39.95
2022-07-25 13:30 | 44767.5625 | 0 | 9.9165 | 39.95
2022-07-25 14:00 | 44767.5833 | 0 | 9.8658 | 39.95
2022-07-25 14:30 | 44767.6042 | 0 | 9.2936 | 39.95
2022-07-25 15:00 | 44767.625 | 0 | 9.7625 | 39.95
2022-07-25 15:30 | 44767.6458 | 0 | 10.6903 | 39.95
2022-07-25 16:00 | 44767.6667 | 0 | 11.4988 | 39.95
2022-07-25 16:30 | 44767.6875 | 0 | 12.4062 | 39.95
2022-07-25 17:00 | 44767.7083 | 0 | 13.4732 | 39.95
2022-07-25 17:30 | 44767.7292 | 0 | 14.5283 | 39.95
2022-07-25 18:00 | 44767.75 | 0 | 15.0967 | 39.95
2022-07-25 18:30 | 44767.7708 | 0 | 15.2087 | 39.95
2022-07-25 19:00 | 44767.7917 | 0 | 15.097 | 39.95
2022-07-25 19:30 | 44767.8125 | 0 | 14.7835 | 39.95
2022-07-25 20:00 | 44767.8333 | 0 | 14.3979 | 39.95
2022-07-25 20:30 | 44767.8542 | 0 | 13.7626 | 39.95
2022-07-25 21:00 | 44767.875 | 0 | 13.2012 | 39.95
2022-07-25 21:30 | 44767.8958 | 0 | 12.4273 | 39.95
2022-07-25 22:00 | 44767.9167 | 0 | 11.9767 | 39.95
2022-07-25 22:30 | 44767.9375 | 0 | 11.0488 | 39.95
2022-07-25 23:00 | 44767.9583 | 0 | 10.2743 | 39.95
2022-07-25 23:30 | 44767.9792 | 0 | 9.8093 | 39.95
2022-07-26 | 44768 | 0 | 9.0891 | 39.95
2022-07-26 00:30 | 44768.0208 | 0 | 8.7175 | 39.95
2022-07-26 01:00 | 44768.0417 | 0 | 8.4197 | 39.95
2022-07-26 01:30 | 44768.0625 | 0 | 8.1997 | 39.95
2022-07-26 02:00 | 44768.0833 | 0 | 8.2407 | 39.95
2022-07-26 02:30 | 44768.1042 | 0 | 8.1519 | 39.95
2022-07-26 03:00 | 44768.125 | 0 | 8.1362 | 39.95
2022-07-26 03:30 | 44768.1458 | 0 | 8.263 | 39.95
2022-07-26 04:00 | 44768.1667 | 0 | 8.646 | 39.95
2022-07-26 04:30 | 44768.1875 | 0 | 9.1261 | 39.95
2022-07-26 05:00 | 44768.2083 | 0 | 9.8534 | 39.95
2022-07-26 05:30 | 44768.2292 | 0 | 10.7879 | 39.95
2022-07-26 06:00 | 44768.25 | 0 | 12.1543 | 39.95
2022-07-26 06:30 | 44768.2708 | 0 | 13.779 | 39.95
2022-07-26 07:00 | 44768.2917 | 0 | 14.5461 | 39.95
2022-07-26 07:30 | 44768.3125 | 0 | 13.6618 | 39.95
2022-07-26 08:00 | 44768.3333 | 0 | 13.3394 | 39.95
2022-07-26 08:30 | 44768.3542 | 0 | 11.2139 | 39.95
2022-07-26 09:00 | 44768.375 | 0 | 10.6442 | 39.95
2022-07-26 09:30 | 44768.3958 | 0 | 9.8641 | 39.95
2022-07-26 10:00 | 44768.4167 | 0 | 9.221 | 39.95
2022-07-26 10:30 | 44768.4375 | 0 | 8.82 | 39.95
2022-07-26 11:00 | 44768.4583 | 0 | 8.2408 | 39.95
2022-07-26 11:30 | 44768.4792 | 0 | 8.1887 | 39.95
2022-07-26 12:00 | 44768.5 | 0 | 7.8625 | 39.95
2022-07-26 12:30 | 44768.5208 | 0 | 7.8705 | 39.95
2022-07-26 13:00 | 44768.5417 | 0 | 8.2135 | 39.95
2022-07-26 13:30 | 44768.5625 | 0 | 10.5154 | 39.95
2022-07-26 14:00 | 44768.5833 | 0 | 10.1379 | 39.95
2022-07-26 14:30 | 44768.6042 | 0 | 9.914 | 39.95
2022-07-26 15:00 | 44768.625 | 0 | 10.2285 | 39.95
2022-07-26 15:30 | 44768.6458 | 0 | 11.1464 | 39.95
2022-07-26 16:00 | 44768.6667 | 0 | 12.237 | 39.95
2022-07-26 16:30 | 44768.6875 | 0 | 12.6142 | 39.95
2022-07-26 17:00 | 44768.7083 | 0 | 13.422 | 39.95
2022-07-26 17:30 | 44768.7292 | 0 | 14.3611 | 39.95
2022-07-26 18:00 | 44768.75 | 0 | 14.5387 | 39.95
2022-07-26 18:30 | 44768.7708 | 0 | 14.6724 | 39.95
2022-07-26 19:00 | 44768.7917 | 0 | 14.4794 | 39.95
2022-07-26 19:30 | 44768.8125 | 0 | 13.9018 | 39.95
2022-07-26 20:00 | 44768.8333 | 0 | 13.6384 | 39.95
2022-07-26 20:30 | 44768.8542 | 0 | 13.3434 | 39.95
2022-07-26 21:00 | 44768.875 | 0 | 12.6977 | 39.95
2022-07-26 21:30 | 44768.8958 | 0 | 12.2535 | 39.95
2022-07-26 22:00 | 44768.9167 | 0 | 11.6505 | 39.95
2022-07-26 22:30 | 44768.9375 | 0 | 10.8704 | 39.95
2022-07-26 23:00 | 44768.9583 | 0 | 10.3257 | 39.95
2022-07-26 23:30 | 44768.9792 | 0 | 9.7442 | 39.95
2022-07-27 | 44769 | 0 | 9.0333 | 39.95
2022-07-27 00:30 | 44769.0208 | 0 | 8.6135 | 39.95
2022-07-27 01:00 | 44769.0417 | 0 | 8.4432 | 39.95
2022-07-27 01:30 | 44769.0625 | 0 | 8.2334 | 39.95
2022-07-27 02:00 | 44769.0833 | 0 | 8.2481 | 39.95
2022-07-27 02:30 | 44769.1042 | 0 | 8.1963 | 39.95
2022-07-27 03:00 | 44769.125 | 0 | 8.2851 | 39.95
2022-07-27 03:30 | 44769.1458 | 0 | 8.3227 | 39.95
2022-07-27 04:00 | 44769.1667 | 0 | 8.6386 | 39.95
2022-07-27 04:30 | 44769.1875 | 0 | 9.0148 | 39.95
2022-07-27 05:00 | 44769.2083 | 0 | 9.7337 | 39.95
2022-07-27 05:30 | 44769.2292 | 0 | 10.8382 | 39.95
2022-07-27 06:00 | 44769.25 | 0 | 12.0978 | 39.95
2022-07-27 06:30 | 44769.2708 | 0 | 13.7423 | 39.95
2022-07-27 07:00 | 44769.2917 | 0 | 14.7542 | 39.95
2022-07-27 07:30 | 44769.3125 | 0 | 14.0545 | 39.95
2022-07-27 08:00 | 44769.3333 | 0 | 13.0122 | 39.95
2022-07-27 08:30 | 44769.3542 | 0 | 11.7591 | 39.95
2022-07-27 09:00 | 44769.375 | 0 | 10.7304 | 39.95
2022-07-27 09:30 | 44769.3958 | 0 | 9.8107 | 39.95
2022-07-27 10:00 | 44769.4167 | 0 | 9.258 | 39.95
2022-07-27 10:30 | 44769.4375 | 0 | 8.7175 | 39.95
2022-07-27 11:00 | 44769.4583 | 0 | 8.1916 | 39.95
2022-07-27 11:30 | 44769.4792 | 0 | 7.8561 | 39.95
2022-07-27 12:00 | 44769.5 | 0 | 7.5935 | 39.95
2022-07-27 12:30 | 44769.5208 | 0 | 7.6156 | 39.95
2022-07-27 13:00 | 44769.5417 | 0 | 7.828 | 39.95
2022-07-27 13:30 | 44769.5625 | 0 | 8.3076 | 39.95
2022-07-27 14:00 | 44769.5833 | 0 | 8.8575 | 39.95
2022-07-27 14:30 | 44769.6042 | 0 | 9.3081 | 39.95
2022-07-27 15:00 | 44769.625 | 0 | 9.8929 | 39.95
2022-07-27 15:30 | 44769.6458 | 0 | 10.7152 | 39.95
2022-07-27 16:00 | 44769.6667 | 0 | 11.8809 | 39.95
2022-07-27 16:30 | 44769.6875 | 0 | 12.8454 | 39.95
2022-07-27 17:00 | 44769.7083 | 0 | 14.0786 | 39.95
2022-07-27 17:30 | 44769.7292 | 0 | 15.1332 | 39.95
2022-07-27 18:00 | 44769.75 | 0 | 16.0776 | 39.95
2022-07-27 18:30 | 44769.7708 | 0 | 16.3102 | 39.95
2022-07-27 19:00 | 44769.7917 | 0 | 16.2954 | 39.95
2022-07-27 19:30 | 44769.8125 | 0 | 16.0052 | 39.95
2022-07-27 20:00 | 44769.8333 | 0 | 15.7602 | 39.95
2022-07-27 20:30 | 44769.8542 | 0 | 15.1307 | 39.95
2022-07-27 21:00 | 44769.875 | 0 | 14.3757 | 39.95
2022-07-27 21:30 | 44769.8958 | 0 | 13.5231 | 39.95
2022-07-27 22:00 | 44769.9167 | 0 | 12.4932 | 39.95
2022-07-27 22:30 | 44769.9375 | 0 | 11.4194 | 39.95
2022-07-27 23:00 | 44769.9583 | 0 | 10.9086 | 39.95
2022-07-27 23:30 | 44769.9792 | 0 | 10.3247 | 39.95
2022-07-28 | 44770 | 0 | 9.5457 | 39.95
2022-07-28 00:30 | 44770.0208 | 0 | 9.201 | 39.95
2022-07-28 01:00 | 44770.0417 | 0 | 9.0598 | 39.95
2022-07-28 01:30 | 44770.0625 | 0 | 8.6431 | 39.95
2022-07-28 02:00 | 44770.0833 | 0 | 8.5795 | 39.95
2022-07-28 02:30 | 44770.1042 | 0 | 8.5012 | 39.95
2022-07-28 03:00 | 44770.125 | 0 | 8.5606 | 39.95
2022-07-28 03:30 | 44770.1458 | 0 | 8.6206 | 39.95
2022-07-28 04:00 | 44770.1667 | 0 | 9.0184 | 39.95
2022-07-28 04:30 | 44770.1875 | 0 | 9.5057 | 39.95
2022-07-28 05:00 | 44770.2083 | 0 | 10.3084 | 39.95
2022-07-28 05:30 | 44770.2292 | 0 | 11.2875 | 39.95
2022-07-28 06:00 | 44770.25 | 0 | 13.0919 | 39.95
2022-07-28 06:30 | 44770.2708 | 0 | 14.9511 | 39.95
2022-07-28 07:00 | 44770.2917 | 0 | 16.4053 | 39.95
2022-07-28 07:30 | 44770.3125 | 0 | 8.1931 | 39.95
2022-07-28 08:00 | 44770.3333 | 0 | 0.022333 | 39.95
2022-07-28 08:30 | 44770.3542 | 0 | 0.022333 | 39.95
2022-07-28 09:00 | 44770.375 | 0 | 0.022333 | 39.95
2022-07-28 09:30 | 44770.3958 | 0 | 0.022333 | 39.95
2022-07-28 10:00 | 44770.4167 | 0 | 0.022333 | 39.95
2022-07-28 10:30 | 44770.4375 | 0 | 0.022333 | 39.95
2022-07-28 11:00 | 44770.4583 | 0 | 0.022333 | 39.95
2022-07-28 11:30 | 44770.4792 | 0 | 0.022333 | 39.95
2022-07-28 12:00 | 44770.5 | 0 | 0.022333 | 39.95
2022-07-28 12:30 | 44770.5208 | 0 | 0.022333 | 39.95
2022-07-28 13:00 | 44770.5417 | 0 | 0.022333 | 39.95
2022-07-28 13:30 | 44770.5625 | 0 | 0.022333 | 39.95
2022-07-28 14:00 | 44770.5833 | 0 | 0.13032 | 39.95
2022-07-28 14:30 | 44770.6042 | 0 | 0.40199 | 39.95
2022-07-28 15:00 | 44770.625 | 0 | 0.40199 | 39.95
2022-07-28 15:30 | 44770.6458 | 0 | 0.40199 | 39.95
2022-07-28 16:00 | 44770.6667 | 0 | 0.40199 | 39.95
2022-07-28 16:30 | 44770.6875 | 0 | 9.8931 | 39.95
2022-07-28 17:00 | 44770.7083 | 0 | 13.3439 | 39.95
2022-07-28 17:30 | 44770.7292 | 0 | 14.3562 | 39.95
2022-07-28 18:00 | 44770.75 | 0 | 14.9159 | 39.95
2022-07-28 18:30 | 44770.7708 | 0 | 15.4614 | 39.95
2022-07-28 19:00 | 44770.7917 | 0 | 15.3767 | 39.95
2022-07-28 19:30 | 44770.8125 | 0 | 15.0338 | 39.95
2022-07-28 20:00 | 44770.8333 | 0 | 14.7933 | 39.95
2022-07-28 20:30 | 44770.8542 | 0 | 14.454 | 39.95
2022-07-28 21:00 | 44770.875 | 0 | 13.7978 | 39.95
2022-07-28 21:30 | 44770.8958 | 0 | 13.0602 | 39.95
2022-07-28 22:00 | 44770.9167 | 0 | 12.3854 | 39.95
2022-07-28 22:30 | 44770.9375 | 0 | 11.4162 | 39.95
2022-07-28 23:00 | 44770.9583 | 0 | 10.7147 | 39.95
2022-07-28 23:30 | 44770.9792 | 0 | 10.1397 | 39.95
2022-07-29 | 44771 | 0 | 9.3907 | 39.95
2022-07-29 00:30 | 44771.0208 | 0 | 8.8605 | 39.95
2022-07-29 01:00 | 44771.0417 | 0 | 8.8275 | 39.95
2022-07-29 01:30 | 44771.0625 | 0 | 8.6911 | 39.95
2022-07-29 02:00 | 44771.0833 | 0 | 8.4759 | 39.95
2022-07-29 02:30 | 44771.1042 | 0 | 8.4897 | 39.95
2022-07-29 03:00 | 44771.125 | 0 | 8.4894 | 39.95
2022-07-29 03:30 | 44771.1458 | 0 | 8.6296 | 39.95
2022-07-29 04:00 | 44771.1667 | 0 | 8.9581 | 39.95
2022-07-29 04:30 | 44771.1875 | 0 | 9.4123 | 39.95
2022-07-29 05:00 | 44771.2083 | 0 | 10.2576 | 39.95
2022-07-29 05:30 | 44771.2292 | 0 | 11.2532 | 39.95
2022-07-29 06:00 | 44771.25 | 0 | 12.8767 | 39.95
2022-07-29 06:30 | 44771.2708 | 0 | 14.694 | 39.95
2022-07-29 07:00 | 44771.2917 | 0 | 15.7158 | 39.95
2022-07-29 07:30 | 44771.3125 | 0 | 15.2895 | 39.95
2022-07-29 08:00 | 44771.3333 | 0 | 14.0762 | 39.95
2022-07-29 08:30 | 44771.3542 | 0 | 12.8142 | 39.95
2022-07-29 09:00 | 44771.375 | 0 | 11.7349 | 39.95
2022-07-29 09:30 | 44771.3958 | 0 | 10.5152 | 39.95
2022-07-29 10:00 | 44771.4167 | 0 | 9.5158 | 39.95
2022-07-29 10:30 | 44771.4375 | 0 | 8.8136 | 39.95
2022-07-29 11:00 | 44771.4583 | 0 | 8.5442 | 39.95
2022-07-29 11:30 | 44771.4792 | 0 | 8.1757 | 39.95
2022-07-29 12:00 | 44771.5 | 0 | 7.8462 | 39.95
2022-07-29 12:30 | 44771.5208 | 0 | 7.7614 | 39.95
2022-07-29 13:00 | 44771.5417 | 0 | 7.73 | 39.95
2022-07-29 13:30 | 44771.5625 | 0 | 7.9548 | 39.95
2022-07-29 14:00 | 44771.5833 | 0 | 8.4555 | 39.95
2022-07-29 14:30 | 44771.6042 | 0 | 8.8911 | 39.95
2022-07-29 15:00 | 44771.625 | 0 | 9.6228 | 39.95
2022-07-29 15:30 | 44771.6458 | 0 | 10.4164 | 39.95
2022-07-29 16:00 | 44771.6667 | 0 | 11.1646 | 39.95
2022-07-29 16:30 | 44771.6875 | 0 | 12.3082 | 39.95
2022-07-29 17:00 | 44771.7083 | 0 | 13.0948 | 39.95
2022-07-29 17:30 | 44771.7292 | 0 | 14.0179 | 39.95
2022-07-29 18:00 | 44771.75 | 0 | 14.3897 | 39.95
2022-07-29 18:30 | 44771.7708 | 0 | 14.3851 | 39.95
2022-07-29 19:00 | 44771.7917 | 0 | 14.5854 | 39.95
2022-07-29 19:30 | 44771.8125 | 0 | 14.6222 | 39.95
2022-07-29 20:00 | 44771.8333 | 0 | 14.342 | 39.95
2022-07-29 20:30 | 44771.8542 | 0 | 13.9975 | 39.95
2022-07-29 21:00 | 44771.875 | 0 | 13.4807 | 39.95
2022-07-29 21:30 | 44771.8958 | 0 | 12.9068 | 39.95
2022-07-29 22:00 | 44771.9167 | 0 | 12.2298 | 39.95
2022-07-29 22:30 | 44771.9375 | 0 | 11.4927 | 39.95
2022-07-29 23:00 | 44771.9583 | 0 | 10.8547 | 39.95
2022-07-29 23:30 | 44771.9792 | 0 | 10.3819 | 39.95
2022-07-30 | 44772 | 0 | 9.6498 | 39.95
2022-07-30 00:30 | 44772.0208 | 0 | 8.9987 | 39.95
2022-07-30 01:00 | 44772.0417 | 0 | 8.7268 | 39.95
2022-07-30 01:30 | 44772.0625 | 0 | 8.4776 | 39.95
2022-07-30 02:00 | 44772.0833 | 0 | 8.3885 | 39.95
2022-07-30 02:30 | 44772.1042 | 0 | 8.3239 | 39.95
2022-07-30 03:00 | 44772.125 | 0 | 8.2195 | 39.95
2022-07-30 03:30 | 44772.1458 | 0 | 8.2703 | 39.95
2022-07-30 04:00 | 44772.1667 | 0 | 8.4234 | 39.95
2022-07-30 04:30 | 44772.1875 | 0 | 8.392 | 39.95
2022-07-30 05:00 | 44772.2083 | 0 | 8.6421 | 39.95
2022-07-30 05:30 | 44772.2292 | 0 | 9.0566 | 39.95
2022-07-30 06:00 | 44772.25 | 0 | 9.6 | 39.95
2022-07-30 06:30 | 44772.2708 | 0 | 10.3263 | 39.95
2022-07-30 07:00 | 44772.2917 | 0 | 10.8712 | 39.95
2022-07-30 07:30 | 44772.3125 | 0 | 10.7617 | 39.95
2022-07-30 08:00 | 44772.3333 | 0 | 10.8696 | 39.95
2022-07-30 08:30 | 44772.3542 | 0 | 9.9959 | 39.95
2022-07-30 09:00 | 44772.375 | 0 | 8.8963 | 39.95
2022-07-30 09:30 | 44772.3958 | 0 | 8.035 | 39.95
2022-07-30 10:00 | 44772.4167 | 0 | 7.2207 | 39.95
2022-07-30 10:30 | 44772.4375 | 0 | 6.5959 | 39.95
2022-07-30 11:00 | 44772.4583 | 0 | 6.2261 | 39.95
2022-07-30 11:30 | 44772.4792 | 0 | 5.9805 | 39.95
2022-07-30 12:00 | 44772.5 | 0 | 6.5022 | 39.95
2022-07-30 12:30 | 44772.5208 | 0 | 6.0008 | 39.95
2022-07-30 13:00 | 44772.5417 | 0 | 5.878 | 39.95
2022-07-30 13:30 | 44772.5625 | 0 | 5.9775 | 39.95
2022-07-30 14:00 | 44772.5833 | 0 | 8.3262 | 39.95
2022-07-30 14:30 | 44772.6042 | 0 | 7.3483 | 39.95
2022-07-30 15:00 | 44772.625 | 0 | 7.8201 | 39.95
2022-07-30 15:30 | 44772.6458 | 0 | 8.7741 | 39.95
2022-07-30 16:00 | 44772.6667 | 0 | 9.7078 | 39.95
2022-07-30 16:30 | 44772.6875 | 0 | 10.815 | 39.95
2022-07-30 17:00 | 44772.7083 | 0 | 12.0123 | 39.95
2022-07-30 17:30 | 44772.7292 | 0 | 12.762 | 39.95
2022-07-30 18:00 | 44772.75 | 0 | 13.124 | 39.95
2022-07-30 18:30 | 44772.7708 | 0 | 13.139 | 39.95
2022-07-30 19:00 | 44772.7917 | 0 | 13.0169 | 39.95
2022-07-30 19:30 | 44772.8125 | 0 | 12.7721 | 39.95
2022-07-30 20:00 | 44772.8333 | 0 | 12.7694 | 39.95
2022-07-30 20:30 | 44772.8542 | 0 | 12.204 | 39.95
2022-07-30 21:00 | 44772.875 | 0 | 11.7494 | 39.95
2022-07-30 21:30 | 44772.8958 | 0 | 11.2241 | 39.95
2022-07-30 22:00 | 44772.9167 | 0 | 10.7196 | 39.95
2022-07-30 22:30 | 44772.9375 | 0 | 10.0979 | 39.95
2022-07-30 23:00 | 44772.9583 | 0 | 9.6236 | 39.95
2022-07-30 23:30 | 44772.9792 | 0 | 9.039 | 39.95
2022-07-31 | 44773 | 0 | 8.5048 | 39.95
2022-07-31 00:30 | 44773.0208 | 0 | 8.1628 | 39.95
2022-07-31 01:00 | 44773.0417 | 0 | 7.9408 | 39.95
2022-07-31 01:30 | 44773.0625 | 0 | 7.7214 | 39.95
2022-07-31 02:00 | 44773.0833 | 0 | 7.6682 | 39.95
2022-07-31 02:30 | 44773.1042 | 0 | 7.4553 | 39.95
2022-07-31 03:00 | 44773.125 | 0 | 7.49 | 39.95
2022-07-31 03:30 | 44773.1458 | 0 | 7.4112 | 39.95
2022-07-31 04:00 | 44773.1667 | 0 | 7.4506 | 39.95
2022-07-31 04:30 | 44773.1875 | 0 | 7.4644 | 39.95
2022-07-31 05:00 | 44773.2083 | 0 | 7.6439 | 39.95
2022-07-31 05:30 | 44773.2292 | 0 | 7.7024 | 39.95
2022-07-31 06:00 | 44773.25 | 0 | 8.2287 | 39.95
2022-07-31 06:30 | 44773.2708 | 0 | 8.8095 | 39.95
2022-07-31 07:00 | 44773.2917 | 0 | 9.4059 | 39.95
2022-07-31 07:30 | 44773.3125 | 0 | 9.6473 | 39.95
2022-07-31 08:00 | 44773.3333 | 0 | 9.8923 | 39.95
2022-07-31 08:30 | 44773.3542 | 0 | 9.5191 | 39.95
2022-07-31 09:00 | 44773.375 | 0 | 7.7198 | 39.95
2022-07-31 09:30 | 44773.3958 | 0 | 9.203 | 39.95
2022-07-31 10:00 | 44773.4167 | 0 | 8.6703 | 39.95
2022-07-31 10:30 | 44773.4375 | 0 | 9.2614 | 39.95
2022-07-31 11:00 | 44773.4583 | 0 | 9.4049 | 39.95
2022-07-31 11:30 | 44773.4792 | 0 | 8.0908 | 39.95
2022-07-31 12:00 | 44773.5 | 0 | 8.7576 | 39.95
2022-07-31 12:30 | 44773.5208 | 0 | 8.2451 | 39.95
2022-07-31 13:00 | 44773.5417 | 0 | 6.5039 | 39.95
2022-07-31 13:30 | 44773.5625 | 0 | 7.0052 | 39.95
2022-07-31 14:00 | 44773.5833 | 0 | 8.0616 | 39.95
2022-07-31 14:30 | 44773.6042 | 0 | 8.4898 | 39.95
2022-07-31 15:00 | 44773.625 | 0 | 9.93 | 39.95
2022-07-31 15:30 | 44773.6458 | 0 | 10.7573 | 39.95
2022-07-31 16:00 | 44773.6667 | 0 | 11.3725 | 39.95
2022-07-31 16:30 | 44773.6875 | 0 | 11.8734 | 39.95
2022-07-31 17:00 | 44773.7083 | 0 | 12.4012 | 39.95
2022-07-31 17:30 | 44773.7292 | 0 | 13.3438 | 39.95
2022-07-31 18:00 | 44773.75 | 0 | 13.7271 | 39.95
2022-07-31 18:30 | 44773.7708 | 0 | 13.6356 | 39.95
2022-07-31 19:00 | 44773.7917 | 0 | 13.3334 | 39.95
2022-07-31 19:30 | 44773.8125 | 0 | 12.976 | 39.95
2022-07-31 20:00 | 44773.8333 | 0 | 12.6739 | 39.95
2022-07-31 20:30 | 44773.8542 | 0 | 12.0243 | 39.95
2022-07-31 21:00 | 44773.875 | 0 | 11.5323 | 39.95
2022-07-31 21:30 | 44773.8958 | 0 | 10.9511 | 39.95
2022-07-31 22:00 | 44773.9167 | 0 | 10.3151 | 39.95
2022-07-31 22:30 | 44773.9375 | 0 | 9.5774 | 39.95
2022-07-31 23:00 | 44773.9583 | 0 | 9.0208 | 39.95
2022-07-31 23:30 | 44773.9792 | 0 | 8.4538 | 39.95
2022-08-01 | 44774 | 0 | 8.0623 | 39.95
2022-08-01 00:30 | 44774.0208 | 0 | 7.8337 | 39.95
2022-08-01 01:00 | 44774.0417 | 0 | 7.7536 | 39.95
2022-08-01 01:30 | 44774.0625 | 0 | 7.5541 | 39.95
2022-08-01 02:00 | 44774.0833 | 0 | 7.5909 | 39.95
2022-08-01 02:30 | 44774.1042 | 0 | 7.6229 | 39.95
2022-08-01 03:00 | 44774.125 | 0 | 7.6428 | 39.95
2022-08-01 03:30 | 44774.1458 | 0 | 7.7928 | 39.95
2022-08-01 04:00 | 44774.1667 | 0 | 8.1819 | 39.95
2022-08-01 04:30 | 44774.1875 | 0 | 8.6979 | 39.95
2022-08-01 05:00 | 44774.2083 | 0 | 9.4062 | 39.95
2022-08-01 05:30 | 44774.2292 | 0 | 10.1497 | 39.95
2022-08-01 06:00 | 44774.25 | 0 | 11.6395 | 39.95
2022-08-01 06:30 | 44774.2708 | 0 | 12.8153 | 39.95
2022-08-01 07:00 | 44774.2917 | 0 | 13.9429 | 39.95
2022-08-01 07:30 | 44774.3125 | 0 | 13.8773 | 39.95
2022-08-01 08:00 | 44774.3333 | 0 | 13.893 | 39.95
2022-08-01 08:30 | 44774.3542 | 0 | 13.3393 | 39.95
2022-08-01 09:00 | 44774.375 | 0 | 13.0076 | 39.95
2022-08-01 09:30 | 44774.3958 | 0 | 12.9696 | 39.95
2022-08-01 10:00 | 44774.4167 | 0 | 12.9789 | 39.95
2022-08-01 10:30 | 44774.4375 | 0 | 12.0673 | 39.95
2022-08-01 11:00 | 44774.4583 | 0 | 12.347 | 39.95
2022-08-01 11:30 | 44774.4792 | 0 | 12.083 | 39.95
2022-08-01 12:00 | 44774.5 | 0 | 12.2364 | 39.95
2022-08-01 12:30 | 44774.5208 | 0 | 11.5688 | 39.95
2022-08-01 13:00 | 44774.5417 | 0 | 10.9083 | 39.95
2022-08-01 13:30 | 44774.5625 | 0 | 10.5271 | 39.95
2022-08-01 14:00 | 44774.5833 | 0 | 11.0952 | 39.95
2022-08-01 14:30 | 44774.6042 | 0 | 10.7645 | 39.95
2022-08-01 15:00 | 44774.625 | 0 | 10.8069 | 39.95
2022-08-01 15:30 | 44774.6458 | 0 | 11.6877 | 39.95
2022-08-01 16:00 | 44774.6667 | 0 | 12.0564 | 39.95
2022-08-01 16:30 | 44774.6875 | 0 | 12.9859 | 39.95
2022-08-01 17:00 | 44774.7083 | 0 | 13.9909 | 39.95
2022-08-01 17:30 | 44774.7292 | 0 | 15.116 | 39.95
2022-08-01 18:00 | 44774.75 | 0 | 15.6999 | 39.95
2022-08-01 18:30 | 44774.7708 | 0 | 15.5904 | 39.95
2022-08-01 19:00 | 44774.7917 | 0 | 15.4809 | 39.95
2022-08-01 19:30 | 44774.8125 | 0 | 15.2576 | 39.95
2022-08-01 20:00 | 44774.8333 | 0 | 15.0094 | 39.95
2022-08-01 20:30 | 44774.8542 | 0 | 14.1142 | 39.95
2022-08-01 21:00 | 44774.875 | 0 | 13.4889 | 39.95
2022-08-01 21:30 | 44774.8958 | 0 | 12.7169 | 39.95
2022-08-01 22:00 | 44774.9167 | 0 | 11.9714 | 39.95
2022-08-01 22:30 | 44774.9375 | 0 | 11.094 | 39.95
2022-08-01 23:00 | 44774.9583 | 0 | 10.5902 | 39.95
2022-08-01 23:30 | 44774.9792 | 0 | 10.0211 | 39.95
2022-08-02 | 44775 | 0 | 9.4207 | 39.95
2022-08-02 00:30 | 44775.0208 | 0 | 9.0346 | 39.95
2022-08-02 01:00 | 44775.0417 | 0 | 8.8586 | 39.95
2022-08-02 01:30 | 44775.0625 | 0 | 8.5513 | 39.95
2022-08-02 02:00 | 44775.0833 | 0 | 8.4098 | 39.95
2022-08-02 02:30 | 44775.1042 | 0 | 8.3907 | 39.95
2022-08-02 03:00 | 44775.125 | 0 | 8.4619 | 39.95
2022-08-02 03:30 | 44775.1458 | 0 | 8.5107 | 39.95
2022-08-02 04:00 | 44775.1667 | 0 | 8.622 | 39.95
2022-08-02 04:30 | 44775.1875 | 0 | 9.0828 | 39.95
2022-08-02 05:00 | 44775.2083 | 0 | 9.9215 | 39.95
2022-08-02 05:30 | 44775.2292 | 0 | 10.7081 | 39.95
2022-08-02 06:00 | 44775.25 | 0 | 12.0112 | 39.95
2022-08-02 06:30 | 44775.2708 | 0 | 13.6133 | 39.95
2022-08-02 07:00 | 44775.2917 | 0 | 14.8086 | 39.95
2022-08-02 07:30 | 44775.3125 | 0 | 14.7451 | 39.95
2022-08-02 08:00 | 44775.3333 | 0 | 14.0986 | 39.95
2022-08-02 08:30 | 44775.3542 | 0 | 12.9271 | 39.95
2022-08-02 09:00 | 44775.375 | 0 | 10.9536 | 39.95
2022-08-02 09:30 | 44775.3958 | 0 | 9.7985 | 39.95
2022-08-02 10:00 | 44775.4167 | 0 | 8.9329 | 39.95
2022-08-02 10:30 | 44775.4375 | 0 | 8.5229 | 39.95
2022-08-02 11:00 | 44775.4583 | 0 | 8.0135 | 39.95
2022-08-02 11:30 | 44775.4792 | 0 | 7.8248 | 39.95
2022-08-02 12:00 | 44775.5 | 0 | 7.5922 | 39.95
2022-08-02 12:30 | 44775.5208 | 0 | 7.6546 | 39.95
2022-08-02 13:00 | 44775.5417 | 0 | 7.9468 | 39.95
2022-08-02 13:30 | 44775.5625 | 0 | 8.3566 | 39.95
2022-08-02 14:00 | 44775.5833 | 0 | 8.9471 | 39.95
2022-08-02 14:30 | 44775.6042 | 0 | 9.4147 | 39.95
2022-08-02 15:00 | 44775.625 | 0 | 10.1686 | 39.95
2022-08-02 15:30 | 44775.6458 | 0 | 10.7506 | 39.95
2022-08-02 16:00 | 44775.6667 | 0 | 11.096 | 39.95
2022-08-02 16:30 | 44775.6875 | 0 | 12.4623 | 39.95
2022-08-02 17:00 | 44775.7083 | 0 | 13.2083 | 39.95
2022-08-02 17:30 | 44775.7292 | 0 | 14.2596 | 39.95
2022-08-02 18:00 | 44775.75 | 0 | 14.7652 | 39.95
2022-08-02 18:30 | 44775.7708 | 0 | 14.8059 | 39.95
2022-08-02 19:00 | 44775.7917 | 0 | 14.1883 | 39.95
2022-08-02 19:30 | 44775.8125 | 0 | 14.0993 | 39.95
2022-08-02 20:00 | 44775.8333 | 0 | 13.6754 | 39.95
2022-08-02 20:30 | 44775.8542 | 0 | 13.2761 | 39.95
2022-08-02 21:00 | 44775.875 | 0 | 12.8371 | 39.95
2022-08-02 21:30 | 44775.8958 | 0 | 12.4711 | 39.95
2022-08-02 22:00 | 44775.9167 | 0 | 11.7614 | 39.95
2022-08-02 22:30 | 44775.9375 | 0 | 10.9251 | 39.95
2022-08-02 23:00 | 44775.9583 | 0 | 10.2094 | 39.95
2022-08-02 23:30 | 44775.9792 | 0 | 9.8983 | 39.95
2022-08-03 | 44776 | 0 | 9.2991 | 39.95
2022-08-03 00:30 | 44776.0208 | 0 | 8.8888 | 39.95
2022-08-03 01:00 | 44776.0417 | 0 | 8.6033 | 39.95
2022-08-03 01:30 | 44776.0625 | 0 | 8.4453 | 39.95
2022-08-03 02:00 | 44776.0833 | 0 | 8.4566 | 39.95
2022-08-03 02:30 | 44776.1042 | 0 | 8.6765 | 39.95
2022-08-03 03:00 | 44776.125 | 0 | 8.4474 | 39.95
2022-08-03 03:30 | 44776.1458 | 0 | 8.348 | 39.95
2022-08-03 04:00 | 44776.1667 | 0 | 8.5946 | 39.95
2022-08-03 04:30 | 44776.1875 | 0 | 8.9739 | 39.95
2022-08-03 05:00 | 44776.2083 | 0 | 9.5383 | 39.95
2022-08-03 05:30 | 44776.2292 | 0 | 10.2229 | 39.95
2022-08-03 06:00 | 44776.25 | 0 | 11.6083 | 39.95
2022-08-03 06:30 | 44776.2708 | 0 | 12.8668 | 39.95
2022-08-03 07:00 | 44776.2917 | 0 | 13.2806 | 39.95
2022-08-03 07:30 | 44776.3125 | 0 | 13.5345 | 39.95
2022-08-03 08:00 | 44776.3333 | 0 | 12.1309 | 39.95
2022-08-03 08:30 | 44776.3542 | 0 | 11.0404 | 39.95
2022-08-03 09:00 | 44776.375 | 0 | 10.9195 | 39.95
2022-08-03 09:30 | 44776.3958 | 0 | 11.1007 | 39.95
2022-08-03 10:00 | 44776.4167 | 0 | 10.0107 | 39.95
2022-08-03 10:30 | 44776.4375 | 0 | 8.6054 | 39.95
2022-08-03 11:00 | 44776.4583 | 0 | 9.072 | 39.95
2022-08-03 11:30 | 44776.4792 | 0 | 8.8548 | 39.95
2022-08-03 12:00 | 44776.5 | 0 | 7.86 | 39.95
2022-08-03 12:30 | 44776.5208 | 0 | 8.4505 | 39.95
2022-08-03 13:00 | 44776.5417 | 0 | 9.1961 | 39.95
2022-08-03 13:30 | 44776.5625 | 0 | 8.5302 | 39.95
2022-08-03 14:00 | 44776.5833 | 0 | 8.9366 | 39.95
2022-08-03 14:30 | 44776.6042 | 0 | 9.1682 | 39.95
2022-08-03 15:00 | 44776.625 | 0 | 9.7753 | 39.95
2022-08-03 15:30 | 44776.6458 | 0 | 10.6088 | 39.95
2022-08-03 16:00 | 44776.6667 | 0 | 11.3962 | 39.95
2022-08-03 16:30 | 44776.6875 | 0 | 12.1453 | 39.95
2022-08-03 17:00 | 44776.7083 | 0 | 13.0066 | 39.95
2022-08-03 17:30 | 44776.7292 | 0 | 13.7663 | 39.95
2022-08-03 18:00 | 44776.75 | 0 | 14.2514 | 39.95
2022-08-03 18:30 | 44776.7708 | 0 | 14.3461 | 39.95
2022-08-03 19:00 | 44776.7917 | 0 | 14.2061 | 39.95
2022-08-03 19:30 | 44776.8125 | 0 | 13.7161 | 39.95
2022-08-03 20:00 | 44776.8333 | 0 | 13.5852 | 39.95
2022-08-03 20:30 | 44776.8542 | 0 | 13.0674 | 39.95
2022-08-03 21:00 | 44776.875 | 0 | 12.5424 | 39.95
2022-08-03 21:30 | 44776.8958 | 0 | 12.1875 | 39.95
2022-08-03 22:00 | 44776.9167 | 0 | 11.5936 | 39.95
2022-08-03 22:30 | 44776.9375 | 0 | 10.7923 | 39.95
2022-08-03 23:00 | 44776.9583 | 0 | 10.1765 | 39.95
2022-08-03 23:30 | 44776.9792 | 0 | 9.7874 | 39.95
2022-08-04 | 44777 | 0 | 9.1955 | 39.95
2022-08-04 00:30 | 44777.0208 | 0 | 8.6716 | 39.95
2022-08-04 01:00 | 44777.0417 | 0 | 8.5865 | 39.95
2022-08-04 01:30 | 44777.0625 | 0 | 8.2447 | 39.95
2022-08-04 02:00 | 44777.0833 | 0 | 8.2578 | 39.95
2022-08-04 02:30 | 44777.1042 | 0 | 8.2397 | 39.95
2022-08-04 03:00 | 44777.125 | 0 | 8.2066 | 39.95
2022-08-04 03:30 | 44777.1458 | 0 | 8.2736 | 39.95
2022-08-04 04:00 | 44777.1667 | 0 | 8.4911 | 39.95
2022-08-04 04:30 | 44777.1875 | 0 | 8.738 | 39.95
2022-08-04 05:00 | 44777.2083 | 0 | 9.5498 | 39.95
2022-08-04 05:30 | 44777.2292 | 0 | 10.2589 | 39.95
2022-08-04 06:00 | 44777.25 | 0 | 11.7097 | 39.95
2022-08-04 06:30 | 44777.2708 | 0 | 12.7338 | 39.95
2022-08-04 07:00 | 44777.2917 | 0 | 13.5955 | 39.95
2022-08-04 07:30 | 44777.3125 | 0 | 13.5014 | 39.95
2022-08-04 08:00 | 44777.3333 | 0 | 12.8419 | 39.95
2022-08-04 08:30 | 44777.3542 | 0 | 11.8754 | 39.95
2022-08-04 09:00 | 44777.375 | 0 | 10.3946 | 39.95
2022-08-04 09:30 | 44777.3958 | 0 | 9.2737 | 39.95
2022-08-04 10:00 | 44777.4167 | 0 | 10.3487 | 39.95
2022-08-04 10:30 | 44777.4375 | 0 | 9.9947 | 39.95
2022-08-04 11:00 | 44777.4583 | 0 | 8.6287 | 39.95
2022-08-04 11:30 | 44777.4792 | 0 | 8.3564 | 39.95
2022-08-04 12:00 | 44777.5 | 0 | 8.0801 | 39.95
2022-08-04 12:30 | 44777.5208 | 0 | 7.7329 | 39.95
2022-08-04 13:00 | 44777.5417 | 0 | 8.0199 | 39.95
2022-08-04 13:30 | 44777.5625 | 0 | 8.3881 | 39.95
2022-08-04 14:00 | 44777.5833 | 0 | 8.8602 | 39.95
2022-08-04 14:30 | 44777.6042 | 0 | 9.1759 | 39.95
2022-08-04 15:00 | 44777.625 | 0 | 9.8994 | 39.95
2022-08-04 15:30 | 44777.6458 | 0 | 10.6113 | 39.95
2022-08-04 16:00 | 44777.6667 | 0 | 11.4857 | 39.95
2022-08-04 16:30 | 44777.6875 | 0 | 12.5027 | 39.95
2022-08-04 17:00 | 44777.7083 | 0 | 13.0898 | 39.95
2022-08-04 17:30 | 44777.7292 | 0 | 13.8808 | 39.95
2022-08-04 18:00 | 44777.75 | 0 | 14.3227 | 39.95
2022-08-04 18:30 | 44777.7708 | 0 | 14.4087 | 39.95
2022-08-04 19:00 | 44777.7917 | 0 | 14.0796 | 39.95
2022-08-04 19:30 | 44777.8125 | 0 | 13.6654 | 39.95
2022-08-04 20:00 | 44777.8333 | 0 | 13.3726 | 39.95
2022-08-04 20:30 | 44777.8542 | 0 | 12.9543 | 39.95
2022-08-04 21:00 | 44777.875 | 0 | 12.4842 | 39.95
2022-08-04 21:30 | 44777.8958 | 0 | 12.0408 | 39.95
2022-08-04 22:00 | 44777.9167 | 0 | 11.4934 | 39.95
2022-08-04 22:30 | 44777.9375 | 0 | 10.98 | 39.95
2022-08-04 23:00 | 44777.9583 | 0 | 10.3155 | 39.95
2022-08-04 23:30 | 44777.9792 | 0 | 9.7917 | 39.95
2022-08-05 | 44778 | 0 | 9.1818 | 39.95
2022-08-05 00:30 | 44778.0208 | 0 | 8.745 | 39.95
2022-08-05 01:00 | 44778.0417 | 0 | 8.6898 | 39.95
2022-08-05 01:30 | 44778.0625 | 0 | 8.4378 | 39.95
2022-08-05 02:00 | 44778.0833 | 0 | 8.297 | 39.95
2022-08-05 02:30 | 44778.1042 | 0 | 8.3025 | 39.95
2022-08-05 03:00 | 44778.125 | 0 | 8.3194 | 39.95
2022-08-05 03:30 | 44778.1458 | 0 | 8.264 | 39.95
2022-08-05 04:00 | 44778.1667 | 0 | 8.6513 | 39.95
2022-08-05 04:30 | 44778.1875 | 0 | 8.8624 | 39.95
2022-08-05 05:00 | 44778.2083 | 0 | 9.6489 | 39.95
2022-08-05 05:30 | 44778.2292 | 0 | 10.5228 | 39.95
2022-08-05 06:00 | 44778.25 | 0 | 11.6126 | 39.95
2022-08-05 06:30 | 44778.2708 | 0 | 12.4186 | 39.95
2022-08-05 07:00 | 44778.2917 | 0 | 12.8285 | 39.95
2022-08-05 07:30 | 44778.3125 | 0 | 12.1636 | 39.95
2022-08-05 08:00 | 44778.3333 | 0 | 11.6134 | 39.95
2022-08-05 08:30 | 44778.3542 | 0 | 10.6676 | 39.95
2022-08-05 09:00 | 44778.375 | 0 | 10.3942 | 39.95
2022-08-05 09:30 | 44778.3958 | 0 | 10.1688 | 39.95
2022-08-05 10:00 | 44778.4167 | 0 | 9.8126 | 39.95
2022-08-05 10:30 | 44778.4375 | 0 | 9.5911 | 39.95
2022-08-05 11:00 | 44778.4583 | 0 | 9.9413 | 39.95
2022-08-05 11:30 | 44778.4792 | 0 | 9.676 | 39.95
2022-08-05 12:00 | 44778.5 | 0 | 8.9441 | 39.95
2022-08-05 12:30 | 44778.5208 | 0 | 10.0961 | 39.95
2022-08-05 13:00 | 44778.5417 | 0 | 11.5627 | 39.95
2022-08-05 13:30 | 44778.5625 | 0 | 12.2795 | 39.95
2022-08-05 14:00 | 44778.5833 | 0 | 12.1277 | 39.95
2022-08-05 14:30 | 44778.6042 | 0 | 12.1503 | 39.95
2022-08-05 15:00 | 44778.625 | 0 | 12.1674 | 39.95
2022-08-05 15:30 | 44778.6458 | 0 | 11.7761 | 39.95
2022-08-05 16:00 | 44778.6667 | 0 | 12.0502 | 39.95
2022-08-05 16:30 | 44778.6875 | 0 | 12.475 | 39.95
2022-08-05 17:00 | 44778.7083 | 0 | 13.0165 | 39.95
2022-08-05 17:30 | 44778.7292 | 0 | 13.3609 | 39.95
2022-08-05 18:00 | 44778.75 | 0 | 13.4528 | 39.95
2022-08-05 18:30 | 44778.7708 | 0 | 13.5109 | 39.95
2022-08-05 19:00 | 44778.7917 | 0 | 13.2826 | 39.95
2022-08-05 19:30 | 44778.8125 | 0 | 12.8749 | 39.95
2022-08-05 20:00 | 44778.8333 | 0 | 12.8901 | 39.95
2022-08-05 20:30 | 44778.8542 | 0 | 12.5159 | 39.95
2022-08-05 21:00 | 44778.875 | 0 | 12.1167 | 39.95
2022-08-05 21:30 | 44778.8958 | 0 | 11.5292 | 39.95
2022-08-05 22:00 | 44778.9167 | 0 | 11.3029 | 39.95
2022-08-05 22:30 | 44778.9375 | 0 | 10.5367 | 39.95
2022-08-05 23:00 | 44778.9583 | 0 | 9.856 | 39.95
2022-08-05 23:30 | 44778.9792 | 0 | 9.4313 | 39.95
2022-08-06 | 44779 | 0 | 8.8305 | 39.95
2022-08-06 00:30 | 44779.0208 | 0 | 8.3774 | 39.95
2022-08-06 01:00 | 44779.0417 | 0 | 8.2114 | 39.95
2022-08-06 01:30 | 44779.0625 | 0 | 7.9953 | 39.95
2022-08-06 02:00 | 44779.0833 | 0 | 7.8709 | 39.95
2022-08-06 02:30 | 44779.1042 | 0 | 7.9586 | 39.95
2022-08-06 03:00 | 44779.125 | 0 | 7.8941 | 39.95
2022-08-06 03:30 | 44779.1458 | 0 | 7.9196 | 39.95
2022-08-06 04:00 | 44779.1667 | 0 | 7.9749 | 39.95
2022-08-06 04:30 | 44779.1875 | 0 | 8.0663 | 39.95
2022-08-06 05:00 | 44779.2083 | 0 | 8.2128 | 39.95
2022-08-06 05:30 | 44779.2292 | 0 | 8.4626 | 39.95
2022-08-06 06:00 | 44779.25 | 0 | 8.8771 | 39.95
2022-08-06 06:30 | 44779.2708 | 0 | 9.2186 | 39.95
2022-08-06 07:00 | 44779.2917 | 0 | 9.9618 | 39.95
2022-08-06 07:30 | 44779.3125 | 0 | 9.7682 | 39.95
2022-08-06 08:00 | 44779.3333 | 0 | 10.4636 | 39.95
2022-08-06 08:30 | 44779.3542 | 0 | 11.0575 | 39.95
2022-08-06 09:00 | 44779.375 | 0 | 10.7776 | 39.95
2022-08-06 09:30 | 44779.3958 | 0 | 10.2402 | 39.95
2022-08-06 10:00 | 44779.4167 | 0 | 9.5935 | 39.95
2022-08-06 10:30 | 44779.4375 | 0 | 10.0109 | 39.95
2022-08-06 11:00 | 44779.4583 | 0 | 9.5792 | 39.95
2022-08-06 11:30 | 44779.4792 | 0 | 9.6523 | 39.95
2022-08-06 12:00 | 44779.5 | 0 | 9.2321 | 39.95
2022-08-06 12:30 | 44779.5208 | 0 | 9.4404 | 39.95
2022-08-06 13:00 | 44779.5417 | 0 | 8.8937 | 39.95
2022-08-06 13:30 | 44779.5625 | 0 | 8.2928 | 39.95
2022-08-06 14:00 | 44779.5833 | 0 | 6.8141 | 39.95
2022-08-06 14:30 | 44779.6042 | 0 | 7.0927 | 39.95
2022-08-06 15:00 | 44779.625 | 0 | 7.8276 | 39.95
2022-08-06 15:30 | 44779.6458 | 0 | 9.484 | 39.95
2022-08-06 16:00 | 44779.6667 | 0 | 10.2351 | 39.95
2022-08-06 16:30 | 44779.6875 | 0 | 10.7596 | 39.95
2022-08-06 17:00 | 44779.7083 | 0 | 11.1171 | 39.95
2022-08-06 17:30 | 44779.7292 | 0 | 11.6229 | 39.95
2022-08-06 18:00 | 44779.75 | 0 | 11.7693 | 39.95
2022-08-06 18:30 | 44779.7708 | 0 | 12.1228 | 39.95
2022-08-06 19:00 | 44779.7917 | 0 | 11.7155 | 39.95
2022-08-06 19:30 | 44779.8125 | 0 | 11.5162 | 39.95
2022-08-06 20:00 | 44779.8333 | 0 | 11.422 | 39.95
2022-08-06 20:30 | 44779.8542 | 0 | 10.7704 | 39.95
2022-08-06 21:00 | 44779.875 | 0 | 10.5293 | 39.95
2022-08-06 21:30 | 44779.8958 | 0 | 10.2049 | 39.95
2022-08-06 22:00 | 44779.9167 | 0 | 9.9575 | 39.95
2022-08-06 22:30 | 44779.9375 | 0 | 9.4619 | 39.95
2022-08-06 23:00 | 44779.9583 | 0 | 9.0701 | 39.95
2022-08-06 23:30 | 44779.9792 | 0 | 8.6005 | 39.95
2022-08-07 | 44780 | 0 | 8.079 | 39.95
2022-08-07 00:30 | 44780.0208 | 0 | 7.7222 | 39.95
2022-08-07 01:00 | 44780.0417 | 0 | 7.6527 | 39.95
2022-08-07 01:30 | 44780.0625 | 0 | 7.3762 | 39.95
2022-08-07 02:00 | 44780.0833 | 0 | 7.3603 | 39.95
2022-08-07 02:30 | 44780.1042 | 0 | 7.2804 | 39.95
2022-08-07 03:00 | 44780.125 | 0 | 7.2912 | 39.95
2022-08-07 03:30 | 44780.1458 | 0 | 7.2292 | 39.95
2022-08-07 04:00 | 44780.1667 | 0 | 7.2719 | 39.95
2022-08-07 04:30 | 44780.1875 | 0 | 7.1861 | 39.95
2022-08-07 05:00 | 44780.2083 | 0 | 7.4416 | 39.95
2022-08-07 05:30 | 44780.2292 | 0 | 7.5609 | 39.95
2022-08-07 06:00 | 44780.25 | 0 | 8.0514 | 39.95
2022-08-07 06:30 | 44780.2708 | 0 | 8.4155 | 39.95
2022-08-07 07:00 | 44780.2917 | 0 | 8.607 | 39.95
2022-08-07 07:30 | 44780.3125 | 0 | 8.2777 | 39.95
2022-08-07 08:00 | 44780.3333 | 0 | 7.9861 | 39.95
2022-08-07 08:30 | 44780.3542 | 0 | 7.3556 | 39.95
2022-08-07 09:00 | 44780.375 | 0 | 6.8308 | 39.95
2022-08-07 09:30 | 44780.3958 | 0 | 6.3131 | 39.95
2022-08-07 10:00 | 44780.4167 | 0 | 5.7758 | 39.95
2022-08-07 10:30 | 44780.4375 | 0 | 5.3095 | 39.95
2022-08-07 11:00 | 44780.4583 | 0 | 4.9287 | 39.95
2022-08-07 11:30 | 44780.4792 | 0 | 4.6497 | 39.95
2022-08-07 12:00 | 44780.5 | 0 | 4.389 | 39.95
2022-08-07 12:30 | 44780.5208 | 0 | 4.3549 | 39.95
2022-08-07 13:00 | 44780.5417 | 0 | 4.7022 | 39.95
2022-08-07 13:30 | 44780.5625 | 0 | 5.1618 | 39.95
2022-08-07 14:00 | 44780.5833 | 0 | 6.9218 | 39.95
2022-08-07 14:30 | 44780.6042 | 0 | 6.2612 | 39.95
2022-08-07 15:00 | 44780.625 | 0 | 7.1411 | 39.95
2022-08-07 15:30 | 44780.6458 | 0 | 7.8803 | 39.95
2022-08-07 16:00 | 44780.6667 | 0 | 8.849 | 39.95
2022-08-07 16:30 | 44780.6875 | 0 | 10.076 | 39.95
2022-08-07 17:00 | 44780.7083 | 0 | 11.0416 | 39.95
2022-08-07 17:30 | 44780.7292 | 0 | 11.9349 | 39.95
2022-08-07 18:00 | 44780.75 | 0 | 12.4919 | 39.95
2022-08-07 18:30 | 44780.7708 | 0 | 12.4811 | 39.95
2022-08-07 19:00 | 44780.7917 | 0 | 12.2663 | 39.95
2022-08-07 19:30 | 44780.8125 | 0 | 11.8779 | 39.95
2022-08-07 20:00 | 44780.8333 | 0 | 11.8176 | 39.95
2022-08-07 20:30 | 44780.8542 | 0 | 11.4435 | 39.95
2022-08-07 21:00 | 44780.875 | 0 | 10.956 | 39.95
2022-08-07 21:30 | 44780.8958 | 0 | 10.4437 | 39.95
2022-08-07 22:00 | 44780.9167 | 0 | 9.9332 | 39.95
2022-08-07 22:30 | 44780.9375 | 0 | 9.306 | 39.95
2022-08-07 23:00 | 44780.9583 | 0 | 8.7875 | 39.95
2022-08-07 23:30 | 44780.9792 | 0 | 8.351 | 39.95
2022-08-08 | 44781 | 0 | 7.885 | 39.95
2022-08-08 00:30 | 44781.0208 | 0 | 7.6421 | 39.95
2022-08-08 01:00 | 44781.0417 | 0 | 7.6505 | 39.95
2022-08-08 01:30 | 44781.0625 | 0 | 7.4829 | 39.95
2022-08-08 02:00 | 44781.0833 | 0 | 7.3592 | 39.95
2022-08-08 02:30 | 44781.1042 | 0 | 7.3974 | 39.95
2022-08-08 03:00 | 44781.125 | 0 | 7.4569 | 39.95
2022-08-08 03:30 | 44781.1458 | 0 | 7.5609 | 39.95
2022-08-08 04:00 | 44781.1667 | 0 | 8.0603 | 39.95
2022-08-08 04:30 | 44781.1875 | 0 | 8.5065 | 39.95
2022-08-08 05:00 | 44781.2083 | 0 | 9.1745 | 39.95
2022-08-08 05:30 | 44781.2292 | 0 | 10.2859 | 39.95
2022-08-08 06:00 | 44781.25 | 0 | 11.7045 | 39.95
2022-08-08 06:30 | 44781.2708 | 0 | 13.281 | 39.95
2022-08-08 07:00 | 44781.2917 | 0 | 13.8088 | 39.95
2022-08-08 07:30 | 44781.3125 | 0 | 13.2285 | 39.95
2022-08-08 08:00 | 44781.3333 | 0 | 12.2629 | 39.95
2022-08-08 08:30 | 44781.3542 | 0 | 10.9042 | 39.95
2022-08-08 09:00 | 44781.375 | 0 | 9.8364 | 39.95
2022-08-08 09:30 | 44781.3958 | 0 | 9.0976 | 39.95
2022-08-08 10:00 | 44781.4167 | 0 | 8.2991 | 39.95
2022-08-08 10:30 | 44781.4375 | 0 | 7.8985 | 39.95
2022-08-08 11:00 | 44781.4583 | 0 | 7.531 | 39.95
2022-08-08 11:30 | 44781.4792 | 0 | 7.2658 | 39.95
2022-08-08 12:00 | 44781.5 | 0 | 7.1283 | 39.95
2022-08-08 12:30 | 44781.5208 | 0 | 7.2095 | 39.95
2022-08-08 13:00 | 44781.5417 | 0 | 7.1325 | 39.95
2022-08-08 13:30 | 44781.5625 | 0 | 7.5961 | 39.95
2022-08-08 14:00 | 44781.5833 | 0 | 8.0722 | 39.95
2022-08-08 14:30 | 44781.6042 | 0 | 8.6675 | 39.95
2022-08-08 15:00 | 44781.625 | 0 | 9.164 | 39.95
2022-08-08 15:30 | 44781.6458 | 0 | 9.8906 | 39.95
2022-08-08 16:00 | 44781.6667 | 0 | 10.8614 | 39.95
2022-08-08 16:30 | 44781.6875 | 0 | 11.8007 | 39.95
2022-08-08 17:00 | 44781.7083 | 0 | 12.7126 | 39.95
2022-08-08 17:30 | 44781.7292 | 0 | 13.7975 | 39.95
2022-08-08 18:00 | 44781.75 | 0 | 14.4149 | 39.95
2022-08-08 18:30 | 44781.7708 | 0 | 14.7553 | 39.95
2022-08-08 19:00 | 44781.7917 | 0 | 14.3736 | 39.95
2022-08-08 19:30 | 44781.8125 | 0 | 14.1845 | 39.95
2022-08-08 20:00 | 44781.8333 | 0 | 14.0594 | 39.95
2022-08-08 20:30 | 44781.8542 | 0 | 13.5953 | 39.95
2022-08-08 21:00 | 44781.875 | 0 | 12.8781 | 39.95
2022-08-08 21:30 | 44781.8958 | 0 | 12.2854 | 39.95
2022-08-08 22:00 | 44781.9167 | 0 | 11.6102 | 39.95
2022-08-08 22:30 | 44781.9375 | 0 | 10.8112 | 39.95
2022-08-08 23:00 | 44781.9583 | 0 | 10.176 | 39.95
2022-08-08 23:30 | 44781.9792 | 0 | 9.5741 | 39.95
2022-08-09 | 44782 | 0 | 8.9259 | 39.95
2022-08-09 00:30 | 44782.0208 | 0 | 8.5133 | 39.95
2022-08-09 01:00 | 44782.0417 | 0 | 8.4673 | 39.95
2022-08-09 01:30 | 44782.0625 | 0 | 8.1284 | 39.95
2022-08-09 02:00 | 44782.0833 | 0 | 8.0404 | 39.95
2022-08-09 02:30 | 44782.1042 | 0 | 8.1033 | 39.95
2022-08-09 03:00 | 44782.125 | 0 | 8.0739 | 39.95
2022-08-09 03:30 | 44782.1458 | 0 | 7.9876 | 39.95
2022-08-09 04:00 | 44782.1667 | 0 | 8.3242 | 39.95
2022-08-09 04:30 | 44782.1875 | 0 | 8.8315 | 39.95
2022-08-09 05:00 | 44782.2083 | 0 | 9.4585 | 39.95
2022-08-09 05:30 | 44782.2292 | 0 | 10.4567 | 39.95
2022-08-09 06:00 | 44782.25 | 0 | 11.9649 | 39.95
2022-08-09 06:30 | 44782.2708 | 0 | 13.3872 | 39.95
2022-08-09 07:00 | 44782.2917 | 0 | 14.0847 | 39.95
2022-08-09 07:30 | 44782.3125 | 0 | 13.2155 | 39.95
2022-08-09 08:00 | 44782.3333 | 0 | 12.382 | 39.95
2022-08-09 08:30 | 44782.3542 | 0 | 11.2491 | 39.95
2022-08-09 09:00 | 44782.375 | 0 | 10.1873 | 39.95
2022-08-09 09:30 | 44782.3958 | 0 | 9.069 | 39.95
2022-08-09 10:00 | 44782.4167 | 0 | 8.4454 | 39.95
2022-08-09 10:30 | 44782.4375 | 0 | 7.907 | 39.95
2022-08-09 11:00 | 44782.4583 | 0 | 7.5861 | 39.95
2022-08-09 11:30 | 44782.4792 | 0 | 7.2971 | 39.95
2022-08-09 12:00 | 44782.5 | 0 | 7.2113 | 39.95
2022-08-09 12:30 | 44782.5208 | 0 | 7.2229 | 39.95
2022-08-09 13:00 | 44782.5417 | 0 | 7.6238 | 39.95
2022-08-09 13:30 | 44782.5625 | 0 | 8.9721 | 39.95
2022-08-09 14:00 | 44782.5833 | 0 | 10.5965 | 39.95
2022-08-09 14:30 | 44782.6042 | 0 | 9.2774 | 39.95
2022-08-09 15:00 | 44782.625 | 0 | 8.8125 | 39.95
2022-08-09 15:30 | 44782.6458 | 0 | 9.816 | 39.95
2022-08-09 16:00 | 44782.6667 | 0 | 10.6047 | 39.95
2022-08-09 16:30 | 44782.6875 | 0 | 11.7571 | 39.95
2022-08-09 17:00 | 44782.7083 | 0 | 12.7412 | 39.95
2022-08-09 17:30 | 44782.7292 | 0 | 13.2229 | 39.95
2022-08-09 18:00 | 44782.75 | 0 | 14.0071 | 39.95
2022-08-09 18:30 | 44782.7708 | 0 | 14.3279 | 39.95
2022-08-09 19:00 | 44782.7917 | 0 | 14.1635 | 39.95
2022-08-09 19:30 | 44782.8125 | 0 | 14.012 | 39.95
2022-08-09 20:00 | 44782.8333 | 0 | 13.6156 | 39.95
2022-08-09 20:30 | 44782.8542 | 0 | 13.199 | 39.95
2022-08-09 21:00 | 44782.875 | 0 | 12.5909 | 39.95
2022-08-09 21:30 | 44782.8958 | 0 | 12.3034 | 39.95
2022-08-09 22:00 | 44782.9167 | 0 | 11.8109 | 39.95
2022-08-09 22:30 | 44782.9375 | 0 | 11.0172 | 39.95
2022-08-09 23:00 | 44782.9583 | 0 | 10.4013 | 39.95
2022-08-09 23:30 | 44782.9792 | 0 | 10.0025 | 39.95
2022-08-10 | 44783 | 0 | 9.3081 | 39.95
2022-08-10 00:30 | 44783.0208 | 0 | 8.9247 | 39.95
2022-08-10 01:00 | 44783.0417 | 0 | 8.5172 | 39.95
2022-08-10 01:30 | 44783.0625 | 0 | 8.4652 | 39.95
2022-08-10 02:00 | 44783.0833 | 0 | 8.3673 | 39.95
2022-08-10 02:30 | 44783.1042 | 0 | 8.3791 | 39.95
2022-08-10 03:00 | 44783.125 | 0 | 8.2685 | 39.95
2022-08-10 03:30 | 44783.1458 | 0 | 8.2905 | 39.95
2022-08-10 04:00 | 44783.1667 | 0 | 8.4895 | 39.95
2022-08-10 04:30 | 44783.1875 | 0 | 8.5066 | 39.95
2022-08-10 05:00 | 44783.2083 | 0 | 8.9929 | 39.95
2022-08-10 05:30 | 44783.2292 | 0 | 9.2694 | 39.95
2022-08-10 06:00 | 44783.25 | 0 | 9.7876 | 39.95
2022-08-10 06:30 | 44783.2708 | 0 | 10.4093 | 39.95
2022-08-10 07:00 | 44783.2917 | 0 | 10.8025 | 39.95
2022-08-10 07:30 | 44783.3125 | 0 | 10.3101 | 39.95
2022-08-10 08:00 | 44783.3333 | 0 | 9.9043 | 39.95
2022-08-10 08:30 | 44783.3542 | 0 | 9.2712 | 39.95
2022-08-10 09:00 | 44783.375 | 0 | 8.4257 | 39.95
2022-08-10 09:30 | 44783.3958 | 0 | 7.5853 | 39.95
2022-08-10 10:00 | 44783.4167 | 0 | 6.8258 | 39.95
2022-08-10 10:30 | 44783.4375 | 0 | 6.2868 | 39.95
2022-08-10 11:00 | 44783.4583 | 0 | 5.8756 | 39.95
2022-08-10 11:30 | 44783.4792 | 0 | 6.0825 | 39.95
2022-08-10 12:00 | 44783.5 | 0 | 6.6006 | 39.95
2022-08-10 12:30 | 44783.5208 | 0 | 6.5059 | 39.95
2022-08-10 13:00 | 44783.5417 | 0 | 7.2821 | 39.95
2022-08-10 13:30 | 44783.5625 | 0 | 6.7345 | 39.95
2022-08-10 14:00 | 44783.5833 | 0 | 8.1794 | 39.95
2022-08-10 14:30 | 44783.6042 | 0 | 8.0286 | 39.95
2022-08-10 15:00 | 44783.625 | 0 | 7.6775 | 39.95
2022-08-10 15:30 | 44783.6458 | 0 | 8.6706 | 39.95
2022-08-10 16:00 | 44783.6667 | 0 | 9.8091 | 39.95
2022-08-10 16:30 | 44783.6875 | 0 | 10.6249 | 39.95
2022-08-10 17:00 | 44783.7083 | 0 | 11.9554 | 39.95
2022-08-10 17:30 | 44783.7292 | 0 | 12.7068 | 39.95
2022-08-10 18:00 | 44783.75 | 0 | 13.2685 | 39.95
2022-08-10 18:30 | 44783.7708 | 0 | 13.5518 | 39.95
2022-08-10 19:00 | 44783.7917 | 0 | 13.0764 | 39.95
2022-08-10 19:30 | 44783.8125 | 0 | 13.1112 | 39.95
2022-08-10 20:00 | 44783.8333 | 0 | 12.6382 | 39.95
2022-08-10 20:30 | 44783.8542 | 0 | 12.3733 | 39.95
2022-08-10 21:00 | 44783.875 | 0 | 11.7829 | 39.95
2022-08-10 21:30 | 44783.8958 | 0 | 11.1171 | 39.95
2022-08-10 22:00 | 44783.9167 | 0 | 10.4773 | 39.95
2022-08-10 22:30 | 44783.9375 | 0 | 9.743 | 39.95
2022-08-10 23:00 | 44783.9583 | 0 | 9.183 | 39.95
2022-08-10 23:30 | 44783.9792 | 0 | 8.9656 | 39.95
2022-08-11 | 44784 | 0 | 8.4248 | 39.95
2022-08-11 00:30 | 44784.0208 | 0 | 8.1567 | 39.95
2022-08-11 01:00 | 44784.0417 | 0 | 7.9307 | 39.95
2022-08-11 01:30 | 44784.0625 | 0 | 7.8515 | 39.95
2022-08-11 02:00 | 44784.0833 | 0 | 7.8952 | 39.95
2022-08-11 02:30 | 44784.1042 | 0 | 7.7621 | 39.95
2022-08-11 03:00 | 44784.125 | 0 | 7.7612 | 39.95
2022-08-11 03:30 | 44784.1458 | 0 | 7.9266 | 39.95
2022-08-11 04:00 | 44784.1667 | 0 | 8.2828 | 39.95
2022-08-11 04:30 | 44784.1875 | 0 | 8.5589 | 39.95
2022-08-11 05:00 | 44784.2083 | 0 | 9.5001 | 39.95
2022-08-11 05:30 | 44784.2292 | 0 | 10.3493 | 39.95
2022-08-11 06:00 | 44784.25 | 0 | 11.8755 | 39.95
2022-08-11 06:30 | 44784.2708 | 0 | 13.2604 | 39.95
2022-08-11 07:00 | 44784.2917 | 0 | 14.009 | 39.95
2022-08-11 07:30 | 44784.3125 | 0 | 13.4419 | 39.95
2022-08-11 08:00 | 44784.3333 | 0 | 12.2992 | 39.95
2022-08-11 08:30 | 44784.3542 | 0 | 10.9603 | 39.95
2022-08-11 09:00 | 44784.375 | 0 | 10.1865 | 39.95
2022-08-11 09:30 | 44784.3958 | 0 | 9.1269 | 39.95
2022-08-11 10:00 | 44784.4167 | 0 | 10.4649 | 39.95
2022-08-11 10:30 | 44784.4375 | 0 | 8.2612 | 39.95
2022-08-11 11:00 | 44784.4583 | 0 | 8.6232 | 39.95
2022-08-11 11:30 | 44784.4792 | 0 | 8.7379 | 39.95
2022-08-11 12:00 | 44784.5 | 0 | 9.9204 | 39.95
2022-08-11 12:30 | 44784.5208 | 0 | 8.1564 | 39.95
2022-08-11 13:00 | 44784.5417 | 0 | 9.8507 | 39.95
2022-08-11 13:30 | 44784.5625 | 0 | 10.7007 | 39.95
2022-08-11 14:00 | 44784.5833 | 0 | 11.4887 | 39.95
2022-08-11 14:30 | 44784.6042 | 0 | 11.3236 | 39.95
2022-08-11 15:00 | 44784.625 | 0 | 11.4894 | 39.95
2022-08-11 15:30 | 44784.6458 | 0 | 11.4123 | 39.95
2022-08-11 16:00 | 44784.6667 | 0 | 11.8929 | 39.95
2022-08-11 16:30 | 44784.6875 | 0 | 12.5658 | 39.95
2022-08-11 17:00 | 44784.7083 | 0 | 13.2164 | 39.95
2022-08-11 17:30 | 44784.7292 | 0 | 14.0717 | 39.95
2022-08-11 18:00 | 44784.75 | 0 | 14.479 | 39.95
2022-08-11 18:30 | 44784.7708 | 0 | 14.51 | 39.95
2022-08-11 19:00 | 44784.7917 | 0 | 14.3319 | 39.95
2022-08-11 19:30 | 44784.8125 | 0 | 14.1827 | 39.95
2022-08-11 20:00 | 44784.8333 | 0 | 14.095 | 39.95
2022-08-11 20:30 | 44784.8542 | 0 | 13.4091 | 39.95
2022-08-11 21:00 | 44784.875 | 0 | 12.6115 | 39.95
2022-08-11 21:30 | 44784.8958 | 0 | 12.2121 | 39.95
2022-08-11 22:00 | 44784.9167 | 0 | 11.4249 | 39.95
2022-08-11 22:30 | 44784.9375 | 0 | 10.7218 | 39.95
2022-08-11 23:00 | 44784.9583 | 0 | 10.1035 | 39.95
2022-08-11 23:30 | 44784.9792 | 0 | 9.5616 | 39.95
2022-08-12 | 44785 | 0 | 9.1199 | 39.95
2022-08-12 00:30 | 44785.0208 | 0 | 8.6219 | 39.95
2022-08-12 01:00 | 44785.0417 | 0 | 8.41 | 39.95
2022-08-12 01:30 | 44785.0625 | 0 | 8.3188 | 39.95
2022-08-12 02:00 | 44785.0833 | 0 | 8.236 | 39.95
2022-08-12 02:30 | 44785.1042 | 0 | 8.0275 | 39.95
2022-08-12 03:00 | 44785.125 | 0 | 8.085 | 39.95
2022-08-12 03:30 | 44785.1458 | 0 | 8.0049 | 39.95
2022-08-12 04:00 | 44785.1667 | 0 | 8.3356 | 39.95
2022-08-12 04:30 | 44785.1875 | 0 | 8.72 | 39.95
2022-08-12 05:00 | 44785.2083 | 0 | 9.1862 | 39.95
2022-08-12 05:30 | 44785.2292 | 0 | 9.9039 | 39.95
2022-08-12 06:00 | 44785.25 | 0 | 11.1923 | 39.95
2022-08-12 06:30 | 44785.2708 | 0 | 12.3888 | 39.95
2022-08-12 07:00 | 44785.2917 | 0 | 13.4262 | 39.95
2022-08-12 07:30 | 44785.3125 | 0 | 13.611 | 39.95
2022-08-12 08:00 | 44785.3333 | 0 | 13.7267 | 39.95
2022-08-12 08:30 | 44785.3542 | 0 | 13.3141 | 39.95
2022-08-12 09:00 | 44785.375 | 0 | 13.4749 | 39.95
2022-08-12 09:30 | 44785.3958 | 0 | 12.9301 | 39.95
2022-08-12 10:00 | 44785.4167 | 0 | 10.9691 | 39.95
2022-08-12 10:30 | 44785.4375 | 0 | 11.1833 | 39.95
2022-08-12 11:00 | 44785.4583 | 0 | 10.3212 | 39.95
2022-08-12 11:30 | 44785.4792 | 0 | 9.1172 | 39.95
2022-08-12 12:00 | 44785.5 | 0 | 9.3851 | 39.95
2022-08-12 12:30 | 44785.5208 | 0 | 10.1307 | 39.95
2022-08-12 13:00 | 44785.5417 | 0 | 11.0139 | 39.95
2022-08-12 13:30 | 44785.5625 | 0 | 9.8534 | 39.95
2022-08-12 14:00 | 44785.5833 | 0 | 10.7858 | 39.95
2022-08-12 14:30 | 44785.6042 | 0 | 11.492 | 39.95
2022-08-12 15:00 | 44785.625 | 0 | 11.5781 | 39.95
2022-08-12 15:30 | 44785.6458 | 0 | 12.0983 | 39.95
2022-08-12 16:00 | 44785.6667 | 0 | 12.224 | 39.95
2022-08-12 16:30 | 44785.6875 | 0 | 12.8888 | 39.95
2022-08-12 17:00 | 44785.7083 | 0 | 13.3616 | 39.95
2022-08-12 17:30 | 44785.7292 | 0 | 13.8942 | 39.95
2022-08-12 18:00 | 44785.75 | 0 | 14.1342 | 39.95
2022-08-12 18:30 | 44785.7708 | 0 | 14.2088 | 39.95
2022-08-12 19:00 | 44785.7917 | 0 | 13.834 | 39.95
2022-08-12 19:30 | 44785.8125 | 0 | 13.5098 | 39.95
2022-08-12 20:00 | 44785.8333 | 0 | 13.3439 | 39.95
2022-08-12 20:30 | 44785.8542 | 0 | 12.9166 | 39.95
2022-08-12 21:00 | 44785.875 | 0 | 12.529 | 39.95
2022-08-12 21:30 | 44785.8958 | 0 | 12.1954 | 39.95
2022-08-12 22:00 | 44785.9167 | 0 | 11.4787 | 39.95
2022-08-12 22:30 | 44785.9375 | 0 | 10.7575 | 39.95
2022-08-12 23:00 | 44785.9583 | 0 | 10.0922 | 39.95
2022-08-12 23:30 | 44785.9792 | 0 | 9.4935 | 39.95
2022-08-13 | 44786 | 0 | 8.8626 | 39.95
2022-08-13 00:30 | 44786.0208 | 0 | 8.3356 | 39.95
2022-08-13 01:00 | 44786.0417 | 0 | 8.2589 | 39.95
2022-08-13 01:30 | 44786.0625 | 0 | 8.0269 | 39.95
2022-08-13 02:00 | 44786.0833 | 0 | 7.9153 | 39.95
2022-08-13 02:30 | 44786.1042 | 0 | 7.8471 | 39.95
2022-08-13 03:00 | 44786.125 | 0 | 7.6074 | 39.95
2022-08-13 03:30 | 44786.1458 | 0 | 7.5806 | 39.95
2022-08-13 04:00 | 44786.1667 | 0 | 7.6901 | 39.95
2022-08-13 04:30 | 44786.1875 | 0 | 7.6363 | 39.95
2022-08-13 05:00 | 44786.2083 | 0 | 7.9658 | 39.95
2022-08-13 05:30 | 44786.2292 | 0 | 8.3006 | 39.95
2022-08-13 06:00 | 44786.25 | 0 | 8.6625 | 39.95
2022-08-13 06:30 | 44786.2708 | 0 | 9.1973 | 39.95
2022-08-13 07:00 | 44786.2917 | 0 | 9.7525 | 39.95
2022-08-13 07:30 | 44786.3125 | 0 | 10.1969 | 39.95
2022-08-13 08:00 | 44786.3333 | 0 | 10.7802 | 39.95
2022-08-13 08:30 | 44786.3542 | 0 | 11.5092 | 39.95
2022-08-13 09:00 | 44786.375 | 0 | 11.7556 | 39.95
2022-08-13 09:30 | 44786.3958 | 0 | 11.8676 | 39.95
2022-08-13 10:00 | 44786.4167 | 0 | 11.8134 | 39.95
2022-08-13 10:30 | 44786.4375 | 0 | 11.9158 | 39.95
2022-08-13 11:00 | 44786.4583 | 0 | 11.2854 | 39.95
2022-08-13 11:30 | 44786.4792 | 0 | 11.0713 | 39.95
2022-08-13 12:00 | 44786.5 | 0 | 11.0483 | 39.95
2022-08-13 12:30 | 44786.5208 | 0 | 10.6411 | 39.95
2022-08-13 13:00 | 44786.5417 | 0 | 10.7066 | 39.95
2022-08-13 13:30 | 44786.5625 | 0 | 11.0616 | 39.95
2022-08-13 14:00 | 44786.5833 | 0 | 11.123 | 39.95
2022-08-13 14:30 | 44786.6042 | 0 | 11.2847 | 39.95
2022-08-13 15:00 | 44786.625 | 0 | 11.1988 | 39.95
2022-08-13 15:30 | 44786.6458 | 0 | 10.8429 | 39.95
2022-08-13 16:00 | 44786.6667 | 0 | 11.3925 | 39.95
2022-08-13 16:30 | 44786.6875 | 0 | 11.9372 | 39.95
2022-08-13 17:00 | 44786.7083 | 0 | 12.116 | 39.95
2022-08-13 17:30 | 44786.7292 | 0 | 12.6188 | 39.95
2022-08-13 18:00 | 44786.75 | 0 | 13.0811 | 39.95
2022-08-13 18:30 | 44786.7708 | 0 | 13.17 | 39.95
2022-08-13 19:00 | 44786.7917 | 0 | 13.0564 | 39.95
2022-08-13 19:30 | 44786.8125 | 0 | 12.726 | 39.95
2022-08-13 20:00 | 44786.8333 | 0 | 12.5238 | 39.95
2022-08-13 20:30 | 44786.8542 | 0 | 12.1001 | 39.95
2022-08-13 21:00 | 44786.875 | 0 | 11.7984 | 39.95
2022-08-13 21:30 | 44786.8958 | 0 | 11.4486 | 39.95
2022-08-13 22:00 | 44786.9167 | 0 | 11.0265 | 39.95
2022-08-13 22:30 | 44786.9375 | 0 | 10.2858 | 39.95
2022-08-13 23:00 | 44786.9583 | 0 | 9.7282 | 39.95
2022-08-13 23:30 | 44786.9792 | 0 | 9.3479 | 39.95
2022-08-14 | 44787 | 0 | 8.6732 | 39.95
2022-08-14 00:30 | 44787.0208 | 0 | 8.2466 | 39.95
2022-08-14 01:00 | 44787.0417 | 0 | 8.0296 | 39.95
2022-08-14 01:30 | 44787.0625 | 0 | 7.8581 | 39.95
2022-08-14 02:00 | 44787.0833 | 0 | 7.7566 | 39.95
2022-08-14 02:30 | 44787.1042 | 0 | 7.5754 | 39.95
2022-08-14 03:00 | 44787.125 | 0 | 7.622 | 39.95
2022-08-14 03:30 | 44787.1458 | 0 | 7.6128 | 39.95
2022-08-14 04:00 | 44787.1667 | 0 | 7.4737 | 39.95
2022-08-14 04:30 | 44787.1875 | 0 | 7.524 | 39.95
2022-08-14 05:00 | 44787.2083 | 0 | 7.7634 | 39.95
2022-08-14 05:30 | 44787.2292 | 0 | 7.9264 | 39.95
2022-08-14 06:00 | 44787.25 | 0 | 8.3369 | 39.95
2022-08-14 06:30 | 44787.2708 | 0 | 8.7877 | 39.95
2022-08-14 07:00 | 44787.2917 | 0 | 9.0534 | 39.95
2022-08-14 07:30 | 44787.3125 | 0 | 8.6503 | 39.95
2022-08-14 08:00 | 44787.3333 | 0 | 8.2232 | 39.95
2022-08-14 08:30 | 44787.3542 | 0 | 7.9037 | 39.95
2022-08-14 09:00 | 44787.375 | 0 | 7.3564 | 39.95
2022-08-14 09:30 | 44787.3958 | 0 | 6.5943 | 39.95
2022-08-14 10:00 | 44787.4167 | 0 | 6.0029 | 39.95
2022-08-14 10:30 | 44787.4375 | 0 | 5.5135 | 39.95
2022-08-14 11:00 | 44787.4583 | 0 | 4.9686 | 39.95
2022-08-14 11:30 | 44787.4792 | 0 | 4.6878 | 39.95
2022-08-14 12:00 | 44787.5 | 0 | 4.4853 | 39.95
2022-08-14 12:30 | 44787.5208 | 0 | 4.4713 | 39.95
2022-08-14 13:00 | 44787.5417 | 0 | 4.758 | 39.95
2022-08-14 13:30 | 44787.5625 | 0 | 5.1311 | 39.95
2022-08-14 14:00 | 44787.5833 | 0 | 5.6344 | 39.95
2022-08-14 14:30 | 44787.6042 | 0 | 6.0786 | 39.95
2022-08-14 15:00 | 44787.625 | 0 | 6.8512 | 39.95
2022-08-14 15:30 | 44787.6458 | 0 | 7.8516 | 39.95
2022-08-14 16:00 | 44787.6667 | 0 | 8.8344 | 39.95
2022-08-14 16:30 | 44787.6875 | 0 | 9.9772 | 39.95
2022-08-14 17:00 | 44787.7083 | 0 | 11.0855 | 39.95
2022-08-14 17:30 | 44787.7292 | 0 | 11.9276 | 39.95
2022-08-14 18:00 | 44787.75 | 0 | 12.5804 | 39.95
2022-08-14 18:30 | 44787.7708 | 0 | 12.9394 | 39.95
2022-08-14 19:00 | 44787.7917 | 0 | 12.4819 | 39.95
2022-08-14 19:30 | 44787.8125 | 0 | 12.0471 | 39.95
2022-08-14 20:00 | 44787.8333 | 0 | 11.8515 | 39.95
2022-08-14 20:30 | 44787.8542 | 0 | 11.5293 | 39.95
2022-08-14 21:00 | 44787.875 | 0 | 11.1317 | 39.95
2022-08-14 21:30 | 44787.8958 | 0 | 10.6294 | 39.95
2022-08-14 22:00 | 44787.9167 | 0 | 10.0965 | 39.95
2022-08-14 22:30 | 44787.9375 | 0 | 9.3752 | 39.95
2022-08-14 23:00 | 44787.9583 | 0 | 8.9696 | 39.95
2022-08-14 23:30 | 44787.9792 | 0 | 8.5022 | 39.95
2022-08-15 | 44788 | 0 | 8.0853 | 39.95
2022-08-15 00:30 | 44788.0208 | 0 | 7.7849 | 39.95
2022-08-15 01:00 | 44788.0417 | 0 | 7.7593 | 39.95
2022-08-15 01:30 | 44788.0625 | 0 | 7.6387 | 39.95
2022-08-15 02:00 | 44788.0833 | 0 | 7.5443 | 39.95
2022-08-15 02:30 | 44788.1042 | 0 | 7.6733 | 39.95
2022-08-15 03:00 | 44788.125 | 0 | 7.4838 | 39.95
2022-08-15 03:30 | 44788.1458 | 0 | 7.611 | 39.95
2022-08-15 04:00 | 44788.1667 | 0 | 7.9904 | 39.95
2022-08-15 04:30 | 44788.1875 | 0 | 8.5476 | 39.95
2022-08-15 05:00 | 44788.2083 | 0 | 9.3774 | 39.95
2022-08-15 05:30 | 44788.2292 | 0 | 10.3735 | 39.95
2022-08-15 06:00 | 44788.25 | 0 | 12.1749 | 39.95
2022-08-15 06:30 | 44788.2708 | 0 | 13.7259 | 39.95
2022-08-15 07:00 | 44788.2917 | 0 | 14.2006 | 39.95
2022-08-15 07:30 | 44788.3125 | 0 | 13.4764 | 39.95
2022-08-15 08:00 | 44788.3333 | 0 | 12.391 | 39.95
2022-08-15 08:30 | 44788.3542 | 0 | 10.9722 | 39.95
2022-08-15 09:00 | 44788.375 | 0 | 10.0084 | 39.95
2022-08-15 09:30 | 44788.3958 | 0 | 9.0663 | 39.95
2022-08-15 10:00 | 44788.4167 | 0 | 8.075 | 39.95
2022-08-15 10:30 | 44788.4375 | 0 | 7.596 | 39.95
2022-08-15 11:00 | 44788.4583 | 0 | 7.206 | 39.95
2022-08-15 11:30 | 44788.4792 | 0 | 6.9987 | 39.95
2022-08-15 12:00 | 44788.5 | 0 | 6.8409 | 39.95
2022-08-15 12:30 | 44788.5208 | 0 | 6.8386 | 39.95
2022-08-15 13:00 | 44788.5417 | 0 | 7.2954 | 39.95
2022-08-15 13:30 | 44788.5625 | 0 | 7.3317 | 39.95
2022-08-15 14:00 | 44788.5833 | 0 | 7.9443 | 39.95
2022-08-15 14:30 | 44788.6042 | 0 | 8.3974 | 39.95
2022-08-15 15:00 | 44788.625 | 0 | 8.7645 | 39.95
2022-08-15 15:30 | 44788.6458 | 0 | 9.7607 | 39.95
2022-08-15 16:00 | 44788.6667 | 0 | 10.7219 | 39.95
2022-08-15 16:30 | 44788.6875 | 0 | 11.7746 | 39.95
2022-08-15 17:00 | 44788.7083 | 0 | 12.8749 | 39.95
2022-08-15 17:30 | 44788.7292 | 0 | 14.088 | 39.95
2022-08-15 18:00 | 44788.75 | 0 | 14.8322 | 39.95
2022-08-15 18:30 | 44788.7708 | 0 | 15.1648 | 39.95
2022-08-15 19:00 | 44788.7917 | 0 | 14.8046 | 39.95
2022-08-15 19:30 | 44788.8125 | 0 | 14.4477 | 39.95
2022-08-15 20:00 | 44788.8333 | 0 | 14.2354 | 39.95
2022-08-15 20:30 | 44788.8542 | 0 | 13.8397 | 39.95
2022-08-15 21:00 | 44788.875 | 0 | 13.1462 | 39.95
2022-08-15 21:30 | 44788.8958 | 0 | 12.4958 | 39.95
2022-08-15 22:00 | 44788.9167 | 0 | 11.6505 | 39.95
2022-08-15 22:30 | 44788.9375 | 0 | 10.7831 | 39.95
2022-08-15 23:00 | 44788.9583 | 0 | 10.0966 | 39.95
2022-08-15 23:30 | 44788.9792 | 0 | 9.4833 | 39.95
2022-08-16 | 44789 | 0 | 8.9352 | 39.95
2022-08-16 00:30 | 44789.0208 | 0 | 8.5228 | 39.95
2022-08-16 01:00 | 44789.0417 | 0 | 8.4064 | 39.95
2022-08-16 01:30 | 44789.0625 | 0 | 8.1958 | 39.95
2022-08-16 02:00 | 44789.0833 | 0 | 8.0481 | 39.95
2022-08-16 02:30 | 44789.1042 | 0 | 8.1681 | 39.95
2022-08-16 03:00 | 44789.125 | 0 | 8.2107 | 39.95
2022-08-16 03:30 | 44789.1458 | 0 | 8.1812 | 39.95
2022-08-16 04:00 | 44789.1667 | 0 | 8.4241 | 39.95
2022-08-16 04:30 | 44789.1875 | 0 | 8.9224 | 39.95
2022-08-16 05:00 | 44789.2083 | 0 | 9.9567 | 39.95
2022-08-16 05:30 | 44789.2292 | 0 | 10.7479 | 39.95
2022-08-16 06:00 | 44789.25 | 0 | 12.3495 | 39.95
2022-08-16 06:30 | 44789.2708 | 0 | 14.0648 | 39.95
2022-08-16 07:00 | 44789.2917 | 0 | 14.4212 | 39.95
2022-08-16 07:30 | 44789.3125 | 0 | 13.7332 | 39.95
2022-08-16 08:00 | 44789.3333 | 0 | 12.765 | 39.95
2022-08-16 08:30 | 44789.3542 | 0 | 11.2867 | 39.95
2022-08-16 09:00 | 44789.375 | 0 | 10.2176 | 39.95
2022-08-16 09:30 | 44789.3958 | 0 | 9.1408 | 39.95
2022-08-16 10:00 | 44789.4167 | 0 | 8.3937 | 39.95
2022-08-16 10:30 | 44789.4375 | 0 | 7.8986 | 39.95
2022-08-16 11:00 | 44789.4583 | 0 | 7.4465 | 39.95
2022-08-16 11:30 | 44789.4792 | 0 | 7.3138 | 39.95
2022-08-16 12:00 | 44789.5 | 0 | 6.8588 | 39.95
2022-08-16 12:30 | 44789.5208 | 0 | 6.9422 | 39.95
2022-08-16 13:00 | 44789.5417 | 0 | 7.2293 | 39.95
2022-08-16 13:30 | 44789.5625 | 0 | 7.5865 | 39.95
2022-08-16 14:00 | 44789.5833 | 0 | 8.5647 | 39.95
2022-08-16 14:30 | 44789.6042 | 0 | 9.4814 | 39.95
2022-08-16 15:00 | 44789.625 | 0 | 11.3002 | 39.95
2022-08-16 15:30 | 44789.6458 | 0 | 12.0334 | 39.95
2022-08-16 16:00 | 44789.6667 | 0 | 11.3646 | 39.95
2022-08-16 16:30 | 44789.6875 | 0 | 11.8568 | 39.95
2022-08-16 17:00 | 44789.7083 | 0 | 12.9039 | 39.95
2022-08-16 17:30 | 44789.7292 | 0 | 14.3258 | 39.95
2022-08-16 18:00 | 44789.75 | 0 | 14.822 | 39.95
2022-08-16 18:30 | 44789.7708 | 0 | 14.8798 | 39.95
2022-08-16 19:00 | 44789.7917 | 0 | 14.8578 | 39.95
2022-08-16 19:30 | 44789.8125 | 0 | 14.4656 | 39.95
2022-08-16 20:00 | 44789.8333 | 0 | 14.2506 | 39.95
2022-08-16 20:30 | 44789.8542 | 0 | 13.6102 | 39.95
2022-08-16 21:00 | 44789.875 | 0 | 13.2111 | 39.95
2022-08-16 21:30 | 44789.8958 | 0 | 12.7514 | 39.95
2022-08-16 22:00 | 44789.9167 | 0 | 11.8658 | 39.95
2022-08-16 22:30 | 44789.9375 | 0 | 10.9216 | 39.95
2022-08-16 23:00 | 44789.9583 | 0 | 10.3367 | 39.95
2022-08-16 23:30 | 44789.9792 | 0 | 9.8186 | 39.95
2022-08-17 | 44790 | 0 | 9.1464 | 39.95
2022-08-17 00:30 | 44790.0208 | 0 | 8.8753 | 39.95
2022-08-17 01:00 | 44790.0417 | 0 | 8.6152 | 39.95
2022-08-17 01:30 | 44790.0625 | 0 | 8.4069 | 39.95
2022-08-17 02:00 | 44790.0833 | 0 | 8.3176 | 39.95
2022-08-17 02:30 | 44790.1042 | 0 | 8.3892 | 39.95
2022-08-17 03:00 | 44790.125 | 0 | 8.3202 | 39.95
2022-08-17 03:30 | 44790.1458 | 0 | 8.4372 | 39.95
2022-08-17 04:00 | 44790.1667 | 0 | 8.6322 | 39.95
2022-08-17 04:30 | 44790.1875 | 0 | 9.184 | 39.95
2022-08-17 05:00 | 44790.2083 | 0 | 9.9842 | 39.95
2022-08-17 05:30 | 44790.2292 | 0 | 10.9466 | 39.95
2022-08-17 06:00 | 44790.25 | 0 | 12.4392 | 39.95
2022-08-17 06:30 | 44790.2708 | 0 | 13.8448 | 39.95
2022-08-17 07:00 | 44790.2917 | 0 | 14.4378 | 39.95
2022-08-17 07:30 | 44790.3125 | 0 | 13.3754 | 39.95
2022-08-17 08:00 | 44790.3333 | 0 | 12.3861 | 39.95
2022-08-17 08:30 | 44790.3542 | 0 | 10.965 | 39.95
2022-08-17 09:00 | 44790.375 | 0 | 9.9741 | 39.95
2022-08-17 09:30 | 44790.3958 | 0 | 9.1958 | 39.95
2022-08-17 10:00 | 44790.4167 | 0 | 8.3103 | 39.95
2022-08-17 10:30 | 44790.4375 | 0 | 7.6373 | 39.95
2022-08-17 11:00 | 44790.4583 | 0 | 7.3921 | 39.95
2022-08-17 11:30 | 44790.4792 | 0 | 7.4126 | 39.95
2022-08-17 12:00 | 44790.5 | 0 | 7.9824 | 39.95
2022-08-17 12:30 | 44790.5208 | 0 | 7.3139 | 39.95
2022-08-17 13:00 | 44790.5417 | 0 | 7.2814 | 39.95
2022-08-17 13:30 | 44790.5625 | 0 | 8.0855 | 39.95
2022-08-17 14:00 | 44790.5833 | 0 | 8.0097 | 39.95
2022-08-17 14:30 | 44790.6042 | 0 | 8.5981 | 39.95
2022-08-17 15:00 | 44790.625 | 0 | 9.0736 | 39.95
2022-08-17 15:30 | 44790.6458 | 0 | 9.726 | 39.95
2022-08-17 16:00 | 44790.6667 | 0 | 10.5612 | 39.95
2022-08-17 16:30 | 44790.6875 | 0 | 11.6428 | 39.95
2022-08-17 17:00 | 44790.7083 | 0 | 12.7588 | 39.95
2022-08-17 17:30 | 44790.7292 | 0 | 13.61 | 39.95
2022-08-17 18:00 | 44790.75 | 0 | 14.2354 | 39.95
2022-08-17 18:30 | 44790.7708 | 0 | 14.7466 | 39.95
2022-08-17 19:00 | 44790.7917 | 0 | 14.5106 | 39.95
2022-08-17 19:30 | 44790.8125 | 0 | 14.3054 | 39.95
2022-08-17 20:00 | 44790.8333 | 0 | 13.9159 | 39.95
2022-08-17 20:30 | 44790.8542 | 0 | 13.5634 | 39.95
2022-08-17 21:00 | 44790.875 | 0 | 13.1324 | 39.95
2022-08-17 21:30 | 44790.8958 | 0 | 12.4429 | 39.95
2022-08-17 22:00 | 44790.9167 | 0 | 11.7815 | 39.95
2022-08-17 22:30 | 44790.9375 | 0 | 11.0352 | 39.95
2022-08-17 23:00 | 44790.9583 | 0 | 10.4007 | 39.95
2022-08-17 23:30 | 44790.9792 | 0 | 9.7972 | 39.95
2022-08-18 | 44791 | 0 | 9.3101 | 39.95
2022-08-18 00:30 | 44791.0208 | 0 | 8.8183 | 39.95
2022-08-18 01:00 | 44791.0417 | 0 | 8.6683 | 39.95
2022-08-18 01:30 | 44791.0625 | 0 | 8.5686 | 39.95
2022-08-18 02:00 | 44791.0833 | 0 | 8.7196 | 39.95
2022-08-18 02:30 | 44791.1042 | 0 | 8.5338 | 39.95
2022-08-18 03:00 | 44791.125 | 0 | 8.3791 | 39.95
2022-08-18 03:30 | 44791.1458 | 0 | 8.4939 | 39.95
2022-08-18 04:00 | 44791.1667 | 0 | 8.682 | 39.95
2022-08-18 04:30 | 44791.1875 | 0 | 9.2752 | 39.95
2022-08-18 05:00 | 44791.2083 | 0 | 10.1911 | 39.95
2022-08-18 05:30 | 44791.2292 | 0 | 10.9914 | 39.95
2022-08-18 06:00 | 44791.25 | 0 | 12.6147 | 39.95
2022-08-18 06:30 | 44791.2708 | 0 | 13.7979 | 39.95
2022-08-18 07:00 | 44791.2917 | 0 | 14.3891 | 39.95
2022-08-18 07:30 | 44791.3125 | 0 | 13.4853 | 39.95
2022-08-18 08:00 | 44791.3333 | 0 | 12.4985 | 39.95
2022-08-18 08:30 | 44791.3542 | 0 | 11.2787 | 39.95
2022-08-18 09:00 | 44791.375 | 0 | 10.27 | 39.95
2022-08-18 09:30 | 44791.3958 | 0 | 9.2949 | 39.95
2022-08-18 10:00 | 44791.4167 | 0 | 8.5582 | 39.95
2022-08-18 10:30 | 44791.4375 | 0 | 7.934 | 39.95
2022-08-18 11:00 | 44791.4583 | 0 | 7.7652 | 39.95
2022-08-18 11:30 | 44791.4792 | 0 | 7.4649 | 39.95
2022-08-18 12:00 | 44791.5 | 0 | 7.1637 | 39.95
2022-08-18 12:30 | 44791.5208 | 0 | 7.281 | 39.95
2022-08-18 13:00 | 44791.5417 | 0 | 7.6912 | 39.95
2022-08-18 13:30 | 44791.5625 | 0 | 7.9987 | 39.95
2022-08-18 14:00 | 44791.5833 | 0 | 8.5016 | 39.95
2022-08-18 14:30 | 44791.6042 | 0 | 8.7288 | 39.95
2022-08-18 15:00 | 44791.625 | 0 | 9.3091 | 39.95
2022-08-18 15:30 | 44791.6458 | 0 | 9.9693 | 39.95
2022-08-18 16:00 | 44791.6667 | 0 | 10.5592 | 39.95
2022-08-18 16:30 | 44791.6875 | 0 | 11.342 | 39.95
2022-08-18 17:00 | 44791.7083 | 0 | 12.2678 | 39.95
2022-08-18 17:30 | 44791.7292 | 0 | 13.1103 | 39.95
2022-08-18 18:00 | 44791.75 | 0 | 13.6381 | 39.95
2022-08-18 18:30 | 44791.7708 | 0 | 13.9539 | 39.95
2022-08-18 19:00 | 44791.7917 | 0 | 13.7577 | 39.95
2022-08-18 19:30 | 44791.8125 | 0 | 13.5327 | 39.95
2022-08-18 20:00 | 44791.8333 | 0 | 13.4928 | 39.95
2022-08-18 20:30 | 44791.8542 | 0 | 12.9654 | 39.95
2022-08-18 21:00 | 44791.875 | 0 | 12.5451 | 39.95
2022-08-18 21:30 | 44791.8958 | 0 | 11.9685 | 39.95
2022-08-18 22:00 | 44791.9167 | 0 | 11.3103 | 39.95
2022-08-18 22:30 | 44791.9375 | 0 | 10.5884 | 39.95
2022-08-18 23:00 | 44791.9583 | 0 | 10.0357 | 39.95
2022-08-18 23:30 | 44791.9792 | 0 | 9.5593 | 39.95
2022-08-19 | 44792 | 0 | 9.0638 | 39.95
2022-08-19 00:30 | 44792.0208 | 0 | 8.6449 | 39.95
2022-08-19 01:00 | 44792.0417 | 0 | 8.6773 | 39.95
2022-08-19 01:30 | 44792.0625 | 0 | 8.261 | 39.95
2022-08-19 02:00 | 44792.0833 | 0 | 8.253 | 39.95
2022-08-19 02:30 | 44792.1042 | 0 | 8.2185 | 39.95
2022-08-19 03:00 | 44792.125 | 0 | 8.1678 | 39.95
2022-08-19 03:30 | 44792.1458 | 0 | 8.2218 | 39.95
2022-08-19 04:00 | 44792.1667 | 0 | 8.543 | 39.95
2022-08-19 04:30 | 44792.1875 | 0 | 9.0419 | 39.95
2022-08-19 05:00 | 44792.2083 | 0 | 9.7464 | 39.95
2022-08-19 05:30 | 44792.2292 | 0 | 10.426 | 39.95
2022-08-19 06:00 | 44792.25 | 0 | 11.8685 | 39.95
2022-08-19 06:30 | 44792.2708 | 0 | 13.1025 | 39.95
2022-08-19 07:00 | 44792.2917 | 0 | 13.6104 | 39.95
2022-08-19 07:30 | 44792.3125 | 0 | 12.9389 | 39.95
2022-08-19 08:00 | 44792.3333 | 0 | 11.8644 | 39.95
2022-08-19 08:30 | 44792.3542 | 0 | 10.7386 | 39.95
2022-08-19 09:00 | 44792.375 | 0 | 9.8931 | 39.95
2022-08-19 09:30 | 44792.3958 | 0 | 9.1872 | 39.95
2022-08-19 10:00 | 44792.4167 | 0 | 8.5729 | 39.95
2022-08-19 10:30 | 44792.4375 | 0 | 8.1344 | 39.95
2022-08-19 11:00 | 44792.4583 | 0 | 7.8155 | 39.95
2022-08-19 11:30 | 44792.4792 | 0 | 7.6211 | 39.95
2022-08-19 12:00 | 44792.5 | 0 | 7.3215 | 39.95
2022-08-19 12:30 | 44792.5208 | 0 | 7.2468 | 39.95
2022-08-19 13:00 | 44792.5417 | 0 | 7.4575 | 39.95
2022-08-19 13:30 | 44792.5625 | 0 | 8.0106 | 39.95
2022-08-19 14:00 | 44792.5833 | 0 | 8.5747 | 39.95
2022-08-19 14:30 | 44792.6042 | 0 | 8.9695 | 39.95
2022-08-19 15:00 | 44792.625 | 0 | 9.4148 | 39.95
2022-08-19 15:30 | 44792.6458 | 0 | 10.3836 | 39.95
2022-08-19 16:00 | 44792.6667 | 0 | 11.1377 | 39.95
2022-08-19 16:30 | 44792.6875 | 0 | 11.9199 | 39.95
2022-08-19 17:00 | 44792.7083 | 0 | 12.5966 | 39.95
2022-08-19 17:30 | 44792.7292 | 0 | 12.8993 | 39.95
2022-08-19 18:00 | 44792.75 | 0 | 13.0372 | 39.95
2022-08-19 18:30 | 44792.7708 | 0 | 13.0336 | 39.95
2022-08-19 19:00 | 44792.7917 | 0 | 12.7844 | 39.95
2022-08-19 19:30 | 44792.8125 | 0 | 12.6766 | 39.95
2022-08-19 20:00 | 44792.8333 | 0 | 12.4795 | 39.95
2022-08-19 20:30 | 44792.8542 | 0 | 12.0892 | 39.95
2022-08-19 21:00 | 44792.875 | 0 | 11.5719 | 39.95
2022-08-19 21:30 | 44792.8958 | 0 | 11.2592 | 39.95
2022-08-19 22:00 | 44792.9167 | 0 | 10.8427 | 39.95
2022-08-19 22:30 | 44792.9375 | 0 | 10.1692 | 39.95
2022-08-19 23:00 | 44792.9583 | 0 | 9.8576 | 39.95
2022-08-19 23:30 | 44792.9792 | 0 | 9.3299 | 39.95
2022-08-20 | 44793 | 0 | 8.7901 | 39.95
2022-08-20 00:30 | 44793.0208 | 0 | 8.3956 | 39.95
2022-08-20 01:00 | 44793.0417 | 0 | 8.3232 | 39.95
2022-08-20 01:30 | 44793.0625 | 0 | 7.9929 | 39.95
2022-08-20 02:00 | 44793.0833 | 0 | 7.934 | 39.95
2022-08-20 02:30 | 44793.1042 | 0 | 7.845 | 39.95
2022-08-20 03:00 | 44793.125 | 0 | 7.8837 | 39.95
2022-08-20 03:30 | 44793.1458 | 0 | 7.8667 | 39.95
2022-08-20 04:00 | 44793.1667 | 0 | 7.9796 | 39.95
2022-08-20 04:30 | 44793.1875 | 0 | 7.9007 | 39.95
2022-08-20 05:00 | 44793.2083 | 0 | 8.2476 | 39.95
2022-08-20 05:30 | 44793.2292 | 0 | 8.4096 | 39.95
2022-08-20 06:00 | 44793.25 | 0 | 8.8384 | 39.95
2022-08-20 06:30 | 44793.2708 | 0 | 9.1602 | 39.95
2022-08-20 07:00 | 44793.2917 | 0 | 9.1793 | 39.95
2022-08-20 07:30 | 44793.3125 | 0 | 8.6342 | 39.95
2022-08-20 08:00 | 44793.3333 | 0 | 8.4504 | 39.95
2022-08-20 08:30 | 44793.3542 | 0 | 7.6565 | 39.95
2022-08-20 09:00 | 44793.375 | 0 | 7.1471 | 39.95
2022-08-20 09:30 | 44793.3958 | 0 | 6.4553 | 39.95
2022-08-20 10:00 | 44793.4167 | 0 | 5.7335 | 39.95
2022-08-20 10:30 | 44793.4375 | 0 | 5.3578 | 39.95
2022-08-20 11:00 | 44793.4583 | 0 | 5.1291 | 39.95
2022-08-20 11:30 | 44793.4792 | 0 | 4.9784 | 39.95
2022-08-20 12:00 | 44793.5 | 0 | 4.6402 | 39.95
2022-08-20 12:30 | 44793.5208 | 0 | 4.7592 | 39.95
2022-08-20 13:00 | 44793.5417 | 0 | 5.0231 | 39.95
2022-08-20 13:30 | 44793.5625 | 0 | 5.1942 | 39.95
2022-08-20 14:00 | 44793.5833 | 0 | 5.7845 | 39.95
2022-08-20 14:30 | 44793.6042 | 0 | 6.369 | 39.95
2022-08-20 15:00 | 44793.625 | 0 | 7.0729 | 39.95
2022-08-20 15:30 | 44793.6458 | 0 | 7.9226 | 39.95
2022-08-20 16:00 | 44793.6667 | 0 | 8.7726 | 39.95
2022-08-20 16:30 | 44793.6875 | 0 | 9.6541 | 39.95
2022-08-20 17:00 | 44793.7083 | 0 | 10.5621 | 39.95
2022-08-20 17:30 | 44793.7292 | 0 | 11.0802 | 39.95
2022-08-20 18:00 | 44793.75 | 0 | 11.4272 | 39.95
2022-08-20 18:30 | 44793.7708 | 0 | 11.5445 | 39.95
2022-08-20 19:00 | 44793.7917 | 0 | 11.331 | 39.95
2022-08-20 19:30 | 44793.8125 | 0 | 10.9832 | 39.95
2022-08-20 20:00 | 44793.8333 | 0 | 10.758 | 39.95
2022-08-20 20:30 | 44793.8542 | 0 | 10.6262 | 39.95
2022-08-20 21:00 | 44793.875 | 0 | 10.2188 | 39.95
2022-08-20 21:30 | 44793.8958 | 0 | 9.9886 | 39.95
2022-08-20 22:00 | 44793.9167 | 0 | 9.6 | 39.95
2022-08-20 22:30 | 44793.9375 | 0 | 9.0566 | 39.95
2022-08-20 23:00 | 44793.9583 | 0 | 8.7115 | 39.95
2022-08-20 23:30 | 44793.9792 | 0 | 8.5668 | 39.95
2022-08-21 | 44794 | 0 | 8.1152 | 39.95
2022-08-21 00:30 | 44794.0208 | 0 | 7.901 | 39.95
2022-08-21 01:00 | 44794.0417 | 0 | 7.8819 | 39.95
2022-08-21 01:30 | 44794.0625 | 0 | 7.4321 | 39.95
2022-08-21 02:00 | 44794.0833 | 0 | 7.309 | 39.95
2022-08-21 02:30 | 44794.1042 | 0 | 7.1199 | 39.95
2022-08-21 03:00 | 44794.125 | 0 | 7.0955 | 39.95
2022-08-21 03:30 | 44794.1458 | 0 | 7.0732 | 39.95
2022-08-21 04:00 | 44794.1667 | 0 | 7.0797 | 39.95
2022-08-21 04:30 | 44794.1875 | 0 | 7.0905 | 39.95
2022-08-21 05:00 | 44794.2083 | 0 | 7.3257 | 39.95
2022-08-21 05:30 | 44794.2292 | 0 | 7.4867 | 39.95
2022-08-21 06:00 | 44794.25 | 0 | 7.8257 | 39.95
2022-08-21 06:30 | 44794.2708 | 0 | 7.9984 | 39.95
2022-08-21 07:00 | 44794.2917 | 0 | 8.1222 | 39.95
2022-08-21 07:30 | 44794.3125 | 0 | 7.8638 | 39.95
2022-08-21 08:00 | 44794.3333 | 0 | 7.5571 | 39.95
2022-08-21 08:30 | 44794.3542 | 0 | 6.9488 | 39.95
2022-08-21 09:00 | 44794.375 | 0 | 6.4191 | 39.95
2022-08-21 09:30 | 44794.3958 | 0 | 6.4161 | 39.95
2022-08-21 10:00 | 44794.4167 | 0 | 7.4521 | 39.95
2022-08-21 10:30 | 44794.4375 | 0 | 5.636 | 39.95
2022-08-21 11:00 | 44794.4583 | 0 | 6.7774 | 39.95
2022-08-21 11:30 | 44794.4792 | 0 | 7.7374 | 39.95
2022-08-21 12:00 | 44794.5 | 0 | 6.7585 | 39.95
2022-08-21 12:30 | 44794.5208 | 0 | 6.779 | 39.95
2022-08-21 13:00 | 44794.5417 | 0 | 5.7058 | 39.95
2022-08-21 13:30 | 44794.5625 | 0 | 7.4848 | 39.95
2022-08-21 14:00 | 44794.5833 | 0 | 6.249 | 39.95
2022-08-21 14:30 | 44794.6042 | 0 | 6.5242 | 39.95
2022-08-21 15:00 | 44794.625 | 0 | 6.7993 | 39.95
2022-08-21 15:30 | 44794.6458 | 0 | 7.8462 | 39.95
2022-08-21 16:00 | 44794.6667 | 0 | 8.8274 | 39.95
2022-08-21 16:30 | 44794.6875 | 0 | 9.9042 | 39.95
2022-08-21 17:00 | 44794.7083 | 0 | 10.8547 | 39.95
2022-08-21 17:30 | 44794.7292 | 0 | 11.7091 | 39.95
2022-08-21 18:00 | 44794.75 | 0 | 12.3678 | 39.95
2022-08-21 18:30 | 44794.7708 | 0 | 12.6796 | 39.95
2022-08-21 19:00 | 44794.7917 | 0 | 12.2642 | 39.95
2022-08-21 19:30 | 44794.8125 | 0 | 11.9947 | 39.95
2022-08-21 20:00 | 44794.8333 | 0 | 11.7839 | 39.95
2022-08-21 20:30 | 44794.8542 | 0 | 11.1019 | 39.95
2022-08-21 21:00 | 44794.875 | 0 | 10.7551 | 39.95
2022-08-21 21:30 | 44794.8958 | 0 | 10.3296 | 39.95
2022-08-21 22:00 | 44794.9167 | 0 | 9.8525 | 39.95
2022-08-21 22:30 | 44794.9375 | 0 | 9.0226 | 39.95
2022-08-21 23:00 | 44794.9583 | 0 | 8.5677 | 39.95
2022-08-21 23:30 | 44794.9792 | 0 | 8.0651 | 39.95
2022-08-22 | 44795 | 0 | 7.8146 | 39.95
2022-08-22 00:30 | 44795.0208 | 0 | 7.717 | 39.95
2022-08-22 01:00 | 44795.0417 | 0 | 7.5743 | 39.95
2022-08-22 01:30 | 44795.0625 | 0 | 7.4308 | 39.95
2022-08-22 02:00 | 44795.0833 | 0 | 7.3936 | 39.95
2022-08-22 02:30 | 44795.1042 | 0 | 7.5163 | 39.95
2022-08-22 03:00 | 44795.125 | 0 | 7.2638 | 39.95
2022-08-22 03:30 | 44795.1458 | 0 | 7.5505 | 39.95
2022-08-22 04:00 | 44795.1667 | 0 | 7.8605 | 39.95
2022-08-22 04:30 | 44795.1875 | 0 | 8.1914 | 39.95
2022-08-22 05:00 | 44795.2083 | 0 | 9.0739 | 39.95
2022-08-22 05:30 | 44795.2292 | 0 | 9.9557 | 39.95
2022-08-22 06:00 | 44795.25 | 0 | 11.1232 | 39.95
2022-08-22 06:30 | 44795.2708 | 0 | 12.4026 | 39.95
2022-08-22 07:00 | 44795.2917 | 0 | 12.6482 | 39.95
2022-08-22 07:30 | 44795.3125 | 0 | 11.7563 | 39.95
2022-08-22 08:00 | 44795.3333 | 0 | 11.0727 | 39.95
2022-08-22 08:30 | 44795.3542 | 0 | 9.7909 | 39.95
2022-08-22 09:00 | 44795.375 | 0 | 9.8191 | 39.95
2022-08-22 09:30 | 44795.3958 | 0 | 9.9126 | 39.95
2022-08-22 10:00 | 44795.4167 | 0 | 8.2543 | 39.95
2022-08-22 10:30 | 44795.4375 | 0 | 9.0615 | 39.95
2022-08-22 11:00 | 44795.4583 | 0 | 9.0693 | 39.95
2022-08-22 11:30 | 44795.4792 | 0 | 7.8924 | 39.95
2022-08-22 12:00 | 44795.5 | 0 | 8.5132 | 39.95
2022-08-22 12:30 | 44795.5208 | 0 | 8.3568 | 39.95
2022-08-22 13:00 | 44795.5417 | 0 | 7.9617 | 39.95
2022-08-22 13:30 | 44795.5625 | 0 | 8.7041 | 39.95
2022-08-22 14:00 | 44795.5833 | 0 | 7.5501 | 39.95
2022-08-22 14:30 | 44795.6042 | 0 | 8.5123 | 39.95
2022-08-22 15:00 | 44795.625 | 0 | 10.8141 | 39.95
2022-08-22 15:30 | 44795.6458 | 0 | 11.1529 | 39.95
2022-08-22 16:00 | 44795.6667 | 0 | 11.1426 | 39.95
2022-08-22 16:30 | 44795.6875 | 0 | 11.9887 | 39.95
2022-08-22 17:00 | 44795.7083 | 0 | 12.6475 | 39.95
2022-08-22 17:30 | 44795.7292 | 0 | 13.6004 | 39.95
2022-08-22 18:00 | 44795.75 | 0 | 14.0824 | 39.95
2022-08-22 18:30 | 44795.7708 | 0 | 14.2875 | 39.95
2022-08-22 19:00 | 44795.7917 | 0 | 13.8626 | 39.95
2022-08-22 19:30 | 44795.8125 | 0 | 13.5985 | 39.95
2022-08-22 20:00 | 44795.8333 | 0 | 13.4151 | 39.95
2022-08-22 20:30 | 44795.8542 | 0 | 12.6223 | 39.95
2022-08-22 21:00 | 44795.875 | 0 | 12.1708 | 39.95
2022-08-22 21:30 | 44795.8958 | 0 | 11.7073 | 39.95
2022-08-22 22:00 | 44795.9167 | 0 | 11.1122 | 39.95
2022-08-22 22:30 | 44795.9375 | 0 | 10.2939 | 39.95
2022-08-22 23:00 | 44795.9583 | 0 | 9.6304 | 39.95
2022-08-22 23:30 | 44795.9792 | 0 | 9.1218 | 39.95
2022-08-23 | 44796 | 0 | 8.628 | 39.95
2022-08-23 00:30 | 44796.0208 | 0 | 8.2248 | 39.95
2022-08-23 01:00 | 44796.0417 | 0 | 8.054 | 39.95
2022-08-23 01:30 | 44796.0625 | 0 | 7.9192 | 39.95
2022-08-23 02:00 | 44796.0833 | 0 | 7.8959 | 39.95
2022-08-23 02:30 | 44796.1042 | 0 | 8.0076 | 39.95
2022-08-23 03:00 | 44796.125 | 0 | 7.8576 | 39.95
2022-08-23 03:30 | 44796.1458 | 0 | 7.979 | 39.95
2022-08-23 04:00 | 44796.1667 | 0 | 8.3098 | 39.95
2022-08-23 04:30 | 44796.1875 | 0 | 8.7128 | 39.95
2022-08-23 05:00 | 44796.2083 | 0 | 9.5506 | 39.95
2022-08-23 05:30 | 44796.2292 | 0 | 10.0869 | 39.95
2022-08-23 06:00 | 44796.25 | 0 | 11.189 | 39.95
2022-08-23 06:30 | 44796.2708 | 0 | 12.2514 | 39.95
2022-08-23 07:00 | 44796.2917 | 0 | 12.47 | 39.95
2022-08-23 07:30 | 44796.3125 | 0 | 11.6112 | 39.95
2022-08-23 08:00 | 44796.3333 | 0 | 10.7272 | 39.95
2022-08-23 08:30 | 44796.3542 | 0 | 9.9032 | 39.95
2022-08-23 09:00 | 44796.375 | 0 | 8.9878 | 39.95
2022-08-23 09:30 | 44796.3958 | 0 | 8.2596 | 39.95
2022-08-23 10:00 | 44796.4167 | 0 | 7.9455 | 39.95
2022-08-23 10:30 | 44796.4375 | 0 | 7.7213 | 39.95
2022-08-23 11:00 | 44796.4583 | 0 | 7.516 | 39.95
2022-08-23 11:30 | 44796.4792 | 0 | 7.6473 | 39.95
2022-08-23 12:00 | 44796.5 | 0 | 8.7177 | 39.95
2022-08-23 12:30 | 44796.5208 | 0 | 9.6554 | 39.95
2022-08-23 13:00 | 44796.5417 | 0 | 9.1118 | 39.95
2022-08-23 13:30 | 44796.5625 | 0 | 9.1222 | 39.95
2022-08-23 14:00 | 44796.5833 | 0 | 8.5969 | 39.95
2022-08-23 14:30 | 44796.6042 | 0 | 9.2388 | 39.95
2022-08-23 15:00 | 44796.625 | 0 | 9.6865 | 39.95
2022-08-23 15:30 | 44796.6458 | 0 | 11.5633 | 39.95
2022-08-23 16:00 | 44796.6667 | 0 | 10.9287 | 39.95
2022-08-23 16:30 | 44796.6875 | 0 | 11.9585 | 39.95
2022-08-23 17:00 | 44796.7083 | 0 | 12.6522 | 39.95
2022-08-23 17:30 | 44796.7292 | 0 | 13.4908 | 39.95
2022-08-23 18:00 | 44796.75 | 0 | 14.0821 | 39.95
2022-08-23 18:30 | 44796.7708 | 0 | 14.0797 | 39.95
2022-08-23 19:00 | 44796.7917 | 0 | 13.7554 | 39.95
2022-08-23 19:30 | 44796.8125 | 0 | 13.359 | 39.95
2022-08-23 20:00 | 44796.8333 | 0 | 13.2322 | 39.95
2022-08-23 20:30 | 44796.8542 | 0 | 12.7336 | 39.95
2022-08-23 21:00 | 44796.875 | 0 | 12.3535 | 39.95
2022-08-23 21:30 | 44796.8958 | 0 | 11.9275 | 39.95
2022-08-23 22:00 | 44796.9167 | 0 | 11.3401 | 39.95
2022-08-23 22:30 | 44796.9375 | 0 | 10.4321 | 39.95
2022-08-23 23:00 | 44796.9583 | 0 | 9.8906 | 39.95
2022-08-23 23:30 | 44796.9792 | 0 | 9.3988 | 39.95
2022-08-24 | 44797 | 0 | 8.8887 | 39.95
2022-08-24 00:30 | 44797.0208 | 0 | 8.5278 | 39.95
2022-08-24 01:00 | 44797.0417 | 0 | 8.3421 | 39.95
2022-08-24 01:30 | 44797.0625 | 0 | 8.328 | 39.95
2022-08-24 02:00 | 44797.0833 | 0 | 8.219 | 39.95
2022-08-24 02:30 | 44797.1042 | 0 | 8.2026 | 39.95
2022-08-24 03:00 | 44797.125 | 0 | 8.3265 | 39.95
2022-08-24 03:30 | 44797.1458 | 0 | 8.4248 | 39.95
2022-08-24 04:00 | 44797.1667 | 0 | 8.662 | 39.95
2022-08-24 04:30 | 44797.1875 | 0 | 8.9223 | 39.95
2022-08-24 05:00 | 44797.2083 | 0 | 9.7094 | 39.95
2022-08-24 05:30 | 44797.2292 | 0 | 10.6265 | 39.95
2022-08-24 06:00 | 44797.25 | 0 | 12.0601 | 39.95
2022-08-24 06:30 | 44797.2708 | 0 | 11.7731 | 39.95
2022-08-24 07:00 | 44797.2917 | 0 | 0.022333 | 39.95
2022-08-24 07:30 | 44797.3125 | 0 | 0.022333 | 39.95
2022-08-24 08:00 | 44797.3333 | 0 | 0.022333 | 39.95
2022-08-24 08:30 | 44797.3542 | 0 | 0.022333 | 39.95
2022-08-24 09:00 | 44797.375 | 0 | 0.022333 | 39.95
2022-08-24 09:30 | 44797.3958 | 0 | 0.022333 | 39.95
2022-08-24 10:00 | 44797.4167 | 0 | 0.022333 | 39.95
2022-08-24 10:30 | 44797.4375 | 0 | 0.022333 | 39.95
2022-08-24 11:00 | 44797.4583 | 0 | 0.022333 | 39.95
2022-08-24 11:30 | 44797.4792 | 0 | 0.022333 | 39.95
2022-08-24 12:00 | 44797.5 | 0 | 0.022333 | 39.95
2022-08-24 12:30 | 44797.5208 | 0 | 0.022333 | 39.95
2022-08-24 13:00 | 44797.5417 | 0 | 0.022333 | 39.95
2022-08-24 13:30 | 44797.5625 | 0 | 3.7139 | 39.95
2022-08-24 14:00 | 44797.5833 | 0 | 7.9728 | 39.95
2022-08-24 14:30 | 44797.6042 | 0 | 8.2943 | 39.95
2022-08-24 15:00 | 44797.625 | 0 | 9.0326 | 39.95
2022-08-24 15:30 | 44797.6458 | 0 | 9.9556 | 39.95
2022-08-24 16:00 | 44797.6667 | 0 | 10.9943 | 39.95
2022-08-24 16:30 | 44797.6875 | 0 | 12.0843 | 39.95
2022-08-24 17:00 | 44797.7083 | 0 | 13.1375 | 39.95
2022-08-24 17:30 | 44797.7292 | 0 | 14.3511 | 39.95
2022-08-24 18:00 | 44797.75 | 0 | 15.047 | 39.95
2022-08-24 18:30 | 44797.7708 | 0 | 15.3628 | 39.95
2022-08-24 19:00 | 44797.7917 | 0 | 15.4623 | 39.95
2022-08-24 19:30 | 44797.8125 | 0 | 14.9113 | 39.95
2022-08-24 20:00 | 44797.8333 | 0 | 14.635 | 39.95
2022-08-24 20:30 | 44797.8542 | 0 | 14.0799 | 39.95
2022-08-24 21:00 | 44797.875 | 0 | 13.5195 | 39.95
2022-08-24 21:30 | 44797.8958 | 0 | 12.9311 | 39.95
2022-08-24 22:00 | 44797.9167 | 0 | 12.0725 | 39.95
2022-08-24 22:30 | 44797.9375 | 0 | 11.1424 | 39.95
2022-08-24 23:00 | 44797.9583 | 0 | 10.5008 | 39.95
2022-08-24 23:30 | 44797.9792 | 0 | 9.9768 | 39.95
2022-08-25 | 44798 | 0 | 9.3998 | 39.95
2022-08-25 00:30 | 44798.0208 | 0 | 8.9637 | 39.95
2022-08-25 01:00 | 44798.0417 | 0 | 8.7094 | 39.95
2022-08-25 01:30 | 44798.0625 | 0 | 8.5564 | 39.95
2022-08-25 02:00 | 44798.0833 | 0 | 8.5761 | 39.95
2022-08-25 02:30 | 44798.1042 | 0 | 8.4635 | 39.95
2022-08-25 03:00 | 44798.125 | 0 | 8.4733 | 39.95
2022-08-25 03:30 | 44798.1458 | 0 | 8.5894 | 39.95
2022-08-25 04:00 | 44798.1667 | 0 | 8.8352 | 39.95
2022-08-25 04:30 | 44798.1875 | 0 | 9.3142 | 39.95
2022-08-25 05:00 | 44798.2083 | 0 | 10.2088 | 39.95
2022-08-25 05:30 | 44798.2292 | 0 | 10.9501 | 39.95
2022-08-25 06:00 | 44798.25 | 0 | 12.6418 | 39.95
2022-08-25 06:30 | 44798.2708 | 0 | 14.1702 | 39.95
2022-08-25 07:00 | 44798.2917 | 0 | 14.3959 | 39.95
2022-08-25 07:30 | 44798.3125 | 0 | 13.4657 | 39.95
2022-08-25 08:00 | 44798.3333 | 0 | 12.1078 | 39.95
2022-08-25 08:30 | 44798.3542 | 0 | 10.9336 | 39.95
2022-08-25 09:00 | 44798.375 | 0 | 9.7522 | 39.95
2022-08-25 09:30 | 44798.3958 | 0 | 8.7432 | 39.95
2022-08-25 10:00 | 44798.4167 | 0 | 8.1098 | 39.95
2022-08-25 10:30 | 44798.4375 | 0 | 7.5294 | 39.95
2022-08-25 11:00 | 44798.4583 | 0 | 7.2837 | 39.95
2022-08-25 11:30 | 44798.4792 | 0 | 6.9827 | 39.95
2022-08-25 12:00 | 44798.5 | 0 | 6.8049 | 39.95
2022-08-25 12:30 | 44798.5208 | 0 | 7.0044 | 39.95
2022-08-25 13:00 | 44798.5417 | 0 | 7.1737 | 39.95
2022-08-25 13:30 | 44798.5625 | 0 | 7.4671 | 39.95
2022-08-25 14:00 | 44798.5833 | 0 | 7.711 | 39.95
2022-08-25 14:30 | 44798.6042 | 0 | 8.2546 | 39.95
2022-08-25 15:00 | 44798.625 | 0 | 8.7715 | 39.95
2022-08-25 15:30 | 44798.6458 | 0 | 9.7077 | 39.95
2022-08-25 16:00 | 44798.6667 | 0 | 10.7477 | 39.95
2022-08-25 16:30 | 44798.6875 | 0 | 11.69 | 39.95
2022-08-25 17:00 | 44798.7083 | 0 | 12.5795 | 39.95
2022-08-25 17:30 | 44798.7292 | 0 | 13.3908 | 39.95
2022-08-25 18:00 | 44798.75 | 0 | 14.0796 | 39.95
2022-08-25 18:30 | 44798.7708 | 0 | 14.507 | 39.95
2022-08-25 19:00 | 44798.7917 | 0 | 14.3405 | 39.95
2022-08-25 19:30 | 44798.8125 | 0 | 14.2357 | 39.95
2022-08-25 20:00 | 44798.8333 | 0 | 14.0583 | 39.95
2022-08-25 20:30 | 44798.8542 | 0 | 13.3425 | 39.95
2022-08-25 21:00 | 44798.875 | 0 | 12.8031 | 39.95
2022-08-25 21:30 | 44798.8958 | 0 | 12.4997 | 39.95
2022-08-25 22:00 | 44798.9167 | 0 | 11.9731 | 39.95
2022-08-25 22:30 | 44798.9375 | 0 | 11.0517 | 39.95
2022-08-25 23:00 | 44798.9583 | 0 | 10.4215 | 39.95
2022-08-25 23:30 | 44798.9792 | 0 | 9.8493 | 39.95
2022-08-26 | 44799 | 0 | 9.291 | 39.95
2022-08-26 00:30 | 44799.0208 | 0 | 8.8756 | 39.95
2022-08-26 01:00 | 44799.0417 | 0 | 8.6284 | 39.95
2022-08-26 01:30 | 44799.0625 | 0 | 8.5338 | 39.95
2022-08-26 02:00 | 44799.0833 | 0 | 8.361 | 39.95
2022-08-26 02:30 | 44799.1042 | 0 | 8.3688 | 39.95
2022-08-26 03:00 | 44799.125 | 0 | 8.442 | 39.95
2022-08-26 03:30 | 44799.1458 | 0 | 8.5882 | 39.95
2022-08-26 04:00 | 44799.1667 | 0 | 8.8023 | 39.95
2022-08-26 04:30 | 44799.1875 | 0 | 9.1222 | 39.95
2022-08-26 05:00 | 44799.2083 | 0 | 10.0538 | 39.95
2022-08-26 05:30 | 44799.2292 | 0 | 10.7241 | 39.95
2022-08-26 06:00 | 44799.25 | 0 | 12.0654 | 39.95
2022-08-26 06:30 | 44799.2708 | 0 | 13.6136 | 39.95
2022-08-26 07:00 | 44799.2917 | 0 | 13.8933 | 39.95
2022-08-26 07:30 | 44799.3125 | 0 | 13.0941 | 39.95
2022-08-26 08:00 | 44799.3333 | 0 | 12.0948 | 39.95
2022-08-26 08:30 | 44799.3542 | 0 | 11.8701 | 39.95
2022-08-26 09:00 | 44799.375 | 0 | 11.7055 | 39.95
2022-08-26 09:30 | 44799.3958 | 0 | 9.8898 | 39.95
2022-08-26 10:00 | 44799.4167 | 0 | 9.7441 | 39.95
2022-08-26 10:30 | 44799.4375 | 0 | 7.934 | 39.95
2022-08-26 11:00 | 44799.4583 | 0 | 8.8473 | 39.95
2022-08-26 11:30 | 44799.4792 | 0 | 11.1771 | 39.95
2022-08-26 12:00 | 44799.5 | 0 | 10.6029 | 39.95
2022-08-26 12:30 | 44799.5208 | 0 | 10.4692 | 39.95
2022-08-26 13:00 | 44799.5417 | 0 | 8.9046 | 39.95
2022-08-26 13:30 | 44799.5625 | 0 | 8.0629 | 39.95
2022-08-26 14:00 | 44799.5833 | 0 | 7.4423 | 39.95
2022-08-26 14:30 | 44799.6042 | 0 | 8.9112 | 39.95
2022-08-26 15:00 | 44799.625 | 0 | 9.1247 | 39.95
2022-08-26 15:30 | 44799.6458 | 0 | 9.817 | 39.95
2022-08-26 16:00 | 44799.6667 | 0 | 10.5978 | 39.95
2022-08-26 16:30 | 44799.6875 | 0 | 11.5168 | 39.95
2022-08-26 17:00 | 44799.7083 | 0 | 12.4798 | 39.95
2022-08-26 17:30 | 44799.7292 | 0 | 13.2636 | 39.95
2022-08-26 18:00 | 44799.75 | 0 | 13.787 | 39.95
2022-08-26 18:30 | 44799.7708 | 0 | 14.099 | 39.95
2022-08-26 19:00 | 44799.7917 | 0 | 13.9904 | 39.95
2022-08-26 19:30 | 44799.8125 | 0 | 13.645 | 39.95
2022-08-26 20:00 | 44799.8333 | 0 | 13.5717 | 39.95
2022-08-26 20:30 | 44799.8542 | 0 | 13.2525 | 39.95
2022-08-26 21:00 | 44799.875 | 0 | 12.9422 | 39.95
2022-08-26 21:30 | 44799.8958 | 0 | 12.4511 | 39.95
2022-08-26 22:00 | 44799.9167 | 0 | 11.6813 | 39.95
2022-08-26 22:30 | 44799.9375 | 0 | 11.0678 | 39.95
2022-08-26 23:00 | 44799.9583 | 0 | 10.4794 | 39.95
2022-08-26 23:30 | 44799.9792 | 0 | 9.8894 | 39.95
2022-08-27 | 44800 | 0 | 9.2039 | 39.95
2022-08-27 00:30 | 44800.0208 | 0 | 8.7541 | 39.95
2022-08-27 01:00 | 44800.0417 | 0 | 8.6785 | 39.95
2022-08-27 01:30 | 44800.0625 | 0 | 8.3783 | 39.95
2022-08-27 02:00 | 44800.0833 | 0 | 8.1216 | 39.95
2022-08-27 02:30 | 44800.1042 | 0 | 8.1511 | 39.95
2022-08-27 03:00 | 44800.125 | 0 | 8.1106 | 39.95
2022-08-27 03:30 | 44800.1458 | 0 | 8.2339 | 39.95
2022-08-27 04:00 | 44800.1667 | 0 | 8.3077 | 39.95
2022-08-27 04:30 | 44800.1875 | 0 | 8.3536 | 39.95
2022-08-27 05:00 | 44800.2083 | 0 | 8.679 | 39.95
2022-08-27 05:30 | 44800.2292 | 0 | 9.0158 | 39.95
2022-08-27 06:00 | 44800.25 | 0 | 9.2825 | 39.95
2022-08-27 06:30 | 44800.2708 | 0 | 9.7054 | 39.95
2022-08-27 07:00 | 44800.2917 | 0 | 9.6918 | 39.95
2022-08-27 07:30 | 44800.3125 | 0 | 9.2066 | 39.95
2022-08-27 08:00 | 44800.3333 | 0 | 8.7324 | 39.95
2022-08-27 08:30 | 44800.3542 | 0 | 7.948 | 39.95
2022-08-27 09:00 | 44800.375 | 0 | 7.2983 | 39.95
2022-08-27 09:30 | 44800.3958 | 0 | 6.5634 | 39.95
2022-08-27 10:00 | 44800.4167 | 0 | 5.9559 | 39.95
2022-08-27 10:30 | 44800.4375 | 0 | 6.4623 | 39.95
2022-08-27 11:00 | 44800.4583 | 0 | 7.4464 | 39.95
2022-08-27 11:30 | 44800.4792 | 0 | 7.929 | 39.95
2022-08-27 12:00 | 44800.5 | 0 | 7.0992 | 39.95
2022-08-27 12:30 | 44800.5208 | 0 | 6.0071 | 39.95
2022-08-27 13:00 | 44800.5417 | 0 | 5.7835 | 39.95
2022-08-27 13:30 | 44800.5625 | 0 | 5.5007 | 39.95
2022-08-27 14:00 | 44800.5833 | 0 | 6.8096 | 39.95
2022-08-27 14:30 | 44800.6042 | 0 | 6.4014 | 39.95
2022-08-27 15:00 | 44800.625 | 0 | 7.6354 | 39.95
2022-08-27 15:30 | 44800.6458 | 0 | 7.9052 | 39.95
2022-08-27 16:00 | 44800.6667 | 0 | 8.7764 | 39.95
2022-08-27 16:30 | 44800.6875 | 0 | 9.7577 | 39.95
2022-08-27 17:00 | 44800.7083 | 0 | 10.5368 | 39.95
2022-08-27 17:30 | 44800.7292 | 0 | 11.2831 | 39.95
2022-08-27 18:00 | 44800.75 | 0 | 11.8491 | 39.95
2022-08-27 18:30 | 44800.7708 | 0 | 11.8774 | 39.95
2022-08-27 19:00 | 44800.7917 | 0 | 11.8357 | 39.95
2022-08-27 19:30 | 44800.8125 | 0 | 11.5507 | 39.95
2022-08-27 20:00 | 44800.8333 | 0 | 11.3867 | 39.95
2022-08-27 20:30 | 44800.8542 | 0 | 10.6694 | 39.95
2022-08-27 21:00 | 44800.875 | 0 | 10.4725 | 39.95
2022-08-27 21:30 | 44800.8958 | 0 | 10.2567 | 39.95
2022-08-27 22:00 | 44800.9167 | 0 | 9.9196 | 39.95
2022-08-27 22:30 | 44800.9375 | 0 | 9.2996 | 39.95
2022-08-27 23:00 | 44800.9583 | 0 | 8.8665 | 39.95
2022-08-27 23:30 | 44800.9792 | 0 | 8.4444 | 39.95
2022-08-28 | 44801 | 0 | 7.9476 | 39.95
2022-08-28 00:30 | 44801.0208 | 0 | 7.6646 | 39.95
2022-08-28 01:00 | 44801.0417 | 0 | 7.4841 | 39.95
2022-08-28 01:30 | 44801.0625 | 0 | 7.3171 | 39.95
2022-08-28 02:00 | 44801.0833 | 0 | 7.3168 | 39.95
2022-08-28 02:30 | 44801.1042 | 0 | 7.1551 | 39.95
2022-08-28 03:00 | 44801.125 | 0 | 7.1322 | 39.95
2022-08-28 03:30 | 44801.1458 | 0 | 6.9478 | 39.95
2022-08-28 04:00 | 44801.1667 | 0 | 6.9705 | 39.95
2022-08-28 04:30 | 44801.1875 | 0 | 7.1392 | 39.95
2022-08-28 05:00 | 44801.2083 | 0 | 7.3343 | 39.95
2022-08-28 05:30 | 44801.2292 | 0 | 7.4546 | 39.95
2022-08-28 06:00 | 44801.25 | 0 | 7.7756 | 39.95
2022-08-28 06:30 | 44801.2708 | 0 | 7.7031 | 39.95
2022-08-28 07:00 | 44801.2917 | 0 | 8.2765 | 39.95
2022-08-28 07:30 | 44801.3125 | 0 | 7.5313 | 39.95
2022-08-28 08:00 | 44801.3333 | 0 | 6.9501 | 39.95
2022-08-28 08:30 | 44801.3542 | 0 | 6.4541 | 39.95
2022-08-28 09:00 | 44801.375 | 0 | 5.9401 | 39.95
2022-08-28 09:30 | 44801.3958 | 0 | 7.7924 | 39.95
2022-08-28 10:00 | 44801.4167 | 0 | 7.7289 | 39.95
2022-08-28 10:30 | 44801.4375 | 0 | 6.3962 | 39.95
2022-08-28 11:00 | 44801.4583 | 0 | 6.2489 | 39.95
2022-08-28 11:30 | 44801.4792 | 0 | 5.0937 | 39.95
2022-08-28 12:00 | 44801.5 | 0 | 4.9002 | 39.95
2022-08-28 12:30 | 44801.5208 | 0 | 5.8571 | 39.95
2022-08-28 13:00 | 44801.5417 | 0 | 5.7046 | 39.95
2022-08-28 13:30 | 44801.5625 | 0 | 5.3337 | 39.95
2022-08-28 14:00 | 44801.5833 | 0 | 6.6474 | 39.95
2022-08-28 14:30 | 44801.6042 | 0 | 7.2444 | 39.95
2022-08-28 15:00 | 44801.625 | 0 | 7.4595 | 39.95
2022-08-28 15:30 | 44801.6458 | 0 | 8.8823 | 39.95
2022-08-28 16:00 | 44801.6667 | 0 | 9.7137 | 39.95
2022-08-28 16:30 | 44801.6875 | 0 | 10.6565 | 39.95
2022-08-28 17:00 | 44801.7083 | 0 | 11.3651 | 39.95
2022-08-28 17:30 | 44801.7292 | 0 | 11.7681 | 39.95
2022-08-28 18:00 | 44801.75 | 0 | 12.203 | 39.95
2022-08-28 18:30 | 44801.7708 | 0 | 12.0456 | 39.95
2022-08-28 19:00 | 44801.7917 | 0 | 11.6867 | 39.95
2022-08-28 19:30 | 44801.8125 | 0 | 11.2729 | 39.95
2022-08-28 20:00 | 44801.8333 | 0 | 11.1395 | 39.95
2022-08-28 20:30 | 44801.8542 | 0 | 10.7157 | 39.95
2022-08-28 21:00 | 44801.875 | 0 | 10.2073 | 39.95
2022-08-28 21:30 | 44801.8958 | 0 | 10.0244 | 39.95
2022-08-28 22:00 | 44801.9167 | 0 | 9.4855 | 39.95
2022-08-28 22:30 | 44801.9375 | 0 | 8.821 | 39.95
2022-08-28 23:00 | 44801.9583 | 0 | 8.3524 | 39.95
2022-08-28 23:30 | 44801.9792 | 0 | 8.0171 | 39.95
2022-08-29 | 44802 | 0 | 7.7858 | 39.95
2022-08-29 00:30 | 44802.0208 | 0 | 7.4905 | 39.95
2022-08-29 01:00 | 44802.0417 | 0 | 7.468 | 39.95
2022-08-29 01:30 | 44802.0625 | 0 | 7.2935 | 39.95
2022-08-29 02:00 | 44802.0833 | 0 | 7.2593 | 39.95
2022-08-29 02:30 | 44802.1042 | 0 | 7.385 | 39.95
2022-08-29 03:00 | 44802.125 | 0 | 7.2779 | 39.95
2022-08-29 03:30 | 44802.1458 | 0 | 7.4299 | 39.95
2022-08-29 04:00 | 44802.1667 | 0 | 7.7563 | 39.95
2022-08-29 04:30 | 44802.1875 | 0 | 8.2089 | 39.95
2022-08-29 05:00 | 44802.2083 | 0 | 8.9475 | 39.95
2022-08-29 05:30 | 44802.2292 | 0 | 9.4948 | 39.95
2022-08-29 06:00 | 44802.25 | 0 | 10.649 | 39.95
2022-08-29 06:30 | 44802.2708 | 0 | 11.8709 | 39.95
2022-08-29 07:00 | 44802.2917 | 0 | 12.2805 | 39.95
2022-08-29 07:30 | 44802.3125 | 0 | 12.6028 | 39.95
2022-08-29 08:00 | 44802.3333 | 0 | 12.8646 | 39.95
2022-08-29 08:30 | 44802.3542 | 0 | 12.9491 | 39.95
2022-08-29 09:00 | 44802.375 | 0 | 13.0762 | 39.95
2022-08-29 09:30 | 44802.3958 | 0 | 11.1802 | 39.95
2022-08-29 10:00 | 44802.4167 | 0 | 9.3192 | 39.95
2022-08-29 10:30 | 44802.4375 | 0 | 8.6147 | 39.95
2022-08-29 11:00 | 44802.4583 | 0 | 7.8893 | 39.95
2022-08-29 11:30 | 44802.4792 | 0 | 8.145 | 39.95
2022-08-29 12:00 | 44802.5 | 0 | 8.0013 | 39.95
2022-08-29 12:30 | 44802.5208 | 0 | 8.4437 | 39.95
2022-08-29 13:00 | 44802.5417 | 0 | 8.0453 | 39.95
2022-08-29 13:30 | 44802.5625 | 0 | 8.7353 | 39.95
2022-08-29 14:00 | 44802.5833 | 0 | 8.5821 | 39.95
2022-08-29 14:30 | 44802.6042 | 0 | 9.1832 | 39.95
2022-08-29 15:00 | 44802.625 | 0 | 10.3015 | 39.95
2022-08-29 15:30 | 44802.6458 | 0 | 10.938 | 39.95
2022-08-29 16:00 | 44802.6667 | 0 | 11.4604 | 39.95
2022-08-29 16:30 | 44802.6875 | 0 | 11.7023 | 39.95
2022-08-29 17:00 | 44802.7083 | 0 | 12.6513 | 39.95
2022-08-29 17:30 | 44802.7292 | 0 | 13.4904 | 39.95
2022-08-29 18:00 | 44802.75 | 0 | 14.2147 | 39.95
2022-08-29 18:30 | 44802.7708 | 0 | 14.1824 | 39.95
2022-08-29 19:00 | 44802.7917 | 0 | 13.8689 | 39.95
2022-08-29 19:30 | 44802.8125 | 0 | 13.5714 | 39.95
2022-08-29 20:00 | 44802.8333 | 0 | 13.1192 | 39.95
2022-08-29 20:30 | 44802.8542 | 0 | 12.6739 | 39.95
2022-08-29 21:00 | 44802.875 | 0 | 12.0272 | 39.95
2022-08-29 21:30 | 44802.8958 | 0 | 11.4781 | 39.95
2022-08-29 22:00 | 44802.9167 | 0 | 10.9639 | 39.95
2022-08-29 22:30 | 44802.9375 | 0 | 10.3756 | 39.95
2022-08-29 23:00 | 44802.9583 | 0 | 9.6661 | 39.95
2022-08-29 23:30 | 44802.9792 | 0 | 9.195 | 39.95
2022-08-30 | 44803 | 0 | 8.6653 | 39.95
2022-08-30 00:30 | 44803.0208 | 0 | 8.247 | 39.95
2022-08-30 01:00 | 44803.0417 | 0 | 8.1324 | 39.95
2022-08-30 01:30 | 44803.0625 | 0 | 7.9165 | 39.95
2022-08-30 02:00 | 44803.0833 | 0 | 7.8286 | 39.95
2022-08-30 02:30 | 44803.1042 | 0 | 7.8078 | 39.95
2022-08-30 03:00 | 44803.125 | 0 | 7.711 | 39.95
2022-08-30 03:30 | 44803.1458 | 0 | 7.803 | 39.95
2022-08-30 04:00 | 44803.1667 | 0 | 8.1746 | 39.95
2022-08-30 04:30 | 44803.1875 | 0 | 8.501 | 39.95
2022-08-30 05:00 | 44803.2083 | 0 | 9.1673 | 39.95
2022-08-30 05:30 | 44803.2292 | 0 | 9.9103 | 39.95
2022-08-30 06:00 | 44803.25 | 0 | 11.1365 | 39.95
2022-08-30 06:30 | 44803.2708 | 0 | 12.2694 | 39.95
2022-08-30 07:00 | 44803.2917 | 0 | 13.1859 | 39.95
2022-08-30 07:30 | 44803.3125 | 0 | 13.0697 | 39.95
2022-08-30 08:00 | 44803.3333 | 0 | 12.5381 | 39.95
2022-08-30 08:30 | 44803.3542 | 0 | 12.1701 | 39.95
2022-08-30 09:00 | 44803.375 | 0 | 11.7565 | 39.95
2022-08-30 09:30 | 44803.3958 | 0 | 12.0761 | 39.95
2022-08-30 10:00 | 44803.4167 | 0 | 11.4557 | 39.95
2022-08-30 10:30 | 44803.4375 | 0 | 11.3095 | 39.95
2022-08-30 11:00 | 44803.4583 | 0 | 11.3071 | 39.95
2022-08-30 11:30 | 44803.4792 | 0 | 10.6213 | 39.95
2022-08-30 12:00 | 44803.5 | 0 | 10.87 | 39.95
2022-08-30 12:30 | 44803.5208 | 0 | 11.0664 | 39.95
2022-08-30 13:00 | 44803.5417 | 0 | 12.4726 | 39.95
2022-08-30 13:30 | 44803.5625 | 0 | 12.553 | 39.95
2022-08-30 14:00 | 44803.5833 | 0 | 12.4914 | 39.95
2022-08-30 14:30 | 44803.6042 | 0 | 11.976 | 39.95
2022-08-30 15:00 | 44803.625 | 0 | 12.1742 | 39.95
2022-08-30 15:30 | 44803.6458 | 0 | 12.249 | 39.95
2022-08-30 16:00 | 44803.6667 | 0 | 12.3695 | 39.95
2022-08-30 16:30 | 44803.6875 | 0 | 13.0755 | 39.95
2022-08-30 17:00 | 44803.7083 | 0 | 13.7563 | 39.95
2022-08-30 17:30 | 44803.7292 | 0 | 14.2247 | 39.95
2022-08-30 18:00 | 44803.75 | 0 | 14.4858 | 39.95
2022-08-30 18:30 | 44803.7708 | 0 | 14.7291 | 39.95
2022-08-30 19:00 | 44803.7917 | 0 | 14.5945 | 39.95
2022-08-30 19:30 | 44803.8125 | 0 | 14.108 | 39.95
2022-08-30 20:00 | 44803.8333 | 0 | 13.7886 | 39.95
2022-08-30 20:30 | 44803.8542 | 0 | 12.9822 | 39.95
2022-08-30 21:00 | 44803.875 | 0 | 12.5957 | 39.95
2022-08-30 21:30 | 44803.8958 | 0 | 12.1293 | 39.95
2022-08-30 22:00 | 44803.9167 | 0 | 11.3916 | 39.95
2022-08-30 22:30 | 44803.9375 | 0 | 10.4925 | 39.95
2022-08-30 23:00 | 44803.9583 | 0 | 9.9741 | 39.95
2022-08-30 23:30 | 44803.9792 | 0 | 9.4657 | 39.95
2022-08-31 | 44804 | 0 | 8.9996 | 39.95
2022-08-31 00:30 | 44804.0208 | 0 | 8.6594 | 39.95
2022-08-31 01:00 | 44804.0417 | 0 | 8.5335 | 39.95
2022-08-31 01:30 | 44804.0625 | 0 | 8.3083 | 39.95
2022-08-31 02:00 | 44804.0833 | 0 | 8.2188 | 39.95
2022-08-31 02:30 | 44804.1042 | 0 | 8.2145 | 39.95
2022-08-31 03:00 | 44804.125 | 0 | 8.2276 | 39.95
2022-08-31 03:30 | 44804.1458 | 0 | 8.3539 | 39.95
2022-08-31 04:00 | 44804.1667 | 0 | 8.4898 | 39.95
2022-08-31 04:30 | 44804.1875 | 0 | 8.8765 | 39.95
2022-08-31 05:00 | 44804.2083 | 0 | 9.4536 | 39.95
2022-08-31 05:30 | 44804.2292 | 0 | 10.0349 | 39.95
2022-08-31 06:00 | 44804.25 | 0 | 11.176 | 39.95
2022-08-31 06:30 | 44804.2708 | 0 | 12.3449 | 39.95
2022-08-31 07:00 | 44804.2917 | 0 | 12.7709 | 39.95
2022-08-31 07:30 | 44804.3125 | 0 | 12.8804 | 39.95
2022-08-31 08:00 | 44804.3333 | 0 | 12.4503 | 39.95
2022-08-31 08:30 | 44804.3542 | 0 | 12.4124 | 39.95
2022-08-31 09:00 | 44804.375 | 0 | 11.7552 | 39.95
2022-08-31 09:30 | 44804.3958 | 0 | 10.1039 | 39.95
2022-08-31 10:00 | 44804.4167 | 0 | 9.0791 | 39.95
2022-08-31 10:30 | 44804.4375 | 0 | 7.7165 | 39.95
2022-08-31 11:00 | 44804.4583 | 0 | 7.4689 | 39.95
2022-08-31 11:30 | 44804.4792 | 0 | 7.4173 | 39.95
2022-08-31 12:00 | 44804.5 | 0 | 7.5839 | 39.95
2022-08-31 12:30 | 44804.5208 | 0 | 8.0476 | 39.95
2022-08-31 13:00 | 44804.5417 | 0 | 8.5576 | 39.95
2022-08-31 13:30 | 44804.5625 | 0 | 11.3698 | 39.95
2022-08-31 14:00 | 44804.5833 | 0 | 12.1396 | 39.95
2022-08-31 14:30 | 44804.6042 | 0 | 10.844 | 39.95
2022-08-31 15:00 | 44804.625 | 0 | 9.8939 | 39.95
2022-08-31 15:30 | 44804.6458 | 0 | 10.5812 | 39.95
2022-08-31 16:00 | 44804.6667 | 0 | 11.8243 | 39.95
2022-08-31 16:30 | 44804.6875 | 0 | 12.464 | 39.95
2022-08-31 17:00 | 44804.7083 | 0 | 12.9046 | 39.95
2022-08-31 17:30 | 44804.7292 | 0 | 13.4473 | 39.95
2022-08-31 18:00 | 44804.75 | 0 | 13.9288 | 39.95
2022-08-31 18:30 | 44804.7708 | 0 | 14.1143 | 39.95
2022-08-31 19:00 | 44804.7917 | 0 | 13.8107 | 39.95
2022-08-31 19:30 | 44804.8125 | 0 | 13.4705 | 39.95
2022-08-31 20:00 | 44804.8333 | 0 | 13.3034 | 39.95
2022-08-31 20:30 | 44804.8542 | 0 | 12.702 | 39.95
2022-08-31 21:00 | 44804.875 | 0 | 12.2395 | 39.95
2022-08-31 21:30 | 44804.8958 | 0 | 11.9508 | 39.95
2022-08-31 22:00 | 44804.9167 | 0 | 11.3187 | 39.95
2022-08-31 22:30 | 44804.9375 | 0 | 10.4466 | 39.95
2022-08-31 23:00 | 44804.9583 | 0 | 9.9484 | 39.95
2022-08-31 23:30 | 44804.9792 | 0 | 9.4549 | 39.95
2022-09-01 | 44805 | 0 | 8.8408 | 39.95
2022-09-01 00:30 | 44805.0208 | 0 | 8.5144 | 39.95
2022-09-01 01:00 | 44805.0417 | 0 | 8.3549 | 39.95
2022-09-01 01:30 | 44805.0625 | 0 | 8.1627 | 39.95
2022-09-01 02:00 | 44805.0833 | 0 | 8.1565 | 39.95
2022-09-01 02:30 | 44805.1042 | 0 | 7.9885 | 39.95
2022-09-01 03:00 | 44805.125 | 0 | 8.0013 | 39.95
2022-09-01 03:30 | 44805.1458 | 0 | 8.1568 | 39.95
2022-09-01 04:00 | 44805.1667 | 0 | 8.4477 | 39.95
2022-09-01 04:30 | 44805.1875 | 0 | 8.7672 | 39.95
2022-09-01 05:00 | 44805.2083 | 0 | 9.368 | 39.95
2022-09-01 05:30 | 44805.2292 | 0 | 10.1426 | 39.95
2022-09-01 06:00 | 44805.25 | 0 | 11.2765 | 39.95
2022-09-01 06:30 | 44805.2708 | 0 | 11.9871 | 39.95
2022-09-01 07:00 | 44805.2917 | 0 | 12.6222 | 39.95
2022-09-01 07:30 | 44805.3125 | 0 | 12.7737 | 39.95
2022-09-01 08:00 | 44805.3333 | 0 | 11.9305 | 39.95
2022-09-01 08:30 | 44805.3542 | 0 | 10.3451 | 39.95
2022-09-01 09:00 | 44805.375 | 0 | 9.8956 | 39.95
2022-09-01 09:30 | 44805.3958 | 0 | 9.8539 | 39.95
2022-09-01 10:00 | 44805.4167 | 0 | 9.5779 | 39.95
2022-09-01 10:30 | 44805.4375 | 0 | 11.3878 | 39.95
2022-09-01 11:00 | 44805.4583 | 0 | 10.1626 | 39.95
2022-09-01 11:30 | 44805.4792 | 0 | 10.1958 | 39.95
2022-09-01 12:00 | 44805.5 | 0 | 9.0411 | 39.95
2022-09-01 12:30 | 44805.5208 | 0 | 11.4593 | 39.95
2022-09-01 13:00 | 44805.5417 | 0 | 11.3049 | 39.95
2022-09-01 13:30 | 44805.5625 | 0 | 9.891 | 39.95
2022-09-01 14:00 | 44805.5833 | 0 | 10.7424 | 39.95
2022-09-01 14:30 | 44805.6042 | 0 | 10.1766 | 39.95
2022-09-01 15:00 | 44805.625 | 0 | 9.9308 | 39.95
2022-09-01 15:30 | 44805.6458 | 0 | 10.3682 | 39.95
2022-09-01 16:00 | 44805.6667 | 0 | 11.2835 | 39.95
2022-09-01 16:30 | 44805.6875 | 0 | 11.9426 | 39.95
2022-09-01 17:00 | 44805.7083 | 0 | 12.7296 | 39.95
2022-09-01 17:30 | 44805.7292 | 0 | 13.3232 | 39.95
2022-09-01 18:00 | 44805.75 | 0 | 13.5838 | 39.95
2022-09-01 18:30 | 44805.7708 | 0 | 13.7134 | 39.95
2022-09-01 19:00 | 44805.7917 | 0 | 13.676 | 39.95
2022-09-01 19:30 | 44805.8125 | 0 | 13.3409 | 39.95
2022-09-01 20:00 | 44805.8333 | 0 | 13.1538 | 39.95
2022-09-01 20:30 | 44805.8542 | 0 | 12.6834 | 39.95
2022-09-01 21:00 | 44805.875 | 0 | 12.2252 | 39.95
2022-09-01 21:30 | 44805.8958 | 0 | 11.8258 | 39.95
2022-09-01 22:00 | 44805.9167 | 0 | 11.3355 | 39.95
2022-09-01 22:30 | 44805.9375 | 0 | 10.6676 | 39.95
2022-09-01 23:00 | 44805.9583 | 0 | 9.98 | 39.95
2022-09-01 23:30 | 44805.9792 | 0 | 9.5411 | 39.95
2022-09-02 | 44806 | 0 | 8.9396 | 39.95
2022-09-02 00:30 | 44806.0208 | 0 | 8.5004 | 39.95
2022-09-02 01:00 | 44806.0417 | 0 | 8.3254 | 39.95
2022-09-02 01:30 | 44806.0625 | 0 | 8.1038 | 39.95
2022-09-02 02:00 | 44806.0833 | 0 | 8.0186 | 39.95
2022-09-02 02:30 | 44806.1042 | 0 | 7.9948 | 39.95
2022-09-02 03:00 | 44806.125 | 0 | 7.9742 | 39.95
2022-09-02 03:30 | 44806.1458 | 0 | 8.0624 | 39.95
2022-09-02 04:00 | 44806.1667 | 0 | 8.2252 | 39.95
2022-09-02 04:30 | 44806.1875 | 0 | 8.7291 | 39.95
2022-09-02 05:00 | 44806.2083 | 0 | 9.1116 | 39.95
2022-09-02 05:30 | 44806.2292 | 0 | 9.7152 | 39.95
2022-09-02 06:00 | 44806.25 | 0 | 10.7067 | 39.95
2022-09-02 06:30 | 44806.2708 | 0 | 11.2551 | 39.95
2022-09-02 07:00 | 44806.2917 | 0 | 11.6675 | 39.95
2022-09-02 07:30 | 44806.3125 | 0 | 12.1014 | 39.95
2022-09-02 08:00 | 44806.3333 | 0 | 11.7302 | 39.95
2022-09-02 08:30 | 44806.3542 | 0 | 11.6032 | 39.95
2022-09-02 09:00 | 44806.375 | 0 | 12.1781 | 39.95
2022-09-02 09:30 | 44806.3958 | 0 | 12.1428 | 39.95
2022-09-02 10:00 | 44806.4167 | 0 | 12.9045 | 39.95
2022-09-02 10:30 | 44806.4375 | 0 | 13.2577 | 39.95
2022-09-02 11:00 | 44806.4583 | 0 | 12.5554 | 39.95
2022-09-02 11:30 | 44806.4792 | 0 | 11.5186 | 39.95
2022-09-02 12:00 | 44806.5 | 0 | 11.5308 | 39.95
2022-09-02 12:30 | 44806.5208 | 0 | 11.9892 | 39.95
2022-09-02 13:00 | 44806.5417 | 0 | 11.6838 | 39.95
2022-09-02 13:30 | 44806.5625 | 0 | 11.7409 | 39.95
2022-09-02 14:00 | 44806.5833 | 0 | 11.7895 | 39.95
2022-09-02 14:30 | 44806.6042 | 0 | 11.5203 | 39.95
2022-09-02 15:00 | 44806.625 | 0 | 11.9447 | 39.95
2022-09-02 15:30 | 44806.6458 | 0 | 11.9119 | 39.95
2022-09-02 16:00 | 44806.6667 | 0 | 12.324 | 39.95
2022-09-02 16:30 | 44806.6875 | 0 | 12.6465 | 39.95
2022-09-02 17:00 | 44806.7083 | 0 | 13.1798 | 39.95
2022-09-02 17:30 | 44806.7292 | 0 | 13.5759 | 39.95
2022-09-02 18:00 | 44806.75 | 0 | 13.4836 | 39.95
2022-09-02 18:30 | 44806.7708 | 0 | 13.4389 | 39.95
2022-09-02 19:00 | 44806.7917 | 0 | 13.134 | 39.95
2022-09-02 19:30 | 44806.8125 | 0 | 13.1923 | 39.95
2022-09-02 20:00 | 44806.8333 | 0 | 12.7379 | 39.95
2022-09-02 20:30 | 44806.8542 | 0 | 12.3744 | 39.95
2022-09-02 21:00 | 44806.875 | 0 | 12.2002 | 39.95
2022-09-02 21:30 | 44806.8958 | 0 | 11.6645 | 39.95
2022-09-02 22:00 | 44806.9167 | 0 | 11.1392 | 39.95
2022-09-02 22:30 | 44806.9375 | 0 | 10.483 | 39.95
2022-09-02 23:00 | 44806.9583 | 0 | 10.1185 | 39.95
2022-09-02 23:30 | 44806.9792 | 0 | 9.6613 | 39.95
2022-09-03 | 44807 | 0 | 8.9413 | 39.95
2022-09-03 00:30 | 44807.0208 | 0 | 8.5104 | 39.95
2022-09-03 01:00 | 44807.0417 | 0 | 8.4059 | 39.95
2022-09-03 01:30 | 44807.0625 | 0 | 8.1645 | 39.95
2022-09-03 02:00 | 44807.0833 | 0 | 8.1452 | 39.95
2022-09-03 02:30 | 44807.1042 | 0 | 8.0728 | 39.95
2022-09-03 03:00 | 44807.125 | 0 | 8.0025 | 39.95
2022-09-03 03:30 | 44807.1458 | 0 | 8.0076 | 39.95
2022-09-03 04:00 | 44807.1667 | 0 | 7.8397 | 39.95
2022-09-03 04:30 | 44807.1875 | 0 | 8.0642 | 39.95
2022-09-03 05:00 | 44807.2083 | 0 | 8.2458 | 39.95
2022-09-03 05:30 | 44807.2292 | 0 | 8.4522 | 39.95
2022-09-03 06:00 | 44807.25 | 0 | 8.677 | 39.95
2022-09-03 06:30 | 44807.2708 | 0 | 9.2191 | 39.95
2022-09-03 07:00 | 44807.2917 | 0 | 10.0024 | 39.95
2022-09-03 07:30 | 44807.3125 | 0 | 10.5776 | 39.95
2022-09-03 08:00 | 44807.3333 | 0 | 10.8292 | 39.95
2022-09-03 08:30 | 44807.3542 | 0 | 11.2366 | 39.95
2022-09-03 09:00 | 44807.375 | 0 | 11.9733 | 39.95
2022-09-03 09:30 | 44807.3958 | 0 | 11.8414 | 39.95
2022-09-03 10:00 | 44807.4167 | 0 | 11.2544 | 39.95
2022-09-03 10:30 | 44807.4375 | 0 | 10.3152 | 39.95
2022-09-03 11:00 | 44807.4583 | 0 | 8.5393 | 39.95
2022-09-03 11:30 | 44807.4792 | 0 | 9.45 | 39.95
2022-09-03 12:00 | 44807.5 | 0 | 7.8298 | 39.95
2022-09-03 12:30 | 44807.5208 | 0 | 9.3393 | 39.95
2022-09-03 13:00 | 44807.5417 | 0 | 9.1671 | 39.95
2022-09-03 13:30 | 44807.5625 | 0 | 8.4209 | 39.95
2022-09-03 14:00 | 44807.5833 | 0 | 8.1196 | 39.95
2022-09-03 14:30 | 44807.6042 | 0 | 9.0858 | 39.95
2022-09-03 15:00 | 44807.625 | 0 | 9.7811 | 39.95
2022-09-03 15:30 | 44807.6458 | 0 | 9.8153 | 39.95
2022-09-03 16:00 | 44807.6667 | 0 | 10.0464 | 39.95
2022-09-03 16:30 | 44807.6875 | 0 | 9.6988 | 39.95
2022-09-03 17:00 | 44807.7083 | 0 | 10.623 | 39.95
2022-09-03 17:30 | 44807.7292 | 0 | 11.3518 | 39.95
2022-09-03 18:00 | 44807.75 | 0 | 11.8056 | 39.95
2022-09-03 18:30 | 44807.7708 | 0 | 11.8178 | 39.95
2022-09-03 19:00 | 44807.7917 | 0 | 11.5101 | 39.95
2022-09-03 19:30 | 44807.8125 | 0 | 11.2071 | 39.95
2022-09-03 20:00 | 44807.8333 | 0 | 11.2747 | 39.95
2022-09-03 20:30 | 44807.8542 | 0 | 10.9787 | 39.95
2022-09-03 21:00 | 44807.875 | 0 | 10.5577 | 39.95
2022-09-03 21:30 | 44807.8958 | 0 | 10.5595 | 39.95
2022-09-03 22:00 | 44807.9167 | 0 | 10.1407 | 39.95
2022-09-03 22:30 | 44807.9375 | 0 | 9.5691 | 39.95
2022-09-03 23:00 | 44807.9583 | 0 | 9.1722 | 39.95
2022-09-03 23:30 | 44807.9792 | 0 | 8.7173 | 39.95
2022-09-04 | 44808 | 0 | 8.0976 | 39.95
2022-09-04 00:30 | 44808.0208 | 0 | 7.6366 | 39.95
2022-09-04 01:00 | 44808.0417 | 0 | 7.4585 | 39.95
2022-09-04 01:30 | 44808.0625 | 0 | 7.3835 | 39.95
2022-09-04 02:00 | 44808.0833 | 0 | 7.2778 | 39.95
2022-09-04 02:30 | 44808.1042 | 0 | 6.9767 | 39.95
2022-09-04 03:00 | 44808.125 | 0 | 6.9335 | 39.95
2022-09-04 03:30 | 44808.1458 | 0 | 7.0098 | 39.95
2022-09-04 04:00 | 44808.1667 | 0 | 6.7987 | 39.95
2022-09-04 04:30 | 44808.1875 | 0 | 6.9252 | 39.95
2022-09-04 05:00 | 44808.2083 | 0 | 7.376 | 39.95
2022-09-04 05:30 | 44808.2292 | 0 | 7.4433 | 39.95
2022-09-04 06:00 | 44808.25 | 0 | 7.6291 | 39.95
2022-09-04 06:30 | 44808.2708 | 0 | 7.6664 | 39.95
2022-09-04 07:00 | 44808.2917 | 0 | 7.4383 | 39.95
2022-09-04 07:30 | 44808.3125 | 0 | 7.03 | 39.95
2022-09-04 08:00 | 44808.3333 | 0 | 6.7477 | 39.95
2022-09-04 08:30 | 44808.3542 | 0 | 6.3044 | 39.95
2022-09-04 09:00 | 44808.375 | 0 | 6.8344 | 39.95
2022-09-04 09:30 | 44808.3958 | 0 | 5.6323 | 39.95
2022-09-04 10:00 | 44808.4167 | 0 | 7.2953 | 39.95
2022-09-04 10:30 | 44808.4375 | 0 | 6.1943 | 39.95
2022-09-04 11:00 | 44808.4583 | 0 | 6.244 | 39.95
2022-09-04 11:30 | 44808.4792 | 0 | 7.7809 | 39.95
2022-09-04 12:00 | 44808.5 | 0 | 8.0401 | 39.95
2022-09-04 12:30 | 44808.5208 | 0 | 7.7659 | 39.95
2022-09-04 13:00 | 44808.5417 | 0 | 8.1264 | 39.95
2022-09-04 13:30 | 44808.5625 | 0 | 7.3863 | 39.95
2022-09-04 14:00 | 44808.5833 | 0 | 6.6189 | 39.95
2022-09-04 14:30 | 44808.6042 | 0 | 8.9805 | 39.95
2022-09-04 15:00 | 44808.625 | 0 | 8.7558 | 39.95
2022-09-04 15:30 | 44808.6458 | 0 | 9.5798 | 39.95
2022-09-04 16:00 | 44808.6667 | 0 | 10.222 | 39.95
2022-09-04 16:30 | 44808.6875 | 0 | 10.2877 | 39.95
2022-09-04 17:00 | 44808.7083 | 0 | 10.8117 | 39.95
2022-09-04 17:30 | 44808.7292 | 0 | 11.4287 | 39.95
2022-09-04 18:00 | 44808.75 | 0 | 12.1157 | 39.95
2022-09-04 18:30 | 44808.7708 | 0 | 12.2535 | 39.95
2022-09-04 19:00 | 44808.7917 | 0 | 12.1906 | 39.95
2022-09-04 19:30 | 44808.8125 | 0 | 11.7509 | 39.95
2022-09-04 20:00 | 44808.8333 | 0 | 11.6077 | 39.95
2022-09-04 20:30 | 44808.8542 | 0 | 11.0859 | 39.95
2022-09-04 21:00 | 44808.875 | 0 | 10.7203 | 39.95
2022-09-04 21:30 | 44808.8958 | 0 | 10.2525 | 39.95
2022-09-04 22:00 | 44808.9167 | 0 | 9.7659 | 39.95
2022-09-04 22:30 | 44808.9375 | 0 | 9.0559 | 39.95
2022-09-04 23:00 | 44808.9583 | 0 | 8.5638 | 39.95
2022-09-04 23:30 | 44808.9792 | 0 | 8.2025 | 39.95
2022-09-05 | 44809 | 0 | 7.7628 | 39.95
2022-09-05 00:30 | 44809.0208 | 0 | 7.7191 | 39.95
2022-09-05 01:00 | 44809.0417 | 0 | 7.6165 | 39.95
2022-09-05 01:30 | 44809.0625 | 0 | 7.4243 | 39.95
2022-09-05 02:00 | 44809.0833 | 0 | 7.2727 | 39.95
2022-09-05 02:30 | 44809.1042 | 0 | 7.3543 | 39.95
2022-09-05 03:00 | 44809.125 | 0 | 7.4517 | 39.95
2022-09-05 03:30 | 44809.1458 | 0 | 7.5339 | 39.95
2022-09-05 04:00 | 44809.1667 | 0 | 7.926 | 39.95
2022-09-05 04:30 | 44809.1875 | 0 | 8.4057 | 39.95
2022-09-05 05:00 | 44809.2083 | 0 | 9.082 | 39.95
2022-09-05 05:30 | 44809.2292 | 0 | 9.7451 | 39.95
2022-09-05 06:00 | 44809.25 | 0 | 11.0726 | 39.95
2022-09-05 06:30 | 44809.2708 | 0 | 11.8982 | 39.95
2022-09-05 07:00 | 44809.2917 | 0 | 11.9399 | 39.95
2022-09-05 07:30 | 44809.3125 | 0 | 11.3845 | 39.95
2022-09-05 08:00 | 44809.3333 | 0 | 10.4005 | 39.95
2022-09-05 08:30 | 44809.3542 | 0 | 9.5186 | 39.95
2022-09-05 09:00 | 44809.375 | 0 | 8.7654 | 39.95
2022-09-05 09:30 | 44809.3958 | 0 | 7.947 | 39.95
2022-09-05 10:00 | 44809.4167 | 0 | 7.5582 | 39.95
2022-09-05 10:30 | 44809.4375 | 0 | 9.4728 | 39.95
2022-09-05 11:00 | 44809.4583 | 0 | 9.7899 | 39.95
2022-09-05 11:30 | 44809.4792 | 0 | 10.0366 | 39.95
2022-09-05 12:00 | 44809.5 | 0 | 10.201 | 39.95
2022-09-05 12:30 | 44809.5208 | 0 | 9.4243 | 39.95
2022-09-05 13:00 | 44809.5417 | 0 | 7.5236 | 39.95
2022-09-05 13:30 | 44809.5625 | 0 | 10.6629 | 39.95
2022-09-05 14:00 | 44809.5833 | 0 | 12.4714 | 39.95
2022-09-05 14:30 | 44809.6042 | 0 | 11.4671 | 39.95
2022-09-05 15:00 | 44809.625 | 0 | 11.5414 | 39.95
2022-09-05 15:30 | 44809.6458 | 0 | 11.7761 | 39.95
2022-09-05 16:00 | 44809.6667 | 0 | 11.6189 | 39.95
2022-09-05 16:30 | 44809.6875 | 0 | 12.134 | 39.95
2022-09-05 17:00 | 44809.7083 | 0 | 12.9309 | 39.95
2022-09-05 17:30 | 44809.7292 | 0 | 13.8439 | 39.95
2022-09-05 18:00 | 44809.75 | 0 | 14.5088 | 39.95
2022-09-05 18:30 | 44809.7708 | 0 | 14.7598 | 39.95
2022-09-05 19:00 | 44809.7917 | 0 | 14.7068 | 39.95
2022-09-05 19:30 | 44809.8125 | 0 | 14.3346 | 39.95
2022-09-05 20:00 | 44809.8333 | 0 | 13.985 | 39.95
2022-09-05 20:30 | 44809.8542 | 0 | 13.1973 | 39.95
2022-09-05 21:00 | 44809.875 | 0 | 12.6511 | 39.95
2022-09-05 21:30 | 44809.8958 | 0 | 12.0648 | 39.95
2022-09-05 22:00 | 44809.9167 | 0 | 11.3902 | 39.95
2022-09-05 22:30 | 44809.9375 | 0 | 10.4723 | 39.95
2022-09-05 23:00 | 44809.9583 | 0 | 9.8865 | 39.95
2022-09-05 23:30 | 44809.9792 | 0 | 9.4556 | 39.95
2022-09-06 | 44810 | 0 | 8.7654 | 39.95
2022-09-06 00:30 | 44810.0208 | 0 | 8.375 | 39.95
2022-09-06 01:00 | 44810.0417 | 0 | 8.3289 | 39.95
2022-09-06 01:30 | 44810.0625 | 0 | 8.029 | 39.95
2022-09-06 02:00 | 44810.0833 | 0 | 7.9427 | 39.95
2022-09-06 02:30 | 44810.1042 | 0 | 7.9555 | 39.95
2022-09-06 03:00 | 44810.125 | 0 | 7.9171 | 39.95
2022-09-06 03:30 | 44810.1458 | 0 | 7.9781 | 39.95
2022-09-06 04:00 | 44810.1667 | 0 | 8.1461 | 39.95
2022-09-06 04:30 | 44810.1875 | 0 | 8.7473 | 39.95
2022-09-06 05:00 | 44810.2083 | 0 | 9.3638 | 39.95
2022-09-06 05:30 | 44810.2292 | 0 | 10.256 | 39.95
2022-09-06 06:00 | 44810.25 | 0 | 11.5559 | 39.95
2022-09-06 06:30 | 44810.2708 | 0 | 12.3292 | 39.95
2022-09-06 07:00 | 44810.2917 | 0 | 12.6631 | 39.95
2022-09-06 07:30 | 44810.3125 | 0 | 12.4029 | 39.95
2022-09-06 08:00 | 44810.3333 | 0 | 10.8916 | 39.95
2022-09-06 08:30 | 44810.3542 | 0 | 9.1304 | 39.95
2022-09-06 09:00 | 44810.375 | 0 | 8.0549 | 39.95
2022-09-06 09:30 | 44810.3958 | 0 | 7.6628 | 39.95
2022-09-06 10:00 | 44810.4167 | 0 | 7.7493 | 39.95
2022-09-06 10:30 | 44810.4375 | 0 | 7.6671 | 39.95
2022-09-06 11:00 | 44810.4583 | 0 | 7.3418 | 39.95
2022-09-06 11:30 | 44810.4792 | 0 | 7.5743 | 39.95
2022-09-06 12:00 | 44810.5 | 0 | 9.6496 | 39.95
2022-09-06 12:30 | 44810.5208 | 0 | 10.1301 | 39.95
2022-09-06 13:00 | 44810.5417 | 0 | 9.3607 | 39.95
2022-09-06 13:30 | 44810.5625 | 0 | 8.5367 | 39.95
2022-09-06 14:00 | 44810.5833 | 0 | 10.5541 | 39.95
2022-09-06 14:30 | 44810.6042 | 0 | 9.9628 | 39.95
2022-09-06 15:00 | 44810.625 | 0 | 10.334 | 39.95
2022-09-06 15:30 | 44810.6458 | 0 | 11.2031 | 39.95
2022-09-06 16:00 | 44810.6667 | 0 | 11.4162 | 39.95
2022-09-06 16:30 | 44810.6875 | 0 | 12.1719 | 39.95
2022-09-06 17:00 | 44810.7083 | 0 | 12.6784 | 39.95
2022-09-06 17:30 | 44810.7292 | 0 | 13.546 | 39.95
2022-09-06 18:00 | 44810.75 | 0 | 14.1389 | 39.95
2022-09-06 18:30 | 44810.7708 | 0 | 14.5153 | 39.95
2022-09-06 19:00 | 44810.7917 | 0 | 14.4951 | 39.95
2022-09-06 19:30 | 44810.8125 | 0 | 14.1934 | 39.95
2022-09-06 20:00 | 44810.8333 | 0 | 14.0425 | 39.95
2022-09-06 20:30 | 44810.8542 | 0 | 13.3149 | 39.95
2022-09-06 21:00 | 44810.875 | 0 | 12.7454 | 39.95
2022-09-06 21:30 | 44810.8958 | 0 | 12.2468 | 39.95
2022-09-06 22:00 | 44810.9167 | 0 | 11.6295 | 39.95
2022-09-06 22:30 | 44810.9375 | 0 | 10.7096 | 39.95
2022-09-06 23:00 | 44810.9583 | 0 | 10.1003 | 39.95
2022-09-06 23:30 | 44810.9792 | 0 | 9.5762 | 39.95
2022-09-07 | 44811 | 0 | 8.9669 | 39.95
2022-09-07 00:30 | 44811.0208 | 0 | 8.5305 | 39.95
2022-09-07 01:00 | 44811.0417 | 0 | 8.479 | 39.95
2022-09-07 01:30 | 44811.0625 | 0 | 8.3098 | 39.95
2022-09-07 02:00 | 44811.0833 | 0 | 8.2878 | 39.95
2022-09-07 02:30 | 44811.1042 | 0 | 8.2465 | 39.95
2022-09-07 03:00 | 44811.125 | 0 | 8.0511 | 39.95
2022-09-07 03:30 | 44811.1458 | 0 | 8.2238 | 39.95
2022-09-07 04:00 | 44811.1667 | 0 | 8.4631 | 39.95
2022-09-07 04:30 | 44811.1875 | 0 | 8.9116 | 39.95
2022-09-07 05:00 | 44811.2083 | 0 | 9.5187 | 39.95
2022-09-07 05:30 | 44811.2292 | 0 | 10.5518 | 39.95
2022-09-07 06:00 | 44811.25 | 0 | 11.852 | 39.95
2022-09-07 06:30 | 44811.2708 | 0 | 12.4074 | 39.95
2022-09-07 07:00 | 44811.2917 | 0 | 12.4754 | 39.95
2022-09-07 07:30 | 44811.3125 | 0 | 12.1336 | 39.95
2022-09-07 08:00 | 44811.3333 | 0 | 10.7113 | 39.95
2022-09-07 08:30 | 44811.3542 | 0 | 9.4522 | 39.95
2022-09-07 09:00 | 44811.375 | 0 | 8.7114 | 39.95
2022-09-07 09:30 | 44811.3958 | 0 | 8.6222 | 39.95
2022-09-07 10:00 | 44811.4167 | 0 | 10.2409 | 39.95
2022-09-07 10:30 | 44811.4375 | 0 | 9.7901 | 39.95
2022-09-07 11:00 | 44811.4583 | 0 | 9.9931 | 39.95
2022-09-07 11:30 | 44811.4792 | 0 | 11.4925 | 39.95
2022-09-07 12:00 | 44811.5 | 0 | 10.6057 | 39.95
2022-09-07 12:30 | 44811.5208 | 0 | 9.2239 | 39.95
2022-09-07 13:00 | 44811.5417 | 0 | 10.6419 | 39.95
2022-09-07 13:30 | 44811.5625 | 0 | 12.0566 | 39.95
2022-09-07 14:00 | 44811.5833 | 0 | 11.4551 | 39.95
2022-09-07 14:30 | 44811.6042 | 0 | 10.8259 | 39.95
2022-09-07 15:00 | 44811.625 | 0 | 11.334 | 39.95
2022-09-07 15:30 | 44811.6458 | 0 | 11.77 | 39.95
2022-09-07 16:00 | 44811.6667 | 0 | 11.1987 | 39.95
2022-09-07 16:30 | 44811.6875 | 0 | 11.4665 | 39.95
2022-09-07 17:00 | 44811.7083 | 0 | 12.6315 | 39.95
2022-09-07 17:30 | 44811.7292 | 0 | 13.602 | 39.95
2022-09-07 18:00 | 44811.75 | 0 | 14.5023 | 39.95
2022-09-07 18:30 | 44811.7708 | 0 | 14.8932 | 39.95
2022-09-07 19:00 | 44811.7917 | 0 | 14.6411 | 39.95
2022-09-07 19:30 | 44811.8125 | 0 | 14.3167 | 39.95
2022-09-07 20:00 | 44811.8333 | 0 | 14.1148 | 39.95
2022-09-07 20:30 | 44811.8542 | 0 | 13.5657 | 39.95
2022-09-07 21:00 | 44811.875 | 0 | 13.0053 | 39.95
2022-09-07 21:30 | 44811.8958 | 0 | 12.5626 | 39.95
2022-09-07 22:00 | 44811.9167 | 0 | 11.8978 | 39.95
2022-09-07 22:30 | 44811.9375 | 0 | 10.8925 | 39.95
2022-09-07 23:00 | 44811.9583 | 0 | 10.3047 | 39.95
2022-09-07 23:30 | 44811.9792 | 0 | 9.771 | 39.95
2022-09-08 | 44812 | 0 | 9.1058 | 39.95
2022-09-08 00:30 | 44812.0208 | 0 | 8.765 | 39.95
2022-09-08 01:00 | 44812.0417 | 0 | 8.6338 | 39.95
2022-09-08 01:30 | 44812.0625 | 0 | 8.3768 | 39.95
2022-09-08 02:00 | 44812.0833 | 0 | 8.3673 | 39.95
2022-09-08 02:30 | 44812.1042 | 0 | 8.2653 | 39.95
2022-09-08 03:00 | 44812.125 | 0 | 8.1133 | 39.95
2022-09-08 03:30 | 44812.1458 | 0 | 8.2273 | 39.95
2022-09-08 04:00 | 44812.1667 | 0 | 8.6811 | 39.95
2022-09-08 04:30 | 44812.1875 | 0 | 9.0372 | 39.95
2022-09-08 05:00 | 44812.2083 | 0 | 9.8056 | 39.95
2022-09-08 05:30 | 44812.2292 | 0 | 10.5267 | 39.95
2022-09-08 06:00 | 44812.25 | 0 | 11.9984 | 39.95
2022-09-08 06:30 | 44812.2708 | 0 | 12.8497 | 39.95
2022-09-08 07:00 | 44812.2917 | 0 | 13.4121 | 39.95
2022-09-08 07:30 | 44812.3125 | 0 | 14.0577 | 39.95
2022-09-08 08:00 | 44812.3333 | 0 | 13.6532 | 39.95
2022-09-08 08:30 | 44812.3542 | 0 | 11.0024 | 39.95
2022-09-08 09:00 | 44812.375 | 0 | 9.5794 | 39.95
2022-09-08 09:30 | 44812.3958 | 0 | 8.9051 | 39.95
2022-09-08 10:00 | 44812.4167 | 0 | 8.261 | 39.95
2022-09-08 10:30 | 44812.4375 | 0 | 9.2774 | 39.95
2022-09-08 11:00 | 44812.4583 | 0 | 8.6397 | 39.95
2022-09-08 11:30 | 44812.4792 | 0 | 10.4096 | 39.95
2022-09-08 12:00 | 44812.5 | 0 | 11.1011 | 39.95
2022-09-08 12:30 | 44812.5208 | 0 | 10.5936 | 39.95
2022-09-08 13:00 | 44812.5417 | 0 | 9.2369 | 39.95
2022-09-08 13:30 | 44812.5625 | 0 | 9.2877 | 39.95
2022-09-08 14:00 | 44812.5833 | 0 | 8.6304 | 39.95
2022-09-08 14:30 | 44812.6042 | 0 | 9.877 | 39.95
2022-09-08 15:00 | 44812.625 | 0 | 11.5698 | 39.95
2022-09-08 15:30 | 44812.6458 | 0 | 11.7249 | 39.95
2022-09-08 16:00 | 44812.6667 | 0 | 11.8817 | 39.95
2022-09-08 16:30 | 44812.6875 | 0 | 12.4899 | 39.95
2022-09-08 17:00 | 44812.7083 | 0 | 13.0339 | 39.95
2022-09-08 17:30 | 44812.7292 | 0 | 13.9177 | 39.95
2022-09-08 18:00 | 44812.75 | 0 | 14.3831 | 39.95
2022-09-08 18:30 | 44812.7708 | 0 | 14.6702 | 39.95
2022-09-08 19:00 | 44812.7917 | 0 | 14.3439 | 39.95
2022-09-08 19:30 | 44812.8125 | 0 | 14.0407 | 39.95
2022-09-08 20:00 | 44812.8333 | 0 | 13.8249 | 39.95
2022-09-08 20:30 | 44812.8542 | 0 | 13.4457 | 39.95
2022-09-08 21:00 | 44812.875 | 0 | 12.7704 | 39.95
2022-09-08 21:30 | 44812.8958 | 0 | 12.2392 | 39.95
2022-09-08 22:00 | 44812.9167 | 0 | 11.5787 | 39.95
2022-09-08 22:30 | 44812.9375 | 0 | 10.8026 | 39.95
2022-09-08 23:00 | 44812.9583 | 0 | 10.2655 | 39.95
2022-09-08 23:30 | 44812.9792 | 0 | 9.5561 | 39.95
2022-09-09 | 44813 | 0 | 8.9546 | 39.95
2022-09-09 00:30 | 44813.0208 | 0 | 8.5034 | 39.95
2022-09-09 01:00 | 44813.0417 | 0 | 8.3917 | 39.95
2022-09-09 01:30 | 44813.0625 | 0 | 8.1511 | 39.95
2022-09-09 02:00 | 44813.0833 | 0 | 8.1624 | 39.95
2022-09-09 02:30 | 44813.1042 | 0 | 8.1764 | 39.95
2022-09-09 03:00 | 44813.125 | 0 | 8.1276 | 39.95
2022-09-09 03:30 | 44813.1458 | 0 | 8.0749 | 39.95
2022-09-09 04:00 | 44813.1667 | 0 | 8.4592 | 39.95
2022-09-09 04:30 | 44813.1875 | 0 | 8.8564 | 39.95
2022-09-09 05:00 | 44813.2083 | 0 | 9.6974 | 39.95
2022-09-09 05:30 | 44813.2292 | 0 | 10.2593 | 39.95
2022-09-09 06:00 | 44813.25 | 0 | 11.1762 | 39.95
2022-09-09 06:30 | 44813.2708 | 0 | 12.4218 | 39.95
2022-09-09 07:00 | 44813.2917 | 0 | 13.645 | 39.95
2022-09-09 07:30 | 44813.3125 | 0 | 14.3673 | 39.95
2022-09-09 08:00 | 44813.3333 | 0 | 14.3393 | 39.95
2022-09-09 08:30 | 44813.3542 | 0 | 14.1845 | 39.95
2022-09-09 09:00 | 44813.375 | 0 | 14.083 | 39.95
2022-09-09 09:30 | 44813.3958 | 0 | 13.3474 | 39.95
2022-09-09 10:00 | 44813.4167 | 0 | 12.6594 | 39.95
2022-09-09 10:30 | 44813.4375 | 0 | 12.464 | 39.95
2022-09-09 11:00 | 44813.4583 | 0 | 12.7819 | 39.95
2022-09-09 11:30 | 44813.4792 | 0 | 11.6152 | 39.95
2022-09-09 12:00 | 44813.5 | 0 | 8.706 | 39.95
2022-09-09 12:30 | 44813.5208 | 0 | 8.1881 | 39.95
2022-09-09 13:00 | 44813.5417 | 0 | 7.1512 | 39.95
2022-09-09 13:30 | 44813.5625 | 0 | 7.7611 | 39.95
2022-09-09 14:00 | 44813.5833 | 0 | 8.641 | 39.95
2022-09-09 14:30 | 44813.6042 | 0 | 9.3858 | 39.95
2022-09-09 15:00 | 44813.625 | 0 | 9.5827 | 39.95
2022-09-09 15:30 | 44813.6458 | 0 | 10.6708 | 39.95
2022-09-09 16:00 | 44813.6667 | 0 | 10.9292 | 39.95
2022-09-09 16:30 | 44813.6875 | 0 | 11.6822 | 39.95
2022-09-09 17:00 | 44813.7083 | 0 | 12.4688 | 39.95
2022-09-09 17:30 | 44813.7292 | 0 | 12.9295 | 39.95
2022-09-09 18:00 | 44813.75 | 0 | 13.5401 | 39.95
2022-09-09 18:30 | 44813.7708 | 0 | 13.6292 | 39.95
2022-09-09 19:00 | 44813.7917 | 0 | 13.5675 | 39.95
2022-09-09 19:30 | 44813.8125 | 0 | 13.0118 | 39.95
2022-09-09 20:00 | 44813.8333 | 0 | 12.8515 | 39.95
2022-09-09 20:30 | 44813.8542 | 0 | 12.4 | 39.95
2022-09-09 21:00 | 44813.875 | 0 | 12.1722 | 39.95
2022-09-09 21:30 | 44813.8958 | 0 | 12.0844 | 39.95
2022-09-09 22:00 | 44813.9167 | 0 | 11.4287 | 39.95
2022-09-09 22:30 | 44813.9375 | 0 | 10.5235 | 39.95
2022-09-09 23:00 | 44813.9583 | 0 | 10.0099 | 39.95
2022-09-09 23:30 | 44813.9792 | 0 | 9.5068 | 39.95
2022-09-10 | 44814 | 0 | 9.0799 | 39.95
2022-09-10 00:30 | 44814.0208 | 0 | 8.6839 | 39.95
2022-09-10 01:00 | 44814.0417 | 0 | 8.4325 | 39.95
2022-09-10 01:30 | 44814.0625 | 0 | 8.1943 | 39.95
2022-09-10 02:00 | 44814.0833 | 0 | 8.0323 | 39.95
2022-09-10 02:30 | 44814.1042 | 0 | 7.9129 | 39.95
2022-09-10 03:00 | 44814.125 | 0 | 7.795 | 39.95
2022-09-10 03:30 | 44814.1458 | 0 | 7.711 | 39.95
2022-09-10 04:00 | 44814.1667 | 0 | 7.7768 | 39.95
2022-09-10 04:30 | 44814.1875 | 0 | 7.8414 | 39.95
2022-09-10 05:00 | 44814.2083 | 0 | 8.0575 | 39.95
2022-09-10 05:30 | 44814.2292 | 0 | 8.3097 | 39.95
2022-09-10 06:00 | 44814.25 | 0 | 8.618 | 39.95
2022-09-10 06:30 | 44814.2708 | 0 | 8.4736 | 39.95
2022-09-10 07:00 | 44814.2917 | 0 | 8.336 | 39.95
2022-09-10 07:30 | 44814.3125 | 0 | 7.8319 | 39.95
2022-09-10 08:00 | 44814.3333 | 0 | 7.8964 | 39.95
2022-09-10 08:30 | 44814.3542 | 0 | 6.9809 | 39.95
2022-09-10 09:00 | 44814.375 | 0 | 6.4539 | 39.95
2022-09-10 09:30 | 44814.3958 | 0 | 6.0356 | 39.95
2022-09-10 10:00 | 44814.4167 | 0 | 5.7403 | 39.95
2022-09-10 10:30 | 44814.4375 | 0 | 6.3395 | 39.95
2022-09-10 11:00 | 44814.4583 | 0 | 5.168 | 39.95
2022-09-10 11:30 | 44814.4792 | 0 | 4.6141 | 39.95
2022-09-10 12:00 | 44814.5 | 0 | 4.8794 | 39.95
2022-09-10 12:30 | 44814.5208 | 0 | 5.4992 | 39.95
2022-09-10 13:00 | 44814.5417 | 0 | 6.5969 | 39.95
2022-09-10 13:30 | 44814.5625 | 0 | 6.9479 | 39.95
2022-09-10 14:00 | 44814.5833 | 0 | 7.8667 | 39.95
2022-09-10 14:30 | 44814.6042 | 0 | 7.5905 | 39.95
2022-09-10 15:00 | 44814.625 | 0 | 7.0447 | 39.95
2022-09-10 15:30 | 44814.6458 | 0 | 7.919 | 39.95
2022-09-10 16:00 | 44814.6667 | 0 | 8.9847 | 39.95
2022-09-10 16:30 | 44814.6875 | 0 | 9.8888 | 39.95
2022-09-10 17:00 | 44814.7083 | 0 | 10.6351 | 39.95
2022-09-10 17:30 | 44814.7292 | 0 | 10.9623 | 39.95
2022-09-10 18:00 | 44814.75 | 0 | 11.4108 | 39.95
2022-09-10 18:30 | 44814.7708 | 0 | 11.521 | 39.95
2022-09-10 19:00 | 44814.7917 | 0 | 11.0859 | 39.95
2022-09-10 19:30 | 44814.8125 | 0 | 10.8739 | 39.95
2022-09-10 20:00 | 44814.8333 | 0 | 10.8942 | 39.95
2022-09-10 20:30 | 44814.8542 | 0 | 10.4433 | 39.95
2022-09-10 21:00 | 44814.875 | 0 | 10.1024 | 39.95
2022-09-10 21:30 | 44814.8958 | 0 | 9.8859 | 39.95
2022-09-10 22:00 | 44814.9167 | 0 | 9.5835 | 39.95
2022-09-10 22:30 | 44814.9375 | 0 | 9.1367 | 39.95
2022-09-10 23:00 | 44814.9583 | 0 | 8.8276 | 39.95
2022-09-10 23:30 | 44814.9792 | 0 | 8.35 | 39.95
2022-09-11 | 44815 | 0 | 7.8417 | 39.95
2022-09-11 00:30 | 44815.0208 | 0 | 7.4175 | 39.95
2022-09-11 01:00 | 44815.0417 | 0 | 7.4079 | 39.95
2022-09-11 01:30 | 44815.0625 | 0 | 7.2667 | 39.95
2022-09-11 02:00 | 44815.0833 | 0 | 7.1649 | 39.95
2022-09-11 02:30 | 44815.1042 | 0 | 7.0678 | 39.95
2022-09-11 03:00 | 44815.125 | 0 | 6.9999 | 39.95
2022-09-11 03:30 | 44815.1458 | 0 | 7.0339 | 39.95
2022-09-11 04:00 | 44815.1667 | 0 | 6.969 | 39.95
2022-09-11 04:30 | 44815.1875 | 0 | 7.0026 | 39.95
2022-09-11 05:00 | 44815.2083 | 0 | 7.2102 | 39.95
2022-09-11 05:30 | 44815.2292 | 0 | 7.2075 | 39.95
2022-09-11 06:00 | 44815.25 | 0 | 7.3859 | 39.95
2022-09-11 06:30 | 44815.2708 | 0 | 6.9919 | 39.95
2022-09-11 07:00 | 44815.2917 | 0 | 7.0927 | 39.95
2022-09-11 07:30 | 44815.3125 | 0 | 6.8082 | 39.95
2022-09-11 08:00 | 44815.3333 | 0 | 6.8973 | 39.95
2022-09-11 08:30 | 44815.3542 | 0 | 6.0368 | 39.95
2022-09-11 09:00 | 44815.375 | 0 | 5.4253 | 39.95
2022-09-11 09:30 | 44815.3958 | 0 | 4.8202 | 39.95
2022-09-11 10:00 | 44815.4167 | 0 | 5.1005 | 39.95
2022-09-11 10:30 | 44815.4375 | 0 | 4.7407 | 39.95
2022-09-11 11:00 | 44815.4583 | 0 | 4.0199 | 39.95
2022-09-11 11:30 | 44815.4792 | 0 | 3.9454 | 39.95
2022-09-11 12:00 | 44815.5 | 0 | 5.2645 | 39.95
2022-09-11 12:30 | 44815.5208 | 0 | 3.9226 | 39.95
2022-09-11 13:00 | 44815.5417 | 0 | 4.1113 | 39.95
2022-09-11 13:30 | 44815.5625 | 0 | 4.4675 | 39.95
2022-09-11 14:00 | 44815.5833 | 0 | 4.9727 | 39.95
2022-09-11 14:30 | 44815.6042 | 0 | 5.5047 | 39.95
2022-09-11 15:00 | 44815.625 | 0 | 6.2269 | 39.95
2022-09-11 15:30 | 44815.6458 | 0 | 7.6423 | 39.95
2022-09-11 16:00 | 44815.6667 | 0 | 8.6615 | 39.95
2022-09-11 16:30 | 44815.6875 | 0 | 9.3669 | 39.95
2022-09-11 17:00 | 44815.7083 | 0 | 10.1033 | 39.95
2022-09-11 17:30 | 44815.7292 | 0 | 10.9847 | 39.95
2022-09-11 18:00 | 44815.75 | 0 | 11.7675 | 39.95
2022-09-11 18:30 | 44815.7708 | 0 | 11.8485 | 39.95
2022-09-11 19:00 | 44815.7917 | 0 | 11.6504 | 39.95
2022-09-11 19:30 | 44815.8125 | 0 | 11.1645 | 39.95
2022-09-11 20:00 | 44815.8333 | 0 | 10.9216 | 39.95
2022-09-11 20:30 | 44815.8542 | 0 | 10.3157 | 39.95
2022-09-11 21:00 | 44815.875 | 0 | 9.9806 | 39.95
2022-09-11 21:30 | 44815.8958 | 0 | 9.6115 | 39.95
2022-09-11 22:00 | 44815.9167 | 0 | 9.2575 | 39.95
2022-09-11 22:30 | 44815.9375 | 0 | 8.6454 | 39.95
2022-09-11 23:00 | 44815.9583 | 0 | 8.2922 | 39.95
2022-09-11 23:30 | 44815.9792 | 0 | 7.9016 | 39.95
2022-09-12 | 44816 | 0 | 7.5415 | 39.95
2022-09-12 00:30 | 44816.0208 | 0 | 7.3436 | 39.95
2022-09-12 01:00 | 44816.0417 | 0 | 7.237 | 39.95
2022-09-12 01:30 | 44816.0625 | 0 | 7.15 | 39.95
2022-09-12 02:00 | 44816.0833 | 0 | 7.1938 | 39.95
2022-09-12 02:30 | 44816.1042 | 0 | 7.2146 | 39.95
2022-09-12 03:00 | 44816.125 | 0 | 7.1027 | 39.95
2022-09-12 03:30 | 44816.1458 | 0 | 7.2316 | 39.95
2022-09-12 04:00 | 44816.1667 | 0 | 7.6285 | 39.95
2022-09-12 04:30 | 44816.1875 | 0 | 7.9679 | 39.95
2022-09-12 05:00 | 44816.2083 | 0 | 8.6195 | 39.95
2022-09-12 05:30 | 44816.2292 | 0 | 9.2303 | 39.95
2022-09-12 06:00 | 44816.25 | 0 | 9.9802 | 39.95
2022-09-12 06:30 | 44816.2708 | 0 | 10.8961 | 39.95
2022-09-12 07:00 | 44816.2917 | 0 | 11.7243 | 39.95
2022-09-12 07:30 | 44816.3125 | 0 | 11.7301 | 39.95
2022-09-12 08:00 | 44816.3333 | 0 | 11.5528 | 39.95
2022-09-12 08:30 | 44816.3542 | 0 | 11.6779 | 39.95
2022-09-12 09:00 | 44816.375 | 0 | 12.177 | 39.95
2022-09-12 09:30 | 44816.3958 | 0 | 11.1224 | 39.95
2022-09-12 10:00 | 44816.4167 | 0 | 10.5118 | 39.95
2022-09-12 10:30 | 44816.4375 | 0 | 8.9343 | 39.95
2022-09-12 11:00 | 44816.4583 | 0 | 9.0246 | 39.95
2022-09-12 11:30 | 44816.4792 | 0 | 9.4446 | 39.95
2022-09-12 12:00 | 44816.5 | 0 | 9.23 | 39.95
2022-09-12 12:30 | 44816.5208 | 0 | 10.0464 | 39.95
2022-09-12 13:00 | 44816.5417 | 0 | 7.7295 | 39.95
2022-09-12 13:30 | 44816.5625 | 0 | 8.6736 | 39.95
2022-09-12 14:00 | 44816.5833 | 0 | 8.4094 | 39.95
2022-09-12 14:30 | 44816.6042 | 0 | 10.0142 | 39.95
2022-09-12 15:00 | 44816.625 | 0 | 10.5797 | 39.95
2022-09-12 15:30 | 44816.6458 | 0 | 10.1159 | 39.95
2022-09-12 16:00 | 44816.6667 | 0 | 10.0297 | 39.95
2022-09-12 16:30 | 44816.6875 | 0 | 11.4703 | 39.95
2022-09-12 17:00 | 44816.7083 | 0 | 12.2658 | 39.95
2022-09-12 17:30 | 44816.7292 | 0 | 12.8694 | 39.95
2022-09-12 18:00 | 44816.75 | 0 | 13.4677 | 39.95
2022-09-12 18:30 | 44816.7708 | 0 | 13.907 | 39.95
2022-09-12 19:00 | 44816.7917 | 0 | 13.5937 | 39.95
2022-09-12 19:30 | 44816.8125 | 0 | 12.984 | 39.95
2022-09-12 20:00 | 44816.8333 | 0 | 12.7952 | 39.95
2022-09-12 20:30 | 44816.8542 | 0 | 12.0802 | 39.95
2022-09-12 21:00 | 44816.875 | 0 | 11.6136 | 39.95
2022-09-12 21:30 | 44816.8958 | 0 | 11.5653 | 39.95
2022-09-12 22:00 | 44816.9167 | 0 | 10.8726 | 39.95
2022-09-12 22:30 | 44816.9375 | 0 | 10.066 | 39.95
2022-09-12 23:00 | 44816.9583 | 0 | 9.4895 | 39.95
2022-09-12 23:30 | 44816.9792 | 0 | 9.0328 | 39.95
2022-09-13 | 44817 | 0 | 8.4057 | 39.95
2022-09-13 00:30 | 44817.0208 | 0 | 8.0376 | 39.95
2022-09-13 01:00 | 44817.0417 | 0 | 7.8656 | 39.95
2022-09-13 01:30 | 44817.0625 | 0 | 7.7208 | 39.95
2022-09-13 02:00 | 44817.0833 | 0 | 7.6549 | 39.95
2022-09-13 02:30 | 44817.1042 | 0 | 7.7339 | 39.95
2022-09-13 03:00 | 44817.125 | 0 | 7.6131 | 39.95
2022-09-13 03:30 | 44817.1458 | 0 | 7.6869 | 39.95
2022-09-13 04:00 | 44817.1667 | 0 | 7.9528 | 39.95
2022-09-13 04:30 | 44817.1875 | 0 | 8.3168 | 39.95
2022-09-13 05:00 | 44817.2083 | 0 | 9.1465 | 39.95
2022-09-13 05:30 | 44817.2292 | 0 | 9.7935 | 39.95
2022-09-13 06:00 | 44817.25 | 0 | 10.5905 | 39.95
2022-09-13 06:30 | 44817.2708 | 0 | 11.1639 | 39.95
2022-09-13 07:00 | 44817.2917 | 0 | 11.1487 | 39.95
2022-09-13 07:30 | 44817.3125 | 0 | 10.3812 | 39.95
2022-09-13 08:00 | 44817.3333 | 0 | 9.5073 | 39.95
2022-09-13 08:30 | 44817.3542 | 0 | 8.5183 | 39.95
2022-09-13 09:00 | 44817.375 | 0 | 7.7947 | 39.95
2022-09-13 09:30 | 44817.3958 | 0 | 7.3679 | 39.95
2022-09-13 10:00 | 44817.4167 | 0 | 6.9898 | 39.95
2022-09-13 10:30 | 44817.4375 | 0 | 6.8761 | 39.95
2022-09-13 11:00 | 44817.4583 | 0 | 6.7114 | 39.95
2022-09-13 11:30 | 44817.4792 | 0 | 6.7704 | 39.95
2022-09-13 12:00 | 44817.5 | 0 | 6.715 | 39.95
2022-09-13 12:30 | 44817.5208 | 0 | 6.9899 | 39.95
2022-09-13 13:00 | 44817.5417 | 0 | 7.2402 | 39.95
2022-09-13 13:30 | 44817.5625 | 0 | 7.5864 | 39.95
2022-09-13 14:00 | 44817.5833 | 0 | 8.1842 | 39.95
2022-09-13 14:30 | 44817.6042 | 0 | 8.5182 | 39.95
2022-09-13 15:00 | 44817.625 | 0 | 9.2616 | 39.95
2022-09-13 15:30 | 44817.6458 | 0 | 9.9554 | 39.95
2022-09-13 16:00 | 44817.6667 | 0 | 10.8987 | 39.95
2022-09-13 16:30 | 44817.6875 | 0 | 11.6358 | 39.95
2022-09-13 17:00 | 44817.7083 | 0 | 12.439 | 39.95
2022-09-13 17:30 | 44817.7292 | 0 | 13.1664 | 39.95
2022-09-13 18:00 | 44817.75 | 0 | 13.6158 | 39.95
2022-09-13 18:30 | 44817.7708 | 0 | 13.6768 | 39.95
2022-09-13 19:00 | 44817.7917 | 0 | 13.2308 | 39.95
2022-09-13 19:30 | 44817.8125 | 0 | 13.1513 | 39.95
2022-09-13 20:00 | 44817.8333 | 0 | 12.7665 | 39.95
2022-09-13 20:30 | 44817.8542 | 0 | 12.317 | 39.95
2022-09-13 21:00 | 44817.875 | 0 | 11.8622 | 39.95
2022-09-13 21:30 | 44817.8958 | 0 | 11.4227 | 39.95
2022-09-13 22:00 | 44817.9167 | 0 | 10.9418 | 39.95
2022-09-13 22:30 | 44817.9375 | 0 | 10.1701 | 39.95
2022-09-13 23:00 | 44817.9583 | 0 | 9.7338 | 39.95
2022-09-13 23:30 | 44817.9792 | 0 | 9.2016 | 39.95
2022-09-14 | 44818 | 0 | 8.6038 | 39.95
2022-09-14 00:30 | 44818.0208 | 0 | 8.3307 | 39.95
2022-09-14 01:00 | 44818.0417 | 0 | 8.2384 | 39.95
2022-09-14 01:30 | 44818.0625 | 0 | 8.1795 | 39.95
2022-09-14 02:00 | 44818.0833 | 0 | 8.0761 | 39.95
2022-09-14 02:30 | 44818.1042 | 0 | 8.001 | 39.95
2022-09-14 03:00 | 44818.125 | 0 | 7.979 | 39.95
2022-09-14 03:30 | 44818.1458 | 0 | 8.0436 | 39.95
2022-09-14 04:00 | 44818.1667 | 0 | 8.2244 | 39.95
2022-09-14 04:30 | 44818.1875 | 0 | 8.6116 | 39.95
2022-09-14 05:00 | 44818.2083 | 0 | 9.2025 | 39.95
2022-09-14 05:30 | 44818.2292 | 0 | 9.7702 | 39.95
2022-09-14 06:00 | 44818.25 | 0 | 10.4635 | 39.95
2022-09-14 06:30 | 44818.2708 | 0 | 11.2321 | 39.95
2022-09-14 07:00 | 44818.2917 | 0 | 11.4386 | 39.95
2022-09-14 07:30 | 44818.3125 | 0 | 10.7277 | 39.95
2022-09-14 08:00 | 44818.3333 | 0 | 9.9242 | 39.95
2022-09-14 08:30 | 44818.3542 | 0 | 9.1439 | 39.95
2022-09-14 09:00 | 44818.375 | 0 | 8.4135 | 39.95
2022-09-14 09:30 | 44818.3958 | 0 | 7.8859 | 39.95
2022-09-14 10:00 | 44818.4167 | 0 | 8.0072 | 39.95
2022-09-14 10:30 | 44818.4375 | 0 | 9.8815 | 39.95
2022-09-14 11:00 | 44818.4583 | 0 | 8.1957 | 39.95
2022-09-14 11:30 | 44818.4792 | 0 | 9.6826 | 39.95
2022-09-14 12:00 | 44818.5 | 0 | 8.7004 | 39.95
2022-09-14 12:30 | 44818.5208 | 0 | 7.2015 | 39.95
2022-09-14 13:00 | 44818.5417 | 0 | 8.8945 | 39.95
2022-09-14 13:30 | 44818.5625 | 0 | 8.9286 | 39.95
2022-09-14 14:00 | 44818.5833 | 0 | 8.2057 | 39.95
2022-09-14 14:30 | 44818.6042 | 0 | 8.5804 | 39.95
2022-09-14 15:00 | 44818.625 | 0 | 8.9923 | 39.95
2022-09-14 15:30 | 44818.6458 | 0 | 10.0487 | 39.95
2022-09-14 16:00 | 44818.6667 | 0 | 10.9062 | 39.95
2022-09-14 16:30 | 44818.6875 | 0 | 11.6183 | 39.95
2022-09-14 17:00 | 44818.7083 | 0 | 12.348 | 39.95
2022-09-14 17:30 | 44818.7292 | 0 | 13.0472 | 39.95
2022-09-14 18:00 | 44818.75 | 0 | 13.4993 | 39.95
2022-09-14 18:30 | 44818.7708 | 0 | 13.8063 | 39.95
2022-09-14 19:00 | 44818.7917 | 0 | 13.4416 | 39.95
2022-09-14 19:30 | 44818.8125 | 0 | 12.9848 | 39.95
2022-09-14 20:00 | 44818.8333 | 0 | 12.8595 | 39.95
2022-09-14 20:30 | 44818.8542 | 0 | 12.4283 | 39.95
2022-09-14 21:00 | 44818.875 | 0 | 11.9123 | 39.95
2022-09-14 21:30 | 44818.8958 | 0 | 11.5758 | 39.95
2022-09-14 22:00 | 44818.9167 | 0 | 10.8615 | 39.95
2022-09-14 22:30 | 44818.9375 | 0 | 10.2845 | 39.95
2022-09-14 23:00 | 44818.9583 | 0 | 9.7648 | 39.95
2022-09-14 23:30 | 44818.9792 | 0 | 9.2987 | 39.95
2022-09-15 | 44819 | 0 | 8.6046 | 39.95
2022-09-15 00:30 | 44819.0208 | 0 | 8.3134 | 39.95
2022-09-15 01:00 | 44819.0417 | 0 | 8.1068 | 39.95
2022-09-15 01:30 | 44819.0625 | 0 | 7.9966 | 39.95
2022-09-15 02:00 | 44819.0833 | 0 | 7.9513 | 39.95
2022-09-15 02:30 | 44819.1042 | 0 | 7.9123 | 39.95
2022-09-15 03:00 | 44819.125 | 0 | 7.7911 | 39.95
2022-09-15 03:30 | 44819.1458 | 0 | 7.7357 | 39.95
2022-09-15 04:00 | 44819.1667 | 0 | 8.1791 | 39.95
2022-09-15 04:30 | 44819.1875 | 0 | 8.4806 | 39.95
2022-09-15 05:00 | 44819.2083 | 0 | 9.1565 | 39.95
2022-09-15 05:30 | 44819.2292 | 0 | 9.7186 | 39.95
2022-09-15 06:00 | 44819.25 | 0 | 10.654 | 39.95
2022-09-15 06:30 | 44819.2708 | 0 | 11.471 | 39.95
2022-09-15 07:00 | 44819.2917 | 0 | 11.7747 | 39.95
2022-09-15 07:30 | 44819.3125 | 0 | 10.6537 | 39.95
2022-09-15 08:00 | 44819.3333 | 0 | 10.0691 | 39.95
2022-09-15 08:30 | 44819.3542 | 0 | 10.0424 | 39.95
2022-09-15 09:00 | 44819.375 | 0 | 11.8267 | 39.95
2022-09-15 09:30 | 44819.3958 | 0 | 10.026 | 39.95
2022-09-15 10:00 | 44819.4167 | 0 | 9.6911 | 39.95
2022-09-15 10:30 | 44819.4375 | 0 | 8.4015 | 39.95
2022-09-15 11:00 | 44819.4583 | 0 | 9.0373 | 39.95
2022-09-15 11:30 | 44819.4792 | 0 | 10.7376 | 39.95
2022-09-15 12:00 | 44819.5 | 0 | 10.6623 | 39.95
2022-09-15 12:30 | 44819.5208 | 0 | 10.2616 | 39.95
2022-09-15 13:00 | 44819.5417 | 0 | 9.3135 | 39.95
2022-09-15 13:30 | 44819.5625 | 0 | 9.0609 | 39.95
2022-09-15 14:00 | 44819.5833 | 0 | 9.6982 | 39.95
2022-09-15 14:30 | 44819.6042 | 0 | 11.3223 | 39.95
2022-09-15 15:00 | 44819.625 | 0 | 11.5743 | 39.95
2022-09-15 15:30 | 44819.6458 | 0 | 11.609 | 39.95
2022-09-15 16:00 | 44819.6667 | 0 | 12.2573 | 39.95
2022-09-15 16:30 | 44819.6875 | 0 | 12.6385 | 39.95
2022-09-15 17:00 | 44819.7083 | 0 | 12.9102 | 39.95
2022-09-15 17:30 | 44819.7292 | 0 | 13.3334 | 39.95
2022-09-15 18:00 | 44819.75 | 0 | 13.6517 | 39.95
2022-09-15 18:30 | 44819.7708 | 0 | 13.7668 | 39.95
2022-09-15 19:00 | 44819.7917 | 0 | 13.5411 | 39.95
2022-09-15 19:30 | 44819.8125 | 0 | 13.2784 | 39.95
2022-09-15 20:00 | 44819.8333 | 0 | 13.0152 | 39.95
2022-09-15 20:30 | 44819.8542 | 0 | 12.6348 | 39.95
2022-09-15 21:00 | 44819.875 | 0 | 11.961 | 39.95
2022-09-15 21:30 | 44819.8958 | 0 | 11.5216 | 39.95
2022-09-15 22:00 | 44819.9167 | 0 | 11.2052 | 39.95
2022-09-15 22:30 | 44819.9375 | 0 | 10.628 | 39.95
2022-09-15 23:00 | 44819.9583 | 0 | 9.9413 | 39.95
2022-09-15 23:30 | 44819.9792 | 0 | 9.3812 | 39.95
2022-09-16 | 44820 | 0 | 8.8408 | 39.95
2022-09-16 00:30 | 44820.0208 | 0 | 8.517 | 39.95
2022-09-16 01:00 | 44820.0417 | 0 | 8.2917 | 39.95
2022-09-16 01:30 | 44820.0625 | 0 | 8.1972 | 39.95
2022-09-16 02:00 | 44820.0833 | 0 | 8.0666 | 39.95
2022-09-16 02:30 | 44820.1042 | 0 | 8.1268 | 39.95
2022-09-16 03:00 | 44820.125 | 0 | 8.0249 | 39.95
2022-09-16 03:30 | 44820.1458 | 0 | 8.0633 | 39.95
2022-09-16 04:00 | 44820.1667 | 0 | 8.3861 | 39.95
2022-09-16 04:30 | 44820.1875 | 0 | 8.6642 | 39.95
2022-09-16 05:00 | 44820.2083 | 0 | 9.3024 | 39.95
2022-09-16 05:30 | 44820.2292 | 0 | 9.9644 | 39.95
2022-09-16 06:00 | 44820.25 | 0 | 10.8682 | 39.95
2022-09-16 06:30 | 44820.2708 | 0 | 11.8405 | 39.95
2022-09-16 07:00 | 44820.2917 | 0 | 12.4012 | 39.95
2022-09-16 07:30 | 44820.3125 | 0 | 13.4365 | 39.95
2022-09-16 08:00 | 44820.3333 | 0 | 12.2591 | 39.95
2022-09-16 08:30 | 44820.3542 | 0 | 10.8314 | 39.95
2022-09-16 09:00 | 44820.375 | 0 | 9.9375 | 39.95
2022-09-16 09:30 | 44820.3958 | 0 | 10.1542 | 39.95
2022-09-16 10:00 | 44820.4167 | 0 | 8.8188 | 39.95
2022-09-16 10:30 | 44820.4375 | 0 | 12.0574 | 39.95
2022-09-16 11:00 | 44820.4583 | 0 | 12.5227 | 39.95
2022-09-16 11:30 | 44820.4792 | 0 | 12.71 | 39.95
2022-09-16 12:00 | 44820.5 | 0 | 12.2629 | 39.95
2022-09-16 12:30 | 44820.5208 | 0 | 11.5161 | 39.95
2022-09-16 13:00 | 44820.5417 | 0 | 11.4613 | 39.95
2022-09-16 13:30 | 44820.5625 | 0 | 11.3591 | 39.95
2022-09-16 14:00 | 44820.5833 | 0 | 11.6314 | 39.95
2022-09-16 14:30 | 44820.6042 | 0 | 10.9532 | 39.95
2022-09-16 15:00 | 44820.625 | 0 | 11.1112 | 39.95
2022-09-16 15:30 | 44820.6458 | 0 | 11.9487 | 39.95
2022-09-16 16:00 | 44820.6667 | 0 | 10.9996 | 39.95
2022-09-16 16:30 | 44820.6875 | 0 | 11.7336 | 39.95
2022-09-16 17:00 | 44820.7083 | 0 | 12.3421 | 39.95
2022-09-16 17:30 | 44820.7292 | 0 | 12.6162 | 39.95
2022-09-16 18:00 | 44820.75 | 0 | 13.076 | 39.95
2022-09-16 18:30 | 44820.7708 | 0 | 13.1974 | 39.95
2022-09-16 19:00 | 44820.7917 | 0 | 13.0339 | 39.95
2022-09-16 19:30 | 44820.8125 | 0 | 12.674 | 39.95
2022-09-16 20:00 | 44820.8333 | 0 | 12.4518 | 39.95
2022-09-16 20:30 | 44820.8542 | 0 | 12.1763 | 39.95
2022-09-16 21:00 | 44820.875 | 0 | 11.786 | 39.95
2022-09-16 21:30 | 44820.8958 | 0 | 11.3003 | 39.95
2022-09-16 22:00 | 44820.9167 | 0 | 11.0315 | 39.95
2022-09-16 22:30 | 44820.9375 | 0 | 10.3611 | 39.95
2022-09-16 23:00 | 44820.9583 | 0 | 9.8192 | 39.95
2022-09-16 23:30 | 44820.9792 | 0 | 9.3875 | 39.95
2022-09-17 | 44821 | 0 | 8.9101 | 39.95
2022-09-17 00:30 | 44821.0208 | 0 | 8.4962 | 39.95
2022-09-17 01:00 | 44821.0417 | 0 | 8.3387 | 39.95
2022-09-17 01:30 | 44821.0625 | 0 | 8.1523 | 39.95
2022-09-17 02:00 | 44821.0833 | 0 | 8.0603 | 39.95
2022-09-17 02:30 | 44821.1042 | 0 | 8.0401 | 39.95
2022-09-17 03:00 | 44821.125 | 0 | 7.8718 | 39.95
2022-09-17 03:30 | 44821.1458 | 0 | 7.8775 | 39.95
2022-09-17 04:00 | 44821.1667 | 0 | 7.9332 | 39.95
2022-09-17 04:30 | 44821.1875 | 0 | 7.8339 | 39.95
2022-09-17 05:00 | 44821.2083 | 0 | 8.1297 | 39.95
2022-09-17 05:30 | 44821.2292 | 0 | 8.2788 | 39.95
2022-09-17 06:00 | 44821.25 | 0 | 8.3366 | 39.95
2022-09-17 06:30 | 44821.2708 | 0 | 8.0624 | 39.95
2022-09-17 07:00 | 44821.2917 | 0 | 8.2565 | 39.95
2022-09-17 07:30 | 44821.3125 | 0 | 7.8687 | 39.95
2022-09-17 08:00 | 44821.3333 | 0 | 8.4742 | 39.95
2022-09-17 08:30 | 44821.3542 | 0 | 8.5156 | 39.95
2022-09-17 09:00 | 44821.375 | 0 | 8.6076 | 39.95
2022-09-17 09:30 | 44821.3958 | 0 | 7.3325 | 39.95
2022-09-17 10:00 | 44821.4167 | 0 | 5.3622 | 39.95
2022-09-17 10:30 | 44821.4375 | 0 | 5.8296 | 39.95
2022-09-17 11:00 | 44821.4583 | 0 | 5.7779 | 39.95
2022-09-17 11:30 | 44821.4792 | 0 | 6.8654 | 39.95
2022-09-17 12:00 | 44821.5 | 0 | 7.1315 | 39.95
2022-09-17 12:30 | 44821.5208 | 0 | 6.8543 | 39.95
2022-09-17 13:00 | 44821.5417 | 0 | 6.9547 | 39.95
2022-09-17 13:30 | 44821.5625 | 0 | 7.1788 | 39.95
2022-09-17 14:00 | 44821.5833 | 0 | 7.8134 | 39.95
2022-09-17 14:30 | 44821.6042 | 0 | 8.2179 | 39.95
2022-09-17 15:00 | 44821.625 | 0 | 8.2503 | 39.95
2022-09-17 15:30 | 44821.6458 | 0 | 8.5875 | 39.95
2022-09-17 16:00 | 44821.6667 | 0 | 9.5888 | 39.95
2022-09-17 16:30 | 44821.6875 | 0 | 10.273 | 39.95
2022-09-17 17:00 | 44821.7083 | 0 | 10.6833 | 39.95
2022-09-17 17:30 | 44821.7292 | 0 | 10.8295 | 39.95
2022-09-17 18:00 | 44821.75 | 0 | 11.3286 | 39.95
2022-09-17 18:30 | 44821.7708 | 0 | 11.4754 | 39.95
2022-09-17 19:00 | 44821.7917 | 0 | 11.3399 | 39.95
2022-09-17 19:30 | 44821.8125 | 0 | 11.0095 | 39.95
2022-09-17 20:00 | 44821.8333 | 0 | 10.8674 | 39.95
2022-09-17 20:30 | 44821.8542 | 0 | 10.3866 | 39.95
2022-09-17 21:00 | 44821.875 | 0 | 10.0396 | 39.95
2022-09-17 21:30 | 44821.8958 | 0 | 9.8296 | 39.95
2022-09-17 22:00 | 44821.9167 | 0 | 9.5097 | 39.95
2022-09-17 22:30 | 44821.9375 | 0 | 8.9583 | 39.95
2022-09-17 23:00 | 44821.9583 | 0 | 8.6606 | 39.95
2022-09-17 23:30 | 44821.9792 | 0 | 8.1772 | 39.95
2022-09-18 | 44822 | 0 | 7.8552 | 39.95
2022-09-18 00:30 | 44822.0208 | 0 | 7.509 | 39.95
2022-09-18 01:00 | 44822.0417 | 0 | 7.3585 | 39.95
2022-09-18 01:30 | 44822.0625 | 0 | 7.2045 | 39.95
2022-09-18 02:00 | 44822.0833 | 0 | 7.1908 | 39.95
2022-09-18 02:30 | 44822.1042 | 0 | 7.1292 | 39.95
2022-09-18 03:00 | 44822.125 | 0 | 7.0232 | 39.95
2022-09-18 03:30 | 44822.1458 | 0 | 6.8521 | 39.95
2022-09-18 04:00 | 44822.1667 | 0 | 6.8118 | 39.95
2022-09-18 04:30 | 44822.1875 | 0 | 6.9059 | 39.95
2022-09-18 05:00 | 44822.2083 | 0 | 7.0041 | 39.95
2022-09-18 05:30 | 44822.2292 | 0 | 7.0681 | 39.95
2022-09-18 06:00 | 44822.25 | 0 | 6.7558 | 39.95
2022-09-18 06:30 | 44822.2708 | 0 | 6.5363 | 39.95
2022-09-18 07:00 | 44822.2917 | 0 | 6.358 | 39.95
2022-09-18 07:30 | 44822.3125 | 0 | 5.9177 | 39.95
2022-09-18 08:00 | 44822.3333 | 0 | 5.4959 | 39.95
2022-09-18 08:30 | 44822.3542 | 0 | 5.2398 | 39.95
2022-09-18 09:00 | 44822.375 | 0 | 4.8494 | 39.95
2022-09-18 09:30 | 44822.3958 | 0 | 4.7706 | 39.95
2022-09-18 10:00 | 44822.4167 | 0 | 4.2775 | 39.95
2022-09-18 10:30 | 44822.4375 | 0 | 3.8186 | 39.95
2022-09-18 11:00 | 44822.4583 | 0 | 3.7641 | 39.95
2022-09-18 11:30 | 44822.4792 | 0 | 3.5071 | 39.95
2022-09-18 12:00 | 44822.5 | 0 | 3.3707 | 39.95
2022-09-18 12:30 | 44822.5208 | 0 | 3.6912 | 39.95
2022-09-18 13:00 | 44822.5417 | 0 | 3.8248 | 39.95
2022-09-18 13:30 | 44822.5625 | 0 | 4.3516 | 39.95
2022-09-18 14:00 | 44822.5833 | 0 | 5.0145 | 39.95
2022-09-18 14:30 | 44822.6042 | 0 | 5.7669 | 39.95
2022-09-18 15:00 | 44822.625 | 0 | 6.5445 | 39.95
2022-09-18 15:30 | 44822.6458 | 0 | 7.5982 | 39.95
2022-09-18 16:00 | 44822.6667 | 0 | 8.502 | 39.95
2022-09-18 16:30 | 44822.6875 | 0 | 9.5872 | 39.95
2022-09-18 17:00 | 44822.7083 | 0 | 10.2423 | 39.95
2022-09-18 17:30 | 44822.7292 | 0 | 10.6486 | 39.95
2022-09-18 18:00 | 44822.75 | 0 | 11.2244 | 39.95
2022-09-18 18:30 | 44822.7708 | 0 | 11.5553 | 39.95
2022-09-18 19:00 | 44822.7917 | 0 | 11.2574 | 39.95
2022-09-18 19:30 | 44822.8125 | 0 | 10.943 | 39.95
2022-09-18 20:00 | 44822.8333 | 0 | 10.6738 | 39.95
2022-09-18 20:30 | 44822.8542 | 0 | 10.1611 | 39.95
2022-09-18 21:00 | 44822.875 | 0 | 9.9208 | 39.95
2022-09-18 21:30 | 44822.8958 | 0 | 9.5456 | 39.95
2022-09-18 22:00 | 44822.9167 | 0 | 9.0988 | 39.95
2022-09-18 22:30 | 44822.9375 | 0 | 8.5364 | 39.95
2022-09-18 23:00 | 44822.9583 | 0 | 8.074 | 39.95
2022-09-18 23:30 | 44822.9792 | 0 | 7.8507 | 39.95
2022-09-19 | 44823 | 0 | 7.4811 | 39.95
2022-09-19 00:30 | 44823.0208 | 0 | 7.3897 | 39.95
2022-09-19 01:00 | 44823.0417 | 0 | 7.2465 | 39.95
2022-09-19 01:30 | 44823.0625 | 0 | 7.1238 | 39.95
2022-09-19 02:00 | 44823.0833 | 0 | 7.0806 | 39.95
2022-09-19 02:30 | 44823.1042 | 0 | 7.3043 | 39.95
2022-09-19 03:00 | 44823.125 | 0 | 7.1688 | 39.95
2022-09-19 03:30 | 44823.1458 | 0 | 7.2947 | 39.95
2022-09-19 04:00 | 44823.1667 | 0 | 7.5636 | 39.95
2022-09-19 04:30 | 44823.1875 | 0 | 7.8355 | 39.95
2022-09-19 05:00 | 44823.2083 | 0 | 8.4642 | 39.95
2022-09-19 05:30 | 44823.2292 | 0 | 9.0563 | 39.95
2022-09-19 06:00 | 44823.25 | 0 | 9.716 | 39.95
2022-09-19 06:30 | 44823.2708 | 0 | 9.8797 | 39.95
2022-09-19 07:00 | 44823.2917 | 0 | 9.8076 | 39.95
2022-09-19 07:30 | 44823.3125 | 0 | 9.4718 | 39.95
2022-09-19 08:00 | 44823.3333 | 0 | 8.9524 | 39.95
2022-09-19 08:30 | 44823.3542 | 0 | 8.4486 | 39.95
2022-09-19 09:00 | 44823.375 | 0 | 7.8638 | 39.95
2022-09-19 09:30 | 44823.3958 | 0 | 7.3424 | 39.95
2022-09-19 10:00 | 44823.4167 | 0 | 7.3888 | 39.95
2022-09-19 10:30 | 44823.4375 | 0 | 7.2271 | 39.95
2022-09-19 11:00 | 44823.4583 | 0 | 6.9986 | 39.95
2022-09-19 11:30 | 44823.4792 | 0 | 7.1902 | 39.95
2022-09-19 12:00 | 44823.5 | 0 | 7.1866 | 39.95
2022-09-19 12:30 | 44823.5208 | 0 | 7.5294 | 39.95
2022-09-19 13:00 | 44823.5417 | 0 | 7.9193 | 39.95
2022-09-19 13:30 | 44823.5625 | 0 | 8.3283 | 39.95
2022-09-19 14:00 | 44823.5833 | 0 | 8.8859 | 39.95
2022-09-19 14:30 | 44823.6042 | 0 | 9.2237 | 39.95
2022-09-19 15:00 | 44823.625 | 0 | 10.0308 | 39.95
2022-09-19 15:30 | 44823.6458 | 0 | 10.6114 | 39.95
2022-09-19 16:00 | 44823.6667 | 0 | 10.997 | 39.95
2022-09-19 16:30 | 44823.6875 | 0 | 11.7017 | 39.95
2022-09-19 17:00 | 44823.7083 | 0 | 12.1266 | 39.95
2022-09-19 17:30 | 44823.7292 | 0 | 12.9039 | 39.95
2022-09-19 18:00 | 44823.75 | 0 | 13.3704 | 39.95
2022-09-19 18:30 | 44823.7708 | 0 | 13.8482 | 39.95
2022-09-19 19:00 | 44823.7917 | 0 | 13.3748 | 39.95
2022-09-19 19:30 | 44823.8125 | 0 | 12.6621 | 39.95
2022-09-19 20:00 | 44823.8333 | 0 | 12.2967 | 39.95
2022-09-19 20:30 | 44823.8542 | 0 | 11.8449 | 39.95
2022-09-19 21:00 | 44823.875 | 0 | 11.4309 | 39.95
2022-09-19 21:30 | 44823.8958 | 0 | 11.2268 | 39.95
2022-09-19 22:00 | 44823.9167 | 0 | 10.7368 | 39.95
2022-09-19 22:30 | 44823.9375 | 0 | 10.0446 | 39.95
2022-09-19 23:00 | 44823.9583 | 0 | 9.6891 | 39.95
2022-09-19 23:30 | 44823.9792 | 0 | 9.0848 | 39.95
2022-09-20 | 44824 | 0 | 8.7079 | 39.95
2022-09-20 00:30 | 44824.0208 | 0 | 8.4513 | 39.95
2022-09-20 01:00 | 44824.0417 | 0 | 8.1258 | 39.95
2022-09-20 01:30 | 44824.0625 | 0 | 8.0508 | 39.95
2022-09-20 02:00 | 44824.0833 | 0 | 7.8843 | 39.95
2022-09-20 02:30 | 44824.1042 | 0 | 7.83 | 39.95
2022-09-20 03:00 | 44824.125 | 0 | 7.6725 | 39.95
2022-09-20 03:30 | 44824.1458 | 0 | 7.705 | 39.95
2022-09-20 04:00 | 44824.1667 | 0 | 7.8335 | 39.95
2022-09-20 04:30 | 44824.1875 | 0 | 8.4184 | 39.95
2022-09-20 05:00 | 44824.2083 | 0 | 8.6305 | 39.95
2022-09-20 05:30 | 44824.2292 | 0 | 9.0238 | 39.95
2022-09-20 06:00 | 44824.25 | 0 | 9.657 | 39.95
2022-09-20 06:30 | 44824.2708 | 0 | 9.8395 | 39.95
2022-09-20 07:00 | 44824.2917 | 0 | 9.9493 | 39.95
2022-09-20 07:30 | 44824.3125 | 0 | 9.6099 | 39.95
2022-09-20 08:00 | 44824.3333 | 0 | 9.0876 | 39.95
2022-09-20 08:30 | 44824.3542 | 0 | 8.7547 | 39.95
2022-09-20 09:00 | 44824.375 | 0 | 8.0523 | 39.95
2022-09-20 09:30 | 44824.3958 | 0 | 7.7517 | 39.95
2022-09-20 10:00 | 44824.4167 | 0 | 7.3534 | 39.95
2022-09-20 10:30 | 44824.4375 | 0 | 7.4263 | 39.95
2022-09-20 11:00 | 44824.4583 | 0 | 7.5803 | 39.95
2022-09-20 11:30 | 44824.4792 | 0 | 7.5198 | 39.95
2022-09-20 12:00 | 44824.5 | 0 | 7.4132 | 39.95
2022-09-20 12:30 | 44824.5208 | 0 | 7.5026 | 39.95
2022-09-20 13:00 | 44824.5417 | 0 | 7.7202 | 39.95
2022-09-20 13:30 | 44824.5625 | 0 | 8.0547 | 39.95
2022-09-20 14:00 | 44824.5833 | 0 | 8.5129 | 39.95
2022-09-20 14:30 | 44824.6042 | 0 | 9.13 | 39.95
2022-09-20 15:00 | 44824.625 | 0 | 9.8529 | 39.95
2022-09-20 15:30 | 44824.6458 | 0 | 10.4848 | 39.95
2022-09-20 16:00 | 44824.6667 | 0 | 11.2743 | 39.95
2022-09-20 16:30 | 44824.6875 | 0 | 12.0304 | 39.95
2022-09-20 17:00 | 44824.7083 | 0 | 12.6061 | 39.95
2022-09-20 17:30 | 44824.7292 | 0 | 13.0942 | 39.95
2022-09-20 18:00 | 44824.75 | 0 | 13.5005 | 39.95
2022-09-20 18:30 | 44824.7708 | 0 | 13.5101 | 39.95
2022-09-20 19:00 | 44824.7917 | 0 | 13.2114 | 39.95
2022-09-20 19:30 | 44824.8125 | 0 | 13.0485 | 39.95
2022-09-20 20:00 | 44824.8333 | 0 | 12.817 | 39.95
2022-09-20 20:30 | 44824.8542 | 0 | 12.2645 | 39.95
2022-09-20 21:00 | 44824.875 | 0 | 11.7451 | 39.95
2022-09-20 21:30 | 44824.8958 | 0 | 11.2987 | 39.95
2022-09-20 22:00 | 44824.9167 | 0 | 10.6347 | 39.95
2022-09-20 22:30 | 44824.9375 | 0 | 9.7257 | 39.95
2022-09-20 23:00 | 44824.9583 | 0 | 9.7305 | 39.95
2022-09-20 23:30 | 44824.9792 | 0 | 9.2689 | 39.95
2022-09-21 | 44825 | 0 | 8.6787 | 39.95
2022-09-21 00:30 | 44825.0208 | 0 | 8.3283 | 39.95
2022-09-21 01:00 | 44825.0417 | 0 | 8.1735 | 39.95
2022-09-21 01:30 | 44825.0625 | 0 | 8.1143 | 39.95
2022-09-21 02:00 | 44825.0833 | 0 | 8.0829 | 39.95
2022-09-21 02:30 | 44825.1042 | 0 | 8.0907 | 39.95
2022-09-21 03:00 | 44825.125 | 0 | 8.0222 | 39.95
2022-09-21 03:30 | 44825.1458 | 0 | 8.0049 | 39.95
2022-09-21 04:00 | 44825.1667 | 0 | 8.1461 | 39.95
2022-09-21 04:30 | 44825.1875 | 0 | 8.5989 | 39.95
2022-09-21 05:00 | 44825.2083 | 0 | 9.1982 | 39.95
2022-09-21 05:30 | 44825.2292 | 0 | 9.7058 | 39.95
2022-09-21 06:00 | 44825.25 | 0 | 10.0786 | 39.95
2022-09-21 06:30 | 44825.2708 | 0 | 10.9727 | 39.95
2022-09-21 07:00 | 44825.2917 | 0 | 11.5627 | 39.95
2022-09-21 07:30 | 44825.3125 | 0 | 11.5522 | 39.95
2022-09-21 08:00 | 44825.3333 | 0 | 11.582 | 39.95
2022-09-21 08:30 | 44825.3542 | 0 | 11.7217 | 39.95
2022-09-21 09:00 | 44825.375 | 0 | 9.7319 | 39.95
2022-09-21 09:30 | 44825.3958 | 0 | 8.843 | 39.95
2022-09-21 10:00 | 44825.4167 | 0 | 9.0652 | 39.95
2022-09-21 10:30 | 44825.4375 | 0 | 10.3214 | 39.95
2022-09-21 11:00 | 44825.4583 | 0 | 9.9997 | 39.95
2022-09-21 11:30 | 44825.4792 | 0 | 11.3176 | 39.95
2022-09-21 12:00 | 44825.5 | 0 | 11.9471 | 39.95
2022-09-21 12:30 | 44825.5208 | 0 | 11.7362 | 39.95
2022-09-21 13:00 | 44825.5417 | 0 | 11.5998 | 39.95
2022-09-21 13:30 | 44825.5625 | 0 | 12.5381 | 39.95
2022-09-21 14:00 | 44825.5833 | 0 | 12.23 | 39.95
2022-09-21 14:30 | 44825.6042 | 0 | 12.8144 | 39.95
2022-09-21 15:00 | 44825.625 | 0 | 12.5944 | 39.95
2022-09-21 15:30 | 44825.6458 | 0 | 13.4019 | 39.95
2022-09-21 16:00 | 44825.6667 | 0 | 13.1448 | 39.95
2022-09-21 16:30 | 44825.6875 | 0 | 12.689 | 39.95
2022-09-21 17:00 | 44825.7083 | 0 | 13.0878 | 39.95
2022-09-21 17:30 | 44825.7292 | 0 | 13.5978 | 39.95
2022-09-21 18:00 | 44825.75 | 0 | 13.96 | 39.95
2022-09-21 18:30 | 44825.7708 | 0 | 14.2036 | 39.95
2022-09-21 19:00 | 44825.7917 | 0 | 13.8979 | 39.95
2022-09-21 19:30 | 44825.8125 | 0 | 13.6697 | 39.95
2022-09-21 20:00 | 44825.8333 | 0 | 12.9888 | 39.95
2022-09-21 20:30 | 44825.8542 | 0 | 12.0099 | 39.95
2022-09-21 21:00 | 44825.875 | 0 | 11.4298 | 39.95
2022-09-21 21:30 | 44825.8958 | 0 | 11.1767 | 39.95
2022-09-21 22:00 | 44825.9167 | 0 | 10.9478 | 39.95
2022-09-21 22:30 | 44825.9375 | 0 | 10.4307 | 39.95
2022-09-21 23:00 | 44825.9583 | 0 | 9.8999 | 39.95
2022-09-21 23:30 | 44825.9792 | 0 | 9.4672 | 39.95
2022-09-22 | 44826 | 0 | 8.9631 | 39.95
2022-09-22 00:30 | 44826.0208 | 0 | 8.5052 | 39.95
2022-09-22 01:00 | 44826.0417 | 0 | 8.2701 | 39.95
2022-09-22 01:30 | 44826.0625 | 0 | 8.0567 | 39.95
2022-09-22 02:00 | 44826.0833 | 0 | 8.0025 | 39.95
2022-09-22 02:30 | 44826.1042 | 0 | 8.1857 | 39.95
2022-09-22 03:00 | 44826.125 | 0 | 8.0353 | 39.95
2022-09-22 03:30 | 44826.1458 | 0 | 7.9144 | 39.95
2022-09-22 04:00 | 44826.1667 | 0 | 7.9605 | 39.95
2022-09-22 04:30 | 44826.1875 | 0 | 8.0436 | 39.95
2022-09-22 05:00 | 44826.2083 | 0 | 8.1681 | 39.95
2022-09-22 05:30 | 44826.2292 | 0 | 8.4831 | 39.95
2022-09-22 06:00 | 44826.25 | 0 | 8.7791 | 39.95
2022-09-22 06:30 | 44826.2708 | 0 | 9.367 | 39.95
2022-09-22 07:00 | 44826.2917 | 0 | 9.9506 | 39.95
2022-09-22 07:30 | 44826.3125 | 0 | 10.181 | 39.95
2022-09-22 08:00 | 44826.3333 | 0 | 11.0229 | 39.95
2022-09-22 08:30 | 44826.3542 | 0 | 10.7602 | 39.95
2022-09-22 09:00 | 44826.375 | 0 | 11.6024 | 39.95
2022-09-22 09:30 | 44826.3958 | 0 | 11.4975 | 39.95
2022-09-22 10:00 | 44826.4167 | 0 | 11.4842 | 39.95
2022-09-22 10:30 | 44826.4375 | 0 | 10.4978 | 39.95
2022-09-22 11:00 | 44826.4583 | 0 | 10.665 | 39.95
2022-09-22 11:30 | 44826.4792 | 0 | 10.9467 | 39.95
2022-09-22 12:00 | 44826.5 | 0 | 9.4902 | 39.95
2022-09-22 12:30 | 44826.5208 | 0 | 7.6789 | 39.95
2022-09-22 13:00 | 44826.5417 | 0 | 8.9308 | 39.95
2022-09-22 13:30 | 44826.5625 | 0 | 10.8469 | 39.95
2022-09-22 14:00 | 44826.5833 | 0 | 9.608 | 39.95
2022-09-22 14:30 | 44826.6042 | 0 | 9.4717 | 39.95
2022-09-22 15:00 | 44826.625 | 0 | 8.743 | 39.95
2022-09-22 15:30 | 44826.6458 | 0 | 9.3935 | 39.95
2022-09-22 16:00 | 44826.6667 | 0 | 10.8233 | 39.95
2022-09-22 16:30 | 44826.6875 | 0 | 10.883 | 39.95
2022-09-22 17:00 | 44826.7083 | 0 | 11.2002 | 39.95
2022-09-22 17:30 | 44826.7292 | 0 | 11.7196 | 39.95
2022-09-22 18:00 | 44826.75 | 0 | 12.0349 | 39.95
2022-09-22 18:30 | 44826.7708 | 0 | 12.2048 | 39.95
2022-09-22 19:00 | 44826.7917 | 0 | 11.807 | 39.95
2022-09-22 19:30 | 44826.8125 | 0 | 11.3432 | 39.95
2022-09-22 20:00 | 44826.8333 | 0 | 11.2299 | 39.95
2022-09-22 20:30 | 44826.8542 | 0 | 10.6762 | 39.95
2022-09-22 21:00 | 44826.875 | 0 | 10.4041 | 39.95
2022-09-22 21:30 | 44826.8958 | 0 | 10.008 | 39.95
2022-09-22 22:00 | 44826.9167 | 0 | 9.6134 | 39.95
2022-09-22 22:30 | 44826.9375 | 0 | 9.0245 | 39.95
2022-09-22 23:00 | 44826.9583 | 0 | 8.6954 | 39.95
2022-09-22 23:30 | 44826.9792 | 0 | 8.5141 | 39.95
2022-09-23 | 44827 | 0 | 7.9805 | 39.95
2022-09-23 00:30 | 44827.0208 | 0 | 7.5595 | 39.95
2022-09-23 01:00 | 44827.0417 | 0 | 7.4603 | 39.95
2022-09-23 01:30 | 44827.0625 | 0 | 7.3993 | 39.95
2022-09-23 02:00 | 44827.0833 | 0 | 7.248 | 39.95
2022-09-23 02:30 | 44827.1042 | 0 | 7.3463 | 39.95
2022-09-23 03:00 | 44827.125 | 0 | 7.2084 | 39.95
2022-09-23 03:30 | 44827.1458 | 0 | 7.1959 | 39.95
2022-09-23 04:00 | 44827.1667 | 0 | 7.4936 | 39.95
2022-09-23 04:30 | 44827.1875 | 0 | 8.1347 | 39.95
2022-09-23 05:00 | 44827.2083 | 0 | 8.7901 | 39.95
2022-09-23 05:30 | 44827.2292 | 0 | 9.193 | 39.95
2022-09-23 06:00 | 44827.25 | 0 | 9.8508 | 39.95
2022-09-23 06:30 | 44827.2708 | 0 | 10.6764 | 39.95
2022-09-23 07:00 | 44827.2917 | 0 | 11.2735 | 39.95
2022-09-23 07:30 | 44827.3125 | 0 | 10.0694 | 39.95
2022-09-23 08:00 | 44827.3333 | 0 | 9.4505 | 39.95
2022-09-23 08:30 | 44827.3542 | 0 | 9.5502 | 39.95
2022-09-23 09:00 | 44827.375 | 0 | 9.3829 | 39.95
2022-09-23 09:30 | 44827.3958 | 0 | 8.0027 | 39.95
2022-09-23 10:00 | 44827.4167 | 0 | 7.7112 | 39.95
2022-09-23 10:30 | 44827.4375 | 0 | 7.3465 | 39.95
2022-09-23 11:00 | 44827.4583 | 0 | 7.3729 | 39.95
2022-09-23 11:30 | 44827.4792 | 0 | 9.5046 | 39.95
2022-09-23 12:00 | 44827.5 | 0 | 9.215 | 39.95
2022-09-23 12:30 | 44827.5208 | 0 | 9.9395 | 39.95
2022-09-23 13:00 | 44827.5417 | 0 | 9.6171 | 39.95
2022-09-23 13:30 | 44827.5625 | 0 | 7.3902 | 39.95
2022-09-23 14:00 | 44827.5833 | 0 | 10.3773 | 39.95
2022-09-23 14:30 | 44827.6042 | 0 | 10.6855 | 39.95
2022-09-23 15:00 | 44827.625 | 0 | 9.3249 | 39.95
2022-09-23 15:30 | 44827.6458 | 0 | 10.0341 | 39.95
2022-09-23 16:00 | 44827.6667 | 0 | 11.2975 | 39.95
2022-09-23 16:30 | 44827.6875 | 0 | 12.2234 | 39.95
2022-09-23 17:00 | 44827.7083 | 0 | 12.4306 | 39.95
2022-09-23 17:30 | 44827.7292 | 0 | 12.5736 | 39.95
2022-09-23 18:00 | 44827.75 | 0 | 12.8255 | 39.95
2022-09-23 18:30 | 44827.7708 | 0 | 12.9404 | 39.95
2022-09-23 19:00 | 44827.7917 | 0 | 12.7662 | 39.95
2022-09-23 19:30 | 44827.8125 | 0 | 12.4099 | 39.95
2022-09-23 20:00 | 44827.8333 | 0 | 11.9913 | 39.95
2022-09-23 20:30 | 44827.8542 | 0 | 11.6231 | 39.95
2022-09-23 21:00 | 44827.875 | 0 | 11.3985 | 39.95
2022-09-23 21:30 | 44827.8958 | 0 | 11.0094 | 39.95
2022-09-23 22:00 | 44827.9167 | 0 | 10.7607 | 39.95
2022-09-23 22:30 | 44827.9375 | 0 | 10.1465 | 39.95
2022-09-23 23:00 | 44827.9583 | 0 | 9.7478 | 39.95
2022-09-23 23:30 | 44827.9792 | 0 | 9.2705 | 39.95
2022-09-24 | 44828 | 0 | 8.8029 | 39.95
2022-09-24 00:30 | 44828.0208 | 0 | 8.5762 | 39.95
2022-09-24 01:00 | 44828.0417 | 0 | 8.3881 | 39.95
2022-09-24 01:30 | 44828.0625 | 0 | 8.1931 | 39.95
2022-09-24 02:00 | 44828.0833 | 0 | 8.1377 | 39.95
2022-09-24 02:30 | 44828.1042 | 0 | 8.1032 | 39.95
2022-09-24 03:00 | 44828.125 | 0 | 7.9859 | 39.95
2022-09-24 03:30 | 44828.1458 | 0 | 8.0213 | 39.95
2022-09-24 04:00 | 44828.1667 | 0 | 7.9208 | 39.95
2022-09-24 04:30 | 44828.1875 | 0 | 7.9808 | 39.95
2022-09-24 05:00 | 44828.2083 | 0 | 8.0338 | 39.95
2022-09-24 05:30 | 44828.2292 | 0 | 8.3567 | 39.95
2022-09-24 06:00 | 44828.25 | 0 | 8.1136 | 39.95
2022-09-24 06:30 | 44828.2708 | 0 | 7.9064 | 39.95
2022-09-24 07:00 | 44828.2917 | 0 | 7.7071 | 39.95
2022-09-24 07:30 | 44828.3125 | 0 | 7.4213 | 39.95
2022-09-24 08:00 | 44828.3333 | 0 | 7.1599 | 39.95
2022-09-24 08:30 | 44828.3542 | 0 | 6.7945 | 39.95
2022-09-24 09:00 | 44828.375 | 0 | 6.3478 | 39.95
2022-09-24 09:30 | 44828.3958 | 0 | 5.8366 | 39.95
2022-09-24 10:00 | 44828.4167 | 0 | 5.6972 | 39.95
2022-09-24 10:30 | 44828.4375 | 0 | 5.4594 | 39.95
2022-09-24 11:00 | 44828.4583 | 0 | 5.1054 | 39.95
2022-09-24 11:30 | 44828.4792 | 0 | 5.1582 | 39.95
2022-09-24 12:00 | 44828.5 | 0 | 5.2307 | 39.95
2022-09-24 12:30 | 44828.5208 | 0 | 5.5272 | 39.95
2022-09-24 13:00 | 44828.5417 | 0 | 5.9034 | 39.95
2022-09-24 13:30 | 44828.5625 | 0 | 6.7554 | 39.95
2022-09-24 14:00 | 44828.5833 | 0 | 6.0745 | 39.95
2022-09-24 14:30 | 44828.6042 | 0 | 6.65 | 39.95
2022-09-24 15:00 | 44828.625 | 0 | 7.6916 | 39.95
2022-09-24 15:30 | 44828.6458 | 0 | 8.5639 | 39.95
2022-09-24 16:00 | 44828.6667 | 0 | 9.4622 | 39.95
2022-09-24 16:30 | 44828.6875 | 0 | 10.2327 | 39.95
2022-09-24 17:00 | 44828.7083 | 0 | 10.8468 | 39.95
2022-09-24 17:30 | 44828.7292 | 0 | 11.0518 | 39.95
2022-09-24 18:00 | 44828.75 | 0 | 11.4583 | 39.95
2022-09-24 18:30 | 44828.7708 | 0 | 11.6603 | 39.95
2022-09-24 19:00 | 44828.7917 | 0 | 11.2491 | 39.95
2022-09-24 19:30 | 44828.8125 | 0 | 10.9129 | 39.95
2022-09-24 20:00 | 44828.8333 | 0 | 10.7188 | 39.95
2022-09-24 20:30 | 44828.8542 | 0 | 10.4414 | 39.95
2022-09-24 21:00 | 44828.875 | 0 | 10.1377 | 39.95
2022-09-24 21:30 | 44828.8958 | 0 | 9.7811 | 39.95
2022-09-24 22:00 | 44828.9167 | 0 | 9.478 | 39.95
2022-09-24 22:30 | 44828.9375 | 0 | 8.967 | 39.95
2022-09-24 23:00 | 44828.9583 | 0 | 8.745 | 39.95
2022-09-24 23:30 | 44828.9792 | 0 | 8.2684 | 39.95
2022-09-25 | 44829 | 0 | 7.9536 | 39.95
2022-09-25 00:30 | 44829.0208 | 0 | 7.7262 | 39.95
2022-09-25 01:00 | 44829.0417 | 0 | 7.4972 | 39.95
2022-09-25 01:30 | 44829.0625 | 0 | 7.4183 | 39.95
2022-09-25 02:00 | 44829.0833 | 0 | 7.2227 | 39.95
2022-09-25 02:30 | 44829.1042 | 0 | 7.1977 | 39.95
2022-09-25 03:00 | 44829.125 | 0 | 7.2307 | 39.95
2022-09-25 03:30 | 44829.1458 | 0 | 7.0008 | 39.95
2022-09-25 04:00 | 44829.1667 | 0 | 7.0684 | 39.95
2022-09-25 04:30 | 44829.1875 | 0 | 7.0321 | 39.95
2022-09-25 05:00 | 44829.2083 | 0 | 7.1479 | 39.95
2022-09-25 05:30 | 44829.2292 | 0 | 7.0695 | 39.95
2022-09-25 06:00 | 44829.25 | 0 | 7.0083 | 39.95
2022-09-25 06:30 | 44829.2708 | 0 | 6.5322 | 39.95
2022-09-25 07:00 | 44829.2917 | 0 | 6.1978 | 39.95
2022-09-25 07:30 | 44829.3125 | 0 | 5.7339 | 39.95
2022-09-25 08:00 | 44829.3333 | 0 | 5.333 | 39.95
2022-09-25 08:30 | 44829.3542 | 0 | 4.9877 | 39.95
2022-09-25 09:00 | 44829.375 | 0 | 4.6247 | 39.95
2022-09-25 09:30 | 44829.3958 | 0 | 4.2942 | 39.95
2022-09-25 10:00 | 44829.4167 | 0 | 4.133 | 39.95
2022-09-25 10:30 | 44829.4375 | 0 | 4.1834 | 39.95
2022-09-25 11:00 | 44829.4583 | 0 | 4.1238 | 39.95
2022-09-25 11:30 | 44829.4792 | 0 | 3.8808 | 39.95
2022-09-25 12:00 | 44829.5 | 0 | 3.8128 | 39.95
2022-09-25 12:30 | 44829.5208 | 0 | 4.1089 | 39.95
2022-09-25 13:00 | 44829.5417 | 0 | 4.5087 | 39.95
2022-09-25 13:30 | 44829.5625 | 0 | 5.0045 | 39.95
2022-09-25 14:00 | 44829.5833 | 0 | 6.4001 | 39.95
2022-09-25 14:30 | 44829.6042 | 0 | 6.3282 | 39.95
2022-09-25 15:00 | 44829.625 | 0 | 7.1094 | 39.95
2022-09-25 15:30 | 44829.6458 | 0 | 7.8164 | 39.95
2022-09-25 16:00 | 44829.6667 | 0 | 8.6501 | 39.95
2022-09-25 16:30 | 44829.6875 | 0 | 9.6379 | 39.95
2022-09-25 17:00 | 44829.7083 | 0 | 10.347 | 39.95
2022-09-25 17:30 | 44829.7292 | 0 | 10.8977 | 39.95
2022-09-25 18:00 | 44829.75 | 0 | 11.5453 | 39.95
2022-09-25 18:30 | 44829.7708 | 0 | 11.9129 | 39.95
2022-09-25 19:00 | 44829.7917 | 0 | 11.4474 | 39.95
2022-09-25 19:30 | 44829.8125 | 0 | 10.9176 | 39.95
2022-09-25 20:00 | 44829.8333 | 0 | 10.7899 | 39.95
2022-09-25 20:30 | 44829.8542 | 0 | 10.2375 | 39.95
2022-09-25 21:00 | 44829.875 | 0 | 9.9833 | 39.95
2022-09-25 21:30 | 44829.8958 | 0 | 9.6556 | 39.95
2022-09-25 22:00 | 44829.9167 | 0 | 9.2155 | 39.95
2022-09-25 22:30 | 44829.9375 | 0 | 8.6698 | 39.95
2022-09-25 23:00 | 44829.9583 | 0 | 8.2932 | 39.95
2022-09-25 23:30 | 44829.9792 | 0 | 8.0439 | 39.95
2022-09-26 | 44830 | 0 | 7.6247 | 39.95
2022-09-26 00:30 | 44830.0208 | 0 | 7.3133 | 39.95
2022-09-26 01:00 | 44830.0417 | 0 | 7.4341 | 39.95
2022-09-26 01:30 | 44830.0625 | 0 | 7.3197 | 39.95
2022-09-26 02:00 | 44830.0833 | 0 | 7.3451 | 39.95
2022-09-26 02:30 | 44830.1042 | 0 | 7.3388 | 39.95
2022-09-26 03:00 | 44830.125 | 0 | 7.382 | 39.95
2022-09-26 03:30 | 44830.1458 | 0 | 7.4823 | 39.95
2022-09-26 04:00 | 44830.1667 | 0 | 7.886 | 39.95
2022-09-26 04:30 | 44830.1875 | 0 | 8.1261 | 39.95
2022-09-26 05:00 | 44830.2083 | 0 | 8.6502 | 39.95
2022-09-26 05:30 | 44830.2292 | 0 | 9.2331 | 39.95
2022-09-26 06:00 | 44830.25 | 0 | 9.6957 | 39.95
2022-09-26 06:30 | 44830.2708 | 0 | 9.6989 | 39.95
2022-09-26 07:00 | 44830.2917 | 0 | 9.7689 | 39.95
2022-09-26 07:30 | 44830.3125 | 0 | 9.3401 | 39.95
2022-09-26 08:00 | 44830.3333 | 0 | 8.9418 | 39.95
2022-09-26 08:30 | 44830.3542 | 0 | 8.3985 | 39.95
2022-09-26 09:00 | 44830.375 | 0 | 7.876 | 39.95
2022-09-26 09:30 | 44830.3958 | 0 | 7.7795 | 39.95
2022-09-26 10:00 | 44830.4167 | 0 | 8.1353 | 39.95
2022-09-26 10:30 | 44830.4375 | 0 | 8.4425 | 39.95
2022-09-26 11:00 | 44830.4583 | 0 | 8.0968 | 39.95
2022-09-26 11:30 | 44830.4792 | 0 | 9.7533 | 39.95
2022-09-26 12:00 | 44830.5 | 0 | 9.8634 | 39.95
2022-09-26 12:30 | 44830.5208 | 0 | 8.4344 | 39.95
2022-09-26 13:00 | 44830.5417 | 0 | 8.778 | 39.95
2022-09-26 13:30 | 44830.5625 | 0 | 8.2234 | 39.95
2022-09-26 14:00 | 44830.5833 | 0 | 8.7648 | 39.95
2022-09-26 14:30 | 44830.6042 | 0 | 9.946 | 39.95
2022-09-26 15:00 | 44830.625 | 0 | 10.941 | 39.95
2022-09-26 15:30 | 44830.6458 | 0 | 11.9855 | 39.95
2022-09-26 16:00 | 44830.6667 | 0 | 11.7134 | 39.95
2022-09-26 16:30 | 44830.6875 | 0 | 11.5851 | 39.95
2022-09-26 17:00 | 44830.7083 | 0 | 12.3347 | 39.95
2022-09-26 17:30 | 44830.7292 | 0 | 12.9245 | 39.95
2022-09-26 18:00 | 44830.75 | 0 | 13.55 | 39.95
2022-09-26 18:30 | 44830.7708 | 0 | 13.8537 | 39.95
2022-09-26 19:00 | 44830.7917 | 0 | 13.461 | 39.95
2022-09-26 19:30 | 44830.8125 | 0 | 12.8999 | 39.95
2022-09-26 20:00 | 44830.8333 | 0 | 12.7969 | 39.95
2022-09-26 20:30 | 44830.8542 | 0 | 12.2791 | 39.95
2022-09-26 21:00 | 44830.875 | 0 | 11.7946 | 39.95
2022-09-26 21:30 | 44830.8958 | 0 | 11.3575 | 39.95
2022-09-26 22:00 | 44830.9167 | 0 | 10.7586 | 39.95
2022-09-26 22:30 | 44830.9375 | 0 | 10.1624 | 39.95
2022-09-26 23:00 | 44830.9583 | 0 | 9.7687 | 39.95
2022-09-26 23:30 | 44830.9792 | 0 | 9.2115 | 39.95
2022-09-27 | 44831 | 0 | 8.7701 | 39.95
2022-09-27 00:30 | 44831.0208 | 0 | 8.3865 | 39.95
2022-09-27 01:00 | 44831.0417 | 0 | 8.0993 | 39.95
2022-09-27 01:30 | 44831.0625 | 0 | 7.9239 | 39.95
2022-09-27 02:00 | 44831.0833 | 0 | 7.7134 | 39.95
2022-09-27 02:30 | 44831.1042 | 0 | 7.8673 | 39.95
2022-09-27 03:00 | 44831.125 | 0 | 7.7741 | 39.95
2022-09-27 03:30 | 44831.1458 | 0 | 7.8417 | 39.95
2022-09-27 04:00 | 44831.1667 | 0 | 8.1333 | 39.95
2022-09-27 04:30 | 44831.1875 | 0 | 8.4528 | 39.95
2022-09-27 05:00 | 44831.2083 | 0 | 9.082 | 39.95
2022-09-27 05:30 | 44831.2292 | 0 | 9.5059 | 39.95
2022-09-27 06:00 | 44831.25 | 0 | 10.0341 | 39.95
2022-09-27 06:30 | 44831.2708 | 0 | 10.9379 | 39.95
2022-09-27 07:00 | 44831.2917 | 0 | 11.4366 | 39.95
2022-09-27 07:30 | 44831.3125 | 0 | 11.6981 | 39.95
2022-09-27 08:00 | 44831.3333 | 0 | 12.2005 | 39.95
2022-09-27 08:30 | 44831.3542 | 0 | 11.5394 | 39.95
2022-09-27 09:00 | 44831.375 | 0 | 11.4584 | 39.95
2022-09-27 09:30 | 44831.3958 | 0 | 11.0741 | 39.95
2022-09-27 10:00 | 44831.4167 | 0 | 11.4177 | 39.95
2022-09-27 10:30 | 44831.4375 | 0 | 11.5861 | 39.95
2022-09-27 11:00 | 44831.4583 | 0 | 8.8923 | 39.95
2022-09-27 11:30 | 44831.4792 | 0 | 9.8894 | 39.95
2022-09-27 12:00 | 44831.5 | 0 | 9.719 | 39.95
2022-09-27 12:30 | 44831.5208 | 0 | 10.6967 | 39.95
2022-09-27 13:00 | 44831.5417 | 0 | 10.8371 | 39.95
2022-09-27 13:30 | 44831.5625 | 0 | 9.6939 | 39.95
2022-09-27 14:00 | 44831.5833 | 0 | 8.9834 | 39.95
2022-09-27 14:30 | 44831.6042 | 0 | 10.4241 | 39.95
2022-09-27 15:00 | 44831.625 | 0 | 11.1471 | 39.95
2022-09-27 15:30 | 44831.6458 | 0 | 12.568 | 39.95
2022-09-27 16:00 | 44831.6667 | 0 | 12.6281 | 39.95
2022-09-27 16:30 | 44831.6875 | 0 | 12.8728 | 39.95
2022-09-27 17:00 | 44831.7083 | 0 | 12.8996 | 39.95
2022-09-27 17:30 | 44831.7292 | 0 | 13.1057 | 39.95
2022-09-27 18:00 | 44831.75 | 0 | 13.5304 | 39.95
2022-09-27 18:30 | 44831.7708 | 0 | 13.7268 | 39.95
2022-09-27 19:00 | 44831.7917 | 0 | 13.4983 | 39.95
2022-09-27 19:30 | 44831.8125 | 0 | 13.0274 | 39.95
2022-09-27 20:00 | 44831.8333 | 0 | 12.522 | 39.95
2022-09-27 20:30 | 44831.8542 | 0 | 12.1332 | 39.95
2022-09-27 21:00 | 44831.875 | 0 | 11.7024 | 39.95
2022-09-27 21:30 | 44831.8958 | 0 | 11.5579 | 39.95
2022-09-27 22:00 | 44831.9167 | 0 | 11.0179 | 39.95
2022-09-27 22:30 | 44831.9375 | 0 | 10.342 | 39.95
2022-09-27 23:00 | 44831.9583 | 0 | 9.6597 | 39.95
2022-09-27 23:30 | 44831.9792 | 0 | 9.455 | 39.95
2022-09-28 | 44832 | 0 | 9.0582 | 39.95
2022-09-28 00:30 | 44832.0208 | 0 | 8.83 | 39.95
2022-09-28 01:00 | 44832.0417 | 0 | 8.4632 | 39.95
2022-09-28 01:30 | 44832.0625 | 0 | 8.3247 | 39.95
2022-09-28 02:00 | 44832.0833 | 0 | 8.2998 | 39.95
2022-09-28 02:30 | 44832.1042 | 0 | 8.317 | 39.95
2022-09-28 03:00 | 44832.125 | 0 | 8.0925 | 39.95
2022-09-28 03:30 | 44832.1458 | 0 | 8.2973 | 39.95
2022-09-28 04:00 | 44832.1667 | 0 | 8.4843 | 39.95
2022-09-28 04:30 | 44832.1875 | 0 | 8.5971 | 39.95
2022-09-28 05:00 | 44832.2083 | 0 | 9.5069 | 39.95
2022-09-28 05:30 | 44832.2292 | 0 | 9.9139 | 39.95
2022-09-28 06:00 | 44832.25 | 0 | 10.5135 | 39.95
2022-09-28 06:30 | 44832.2708 | 0 | 10.8236 | 39.95
2022-09-28 07:00 | 44832.2917 | 0 | 11.3368 | 39.95
2022-09-28 07:30 | 44832.3125 | 0 | 11.474 | 39.95
2022-09-28 08:00 | 44832.3333 | 0 | 10.9107 | 39.95
2022-09-28 08:30 | 44832.3542 | 0 | 10.5076 | 39.95
2022-09-28 09:00 | 44832.375 | 0 | 10.1596 | 39.95
2022-09-28 09:30 | 44832.3958 | 0 | 10.1631 | 39.95
2022-09-28 10:00 | 44832.4167 | 0 | 10.2252 | 39.95
2022-09-28 10:30 | 44832.4375 | 0 | 13.0754 | 39.95
2022-09-28 11:00 | 44832.4583 | 0 | 12.7982 | 39.95
2022-09-28 11:30 | 44832.4792 | 0 | 10.9705 | 39.95
2022-09-28 12:00 | 44832.5 | 0 | 11.7905 | 39.95
2022-09-28 12:30 | 44832.5208 | 0 | 12.0226 | 39.95
2022-09-28 13:00 | 44832.5417 | 0 | 12.4891 | 39.95
2022-09-28 13:30 | 44832.5625 | 0 | 11.4976 | 39.95
2022-09-28 14:00 | 44832.5833 | 0 | 11.4961 | 39.95
2022-09-28 14:30 | 44832.6042 | 0 | 13.3462 | 39.95
2022-09-28 15:00 | 44832.625 | 0 | 12.7326 | 39.95
2022-09-28 15:30 | 44832.6458 | 0 | 13.0248 | 39.95
2022-09-28 16:00 | 44832.6667 | 0 | 13.1373 | 39.95
2022-09-28 16:30 | 44832.6875 | 0 | 13.5812 | 39.95
2022-09-28 17:00 | 44832.7083 | 0 | 13.7885 | 39.95
2022-09-28 17:30 | 44832.7292 | 0 | 14.2936 | 39.95
2022-09-28 18:00 | 44832.75 | 0 | 14.6871 | 39.95
2022-09-28 18:30 | 44832.7708 | 0 | 14.8905 | 39.95
2022-09-28 19:00 | 44832.7917 | 0 | 14.4378 | 39.95
2022-09-28 19:30 | 44832.8125 | 0 | 13.9895 | 39.95
2022-09-28 20:00 | 44832.8333 | 0 | 13.0211 | 39.95
2022-09-28 20:30 | 44832.8542 | 0 | 12.5486 | 39.95
2022-09-28 21:00 | 44832.875 | 0 | 12.1444 | 39.95
2022-09-28 21:30 | 44832.8958 | 0 | 11.9709 | 39.95
2022-09-28 22:00 | 44832.9167 | 0 | 11.4254 | 39.95
2022-09-28 22:30 | 44832.9375 | 0 | 10.539 | 39.95
2022-09-28 23:00 | 44832.9583 | 0 | 10.0496 | 39.95
2022-09-28 23:30 | 44832.9792 | 0 | 9.5728 | 39.95
2022-09-29 | 44833 | 0 | 9.1284 | 39.95
2022-09-29 00:30 | 44833.0208 | 0 | 8.7239 | 39.95
2022-09-29 01:00 | 44833.0417 | 0 | 8.4665 | 39.95
2022-09-29 01:30 | 44833.0625 | 0 | 8.2068 | 39.95
2022-09-29 02:00 | 44833.0833 | 0 | 8.1816 | 39.95
2022-09-29 02:30 | 44833.1042 | 0 | 8.0621 | 39.95
2022-09-29 03:00 | 44833.125 | 0 | 7.8906 | 39.95
2022-09-29 03:30 | 44833.1458 | 0 | 7.9835 | 39.95
2022-09-29 04:00 | 44833.1667 | 0 | 8.3342 | 39.95
2022-09-29 04:30 | 44833.1875 | 0 | 8.5889 | 39.95
2022-09-29 05:00 | 44833.2083 | 0 | 9.1065 | 39.95
2022-09-29 05:30 | 44833.2292 | 0 | 9.4451 | 39.95
2022-09-29 06:00 | 44833.25 | 0 | 10.279 | 39.95
2022-09-29 06:30 | 44833.2708 | 0 | 10.8087 | 39.95
2022-09-29 07:00 | 44833.2917 | 0 | 11.4033 | 39.95
2022-09-29 07:30 | 44833.3125 | 0 | 11.4852 | 39.95
2022-09-29 08:00 | 44833.3333 | 0 | 11.2641 | 39.95
2022-09-29 08:30 | 44833.3542 | 0 | 10.6811 | 39.95
2022-09-29 09:00 | 44833.375 | 0 | 10.7646 | 39.95
2022-09-29 09:30 | 44833.3958 | 0 | 10.5297 | 39.95
2022-09-29 10:00 | 44833.4167 | 0 | 10.2502 | 39.95
2022-09-29 10:30 | 44833.4375 | 0 | 9.9991 | 39.95
2022-09-29 11:00 | 44833.4583 | 0 | 9.4318 | 39.95
2022-09-29 11:30 | 44833.4792 | 0 | 9.4239 | 39.95
2022-09-29 12:00 | 44833.5 | 0 | 8.4226 | 39.95
2022-09-29 12:30 | 44833.5208 | 0 | 9.0257 | 39.95
2022-09-29 13:00 | 44833.5417 | 0 | 9.8553 | 39.95
2022-09-29 13:30 | 44833.5625 | 0 | 10.6359 | 39.95
2022-09-29 14:00 | 44833.5833 | 0 | 9.6312 | 39.95
2022-09-29 14:30 | 44833.6042 | 0 | 7.7182 | 39.95
2022-09-29 15:00 | 44833.625 | 0 | 8.4094 | 39.95
2022-09-29 15:30 | 44833.6458 | 0 | 9.4489 | 39.95
2022-09-29 16:00 | 44833.6667 | 0 | 10.4273 | 39.95
2022-09-29 16:30 | 44833.6875 | 0 | 11.2974 | 39.95
2022-09-29 17:00 | 44833.7083 | 0 | 11.9871 | 39.95
2022-09-29 17:30 | 44833.7292 | 0 | 12.271 | 39.95
2022-09-29 18:00 | 44833.75 | 0 | 12.7902 | 39.95
2022-09-29 18:30 | 44833.7708 | 0 | 13.3268 | 39.95
2022-09-29 19:00 | 44833.7917 | 0 | 13.0265 | 39.95
2022-09-29 19:30 | 44833.8125 | 0 | 12.4974 | 39.95
2022-09-29 20:00 | 44833.8333 | 0 | 12.3782 | 39.95
2022-09-29 20:30 | 44833.8542 | 0 | 12.0477 | 39.95
2022-09-29 21:00 | 44833.875 | 0 | 11.6154 | 39.95
2022-09-29 21:30 | 44833.8958 | 0 | 11.2312 | 39.95
2022-09-29 22:00 | 44833.9167 | 0 | 10.7511 | 39.95
2022-09-29 22:30 | 44833.9375 | 0 | 9.9815 | 39.95
2022-09-29 23:00 | 44833.9583 | 0 | 9.5579 | 39.95
2022-09-29 23:30 | 44833.9792 | 0 | 9.1284 | 39.95
2022-09-30 | 44834 | 0 | 8.6301 | 39.95
2022-09-30 00:30 | 44834.0208 | 0 | 8.3554 | 39.95
2022-09-30 01:00 | 44834.0417 | 0 | 8.2789 | 39.95
2022-09-30 01:30 | 44834.0625 | 0 | 8.0805 | 39.95
2022-09-30 02:00 | 44834.0833 | 0 | 8.0137 | 39.95
2022-09-30 02:30 | 44834.1042 | 0 | 7.9826 | 39.95
2022-09-30 03:00 | 44834.125 | 0 | 7.9158 | 39.95
2022-09-30 03:30 | 44834.1458 | 0 | 7.8551 | 39.95
2022-09-30 04:00 | 44834.1667 | 0 | 8.2095 | 39.95
2022-09-30 04:30 | 44834.1875 | 0 | 8.5722 | 39.95
2022-09-30 05:00 | 44834.2083 | 0 | 9.0952 | 39.95
2022-09-30 05:30 | 44834.2292 | 0 | 9.5706 | 39.95
2022-09-30 06:00 | 44834.25 | 0 | 9.872 | 39.95
2022-09-30 06:30 | 44834.2708 | 0 | 9.9696 | 39.95
2022-09-30 07:00 | 44834.2917 | 0 | 10.0271 | 39.95
2022-09-30 07:30 | 44834.3125 | 0 | 9.4269 | 39.95
2022-09-30 08:00 | 44834.3333 | 0 | 9.0128 | 39.95
2022-09-30 08:30 | 44834.3542 | 0 | 8.0568 | 39.95
2022-09-30 09:00 | 44834.375 | 0 | 7.7798 | 39.95
2022-09-30 09:30 | 44834.3958 | 0 | 7.356 | 39.95
2022-09-30 10:00 | 44834.4167 | 0 | 7.0815 | 39.95
2022-09-30 10:30 | 44834.4375 | 0 | 6.9565 | 39.95
2022-09-30 11:00 | 44834.4583 | 0 | 7.0634 | 39.95
2022-09-30 11:30 | 44834.4792 | 0 | 6.952 | 39.95
2022-09-30 12:00 | 44834.5 | 0 | 7.1116 | 39.95
2022-09-30 12:30 | 44834.5208 | 0 | 7.6658 | 39.95
2022-09-30 13:00 | 44834.5417 | 0 | 7.6762 | 39.95
2022-09-30 13:30 | 44834.5625 | 0 | 8.0703 | 39.95
2022-09-30 14:00 | 44834.5833 | 0 | 10.6862 | 39.95
2022-09-30 14:30 | 44834.6042 | 0 | 10.1825 | 39.95
2022-09-30 15:00 | 44834.625 | 0 | 9.3301 | 39.95
2022-09-30 15:30 | 44834.6458 | 0 | 10.1551 | 39.95
2022-09-30 16:00 | 44834.6667 | 0 | 11.2042 | 39.95
2022-09-30 16:30 | 44834.6875 | 0 | 11.9112 | 39.95
2022-09-30 17:00 | 44834.7083 | 0 | 12.3809 | 39.95
2022-09-30 17:30 | 44834.7292 | 0 | 12.4848 | 39.95
2022-09-30 18:00 | 44834.75 | 0 | 12.8967 | 39.95
2022-09-30 18:30 | 44834.7708 | 0 | 12.9467 | 39.95
2022-09-30 19:00 | 44834.7917 | 0 | 12.704 | 39.95
2022-09-30 19:30 | 44834.8125 | 0 | 12.4138 | 39.95
2022-09-30 20:00 | 44834.8333 | 0 | 12.2871 | 39.95
2022-09-30 20:30 | 44834.8542 | 0 | 11.7395 | 39.95
2022-09-30 21:00 | 44834.875 | 0 | 11.4421 | 39.95
2022-09-30 21:30 | 44834.8958 | 0 | 11.2393 | 39.95
2022-09-30 22:00 | 44834.9167 | 0 | 10.7946 | 39.95
2022-09-30 22:30 | 44834.9375 | 0 | 10.1419 | 39.95
2022-09-30 23:00 | 44834.9583 | 0 | 9.6837 | 39.95
2022-09-30 23:30 | 44834.9792 | 0 | 9.2996 | 39.95
2022-10-01 | 44835 | 0 | 8.7834 | 39.95
2022-10-01 00:30 | 44835.0208 | 0 | 8.532 | 39.95
2022-10-01 01:00 | 44835.0417 | 0 | 8.1866 | 39.95
2022-10-01 01:30 | 44835.0625 | 0 | 8.08 | 39.95
2022-10-01 02:00 | 44835.0833 | 0 | 7.9504 | 39.95
2022-10-01 02:30 | 44835.1042 | 0 | 7.9394 | 39.95
2022-10-01 03:00 | 44835.125 | 0 | 7.8831 | 39.95
2022-10-01 03:30 | 44835.1458 | 0 | 7.7828 | 39.95
2022-10-01 04:00 | 44835.1667 | 0 | 7.9001 | 39.95
2022-10-01 04:30 | 44835.1875 | 0 | 7.8599 | 39.95
2022-10-01 05:00 | 44835.2083 | 0 | 8.0671 | 39.95
2022-10-01 05:30 | 44835.2292 | 0 | 8.2253 | 39.95
2022-10-01 06:00 | 44835.25 | 0 | 8.2041 | 39.95
2022-10-01 06:30 | 44835.2708 | 0 | 8.0508 | 39.95
2022-10-01 07:00 | 44835.2917 | 0 | 7.5037 | 39.95
2022-10-01 07:30 | 44835.3125 | 0 | 7.1151 | 39.95
2022-10-01 08:00 | 44835.3333 | 0 | 6.4134 | 39.95
2022-10-01 08:30 | 44835.3542 | 0 | 6.6446 | 39.95
2022-10-01 09:00 | 44835.375 | 0 | 7.6757 | 39.95
2022-10-01 09:30 | 44835.3958 | 0 | 7.7908 | 39.95
2022-10-01 10:00 | 44835.4167 | 0 | 8.3203 | 39.95
2022-10-01 10:30 | 44835.4375 | 0 | 8.1651 | 39.95
2022-10-01 11:00 | 44835.4583 | 0 | 7.6298 | 39.95
2022-10-01 11:30 | 44835.4792 | 0 | 7.502 | 39.95
2022-10-01 12:00 | 44835.5 | 0 | 8.0582 | 39.95
2022-10-01 12:30 | 44835.5208 | 0 | 7.6797 | 39.95
2022-10-01 13:00 | 44835.5417 | 0 | 9.8484 | 39.95
2022-10-01 13:30 | 44835.5625 | 0 | 8.3807 | 39.95
2022-10-01 14:00 | 44835.5833 | 0 | 8.859 | 39.95
2022-10-01 14:30 | 44835.6042 | 0 | 9.6137 | 39.95
2022-10-01 15:00 | 44835.625 | 0 | 9.4698 | 39.95
2022-10-01 15:30 | 44835.6458 | 0 | 9.0001 | 39.95
2022-10-01 16:00 | 44835.6667 | 0 | 9.728 | 39.95
2022-10-01 16:30 | 44835.6875 | 0 | 10.2679 | 39.95
2022-10-01 17:00 | 44835.7083 | 0 | 10.6294 | 39.95
2022-10-01 17:30 | 44835.7292 | 0 | 10.9485 | 39.95
2022-10-01 18:00 | 44835.75 | 0 | 11.3816 | 39.95
2022-10-01 18:30 | 44835.7708 | 0 | 11.6322 | 39.95
2022-10-01 19:00 | 44835.7917 | 0 | 11.1697 | 39.95
2022-10-01 19:30 | 44835.8125 | 0 | 10.8567 | 39.95
2022-10-01 20:00 | 44835.8333 | 0 | 10.7768 | 39.95
2022-10-01 20:30 | 44835.8542 | 0 | 10.2431 | 39.95
2022-10-01 21:00 | 44835.875 | 0 | 10.1474 | 39.95
2022-10-01 21:30 | 44835.8958 | 0 | 9.7991 | 39.95
2022-10-01 22:00 | 44835.9167 | 0 | 9.4655 | 39.95
2022-10-01 22:30 | 44835.9375 | 0 | 9.0612 | 39.95
2022-10-01 23:00 | 44835.9583 | 0 | 8.6916 | 39.95
2022-10-01 23:30 | 44835.9792 | 0 | 8.4388 | 39.95
2022-10-02 | 44836 | 0 | 7.8525 | 39.95
2022-10-02 00:30 | 44836.0208 | 0 | 7.6127 | 39.95
2022-10-02 01:00 | 44836.0417 | 0 | 7.4377 | 39.95
2022-10-02 01:30 | 44836.0625 | 0 | 7.2504 | 39.95
2022-10-02 02:00 | 44836.0833 | 0 | 7.1351 | 39.95
2022-10-02 02:30 | 44836.1042 | 0 | 7.1554 | 39.95
2022-10-02 03:00 | 44836.125 | 0 | 7.0803 | 39.95
2022-10-02 03:30 | 44836.1458 | 0 | 6.9294 | 39.95
2022-10-02 04:00 | 44836.1667 | 0 | 6.958 | 39.95
2022-10-02 04:30 | 44836.1875 | 0 | 7.0101 | 39.95
2022-10-02 05:00 | 44836.2083 | 0 | 7.1098 | 39.95
2022-10-02 05:30 | 44836.2292 | 0 | 7.1497 | 39.95
2022-10-02 06:00 | 44836.25 | 0 | 6.9645 | 39.95
2022-10-02 06:30 | 44836.2708 | 0 | 6.7471 | 39.95
2022-10-02 07:00 | 44836.2917 | 0 | 8.1598 | 39.95
2022-10-02 07:30 | 44836.3125 | 0 | 8.8352 | 39.95
2022-10-02 08:00 | 44836.3333 | 0 | 9.4571 | 39.95
2022-10-02 08:30 | 44836.3542 | 0 | 9.3332 | 39.95
2022-10-02 09:00 | 44836.375 | 0 | 8.6952 | 39.95
2022-10-02 09:30 | 44836.3958 | 0 | 9.1967 | 39.95
2022-10-02 10:00 | 44836.4167 | 0 | 9.7628 | 39.95
2022-10-02 10:30 | 44836.4375 | 0 | 8.8973 | 39.95
2022-10-02 11:00 | 44836.4583 | 0 | 9.567 | 39.95
2022-10-02 11:30 | 44836.4792 | 0 | 9.7975 | 39.95
2022-10-02 12:00 | 44836.5 | 0 | 9.302 | 39.95
2022-10-02 12:30 | 44836.5208 | 0 | 8.2414 | 39.95
2022-10-02 13:00 | 44836.5417 | 0 | 6.6505 | 39.95
2022-10-02 13:30 | 44836.5625 | 0 | 6.6045 | 39.95
2022-10-02 14:00 | 44836.5833 | 0 | 7.4599 | 39.95
2022-10-02 14:30 | 44836.6042 | 0 | 8.5287 | 39.95
2022-10-02 15:00 | 44836.625 | 0 | 8.4464 | 39.95
2022-10-02 15:30 | 44836.6458 | 0 | 9.2028 | 39.95
2022-10-02 16:00 | 44836.6667 | 0 | 9.0238 | 39.95
2022-10-02 16:30 | 44836.6875 | 0 | 10.1512 | 39.95
2022-10-02 17:00 | 44836.7083 | 0 | 10.4713 | 39.95
2022-10-02 17:30 | 44836.7292 | 0 | 10.9118 | 39.95
2022-10-02 18:00 | 44836.75 | 0 | 11.5736 | 39.95
2022-10-02 18:30 | 44836.7708 | 0 | 11.6052 | 39.95
2022-10-02 19:00 | 44836.7917 | 0 | 11.3006 | 39.95
2022-10-02 19:30 | 44836.8125 | 0 | 10.9012 | 39.95
2022-10-02 20:00 | 44836.8333 | 0 | 10.766 | 39.95
2022-10-02 20:30 | 44836.8542 | 0 | 10.2561 | 39.95
2022-10-02 21:00 | 44836.875 | 0 | 9.9077 | 39.95
2022-10-02 21:30 | 44836.8958 | 0 | 9.7391 | 39.95
2022-10-02 22:00 | 44836.9167 | 0 | 9.3348 | 39.95
2022-10-02 22:30 | 44836.9375 | 0 | 8.7912 | 39.95
2022-10-02 23:00 | 44836.9583 | 0 | 8.3912 | 39.95
2022-10-02 23:30 | 44836.9792 | 0 | 8.0907 | 39.95
2022-10-03 | 44837 | 0 | 7.7846 | 39.95
2022-10-03 00:30 | 44837.0208 | 0 | 7.5184 | 39.95
2022-10-03 01:00 | 44837.0417 | 0 | 7.3873 | 39.95
2022-10-03 01:30 | 44837.0625 | 0 | 7.304 | 39.95
2022-10-03 02:00 | 44837.0833 | 0 | 7.2131 | 39.95
2022-10-03 02:30 | 44837.1042 | 0 | 7.2108 | 39.95
2022-10-03 03:00 | 44837.125 | 0 | 6.9597 | 39.95
2022-10-03 03:30 | 44837.1458 | 0 | 6.994 | 39.95
2022-10-03 04:00 | 44837.1667 | 0 | 7.0473 | 39.95
2022-10-03 04:30 | 44837.1875 | 0 | 7.1694 | 39.95
2022-10-03 05:00 | 44837.2083 | 0 | 7.4359 | 39.95
2022-10-03 05:30 | 44837.2292 | 0 | 7.5997 | 39.95
2022-10-03 06:00 | 44837.25 | 0 | 7.4049 | 39.95
2022-10-03 06:30 | 44837.2708 | 0 | 7.0095 | 39.95
2022-10-03 07:00 | 44837.2917 | 0 | 6.6994 | 39.95
2022-10-03 07:30 | 44837.3125 | 0 | 6.208 | 39.95
2022-10-03 08:00 | 44837.3333 | 0 | 5.7812 | 39.95
2022-10-03 08:30 | 44837.3542 | 0 | 5.4202 | 39.95
2022-10-03 09:00 | 44837.375 | 0 | 5.0618 | 39.95
2022-10-03 09:30 | 44837.3958 | 0 | 5.3912 | 39.95
2022-10-03 10:00 | 44837.4167 | 0 | 6.203 | 39.95
2022-10-03 10:30 | 44837.4375 | 0 | 5.898 | 39.95
2022-10-03 11:00 | 44837.4583 | 0 | 7.2785 | 39.95
2022-10-03 11:30 | 44837.4792 | 0 | 6.7029 | 39.95
2022-10-03 12:00 | 44837.5 | 0 | 7.0439 | 39.95
2022-10-03 12:30 | 44837.5208 | 0 | 5.3462 | 39.95
2022-10-03 13:00 | 44837.5417 | 0 | 6.882 | 39.95
2022-10-03 13:30 | 44837.5625 | 0 | 7.2192 | 39.95
2022-10-03 14:00 | 44837.5833 | 0 | 7.6741 | 39.95
2022-10-03 14:30 | 44837.6042 | 0 | 7.3693 | 39.95
2022-10-03 15:00 | 44837.625 | 0 | 7.1372 | 39.95
2022-10-03 15:30 | 44837.6458 | 0 | 8.217 | 39.95
2022-10-03 16:00 | 44837.6667 | 0 | 9.3731 | 39.95
2022-10-03 16:30 | 44837.6875 | 0 | 10.0911 | 39.95
2022-10-03 17:00 | 44837.7083 | 0 | 10.8824 | 39.95
2022-10-03 17:30 | 44837.7292 | 0 | 11.4677 | 39.95
2022-10-03 18:00 | 44837.75 | 0 | 12.2851 | 39.95
2022-10-03 18:30 | 44837.7708 | 0 | 12.2776 | 39.95
2022-10-03 19:00 | 44837.7917 | 0 | 12.0776 | 39.95
2022-10-03 19:30 | 44837.8125 | 0 | 11.6567 | 39.95
2022-10-03 20:00 | 44837.8333 | 0 | 11.3761 | 39.95
2022-10-03 20:30 | 44837.8542 | 0 | 10.8295 | 39.95
2022-10-03 21:00 | 44837.875 | 0 | 10.3084 | 39.95
2022-10-03 21:30 | 44837.8958 | 0 | 9.8517 | 39.95
2022-10-03 22:00 | 44837.9167 | 0 | 9.3589 | 39.95
2022-10-03 22:30 | 44837.9375 | 0 | 8.799 | 39.95
2022-10-03 23:00 | 44837.9583 | 0 | 8.3719 | 39.95
2022-10-03 23:30 | 44837.9792 | 0 | 8.0731 | 39.95
2022-10-04 | 44838 | 0 | 7.6666 | 39.95
2022-10-04 00:30 | 44838.0208 | 0 | 7.371 | 39.95
2022-10-04 01:00 | 44838.0417 | 0 | 7.3117 | 39.95
2022-10-04 01:30 | 44838.0625 | 0 | 7.2081 | 39.95
2022-10-04 02:00 | 44838.0833 | 0 | 7.2632 | 39.95
2022-10-04 02:30 | 44838.1042 | 0 | 7.2182 | 39.95
2022-10-04 03:00 | 44838.125 | 0 | 7.214 | 39.95
2022-10-04 03:30 | 44838.1458 | 0 | 7.2605 | 39.95
2022-10-04 04:00 | 44838.1667 | 0 | 7.6637 | 39.95
2022-10-04 04:30 | 44838.1875 | 0 | 8.1321 | 39.95
2022-10-04 05:00 | 44838.2083 | 0 | 8.8603 | 39.95
2022-10-04 05:30 | 44838.2292 | 0 | 9.4313 | 39.95
2022-10-04 06:00 | 44838.25 | 0 | 10.1542 | 39.95
2022-10-04 06:30 | 44838.2708 | 0 | 11.1044 | 39.95
2022-10-04 07:00 | 44838.2917 | 0 | 11.1778 | 39.95
2022-10-04 07:30 | 44838.3125 | 0 | 10.1652 | 39.95
2022-10-04 08:00 | 44838.3333 | 0 | 9.6298 | 39.95
2022-10-04 08:30 | 44838.3542 | 0 | 8.1829 | 39.95
2022-10-04 09:00 | 44838.375 | 0 | 8.9691 | 39.95
2022-10-04 09:30 | 44838.3958 | 0 | 10.1121 | 39.95
2022-10-04 10:00 | 44838.4167 | 0 | 9.6921 | 39.95
2022-10-04 10:30 | 44838.4375 | 0 | 10.7729 | 39.95
2022-10-04 11:00 | 44838.4583 | 0 | 11.4692 | 39.95
2022-10-04 11:30 | 44838.4792 | 0 | 11.3902 | 39.95
2022-10-04 12:00 | 44838.5 | 0 | 9.6642 | 39.95
2022-10-04 12:30 | 44838.5208 | 0 | 9.3925 | 39.95
2022-10-04 13:00 | 44838.5417 | 0 | 9.2642 | 39.95
2022-10-04 13:30 | 44838.5625 | 0 | 9.156 | 39.95
2022-10-04 14:00 | 44838.5833 | 0 | 8.8318 | 39.95
2022-10-04 14:30 | 44838.6042 | 0 | 9.4974 | 39.95
2022-10-04 15:00 | 44838.625 | 0 | 9.9937 | 39.95
2022-10-04 15:30 | 44838.6458 | 0 | 10.4728 | 39.95
2022-10-04 16:00 | 44838.6667 | 0 | 10.5277 | 39.95
2022-10-04 16:30 | 44838.6875 | 0 | 11.2919 | 39.95
2022-10-04 17:00 | 44838.7083 | 0 | 11.8985 | 39.95
2022-10-04 17:30 | 44838.7292 | 0 | 12.5899 | 39.95
2022-10-04 18:00 | 44838.75 | 0 | 13.385 | 39.95
2022-10-04 18:30 | 44838.7708 | 0 | 13.871 | 39.95
2022-10-04 19:00 | 44838.7917 | 0 | 13.4458 | 39.95
2022-10-04 19:30 | 44838.8125 | 0 | 12.9839 | 39.95
2022-10-04 20:00 | 44838.8333 | 0 | 12.712 | 39.95
2022-10-04 20:30 | 44838.8542 | 0 | 12.2127 | 39.95
2022-10-04 21:00 | 44838.875 | 0 | 11.8199 | 39.95
2022-10-04 21:30 | 44838.8958 | 0 | 11.2723 | 39.95
2022-10-04 22:00 | 44838.9167 | 0 | 10.7085 | 39.95
2022-10-04 22:30 | 44838.9375 | 0 | 10.0738 | 39.95
2022-10-04 23:00 | 44838.9583 | 0 | 9.5718 | 39.95
2022-10-04 23:30 | 44838.9792 | 0 | 9.1724 | 39.95
2022-10-05 | 44839 | 0 | 8.6332 | 39.95
2022-10-05 00:30 | 44839.0208 | 0 | 8.2774 | 39.95
2022-10-05 01:00 | 44839.0417 | 0 | 8.1464 | 39.95
2022-10-05 01:30 | 44839.0625 | 0 | 7.9376 | 39.95
2022-10-05 02:00 | 44839.0833 | 0 | 8.055 | 39.95
2022-10-05 02:30 | 44839.1042 | 0 | 7.8656 | 39.95
2022-10-05 03:00 | 44839.125 | 0 | 7.9531 | 39.95
2022-10-05 03:30 | 44839.1458 | 0 | 7.8228 | 39.95
2022-10-05 04:00 | 44839.1667 | 0 | 8.177 | 39.95
2022-10-05 04:30 | 44839.1875 | 0 | 8.6589 | 39.95
2022-10-05 05:00 | 44839.2083 | 0 | 9.2738 | 39.95
2022-10-05 05:30 | 44839.2292 | 0 | 9.6939 | 39.95
2022-10-05 06:00 | 44839.25 | 0 | 9.9378 | 39.95
2022-10-05 06:30 | 44839.2708 | 0 | 10.7066 | 39.95
2022-10-05 07:00 | 44839.2917 | 0 | 10.5639 | 39.95
2022-10-05 07:30 | 44839.3125 | 0 | 10.6045 | 39.95
2022-10-05 08:00 | 44839.3333 | 0 | 10.0653 | 39.95
2022-10-05 08:30 | 44839.3542 | 0 | 9.0593 | 39.95
2022-10-05 09:00 | 44839.375 | 0 | 10.0178 | 39.95
2022-10-05 09:30 | 44839.3958 | 0 | 8.2475 | 39.95
2022-10-05 10:00 | 44839.4167 | 0 | 8.687 | 39.95
2022-10-05 10:30 | 44839.4375 | 0 | 7.5937 | 39.95
2022-10-05 11:00 | 44839.4583 | 0 | 7.4193 | 39.95
2022-10-05 11:30 | 44839.4792 | 0 | 8.2616 | 39.95
2022-10-05 12:00 | 44839.5 | 0 | 7.2296 | 39.95
2022-10-05 12:30 | 44839.5208 | 0 | 7.9792 | 39.95
2022-10-05 13:00 | 44839.5417 | 0 | 8.0467 | 39.95
2022-10-05 13:30 | 44839.5625 | 0 | 7.7654 | 39.95
2022-10-05 14:00 | 44839.5833 | 0 | 10.4546 | 39.95
2022-10-05 14:30 | 44839.6042 | 0 | 11.0067 | 39.95
2022-10-05 15:00 | 44839.625 | 0 | 11.5137 | 39.95
2022-10-05 15:30 | 44839.6458 | 0 | 11.8555 | 39.95
2022-10-05 16:00 | 44839.6667 | 0 | 11.7669 | 39.95
2022-10-05 16:30 | 44839.6875 | 0 | 12.201 | 39.95
2022-10-05 17:00 | 44839.7083 | 0 | 12.6739 | 39.95
2022-10-05 17:30 | 44839.7292 | 0 | 13.1732 | 39.95
2022-10-05 18:00 | 44839.75 | 0 | 13.6846 | 39.95
2022-10-05 18:30 | 44839.7708 | 0 | 13.922 | 39.95
2022-10-05 19:00 | 44839.7917 | 0 | 13.5839 | 39.95
2022-10-05 19:30 | 44839.8125 | 0 | 13.0729 | 39.95
2022-10-05 20:00 | 44839.8333 | 0 | 12.8902 | 39.95
2022-10-05 20:30 | 44839.8542 | 0 | 12.3233 | 39.95
2022-10-05 21:00 | 44839.875 | 0 | 11.7835 | 39.95
2022-10-05 21:30 | 44839.8958 | 0 | 11.4054 | 39.95
2022-10-05 22:00 | 44839.9167 | 0 | 10.9111 | 39.95
2022-10-05 22:30 | 44839.9375 | 0 | 10.2022 | 39.95
2022-10-05 23:00 | 44839.9583 | 0 | 9.9026 | 39.95
2022-10-05 23:30 | 44839.9792 | 0 | 9.4624 | 39.95
2022-10-06 | 44840 | 0 | 8.8449 | 39.95
2022-10-06 00:30 | 44840.0208 | 0 | 8.5034 | 39.95
2022-10-06 01:00 | 44840.0417 | 0 | 8.3456 | 39.95
2022-10-06 01:30 | 44840.0625 | 0 | 8.1169 | 39.95
2022-10-06 02:00 | 44840.0833 | 0 | 7.9841 | 39.95
2022-10-06 02:30 | 44840.1042 | 0 | 8.0969 | 39.95
2022-10-06 03:00 | 44840.125 | 0 | 7.8816 | 39.95
2022-10-06 03:30 | 44840.1458 | 0 | 8.0392 | 39.95
2022-10-06 04:00 | 44840.1667 | 0 | 8.2519 | 39.95
2022-10-06 04:30 | 44840.1875 | 0 | 8.7428 | 39.95
2022-10-06 05:00 | 44840.2083 | 0 | 9.3304 | 39.95
2022-10-06 05:30 | 44840.2292 | 0 | 9.9632 | 39.95
2022-10-06 06:00 | 44840.25 | 0 | 10.8095 | 39.95
2022-10-06 06:30 | 44840.2708 | 0 | 11.2122 | 39.95
2022-10-06 07:00 | 44840.2917 | 0 | 11.5388 | 39.95
2022-10-06 07:30 | 44840.3125 | 0 | 10.7438 | 39.95
2022-10-06 08:00 | 44840.3333 | 0 | 10.6863 | 39.95
2022-10-06 08:30 | 44840.3542 | 0 | 9.6808 | 39.95
2022-10-06 09:00 | 44840.375 | 0 | 9.0295 | 39.95
2022-10-06 09:30 | 44840.3958 | 0 | 10.1441 | 39.95
2022-10-06 10:00 | 44840.4167 | 0 | 11.1503 | 39.95
2022-10-06 10:30 | 44840.4375 | 0 | 10.846 | 39.95
2022-10-06 11:00 | 44840.4583 | 0 | 11.1249 | 39.95
2022-10-06 11:30 | 44840.4792 | 0 | 11.8318 | 39.95
2022-10-06 12:00 | 44840.5 | 0 | 12.1408 | 39.95
2022-10-06 12:30 | 44840.5208 | 0 | 11.9684 | 39.95
2022-10-06 13:00 | 44840.5417 | 0 | 10.9912 | 39.95
2022-10-06 13:30 | 44840.5625 | 0 | 11.1037 | 39.95
2022-10-06 14:00 | 44840.5833 | 0 | 11.4814 | 39.95
2022-10-06 14:30 | 44840.6042 | 0 | 11.6599 | 39.95
2022-10-06 15:00 | 44840.625 | 0 | 11.7074 | 39.95
2022-10-06 15:30 | 44840.6458 | 0 | 11.3081 | 39.95
2022-10-06 16:00 | 44840.6667 | 0 | 11.5198 | 39.95
2022-10-06 16:30 | 44840.6875 | 0 | 12.1904 | 39.95
2022-10-06 17:00 | 44840.7083 | 0 | 12.4988 | 39.95
2022-10-06 17:30 | 44840.7292 | 0 | 13.1433 | 39.95
2022-10-06 18:00 | 44840.75 | 0 | 13.5465 | 39.95
2022-10-06 18:30 | 44840.7708 | 0 | 13.9001 | 39.95
2022-10-06 19:00 | 44840.7917 | 0 | 13.5279 | 39.95
2022-10-06 19:30 | 44840.8125 | 0 | 13.0268 | 39.95
2022-10-06 20:00 | 44840.8333 | 0 | 12.8613 | 39.95
2022-10-06 20:30 | 44840.8542 | 0 | 12.3669 | 39.95
2022-10-06 21:00 | 44840.875 | 0 | 11.8864 | 39.95
2022-10-06 21:30 | 44840.8958 | 0 | 11.4924 | 39.95
2022-10-06 22:00 | 44840.9167 | 0 | 10.9729 | 39.95
2022-10-06 22:30 | 44840.9375 | 0 | 10.3991 | 39.95
2022-10-06 23:00 | 44840.9583 | 0 | 9.8377 | 39.95
2022-10-06 23:30 | 44840.9792 | 0 | 9.4803 | 39.95
2022-10-07 | 44841 | 0 | 8.8541 | 39.95
2022-10-07 00:30 | 44841.0208 | 0 | 8.5391 | 39.95
2022-10-07 01:00 | 44841.0417 | 0 | 8.311 | 39.95
2022-10-07 01:30 | 44841.0625 | 0 | 8.0977 | 39.95
2022-10-07 02:00 | 44841.0833 | 0 | 8.1166 | 39.95
2022-10-07 02:30 | 44841.1042 | 0 | 7.934 | 39.95
2022-10-07 03:00 | 44841.125 | 0 | 7.9778 | 39.95
2022-10-07 03:30 | 44841.1458 | 0 | 7.9802 | 39.95
2022-10-07 04:00 | 44841.1667 | 0 | 8.3262 | 39.95
2022-10-07 04:30 | 44841.1875 | 0 | 8.8163 | 39.95
2022-10-07 05:00 | 44841.2083 | 0 | 9.2246 | 39.95
2022-10-07 05:30 | 44841.2292 | 0 | 9.7677 | 39.95
2022-10-07 06:00 | 44841.25 | 0 | 10.0978 | 39.95
2022-10-07 06:30 | 44841.2708 | 0 | 10.2709 | 39.95
2022-10-07 07:00 | 44841.2917 | 0 | 10.4005 | 39.95
2022-10-07 07:30 | 44841.3125 | 0 | 9.9952 | 39.95
2022-10-07 08:00 | 44841.3333 | 0 | 10.1322 | 39.95
2022-10-07 08:30 | 44841.3542 | 0 | 10.9824 | 39.95
2022-10-07 09:00 | 44841.375 | 0 | 11.1099 | 39.95
2022-10-07 09:30 | 44841.3958 | 0 | 11.3668 | 39.95
2022-10-07 10:00 | 44841.4167 | 0 | 10.2973 | 39.95
2022-10-07 10:30 | 44841.4375 | 0 | 10.6598 | 39.95
2022-10-07 11:00 | 44841.4583 | 0 | 10.156 | 39.95
2022-10-07 11:30 | 44841.4792 | 0 | 11.0706 | 39.95
2022-10-07 12:00 | 44841.5 | 0 | 10.6369 | 39.95
2022-10-07 12:30 | 44841.5208 | 0 | 10.1799 | 39.95
2022-10-07 13:00 | 44841.5417 | 0 | 9.2611 | 39.95
2022-10-07 13:30 | 44841.5625 | 0 | 8.1895 | 39.95
2022-10-07 14:00 | 44841.5833 | 0 | 7.9154 | 39.95
2022-10-07 14:30 | 44841.6042 | 0 | 9.5985 | 39.95
2022-10-07 15:00 | 44841.625 | 0 | 10.4323 | 39.95
2022-10-07 15:30 | 44841.6458 | 0 | 10.5349 | 39.95
2022-10-07 16:00 | 44841.6667 | 0 | 10.8789 | 39.95
2022-10-07 16:30 | 44841.6875 | 0 | 12.0278 | 39.95
2022-10-07 17:00 | 44841.7083 | 0 | 12.3017 | 39.95
2022-10-07 17:30 | 44841.7292 | 0 | 12.4554 | 39.95
2022-10-07 18:00 | 44841.75 | 0 | 12.8981 | 39.95
2022-10-07 18:30 | 44841.7708 | 0 | 13.3207 | 39.95
2022-10-07 19:00 | 44841.7917 | 0 | 12.927 | 39.95
2022-10-07 19:30 | 44841.8125 | 0 | 12.6311 | 39.95
2022-10-07 20:00 | 44841.8333 | 0 | 12.4451 | 39.95
2022-10-07 20:30 | 44841.8542 | 0 | 12.1612 | 39.95
2022-10-07 21:00 | 44841.875 | 0 | 11.7534 | 39.95
2022-10-07 21:30 | 44841.8958 | 0 | 11.3551 | 39.95
2022-10-07 22:00 | 44841.9167 | 0 | 11.0948 | 39.95
2022-10-07 22:30 | 44841.9375 | 0 | 10.5552 | 39.95
2022-10-07 23:00 | 44841.9583 | 0 | 10.0786 | 39.95
2022-10-07 23:30 | 44841.9792 | 0 | 9.6361 | 39.95
2022-10-08 | 44842 | 0 | 9.0468 | 39.95
2022-10-08 00:30 | 44842.0208 | 0 | 8.7452 | 39.95
2022-10-08 01:00 | 44842.0417 | 0 | 8.5159 | 39.95
2022-10-08 01:30 | 44842.0625 | 0 | 8.2366 | 39.95
2022-10-08 02:00 | 44842.0833 | 0 | 8.2273 | 39.95
2022-10-08 02:30 | 44842.1042 | 0 | 8.191 | 39.95
2022-10-08 03:00 | 44842.125 | 0 | 8.0073 | 39.95
2022-10-08 03:30 | 44842.1458 | 0 | 7.9876 | 39.95
2022-10-08 04:00 | 44842.1667 | 0 | 8.0573 | 39.95
2022-10-08 04:30 | 44842.1875 | 0 | 8.0022 | 39.95
2022-10-08 05:00 | 44842.2083 | 0 | 8.0934 | 39.95
2022-10-08 05:30 | 44842.2292 | 0 | 8.2723 | 39.95
2022-10-08 06:00 | 44842.25 | 0 | 8.3941 | 39.95
2022-10-08 06:30 | 44842.2708 | 0 | 8.9361 | 39.95
2022-10-08 07:00 | 44842.2917 | 0 | 9.5701 | 39.95
2022-10-08 07:30 | 44842.3125 | 0 | 9.9449 | 39.95
2022-10-08 08:00 | 44842.3333 | 0 | 9.3869 | 39.95
2022-10-08 08:30 | 44842.3542 | 0 | 8.0104 | 39.95
2022-10-08 09:00 | 44842.375 | 0 | 8.9164 | 39.95
2022-10-08 09:30 | 44842.3958 | 0 | 7.1669 | 39.95
2022-10-08 10:00 | 44842.4167 | 0 | 6.5155 | 39.95
2022-10-08 10:30 | 44842.4375 | 0 | 7.2548 | 39.95
2022-10-08 11:00 | 44842.4583 | 0 | 6.7183 | 39.95
2022-10-08 11:30 | 44842.4792 | 0 | 6.3773 | 39.95
2022-10-08 12:00 | 44842.5 | 0 | 5.099 | 39.95
2022-10-08 12:30 | 44842.5208 | 0 | 5.5291 | 39.95
2022-10-08 13:00 | 44842.5417 | 0 | 8.7924 | 39.95
2022-10-08 13:30 | 44842.5625 | 0 | 6.6083 | 39.95
2022-10-08 14:00 | 44842.5833 | 0 | 7.5528 | 39.95
2022-10-08 14:30 | 44842.6042 | 0 | 8.3378 | 39.95
2022-10-08 15:00 | 44842.625 | 0 | 8.5348 | 39.95
2022-10-08 15:30 | 44842.6458 | 0 | 8.9516 | 39.95
2022-10-08 16:00 | 44842.6667 | 0 | 9.3613 | 39.95
2022-10-08 16:30 | 44842.6875 | 0 | 9.9223 | 39.95
2022-10-08 17:00 | 44842.7083 | 0 | 11.0433 | 39.95
2022-10-08 17:30 | 44842.7292 | 0 | 11.4606 | 39.95
2022-10-08 18:00 | 44842.75 | 0 | 11.8068 | 39.95
2022-10-08 18:30 | 44842.7708 | 0 | 11.9905 | 39.95
2022-10-08 19:00 | 44842.7917 | 0 | 11.7395 | 39.95
2022-10-08 19:30 | 44842.8125 | 0 | 11.4391 | 39.95
2022-10-08 20:00 | 44842.8333 | 0 | 11.2045 | 39.95
2022-10-08 20:30 | 44842.8542 | 0 | 10.7554 | 39.95
2022-10-08 21:00 | 44842.875 | 0 | 10.4869 | 39.95
2022-10-08 21:30 | 44842.8958 | 0 | 10.2409 | 39.95
2022-10-08 22:00 | 44842.9167 | 0 | 10.114 | 39.95
2022-10-08 22:30 | 44842.9375 | 0 | 9.3358 | 39.95
2022-10-08 23:00 | 44842.9583 | 0 | 9.2585 | 39.95
2022-10-08 23:30 | 44842.9792 | 0 | 8.8351 | 39.95
2022-10-09 | 44843 | 0 | 8.3277 | 39.95
2022-10-09 00:30 | 44843.0208 | 0 | 8.0121 | 39.95
2022-10-09 01:00 | 44843.0417 | 0 | 7.8796 | 39.95
2022-10-09 01:30 | 44843.0625 | 0 | 7.7092 | 39.95
2022-10-09 02:00 | 44843.0833 | 0 | 7.6351 | 39.95
2022-10-09 02:30 | 44843.1042 | 0 | 7.5681 | 39.95
2022-10-09 03:00 | 44843.125 | 0 | 7.4389 | 39.95
2022-10-09 03:30 | 44843.1458 | 0 | 7.4517 | 39.95
2022-10-09 04:00 | 44843.1667 | 0 | 7.2766 | 39.95
2022-10-09 04:30 | 44843.1875 | 0 | 7.4389 | 39.95
2022-10-09 05:00 | 44843.2083 | 0 | 7.552 | 39.95
2022-10-09 05:30 | 44843.2292 | 0 | 7.6232 | 39.95
2022-10-09 06:00 | 44843.25 | 0 | 7.9421 | 39.95
2022-10-09 06:30 | 44843.2708 | 0 | 7.7321 | 39.95
2022-10-09 07:00 | 44843.2917 | 0 | 8.1029 | 39.95
2022-10-09 07:30 | 44843.3125 | 0 | 8.0689 | 39.95
2022-10-09 08:00 | 44843.3333 | 0 | 9.1211 | 39.95
2022-10-09 08:30 | 44843.3542 | 0 | 9.107 | 39.95
2022-10-09 09:00 | 44843.375 | 0 | 8.8461 | 39.95
2022-10-09 09:30 | 44843.3958 | 0 | 8.7195 | 39.95
2022-10-09 10:00 | 44843.4167 | 0 | 8.592 | 39.95
2022-10-09 10:30 | 44843.4375 | 0 | 9.9297 | 39.95
2022-10-09 11:00 | 44843.4583 | 0 | 9.8829 | 39.95
2022-10-09 11:30 | 44843.4792 | 0 | 10.0403 | 39.95
2022-10-09 12:00 | 44843.5 | 0 | 6.369 | 39.95
2022-10-09 12:30 | 44843.5208 | 0 | 7.1742 | 39.95
2022-10-09 13:00 | 44843.5417 | 0 | 7.5236 | 39.95
2022-10-09 13:30 | 44843.5625 | 0 | 5.865 | 39.95
2022-10-09 14:00 | 44843.5833 | 0 | 6.9177 | 39.95
2022-10-09 14:30 | 44843.6042 | 0 | 7.9258 | 39.95
2022-10-09 15:00 | 44843.625 | 0 | 7.6597 | 39.95
2022-10-09 15:30 | 44843.6458 | 0 | 8.507 | 39.95
2022-10-09 16:00 | 44843.6667 | 0 | 9.1099 | 39.95
2022-10-09 16:30 | 44843.6875 | 0 | 10.4762 | 39.95
2022-10-09 17:00 | 44843.7083 | 0 | 11.2646 | 39.95
2022-10-09 17:30 | 44843.7292 | 0 | 11.7989 | 39.95
2022-10-09 18:00 | 44843.75 | 0 | 12.4938 | 39.95
2022-10-09 18:30 | 44843.7708 | 0 | 12.9658 | 39.95
2022-10-09 19:00 | 44843.7917 | 0 | 12.5805 | 39.95
2022-10-09 19:30 | 44843.8125 | 0 | 11.9682 | 39.95
2022-10-09 20:00 | 44843.8333 | 0 | 11.5862 | 39.95
2022-10-09 20:30 | 44843.8542 | 0 | 11.193 | 39.95
2022-10-09 21:00 | 44843.875 | 0 | 10.6 | 39.95
2022-10-09 21:30 | 44843.8958 | 0 | 10.2203 | 39.95
2022-10-09 22:00 | 44843.9167 | 0 | 9.4993 | 39.95
2022-10-09 22:30 | 44843.9375 | 0 | 8.9918 | 39.95
2022-10-09 23:00 | 44843.9583 | 0 | 8.498 | 39.95
2022-10-09 23:30 | 44843.9792 | 0 | 8.256 | 39.95
2022-10-10 | 44844 | 0 | 7.9969 | 39.95
2022-10-10 00:30 | 44844.0208 | 0 | 7.6339 | 39.95
2022-10-10 01:00 | 44844.0417 | 0 | 7.6562 | 39.95
2022-10-10 01:30 | 44844.0625 | 0 | 7.5976 | 39.95
2022-10-10 02:00 | 44844.0833 | 0 | 7.4791 | 39.95
2022-10-10 02:30 | 44844.1042 | 0 | 7.623 | 39.95
2022-10-10 03:00 | 44844.125 | 0 | 7.5276 | 39.95
2022-10-10 03:30 | 44844.1458 | 0 | 7.5609 | 39.95
2022-10-10 04:00 | 44844.1667 | 0 | 7.9357 | 39.95
2022-10-10 04:30 | 44844.1875 | 0 | 8.395 | 39.95
2022-10-10 05:00 | 44844.2083 | 0 | 8.9745 | 39.95
2022-10-10 05:30 | 44844.2292 | 0 | 9.8188 | 39.95
2022-10-10 06:00 | 44844.25 | 0 | 10.5847 | 39.95
2022-10-10 06:30 | 44844.2708 | 0 | 10.7116 | 39.95
2022-10-10 07:00 | 44844.2917 | 0 | 11.1854 | 39.95
2022-10-10 07:30 | 44844.3125 | 0 | 10.8295 | 39.95
2022-10-10 08:00 | 44844.3333 | 0 | 11.7698 | 39.95
2022-10-10 08:30 | 44844.3542 | 0 | 12.8684 | 39.95
2022-10-10 09:00 | 44844.375 | 0 | 12.8778 | 39.95
2022-10-10 09:30 | 44844.3958 | 0 | 12.9578 | 39.95
2022-10-10 10:00 | 44844.4167 | 0 | 12.7412 | 39.95
2022-10-10 10:30 | 44844.4375 | 0 | 12.345 | 39.95
2022-10-10 11:00 | 44844.4583 | 0 | 12.2204 | 39.95
2022-10-10 11:30 | 44844.4792 | 0 | 11.6925 | 39.95
2022-10-10 12:00 | 44844.5 | 0 | 10.847 | 39.95
2022-10-10 12:30 | 44844.5208 | 0 | 11.2373 | 39.95
2022-10-10 13:00 | 44844.5417 | 0 | 11.8938 | 39.95
2022-10-10 13:30 | 44844.5625 | 0 | 11.0455 | 39.95
2022-10-10 14:00 | 44844.5833 | 0 | 11.3007 | 39.95
2022-10-10 14:30 | 44844.6042 | 0 | 11.3999 | 39.95
2022-10-10 15:00 | 44844.625 | 0 | 11.5908 | 39.95
2022-10-10 15:30 | 44844.6458 | 0 | 11.4662 | 39.95
2022-10-10 16:00 | 44844.6667 | 0 | 11.2181 | 39.95
2022-10-10 16:30 | 44844.6875 | 0 | 11.7234 | 39.95
2022-10-10 17:00 | 44844.7083 | 0 | 12.2958 | 39.95
2022-10-10 17:30 | 44844.7292 | 0 | 12.757 | 39.95
2022-10-10 18:00 | 44844.75 | 0 | 13.4805 | 39.95
2022-10-10 18:30 | 44844.7708 | 0 | 13.8537 | 39.95
2022-10-10 19:00 | 44844.7917 | 0 | 13.5208 | 39.95
2022-10-10 19:30 | 44844.8125 | 0 | 13.0033 | 39.95
2022-10-10 20:00 | 44844.8333 | 0 | 12.4555 | 39.95
2022-10-10 20:30 | 44844.8542 | 0 | 12.1111 | 39.95
2022-10-10 21:00 | 44844.875 | 0 | 11.5009 | 39.95
2022-10-10 21:30 | 44844.8958 | 0 | 11.3274 | 39.95
2022-10-10 22:00 | 44844.9167 | 0 | 10.7316 | 39.95
2022-10-10 22:30 | 44844.9375 | 0 | 9.9656 | 39.95
2022-10-10 23:00 | 44844.9583 | 0 | 9.486 | 39.95
2022-10-10 23:30 | 44844.9792 | 0 | 9.0719 | 39.95
2022-10-11 | 44845 | 0 | 8.4844 | 39.95
2022-10-11 00:30 | 44845.0208 | 0 | 8.2227 | 39.95
2022-10-11 01:00 | 44845.0417 | 0 | 7.9591 | 39.95
2022-10-11 01:30 | 44845.0625 | 0 | 7.9379 | 39.95
2022-10-11 02:00 | 44845.0833 | 0 | 7.7952 | 39.95
2022-10-11 02:30 | 44845.1042 | 0 | 7.7506 | 39.95
2022-10-11 03:00 | 44845.125 | 0 | 7.672 | 39.95
2022-10-11 03:30 | 44845.1458 | 0 | 7.6806 | 39.95
2022-10-11 04:00 | 44845.1667 | 0 | 7.9832 | 39.95
2022-10-11 04:30 | 44845.1875 | 0 | 8.3036 | 39.95
2022-10-11 05:00 | 44845.2083 | 0 | 9.0248 | 39.95
2022-10-11 05:30 | 44845.2292 | 0 | 9.6597 | 39.95
2022-10-11 06:00 | 44845.25 | 0 | 10.0275 | 39.95
2022-10-11 06:30 | 44845.2708 | 0 | 10.146 | 39.95
2022-10-11 07:00 | 44845.2917 | 0 | 10.022 | 39.95
2022-10-11 07:30 | 44845.3125 | 0 | 9.5109 | 39.95
2022-10-11 08:00 | 44845.3333 | 0 | 9.0276 | 39.95
2022-10-11 08:30 | 44845.3542 | 0 | 9.004 | 39.95
2022-10-11 09:00 | 44845.375 | 0 | 8.4363 | 39.95
2022-10-11 09:30 | 44845.3958 | 0 | 8.6485 | 39.95
2022-10-11 10:00 | 44845.4167 | 0 | 8.5441 | 39.95
2022-10-11 10:30 | 44845.4375 | 0 | 7.8464 | 39.95
2022-10-11 11:00 | 44845.4583 | 0 | 8.7931 | 39.95
2022-10-11 11:30 | 44845.4792 | 0 | 8.0978 | 39.95
2022-10-11 12:00 | 44845.5 | 0 | 8.1475 | 39.95
2022-10-11 12:30 | 44845.5208 | 0 | 7.4469 | 39.95
2022-10-11 13:00 | 44845.5417 | 0 | 8.8722 | 39.95
2022-10-11 13:30 | 44845.5625 | 0 | 10.0449 | 39.95
2022-10-11 14:00 | 44845.5833 | 0 | 10.6393 | 39.95
2022-10-11 14:30 | 44845.6042 | 0 | 10.6375 | 39.95
2022-10-11 15:00 | 44845.625 | 0 | 10.5156 | 39.95
2022-10-11 15:30 | 44845.6458 | 0 | 10.9647 | 39.95
2022-10-11 16:00 | 44845.6667 | 0 | 10.9191 | 39.95
2022-10-11 16:30 | 44845.6875 | 0 | 11.6634 | 39.95
2022-10-11 17:00 | 44845.7083 | 0 | 12.3583 | 39.95
2022-10-11 17:30 | 44845.7292 | 0 | 12.8269 | 39.95
2022-10-11 18:00 | 44845.75 | 0 | 13.3389 | 39.95
2022-10-11 18:30 | 44845.7708 | 0 | 13.7247 | 39.95
2022-10-11 19:00 | 44845.7917 | 0 | 13.4713 | 39.95
2022-10-11 19:30 | 44845.8125 | 0 | 13.0223 | 39.95
2022-10-11 20:00 | 44845.8333 | 0 | 12.7783 | 39.95
2022-10-11 20:30 | 44845.8542 | 0 | 11.9629 | 39.95
2022-10-11 21:00 | 44845.875 | 0 | 11.676 | 39.95
2022-10-11 21:30 | 44845.8958 | 0 | 11.4221 | 39.95
2022-10-11 22:00 | 44845.9167 | 0 | 10.7177 | 39.95
2022-10-11 22:30 | 44845.9375 | 0 | 10.122 | 39.95
2022-10-11 23:00 | 44845.9583 | 0 | 9.6854 | 39.95
2022-10-11 23:30 | 44845.9792 | 0 | 9.2346 | 39.95
2022-10-12 | 44846 | 0 | 8.7389 | 39.95
2022-10-12 00:30 | 44846.0208 | 0 | 8.3215 | 39.95
2022-10-12 01:00 | 44846.0417 | 0 | 8.2643 | 39.95
2022-10-12 01:30 | 44846.0625 | 0 | 8.1708 | 39.95
2022-10-12 02:00 | 44846.0833 | 0 | 8.0797 | 39.95
2022-10-12 02:30 | 44846.1042 | 0 | 8.001 | 39.95
2022-10-12 03:00 | 44846.125 | 0 | 7.929 | 39.95
2022-10-12 03:30 | 44846.1458 | 0 | 7.8736 | 39.95
2022-10-12 04:00 | 44846.1667 | 0 | 8.1014 | 39.95
2022-10-12 04:30 | 44846.1875 | 0 | 8.4277 | 39.95
2022-10-12 05:00 | 44846.2083 | 0 | 9.0421 | 39.95
2022-10-12 05:30 | 44846.2292 | 0 | 9.6787 | 39.95
2022-10-12 06:00 | 44846.25 | 0 | 10.3644 | 39.95
2022-10-12 06:30 | 44846.2708 | 0 | 11.132 | 39.95
2022-10-12 07:00 | 44846.2917 | 0 | 10.4396 | 39.95
2022-10-12 07:30 | 44846.3125 | 0 | 9.6543 | 39.95
2022-10-12 08:00 | 44846.3333 | 0 | 8.8961 | 39.95
2022-10-12 08:30 | 44846.3542 | 0 | 8.5493 | 39.95
2022-10-12 09:00 | 44846.375 | 0 | 8.3512 | 39.95
2022-10-12 09:30 | 44846.3958 | 0 | 9.088 | 39.95
2022-10-12 10:00 | 44846.4167 | 0 | 10.2272 | 39.95
2022-10-12 10:30 | 44846.4375 | 0 | 8.7413 | 39.95
2022-10-12 11:00 | 44846.4583 | 0 | 8.2232 | 39.95
2022-10-12 11:30 | 44846.4792 | 0 | 8.2155 | 39.95
2022-10-12 12:00 | 44846.5 | 0 | 9.1708 | 39.95
2022-10-12 12:30 | 44846.5208 | 0 | 7.9565 | 39.95
2022-10-12 13:00 | 44846.5417 | 0 | 8.8352 | 39.95
2022-10-12 13:30 | 44846.5625 | 0 | 9.1461 | 39.95
2022-10-12 14:00 | 44846.5833 | 0 | 9.224 | 39.95
2022-10-12 14:30 | 44846.6042 | 0 | 9.7736 | 39.95
2022-10-12 15:00 | 44846.625 | 0 | 9.0794 | 39.95
2022-10-12 15:30 | 44846.6458 | 0 | 10.3654 | 39.95
2022-10-12 16:00 | 44846.6667 | 0 | 10.527 | 39.95
2022-10-12 16:30 | 44846.6875 | 0 | 11.3478 | 39.95
2022-10-12 17:00 | 44846.7083 | 0 | 12.2252 | 39.95
2022-10-12 17:30 | 44846.7292 | 0 | 13.0347 | 39.95
2022-10-12 18:00 | 44846.75 | 0 | 13.5337 | 39.95
2022-10-12 18:30 | 44846.7708 | 0 | 13.7209 | 39.95
2022-10-12 19:00 | 44846.7917 | 0 | 13.7008 | 39.95
2022-10-12 19:30 | 44846.8125 | 0 | 13.0337 | 39.95
2022-10-12 20:00 | 44846.8333 | 0 | 12.8779 | 39.95
2022-10-12 20:30 | 44846.8542 | 0 | 12.1727 | 39.95
2022-10-12 21:00 | 44846.875 | 0 | 11.7487 | 39.95
2022-10-12 21:30 | 44846.8958 | 0 | 11.4016 | 39.95
2022-10-12 22:00 | 44846.9167 | 0 | 10.8754 | 39.95
2022-10-12 22:30 | 44846.9375 | 0 | 10.2244 | 39.95
2022-10-12 23:00 | 44846.9583 | 0 | 9.5783 | 39.95
2022-10-12 23:30 | 44846.9792 | 0 | 9.225 | 39.95
2022-10-13 | 44847 | 0 | 8.5403 | 39.95
2022-10-13 00:30 | 44847.0208 | 0 | 8.4081 | 39.95
2022-10-13 01:00 | 44847.0417 | 0 | 8.1537 | 39.95
2022-10-13 01:30 | 44847.0625 | 0 | 8.0043 | 39.95
2022-10-13 02:00 | 44847.0833 | 0 | 7.9206 | 39.95
2022-10-13 02:30 | 44847.1042 | 0 | 7.9072 | 39.95
2022-10-13 03:00 | 44847.125 | 0 | 7.7801 | 39.95
2022-10-13 03:30 | 44847.1458 | 0 | 7.8093 | 39.95
2022-10-13 04:00 | 44847.1667 | 0 | 8.0532 | 39.95
2022-10-13 04:30 | 44847.1875 | 0 | 8.4413 | 39.95
2022-10-13 05:00 | 44847.2083 | 0 | 9.0444 | 39.95
2022-10-13 05:30 | 44847.2292 | 0 | 9.5343 | 39.95
2022-10-13 06:00 | 44847.25 | 0 | 10.028 | 39.95
2022-10-13 06:30 | 44847.2708 | 0 | 9.8631 | 39.95
2022-10-13 07:00 | 44847.2917 | 0 | 10.2247 | 39.95
2022-10-13 07:30 | 44847.3125 | 0 | 10.7184 | 39.95
2022-10-13 08:00 | 44847.3333 | 0 | 10.4002 | 39.95
2022-10-13 08:30 | 44847.3542 | 0 | 10.6082 | 39.95
2022-10-13 09:00 | 44847.375 | 0 | 8.2871 | 39.95
2022-10-13 09:30 | 44847.3958 | 0 | 8.8213 | 39.95
2022-10-13 10:00 | 44847.4167 | 0 | 9.7266 | 39.95
2022-10-13 10:30 | 44847.4375 | 0 | 9.3962 | 39.95
2022-10-13 11:00 | 44847.4583 | 0 | 9.725 | 39.95
2022-10-13 11:30 | 44847.4792 | 0 | 9.2045 | 39.95
2022-10-13 12:00 | 44847.5 | 0 | 7.967 | 39.95
2022-10-13 12:30 | 44847.5208 | 0 | 7.6714 | 39.95
2022-10-13 13:00 | 44847.5417 | 0 | 7.8522 | 39.95
2022-10-13 13:30 | 44847.5625 | 0 | 8.207 | 39.95
2022-10-13 14:00 | 44847.5833 | 0 | 8.7455 | 39.95
2022-10-13 14:30 | 44847.6042 | 0 | 9.0706 | 39.95
2022-10-13 15:00 | 44847.625 | 0 | 10.4458 | 39.95
2022-10-13 15:30 | 44847.6458 | 0 | 11.2032 | 39.95
2022-10-13 16:00 | 44847.6667 | 0 | 11.2645 | 39.95
2022-10-13 16:30 | 44847.6875 | 0 | 12.2728 | 39.95
2022-10-13 17:00 | 44847.7083 | 0 | 12.7721 | 39.95
2022-10-13 17:30 | 44847.7292 | 0 | 13.3551 | 39.95
2022-10-13 18:00 | 44847.75 | 0 | 13.7605 | 39.95
2022-10-13 18:30 | 44847.7708 | 0 | 14.1105 | 39.95
2022-10-13 19:00 | 44847.7917 | 0 | 13.7897 | 39.95
2022-10-13 19:30 | 44847.8125 | 0 | 13.4368 | 39.95
2022-10-13 20:00 | 44847.8333 | 0 | 13.186 | 39.95
2022-10-13 20:30 | 44847.8542 | 0 | 12.5591 | 39.95
2022-10-13 21:00 | 44847.875 | 0 | 12.1164 | 39.95
2022-10-13 21:30 | 44847.8958 | 0 | 11.6713 | 39.95
2022-10-13 22:00 | 44847.9167 | 0 | 11.2309 | 39.95
2022-10-13 22:30 | 44847.9375 | 0 | 10.519 | 39.95
2022-10-13 23:00 | 44847.9583 | 0 | 9.972 | 39.95
2022-10-13 23:30 | 44847.9792 | 0 | 9.4919 | 39.95
2022-10-14 | 44848 | 0 | 9.0606 | 39.95
2022-10-14 00:30 | 44848.0208 | 0 | 8.7333 | 39.95
2022-10-14 01:00 | 44848.0417 | 0 | 8.646 | 39.95
2022-10-14 01:30 | 44848.0625 | 0 | 8.3867 | 39.95
2022-10-14 02:00 | 44848.0833 | 0 | 8.2649 | 39.95
2022-10-14 02:30 | 44848.1042 | 0 | 8.343 | 39.95
2022-10-14 03:00 | 44848.125 | 0 | 8.2964 | 39.95
2022-10-14 03:30 | 44848.1458 | 0 | 8.1848 | 39.95
2022-10-14 04:00 | 44848.1667 | 0 | 8.5171 | 39.95
2022-10-14 04:30 | 44848.1875 | 0 | 8.8568 | 39.95
2022-10-14 05:00 | 44848.2083 | 0 | 9.3169 | 39.95
2022-10-14 05:30 | 44848.2292 | 0 | 9.6903 | 39.95
2022-10-14 06:00 | 44848.25 | 0 | 10.3448 | 39.95
2022-10-14 06:30 | 44848.2708 | 0 | 11.0472 | 39.95
2022-10-14 07:00 | 44848.2917 | 0 | 10.7549 | 39.95
2022-10-14 07:30 | 44848.3125 | 0 | 10.0018 | 39.95
2022-10-14 08:00 | 44848.3333 | 0 | 10.3547 | 39.95
2022-10-14 08:30 | 44848.3542 | 0 | 11.3332 | 39.95
2022-10-14 09:00 | 44848.375 | 0 | 10.9179 | 39.95
2022-10-14 09:30 | 44848.3958 | 0 | 9.5539 | 39.95
2022-10-14 10:00 | 44848.4167 | 0 | 11.1684 | 39.95
2022-10-14 10:30 | 44848.4375 | 0 | 12.5227 | 39.95
2022-10-14 11:00 | 44848.4583 | 0 | 10.1348 | 39.95
2022-10-14 11:30 | 44848.4792 | 0 | 11.9311 | 39.95
2022-10-14 12:00 | 44848.5 | 0 | 10.9477 | 39.95
2022-10-14 12:30 | 44848.5208 | 0 | 10.0891 | 39.95
2022-10-14 13:00 | 44848.5417 | 0 | 10.1611 | 39.95
2022-10-14 13:30 | 44848.5625 | 0 | 9.277 | 39.95
2022-10-14 14:00 | 44848.5833 | 0 | 10.7936 | 39.95
2022-10-14 14:30 | 44848.6042 | 0 | 11.0079 | 39.95
2022-10-14 15:00 | 44848.625 | 0 | 11.7567 | 39.95
2022-10-14 15:30 | 44848.6458 | 0 | 11.037 | 39.95
2022-10-14 16:00 | 44848.6667 | 0 | 11.9981 | 39.95
2022-10-14 16:30 | 44848.6875 | 0 | 12.567 | 39.95
2022-10-14 17:00 | 44848.7083 | 0 | 13.1228 | 39.95
2022-10-14 17:30 | 44848.7292 | 0 | 13.3514 | 39.95
2022-10-14 18:00 | 44848.75 | 0 | 13.3522 | 39.95
2022-10-14 18:30 | 44848.7708 | 0 | 13.3427 | 39.95
2022-10-14 19:00 | 44848.7917 | 0 | 13.3731 | 39.95
2022-10-14 19:30 | 44848.8125 | 0 | 13.1361 | 39.95
2022-10-14 20:00 | 44848.8333 | 0 | 12.8544 | 39.95
2022-10-14 20:30 | 44848.8542 | 0 | 12.3866 | 39.95
2022-10-14 21:00 | 44848.875 | 0 | 12.134 | 39.95
2022-10-14 21:30 | 44848.8958 | 0 | 11.9197 | 39.95
2022-10-14 22:00 | 44848.9167 | 0 | 11.6276 | 39.95
2022-10-14 22:30 | 44848.9375 | 0 | 10.9758 | 39.95
2022-10-14 23:00 | 44848.9583 | 0 | 10.4573 | 39.95
2022-10-14 23:30 | 44848.9792 | 0 | 10.0622 | 39.95
2022-10-15 | 44849 | 0 | 9.4604 | 39.95
2022-10-15 00:30 | 44849.0208 | 0 | 9.0866 | 39.95
2022-10-15 01:00 | 44849.0417 | 0 | 8.8819 | 39.95
2022-10-15 01:30 | 44849.0625 | 0 | 8.5504 | 39.95
2022-10-15 02:00 | 44849.0833 | 0 | 8.4298 | 39.95
2022-10-15 02:30 | 44849.1042 | 0 | 8.3271 | 39.95
2022-10-15 03:00 | 44849.125 | 0 | 8.1243 | 39.95
2022-10-15 03:30 | 44849.1458 | 0 | 8.0141 | 39.95
2022-10-15 04:00 | 44849.1667 | 0 | 7.9876 | 39.95
2022-10-15 04:30 | 44849.1875 | 0 | 8.0204 | 39.95
2022-10-15 05:00 | 44849.2083 | 0 | 8.1851 | 39.95
2022-10-15 05:30 | 44849.2292 | 0 | 8.0677 | 39.95
2022-10-15 06:00 | 44849.25 | 0 | 7.8471 | 39.95
2022-10-15 06:30 | 44849.2708 | 0 | 7.5118 | 39.95
2022-10-15 07:00 | 44849.2917 | 0 | 7.1987 | 39.95
2022-10-15 07:30 | 44849.3125 | 0 | 6.6257 | 39.95
2022-10-15 08:00 | 44849.3333 | 0 | 6.3928 | 39.95
2022-10-15 08:30 | 44849.3542 | 0 | 5.9983 | 39.95
2022-10-15 09:00 | 44849.375 | 0 | 5.733 | 39.95
2022-10-15 09:30 | 44849.3958 | 0 | 7.233 | 39.95
2022-10-15 10:00 | 44849.4167 | 0 | 7.1934 | 39.95
2022-10-15 10:30 | 44849.4375 | 0 | 6.8699 | 39.95
2022-10-15 11:00 | 44849.4583 | 0 | 6.8046 | 39.95
2022-10-15 11:30 | 44849.4792 | 0 | 6.948 | 39.95
2022-10-15 12:00 | 44849.5 | 0 | 7.0932 | 39.95
2022-10-15 12:30 | 44849.5208 | 0 | 7.3847 | 39.95
2022-10-15 13:00 | 44849.5417 | 0 | 8.7458 | 39.95
2022-10-15 13:30 | 44849.5625 | 0 | 8.696 | 39.95
2022-10-15 14:00 | 44849.5833 | 0 | 8.169 | 39.95
2022-10-15 14:30 | 44849.6042 | 0 | 8.7336 | 39.95
2022-10-15 15:00 | 44849.625 | 0 | 9.6964 | 39.95
2022-10-15 15:30 | 44849.6458 | 0 | 9.7859 | 39.95
2022-10-15 16:00 | 44849.6667 | 0 | 9.9285 | 39.95
2022-10-15 16:30 | 44849.6875 | 0 | 10.3003 | 39.95
2022-10-15 17:00 | 44849.7083 | 0 | 10.6166 | 39.95
2022-10-15 17:30 | 44849.7292 | 0 | 10.9028 | 39.95
2022-10-15 18:00 | 44849.75 | 0 | 11.3298 | 39.95
2022-10-15 18:30 | 44849.7708 | 0 | 11.6621 | 39.95
2022-10-15 19:00 | 44849.7917 | 0 | 11.479 | 39.95
2022-10-15 19:30 | 44849.8125 | 0 | 11.1675 | 39.95
2022-10-15 20:00 | 44849.8333 | 0 | 11.0627 | 39.95
2022-10-15 20:30 | 44849.8542 | 0 | 10.5521 | 39.95
2022-10-15 21:00 | 44849.875 | 0 | 10.179 | 39.95
2022-10-15 21:30 | 44849.8958 | 0 | 9.9321 | 39.95
2022-10-15 22:00 | 44849.9167 | 0 | 9.8091 | 39.95
2022-10-15 22:30 | 44849.9375 | 0 | 9.2715 | 39.95
2022-10-15 23:00 | 44849.9583 | 0 | 8.8178 | 39.95
2022-10-15 23:30 | 44849.9792 | 0 | 8.4155 | 39.95
2022-10-16 | 44850 | 0 | 8.1312 | 39.95
2022-10-16 00:30 | 44850.0208 | 0 | 7.8278 | 39.95
2022-10-16 01:00 | 44850.0417 | 0 | 7.6923 | 39.95
2022-10-16 01:30 | 44850.0625 | 0 | 7.5792 | 39.95
2022-10-16 02:00 | 44850.0833 | 0 | 7.4192 | 39.95
2022-10-16 02:30 | 44850.1042 | 0 | 7.3561 | 39.95
2022-10-16 03:00 | 44850.125 | 0 | 7.2764 | 39.95
2022-10-16 03:30 | 44850.1458 | 0 | 7.2233 | 39.95
2022-10-16 04:00 | 44850.1667 | 0 | 7.1676 | 39.95
2022-10-16 04:30 | 44850.1875 | 0 | 7.2498 | 39.95
2022-10-16 05:00 | 44850.2083 | 0 | 7.2843 | 39.95
2022-10-16 05:30 | 44850.2292 | 0 | 6.9193 | 39.95
2022-10-16 06:00 | 44850.25 | 0 | 6.9648 | 39.95
2022-10-16 06:30 | 44850.2708 | 0 | 6.7825 | 39.95
2022-10-16 07:00 | 44850.2917 | 0 | 5.8879 | 39.95
2022-10-16 07:30 | 44850.3125 | 0 | 6.2357 | 39.95
2022-10-16 08:00 | 44850.3333 | 0 | 7.3918 | 39.95
2022-10-16 08:30 | 44850.3542 | 0 | 8.1421 | 39.95
2022-10-16 09:00 | 44850.375 | 0 | 6.9793 | 39.95
2022-10-16 09:30 | 44850.3958 | 0 | 5.5387 | 39.95
2022-10-16 10:00 | 44850.4167 | 0 | 6.5141 | 39.95
2022-10-16 10:30 | 44850.4375 | 0 | 7.805 | 39.95
2022-10-16 11:00 | 44850.4583 | 0 | 9.0221 | 39.95
2022-10-16 11:30 | 44850.4792 | 0 | 6.5799 | 39.95
2022-10-16 12:00 | 44850.5 | 0 | 5.0007 | 39.95
2022-10-16 12:30 | 44850.5208 | 0 | 7.0633 | 39.95
2022-10-16 13:00 | 44850.5417 | 0 | 7.9602 | 39.95
2022-10-16 13:30 | 44850.5625 | 0 | 7.7767 | 39.95
2022-10-16 14:00 | 44850.5833 | 0 | 8.7078 | 39.95
2022-10-16 14:30 | 44850.6042 | 0 | 8.1002 | 39.95
2022-10-16 15:00 | 44850.625 | 0 | 8.733 | 39.95
2022-10-16 15:30 | 44850.6458 | 0 | 9.486 | 39.95
2022-10-16 16:00 | 44850.6667 | 0 | 9.8475 | 39.95
2022-10-16 16:30 | 44850.6875 | 0 | 10.3134 | 39.95
2022-10-16 17:00 | 44850.7083 | 0 | 10.7381 | 39.95
2022-10-16 17:30 | 44850.7292 | 0 | 11.161 | 39.95
2022-10-16 18:00 | 44850.75 | 0 | 11.8205 | 39.95
2022-10-16 18:30 | 44850.7708 | 0 | 11.9474 | 39.95
2022-10-16 19:00 | 44850.7917 | 0 | 11.6822 | 39.95
2022-10-16 19:30 | 44850.8125 | 0 | 11.1693 | 39.95
2022-10-16 20:00 | 44850.8333 | 0 | 10.8055 | 39.95
2022-10-16 20:30 | 44850.8542 | 0 | 10.255 | 39.95
2022-10-16 21:00 | 44850.875 | 0 | 9.8898 | 39.95
2022-10-16 21:30 | 44850.8958 | 0 | 9.5656 | 39.95
2022-10-16 22:00 | 44850.9167 | 0 | 9.282 | 39.95
2022-10-16 22:30 | 44850.9375 | 0 | 8.5606 | 39.95
2022-10-16 23:00 | 44850.9583 | 0 | 8.3119 | 39.95
2022-10-16 23:30 | 44850.9792 | 0 | 8.0245 | 39.95
2022-10-17 | 44851 | 0 | 7.7786 | 39.95
2022-10-17 00:30 | 44851.0208 | 0 | 7.6337 | 39.95
2022-10-17 01:00 | 44851.0417 | 0 | 7.5273 | 39.95
2022-10-17 01:30 | 44851.0625 | 0 | 7.3266 | 39.95
2022-10-17 02:00 | 44851.0833 | 0 | 7.401 | 39.95
2022-10-17 02:30 | 44851.1042 | 0 | 7.5684 | 39.95
2022-10-17 03:00 | 44851.125 | 0 | 7.3159 | 39.95
2022-10-17 03:30 | 44851.1458 | 0 | 7.3579 | 39.95
2022-10-17 04:00 | 44851.1667 | 0 | 7.7834 | 39.95
2022-10-17 04:30 | 44851.1875 | 0 | 8.1919 | 39.95
2022-10-17 05:00 | 44851.2083 | 0 | 8.6638 | 39.95
2022-10-17 05:30 | 44851.2292 | 0 | 9.2154 | 39.95
2022-10-17 06:00 | 44851.25 | 0 | 9.5954 | 39.95
2022-10-17 06:30 | 44851.2708 | 0 | 10.7699 | 39.95
2022-10-17 07:00 | 44851.2917 | 0 | 10.8647 | 39.95
2022-10-17 07:30 | 44851.3125 | 0 | 10.3607 | 39.95
2022-10-17 08:00 | 44851.3333 | 0 | 11.6172 | 39.95
2022-10-17 08:30 | 44851.3542 | 0 | 10.2856 | 39.95
2022-10-17 09:00 | 44851.375 | 0 | 11.1771 | 39.95
2022-10-17 09:30 | 44851.3958 | 0 | 12.291 | 39.95
2022-10-17 10:00 | 44851.4167 | 0 | 11.9977 | 39.95
2022-10-17 10:30 | 44851.4375 | 0 | 12.8946 | 39.95
2022-10-17 11:00 | 44851.4583 | 0 | 12.2232 | 39.95
2022-10-17 11:30 | 44851.4792 | 0 | 11.5269 | 39.95
2022-10-17 12:00 | 44851.5 | 0 | 12.7349 | 39.95
2022-10-17 12:30 | 44851.5208 | 0 | 13.3943 | 39.95
2022-10-17 13:00 | 44851.5417 | 0 | 11.5853 | 39.95
2022-10-17 13:30 | 44851.5625 | 0 | 9.6862 | 39.95
2022-10-17 14:00 | 44851.5833 | 0 | 8.5536 | 39.95
2022-10-17 14:30 | 44851.6042 | 0 | 9.5142 | 39.95
2022-10-17 15:00 | 44851.625 | 0 | 9.4574 | 39.95
2022-10-17 15:30 | 44851.6458 | 0 | 10.3853 | 39.95
2022-10-17 16:00 | 44851.6667 | 0 | 11.0046 | 39.95
2022-10-17 16:30 | 44851.6875 | 0 | 11.788 | 39.95
2022-10-17 17:00 | 44851.7083 | 0 | 12.3845 | 39.95
2022-10-17 17:30 | 44851.7292 | 0 | 13.1256 | 39.95
2022-10-17 18:00 | 44851.75 | 0 | 13.9846 | 39.95
2022-10-17 18:30 | 44851.7708 | 0 | 14.0797 | 39.95
2022-10-17 19:00 | 44851.7917 | 0 | 13.819 | 39.95
2022-10-17 19:30 | 44851.8125 | 0 | 13.2917 | 39.95
2022-10-17 20:00 | 44851.8333 | 0 | 12.8021 | 39.95
2022-10-17 20:30 | 44851.8542 | 0 | 12.1083 | 39.95
2022-10-17 21:00 | 44851.875 | 0 | 11.6779 | 39.95
2022-10-17 21:30 | 44851.8958 | 0 | 11.2387 | 39.95
2022-10-17 22:00 | 44851.9167 | 0 | 10.7847 | 39.95
2022-10-17 22:30 | 44851.9375 | 0 | 9.9633 | 39.95
2022-10-17 23:00 | 44851.9583 | 0 | 9.5273 | 39.95
2022-10-17 23:30 | 44851.9792 | 0 | 9.1987 | 39.95
2022-10-18 | 44852 | 0 | 8.6746 | 39.95
2022-10-18 00:30 | 44852.0208 | 0 | 8.4706 | 39.95
2022-10-18 01:00 | 44852.0417 | 0 | 8.2669 | 39.95
2022-10-18 01:30 | 44852.0625 | 0 | 7.9888 | 39.95
2022-10-18 02:00 | 44852.0833 | 0 | 7.9273 | 39.95
2022-10-18 02:30 | 44852.1042 | 0 | 7.9072 | 39.95
2022-10-18 03:00 | 44852.125 | 0 | 7.8063 | 39.95
2022-10-18 03:30 | 44852.1458 | 0 | 7.8167 | 39.95
2022-10-18 04:00 | 44852.1667 | 0 | 8.2019 | 39.95
2022-10-18 04:30 | 44852.1875 | 0 | 8.5604 | 39.95
2022-10-18 05:00 | 44852.2083 | 0 | 8.9849 | 39.95
2022-10-18 05:30 | 44852.2292 | 0 | 9.5636 | 39.95
2022-10-18 06:00 | 44852.25 | 0 | 10.05 | 39.95
2022-10-18 06:30 | 44852.2708 | 0 | 10.4198 | 39.95
2022-10-18 07:00 | 44852.2917 | 0 | 11.1704 | 39.95
2022-10-18 07:30 | 44852.3125 | 0 | 10.9983 | 39.95
2022-10-18 08:00 | 44852.3333 | 0 | 11.2435 | 39.95
2022-10-18 08:30 | 44852.3542 | 0 | 10.7815 | 39.95
2022-10-18 09:00 | 44852.375 | 0 | 12.3011 | 39.95
2022-10-18 09:30 | 44852.3958 | 0 | 11.9917 | 39.95
2022-10-18 10:00 | 44852.4167 | 0 | 9.0519 | 39.95
2022-10-18 10:30 | 44852.4375 | 0 | 9.0212 | 39.95
2022-10-18 11:00 | 44852.4583 | 0 | 9.7553 | 39.95
2022-10-18 11:30 | 44852.4792 | 0 | 8.87 | 39.95
2022-10-18 12:00 | 44852.5 | 0 | 9.0284 | 39.95
2022-10-18 12:30 | 44852.5208 | 0 | 9.3391 | 39.95
2022-10-18 13:00 | 44852.5417 | 0 | 9.0856 | 39.95
2022-10-18 13:30 | 44852.5625 | 0 | 9.9049 | 39.95
2022-10-18 14:00 | 44852.5833 | 0 | 9.398 | 39.95
2022-10-18 14:30 | 44852.6042 | 0 | 10.5134 | 39.95
2022-10-18 15:00 | 44852.625 | 0 | 11.1345 | 39.95
2022-10-18 15:30 | 44852.6458 | 0 | 11.8274 | 39.95
2022-10-18 16:00 | 44852.6667 | 0 | 12.0845 | 39.95
2022-10-18 16:30 | 44852.6875 | 0 | 12.3456 | 39.95
2022-10-18 17:00 | 44852.7083 | 0 | 12.8409 | 39.95
2022-10-18 17:30 | 44852.7292 | 0 | 13.2109 | 39.95
2022-10-18 18:00 | 44852.75 | 0 | 13.6211 | 39.95
2022-10-18 18:30 | 44852.7708 | 0 | 13.7081 | 39.95
2022-10-18 19:00 | 44852.7917 | 0 | 13.6205 | 39.95
2022-10-18 19:30 | 44852.8125 | 0 | 13.1792 | 39.95
2022-10-18 20:00 | 44852.8333 | 0 | 13.064 | 39.95
2022-10-18 20:30 | 44852.8542 | 0 | 12.4931 | 39.95
2022-10-18 21:00 | 44852.875 | 0 | 11.9748 | 39.95
2022-10-18 21:30 | 44852.8958 | 0 | 11.537 | 39.95
2022-10-18 22:00 | 44852.9167 | 0 | 10.9996 | 39.95
2022-10-18 22:30 | 44852.9375 | 0 | 10.2946 | 39.95
2022-10-18 23:00 | 44852.9583 | 0 | 9.972 | 39.95
2022-10-18 23:30 | 44852.9792 | 0 | 9.7428 | 39.95
2022-10-19 | 44853 | 0 | 8.9118 | 39.95
2022-10-19 00:30 | 44853.0208 | 0 | 8.5692 | 39.95
2022-10-19 01:00 | 44853.0417 | 0 | 8.532 | 39.95
2022-10-19 01:30 | 44853.0625 | 0 | 8.4495 | 39.95
2022-10-19 02:00 | 44853.0833 | 0 | 8.3334 | 39.95
2022-10-19 02:30 | 44853.1042 | 0 | 8.3479 | 39.95
2022-10-19 03:00 | 44853.125 | 0 | 8.2839 | 39.95
2022-10-19 03:30 | 44853.1458 | 0 | 8.2559 | 39.95
2022-10-19 04:00 | 44853.1667 | 0 | 8.6176 | 39.95
2022-10-19 04:30 | 44853.1875 | 0 | 9.0087 | 39.95
2022-10-19 05:00 | 44853.2083 | 0 | 9.4915 | 39.95
2022-10-19 05:30 | 44853.2292 | 0 | 9.9577 | 39.95
2022-10-19 06:00 | 44853.25 | 0 | 11.1333 | 39.95
2022-10-19 06:30 | 44853.2708 | 0 | 11.815 | 39.95
2022-10-19 07:00 | 44853.2917 | 0 | 12.3136 | 39.95
2022-10-19 07:30 | 44853.3125 | 0 | 12.5125 | 39.95
2022-10-19 08:00 | 44853.3333 | 0 | 12.6767 | 39.95
2022-10-19 08:30 | 44853.3542 | 0 | 12.4783 | 39.95
2022-10-19 09:00 | 44853.375 | 0 | 12.6848 | 39.95
2022-10-19 09:30 | 44853.3958 | 0 | 13.2392 | 39.95
2022-10-19 10:00 | 44853.4167 | 0 | 10.0826 | 39.95
2022-10-19 10:30 | 44853.4375 | 0 | 11.7414 | 39.95
2022-10-19 11:00 | 44853.4583 | 0 | 11.3367 | 39.95
2022-10-19 11:30 | 44853.4792 | 0 | 11.2051 | 39.95
2022-10-19 12:00 | 44853.5 | 0 | 11.4927 | 39.95
2022-10-19 12:30 | 44853.5208 | 0 | 11.909 | 39.95
2022-10-19 13:00 | 44853.5417 | 0 | 12.3276 | 39.95
2022-10-19 13:30 | 44853.5625 | 0 | 12.2477 | 39.95
2022-10-19 14:00 | 44853.5833 | 0 | 12.8566 | 39.95
2022-10-19 14:30 | 44853.6042 | 0 | 13.158 | 39.95
2022-10-19 15:00 | 44853.625 | 0 | 13.1896 | 39.95
2022-10-19 15:30 | 44853.6458 | 0 | 13.4702 | 39.95
2022-10-19 16:00 | 44853.6667 | 0 | 13.1864 | 39.95
2022-10-19 16:30 | 44853.6875 | 0 | 13.2264 | 39.95
2022-10-19 17:00 | 44853.7083 | 0 | 13.5806 | 39.95
2022-10-19 17:30 | 44853.7292 | 0 | 13.7572 | 39.95
2022-10-19 18:00 | 44853.75 | 0 | 13.8543 | 39.95
2022-10-19 18:30 | 44853.7708 | 0 | 14.1722 | 39.95
2022-10-19 19:00 | 44853.7917 | 0 | 13.7349 | 39.95
2022-10-19 19:30 | 44853.8125 | 0 | 13.2998 | 39.95
2022-10-19 20:00 | 44853.8333 | 0 | 12.9551 | 39.95
2022-10-19 20:30 | 44853.8542 | 0 | 12.4222 | 39.95
2022-10-19 21:00 | 44853.875 | 0 | 12.0966 | 39.95
2022-10-19 21:30 | 44853.8958 | 0 | 11.6696 | 39.95
2022-10-19 22:00 | 44853.9167 | 0 | 11.0067 | 39.95
2022-10-19 22:30 | 44853.9375 | 0 | 10.4543 | 39.95
2022-10-19 23:00 | 44853.9583 | 0 | 10.0774 | 39.95
2022-10-19 23:30 | 44853.9792 | 0 | 9.5561 | 39.95
2022-10-20 | 44854 | 0 | 9.0546 | 39.95
2022-10-20 00:30 | 44854.0208 | 0 | 8.7044 | 39.95
2022-10-20 01:00 | 44854.0417 | 0 | 8.4798 | 39.95
2022-10-20 01:30 | 44854.0625 | 0 | 8.3744 | 39.95
2022-10-20 02:00 | 44854.0833 | 0 | 8.2482 | 39.95
2022-10-20 02:30 | 44854.1042 | 0 | 8.2568 | 39.95
2022-10-20 03:00 | 44854.125 | 0 | 8.001 | 39.95
2022-10-20 03:30 | 44854.1458 | 0 | 8.1919 | 39.95
2022-10-20 04:00 | 44854.1667 | 0 | 8.6285 | 39.95
2022-10-20 04:30 | 44854.1875 | 0 | 8.8009 | 39.95
2022-10-20 05:00 | 44854.2083 | 0 | 9.4973 | 39.95
2022-10-20 05:30 | 44854.2292 | 0 | 10.0503 | 39.95
2022-10-20 06:00 | 44854.25 | 0 | 11.1143 | 39.95
2022-10-20 06:30 | 44854.2708 | 0 | 11.9897 | 39.95
2022-10-20 07:00 | 44854.2917 | 0 | 12.6368 | 39.95
2022-10-20 07:30 | 44854.3125 | 0 | 12.752 | 39.95
2022-10-20 08:00 | 44854.3333 | 0 | 13.0485 | 39.95
2022-10-20 08:30 | 44854.3542 | 0 | 24.0174 | 39.95
2022-10-20 09:00 | 44854.375 | 0 | 22.377 | 39.95
2022-10-20 09:30 | 44854.3958 | 0 | 21.4835 | 39.95
2022-10-20 10:00 | 44854.4167 | 0 | 20.6842 | 39.95
2022-10-20 10:30 | 44854.4375 | 0 | 20.1729 | 39.95
2022-10-20 11:00 | 44854.4583 | 0 | 22.1648 | 39.95
2022-10-20 11:30 | 44854.4792 | 0 | 21.5082 | 39.95
2022-10-20 12:00 | 44854.5 | 0 | 13.7174 | 39.95
2022-10-20 12:30 | 44854.5208 | 0 | 11.6119 | 39.95
2022-10-20 13:00 | 44854.5417 | 0 | 11.1262 | 39.95
2022-10-20 13:30 | 44854.5625 | 0 | 12.0507 | 39.95
2022-10-20 14:00 | 44854.5833 | 0 | 11.266 | 39.95
2022-10-20 14:30 | 44854.6042 | 0 | 12.1156 | 39.95
2022-10-20 15:00 | 44854.625 | 0 | 12.0969 | 39.95
2022-10-20 15:30 | 44854.6458 | 0 | 12.2793 | 39.95
2022-10-20 16:00 | 44854.6667 | 0 | 12.8067 | 39.95
2022-10-20 16:30 | 44854.6875 | 0 | 12.8502 | 39.95
2022-10-20 17:00 | 44854.7083 | 0 | 13.0781 | 39.95
2022-10-20 17:30 | 44854.7292 | 0 | 13.5333 | 39.95
2022-10-20 18:00 | 44854.75 | 0 | 13.8596 | 39.95
2022-10-20 18:30 | 44854.7708 | 0 | 14.1634 | 39.95
2022-10-20 19:00 | 44854.7917 | 0 | 14.0136 | 39.95
2022-10-20 19:30 | 44854.8125 | 0 | 13.5236 | 39.95
2022-10-20 20:00 | 44854.8333 | 0 | 13.2355 | 39.95
2022-10-20 20:30 | 44854.8542 | 0 | 12.9966 | 39.95
2022-10-20 21:00 | 44854.875 | 0 | 12.5741 | 39.95
2022-10-20 21:30 | 44854.8958 | 0 | 12.1328 | 39.95
2022-10-20 22:00 | 44854.9167 | 0 | 11.6521 | 39.95
2022-10-20 22:30 | 44854.9375 | 0 | 11.0225 | 39.95
2022-10-20 23:00 | 44854.9583 | 0 | 10.5227 | 39.95
2022-10-20 23:30 | 44854.9792 | 0 | 10.2011 | 39.95
2022-10-21 | 44855 | 0 | 9.5925 | 39.95
2022-10-21 00:30 | 44855.0208 | 0 | 9.1784 | 39.95
2022-10-21 01:00 | 44855.0417 | 0 | 8.9289 | 39.95
2022-10-21 01:30 | 44855.0625 | 0 | 8.9021 | 39.95
2022-10-21 02:00 | 44855.0833 | 0 | 8.7729 | 39.95
2022-10-21 02:30 | 44855.1042 | 0 | 8.7008 | 39.95
2022-10-21 03:00 | 44855.125 | 0 | 8.694 | 39.95
2022-10-21 03:30 | 44855.1458 | 0 | 8.8003 | 39.95
2022-10-21 04:00 | 44855.1667 | 0 | 9.0942 | 39.95
2022-10-21 04:30 | 44855.1875 | 0 | 9.2931 | 39.95
2022-10-21 05:00 | 44855.2083 | 0 | 9.7337 | 39.95
2022-10-21 05:30 | 44855.2292 | 0 | 10.3368 | 39.95
2022-10-21 06:00 | 44855.25 | 0 | 11.3597 | 39.95
2022-10-21 06:30 | 44855.2708 | 0 | 12.02 | 39.95
2022-10-21 07:00 | 44855.2917 | 0 | 13.0423 | 39.95
2022-10-21 07:30 | 44855.3125 | 0 | 12.0897 | 39.95
2022-10-21 08:00 | 44855.3333 | 0 | 10.9151 | 39.95
2022-10-21 08:30 | 44855.3542 | 0 | 11.2635 | 39.95
2022-10-21 09:00 | 44855.375 | 0 | 12.2825 | 39.95
2022-10-21 09:30 | 44855.3958 | 0 | 13.9496 | 39.95
2022-10-21 10:00 | 44855.4167 | 0 | 14.0919 | 39.95
2022-10-21 10:30 | 44855.4375 | 0 | 14.1571 | 39.95
2022-10-21 11:00 | 44855.4583 | 0 | 13.7722 | 39.95
2022-10-21 11:30 | 44855.4792 | 0 | 12.8957 | 39.95
2022-10-21 12:00 | 44855.5 | 0 | 12.9223 | 39.95
2022-10-21 12:30 | 44855.5208 | 0 | 12.7562 | 39.95
2022-10-21 13:00 | 44855.5417 | 0 | 13.4606 | 39.95
2022-10-21 13:30 | 44855.5625 | 0 | 12.9628 | 39.95
2022-10-21 14:00 | 44855.5833 | 0 | 11.9491 | 39.95
2022-10-21 14:30 | 44855.6042 | 0 | 13.0828 | 39.95
2022-10-21 15:00 | 44855.625 | 0 | 12.4682 | 39.95
2022-10-21 15:30 | 44855.6458 | 0 | 12.9446 | 39.95
2022-10-21 16:00 | 44855.6667 | 0 | 13.1422 | 39.95
2022-10-21 16:30 | 44855.6875 | 0 | 13.5273 | 39.95
2022-10-21 17:00 | 44855.7083 | 0 | 13.6372 | 39.95
2022-10-21 17:30 | 44855.7292 | 0 | 13.7131 | 39.95
2022-10-21 18:00 | 44855.75 | 0 | 13.7989 | 39.95
2022-10-21 18:30 | 44855.7708 | 0 | 13.8314 | 39.95
2022-10-21 19:00 | 44855.7917 | 0 | 13.4227 | 39.95
2022-10-21 19:30 | 44855.8125 | 0 | 13.2403 | 39.95
2022-10-21 20:00 | 44855.8333 | 0 | 13.0485 | 39.95
2022-10-21 20:30 | 44855.8542 | 0 | 12.4653 | 39.95
2022-10-21 21:00 | 44855.875 | 0 | 12.0271 | 39.95
2022-10-21 21:30 | 44855.8958 | 0 | 11.7878 | 39.95
2022-10-21 22:00 | 44855.9167 | 0 | 11.4022 | 39.95
2022-10-21 22:30 | 44855.9375 | 0 | 10.6754 | 39.95
2022-10-21 23:00 | 44855.9583 | 0 | 10.1914 | 39.95
2022-10-21 23:30 | 44855.9792 | 0 | 9.8177 | 39.95
2022-10-22 | 44856 | 0 | 9.2675 | 39.95
2022-10-22 00:30 | 44856.0208 | 0 | 8.9402 | 39.95
2022-10-22 01:00 | 44856.0417 | 0 | 8.6698 | 39.95
2022-10-22 01:30 | 44856.0625 | 0 | 8.5865 | 39.95
2022-10-22 02:00 | 44856.0833 | 0 | 8.5245 | 39.95
2022-10-22 02:30 | 44856.1042 | 0 | 8.4493 | 39.95
2022-10-22 03:00 | 44856.125 | 0 | 8.4182 | 39.95
2022-10-22 03:30 | 44856.1458 | 0 | 8.2842 | 39.95
2022-10-22 04:00 | 44856.1667 | 0 | 8.5427 | 39.95
2022-10-22 04:30 | 44856.1875 | 0 | 8.4852 | 39.95
2022-10-22 05:00 | 44856.2083 | 0 | 8.5659 | 39.95
2022-10-22 05:30 | 44856.2292 | 0 | 8.5647 | 39.95
2022-10-22 06:00 | 44856.25 | 0 | 8.7472 | 39.95
2022-10-22 06:30 | 44856.2708 | 0 | 8.9977 | 39.95
2022-10-22 07:00 | 44856.2917 | 0 | 9.7227 | 39.95
2022-10-22 07:30 | 44856.3125 | 0 | 10.1445 | 39.95
2022-10-22 08:00 | 44856.3333 | 0 | 10.5065 | 39.95
2022-10-22 08:30 | 44856.3542 | 0 | 10.6635 | 39.95
2022-10-22 09:00 | 44856.375 | 0 | 11.1959 | 39.95
2022-10-22 09:30 | 44856.3958 | 0 | 11.2027 | 39.95
2022-10-22 10:00 | 44856.4167 | 0 | 10.6568 | 39.95
2022-10-22 10:30 | 44856.4375 | 0 | 10.7389 | 39.95
2022-10-22 11:00 | 44856.4583 | 0 | 10.3871 | 39.95
2022-10-22 11:30 | 44856.4792 | 0 | 10.6496 | 39.95
2022-10-22 12:00 | 44856.5 | 0 | 10.022 | 39.95
2022-10-22 12:30 | 44856.5208 | 0 | 10.0842 | 39.95
2022-10-22 13:00 | 44856.5417 | 0 | 10.7574 | 39.95
2022-10-22 13:30 | 44856.5625 | 0 | 10.8861 | 39.95
2022-10-22 14:00 | 44856.5833 | 0 | 10.9786 | 39.95
2022-10-22 14:30 | 44856.6042 | 0 | 11.1127 | 39.95
2022-10-22 15:00 | 44856.625 | 0 | 11.2571 | 39.95
2022-10-22 15:30 | 44856.6458 | 0 | 11.0841 | 39.95
2022-10-22 16:00 | 44856.6667 | 0 | 11.2351 | 39.95
2022-10-22 16:30 | 44856.6875 | 0 | 11.4102 | 39.95
2022-10-22 17:00 | 44856.7083 | 0 | 11.4826 | 39.95
2022-10-22 17:30 | 44856.7292 | 0 | 11.6291 | 39.95
2022-10-22 18:00 | 44856.75 | 0 | 11.825 | 39.95
2022-10-22 18:30 | 44856.7708 | 0 | 11.8289 | 39.95
2022-10-22 19:00 | 44856.7917 | 0 | 11.766 | 39.95
2022-10-22 19:30 | 44856.8125 | 0 | 11.5309 | 39.95
2022-10-22 20:00 | 44856.8333 | 0 | 11.2608 | 39.95
2022-10-22 20:30 | 44856.8542 | 0 | 10.6538 | 39.95
2022-10-22 21:00 | 44856.875 | 0 | 10.2957 | 39.95
2022-10-22 21:30 | 44856.8958 | 0 | 9.9955 | 39.95
2022-10-22 22:00 | 44856.9167 | 0 | 9.882 | 39.95
2022-10-22 22:30 | 44856.9375 | 0 | 9.2037 | 39.95
2022-10-22 23:00 | 44856.9583 | 0 | 8.8163 | 39.95
2022-10-22 23:30 | 44856.9792 | 0 | 8.4986 | 39.95
2022-10-23 | 44857 | 0 | 8.1334 | 39.95
2022-10-23 00:30 | 44857.0208 | 0 | 7.8132 | 39.95
2022-10-23 01:00 | 44857.0417 | 0 | 7.7899 | 39.95
2022-10-23 01:30 | 44857.0625 | 0 | 7.5729 | 39.95
2022-10-23 02:00 | 44857.0833 | 0 | 7.5088 | 39.95
2022-10-23 02:30 | 44857.1042 | 0 | 7.4651 | 39.95
2022-10-23 03:00 | 44857.125 | 0 | 7.4901 | 39.95
2022-10-23 03:30 | 44857.1458 | 0 | 7.3707 | 39.95
2022-10-23 04:00 | 44857.1667 | 0 | 7.3915 | 39.95
2022-10-23 04:30 | 44857.1875 | 0 | 7.3856 | 39.95
2022-10-23 05:00 | 44857.2083 | 0 | 7.3686 | 39.95
2022-10-23 05:30 | 44857.2292 | 0 | 7.4844 | 39.95
2022-10-23 06:00 | 44857.25 | 0 | 7.9442 | 39.95
2022-10-23 06:30 | 44857.2708 | 0 | 8.4019 | 39.95
2022-10-23 07:00 | 44857.2917 | 0 | 8.9351 | 39.95
2022-10-23 07:30 | 44857.3125 | 0 | 8.7846 | 39.95
2022-10-23 08:00 | 44857.3333 | 0 | 9.5448 | 39.95
2022-10-23 08:30 | 44857.3542 | 0 | 10.1301 | 39.95
2022-10-23 09:00 | 44857.375 | 0 | 9.5023 | 39.95
2022-10-23 09:30 | 44857.3958 | 0 | 9.1953 | 39.95
2022-10-23 10:00 | 44857.4167 | 0 | 8.898 | 39.95
2022-10-23 10:30 | 44857.4375 | 0 | 7.9904 | 39.95
2022-10-23 11:00 | 44857.4583 | 0 | 7.8135 | 39.95
2022-10-23 11:30 | 44857.4792 | 0 | 8.7521 | 39.95
2022-10-23 12:00 | 44857.5 | 0 | 8.7393 | 39.95
2022-10-23 12:30 | 44857.5208 | 0 | 9.4521 | 39.95
2022-10-23 13:00 | 44857.5417 | 0 | 9.7028 | 39.95
2022-10-23 13:30 | 44857.5625 | 0 | 9.2864 | 39.95
2022-10-23 14:00 | 44857.5833 | 0 | 9.0856 | 39.95
2022-10-23 14:30 | 44857.6042 | 0 | 9.5155 | 39.95
2022-10-23 15:00 | 44857.625 | 0 | 9.3735 | 39.95
2022-10-23 15:30 | 44857.6458 | 0 | 10.2844 | 39.95
2022-10-23 16:00 | 44857.6667 | 0 | 10.7798 | 39.95
2022-10-23 16:30 | 44857.6875 | 0 | 10.9651 | 39.95
2022-10-23 17:00 | 44857.7083 | 0 | 11.2896 | 39.95
2022-10-23 17:30 | 44857.7292 | 0 | 11.6984 | 39.95
2022-10-23 18:00 | 44857.75 | 0 | 12.0736 | 39.95
2022-10-23 18:30 | 44857.7708 | 0 | 12.3892 | 39.95
2022-10-23 19:00 | 44857.7917 | 0 | 12.0258 | 39.95
2022-10-23 19:30 | 44857.8125 | 0 | 11.4106 | 39.95
2022-10-23 20:00 | 44857.8333 | 0 | 11.2854 | 39.95
2022-10-23 20:30 | 44857.8542 | 0 | 10.7491 | 39.95
2022-10-23 21:00 | 44857.875 | 0 | 10.3195 | 39.95
2022-10-23 21:30 | 44857.8958 | 0 | 9.9234 | 39.95
2022-10-23 22:00 | 44857.9167 | 0 | 9.5038 | 39.95
2022-10-23 22:30 | 44857.9375 | 0 | 8.9569 | 39.95
2022-10-23 23:00 | 44857.9583 | 0 | 8.5731 | 39.95
2022-10-23 23:30 | 44857.9792 | 0 | 8.2214 | 39.95
2022-10-24 | 44858 | 0 | 7.9085 | 39.95
2022-10-24 00:30 | 44858.0208 | 0 | 7.6908 | 39.95
2022-10-24 01:00 | 44858.0417 | 0 | 7.6762 | 39.95
2022-10-24 01:30 | 44858.0625 | 0 | 7.6131 | 39.95
2022-10-24 02:00 | 44858.0833 | 0 | 7.5443 | 39.95
2022-10-24 02:30 | 44858.1042 | 0 | 7.6267 | 39.95
2022-10-24 03:00 | 44858.125 | 0 | 7.4067 | 39.95
2022-10-24 03:30 | 44858.1458 | 0 | 7.6086 | 39.95
2022-10-24 04:00 | 44858.1667 | 0 | 7.9215 | 39.95
2022-10-24 04:30 | 44858.1875 | 0 | 8.232 | 39.95
2022-10-24 05:00 | 44858.2083 | 0 | 8.6666 | 39.95
2022-10-24 05:30 | 44858.2292 | 0 | 9.1252 | 39.95
2022-10-24 06:00 | 44858.25 | 0 | 9.8384 | 39.95
2022-10-24 06:30 | 44858.2708 | 0 | 10.1063 | 39.95
2022-10-24 07:00 | 44858.2917 | 0 | 9.7888 | 39.95
2022-10-24 07:30 | 44858.3125 | 0 | 9.5094 | 39.95
2022-10-24 08:00 | 44858.3333 | 0 | 9.0617 | 39.95
2022-10-24 08:30 | 44858.3542 | 0 | 8.624 | 39.95
2022-10-24 09:00 | 44858.375 | 0 | 8.3533 | 39.95
2022-10-24 09:30 | 44858.3958 | 0 | 8.1523 | 39.95
2022-10-24 10:00 | 44858.4167 | 0 | 8.2223 | 39.95
2022-10-24 10:30 | 44858.4375 | 0 | 8.3232 | 39.95
2022-10-24 11:00 | 44858.4583 | 0 | 8.5081 | 39.95
2022-10-24 11:30 | 44858.4792 | 0 | 8.4805 | 39.95
2022-10-24 12:00 | 44858.5 | 0 | 8.7877 | 39.95
2022-10-24 12:30 | 44858.5208 | 0 | 10.5265 | 39.95
2022-10-24 13:00 | 44858.5417 | 0 | 9.9593 | 39.95
2022-10-24 13:30 | 44858.5625 | 0 | 10.5035 | 39.95
2022-10-24 14:00 | 44858.5833 | 0 | 11.1975 | 39.95
2022-10-24 14:30 | 44858.6042 | 0 | 12.4951 | 39.95
2022-10-24 15:00 | 44858.625 | 0 | 11.7197 | 39.95
2022-10-24 15:30 | 44858.6458 | 0 | 12.7282 | 39.95
2022-10-24 16:00 | 44858.6667 | 0 | 13.7148 | 39.95
2022-10-24 16:30 | 44858.6875 | 0 | 14.6219 | 39.95
2022-10-24 17:00 | 44858.7083 | 0 | 14.8774 | 39.95
2022-10-24 17:30 | 44858.7292 | 0 | 15.0278 | 39.95
2022-10-24 18:00 | 44858.75 | 0 | 15.5474 | 39.95
2022-10-24 18:30 | 44858.7708 | 0 | 15.9285 | 39.95
2022-10-24 19:00 | 44858.7917 | 0 | 15.7782 | 39.95
2022-10-24 19:30 | 44858.8125 | 0 | 15.4304 | 39.95
2022-10-24 20:00 | 44858.8333 | 0 | 14.8887 | 39.95
2022-10-24 20:30 | 44858.8542 | 0 | 14.1663 | 39.95
2022-10-24 21:00 | 44858.875 | 0 | 13.5914 | 39.95
2022-10-24 21:30 | 44858.8958 | 0 | 13.2103 | 39.95
2022-10-24 22:00 | 44858.9167 | 0 | 12.2735 | 39.95
2022-10-24 22:30 | 44858.9375 | 0 | 11.4519 | 39.95
2022-10-24 23:00 | 44858.9583 | 0 | 10.9278 | 39.95
2022-10-24 23:30 | 44858.9792 | 0 | 10.4016 | 39.95
2022-10-25 | 44859 | 0 | 9.8591 | 39.95
2022-10-25 00:30 | 44859.0208 | 0 | 9.4016 | 39.95
2022-10-25 01:00 | 44859.0417 | 0 | 9.2678 | 39.95
2022-10-25 01:30 | 44859.0625 | 0 | 8.9539 | 39.95
2022-10-25 02:00 | 44859.0833 | 0 | 8.8678 | 39.95
2022-10-25 02:30 | 44859.1042 | 0 | 8.7967 | 39.95
2022-10-25 03:00 | 44859.125 | 0 | 8.8107 | 39.95
2022-10-25 03:30 | 44859.1458 | 0 | 8.8 | 39.95
2022-10-25 04:00 | 44859.1667 | 0 | 8.7967 | 39.95
2022-10-25 04:30 | 44859.1875 | 0 | 9.1385 | 39.95
2022-10-25 05:00 | 44859.2083 | 0 | 9.5316 | 39.95
2022-10-25 05:30 | 44859.2292 | 0 | 9.598 | 39.95
2022-10-25 06:00 | 44859.25 | 0 | 10.6314 | 39.95
2022-10-25 06:30 | 44859.2708 | 0 | 11.9686 | 39.95
2022-10-25 07:00 | 44859.2917 | 0 | 13.4901 | 39.95
2022-10-25 07:30 | 44859.3125 | 0 | 12.9065 | 39.95
2022-10-25 08:00 | 44859.3333 | 0 | 13.2781 | 39.95
2022-10-25 08:30 | 44859.3542 | 0 | 10.4416 | 39.95
2022-10-25 09:00 | 44859.375 | 0 | 9.565 | 39.95
2022-10-25 09:30 | 44859.3958 | 0 | 9.3795 | 39.95
2022-10-25 10:00 | 44859.4167 | 0 | 10.2712 | 39.95
2022-10-25 10:30 | 44859.4375 | 0 | 12.9932 | 39.95
2022-10-25 11:00 | 44859.4583 | 0 | 12.2622 | 39.95
2022-10-25 11:30 | 44859.4792 | 0 | 11.0454 | 39.95
2022-10-25 12:00 | 44859.5 | 0 | 11.2568 | 39.95
2022-10-25 12:30 | 44859.5208 | 0 | 13.6261 | 39.95
2022-10-25 13:00 | 44859.5417 | 0 | 13.8618 | 39.95
2022-10-25 13:30 | 44859.5625 | 0 | 14.4708 | 39.95
2022-10-25 14:00 | 44859.5833 | 0 | 14.6006 | 39.95
2022-10-25 14:30 | 44859.6042 | 0 | 12.9736 | 39.95
2022-10-25 15:00 | 44859.625 | 0 | 14.0819 | 39.95
2022-10-25 15:30 | 44859.6458 | 0 | 14.9715 | 39.95
2022-10-25 16:00 | 44859.6667 | 0 | 13.2734 | 39.95
2022-10-25 16:30 | 44859.6875 | 0 | 14.201 | 39.95
2022-10-25 17:00 | 44859.7083 | 0 | 14.7274 | 39.95
2022-10-25 17:30 | 44859.7292 | 0 | 15.0305 | 39.95
2022-10-25 18:00 | 44859.75 | 0 | 15.4535 | 39.95
2022-10-25 18:30 | 44859.7708 | 0 | 15.5298 | 39.95
2022-10-25 19:00 | 44859.7917 | 0 | 15.6942 | 39.95
2022-10-25 19:30 | 44859.8125 | 0 | 14.8313 | 39.95
2022-10-25 20:00 | 44859.8333 | 0 | 14.4972 | 39.95
2022-10-25 20:30 | 44859.8542 | 0 | 13.9161 | 39.95
2022-10-25 21:00 | 44859.875 | 0 | 13.4839 | 39.95
2022-10-25 21:30 | 44859.8958 | 0 | 12.8988 | 39.95
2022-10-25 22:00 | 44859.9167 | 0 | 12.2771 | 39.95
2022-10-25 22:30 | 44859.9375 | 0 | 11.489 | 39.95
2022-10-25 23:00 | 44859.9583 | 0 | 10.9996 | 39.95
2022-10-25 23:30 | 44859.9792 | 0 | 10.6371 | 39.95
2022-10-26 | 44860 | 0 | 10.0424 | 39.95
2022-10-26 00:30 | 44860.0208 | 0 | 9.5539 | 39.95
2022-10-26 01:00 | 44860.0417 | 0 | 9.361 | 39.95
2022-10-26 01:30 | 44860.0625 | 0 | 9.0473 | 39.95
2022-10-26 02:00 | 44860.0833 | 0 | 8.9354 | 39.95
2022-10-26 02:30 | 44860.1042 | 0 | 8.8658 | 39.95
2022-10-26 03:00 | 44860.125 | 0 | 8.8375 | 39.95
2022-10-26 03:30 | 44860.1458 | 0 | 8.7794 | 39.95
2022-10-26 04:00 | 44860.1667 | 0 | 8.9247 | 39.95
2022-10-26 04:30 | 44860.1875 | 0 | 9.2189 | 39.95
2022-10-26 05:00 | 44860.2083 | 0 | 9.6406 | 39.95
2022-10-26 05:30 | 44860.2292 | 0 | 9.8255 | 39.95
2022-10-26 06:00 | 44860.25 | 0 | 10.4135 | 39.95
2022-10-26 06:30 | 44860.2708 | 0 | 10.5017 | 39.95
2022-10-26 07:00 | 44860.2917 | 0 | 11.8888 | 39.95
2022-10-26 07:30 | 44860.3125 | 0 | 11.6155 | 39.95
2022-10-26 08:00 | 44860.3333 | 0 | 11.0814 | 39.95
2022-10-26 08:30 | 44860.3542 | 0 | 10.6924 | 39.95
2022-10-26 09:00 | 44860.375 | 0 | 10.498 | 39.95
2022-10-26 09:30 | 44860.3958 | 0 | 10.0616 | 39.95
2022-10-26 10:00 | 44860.4167 | 0 | 9.7079 | 39.95
2022-10-26 10:30 | 44860.4375 | 0 | 9.6409 | 39.95
2022-10-26 11:00 | 44860.4583 | 0 | 9.2279 | 39.95
2022-10-26 11:30 | 44860.4792 | 0 | 9.7073 | 39.95
2022-10-26 12:00 | 44860.5 | 0 | 10.1096 | 39.95
2022-10-26 12:30 | 44860.5208 | 0 | 10.4515 | 39.95
2022-10-26 13:00 | 44860.5417 | 0 | 11.2732 | 39.95
2022-10-26 13:30 | 44860.5625 | 0 | 11.8047 | 39.95
2022-10-26 14:00 | 44860.5833 | 0 | 12.7084 | 39.95
2022-10-26 14:30 | 44860.6042 | 0 | 13.3691 | 39.95
2022-10-26 15:00 | 44860.625 | 0 | 13.9869 | 39.95
2022-10-26 15:30 | 44860.6458 | 0 | 14.896 | 39.95
2022-10-26 16:00 | 44860.6667 | 0 | 15.8149 | 39.95
2022-10-26 16:30 | 44860.6875 | 0 | 16.6609 | 39.95
2022-10-26 17:00 | 44860.7083 | 0 | 17.0156 | 39.95
2022-10-26 17:30 | 44860.7292 | 0 | 17.0333 | 39.95
2022-10-26 18:00 | 44860.75 | 0 | 17.0571 | 39.95
2022-10-26 18:30 | 44860.7708 | 0 | 17.3534 | 39.95
2022-10-26 19:00 | 44860.7917 | 0 | 17.4165 | 39.95
2022-10-26 19:30 | 44860.8125 | 0 | 16.8114 | 39.95
2022-10-26 20:00 | 44860.8333 | 0 | 16.3378 | 39.95
2022-10-26 20:30 | 44860.8542 | 0 | 15.5815 | 39.95
2022-10-26 21:00 | 44860.875 | 0 | 14.8484 | 39.95
2022-10-26 21:30 | 44860.8958 | 0 | 14.2429 | 39.95
2022-10-26 22:00 | 44860.9167 | 0 | 13.3074 | 39.95
2022-10-26 22:30 | 44860.9375 | 0 | 12.3806 | 39.95
2022-10-26 23:00 | 44860.9583 | 0 | 11.5995 | 39.95
2022-10-26 23:30 | 44860.9792 | 0 | 10.9427 | 39.95
2022-10-27 | 44861 | 0 | 10.1545 | 39.95
2022-10-27 00:30 | 44861.0208 | 0 | 9.9032 | 39.95
2022-10-27 01:00 | 44861.0417 | 0 | 9.6219 | 39.95
2022-10-27 01:30 | 44861.0625 | 0 | 9.3708 | 39.95
2022-10-27 02:00 | 44861.0833 | 0 | 9.1248 | 39.95
2022-10-27 02:30 | 44861.1042 | 0 | 8.9914 | 39.95
2022-10-27 03:00 | 44861.125 | 0 | 8.8473 | 39.95
2022-10-27 03:30 | 44861.1458 | 0 | 8.8673 | 39.95
2022-10-27 04:00 | 44861.1667 | 0 | 9.1165 | 39.95
2022-10-27 04:30 | 44861.1875 | 0 | 9.2329 | 39.95
2022-10-27 05:00 | 44861.2083 | 0 | 9.6504 | 39.95
2022-10-27 05:30 | 44861.2292 | 0 | 10.0189 | 39.95
2022-10-27 06:00 | 44861.25 | 0 | 10.7408 | 39.95
2022-10-27 06:30 | 44861.2708 | 0 | 11.609 | 39.95
2022-10-27 07:00 | 44861.2917 | 0 | 12.0365 | 39.95
2022-10-27 07:30 | 44861.3125 | 0 | 12.522 | 39.95
2022-10-27 08:00 | 44861.3333 | 0 | 12.5162 | 39.95
2022-10-27 08:30 | 44861.3542 | 0 | 11.7442 | 39.95
2022-10-27 09:00 | 44861.375 | 0 | 10.4113 | 39.95
2022-10-27 09:30 | 44861.3958 | 0 | 11.3629 | 39.95
2022-10-27 10:00 | 44861.4167 | 0 | 10.7732 | 39.95
2022-10-27 10:30 | 44861.4375 | 0 | 10.5679 | 39.95
2022-10-27 11:00 | 44861.4583 | 0 | 11.3603 | 39.95
2022-10-27 11:30 | 44861.4792 | 0 | 12.045 | 39.95
2022-10-27 12:00 | 44861.5 | 0 | 12.4233 | 39.95
2022-10-27 12:30 | 44861.5208 | 0 | 12.774 | 39.95
2022-10-27 13:00 | 44861.5417 | 0 | 13.4548 | 39.95
2022-10-27 13:30 | 44861.5625 | 0 | 14.1067 | 39.95
2022-10-27 14:00 | 44861.5833 | 0 | 14.8354 | 39.95
2022-10-27 14:30 | 44861.6042 | 0 | 16.1559 | 39.95
2022-10-27 15:00 | 44861.625 | 0 | 16.1387 | 39.95
2022-10-27 15:30 | 44861.6458 | 0 | 16.5411 | 39.95
2022-10-27 16:00 | 44861.6667 | 0 | 16.6223 | 39.95
2022-10-27 16:30 | 44861.6875 | 0 | 17.7718 | 39.95
2022-10-27 17:00 | 44861.7083 | 0 | 17.0736 | 39.95
2022-10-27 17:30 | 44861.7292 | 0 | 16.7881 | 39.95
2022-10-27 18:00 | 44861.75 | 0 | 16.8528 | 39.95
2022-10-27 18:30 | 44861.7708 | 0 | 17.2314 | 39.95
2022-10-27 19:00 | 44861.7917 | 0 | 17.1473 | 39.95
2022-10-27 19:30 | 44861.8125 | 0 | 16.7604 | 39.95
2022-10-27 20:00 | 44861.8333 | 0 | 16.2598 | 39.95
2022-10-27 20:30 | 44861.8542 | 0 | 15.6605 | 39.95
2022-10-27 21:00 | 44861.875 | 0 | 14.9605 | 39.95
2022-10-27 21:30 | 44861.8958 | 0 | 14.3205 | 39.95
2022-10-27 22:00 | 44861.9167 | 0 | 13.4763 | 39.95
2022-10-27 22:30 | 44861.9375 | 0 | 12.4797 | 39.95
2022-10-27 23:00 | 44861.9583 | 0 | 11.7103 | 39.95
2022-10-27 23:30 | 44861.9792 | 0 | 11.0158 | 39.95
2022-10-28 | 44862 | 0 | 10.3724 | 39.95
2022-10-28 00:30 | 44862.0208 | 0 | 10.0652 | 39.95
2022-10-28 01:00 | 44862.0417 | 0 | 9.845 | 39.95
2022-10-28 01:30 | 44862.0625 | 0 | 9.5917 | 39.95
2022-10-28 02:00 | 44862.0833 | 0 | 9.352 | 39.95
2022-10-28 02:30 | 44862.1042 | 0 | 9.2616 | 39.95
2022-10-28 03:00 | 44862.125 | 0 | 9.1296 | 39.95
2022-10-28 03:30 | 44862.1458 | 0 | 9.2183 | 39.95
2022-10-28 04:00 | 44862.1667 | 0 | 9.282 | 39.95
2022-10-28 04:30 | 44862.1875 | 0 | 9.5719 | 39.95
2022-10-28 05:00 | 44862.2083 | 0 | 9.9624 | 39.95
2022-10-28 05:30 | 44862.2292 | 0 | 10.0751 | 39.95
2022-10-28 06:00 | 44862.25 | 0 | 10.7417 | 39.95
2022-10-28 06:30 | 44862.2708 | 0 | 11.1877 | 39.95
2022-10-28 07:00 | 44862.2917 | 0 | 11.6335 | 39.95
2022-10-28 07:30 | 44862.3125 | 0 | 11.2333 | 39.95
2022-10-28 08:00 | 44862.3333 | 0 | 11.6213 | 39.95
2022-10-28 08:30 | 44862.3542 | 0 | 11.5732 | 39.95
2022-10-28 09:00 | 44862.375 | 0 | 11.4099 | 39.95
2022-10-28 09:30 | 44862.3958 | 0 | 11.3941 | 39.95
2022-10-28 10:00 | 44862.4167 | 0 | 11.219 | 39.95
2022-10-28 10:30 | 44862.4375 | 0 | 11.0834 | 39.95
2022-10-28 11:00 | 44862.4583 | 0 | 11.1916 | 39.95
2022-10-28 11:30 | 44862.4792 | 0 | 11.2646 | 39.95
2022-10-28 12:00 | 44862.5 | 0 | 11.5242 | 39.95
2022-10-28 12:30 | 44862.5208 | 0 | 11.7769 | 39.95
2022-10-28 13:00 | 44862.5417 | 0 | 12.2284 | 39.95
2022-10-28 13:30 | 44862.5625 | 0 | 13.0226 | 39.95
2022-10-28 14:00 | 44862.5833 | 0 | 13.8622 | 39.95
2022-10-28 14:30 | 44862.6042 | 0 | 14.2777 | 39.95
2022-10-28 15:00 | 44862.625 | 0 | 14.9481 | 39.95
2022-10-28 15:30 | 44862.6458 | 0 | 16.0279 | 39.95
2022-10-28 16:00 | 44862.6667 | 0 | 16.8351 | 39.95
2022-10-28 16:30 | 44862.6875 | 0 | 17.581 | 39.95
2022-10-28 17:00 | 44862.7083 | 0 | 16.8394 | 39.95
2022-10-28 17:30 | 44862.7292 | 0 | 16.5099 | 39.95
2022-10-28 18:00 | 44862.75 | 0 | 16.1956 | 39.95
2022-10-28 18:30 | 44862.7708 | 0 | 16.3865 | 39.95
2022-10-28 19:00 | 44862.7917 | 0 | 16.1221 | 39.95
2022-10-28 19:30 | 44862.8125 | 0 | 15.5793 | 39.95
2022-10-28 20:00 | 44862.8333 | 0 | 15.2287 | 39.95
2022-10-28 20:30 | 44862.8542 | 0 | 14.662 | 39.95
2022-10-28 21:00 | 44862.875 | 0 | 14.161 | 39.95
2022-10-28 21:30 | 44862.8958 | 0 | 13.4958 | 39.95
2022-10-28 22:00 | 44862.9167 | 0 | 12.8576 | 39.95
2022-10-28 22:30 | 44862.9375 | 0 | 11.9089 | 39.95
2022-10-28 23:00 | 44862.9583 | 0 | 11.2529 | 39.95
2022-10-28 23:30 | 44862.9792 | 0 | 10.5802 | 39.95
2022-10-29 | 44863 | 0 | 9.8562 | 39.95
2022-10-29 00:30 | 44863.0208 | 0 | 9.3842 | 39.95
2022-10-29 01:00 | 44863.0417 | 0 | 9.1659 | 39.95
2022-10-29 01:30 | 44863.0625 | 0 | 8.8056 | 39.95
2022-10-29 02:00 | 44863.0833 | 0 | 8.6588 | 39.95
2022-10-29 02:30 | 44863.1042 | 0 | 8.646 | 39.95
2022-10-29 03:00 | 44863.125 | 0 | 8.4939 | 39.95
2022-10-29 03:30 | 44863.1458 | 0 | 8.3077 | 39.95
2022-10-29 04:00 | 44863.1667 | 0 | 8.3634 | 39.95
2022-10-29 04:30 | 44863.1875 | 0 | 8.336 | 39.95
2022-10-29 05:00 | 44863.2083 | 0 | 8.3363 | 39.95
2022-10-29 05:30 | 44863.2292 | 0 | 7.9795 | 39.95
2022-10-29 06:00 | 44863.25 | 0 | 7.6589 | 39.95
2022-10-29 06:30 | 44863.2708 | 0 | 7.3321 | 39.95
2022-10-29 07:00 | 44863.2917 | 0 | 7.3119 | 39.95
2022-10-29 07:30 | 44863.3125 | 0 | 6.836 | 39.95
2022-10-29 08:00 | 44863.3333 | 0 | 6.9291 | 39.95
2022-10-29 08:30 | 44863.3542 | 0 | 6.7257 | 39.95
2022-10-29 09:00 | 44863.375 | 0 | 6.7174 | 39.95
2022-10-29 09:30 | 44863.3958 | 0 | 6.5042 | 39.95
2022-10-29 10:00 | 44863.4167 | 0 | 6.2341 | 39.95
2022-10-29 10:30 | 44863.4375 | 0 | 6.2645 | 39.95
2022-10-29 11:00 | 44863.4583 | 0 | 6.3999 | 39.95
2022-10-29 11:30 | 44863.4792 | 0 | 6.4988 | 39.95
2022-10-29 12:00 | 44863.5 | 0 | 6.6149 | 39.95
2022-10-29 12:30 | 44863.5208 | 0 | 6.9456 | 39.95
2022-10-29 13:00 | 44863.5417 | 0 | 7.4908 | 39.95
2022-10-29 13:30 | 44863.5625 | 0 | 7.9841 | 39.95
2022-10-29 14:00 | 44863.5833 | 0 | 8.8346 | 39.95
2022-10-29 14:30 | 44863.6042 | 0 | 9.1812 | 39.95
2022-10-29 15:00 | 44863.625 | 0 | 9.8798 | 39.95
2022-10-29 15:30 | 44863.6458 | 0 | 11.1674 | 39.95
2022-10-29 16:00 | 44863.6667 | 0 | 12.0009 | 39.95
2022-10-29 16:30 | 44863.6875 | 0 | 12.7281 | 39.95
2022-10-29 17:00 | 44863.7083 | 0 | 13.1515 | 39.95
2022-10-29 17:30 | 44863.7292 | 0 | 13.3271 | 39.95
2022-10-29 18:00 | 44863.75 | 0 | 13.4082 | 39.95
2022-10-29 18:30 | 44863.7708 | 0 | 13.5973 | 39.95
2022-10-29 19:00 | 44863.7917 | 0 | 13.5949 | 39.95
2022-10-29 19:30 | 44863.8125 | 0 | 13.1286 | 39.95
2022-10-29 20:00 | 44863.8333 | 0 | 12.8556 | 39.95
2022-10-29 20:30 | 44863.8542 | 0 | 12.3116 | 39.95
2022-10-29 21:00 | 44863.875 | 0 | 11.7989 | 39.95
2022-10-29 21:30 | 44863.8958 | 0 | 11.3174 | 39.95
2022-10-29 22:00 | 44863.9167 | 0 | 10.9369 | 39.95
2022-10-29 22:30 | 44863.9375 | 0 | 10.2912 | 39.95
2022-10-29 23:00 | 44863.9583 | 0 | 9.6028 | 39.95
2022-10-29 23:30 | 44863.9792 | 0 | 9.1245 | 39.95
2022-10-30 | 44864 | 0 | 8.6115 | 39.95
2022-10-30 00:30 | 44864.0208 | 0 | 8.367 | 39.95
2022-10-30 01:00 | 44864.0417 | 0 | 8.0817 | 39.95
2022-10-30 01:30 | 44864.0625 | 0 | 7.8358 | 39.95
2022-10-30 02:00 | 44864.0833 | 0 | 7.6848 | 39.95
2022-10-30 02:30 | 44864.1042 | 0 | 7.6128 | 39.95
2022-10-30 03:00 | 44864.125 | 0 | 7.5991 | 39.95
2022-10-30 03:30 | 44864.1458 | 0 | 7.3295 | 39.95
2022-10-30 04:00 | 44864.1667 | 0 | 7.3212 | 39.95
2022-10-30 04:30 | 44864.1875 | 0 | 7.2134 | 39.95
2022-10-30 05:00 | 44864.2083 | 0 | 7.2382 | 39.95
2022-10-30 05:30 | 44864.2292 | 0 | 7.0229 | 39.95
2022-10-30 06:00 | 44864.25 | 0 | 6.6032 | 39.95
2022-10-30 06:30 | 44864.2708 | 0 | 6.1969 | 39.95
2022-10-30 07:00 | 44864.2917 | 0 | 5.9485 | 39.95
2022-10-30 07:30 | 44864.3125 | 0 | 5.6385 | 39.95
2022-10-30 08:00 | 44864.3333 | 0 | 5.5177 | 39.95
2022-10-30 08:30 | 44864.3542 | 0 | 5.5013 | 39.95
2022-10-30 09:00 | 44864.375 | 0 | 5.5957 | 39.95
2022-10-30 09:30 | 44864.3958 | 0 | 5.5584 | 39.95
2022-10-30 10:00 | 44864.4167 | 0 | 5.6677 | 39.95
2022-10-30 10:30 | 44864.4375 | 0 | 5.7496 | 39.95
2022-10-30 11:00 | 44864.4583 | 0 | 5.7035 | 39.95
2022-10-30 11:30 | 44864.4792 | 0 | 5.7928 | 39.95
2022-10-30 12:00 | 44864.5 | 0 | 6.0429 | 39.95
2022-10-30 12:30 | 44864.5208 | 0 | 6.1543 | 39.95
2022-10-30 13:00 | 44864.5417 | 0 | 6.4828 | 39.95
2022-10-30 13:30 | 44864.5625 | 0 | 6.8112 | 39.95
2022-10-30 14:00 | 44864.5833 | 0 | 7.2843 | 39.95
2022-10-30 14:30 | 44864.6042 | 0 | 8.0406 | 39.95
2022-10-30 15:00 | 44864.625 | 0 | 8.6978 | 39.95
2022-10-30 15:30 | 44864.6458 | 0 | 9.5486 | 39.95
2022-10-30 16:00 | 44864.6667 | 0 | 10.4782 | 39.95
2022-10-30 16:30 | 44864.6875 | 0 | 11.3413 | 39.95
2022-10-30 17:00 | 44864.7083 | 0 | 11.7385 | 39.95
2022-10-30 17:30 | 44864.7292 | 0 | 12.2922 | 39.95
2022-10-30 18:00 | 44864.75 | 0 | 12.6877 | 39.95
2022-10-30 18:30 | 44864.7708 | 0 | 13.1325 | 39.95
2022-10-30 19:00 | 44864.7917 | 0 | 13.0972 | 39.95
2022-10-30 19:30 | 44864.8125 | 0 | 12.5837 | 39.95
2022-10-30 20:00 | 44864.8333 | 0 | 12.2702 | 39.95
2022-10-30 20:30 | 44864.8542 | 0 | 11.7458 | 39.95
2022-10-30 21:00 | 44864.875 | 0 | 11.1823 | 39.95
2022-10-30 21:30 | 44864.8958 | 0 | 10.7277 | 39.95
2022-10-30 22:00 | 44864.9167 | 0 | 10.1863 | 39.95
2022-10-30 22:30 | 44864.9375 | 0 | 9.3843 | 39.95
2022-10-30 23:00 | 44864.9583 | 0 | 9.0626 | 39.95
2022-10-30 23:30 | 44864.9792 | 0 | 8.5716 | 39.95
2022-10-31 | 44865 | 0 | 8.3331 | 39.95
2022-10-31 00:30 | 44865.0208 | 0 | 8.1059 | 39.95
2022-10-31 01:00 | 44865.0417 | 0 | 8.1133 | 39.95
2022-10-31 01:30 | 44865.0625 | 0 | 7.9436 | 39.95
2022-10-31 02:00 | 44865.0833 | 0 | 7.8799 | 39.95
2022-10-31 02:30 | 44865.1042 | 0 | 7.7688 | 39.95
2022-10-31 03:00 | 44865.125 | 0 | 7.6908 | 39.95
2022-10-31 03:30 | 44865.1458 | 0 | 7.9775 | 39.95
2022-10-31 04:00 | 44865.1667 | 0 | 8.0761 | 39.95
2022-10-31 04:30 | 44865.1875 | 0 | 8.4139 | 39.95
2022-10-31 05:00 | 44865.2083 | 0 | 8.9726 | 39.95
2022-10-31 05:30 | 44865.2292 | 0 | 9.3732 | 39.95
2022-10-31 06:00 | 44865.25 | 0 | 9.574 | 39.95
2022-10-31 06:30 | 44865.2708 | 0 | 10.0988 | 39.95
2022-10-31 07:00 | 44865.2917 | 0 | 10.4716 | 39.95
2022-10-31 07:30 | 44865.3125 | 0 | 10.5529 | 39.95
2022-10-31 08:00 | 44865.3333 | 0 | 10.1164 | 39.95
2022-10-31 08:30 | 44865.3542 | 0 | 9.8427 | 39.95
2022-10-31 09:00 | 44865.375 | 0 | 9.9621 | 39.95
2022-10-31 09:30 | 44865.3958 | 0 | 9.9946 | 39.95
2022-10-31 10:00 | 44865.4167 | 0 | 10.1346 | 39.95
2022-10-31 10:30 | 44865.4375 | 0 | 10.3809 | 39.95
2022-10-31 11:00 | 44865.4583 | 0 | 11.4622 | 39.95
2022-10-31 11:30 | 44865.4792 | 0 | 11.8835 | 39.95
2022-10-31 12:00 | 44865.5 | 0 | 11.526 | 39.95
2022-10-31 12:30 | 44865.5208 | 0 | 13.2678 | 39.95
2022-10-31 13:00 | 44865.5417 | 0 | 15.0109 | 39.95
2022-10-31 13:30 | 44865.5625 | 0 | 15.268 | 39.95
2022-10-31 14:00 | 44865.5833 | 0 | 14.877 | 39.95
2022-10-31 14:30 | 44865.6042 | 0 | 13.8151 | 39.95
2022-10-31 15:00 | 44865.625 | 0 | 13.7544 | 39.95
2022-10-31 15:30 | 44865.6458 | 0 | 14.9446 | 39.95
2022-10-31 16:00 | 44865.6667 | 0 | 15.0653 | 39.95
2022-10-31 16:30 | 44865.6875 | 0 | 14.8268 | 39.95
2022-10-31 17:00 | 44865.7083 | 0 | 15.2562 | 39.95
2022-10-31 17:30 | 44865.7292 | 0 | 15.4207 | 39.95
2022-10-31 18:00 | 44865.75 | 0 | 15.9156 | 39.95
2022-10-31 18:30 | 44865.7708 | 0 | 16.604 | 39.95
2022-10-31 19:00 | 44865.7917 | 0 | 16.6214 | 39.95
2022-10-31 19:30 | 44865.8125 | 0 | 16.2778 | 39.95
2022-10-31 20:00 | 44865.8333 | 0 | 16.0081 | 39.95
2022-10-31 20:30 | 44865.8542 | 0 | 15.1972 | 39.95
2022-10-31 21:00 | 44865.875 | 0 | 14.4938 | 39.95
2022-10-31 21:30 | 44865.8958 | 0 | 14.0675 | 39.95
2022-10-31 22:00 | 44865.9167 | 0 | 13.3225 | 39.95
2022-10-31 22:30 | 44865.9375 | 0 | 12.5786 | 39.95
2022-10-31 23:00 | 44865.9583 | 0 | 11.9013 | 39.95
2022-10-31 23:30 | 44865.9792 | 0 | 10.9401 | 39.95
2022-11-01 | 44866 | 0 | 10.3645 | 37.78
2022-11-01 00:30 | 44866.0208 | 0 | 10.0484 | 37.78
2022-11-01 01:00 | 44866.0417 | 0 | 9.7996 | 37.78
2022-11-01 01:30 | 44866.0625 | 0 | 9.5917 | 37.78
2022-11-01 02:00 | 44866.0833 | 0 | 9.5159 | 37.78
2022-11-01 02:30 | 44866.1042 | 0 | 9.5369 | 37.78
2022-11-01 03:00 | 44866.125 | 0 | 9.2826 | 37.78
2022-11-01 03:30 | 44866.1458 | 0 | 9.2555 | 37.78
2022-11-01 04:00 | 44866.1667 | 0 | 9.5596 | 37.78
2022-11-01 04:30 | 44866.1875 | 0 | 10.0809 | 37.78
2022-11-01 05:00 | 44866.2083 | 0 | 10.3567 | 37.78
2022-11-01 05:30 | 44866.2292 | 0 | 10.6965 | 37.78
2022-11-01 06:00 | 44866.25 | 0 | 11.7812 | 37.78
2022-11-01 06:30 | 44866.2708 | 0 | 12.3852 | 37.78
2022-11-01 07:00 | 44866.2917 | 0 | 13.9567 | 37.78
2022-11-01 07:30 | 44866.3125 | 0 | 14.3468 | 37.78
2022-11-01 08:00 | 44866.3333 | 0 | 13.6877 | 37.78
2022-11-01 08:30 | 44866.3542 | 0 | 13.9992 | 37.78
2022-11-01 09:00 | 44866.375 | 0 | 14.2054 | 37.78
2022-11-01 09:30 | 44866.3958 | 0 | 13.2592 | 37.78
2022-11-01 10:00 | 44866.4167 | 0 | 12.9846 | 37.78
2022-11-01 10:30 | 44866.4375 | 0 | 13.74 | 37.78
2022-11-01 11:00 | 44866.4583 | 0 | 13.0208 | 37.78
2022-11-01 11:30 | 44866.4792 | 0 | 12.7715 | 37.78
2022-11-01 12:00 | 44866.5 | 0 | 11.6607 | 37.78
2022-11-01 12:30 | 44866.5208 | 0 | 10.1575 | 37.78
2022-11-01 13:00 | 44866.5417 | 0 | 10.5356 | 37.78
2022-11-01 13:30 | 44866.5625 | 0 | 8.9444 | 37.78
2022-11-01 14:00 | 44866.5833 | 0 | 9.4761 | 37.78
2022-11-01 14:30 | 44866.6042 | 0 | 11.9178 | 37.78
2022-11-01 15:00 | 44866.625 | 0 | 11.1259 | 37.78
2022-11-01 15:30 | 44866.6458 | 0 | 12.6488 | 37.78
2022-11-01 16:00 | 44866.6667 | 0 | 13.2423 | 37.78
2022-11-01 16:30 | 44866.6875 | 0 | 12.7245 | 37.78
2022-11-01 17:00 | 44866.7083 | 0 | 12.8883 | 37.78
2022-11-01 17:30 | 44866.7292 | 0 | 13.4103 | 37.78
2022-11-01 18:00 | 44866.75 | 0 | 13.8174 | 37.78
2022-11-01 18:30 | 44866.7708 | 0 | 14.4654 | 37.78
2022-11-01 19:00 | 44866.7917 | 0 | 14.1829 | 37.78
2022-11-01 19:30 | 44866.8125 | 0 | 13.7647 | 37.78
2022-11-01 20:00 | 44866.8333 | 0 | 13.4013 | 37.78
2022-11-01 20:30 | 44866.8542 | 0 | 12.7508 | 37.78
2022-11-01 21:00 | 44866.875 | 0 | 12.257 | 37.78
2022-11-01 21:30 | 44866.8958 | 0 | 11.7747 | 37.78
2022-11-01 22:00 | 44866.9167 | 0 | 11.1913 | 37.78
2022-11-01 22:30 | 44866.9375 | 0 | 10.4983 | 37.78
2022-11-01 23:00 | 44866.9583 | 0 | 9.9 | 37.78
2022-11-01 23:30 | 44866.9792 | 0 | 9.5194 | 37.78
2022-11-02 | 44867 | 0 | 8.8976 | 37.78
2022-11-02 00:30 | 44867.0208 | 0 | 8.6275 | 37.78
2022-11-02 01:00 | 44867.0417 | 0 | 8.5645 | 37.78
2022-11-02 01:30 | 44867.0625 | 0 | 8.3631 | 37.78
2022-11-02 02:00 | 44867.0833 | 0 | 8.223 | 37.78
2022-11-02 02:30 | 44867.1042 | 0 | 8.3688 | 37.78
2022-11-02 03:00 | 44867.125 | 0 | 8.2938 | 37.78
2022-11-02 03:30 | 44867.1458 | 0 | 8.1946 | 37.78
2022-11-02 04:00 | 44867.1667 | 0 | 8.4304 | 37.78
2022-11-02 04:30 | 44867.1875 | 0 | 8.6951 | 37.78
2022-11-02 05:00 | 44867.2083 | 0 | 9.0161 | 37.78
2022-11-02 05:30 | 44867.2292 | 0 | 9.118 | 37.78
2022-11-02 06:00 | 44867.25 | 0 | 9.4297 | 37.78
2022-11-02 06:30 | 44867.2708 | 0 | 9.3997 | 37.78
2022-11-02 07:00 | 44867.2917 | 0 | 9.3866 | 37.78
2022-11-02 07:30 | 44867.3125 | 0 | 8.5348 | 37.78
2022-11-02 08:00 | 44867.3333 | 0 | 7.7509 | 37.78
2022-11-02 08:30 | 44867.3542 | 0 | 7.0402 | 37.78
2022-11-02 09:00 | 44867.375 | 0 | 6.615 | 37.78
2022-11-02 09:30 | 44867.3958 | 0 | 6.3556 | 37.78
2022-11-02 10:00 | 44867.4167 | 0 | 5.977 | 37.78
2022-11-02 10:30 | 44867.4375 | 0 | 6.2064 | 37.78
2022-11-02 11:00 | 44867.4583 | 0 | 6.1325 | 37.78
2022-11-02 11:30 | 44867.4792 | 0 | 5.9777 | 37.78
2022-11-02 12:00 | 44867.5 | 0 | 6.0361 | 37.78
2022-11-02 12:30 | 44867.5208 | 0 | 6.0063 | 37.78
2022-11-02 13:00 | 44867.5417 | 0 | 6.4018 | 37.78
2022-11-02 13:30 | 44867.5625 | 0 | 6.9224 | 37.78
2022-11-02 14:00 | 44867.5833 | 0 | 7.6285 | 37.78
2022-11-02 14:30 | 44867.6042 | 0 | 7.9401 | 37.78
2022-11-02 15:00 | 44867.625 | 0 | 8.6581 | 37.78
2022-11-02 15:30 | 44867.6458 | 0 | 9.6479 | 37.78
2022-11-02 16:00 | 44867.6667 | 0 | 10.5373 | 37.78
2022-11-02 16:30 | 44867.6875 | 0 | 11.3522 | 37.78
2022-11-02 17:00 | 44867.7083 | 0 | 12.0981 | 37.78
2022-11-02 17:30 | 44867.7292 | 0 | 12.534 | 37.78
2022-11-02 18:00 | 44867.75 | 0 | 12.8688 | 37.78
2022-11-02 18:30 | 44867.7708 | 0 | 13.4082 | 37.78
2022-11-02 19:00 | 44867.7917 | 0 | 13.4976 | 37.78
2022-11-02 19:30 | 44867.8125 | 0 | 12.9788 | 37.78
2022-11-02 20:00 | 44867.8333 | 0 | 12.6985 | 37.78
2022-11-02 20:30 | 44867.8542 | 0 | 12.087 | 37.78
2022-11-02 21:00 | 44867.875 | 0 | 11.5055 | 37.78
2022-11-02 21:30 | 44867.8958 | 0 | 11.149 | 37.78
2022-11-02 22:00 | 44867.9167 | 0 | 10.627 | 37.78
2022-11-02 22:30 | 44867.9375 | 0 | 10.0351 | 37.78
2022-11-02 23:00 | 44867.9583 | 0 | 9.5869 | 37.78
2022-11-02 23:30 | 44867.9792 | 0 | 9.2672 | 37.78
2022-11-03 | 44868 | 0 | 8.705 | 37.78
2022-11-03 00:30 | 44868.0208 | 0 | 8.3883 | 37.78
2022-11-03 01:00 | 44868.0417 | 0 | 8.2419 | 37.78
2022-11-03 01:30 | 44868.0625 | 0 | 8.1264 | 37.78
2022-11-03 02:00 | 44868.0833 | 0 | 8.0171 | 37.78
2022-11-03 02:30 | 44868.1042 | 0 | 8.0213 | 37.78
2022-11-03 03:00 | 44868.125 | 0 | 7.943 | 37.78
2022-11-03 03:30 | 44868.1458 | 0 | 7.9987 | 37.78
2022-11-03 04:00 | 44868.1667 | 0 | 8.1955 | 37.78
2022-11-03 04:30 | 44868.1875 | 0 | 8.4748 | 37.78
2022-11-03 05:00 | 44868.2083 | 0 | 9.0192 | 37.78
2022-11-03 05:30 | 44868.2292 | 0 | 9.0132 | 37.78
2022-11-03 06:00 | 44868.25 | 0 | 9.2198 | 37.78
2022-11-03 06:30 | 44868.2708 | 0 | 9.2972 | 37.78
2022-11-03 07:00 | 44868.2917 | 0 | 9.1478 | 37.78
2022-11-03 07:30 | 44868.3125 | 0 | 8.5441 | 37.78
2022-11-03 08:00 | 44868.3333 | 0 | 7.9925 | 37.78
2022-11-03 08:30 | 44868.3542 | 0 | 7.3733 | 37.78
2022-11-03 09:00 | 44868.375 | 0 | 6.815 | 37.78
2022-11-03 09:30 | 44868.3958 | 0 | 6.7665 | 37.78
2022-11-03 10:00 | 44868.4167 | 0 | 6.4541 | 37.78
2022-11-03 10:30 | 44868.4375 | 0 | 6.3457 | 37.78
2022-11-03 11:00 | 44868.4583 | 0 | 6.4862 | 37.78
2022-11-03 11:30 | 44868.4792 | 0 | 6.5503 | 37.78
2022-11-03 12:00 | 44868.5 | 0 | 6.6057 | 37.78
2022-11-03 12:30 | 44868.5208 | 0 | 6.9121 | 37.78
2022-11-03 13:00 | 44868.5417 | 0 | 7.1188 | 37.78
2022-11-03 13:30 | 44868.5625 | 0 | 7.4821 | 37.78
2022-11-03 14:00 | 44868.5833 | 0 | 8.0757 | 37.78
2022-11-03 14:30 | 44868.6042 | 0 | 8.735 | 37.78
2022-11-03 15:00 | 44868.625 | 0 | 9.3325 | 37.78
2022-11-03 15:30 | 44868.6458 | 0 | 10.0152 | 37.78
2022-11-03 16:00 | 44868.6667 | 0 | 10.7948 | 37.78
2022-11-03 16:30 | 44868.6875 | 0 | 11.5874 | 37.78
2022-11-03 17:00 | 44868.7083 | 0 | 12.1025 | 37.78
2022-11-03 17:30 | 44868.7292 | 0 | 12.4039 | 37.78
2022-11-03 18:00 | 44868.75 | 0 | 12.9274 | 37.78
2022-11-03 18:30 | 44868.7708 | 0 | 13.2647 | 37.78
2022-11-03 19:00 | 44868.7917 | 0 | 13.1483 | 37.78
2022-11-03 19:30 | 44868.8125 | 0 | 12.8981 | 37.78
2022-11-03 20:00 | 44868.8333 | 0 | 12.6645 | 37.78
2022-11-03 20:30 | 44868.8542 | 0 | 12.2314 | 37.78
2022-11-03 21:00 | 44868.875 | 0 | 11.6838 | 37.78
2022-11-03 21:30 | 44868.8958 | 0 | 11.1087 | 37.78
2022-11-03 22:00 | 44868.9167 | 0 | 10.678 | 37.78
2022-11-03 22:30 | 44868.9375 | 0 | 10.1433 | 37.78
2022-11-03 23:00 | 44868.9583 | 0 | 9.6427 | 37.78
2022-11-03 23:30 | 44868.9792 | 0 | 9.2377 | 37.78
2022-11-04 | 44869 | 0 | 8.7759 | 37.78
2022-11-04 00:30 | 44869.0208 | 0 | 8.3469 | 37.78
2022-11-04 01:00 | 44869.0417 | 0 | 8.3331 | 37.78
2022-11-04 01:30 | 44869.0625 | 0 | 8.0436 | 37.78
2022-11-04 02:00 | 44869.0833 | 0 | 7.9957 | 37.78
2022-11-04 02:30 | 44869.1042 | 0 | 8.0774 | 37.78
2022-11-04 03:00 | 44869.125 | 0 | 7.9876 | 37.78
2022-11-04 03:30 | 44869.1458 | 0 | 7.9391 | 37.78
2022-11-04 04:00 | 44869.1667 | 0 | 8.1797 | 37.78
2022-11-04 04:30 | 44869.1875 | 0 | 8.6017 | 37.78
2022-11-04 05:00 | 44869.2083 | 0 | 8.9616 | 37.78
2022-11-04 05:30 | 44869.2292 | 0 | 8.9515 | 37.78
2022-11-04 06:00 | 44869.25 | 0 | 9.0849 | 37.78
2022-11-04 06:30 | 44869.2708 | 0 | 9.4159 | 37.78
2022-11-04 07:00 | 44869.2917 | 0 | 9.407 | 37.78
2022-11-04 07:30 | 44869.3125 | 0 | 8.7434 | 37.78
2022-11-04 08:00 | 44869.3333 | 0 | 8.3066 | 37.78
2022-11-04 08:30 | 44869.3542 | 0 | 7.7251 | 37.78
2022-11-04 09:00 | 44869.375 | 0 | 7.4939 | 37.78
2022-11-04 09:30 | 44869.3958 | 0 | 7.4016 | 37.78
2022-11-04 10:00 | 44869.4167 | 0 | 7.3337 | 37.78
2022-11-04 10:30 | 44869.4375 | 0 | 7.4967 | 37.78
2022-11-04 11:00 | 44869.4583 | 0 | 8.009 | 37.78
2022-11-04 11:30 | 44869.4792 | 0 | 7.1699 | 37.78
2022-11-04 12:00 | 44869.5 | 0 | 6.8421 | 37.78
2022-11-04 12:30 | 44869.5208 | 0 | 7.6407 | 37.78
2022-11-04 13:00 | 44869.5417 | 0 | 7.0308 | 37.78
2022-11-04 13:30 | 44869.5625 | 0 | 8.1699 | 37.78
2022-11-04 14:00 | 44869.5833 | 0 | 8.1808 | 37.78
2022-11-04 14:30 | 44869.6042 | 0 | 8.2619 | 37.78
2022-11-04 15:00 | 44869.625 | 0 | 9.0466 | 37.78
2022-11-04 15:30 | 44869.6458 | 0 | 10.614 | 37.78
2022-11-04 16:00 | 44869.6667 | 0 | 11.5126 | 37.78
2022-11-04 16:30 | 44869.6875 | 0 | 11.717 | 37.78
2022-11-04 17:00 | 44869.7083 | 0 | 11.738 | 37.78
2022-11-04 17:30 | 44869.7292 | 0 | 12.2656 | 37.78
2022-11-04 18:00 | 44869.75 | 0 | 12.4768 | 37.78
2022-11-04 18:30 | 44869.7708 | 0 | 12.751 | 37.78
2022-11-04 19:00 | 44869.7917 | 0 | 12.7019 | 37.78
2022-11-04 19:30 | 44869.8125 | 0 | 12.4962 | 37.78
2022-11-04 20:00 | 44869.8333 | 0 | 12.3991 | 37.78
2022-11-04 20:30 | 44869.8542 | 0 | 11.9135 | 37.78
2022-11-04 21:00 | 44869.875 | 0 | 11.7404 | 37.78
2022-11-04 21:30 | 44869.8958 | 0 | 11.3879 | 37.78
2022-11-04 22:00 | 44869.9167 | 0 | 11.0264 | 37.78
2022-11-04 22:30 | 44869.9375 | 0 | 10.2066 | 37.78
2022-11-04 23:00 | 44869.9583 | 0 | 9.763 | 37.78
2022-11-04 23:30 | 44869.9792 | 0 | 9.257 | 37.78
2022-11-05 | 44870 | 0 | 8.8363 | 37.78
2022-11-05 00:30 | 44870.0208 | 0 | 8.3502 | 37.78
2022-11-05 01:00 | 44870.0417 | 0 | 8.2276 | 37.78
2022-11-05 01:30 | 44870.0625 | 0 | 8.0883 | 37.78
2022-11-05 02:00 | 44870.0833 | 0 | 8.1216 | 37.78
2022-11-05 02:30 | 44870.1042 | 0 | 8.0707 | 37.78
2022-11-05 03:00 | 44870.125 | 0 | 7.899 | 37.78
2022-11-05 03:30 | 44870.1458 | 0 | 7.7831 | 37.78
2022-11-05 04:00 | 44870.1667 | 0 | 8.06 | 37.78
2022-11-05 04:30 | 44870.1875 | 0 | 8.0823 | 37.78
2022-11-05 05:00 | 44870.2083 | 0 | 8.1672 | 37.78
2022-11-05 05:30 | 44870.2292 | 0 | 7.9968 | 37.78
2022-11-05 06:00 | 44870.25 | 0 | 7.3924 | 37.78
2022-11-05 06:30 | 44870.2708 | 0 | 6.9909 | 37.78
2022-11-05 07:00 | 44870.2917 | 0 | 6.6974 | 37.78
2022-11-05 07:30 | 44870.3125 | 0 | 7.0183 | 37.78
2022-11-05 08:00 | 44870.3333 | 0 | 7.766 | 37.78
2022-11-05 08:30 | 44870.3542 | 0 | 8.7434 | 37.78
2022-11-05 09:00 | 44870.375 | 0 | 8.2641 | 37.78
2022-11-05 09:30 | 44870.3958 | 0 | 8.6793 | 37.78
2022-11-05 10:00 | 44870.4167 | 0 | 7.3355 | 37.78
2022-11-05 10:30 | 44870.4375 | 0 | 6.5851 | 37.78
2022-11-05 11:00 | 44870.4583 | 0 | 5.2521 | 37.78
2022-11-05 11:30 | 44870.4792 | 0 | 5.9216 | 37.78
2022-11-05 12:00 | 44870.5 | 0 | 5.4485 | 37.78
2022-11-05 12:30 | 44870.5208 | 0 | 5.7892 | 37.78
2022-11-05 13:00 | 44870.5417 | 0 | 5.7275 | 37.78
2022-11-05 13:30 | 44870.5625 | 0 | 6.664 | 37.78
2022-11-05 14:00 | 44870.5833 | 0 | 7.239 | 37.78
2022-11-05 14:30 | 44870.6042 | 0 | 6.4747 | 37.78
2022-11-05 15:00 | 44870.625 | 0 | 8.0869 | 37.78
2022-11-05 15:30 | 44870.6458 | 0 | 8.7514 | 37.78
2022-11-05 16:00 | 44870.6667 | 0 | 9.2268 | 37.78
2022-11-05 16:30 | 44870.6875 | 0 | 9.6073 | 37.78
2022-11-05 17:00 | 44870.7083 | 0 | 10.0208 | 37.78
2022-11-05 17:30 | 44870.7292 | 0 | 10.4344 | 37.78
2022-11-05 18:00 | 44870.75 | 0 | 10.9995 | 37.78
2022-11-05 18:30 | 44870.7708 | 0 | 11.3838 | 37.78
2022-11-05 19:00 | 44870.7917 | 0 | 11.2533 | 37.78
2022-11-05 19:30 | 44870.8125 | 0 | 10.3228 | 37.78
2022-11-05 20:00 | 44870.8333 | 0 | 10.3248 | 37.78
2022-11-05 20:30 | 44870.8542 | 0 | 10.0432 | 37.78
2022-11-05 21:00 | 44870.875 | 0 | 9.7653 | 37.78
2022-11-05 21:30 | 44870.8958 | 0 | 9.5277 | 37.78
2022-11-05 22:00 | 44870.9167 | 0 | 9.2238 | 37.78
2022-11-05 22:30 | 44870.9375 | 0 | 8.7362 | 37.78
2022-11-05 23:00 | 44870.9583 | 0 | 8.4522 | 37.78
2022-11-05 23:30 | 44870.9792 | 0 | 8.0341 | 37.78
2022-11-06 | 44871 | 0 | 7.6835 | 37.78
2022-11-06 00:30 | 44871.0208 | 0 | 7.4287 | 37.78
2022-11-06 01:00 | 44871.0417 | 0 | 7.2879 | 37.78
2022-11-06 01:30 | 44871.0625 | 0 | 7.111 | 37.78
2022-11-06 02:00 | 44871.0833 | 0 | 7.0982 | 37.78
2022-11-06 02:30 | 44871.1042 | 0 | 6.9874 | 37.78
2022-11-06 03:00 | 44871.125 | 0 | 6.8957 | 37.78
2022-11-06 03:30 | 44871.1458 | 0 | 6.8848 | 37.78
2022-11-06 04:00 | 44871.1667 | 0 | 6.8162 | 37.78
2022-11-06 04:30 | 44871.1875 | 0 | 6.9806 | 37.78
2022-11-06 05:00 | 44871.2083 | 0 | 6.9764 | 37.78
2022-11-06 05:30 | 44871.2292 | 0 | 6.7314 | 37.78
2022-11-06 06:00 | 44871.25 | 0 | 6.2309 | 37.78
2022-11-06 06:30 | 44871.2708 | 0 | 5.6865 | 37.78
2022-11-06 07:00 | 44871.2917 | 0 | 5.3462 | 37.78
2022-11-06 07:30 | 44871.3125 | 0 | 4.8162 | 37.78
2022-11-06 08:00 | 44871.3333 | 0 | 5.0924 | 37.78
2022-11-06 08:30 | 44871.3542 | 0 | 5.6158 | 37.78
2022-11-06 09:00 | 44871.375 | 0 | 5.7344 | 37.78
2022-11-06 09:30 | 44871.3958 | 0 | 5.7113 | 37.78
2022-11-06 10:00 | 44871.4167 | 0 | 6.0115 | 37.78
2022-11-06 10:30 | 44871.4375 | 0 | 7.0492 | 37.78
2022-11-06 11:00 | 44871.4583 | 0 | 5.6673 | 37.78
2022-11-06 11:30 | 44871.4792 | 0 | 6.6352 | 37.78
2022-11-06 12:00 | 44871.5 | 0 | 6.2187 | 37.78
2022-11-06 12:30 | 44871.5208 | 0 | 4.5032 | 37.78
2022-11-06 13:00 | 44871.5417 | 0 | 4.8909 | 37.78
2022-11-06 13:30 | 44871.5625 | 0 | 5.0151 | 37.78
2022-11-06 14:00 | 44871.5833 | 0 | 5.6455 | 37.78
2022-11-06 14:30 | 44871.6042 | 0 | 5.9285 | 37.78
2022-11-06 15:00 | 44871.625 | 0 | 7.5373 | 37.78
2022-11-06 15:30 | 44871.6458 | 0 | 8.0734 | 37.78
2022-11-06 16:00 | 44871.6667 | 0 | 9.0051 | 37.78
2022-11-06 16:30 | 44871.6875 | 0 | 9.4523 | 37.78
2022-11-06 17:00 | 44871.7083 | 0 | 10.3196 | 37.78
2022-11-06 17:30 | 44871.7292 | 0 | 11.1499 | 37.78
2022-11-06 18:00 | 44871.75 | 0 | 11.6678 | 37.78
2022-11-06 18:30 | 44871.7708 | 0 | 11.9471 | 37.78
2022-11-06 19:00 | 44871.7917 | 0 | 11.5632 | 37.78
2022-11-06 19:30 | 44871.8125 | 0 | 11.1041 | 37.78
2022-11-06 20:00 | 44871.8333 | 0 | 10.6973 | 37.78
2022-11-06 20:30 | 44871.8542 | 0 | 10.2045 | 37.78
2022-11-06 21:00 | 44871.875 | 0 | 9.9538 | 37.78
2022-11-06 21:30 | 44871.8958 | 0 | 9.5105 | 37.78
2022-11-06 22:00 | 44871.9167 | 0 | 8.9606 | 37.78
2022-11-06 22:30 | 44871.9375 | 0 | 8.395 | 37.78
2022-11-06 23:00 | 44871.9583 | 0 | 8.2047 | 37.78
2022-11-06 23:30 | 44871.9792 | 0 | 8.0025 | 37.78
2022-11-07 | 44872 | 0 | 7.9105 | 37.78
2022-11-07 00:30 | 44872.0208 | 0 | 7.6019 | 37.78
2022-11-07 01:00 | 44872.0417 | 0 | 7.563 | 37.78
2022-11-07 01:30 | 44872.0625 | 0 | 7.3781 | 37.78
2022-11-07 02:00 | 44872.0833 | 0 | 7.3314 | 37.78
2022-11-07 02:30 | 44872.1042 | 0 | 7.4019 | 37.78
2022-11-07 03:00 | 44872.125 | 0 | 7.2793 | 37.78
2022-11-07 03:30 | 44872.1458 | 0 | 7.3364 | 37.78
2022-11-07 04:00 | 44872.1667 | 0 | 7.7593 | 37.78
2022-11-07 04:30 | 44872.1875 | 0 | 8.0323 | 37.78
2022-11-07 05:00 | 44872.2083 | 0 | 8.3131 | 37.78
2022-11-07 05:30 | 44872.2292 | 0 | 8.5764 | 37.78
2022-11-07 06:00 | 44872.25 | 0 | 8.9092 | 37.78
2022-11-07 06:30 | 44872.2708 | 0 | 8.8101 | 37.78
2022-11-07 07:00 | 44872.2917 | 0 | 8.7583 | 37.78
2022-11-07 07:30 | 44872.3125 | 0 | 8.6037 | 37.78
2022-11-07 08:00 | 44872.3333 | 0 | 8.4027 | 37.78
2022-11-07 08:30 | 44872.3542 | 0 | 8.7595 | 37.78
2022-11-07 09:00 | 44872.375 | 0 | 9.5972 | 37.78
2022-11-07 09:30 | 44872.3958 | 0 | 8.3609 | 37.78
2022-11-07 10:00 | 44872.4167 | 0 | 7.7804 | 37.78
2022-11-07 10:30 | 44872.4375 | 0 | 7.4061 | 37.78
2022-11-07 11:00 | 44872.4583 | 0 | 7.1224 | 37.78
2022-11-07 11:30 | 44872.4792 | 0 | 7.1479 | 37.78
2022-11-07 12:00 | 44872.5 | 0 | 7.0955 | 37.78
2022-11-07 12:30 | 44872.5208 | 0 | 7.4263 | 37.78
2022-11-07 13:00 | 44872.5417 | 0 | 7.7741 | 37.78
2022-11-07 13:30 | 44872.5625 | 0 | 7.7977 | 37.78
2022-11-07 14:00 | 44872.5833 | 0 | 8.8046 | 37.78
2022-11-07 14:30 | 44872.6042 | 0 | 9.1704 | 37.78
2022-11-07 15:00 | 44872.625 | 0 | 9.7743 | 37.78
2022-11-07 15:30 | 44872.6458 | 0 | 10.29 | 37.78
2022-11-07 16:00 | 44872.6667 | 0 | 10.9121 | 37.78
2022-11-07 16:30 | 44872.6875 | 0 | 11.9042 | 37.78
2022-11-07 17:00 | 44872.7083 | 0 | 12.4 | 37.78
2022-11-07 17:30 | 44872.7292 | 0 | 12.8738 | 37.78
2022-11-07 18:00 | 44872.75 | 0 | 13.2845 | 37.78
2022-11-07 18:30 | 44872.7708 | 0 | 13.6453 | 37.78
2022-11-07 19:00 | 44872.7917 | 0 | 13.414 | 37.78
2022-11-07 19:30 | 44872.8125 | 0 | 13.0807 | 37.78
2022-11-07 20:00 | 44872.8333 | 0 | 12.7243 | 37.78
2022-11-07 20:30 | 44872.8542 | 0 | 12.0856 | 37.78
2022-11-07 21:00 | 44872.875 | 0 | 11.6752 | 37.78
2022-11-07 21:30 | 44872.8958 | 0 | 11.2088 | 37.78
2022-11-07 22:00 | 44872.9167 | 0 | 10.5478 | 37.78
2022-11-07 22:30 | 44872.9375 | 0 | 9.8965 | 37.78
2022-11-07 23:00 | 44872.9583 | 0 | 9.4608 | 37.78
2022-11-07 23:30 | 44872.9792 | 0 | 9.126 | 37.78
2022-11-08 | 44873 | 0 | 8.6677 | 37.78
2022-11-08 00:30 | 44873.0208 | 0 | 8.3223 | 37.78
2022-11-08 01:00 | 44873.0417 | 0 | 8.1708 | 37.78
2022-11-08 01:30 | 44873.0625 | 0 | 8.0508 | 37.78
2022-11-08 02:00 | 44873.0833 | 0 | 7.9331 | 37.78
2022-11-08 02:30 | 44873.1042 | 0 | 7.898 | 37.78
2022-11-08 03:00 | 44873.125 | 0 | 7.8998 | 37.78
2022-11-08 03:30 | 44873.1458 | 0 | 7.9069 | 37.78
2022-11-08 04:00 | 44873.1667 | 0 | 8.2875 | 37.78
2022-11-08 04:30 | 44873.1875 | 0 | 8.5332 | 37.78
2022-11-08 05:00 | 44873.2083 | 0 | 8.8963 | 37.78
2022-11-08 05:30 | 44873.2292 | 0 | 9.0096 | 37.78
2022-11-08 06:00 | 44873.25 | 0 | 9.0947 | 37.78
2022-11-08 06:30 | 44873.2708 | 0 | 9.1877 | 37.78
2022-11-08 07:00 | 44873.2917 | 0 | 8.9265 | 37.78
2022-11-08 07:30 | 44873.3125 | 0 | 9.1874 | 37.78
2022-11-08 08:00 | 44873.3333 | 0 | 8.4674 | 37.78
2022-11-08 08:30 | 44873.3542 | 0 | 8.6613 | 37.78
2022-11-08 09:00 | 44873.375 | 0 | 9.3537 | 37.78
2022-11-08 09:30 | 44873.3958 | 0 | 11.1243 | 37.78
2022-11-08 10:00 | 44873.4167 | 0 | 9.6629 | 37.78
2022-11-08 10:30 | 44873.4375 | 0 | 8.7006 | 37.78
2022-11-08 11:00 | 44873.4583 | 0 | 8.117 | 37.78
2022-11-08 11:30 | 44873.4792 | 0 | 9.3656 | 37.78
2022-11-08 12:00 | 44873.5 | 0 | 9.285 | 37.78
2022-11-08 12:30 | 44873.5208 | 0 | 7.5915 | 37.78
2022-11-08 13:00 | 44873.5417 | 0 | 9.3047 | 37.78
2022-11-08 13:30 | 44873.5625 | 0 | 10.0858 | 37.78
2022-11-08 14:00 | 44873.5833 | 0 | 10.3547 | 37.78
2022-11-08 14:30 | 44873.6042 | 0 | 8.999 | 37.78
2022-11-08 15:00 | 44873.625 | 0 | 11.5828 | 37.78
2022-11-08 15:30 | 44873.6458 | 0 | 9.811 | 37.78
2022-11-08 16:00 | 44873.6667 | 0 | 10.7197 | 37.78
2022-11-08 16:30 | 44873.6875 | 0 | 11.4479 | 37.78
2022-11-08 17:00 | 44873.7083 | 0 | 11.9727 | 37.78
2022-11-08 17:30 | 44873.7292 | 0 | 12.6441 | 37.78
2022-11-08 18:00 | 44873.75 | 0 | 13.0402 | 37.78
2022-11-08 18:30 | 44873.7708 | 0 | 13.7702 | 37.78
2022-11-08 19:00 | 44873.7917 | 0 | 13.3712 | 37.78
2022-11-08 19:30 | 44873.8125 | 0 | 13.0744 | 37.78
2022-11-08 20:00 | 44873.8333 | 0 | 12.829 | 37.78
2022-11-08 20:30 | 44873.8542 | 0 | 12.1784 | 37.78
2022-11-08 21:00 | 44873.875 | 0 | 11.7916 | 37.78
2022-11-08 21:30 | 44873.8958 | 0 | 11.554 | 37.78
2022-11-08 22:00 | 44873.9167 | 0 | 10.9928 | 37.78
2022-11-08 22:30 | 44873.9375 | 0 | 10.1405 | 37.78
2022-11-08 23:00 | 44873.9583 | 0 | 9.7015 | 37.78
2022-11-08 23:30 | 44873.9792 | 0 | 9.303 | 37.78
2022-11-09 | 44874 | 0 | 8.8714 | 37.78
2022-11-09 00:30 | 44874.0208 | 0 | 8.4541 | 37.78
2022-11-09 01:00 | 44874.0417 | 0 | 8.2282 | 37.78
2022-11-09 01:30 | 44874.0625 | 0 | 8.099 | 37.78
2022-11-09 02:00 | 44874.0833 | 0 | 8.0237 | 37.78
2022-11-09 02:30 | 44874.1042 | 0 | 8.0272 | 37.78
2022-11-09 03:00 | 44874.125 | 0 | 7.9093 | 37.78
2022-11-09 03:30 | 44874.1458 | 0 | 8.0177 | 37.78
2022-11-09 04:00 | 44874.1667 | 0 | 8.3334 | 37.78
2022-11-09 04:30 | 44874.1875 | 0 | 8.4569 | 37.78
2022-11-09 05:00 | 44874.2083 | 0 | 8.9613 | 37.78
2022-11-09 05:30 | 44874.2292 | 0 | 9.1671 | 37.78
2022-11-09 06:00 | 44874.25 | 0 | 9.1882 | 37.78
2022-11-09 06:30 | 44874.2708 | 0 | 9.3551 | 37.78
2022-11-09 07:00 | 44874.2917 | 0 | 9.4924 | 37.78
2022-11-09 07:30 | 44874.3125 | 0 | 8.6574 | 37.78
2022-11-09 08:00 | 44874.3333 | 0 | 8.8031 | 37.78
2022-11-09 08:30 | 44874.3542 | 0 | 9.8747 | 37.78
2022-11-09 09:00 | 44874.375 | 0 | 8.617 | 37.78
2022-11-09 09:30 | 44874.3958 | 0 | 7.9013 | 37.78
2022-11-09 10:00 | 44874.4167 | 0 | 8.9581 | 37.78
2022-11-09 10:30 | 44874.4375 | 0 | 7.7005 | 37.78
2022-11-09 11:00 | 44874.4583 | 0 | 9.6139 | 37.78
2022-11-09 11:30 | 44874.4792 | 0 | 9.263 | 37.78
2022-11-09 12:00 | 44874.5 | 0 | 9.9014 | 37.78
2022-11-09 12:30 | 44874.5208 | 0 | 9.6562 | 37.78
2022-11-09 13:00 | 44874.5417 | 0 | 9.6954 | 37.78
2022-11-09 13:30 | 44874.5625 | 0 | 9.1905 | 37.78
2022-11-09 14:00 | 44874.5833 | 0 | 10.2097 | 37.78
2022-11-09 14:30 | 44874.6042 | 0 | 9.6518 | 37.78
2022-11-09 15:00 | 44874.625 | 0 | 10.8862 | 37.78
2022-11-09 15:30 | 44874.6458 | 0 | 11.1315 | 37.78
2022-11-09 16:00 | 44874.6667 | 0 | 10.6456 | 37.78
2022-11-09 16:30 | 44874.6875 | 0 | 11.8384 | 37.78
2022-11-09 17:00 | 44874.7083 | 0 | 12.2636 | 37.78
2022-11-09 17:30 | 44874.7292 | 0 | 12.7537 | 37.78
2022-11-09 18:00 | 44874.75 | 0 | 13.3012 | 37.78
2022-11-09 18:30 | 44874.7708 | 0 | 13.7447 | 37.78
2022-11-09 19:00 | 44874.7917 | 0 | 13.4478 | 37.78
2022-11-09 19:30 | 44874.8125 | 0 | 13.1178 | 37.78
2022-11-09 20:00 | 44874.8333 | 0 | 12.8323 | 37.78
2022-11-09 20:30 | 44874.8542 | 0 | 12.3895 | 37.78
2022-11-09 21:00 | 44874.875 | 0 | 11.8006 | 37.78
2022-11-09 21:30 | 44874.8958 | 0 | 11.4176 | 37.78
2022-11-09 22:00 | 44874.9167 | 0 | 10.8961 | 37.78
2022-11-09 22:30 | 44874.9375 | 0 | 10.1601 | 37.78
2022-11-09 23:00 | 44874.9583 | 0 | 9.7003 | 37.78
2022-11-09 23:30 | 44874.9792 | 0 | 9.3125 | 37.78
2022-11-10 | 44875 | 0 | 8.7698 | 37.78
2022-11-10 00:30 | 44875.0208 | 0 | 8.4426 | 37.78
2022-11-10 01:00 | 44875.0417 | 0 | 8.2245 | 37.78
2022-11-10 01:30 | 44875.0625 | 0 | 8.0436 | 37.78
2022-11-10 02:00 | 44875.0833 | 0 | 8.0841 | 37.78
2022-11-10 02:30 | 44875.1042 | 0 | 7.9841 | 37.78
2022-11-10 03:00 | 44875.125 | 0 | 7.9987 | 37.78
2022-11-10 03:30 | 44875.1458 | 0 | 8.1296 | 37.78
2022-11-10 04:00 | 44875.1667 | 0 | 8.3703 | 37.78
2022-11-10 04:30 | 44875.1875 | 0 | 8.6543 | 37.78
2022-11-10 05:00 | 44875.2083 | 0 | 9.1201 | 37.78
2022-11-10 05:30 | 44875.2292 | 0 | 9.217 | 37.78
2022-11-10 06:00 | 44875.25 | 0 | 9.1999 | 37.78
2022-11-10 06:30 | 44875.2708 | 0 | 9.425 | 37.78
2022-11-10 07:00 | 44875.2917 | 0 | 9.4034 | 37.78
2022-11-10 07:30 | 44875.3125 | 0 | 8.6871 | 37.78
2022-11-10 08:00 | 44875.3333 | 0 | 8.3572 | 37.78
2022-11-10 08:30 | 44875.3542 | 0 | 8.5497 | 37.78
2022-11-10 09:00 | 44875.375 | 0 | 7.7535 | 37.78
2022-11-10 09:30 | 44875.3958 | 0 | 9.0438 | 37.78
2022-11-10 10:00 | 44875.4167 | 0 | 9.5955 | 37.78
2022-11-10 10:30 | 44875.4375 | 0 | 7.4235 | 37.78
2022-11-10 11:00 | 44875.4583 | 0 | 9.4852 | 37.78
2022-11-10 11:30 | 44875.4792 | 0 | 9.1674 | 37.78
2022-11-10 12:00 | 44875.5 | 0 | 8.7266 | 37.78
2022-11-10 12:30 | 44875.5208 | 0 | 8.9331 | 37.78
2022-11-10 13:00 | 44875.5417 | 0 | 9.8448 | 37.78
2022-11-10 13:30 | 44875.5625 | 0 | 10.0264 | 37.78
2022-11-10 14:00 | 44875.5833 | 0 | 10.8496 | 37.78
2022-11-10 14:30 | 44875.6042 | 0 | 10.674 | 37.78
2022-11-10 15:00 | 44875.625 | 0 | 10.6273 | 37.78
2022-11-10 15:30 | 44875.6458 | 0 | 10.4629 | 37.78
2022-11-10 16:00 | 44875.6667 | 0 | 11.0686 | 37.78
2022-11-10 16:30 | 44875.6875 | 0 | 11.9143 | 37.78
2022-11-10 17:00 | 44875.7083 | 0 | 12.4714 | 37.78
2022-11-10 17:30 | 44875.7292 | 0 | 12.9062 | 37.78
2022-11-10 18:00 | 44875.75 | 0 | 13.2191 | 37.78
2022-11-10 18:30 | 44875.7708 | 0 | 13.6523 | 37.78
2022-11-10 19:00 | 44875.7917 | 0 | 13.4324 | 37.78
2022-11-10 19:30 | 44875.8125 | 0 | 13.0503 | 37.78
2022-11-10 20:00 | 44875.8333 | 0 | 13.0339 | 37.78
2022-11-10 20:30 | 44875.8542 | 0 | 12.2988 | 37.78
2022-11-10 21:00 | 44875.875 | 0 | 11.8931 | 37.78
2022-11-10 21:30 | 44875.8958 | 0 | 11.4858 | 37.78
2022-11-10 22:00 | 44875.9167 | 0 | 10.8556 | 37.78
2022-11-10 22:30 | 44875.9375 | 0 | 10.2022 | 37.78
2022-11-10 23:00 | 44875.9583 | 0 | 9.6882 | 37.78
2022-11-10 23:30 | 44875.9792 | 0 | 9.2806 | 37.78
2022-11-11 | 44876 | 0 | 8.7475 | 37.78
2022-11-11 00:30 | 44876.0208 | 0 | 8.3941 | 37.78
2022-11-11 01:00 | 44876.0417 | 0 | 8.2639 | 37.78
2022-11-11 01:30 | 44876.0625 | 0 | 8.1526 | 37.78
2022-11-11 02:00 | 44876.0833 | 0 | 8.0669 | 37.78
2022-11-11 02:30 | 44876.1042 | 0 | 8.1356 | 37.78
2022-11-11 03:00 | 44876.125 | 0 | 7.9859 | 37.78
2022-11-11 03:30 | 44876.1458 | 0 | 8.0079 | 37.78
2022-11-11 04:00 | 44876.1667 | 0 | 8.4438 | 37.78
2022-11-11 04:30 | 44876.1875 | 0 | 8.6686 | 37.78
2022-11-11 05:00 | 44876.2083 | 0 | 8.9685 | 37.78
2022-11-11 05:30 | 44876.2292 | 0 | 9.1287 | 37.78
2022-11-11 06:00 | 44876.25 | 0 | 9.3612 | 37.78
2022-11-11 06:30 | 44876.2708 | 0 | 9.5387 | 37.78
2022-11-11 07:00 | 44876.2917 | 0 | 9.4893 | 37.78
2022-11-11 07:30 | 44876.3125 | 0 | 9.0236 | 37.78
2022-11-11 08:00 | 44876.3333 | 0 | 8.6922 | 37.78
2022-11-11 08:30 | 44876.3542 | 0 | 8.4804 | 37.78
2022-11-11 09:00 | 44876.375 | 0 | 8.3875 | 37.78
2022-11-11 09:30 | 44876.3958 | 0 | 8.2139 | 37.78
2022-11-11 10:00 | 44876.4167 | 0 | 7.8406 | 37.78
2022-11-11 10:30 | 44876.4375 | 0 | 7.9394 | 37.78
2022-11-11 11:00 | 44876.4583 | 0 | 8.0692 | 37.78
2022-11-11 11:30 | 44876.4792 | 0 | 8.2892 | 37.78
2022-11-11 12:00 | 44876.5 | 0 | 8.0843 | 37.78
2022-11-11 12:30 | 44876.5208 | 0 | 8.0046 | 37.78
2022-11-11 13:00 | 44876.5417 | 0 | 8.0189 | 37.78
2022-11-11 13:30 | 44876.5625 | 0 | 8.7798 | 37.78
2022-11-11 14:00 | 44876.5833 | 0 | 8.9854 | 37.78
2022-11-11 14:30 | 44876.6042 | 0 | 9.7778 | 37.78
2022-11-11 15:00 | 44876.625 | 0 | 10.2459 | 37.78
2022-11-11 15:30 | 44876.6458 | 0 | 11.8645 | 37.78
2022-11-11 16:00 | 44876.6667 | 0 | 11.5985 | 37.78
2022-11-11 16:30 | 44876.6875 | 0 | 13.1855 | 37.78
2022-11-11 17:00 | 44876.7083 | 0 | 12.9892 | 37.78
2022-11-11 17:30 | 44876.7292 | 0 | 12.9544 | 37.78
2022-11-11 18:00 | 44876.75 | 0 | 13.0277 | 37.78
2022-11-11 18:30 | 44876.7708 | 0 | 13.1325 | 37.78
2022-11-11 19:00 | 44876.7917 | 0 | 13.2519 | 37.78
2022-11-11 19:30 | 44876.8125 | 0 | 12.9482 | 37.78
2022-11-11 20:00 | 44876.8333 | 0 | 12.9187 | 37.78
2022-11-11 20:30 | 44876.8542 | 0 | 12.4186 | 37.78
2022-11-11 21:00 | 44876.875 | 0 | 12.0452 | 37.78
2022-11-11 21:30 | 44876.8958 | 0 | 11.5582 | 37.78
2022-11-11 22:00 | 44876.9167 | 0 | 11.1904 | 37.78
2022-11-11 22:30 | 44876.9375 | 0 | 10.4441 | 37.78
2022-11-11 23:00 | 44876.9583 | 0 | 10.0354 | 37.78
2022-11-11 23:30 | 44876.9792 | 0 | 9.5755 | 37.78
2022-11-12 | 44877 | 0 | 9.0273 | 37.78
2022-11-12 00:30 | 44877.0208 | 0 | 8.6274 | 37.78
2022-11-12 01:00 | 44877.0417 | 0 | 8.4251 | 37.78
2022-11-12 01:30 | 44877.0625 | 0 | 8.3473 | 37.78
2022-11-12 02:00 | 44877.0833 | 0 | 8.0802 | 37.78
2022-11-12 02:30 | 44877.1042 | 0 | 8.1749 | 37.78
2022-11-12 03:00 | 44877.125 | 0 | 7.9504 | 37.78
2022-11-12 03:30 | 44877.1458 | 0 | 8.032 | 37.78
2022-11-12 04:00 | 44877.1667 | 0 | 8.0797 | 37.78
2022-11-12 04:30 | 44877.1875 | 0 | 7.9713 | 37.78
2022-11-12 05:00 | 44877.2083 | 0 | 8.0734 | 37.78
2022-11-12 05:30 | 44877.2292 | 0 | 7.7214 | 37.78
2022-11-12 06:00 | 44877.25 | 0 | 7.4227 | 37.78
2022-11-12 06:30 | 44877.2708 | 0 | 7.147 | 37.78
2022-11-12 07:00 | 44877.2917 | 0 | 7.1396 | 37.78
2022-11-12 07:30 | 44877.3125 | 0 | 6.3745 | 37.78
2022-11-12 08:00 | 44877.3333 | 0 | 6.5426 | 37.78
2022-11-12 08:30 | 44877.3542 | 0 | 6.2056 | 37.78
2022-11-12 09:00 | 44877.375 | 0 | 5.6731 | 37.78
2022-11-12 09:30 | 44877.3958 | 0 | 5.9283 | 37.78
2022-11-12 10:00 | 44877.4167 | 0 | 5.9634 | 37.78
2022-11-12 10:30 | 44877.4375 | 0 | 5.8059 | 37.78
2022-11-12 11:00 | 44877.4583 | 0 | 5.8345 | 37.78
2022-11-12 11:30 | 44877.4792 | 0 | 6.2896 | 37.78
2022-11-12 12:00 | 44877.5 | 0 | 6.1568 | 37.78
2022-11-12 12:30 | 44877.5208 | 0 | 6.0687 | 37.78
2022-11-12 13:00 | 44877.5417 | 0 | 6.8958 | 37.78
2022-11-12 13:30 | 44877.5625 | 0 | 8.1855 | 37.78
2022-11-12 14:00 | 44877.5833 | 0 | 8.8181 | 37.78
2022-11-12 14:30 | 44877.6042 | 0 | 9.3746 | 37.78
2022-11-12 15:00 | 44877.625 | 0 | 10.9177 | 37.78
2022-11-12 15:30 | 44877.6458 | 0 | 10.7496 | 37.78
2022-11-12 16:00 | 44877.6667 | 0 | 10.8683 | 37.78
2022-11-12 16:30 | 44877.6875 | 0 | 10.4759 | 37.78
2022-11-12 17:00 | 44877.7083 | 0 | 11.76 | 37.78
2022-11-12 17:30 | 44877.7292 | 0 | 11.8167 | 37.78
2022-11-12 18:00 | 44877.75 | 0 | 12.0051 | 37.78
2022-11-12 18:30 | 44877.7708 | 0 | 12.5588 | 37.78
2022-11-12 19:00 | 44877.7917 | 0 | 12.4479 | 37.78
2022-11-12 19:30 | 44877.8125 | 0 | 12.1618 | 37.78
2022-11-12 20:00 | 44877.8333 | 0 | 11.9084 | 37.78
2022-11-12 20:30 | 44877.8542 | 0 | 11.4365 | 37.78
2022-11-12 21:00 | 44877.875 | 0 | 10.985 | 37.78
2022-11-12 21:30 | 44877.8958 | 0 | 10.7825 | 37.78
2022-11-12 22:00 | 44877.9167 | 0 | 10.4847 | 37.78
2022-11-12 22:30 | 44877.9375 | 0 | 10.0134 | 37.78
2022-11-12 23:00 | 44877.9583 | 0 | 9.4792 | 37.78
2022-11-12 23:30 | 44877.9792 | 0 | 9.031 | 37.78
2022-11-13 | 44878 | 0 | 8.6247 | 37.78
2022-11-13 00:30 | 44878.0208 | 0 | 8.3012 | 37.78
2022-11-13 01:00 | 44878.0417 | 0 | 8.1788 | 37.78
2022-11-13 01:30 | 44878.0625 | 0 | 7.9597 | 37.78
2022-11-13 02:00 | 44878.0833 | 0 | 7.9019 | 37.78
2022-11-13 02:30 | 44878.1042 | 0 | 7.8159 | 37.78
2022-11-13 03:00 | 44878.125 | 0 | 7.7232 | 37.78
2022-11-13 03:30 | 44878.1458 | 0 | 7.6964 | 37.78
2022-11-13 04:00 | 44878.1667 | 0 | 7.686 | 37.78
2022-11-13 04:30 | 44878.1875 | 0 | 7.5273 | 37.78
2022-11-13 05:00 | 44878.2083 | 0 | 7.4052 | 37.78
2022-11-13 05:30 | 44878.2292 | 0 | 7.1031 | 37.78
2022-11-13 06:00 | 44878.25 | 0 | 6.935 | 37.78
2022-11-13 06:30 | 44878.2708 | 0 | 6.386 | 37.78
2022-11-13 07:00 | 44878.2917 | 0 | 6.3788 | 37.78
2022-11-13 07:30 | 44878.3125 | 0 | 5.9676 | 37.78
2022-11-13 08:00 | 44878.3333 | 0 | 5.8717 | 37.78
2022-11-13 08:30 | 44878.3542 | 0 | 5.5564 | 37.78
2022-11-13 09:00 | 44878.375 | 0 | 6.4494 | 37.78
2022-11-13 09:30 | 44878.3958 | 0 | 5.9697 | 37.78
2022-11-13 10:00 | 44878.4167 | 0 | 6.8359 | 37.78
2022-11-13 10:30 | 44878.4375 | 0 | 5.6159 | 37.78
2022-11-13 11:00 | 44878.4583 | 0 | 5.6084 | 37.78
2022-11-13 11:30 | 44878.4792 | 0 | 5.7239 | 37.78
2022-11-13 12:00 | 44878.5 | 0 | 5.8747 | 37.78
2022-11-13 12:30 | 44878.5208 | 0 | 7.1121 | 37.78
2022-11-13 13:00 | 44878.5417 | 0 | 7.9635 | 37.78
2022-11-13 13:30 | 44878.5625 | 0 | 6.9457 | 37.78
2022-11-13 14:00 | 44878.5833 | 0 | 7.426 | 37.78
2022-11-13 14:30 | 44878.6042 | 0 | 8.0204 | 37.78
2022-11-13 15:00 | 44878.625 | 0 | 8.5588 | 37.78
2022-11-13 15:30 | 44878.6458 | 0 | 9.5285 | 37.78
2022-11-13 16:00 | 44878.6667 | 0 | 10.4535 | 37.78
2022-11-13 16:30 | 44878.6875 | 0 | 11.4714 | 37.78
2022-11-13 17:00 | 44878.7083 | 0 | 12.1397 | 37.78
2022-11-13 17:30 | 44878.7292 | 0 | 12.5477 | 37.78
2022-11-13 18:00 | 44878.75 | 0 | 13.0729 | 37.78
2022-11-13 18:30 | 44878.7708 | 0 | 13.3668 | 37.78
2022-11-13 19:00 | 44878.7917 | 0 | 13.304 | 37.78
2022-11-13 19:30 | 44878.8125 | 0 | 12.9657 | 37.78
2022-11-13 20:00 | 44878.8333 | 0 | 12.8203 | 37.78
2022-11-13 20:30 | 44878.8542 | 0 | 12.155 | 37.78
2022-11-13 21:00 | 44878.875 | 0 | 11.7788 | 37.78
2022-11-13 21:30 | 44878.8958 | 0 | 11.2376 | 37.78
2022-11-13 22:00 | 44878.9167 | 0 | 10.8832 | 37.78
2022-11-13 22:30 | 44878.9375 | 0 | 10.3058 | 37.78
2022-11-13 23:00 | 44878.9583 | 0 | 9.7164 | 37.78
2022-11-13 23:30 | 44878.9792 | 0 | 9.3394 | 37.78
2022-11-14 | 44879 | 0 | 9.0665 | 37.78
2022-11-14 00:30 | 44879.0208 | 0 | 8.699 | 37.78
2022-11-14 01:00 | 44879.0417 | 0 | 8.6514 | 37.78
2022-11-14 01:30 | 44879.0625 | 0 | 8.4963 | 37.78
2022-11-14 02:00 | 44879.0833 | 0 | 8.5692 | 37.78
2022-11-14 02:30 | 44879.1042 | 0 | 8.5685 | 37.78
2022-11-14 03:00 | 44879.125 | 0 | 8.5499 | 37.78
2022-11-14 03:30 | 44879.1458 | 0 | 8.5126 | 37.78
2022-11-14 04:00 | 44879.1667 | 0 | 8.8017 | 37.78
2022-11-14 04:30 | 44879.1875 | 0 | 8.8967 | 37.78
2022-11-14 05:00 | 44879.2083 | 0 | 9.3258 | 37.78
2022-11-14 05:30 | 44879.2292 | 0 | 9.3198 | 37.78
2022-11-14 06:00 | 44879.25 | 0 | 9.739 | 37.78
2022-11-14 06:30 | 44879.2708 | 0 | 11.063 | 37.78
2022-11-14 07:00 | 44879.2917 | 0 | 12.3894 | 37.78
2022-11-14 07:30 | 44879.3125 | 0 | 24.2039 | 37.78
2022-11-14 08:00 | 44879.3333 | 0 | 25.3587 | 37.78
2022-11-14 08:30 | 44879.3542 | 0 | 21.9171 | 37.78
2022-11-14 09:00 | 44879.375 | 0 | 20.7301 | 37.78
2022-11-14 09:30 | 44879.3958 | 0 | 19.6626 | 37.78
2022-11-14 10:00 | 44879.4167 | 0 | 18.8804 | 37.78
2022-11-14 10:30 | 44879.4375 | 0 | 21.7024 | 37.78
2022-11-14 11:00 | 44879.4583 | 0 | 24.2858 | 37.78
2022-11-14 11:30 | 44879.4792 | 0 | 22.3492 | 37.78
2022-11-14 12:00 | 44879.5 | 0 | 26.0714 | 37.78
2022-11-14 12:30 | 44879.5208 | 0 | 19.411 | 37.78
2022-11-14 13:00 | 44879.5417 | 0 | 20.4109 | 37.78
2022-11-14 13:30 | 44879.5625 | 0 | 27.458 | 37.78
2022-11-14 14:00 | 44879.5833 | 0 | 27.127 | 37.78
2022-11-14 14:30 | 44879.6042 | 0 | 25.1963 | 37.78
2022-11-14 15:00 | 44879.625 | 0 | 25.4609 | 37.78
2022-11-14 15:30 | 44879.6458 | 0 | 26.1893 | 37.78
2022-11-14 16:00 | 44879.6667 | 0 | 27.0883 | 37.78
2022-11-14 16:30 | 44879.6875 | 0 | 29.0033 | 37.78
2022-11-14 17:00 | 44879.7083 | 0 | 29.9706 | 37.78
2022-11-14 17:30 | 44879.7292 | 0 | 30.4585 | 37.78
2022-11-14 18:00 | 44879.75 | 0 | 30.7333 | 37.78
2022-11-14 18:30 | 44879.7708 | 0 | 31.7749 | 37.78
2022-11-14 19:00 | 44879.7917 | 0 | 31.566 | 37.78
2022-11-14 19:30 | 44879.8125 | 0 | 30.9894 | 37.78
2022-11-14 20:00 | 44879.8333 | 0 | 30.3097 | 37.78
2022-11-14 20:30 | 44879.8542 | 0 | 28.547 | 37.78
2022-11-14 21:00 | 44879.875 | 0 | 27.8324 | 37.78
2022-11-14 21:30 | 44879.8958 | 0 | 26.666 | 37.78
2022-11-14 22:00 | 44879.9167 | 0 | 25.252 | 37.78
2022-11-14 22:30 | 44879.9375 | 0 | 23.5382 | 37.78
2022-11-14 23:00 | 44879.9583 | 0 | 22.3133 | 37.78
2022-11-14 23:30 | 44879.9792 | 0 | 21.2383 | 37.78
2022-11-15 | 44880 | 0 | 20.1413 | 37.78
2022-11-15 00:30 | 44880.0208 | 0 | 19.0674 | 37.78
2022-11-15 01:00 | 44880.0417 | 0 | 18.6838 | 37.78
2022-11-15 01:30 | 44880.0625 | 0 | 18.0882 | 37.78
2022-11-15 02:00 | 44880.0833 | 0 | 17.7476 | 37.78
2022-11-15 02:30 | 44880.1042 | 0 | 17.5148 | 37.78
2022-11-15 03:00 | 44880.125 | 0 | 17.2202 | 37.78
2022-11-15 03:30 | 44880.1458 | 0 | 17.2968 | 37.78
2022-11-15 04:00 | 44880.1667 | 0 | 17.6693 | 37.78
2022-11-15 04:30 | 44880.1875 | 0 | 18.1857 | 37.78
2022-11-15 05:00 | 44880.2083 | 0 | 18.5709 | 37.78
2022-11-15 05:30 | 44880.2292 | 0 | 19.1009 | 37.78
2022-11-15 06:00 | 44880.25 | 0 | 20.1885 | 37.78
2022-11-15 06:30 | 44880.2708 | 0 | 20.5187 | 37.78
2022-11-15 07:00 | 44880.2917 | 0 | 20.902 | 37.78
2022-11-15 07:30 | 44880.3125 | 0 | 20.0243 | 37.78
2022-11-15 08:00 | 44880.3333 | 0 | 20.078 | 37.78
2022-11-15 08:30 | 44880.3542 | 0 | 20.0782 | 37.78
2022-11-15 09:00 | 44880.375 | 0 | 20.1807 | 37.78
2022-11-15 09:30 | 44880.3958 | 0 | 20.2322 | 37.78
2022-11-15 10:00 | 44880.4167 | 0 | 19.9743 | 37.78
2022-11-15 10:30 | 44880.4375 | 0 | 20.6391 | 37.78
2022-11-15 11:00 | 44880.4583 | 0 | 22.2221 | 37.78
2022-11-15 11:30 | 44880.4792 | 0 | 22.335 | 37.78
2022-11-15 12:00 | 44880.5 | 0 | 22.2424 | 37.78
2022-11-15 12:30 | 44880.5208 | 0 | 22.902 | 37.78
2022-11-15 13:00 | 44880.5417 | 0 | 23.7888 | 37.78
2022-11-15 13:30 | 44880.5625 | 0 | 26.0702 | 37.78
2022-11-15 14:00 | 44880.5833 | 0 | 28.679 | 37.78
2022-11-15 14:30 | 44880.6042 | 0 | 29.9274 | 37.78
2022-11-15 15:00 | 44880.625 | 0 | 29.7628 | 37.78
2022-11-15 15:30 | 44880.6458 | 0 | 31.0377 | 37.78
2022-11-15 16:00 | 44880.6667 | 0 | 32.1823 | 37.78
2022-11-15 16:30 | 44880.6875 | 0 | 33.5049 | 37.78
2022-11-15 17:00 | 44880.7083 | 0 | 33.8292 | 37.78
2022-11-15 17:30 | 44880.7292 | 0 | 33.8426 | 37.78
2022-11-15 18:00 | 44880.75 | 0 | 33.7801 | 37.78
2022-11-15 18:30 | 44880.7708 | 0 | 33.7299 | 37.78
2022-11-15 19:00 | 44880.7917 | 0 | 17.7863 | 37.78
2022-11-15 19:30 | 44880.8125 | 0 | 17.0342 | 37.78
2022-11-15 20:00 | 44880.8333 | 0 | 16.6368 | 37.78
2022-11-15 20:30 | 44880.8542 | 0 | 15.7141 | 37.78
2022-11-15 21:00 | 44880.875 | 0 | 15.1424 | 37.78
2022-11-15 21:30 | 44880.8958 | 0 | 14.1404 | 37.78
2022-11-15 22:00 | 44880.9167 | 0 | 13.2021 | 37.78
2022-11-15 22:30 | 44880.9375 | 0 | 12.0998 | 37.78
2022-11-15 23:00 | 44880.9583 | 0 | 11.6628 | 37.78
2022-11-15 23:30 | 44880.9792 | 0 | 11.0451 | 37.78
2022-11-16 | 44881 | 0 | 10.5391 | 37.78
2022-11-16 00:30 | 44881.0208 | 0 | 9.929 | 37.78
2022-11-16 01:00 | 44881.0417 | 0 | 9.7677 | 37.78
2022-11-16 01:30 | 44881.0625 | 0 | 9.5065 | 37.78
2022-11-16 02:00 | 44881.0833 | 0 | 9.3833 | 37.78
2022-11-16 02:30 | 44881.1042 | 0 | 9.2776 | 37.78
2022-11-16 03:00 | 44881.125 | 0 | 9.1611 | 37.78
2022-11-16 03:30 | 44881.1458 | 0 | 9.0629 | 37.78
2022-11-16 04:00 | 44881.1667 | 0 | 9.227 | 37.78
2022-11-16 04:30 | 44881.1875 | 0 | 9.2907 | 37.78
2022-11-16 05:00 | 44881.2083 | 0 | 9.76 | 37.78
2022-11-16 05:30 | 44881.2292 | 0 | 9.9094 | 37.78
2022-11-16 06:00 | 44881.25 | 0 | 10.048 | 37.78
2022-11-16 06:30 | 44881.2708 | 0 | 10.6614 | 37.78
2022-11-16 07:00 | 44881.2917 | 0 | 5.6552 | 37.78
2022-11-16 07:30 | 44881.3125 | 0 | 0.022333 | 37.78
2022-11-16 08:00 | 44881.3333 | 0 | 0.022333 | 37.78
2022-11-16 08:30 | 44881.3542 | 0 | 0.022333 | 37.78
2022-11-16 09:00 | 44881.375 | 0 | 0.022333 | 37.78
2022-11-16 09:30 | 44881.3958 | 0 | 0.022333 | 37.78
2022-11-16 10:00 | 44881.4167 | 0 | 0.022333 | 37.78
2022-11-16 10:30 | 44881.4375 | 0 | 0.022333 | 37.78
2022-11-16 11:00 | 44881.4583 | 0 | 0.022333 | 37.78
2022-11-16 11:30 | 44881.4792 | 0 | 0.022333 | 37.78
2022-11-16 12:00 | 44881.5 | 0 | 0.022333 | 37.78
2022-11-16 12:30 | 44881.5208 | 0 | 0.022333 | 37.78
2022-11-16 13:00 | 44881.5417 | 0 | 0.022333 | 37.78
2022-11-16 13:30 | 44881.5625 | 0 | 0.022333 | 37.78
2022-11-16 14:00 | 44881.5833 | 0 | 0.022333 | 37.78
2022-11-16 14:30 | 44881.6042 | 0 | 0.022333 | 37.78
2022-11-16 15:00 | 44881.625 | 0 | 0.022333 | 37.78
2022-11-16 15:30 | 44881.6458 | 0 | 0.022333 | 37.78
2022-11-16 16:00 | 44881.6667 | 0 | 0.022333 | 37.78
2022-11-16 16:30 | 44881.6875 | 0 | 0.022333 | 37.78
2022-11-16 17:00 | 44881.7083 | 0 | 0.022333 | 37.78
2022-11-16 17:30 | 44881.7292 | 0 | 0.022333 | 37.78
2022-11-16 18:00 | 44881.75 | 0 | 0.022333 | 37.78
2022-11-16 18:30 | 44881.7708 | 0 | 0.022333 | 37.78
2022-11-16 19:00 | 44881.7917 | 0 | 0.022333 | 37.78
2022-11-16 19:30 | 44881.8125 | 0 | 0.022333 | 37.78
2022-11-16 20:00 | 44881.8333 | 0 | 0.022333 | 37.78
2022-11-16 20:30 | 44881.8542 | 0 | 0.022333 | 37.78
2022-11-16 21:00 | 44881.875 | 0 | 0.022333 | 37.78
2022-11-16 21:30 | 44881.8958 | 0 | 0.022333 | 37.78
2022-11-16 22:00 | 44881.9167 | 0 | 0.022333 | 37.78
2022-11-16 22:30 | 44881.9375 | 0 | 0.022333 | 37.78
2022-11-16 23:00 | 44881.9583 | 0 | 0.022333 | 37.78
2022-11-16 23:30 | 44881.9792 | 0 | 0.022333 | 37.78
2022-11-17 | 44882 | 0 | 0.022333 | 37.78
2022-11-17 00:30 | 44882.0208 | 0 | 0.022333 | 37.78
2022-11-17 01:00 | 44882.0417 | 0 | 0.022333 | 37.78
2022-11-17 01:30 | 44882.0625 | 0 | 0.022333 | 37.78
2022-11-17 02:00 | 44882.0833 | 0 | 0.022333 | 37.78
2022-11-17 02:30 | 44882.1042 | 0 | 0.022333 | 37.78
2022-11-17 03:00 | 44882.125 | 0 | 0.022333 | 37.78
2022-11-17 03:30 | 44882.1458 | 0 | 0.022333 | 37.78
2022-11-17 04:00 | 44882.1667 | 0 | 0.022333 | 37.78
2022-11-17 04:30 | 44882.1875 | 0 | 0.022333 | 37.78
2022-11-17 05:00 | 44882.2083 | 0 | 0.022333 | 37.78
2022-11-17 05:30 | 44882.2292 | 0 | 0.022333 | 37.78
2022-11-17 06:00 | 44882.25 | 0 | 0.022333 | 37.78
2022-11-17 06:30 | 44882.2708 | 0 | 0.022333 | 37.78
2022-11-17 07:00 | 44882.2917 | 0 | 0.022333 | 37.78
2022-11-17 07:30 | 44882.3125 | 0 | 0.022333 | 37.78
2022-11-17 08:00 | 44882.3333 | 0 | 0.022333 | 37.78
2022-11-17 08:30 | 44882.3542 | 0 | 0.022333 | 37.78
2022-11-17 09:00 | 44882.375 | 0 | 0.022333 | 37.78
2022-11-17 09:30 | 44882.3958 | 0 | 0.022333 | 37.78
2022-11-17 10:00 | 44882.4167 | 0 | 0.022333 | 37.78
2022-11-17 10:30 | 44882.4375 | 0 | 0.022333 | 37.78
2022-11-17 11:00 | 44882.4583 | 0 | 0.022333 | 37.78
2022-11-17 11:30 | 44882.4792 | 0 | 0.022333 | 37.78
2022-11-17 12:00 | 44882.5 | 0 | 0.022333 | 37.78
2022-11-17 12:30 | 44882.5208 | 0 | 0.022333 | 37.78
2022-11-17 13:00 | 44882.5417 | 0 | 0.022333 | 37.78
2022-11-17 13:30 | 44882.5625 | 0 | 0.022333 | 37.78
2022-11-17 14:00 | 44882.5833 | 0 | 0.022333 | 37.78
2022-11-17 14:30 | 44882.6042 | 0 | 0.022333 | 37.78
2022-11-17 15:00 | 44882.625 | 0 | 0.022333 | 37.78
2022-11-17 15:30 | 44882.6458 | 0 | 0.022333 | 37.78
2022-11-17 16:00 | 44882.6667 | 0 | 0.022333 | 37.78
2022-11-17 16:30 | 44882.6875 | 0 | 0.022333 | 37.78
2022-11-17 17:00 | 44882.7083 | 0 | 0.022333 | 37.78
2022-11-17 17:30 | 44882.7292 | 0 | 0.022333 | 37.78
2022-11-17 18:00 | 44882.75 | 0 | 0.022333 | 37.78
2022-11-17 18:30 | 44882.7708 | 0 | 0.022333 | 37.78
2022-11-17 19:00 | 44882.7917 | 0 | 0.022333 | 37.78
2022-11-17 19:30 | 44882.8125 | 0 | 0.022333 | 37.78
2022-11-17 20:00 | 44882.8333 | 0 | 0.022333 | 37.78
2022-11-17 20:30 | 44882.8542 | 0 | 0.022333 | 37.78
2022-11-17 21:00 | 44882.875 | 0 | 0.022333 | 37.78
2022-11-17 21:30 | 44882.8958 | 0 | 0.022333 | 37.78
2022-11-17 22:00 | 44882.9167 | 0 | 0.022333 | 37.78
2022-11-17 22:30 | 44882.9375 | 0 | 0.022333 | 37.78
2022-11-17 23:00 | 44882.9583 | 0 | 0.022333 | 37.78
2022-11-17 23:30 | 44882.9792 | 0 | 0.022333 | 37.78
2022-11-18 | 44883 | 0 | 0.022333 | 37.78
2022-11-18 00:30 | 44883.0208 | 0 | 0.022333 | 37.78
2022-11-18 01:00 | 44883.0417 | 0 | 0.022333 | 37.78
2022-11-18 01:30 | 44883.0625 | 0 | 0.022333 | 37.78
2022-11-18 02:00 | 44883.0833 | 0 | 0.022333 | 37.78
2022-11-18 02:30 | 44883.1042 | 0 | 0.022333 | 37.78
2022-11-18 03:00 | 44883.125 | 0 | 0.022333 | 37.78
2022-11-18 03:30 | 44883.1458 | 0 | 0.022333 | 37.78
2022-11-18 04:00 | 44883.1667 | 0 | 0.022333 | 37.78
2022-11-18 04:30 | 44883.1875 | 0 | 0.022333 | 37.78
2022-11-18 05:00 | 44883.2083 | 0 | 0.022333 | 37.78
2022-11-18 05:30 | 44883.2292 | 0 | 0.022333 | 37.78
2022-11-18 06:00 | 44883.25 | 0 | 0.022333 | 37.78
2022-11-18 06:30 | 44883.2708 | 0 | 0.022333 | 37.78
2022-11-18 07:00 | 44883.2917 | 0 | 0.022333 | 37.78
2022-11-18 07:30 | 44883.3125 | 0 | 0.022333 | 37.78
2022-11-18 08:00 | 44883.3333 | 0 | 0.022333 | 37.78
2022-11-18 08:30 | 44883.3542 | 0 | 0.022333 | 37.78
2022-11-18 09:00 | 44883.375 | 0 | 0.022333 | 37.78
2022-11-18 09:30 | 44883.3958 | 0 | 0.022333 | 37.78
2022-11-18 10:00 | 44883.4167 | 0 | 0.022333 | 37.78
2022-11-18 10:30 | 44883.4375 | 0 | 0.022333 | 37.78
2022-11-18 11:00 | 44883.4583 | 0 | 0.022333 | 37.78
2022-11-18 11:30 | 44883.4792 | 0 | 0.022333 | 37.78
2022-11-18 12:00 | 44883.5 | 0 | 0.022333 | 37.78
2022-11-18 12:30 | 44883.5208 | 0 | 0.022333 | 37.78
2022-11-18 13:00 | 44883.5417 | 0 | 0.022333 | 37.78
2022-11-18 13:30 | 44883.5625 | 0 | 0.022333 | 37.78
2022-11-18 14:00 | 44883.5833 | 0 | 0.022333 | 37.78
2022-11-18 14:30 | 44883.6042 | 0 | 0.022333 | 37.78
2022-11-18 15:00 | 44883.625 | 0 | 0.022333 | 37.78
2022-11-18 15:30 | 44883.6458 | 0 | 0.022333 | 37.78
2022-11-18 16:00 | 44883.6667 | 0 | 0.022333 | 37.78
2022-11-18 16:30 | 44883.6875 | 0 | 0.022333 | 37.78
2022-11-18 17:00 | 44883.7083 | 0 | 0.022333 | 37.78
2022-11-18 17:30 | 44883.7292 | 0 | 0.022333 | 37.78
2022-11-18 18:00 | 44883.75 | 0 | 0.022333 | 37.78
2022-11-18 18:30 | 44883.7708 | 0 | 0.022333 | 37.78
2022-11-18 19:00 | 44883.7917 | 0 | 0.022333 | 37.78
2022-11-18 19:30 | 44883.8125 | 0 | 0.022333 | 37.78
2022-11-18 20:00 | 44883.8333 | 0 | 0.022333 | 37.78
2022-11-18 20:30 | 44883.8542 | 0 | 0.022333 | 37.78
2022-11-18 21:00 | 44883.875 | 0 | 0.022333 | 37.78
2022-11-18 21:30 | 44883.8958 | 0 | 0.022333 | 37.78
2022-11-18 22:00 | 44883.9167 | 0 | 0.022333 | 37.78
2022-11-18 22:30 | 44883.9375 | 0 | 0.022333 | 37.78
2022-11-18 23:00 | 44883.9583 | 0 | 0.022333 | 37.78
2022-11-18 23:30 | 44883.9792 | 0 | 0.022333 | 37.78
2022-11-19 | 44884 | 0 | 0.022333 | 37.78
2022-11-19 00:30 | 44884.0208 | 0 | 0.022333 | 37.78
2022-11-19 01:00 | 44884.0417 | 0 | 0.022333 | 37.78
2022-11-19 01:30 | 44884.0625 | 0 | 0.022333 | 37.78
2022-11-19 02:00 | 44884.0833 | 0 | 0.022333 | 37.78
2022-11-19 02:30 | 44884.1042 | 0 | 0.022333 | 37.78
2022-11-19 03:00 | 44884.125 | 0 | 0.022333 | 37.78
2022-11-19 03:30 | 44884.1458 | 0 | 0.022333 | 37.78
2022-11-19 04:00 | 44884.1667 | 0 | 0.022333 | 37.78
2022-11-19 04:30 | 44884.1875 | 0 | 0.022333 | 37.78
2022-11-19 05:00 | 44884.2083 | 0 | 0.022333 | 37.78
2022-11-19 05:30 | 44884.2292 | 0 | 0.022333 | 37.78
2022-11-19 06:00 | 44884.25 | 0 | 0.022333 | 37.78
2022-11-19 06:30 | 44884.2708 | 0 | 0.022333 | 37.78
2022-11-19 07:00 | 44884.2917 | 0 | 0.022333 | 37.78
2022-11-19 07:30 | 44884.3125 | 0 | 0.022333 | 37.78
2022-11-19 08:00 | 44884.3333 | 0 | 0.022333 | 37.78
2022-11-19 08:30 | 44884.3542 | 0 | 0.022333 | 37.78
2022-11-19 09:00 | 44884.375 | 0 | 0.022333 | 37.78
2022-11-19 09:30 | 44884.3958 | 0 | 0.022333 | 37.78
2022-11-19 10:00 | 44884.4167 | 0 | 0.022333 | 37.78
2022-11-19 10:30 | 44884.4375 | 0 | 0.022333 | 37.78
2022-11-19 11:00 | 44884.4583 | 0 | 0.022333 | 37.78
2022-11-19 11:30 | 44884.4792 | 0 | 0.022333 | 37.78
2022-11-19 12:00 | 44884.5 | 0 | 5.5938 | 37.78
2022-11-19 12:30 | 44884.5208 | 0 | 6.1929 | 37.78
2022-11-19 13:00 | 44884.5417 | 0 | 6.5651 | 37.78
2022-11-19 13:30 | 44884.5625 | 0 | 6.6968 | 37.78
2022-11-19 14:00 | 44884.5833 | 0 | 7.4019 | 37.78
2022-11-19 14:30 | 44884.6042 | 0 | 8.0753 | 37.78
2022-11-19 15:00 | 44884.625 | 0 | 8.9077 | 37.78
2022-11-19 15:30 | 44884.6458 | 0 | 9.7769 | 37.78
2022-11-19 16:00 | 44884.6667 | 0 | 10.73 | 37.78
2022-11-19 16:30 | 44884.6875 | 0 | 11.3877 | 37.78
2022-11-19 17:00 | 44884.7083 | 0 | 12.055 | 37.78
2022-11-19 17:30 | 44884.7292 | 0 | 12.3211 | 37.78
2022-11-19 18:00 | 44884.75 | 0 | 12.5548 | 37.78
2022-11-19 18:30 | 44884.7708 | 0 | 12.9089 | 37.78
2022-11-19 19:00 | 44884.7917 | 0 | 12.9288 | 37.78
2022-11-19 19:30 | 44884.8125 | 0 | 12.665 | 37.78
2022-11-19 20:00 | 44884.8333 | 0 | 12.3977 | 37.78
2022-11-19 20:30 | 44884.8542 | 0 | 12.0954 | 37.78
2022-11-19 21:00 | 44884.875 | 0 | 11.7467 | 37.78
2022-11-19 21:30 | 44884.8958 | 0 | 11.4986 | 37.78
2022-11-19 22:00 | 44884.9167 | 0 | 10.9759 | 37.78
2022-11-19 22:30 | 44884.9375 | 0 | 10.3877 | 37.78
2022-11-19 23:00 | 44884.9583 | 0 | 9.9632 | 37.78
2022-11-19 23:30 | 44884.9792 | 0 | 9.4879 | 37.78
2022-11-20 | 44885 | 0 | 9.0971 | 37.78
2022-11-20 00:30 | 44885.0208 | 0 | 8.707 | 37.78
2022-11-20 01:00 | 44885.0417 | 0 | 8.4301 | 37.78
2022-11-20 01:30 | 44885.0625 | 0 | 8.3524 | 37.78
2022-11-20 02:00 | 44885.0833 | 0 | 8.2431 | 37.78
2022-11-20 02:30 | 44885.1042 | 0 | 8.1458 | 37.78
2022-11-20 03:00 | 44885.125 | 0 | 8.1106 | 37.78
2022-11-20 03:30 | 44885.1458 | 0 | 8.2589 | 37.78
2022-11-20 04:00 | 44885.1667 | 0 | 8.2413 | 37.78
2022-11-20 04:30 | 44885.1875 | 0 | 8.0844 | 37.78
2022-11-20 05:00 | 44885.2083 | 0 | 7.8662 | 37.78
2022-11-20 05:30 | 44885.2292 | 0 | 7.8209 | 37.78
2022-11-20 06:00 | 44885.25 | 0 | 7.9326 | 37.78
2022-11-20 06:30 | 44885.2708 | 0 | 7.676 | 37.78
2022-11-20 07:00 | 44885.2917 | 0 | 8.2826 | 37.78
2022-11-20 07:30 | 44885.3125 | 0 | 7.5381 | 37.78
2022-11-20 08:00 | 44885.3333 | 0 | 7.5567 | 37.78
2022-11-20 08:30 | 44885.3542 | 0 | 8.0232 | 37.78
2022-11-20 09:00 | 44885.375 | 0 | 10.8772 | 37.78
2022-11-20 09:30 | 44885.3958 | 0 | 11.0931 | 37.78
2022-11-20 10:00 | 44885.4167 | 0 | 12.4162 | 37.78
2022-11-20 10:30 | 44885.4375 | 0 | 9.3374 | 37.78
2022-11-20 11:00 | 44885.4583 | 0 | 9.3525 | 37.78
2022-11-20 11:30 | 44885.4792 | 0 | 11.587 | 37.78
2022-11-20 12:00 | 44885.5 | 0 | 12.5532 | 37.78
2022-11-20 12:30 | 44885.5208 | 0 | 12.4063 | 37.78
2022-11-20 13:00 | 44885.5417 | 0 | 10.9257 | 37.78
2022-11-20 13:30 | 44885.5625 | 0 | 13.5782 | 37.78
2022-11-20 14:00 | 44885.5833 | 0 | 13.2491 | 37.78
2022-11-20 14:30 | 44885.6042 | 0 | 13.6896 | 37.78
2022-11-20 15:00 | 44885.625 | 0 | 15.375 | 37.78
2022-11-20 15:30 | 44885.6458 | 0 | 16.1487 | 37.78
2022-11-20 16:00 | 44885.6667 | 0 | 17.5473 | 37.78
2022-11-20 16:30 | 44885.6875 | 0 | 17.5122 | 37.78
2022-11-20 17:00 | 44885.7083 | 0 | 15.5719 | 37.78
2022-11-20 17:30 | 44885.7292 | 0 | 15.7097 | 37.78
2022-11-20 18:00 | 44885.75 | 0 | 16.0188 | 37.78
2022-11-20 18:30 | 44885.7708 | 0 | 15.9604 | 37.78
2022-11-20 19:00 | 44885.7917 | 0 | 16.0695 | 37.78
2022-11-20 19:30 | 44885.8125 | 0 | 15.5349 | 37.78
2022-11-20 20:00 | 44885.8333 | 0 | 15.1939 | 37.78
2022-11-20 20:30 | 44885.8542 | 0 | 14.3622 | 37.78
2022-11-20 21:00 | 44885.875 | 0 | 13.7164 | 37.78
2022-11-20 21:30 | 44885.8958 | 0 | 12.9737 | 37.78
2022-11-20 22:00 | 44885.9167 | 0 | 12.1307 | 37.78
2022-11-20 22:30 | 44885.9375 | 0 | 11.1839 | 37.78
2022-11-20 23:00 | 44885.9583 | 0 | 10.5898 | 37.78
2022-11-20 23:30 | 44885.9792 | 0 | 10.0753 | 37.78
2022-11-21 | 44886 | 0 | 9.6475 | 37.78
2022-11-21 00:30 | 44886.0208 | 0 | 9.3633 | 37.78
2022-11-21 01:00 | 44886.0417 | 0 | 9.1734 | 37.78
2022-11-21 01:30 | 44886.0625 | 0 | 9.1439 | 37.78
2022-11-21 02:00 | 44886.0833 | 0 | 8.8804 | 37.78
2022-11-21 02:30 | 44886.1042 | 0 | 8.987 | 37.78
2022-11-21 03:00 | 44886.125 | 0 | 8.8117 | 37.78
2022-11-21 03:30 | 44886.1458 | 0 | 8.9411 | 37.78
2022-11-21 04:00 | 44886.1667 | 0 | 9.4154 | 37.78
2022-11-21 04:30 | 44886.1875 | 0 | 9.7192 | 37.78
2022-11-21 05:00 | 44886.2083 | 0 | 10.2504 | 37.78
2022-11-21 05:30 | 44886.2292 | 0 | 10.6295 | 37.78
2022-11-21 06:00 | 44886.25 | 0 | 11.5666 | 37.78
2022-11-21 06:30 | 44886.2708 | 0 | 11.8545 | 37.78
2022-11-21 07:00 | 44886.2917 | 0 | 11.9502 | 37.78
2022-11-21 07:30 | 44886.3125 | 0 | 12.2469 | 37.78
2022-11-21 08:00 | 44886.3333 | 0 | 12.5942 | 37.78
2022-11-21 08:30 | 44886.3542 | 0 | 11.956 | 37.78
2022-11-21 09:00 | 44886.375 | 0 | 10.0575 | 37.78
2022-11-21 09:30 | 44886.3958 | 0 | 11.2211 | 37.78
2022-11-21 10:00 | 44886.4167 | 0 | 9.7888 | 37.78
2022-11-21 10:30 | 44886.4375 | 0 | 10.6214 | 37.78
2022-11-21 11:00 | 44886.4583 | 0 | 11.3348 | 37.78
2022-11-21 11:30 | 44886.4792 | 0 | 10.9431 | 37.78
2022-11-21 12:00 | 44886.5 | 0 | 11.191 | 37.78
2022-11-21 12:30 | 44886.5208 | 0 | 11.7041 | 37.78
2022-11-21 13:00 | 44886.5417 | 0 | 12.6187 | 37.78
2022-11-21 13:30 | 44886.5625 | 0 | 13.4916 | 37.78
2022-11-21 14:00 | 44886.5833 | 0 | 14.4067 | 37.78
2022-11-21 14:30 | 44886.6042 | 0 | 15.0637 | 37.78
2022-11-21 15:00 | 44886.625 | 0 | 15.8723 | 37.78
2022-11-21 15:30 | 44886.6458 | 0 | 17.1497 | 37.78
2022-11-21 16:00 | 44886.6667 | 0 | 17.9062 | 37.78
2022-11-21 16:30 | 44886.6875 | 0 | 18.322 | 37.78
2022-11-21 17:00 | 44886.7083 | 0 | 18.7805 | 37.78
2022-11-21 17:30 | 44886.7292 | 0 | 18.7311 | 37.78
2022-11-21 18:00 | 44886.75 | 0 | 18.7383 | 37.78
2022-11-21 18:30 | 44886.7708 | 0 | 18.9527 | 37.78
2022-11-21 19:00 | 44886.7917 | 0 | 19.1748 | 37.78
2022-11-21 19:30 | 44886.8125 | 0 | 18.8985 | 37.78
2022-11-21 20:00 | 44886.8333 | 0 | 18.2954 | 37.78
2022-11-21 20:30 | 44886.8542 | 0 | 17.2779 | 37.78
2022-11-21 21:00 | 44886.875 | 0 | 16.3548 | 37.78
2022-11-21 21:30 | 44886.8958 | 0 | 15.4772 | 37.78
2022-11-21 22:00 | 44886.9167 | 0 | 13.9915 | 37.78
2022-11-21 22:30 | 44886.9375 | 0 | 12.7939 | 37.78
2022-11-21 23:00 | 44886.9583 | 0 | 11.8538 | 37.78
2022-11-21 23:30 | 44886.9792 | 0 | 11.1153 | 37.78
2022-11-22 | 44887 | 0 | 10.4198 | 37.78
2022-11-22 00:30 | 44887.0208 | 0 | 10.1387 | 37.78
2022-11-22 01:00 | 44887.0417 | 0 | 9.8536 | 37.78
2022-11-22 01:30 | 44887.0625 | 0 | 9.6537 | 37.78
2022-11-22 02:00 | 44887.0833 | 0 | 9.4128 | 37.78
2022-11-22 02:30 | 44887.1042 | 0 | 9.3936 | 37.78
2022-11-22 03:00 | 44887.125 | 0 | 9.2022 | 37.78
2022-11-22 03:30 | 44887.1458 | 0 | 9.1215 | 37.78
2022-11-22 04:00 | 44887.1667 | 0 | 9.4154 | 37.78
2022-11-22 04:30 | 44887.1875 | 0 | 9.6503 | 37.78
2022-11-22 05:00 | 44887.2083 | 0 | 9.9709 | 37.78
2022-11-22 05:30 | 44887.2292 | 0 | 10.3739 | 37.78
2022-11-22 06:00 | 44887.25 | 0 | 10.7947 | 37.78
2022-11-22 06:30 | 44887.2708 | 0 | 11.0761 | 37.78
2022-11-22 07:00 | 44887.2917 | 0 | 11.1787 | 37.78
2022-11-22 07:30 | 44887.3125 | 0 | 11.0175 | 37.78
2022-11-22 08:00 | 44887.3333 | 0 | 10.4428 | 37.78
2022-11-22 08:30 | 44887.3542 | 0 | 9.3351 | 37.78
2022-11-22 09:00 | 44887.375 | 0 | 8.7128 | 37.78
2022-11-22 09:30 | 44887.3958 | 0 | 8.4441 | 37.78
2022-11-22 10:00 | 44887.4167 | 0 | 8.5255 | 37.78
2022-11-22 10:30 | 44887.4375 | 0 | 8.7574 | 37.78
2022-11-22 11:00 | 44887.4583 | 0 | 9.0303 | 37.78
2022-11-22 11:30 | 44887.4792 | 0 | 9.2303 | 37.78
2022-11-22 12:00 | 44887.5 | 0 | 9.1098 | 37.78
2022-11-22 12:30 | 44887.5208 | 0 | 9.4036 | 37.78
2022-11-22 13:00 | 44887.5417 | 0 | 10.0456 | 37.78
2022-11-22 13:30 | 44887.5625 | 0 | 10.6085 | 37.78
2022-11-22 14:00 | 44887.5833 | 0 | 11.282 | 37.78
2022-11-22 14:30 | 44887.6042 | 0 | 12.4979 | 37.78
2022-11-22 15:00 | 44887.625 | 0 | 13.0479 | 37.78
2022-11-22 15:30 | 44887.6458 | 0 | 13.742 | 37.78
2022-11-22 16:00 | 44887.6667 | 0 | 14.3238 | 37.78
2022-11-22 16:30 | 44887.6875 | 0 | 14.9521 | 37.78
2022-11-22 17:00 | 44887.7083 | 0 | 14.856 | 37.78
2022-11-22 17:30 | 44887.7292 | 0 | 15.0157 | 37.78
2022-11-22 18:00 | 44887.75 | 0 | 14.9858 | 37.78
2022-11-22 18:30 | 44887.7708 | 0 | 15.101 | 37.78
2022-11-22 19:00 | 44887.7917 | 0 | 15.0059 | 37.78
2022-11-22 19:30 | 44887.8125 | 0 | 14.5925 | 37.78
2022-11-22 20:00 | 44887.8333 | 0 | 14.3604 | 37.78
2022-11-22 20:30 | 44887.8542 | 0 | 13.5806 | 37.78
2022-11-22 21:00 | 44887.875 | 0 | 13.1287 | 37.78
2022-11-22 21:30 | 44887.8958 | 0 | 12.6181 | 37.78
2022-11-22 22:00 | 44887.9167 | 0 | 12.1257 | 37.78
2022-11-22 22:30 | 44887.9375 | 0 | 11.3963 | 37.78
2022-11-22 23:00 | 44887.9583 | 0 | 10.89 | 37.78
2022-11-22 23:30 | 44887.9792 | 0 | 10.3384 | 37.78
2022-11-23 | 44888 | 0 | 9.8416 | 37.78
2022-11-23 00:30 | 44888.0208 | 0 | 9.3687 | 37.78
2022-11-23 01:00 | 44888.0417 | 0 | 9.0784 | 37.78
2022-11-23 01:30 | 44888.0625 | 0 | 9.001 | 37.78
2022-11-23 02:00 | 44888.0833 | 0 | 8.872 | 37.78
2022-11-23 02:30 | 44888.1042 | 0 | 8.9307 | 37.78
2022-11-23 03:00 | 44888.125 | 0 | 8.8809 | 37.78
2022-11-23 03:30 | 44888.1458 | 0 | 8.8884 | 37.78
2022-11-23 04:00 | 44888.1667 | 0 | 9.09 | 37.78
2022-11-23 04:30 | 44888.1875 | 0 | 9.1117 | 37.78
2022-11-23 05:00 | 44888.2083 | 0 | 9.4084 | 37.78
2022-11-23 05:30 | 44888.2292 | 0 | 9.7239 | 37.78
2022-11-23 06:00 | 44888.25 | 0 | 10.4034 | 37.78
2022-11-23 06:30 | 44888.2708 | 0 | 10.4972 | 37.78
2022-11-23 07:00 | 44888.2917 | 0 | 10.9529 | 37.78
2022-11-23 07:30 | 44888.3125 | 0 | 11.5659 | 37.78
2022-11-23 08:00 | 44888.3333 | 0 | 11.7812 | 37.78
2022-11-23 08:30 | 44888.3542 | 0 | 11.7191 | 37.78
2022-11-23 09:00 | 44888.375 | 0 | 11.9461 | 37.78
2022-11-23 09:30 | 44888.3958 | 0 | 10.6818 | 37.78
2022-11-23 10:00 | 44888.4167 | 0 | 8.6788 | 37.78
2022-11-23 10:30 | 44888.4375 | 0 | 9.1639 | 37.78
2022-11-23 11:00 | 44888.4583 | 0 | 9.2111 | 37.78
2022-11-23 11:30 | 44888.4792 | 0 | 11.5874 | 37.78
2022-11-23 12:00 | 44888.5 | 0 | 10.3466 | 37.78
2022-11-23 12:30 | 44888.5208 | 0 | 11.0591 | 37.78
2022-11-23 13:00 | 44888.5417 | 0 | 12.5476 | 37.78
2022-11-23 13:30 | 44888.5625 | 0 | 13.0265 | 37.78
2022-11-23 14:00 | 44888.5833 | 0 | 13.6035 | 37.78
2022-11-23 14:30 | 44888.6042 | 0 | 12.3713 | 37.78
2022-11-23 15:00 | 44888.625 | 0 | 12.8984 | 37.78
2022-11-23 15:30 | 44888.6458 | 0 | 13.2636 | 37.78
2022-11-23 16:00 | 44888.6667 | 0 | 13.2561 | 37.78
2022-11-23 16:30 | 44888.6875 | 0 | 13.4731 | 37.78
2022-11-23 17:00 | 44888.7083 | 0 | 13.5467 | 37.78
2022-11-23 17:30 | 44888.7292 | 0 | 13.6628 | 37.78
2022-11-23 18:00 | 44888.75 | 0 | 13.7477 | 37.78
2022-11-23 18:30 | 44888.7708 | 0 | 14.3884 | 37.78
2022-11-23 19:00 | 44888.7917 | 0 | 14.2598 | 37.78
2022-11-23 19:30 | 44888.8125 | 0 | 13.8143 | 37.78
2022-11-23 20:00 | 44888.8333 | 0 | 13.6789 | 37.78
2022-11-23 20:30 | 44888.8542 | 0 | 13.0622 | 37.78
2022-11-23 21:00 | 44888.875 | 0 | 12.7617 | 37.78
2022-11-23 21:30 | 44888.8958 | 0 | 12.0736 | 37.78
2022-11-23 22:00 | 44888.9167 | 0 | 11.3184 | 37.78
2022-11-23 22:30 | 44888.9375 | 0 | 10.506 | 37.78
2022-11-23 23:00 | 44888.9583 | 0 | 10.0625 | 37.78
2022-11-23 23:30 | 44888.9792 | 0 | 9.6052 | 37.78
2022-11-24 | 44889 | 0 | 9.3094 | 37.78
2022-11-24 00:30 | 44889.0208 | 0 | 8.7976 | 37.78
2022-11-24 01:00 | 44889.0417 | 0 | 8.6672 | 37.78
2022-11-24 01:30 | 44889.0625 | 0 | 8.557 | 37.78
2022-11-24 02:00 | 44889.0833 | 0 | 8.4093 | 37.78
2022-11-24 02:30 | 44889.1042 | 0 | 8.5326 | 37.78
2022-11-24 03:00 | 44889.125 | 0 | 8.2789 | 37.78
2022-11-24 03:30 | 44889.1458 | 0 | 8.4388 | 37.78
2022-11-24 04:00 | 44889.1667 | 0 | 8.677 | 37.78
2022-11-24 04:30 | 44889.1875 | 0 | 9.0289 | 37.78
2022-11-24 05:00 | 44889.2083 | 0 | 9.5389 | 37.78
2022-11-24 05:30 | 44889.2292 | 0 | 9.7037 | 37.78
2022-11-24 06:00 | 44889.25 | 0 | 10.1149 | 37.78
2022-11-24 06:30 | 44889.2708 | 0 | 10.3655 | 37.78
2022-11-24 07:00 | 44889.2917 | 0 | 11.4354 | 37.78
2022-11-24 07:30 | 44889.3125 | 0 | 11.0388 | 37.78
2022-11-24 08:00 | 44889.3333 | 0 | 10.938 | 37.78
2022-11-24 08:30 | 44889.3542 | 0 | 9.5762 | 37.78
2022-11-24 09:00 | 44889.375 | 0 | 10.8322 | 37.78
2022-11-24 09:30 | 44889.3958 | 0 | 11.8135 | 37.78
2022-11-24 10:00 | 44889.4167 | 0 | 11.312 | 37.78
2022-11-24 10:30 | 44889.4375 | 0 | 11.247 | 37.78
2022-11-24 11:00 | 44889.4583 | 0 | 10.846 | 37.78
2022-11-24 11:30 | 44889.4792 | 0 | 11.9893 | 37.78
2022-11-24 12:00 | 44889.5 | 0 | 10.828 | 37.78
2022-11-24 12:30 | 44889.5208 | 0 | 11.8644 | 37.78
2022-11-24 13:00 | 44889.5417 | 0 | 11.1939 | 37.78
2022-11-24 13:30 | 44889.5625 | 0 | 12.4184 | 37.78
2022-11-24 14:00 | 44889.5833 | 0 | 13.3371 | 37.78
2022-11-24 14:30 | 44889.6042 | 0 | 13.4651 | 37.78
2022-11-24 15:00 | 44889.625 | 0 | 13.3671 | 37.78
2022-11-24 15:30 | 44889.6458 | 0 | 13.9892 | 37.78
2022-11-24 16:00 | 44889.6667 | 0 | 14.1568 | 37.78
2022-11-24 16:30 | 44889.6875 | 0 | 14.4181 | 37.78
2022-11-24 17:00 | 44889.7083 | 0 | 14.409 | 37.78
2022-11-24 17:30 | 44889.7292 | 0 | 14.4751 | 37.78
2022-11-24 18:00 | 44889.75 | 0 | 14.6976 | 37.78
2022-11-24 18:30 | 44889.7708 | 0 | 14.8479 | 37.78
2022-11-24 19:00 | 44889.7917 | 0 | 14.8357 | 37.78
2022-11-24 19:30 | 44889.8125 | 0 | 14.6291 | 37.78
2022-11-24 20:00 | 44889.8333 | 0 | 14.4845 | 37.78
2022-11-24 20:30 | 44889.8542 | 0 | 13.9016 | 37.78
2022-11-24 21:00 | 44889.875 | 0 | 13.4638 | 37.78
2022-11-24 21:30 | 44889.8958 | 0 | 13.1197 | 37.78
2022-11-24 22:00 | 44889.9167 | 0 | 12.3883 | 37.78
2022-11-24 22:30 | 44889.9375 | 0 | 11.6116 | 37.78
2022-11-24 23:00 | 44889.9583 | 0 | 11.0103 | 37.78
2022-11-24 23:30 | 44889.9792 | 0 | 10.4063 | 37.78
2022-11-25 | 44890 | 0 | 9.7407 | 37.78
2022-11-25 00:30 | 44890.0208 | 0 | 9.506 | 37.78
2022-11-25 01:00 | 44890.0417 | 0 | 9.3333 | 37.78
2022-11-25 01:30 | 44890.0625 | 0 | 9.0793 | 37.78
2022-11-25 02:00 | 44890.0833 | 0 | 8.8095 | 37.78
2022-11-25 02:30 | 44890.1042 | 0 | 8.978 | 37.78
2022-11-25 03:00 | 44890.125 | 0 | 8.6661 | 37.78
2022-11-25 03:30 | 44890.1458 | 0 | 8.6951 | 37.78
2022-11-25 04:00 | 44890.1667 | 0 | 9.0507 | 37.78
2022-11-25 04:30 | 44890.1875 | 0 | 9.2943 | 37.78
2022-11-25 05:00 | 44890.2083 | 0 | 9.6895 | 37.78
2022-11-25 05:30 | 44890.2292 | 0 | 9.7561 | 37.78
2022-11-25 06:00 | 44890.25 | 0 | 10.1789 | 37.78
2022-11-25 06:30 | 44890.2708 | 0 | 10.3442 | 37.78
2022-11-25 07:00 | 44890.2917 | 0 | 10.7052 | 37.78
2022-11-25 07:30 | 44890.3125 | 0 | 10.4871 | 37.78
2022-11-25 08:00 | 44890.3333 | 0 | 10.3594 | 37.78
2022-11-25 08:30 | 44890.3542 | 0 | 10.1061 | 37.78
2022-11-25 09:00 | 44890.375 | 0 | 10.2471 | 37.78
2022-11-25 09:30 | 44890.3958 | 0 | 10.3223 | 37.78
2022-11-25 10:00 | 44890.4167 | 0 | 10.2292 | 37.78
2022-11-25 10:30 | 44890.4375 | 0 | 10.321 | 37.78
2022-11-25 11:00 | 44890.4583 | 0 | 10.5788 | 37.78
2022-11-25 11:30 | 44890.4792 | 0 | 10.9267 | 37.78
2022-11-25 12:00 | 44890.5 | 0 | 11.3574 | 37.78
2022-11-25 12:30 | 44890.5208 | 0 | 11.4621 | 37.78
2022-11-25 13:00 | 44890.5417 | 0 | 11.9428 | 37.78
2022-11-25 13:30 | 44890.5625 | 0 | 11.5568 | 37.78
2022-11-25 14:00 | 44890.5833 | 0 | 12.6614 | 37.78
2022-11-25 14:30 | 44890.6042 | 0 | 13.4269 | 37.78
2022-11-25 15:00 | 44890.625 | 0 | 14.0987 | 37.78
2022-11-25 15:30 | 44890.6458 | 0 | 15.0504 | 37.78
2022-11-25 16:00 | 44890.6667 | 0 | 15.1712 | 37.78
2022-11-25 16:30 | 44890.6875 | 0 | 15.8958 | 37.78
2022-11-25 17:00 | 44890.7083 | 0 | 15.4724 | 37.78
2022-11-25 17:30 | 44890.7292 | 0 | 15.2056 | 37.78
2022-11-25 18:00 | 44890.75 | 0 | 14.9514 | 37.78
2022-11-25 18:30 | 44890.7708 | 0 | 14.973 | 37.78
2022-11-25 19:00 | 44890.7917 | 0 | 14.8643 | 37.78
2022-11-25 19:30 | 44890.8125 | 0 | 14.6621 | 37.78
2022-11-25 20:00 | 44890.8333 | 0 | 14.463 | 37.78
2022-11-25 20:30 | 44890.8542 | 0 | 13.6956 | 37.78
2022-11-25 21:00 | 44890.875 | 0 | 13.6432 | 37.78
2022-11-25 21:30 | 44890.8958 | 0 | 13.2247 | 37.78
2022-11-25 22:00 | 44890.9167 | 0 | 12.6229 | 37.78
2022-11-25 22:30 | 44890.9375 | 0 | 11.9105 | 37.78
2022-11-25 23:00 | 44890.9583 | 0 | 11.3191 | 37.78
2022-11-25 23:30 | 44890.9792 | 0 | 10.8363 | 37.78
2022-11-26 | 44891 | 0 | 10.35 | 37.78
2022-11-26 00:30 | 44891.0208 | 0 | 9.7234 | 37.78
2022-11-26 01:00 | 44891.0417 | 0 | 9.383 | 37.78
2022-11-26 01:30 | 44891.0625 | 0 | 9.064 | 37.78
2022-11-26 02:00 | 44891.0833 | 0 | 8.939 | 37.78
2022-11-26 02:30 | 44891.1042 | 0 | 8.8262 | 37.78
2022-11-26 03:00 | 44891.125 | 0 | 8.7714 | 37.78
2022-11-26 03:30 | 44891.1458 | 0 | 8.8291 | 37.78
2022-11-26 04:00 | 44891.1667 | 0 | 8.8315 | 37.78
2022-11-26 04:30 | 44891.1875 | 0 | 8.7255 | 37.78
2022-11-26 05:00 | 44891.2083 | 0 | 8.702 | 37.78
2022-11-26 05:30 | 44891.2292 | 0 | 8.4543 | 37.78
2022-11-26 06:00 | 44891.25 | 0 | 8.0475 | 37.78
2022-11-26 06:30 | 44891.2708 | 0 | 7.5371 | 37.78
2022-11-26 07:00 | 44891.2917 | 0 | 7.4177 | 37.78
2022-11-26 07:30 | 44891.3125 | 0 | 7.2396 | 37.78
2022-11-26 08:00 | 44891.3333 | 0 | 7.323 | 37.78
2022-11-26 08:30 | 44891.3542 | 0 | 7.4119 | 37.78
2022-11-26 09:00 | 44891.375 | 0 | 7.396 | 37.78
2022-11-26 09:30 | 44891.3958 | 0 | 7.5225 | 37.78
2022-11-26 10:00 | 44891.4167 | 0 | 7.7861 | 37.78
2022-11-26 10:30 | 44891.4375 | 0 | 8.1073 | 37.78
2022-11-26 11:00 | 44891.4583 | 0 | 8.3938 | 37.78
2022-11-26 11:30 | 44891.4792 | 0 | 8.6395 | 37.78
2022-11-26 12:00 | 44891.5 | 0 | 8.8509 | 37.78
2022-11-26 12:30 | 44891.5208 | 0 | 9.366 | 37.78
2022-11-26 13:00 | 44891.5417 | 0 | 10.2268 | 37.78
2022-11-26 13:30 | 44891.5625 | 0 | 10.8715 | 37.78
2022-11-26 14:00 | 44891.5833 | 0 | 11.2104 | 37.78
2022-11-26 14:30 | 44891.6042 | 0 | 11.5308 | 37.78
2022-11-26 15:00 | 44891.625 | 0 | 12.0638 | 37.78
2022-11-26 15:30 | 44891.6458 | 0 | 12.8428 | 37.78
2022-11-26 16:00 | 44891.6667 | 0 | 13.5806 | 37.78
2022-11-26 16:30 | 44891.6875 | 0 | 14.2453 | 37.78
2022-11-26 17:00 | 44891.7083 | 0 | 14.3797 | 37.78
2022-11-26 17:30 | 44891.7292 | 0 | 14.5636 | 37.78
2022-11-26 18:00 | 44891.75 | 0 | 14.384 | 37.78
2022-11-26 18:30 | 44891.7708 | 0 | 14.3426 | 37.78
2022-11-26 19:00 | 44891.7917 | 0 | 14.3085 | 37.78
2022-11-26 19:30 | 44891.8125 | 0 | 13.8852 | 37.78
2022-11-26 20:00 | 44891.8333 | 0 | 13.7727 | 37.78
2022-11-26 20:30 | 44891.8542 | 0 | 13.1288 | 37.78
2022-11-26 21:00 | 44891.875 | 0 | 12.6909 | 37.78
2022-11-26 21:30 | 44891.8958 | 0 | 12.1743 | 37.78
2022-11-26 22:00 | 44891.9167 | 0 | 11.6867 | 37.78
2022-11-26 22:30 | 44891.9375 | 0 | 10.9515 | 37.78
2022-11-26 23:00 | 44891.9583 | 0 | 10.3151 | 37.78
2022-11-26 23:30 | 44891.9792 | 0 | 9.915 | 37.78
2022-11-27 | 44892 | 0 | 9.3181 | 37.78
2022-11-27 00:30 | 44892.0208 | 0 | 9.0507 | 37.78
2022-11-27 01:00 | 44892.0417 | 0 | 8.6764 | 37.78
2022-11-27 01:30 | 44892.0625 | 0 | 8.2491 | 37.78
2022-11-27 02:00 | 44892.0833 | 0 | 8.1874 | 37.78
2022-11-27 02:30 | 44892.1042 | 0 | 8.0755 | 37.78
2022-11-27 03:00 | 44892.125 | 0 | 7.9463 | 37.78
2022-11-27 03:30 | 44892.1458 | 0 | 7.9284 | 37.78
2022-11-27 04:00 | 44892.1667 | 0 | 7.8882 | 37.78
2022-11-27 04:30 | 44892.1875 | 0 | 7.6958 | 37.78
2022-11-27 05:00 | 44892.2083 | 0 | 7.6203 | 37.78
2022-11-27 05:30 | 44892.2292 | 0 | 7.7402 | 37.78
2022-11-27 06:00 | 44892.25 | 0 | 7.4561 | 37.78
2022-11-27 06:30 | 44892.2708 | 0 | 6.9487 | 37.78
2022-11-27 07:00 | 44892.2917 | 0 | 7.2532 | 37.78
2022-11-27 07:30 | 44892.3125 | 0 | 7.0679 | 37.78
2022-11-27 08:00 | 44892.3333 | 0 | 7.7277 | 37.78
2022-11-27 08:30 | 44892.3542 | 0 | 8.0236 | 37.78
2022-11-27 09:00 | 44892.375 | 0 | 7.693 | 37.78
2022-11-27 09:30 | 44892.3958 | 0 | 7.4368 | 37.78
2022-11-27 10:00 | 44892.4167 | 0 | 8.5926 | 37.78
2022-11-27 10:30 | 44892.4375 | 0 | 8.6803 | 37.78
2022-11-27 11:00 | 44892.4583 | 0 | 8.594 | 37.78
2022-11-27 11:30 | 44892.4792 | 0 | 8.3505 | 37.78
2022-11-27 12:00 | 44892.5 | 0 | 8.8689 | 37.78
2022-11-27 12:30 | 44892.5208 | 0 | 9.2081 | 37.78
2022-11-27 13:00 | 44892.5417 | 0 | 13.1159 | 37.78
2022-11-27 13:30 | 44892.5625 | 0 | 14.3492 | 37.78
2022-11-27 14:00 | 44892.5833 | 0 | 13.6675 | 37.78
2022-11-27 14:30 | 44892.6042 | 0 | 12.4228 | 37.78
2022-11-27 15:00 | 44892.625 | 0 | 13.5953 | 37.78
2022-11-27 15:30 | 44892.6458 | 0 | 13.3187 | 37.78
2022-11-27 16:00 | 44892.6667 | 0 | 12.6529 | 37.78
2022-11-27 16:30 | 44892.6875 | 0 | 11.1524 | 37.78
2022-11-27 17:00 | 44892.7083 | 0 | 12.1603 | 37.78
2022-11-27 17:30 | 44892.7292 | 0 | 12.7114 | 37.78
2022-11-27 18:00 | 44892.75 | 0 | 13.1076 | 37.78
2022-11-27 18:30 | 44892.7708 | 0 | 13.6664 | 37.78
2022-11-27 19:00 | 44892.7917 | 0 | 13.7048 | 37.78
2022-11-27 19:30 | 44892.8125 | 0 | 13.3237 | 37.78
2022-11-27 20:00 | 44892.8333 | 0 | 13.1711 | 37.78
2022-11-27 20:30 | 44892.8542 | 0 | 12.495 | 37.78
2022-11-27 21:00 | 44892.875 | 0 | 12.0476 | 37.78
2022-11-27 21:30 | 44892.8958 | 0 | 11.5168 | 37.78
2022-11-27 22:00 | 44892.9167 | 0 | 11.0922 | 37.78
2022-11-27 22:30 | 44892.9375 | 0 | 10.3269 | 37.78
2022-11-27 23:00 | 44892.9583 | 0 | 9.704 | 37.78
2022-11-27 23:30 | 44892.9792 | 0 | 9.5346 | 37.78
2022-11-28 | 44893 | 0 | 9.1617 | 37.78
2022-11-28 00:30 | 44893.0208 | 0 | 8.9747 | 37.78
2022-11-28 01:00 | 44893.0417 | 0 | 8.769 | 37.78
2022-11-28 01:30 | 44893.0625 | 0 | 8.7023 | 37.78
2022-11-28 02:00 | 44893.0833 | 0 | 8.6314 | 37.78
2022-11-28 02:30 | 44893.1042 | 0 | 8.7732 | 37.78
2022-11-28 03:00 | 44893.125 | 0 | 8.5005 | 37.78
2022-11-28 03:30 | 44893.1458 | 0 | 8.6826 | 37.78
2022-11-28 04:00 | 44893.1667 | 0 | 9.021 | 37.78
2022-11-28 04:30 | 44893.1875 | 0 | 9.347 | 37.78
2022-11-28 05:00 | 44893.2083 | 0 | 9.6156 | 37.78
2022-11-28 05:30 | 44893.2292 | 0 | 10.3603 | 37.78
2022-11-28 06:00 | 44893.25 | 0 | 11.1592 | 37.78
2022-11-28 06:30 | 44893.2708 | 0 | 12.3669 | 37.78
2022-11-28 07:00 | 44893.2917 | 0 | 12.9348 | 37.78
2022-11-28 07:30 | 44893.3125 | 0 | 12.867 | 37.78
2022-11-28 08:00 | 44893.3333 | 0 | 12.9046 | 37.78
2022-11-28 08:30 | 44893.3542 | 0 | 11.6823 | 37.78
2022-11-28 09:00 | 44893.375 | 0 | 11.6548 | 37.78
2022-11-28 09:30 | 44893.3958 | 0 | 11.3521 | 37.78
2022-11-28 10:00 | 44893.4167 | 0 | 12.8161 | 37.78
2022-11-28 10:30 | 44893.4375 | 0 | 13.2013 | 37.78
2022-11-28 11:00 | 44893.4583 | 0 | 13.3535 | 37.78
2022-11-28 11:30 | 44893.4792 | 0 | 13.7263 | 37.78
2022-11-28 12:00 | 44893.5 | 0 | 14.3574 | 37.78
2022-11-28 12:30 | 44893.5208 | 0 | 13.798 | 37.78
2022-11-28 13:00 | 44893.5417 | 0 | 14.6333 | 37.78
2022-11-28 13:30 | 44893.5625 | 0 | 14.0504 | 37.78
2022-11-28 14:00 | 44893.5833 | 0 | 13.5599 | 37.78
2022-11-28 14:30 | 44893.6042 | 0 | 14.6608 | 37.78
2022-11-28 15:00 | 44893.625 | 0 | 15.5337 | 37.78
2022-11-28 15:30 | 44893.6458 | 0 | 16.2812 | 37.78
2022-11-28 16:00 | 44893.6667 | 0 | 15.2598 | 37.78
2022-11-28 16:30 | 44893.6875 | 0 | 16.8972 | 37.78
2022-11-28 17:00 | 44893.7083 | 0 | 17.4049 | 37.78
2022-11-28 17:30 | 44893.7292 | 0 | 17.1655 | 37.78
2022-11-28 18:00 | 44893.75 | 0 | 16.1775 | 37.78
2022-11-28 18:30 | 44893.7708 | 0 | 15.9658 | 37.78
2022-11-28 19:00 | 44893.7917 | 0 | 15.7532 | 37.78
2022-11-28 19:30 | 44893.8125 | 0 | 15.6061 | 37.78
2022-11-28 20:00 | 44893.8333 | 0 | 15.3168 | 37.78
2022-11-28 20:30 | 44893.8542 | 0 | 14.6225 | 37.78
2022-11-28 21:00 | 44893.875 | 0 | 14.1905 | 37.78
2022-11-28 21:30 | 44893.8958 | 0 | 13.664 | 37.78
2022-11-28 22:00 | 44893.9167 | 0 | 12.8517 | 37.78
2022-11-28 22:30 | 44893.9375 | 0 | 12.294 | 37.78
2022-11-28 23:00 | 44893.9583 | 0 | 11.9131 | 37.78
2022-11-28 23:30 | 44893.9792 | 0 | 11.2747 | 37.78
2022-11-29 | 44894 | 0 | 10.6555 | 37.78
2022-11-29 00:30 | 44894.0208 | 0 | 10.0561 | 37.78
2022-11-29 01:00 | 44894.0417 | 0 | 9.9131 | 37.78
2022-11-29 01:30 | 44894.0625 | 0 | 9.5506 | 37.78
2022-11-29 02:00 | 44894.0833 | 0 | 9.5238 | 37.78
2022-11-29 02:30 | 44894.1042 | 0 | 9.6066 | 37.78
2022-11-29 03:00 | 44894.125 | 0 | 9.3958 | 37.78
2022-11-29 03:30 | 44894.1458 | 0 | 9.3336 | 37.78
2022-11-29 04:00 | 44894.1667 | 0 | 9.8855 | 37.78
2022-11-29 04:30 | 44894.1875 | 0 | 9.9237 | 37.78
2022-11-29 05:00 | 44894.2083 | 0 | 10.231 | 37.78
2022-11-29 05:30 | 44894.2292 | 0 | 10.2763 | 37.78
2022-11-29 06:00 | 44894.25 | 0 | 10.9262 | 37.78
2022-11-29 06:30 | 44894.2708 | 0 | 12.0577 | 37.78
2022-11-29 07:00 | 44894.2917 | 0 | 13.647 | 37.78
2022-11-29 07:30 | 44894.3125 | 0 | 13.0267 | 37.78
2022-11-29 08:00 | 44894.3333 | 0 | 14.2696 | 37.78
2022-11-29 08:30 | 44894.3542 | 0 | 14.4057 | 37.78
2022-11-29 09:00 | 44894.375 | 0 | 14.4197 | 37.78
2022-11-29 09:30 | 44894.3958 | 0 | 14.1151 | 37.78
2022-11-29 10:00 | 44894.4167 | 0 | 13.5604 | 37.78
2022-11-29 10:30 | 44894.4375 | 0 | 13.7253 | 37.78
2022-11-29 11:00 | 44894.4583 | 0 | 13.1303 | 37.78
2022-11-29 11:30 | 44894.4792 | 0 | 13.5156 | 37.78
2022-11-29 12:00 | 44894.5 | 0 | 11.4272 | 37.78
2022-11-29 12:30 | 44894.5208 | 0 | 11.5904 | 37.78
2022-11-29 13:00 | 44894.5417 | 0 | 14.0184 | 37.78
2022-11-29 13:30 | 44894.5625 | 0 | 13.7181 | 37.78
2022-11-29 14:00 | 44894.5833 | 0 | 13.3988 | 37.78
2022-11-29 14:30 | 44894.6042 | 0 | 14.0063 | 37.78
2022-11-29 15:00 | 44894.625 | 0 | 14.3175 | 37.78
2022-11-29 15:30 | 44894.6458 | 0 | 14.2905 | 37.78
2022-11-29 16:00 | 44894.6667 | 0 | 14.3673 | 37.78
2022-11-29 16:30 | 44894.6875 | 0 | 14.6217 | 37.78
2022-11-29 17:00 | 44894.7083 | 0 | 14.7303 | 37.78
2022-11-29 17:30 | 44894.7292 | 0 | 15.0635 | 37.78
2022-11-29 18:00 | 44894.75 | 0 | 15.321 | 37.78
2022-11-29 18:30 | 44894.7708 | 0 | 15.8496 | 37.78
2022-11-29 19:00 | 44894.7917 | 0 | 15.9161 | 37.78
2022-11-29 19:30 | 44894.8125 | 0 | 15.657 | 37.78
2022-11-29 20:00 | 44894.8333 | 0 | 15.4298 | 37.78
2022-11-29 20:30 | 44894.8542 | 0 | 14.6571 | 37.78
2022-11-29 21:00 | 44894.875 | 0 | 14.2116 | 37.78
2022-11-29 21:30 | 44894.8958 | 0 | 13.691 | 37.78
2022-11-29 22:00 | 44894.9167 | 0 | 12.8312 | 37.78
2022-11-29 22:30 | 44894.9375 | 0 | 12.0957 | 37.78
2022-11-29 23:00 | 44894.9583 | 0 | 11.3901 | 37.78
2022-11-29 23:30 | 44894.9792 | 0 | 11.0264 | 37.78
2022-11-30 | 44895 | 0 | 10.3811 | 37.78
2022-11-30 00:30 | 44895.0208 | 0 | 9.79 | 37.78
2022-11-30 01:00 | 44895.0417 | 0 | 9.553 | 37.78
2022-11-30 01:30 | 44895.0625 | 0 | 9.3613 | 37.78
2022-11-30 02:00 | 44895.0833 | 0 | 9.3315 | 37.78
2022-11-30 02:30 | 44895.1042 | 0 | 9.3416 | 37.78
2022-11-30 03:00 | 44895.125 | 0 | 9.2219 | 37.78
2022-11-30 03:30 | 44895.1458 | 0 | 9.221 | 37.78
2022-11-30 04:00 | 44895.1667 | 0 | 9.4944 | 37.78
2022-11-30 04:30 | 44895.1875 | 0 | 9.7726 | 37.78
2022-11-30 05:00 | 44895.2083 | 0 | 9.9973 | 37.78
2022-11-30 05:30 | 44895.2292 | 0 | 10.444 | 37.78
2022-11-30 06:00 | 44895.25 | 0 | 11.2426 | 37.78
2022-11-30 06:30 | 44895.2708 | 0 | 12.518 | 37.78
2022-11-30 07:00 | 44895.2917 | 0 | 13.2908 | 37.78
2022-11-30 07:30 | 44895.3125 | 0 | 13.3126 | 37.78
2022-11-30 08:00 | 44895.3333 | 0 | 13.3451 | 37.78
2022-11-30 08:30 | 44895.3542 | 0 | 13.3841 | 37.78
2022-11-30 09:00 | 44895.375 | 0 | 13.0171 | 37.78
2022-11-30 09:30 | 44895.3958 | 0 | 13.5744 | 37.78
2022-11-30 10:00 | 44895.4167 | 0 | 12.9648 | 37.78
2022-11-30 10:30 | 44895.4375 | 0 | 13.7259 | 37.78
2022-11-30 11:00 | 44895.4583 | 0 | 13.2218 | 37.78
2022-11-30 11:30 | 44895.4792 | 0 | 12.0927 | 37.78
2022-11-30 12:00 | 44895.5 | 0 | 13.0274 | 37.78
2022-11-30 12:30 | 44895.5208 | 0 | 12.7841 | 37.78
2022-11-30 13:00 | 44895.5417 | 0 | 12.888 | 37.78
2022-11-30 13:30 | 44895.5625 | 0 | 12.6587 | 37.78
2022-11-30 14:00 | 44895.5833 | 0 | 12.9416 | 37.78
2022-11-30 14:30 | 44895.6042 | 0 | 12.7407 | 37.78
2022-11-30 15:00 | 44895.625 | 0 | 12.6495 | 37.78
2022-11-30 15:30 | 44895.6458 | 0 | 12.8204 | 37.78
2022-11-30 16:00 | 44895.6667 | 0 | 12.6712 | 37.78
2022-11-30 16:30 | 44895.6875 | 0 | 12.8606 | 37.78
2022-11-30 17:00 | 44895.7083 | 0 | 12.9327 | 37.78
2022-11-30 17:30 | 44895.7292 | 0 | 13.1673 | 37.78
2022-11-30 18:00 | 44895.75 | 0 | 13.1778 | 37.78
2022-11-30 18:30 | 44895.7708 | 0 | 13.3442 | 37.78
2022-11-30 19:00 | 44895.7917 | 0 | 13.3724 | 37.78
2022-11-30 19:30 | 44895.8125 | 0 | 12.8874 | 37.78
2022-11-30 20:00 | 44895.8333 | 0 | 12.8294 | 37.78
2022-11-30 20:30 | 44895.8542 | 0 | 12.2385 | 37.78
2022-11-30 21:00 | 44895.875 | 0 | 11.7774 | 37.78
2022-11-30 21:30 | 44895.8958 | 0 | 11.4004 | 37.78
2022-11-30 22:00 | 44895.9167 | 0 | 10.7576 | 37.78
2022-11-30 22:30 | 44895.9375 | 0 | 10.1403 | 37.78
2022-11-30 23:00 | 44895.9583 | 0 | 9.8061 | 37.78
2022-11-30 23:30 | 44895.9792 | 0 | 9.3988 | 37.78
2022-12-01 | 44896 | 0 | 8.853 | 37.78
2022-12-01 00:30 | 44896.0208 | 0 | 8.6475 | 37.78
2022-12-01 01:00 | 44896.0417 | 0 | 8.4686 | 37.78
2022-12-01 01:30 | 44896.0625 | 0 | 8.3074 | 37.78
2022-12-01 02:00 | 44896.0833 | 0 | 8.222 | 37.78
2022-12-01 02:30 | 44896.1042 | 0 | 8.2369 | 37.78
2022-12-01 03:00 | 44896.125 | 0 | 8.0582 | 37.78
2022-12-01 03:30 | 44896.1458 | 0 | 8.2104 | 37.78
2022-12-01 04:00 | 44896.1667 | 0 | 8.5614 | 37.78
2022-12-01 04:30 | 44896.1875 | 0 | 8.822 | 37.78
2022-12-01 05:00 | 44896.2083 | 0 | 9.4782 | 37.78
2022-12-01 05:30 | 44896.2292 | 0 | 9.9914 | 37.78
2022-12-01 06:00 | 44896.25 | 0 | 10.555 | 37.78
2022-12-01 06:30 | 44896.2708 | 0 | 11.4413 | 37.78
2022-12-01 07:00 | 44896.2917 | 0 | 12.2493 | 37.78
2022-12-01 07:30 | 44896.3125 | 0 | 12.2838 | 37.78
2022-12-01 08:00 | 44896.3333 | 0 | 12.3949 | 37.78
2022-12-01 08:30 | 44896.3542 | 0 | 12.7561 | 37.78
2022-12-01 09:00 | 44896.375 | 0 | 12.7278 | 37.78
2022-12-01 09:30 | 44896.3958 | 0 | 12.7405 | 37.78
2022-12-01 10:00 | 44896.4167 | 0 | 12.9851 | 37.78
2022-12-01 10:30 | 44896.4375 | 0 | 12.4995 | 37.78
2022-12-01 11:00 | 44896.4583 | 0 | 11.5635 | 37.78
2022-12-01 11:30 | 44896.4792 | 0 | 11.6594 | 37.78
2022-12-01 12:00 | 44896.5 | 0 | 11.2022 | 37.78
2022-12-01 12:30 | 44896.5208 | 0 | 11.2654 | 37.78
2022-12-01 13:00 | 44896.5417 | 0 | 12.2909 | 37.78
2022-12-01 13:30 | 44896.5625 | 0 | 12.3074 | 37.78
2022-12-01 14:00 | 44896.5833 | 0 | 12.2383 | 37.78
2022-12-01 14:30 | 44896.6042 | 0 | 11.9099 | 37.78
2022-12-01 15:00 | 44896.625 | 0 | 11.4581 | 37.78
2022-12-01 15:30 | 44896.6458 | 0 | 11.7885 | 37.78
2022-12-01 16:00 | 44896.6667 | 0 | 11.8465 | 37.78
2022-12-01 16:30 | 44896.6875 | 0 | 12.5292 | 37.78
2022-12-01 17:00 | 44896.7083 | 0 | 12.9213 | 37.78
2022-12-01 17:30 | 44896.7292 | 0 | 13.0083 | 37.78
2022-12-01 18:00 | 44896.75 | 0 | 13.1801 | 37.78
2022-12-01 18:30 | 44896.7708 | 0 | 13.3228 | 37.78
2022-12-01 19:00 | 44896.7917 | 0 | 13.2144 | 37.78
2022-12-01 19:30 | 44896.8125 | 0 | 12.7936 | 37.78
2022-12-01 20:00 | 44896.8333 | 0 | 12.5735 | 37.78
2022-12-01 20:30 | 44896.8542 | 0 | 12.0568 | 37.78
2022-12-01 21:00 | 44896.875 | 0 | 11.7054 | 37.78
2022-12-01 21:30 | 44896.8958 | 0 | 11.2393 | 37.78
2022-12-01 22:00 | 44896.9167 | 0 | 10.7375 | 37.78
2022-12-01 22:30 | 44896.9375 | 0 | 9.9813 | 37.78
2022-12-01 23:00 | 44896.9583 | 0 | 9.6439 | 37.78
2022-12-01 23:30 | 44896.9792 | 0 | 9.2174 | 37.78
2022-12-02 | 44897 | 0 | 8.6736 | 37.78
2022-12-02 00:30 | 44897.0208 | 0 | 8.346 | 37.78
2022-12-02 01:00 | 44897.0417 | 0 | 8.099 | 37.78
2022-12-02 01:30 | 44897.0625 | 0 | 7.9492 | 37.78
2022-12-02 02:00 | 44897.0833 | 0 | 7.9799 | 37.78
2022-12-02 02:30 | 44897.1042 | 0 | 8.004 | 37.78
2022-12-02 03:00 | 44897.125 | 0 | 7.9391 | 37.78
2022-12-02 03:30 | 44897.1458 | 0 | 8.0091 | 37.78
2022-12-02 04:00 | 44897.1667 | 0 | 8.3733 | 37.78
2022-12-02 04:30 | 44897.1875 | 0 | 8.5961 | 37.78
2022-12-02 05:00 | 44897.2083 | 0 | 8.9098 | 37.78
2022-12-02 05:30 | 44897.2292 | 0 | 8.9804 | 37.78
2022-12-02 06:00 | 44897.25 | 0 | 9.4126 | 37.78
2022-12-02 06:30 | 44897.2708 | 0 | 9.2655 | 37.78
2022-12-02 07:00 | 44897.2917 | 0 | 9.8254 | 37.78
2022-12-02 07:30 | 44897.3125 | 0 | 9.9511 | 37.78
2022-12-02 08:00 | 44897.3333 | 0 | 9.7383 | 37.78
2022-12-02 08:30 | 44897.3542 | 0 | 10.5199 | 37.78
2022-12-02 09:00 | 44897.375 | 0 | 10.9156 | 37.78
2022-12-02 09:30 | 44897.3958 | 0 | 9.624 | 37.78
2022-12-02 10:00 | 44897.4167 | 0 | 7.6191 | 37.78
2022-12-02 10:30 | 44897.4375 | 0 | 8.6372 | 37.78
2022-12-02 11:00 | 44897.4583 | 0 | 9.5646 | 37.78
2022-12-02 11:30 | 44897.4792 | 0 | 12.1585 | 37.78
2022-12-02 12:00 | 44897.5 | 0 | 9.6561 | 37.78
2022-12-02 12:30 | 44897.5208 | 0 | 10.2303 | 37.78
2022-12-02 13:00 | 44897.5417 | 0 | 10.2791 | 37.78
2022-12-02 13:30 | 44897.5625 | 0 | 9.7064 | 37.78
2022-12-02 14:00 | 44897.5833 | 0 | 10.1485 | 37.78
2022-12-02 14:30 | 44897.6042 | 0 | 9.8576 | 37.78
2022-12-02 15:00 | 44897.625 | 0 | 9.5264 | 37.78
2022-12-02 15:30 | 44897.6458 | 0 | 10.7532 | 37.78
2022-12-02 16:00 | 44897.6667 | 0 | 9.6937 | 37.78
2022-12-02 16:30 | 44897.6875 | 0 | 11.2457 | 37.78
2022-12-02 17:00 | 44897.7083 | 0 | 11.7577 | 37.78
2022-12-02 17:30 | 44897.7292 | 0 | 11.861 | 37.78
2022-12-02 18:00 | 44897.75 | 0 | 11.9777 | 37.78
2022-12-02 18:30 | 44897.7708 | 0 | 12.3864 | 37.78
2022-12-02 19:00 | 44897.7917 | 0 | 12.3952 | 37.78
2022-12-02 19:30 | 44897.8125 | 0 | 12.1146 | 37.78
2022-12-02 20:00 | 44897.8333 | 0 | 12.1371 | 37.78
2022-12-02 20:30 | 44897.8542 | 0 | 11.846 | 37.78
2022-12-02 21:00 | 44897.875 | 0 | 11.3096 | 37.78
2022-12-02 21:30 | 44897.8958 | 0 | 10.8983 | 37.78
2022-12-02 22:00 | 44897.9167 | 0 | 10.6829 | 37.78
2022-12-02 22:30 | 44897.9375 | 0 | 10.1917 | 37.78
2022-12-02 23:00 | 44897.9583 | 0 | 9.6969 | 37.78
2022-12-02 23:30 | 44897.9792 | 0 | 9.2006 | 37.78
2022-12-03 | 44898 | 0 | 8.7624 | 37.78
2022-12-03 00:30 | 44898.0208 | 0 | 8.3592 | 37.78
2022-12-03 01:00 | 44898.0417 | 0 | 8.1699 | 37.78
2022-12-03 01:30 | 44898.0625 | 0 | 8.032 | 37.78
2022-12-03 02:00 | 44898.0833 | 0 | 7.9876 | 37.78
2022-12-03 02:30 | 44898.1042 | 0 | 7.9492 | 37.78
2022-12-03 03:00 | 44898.125 | 0 | 7.7971 | 37.78
2022-12-03 03:30 | 44898.1458 | 0 | 7.8822 | 37.78
2022-12-03 04:00 | 44898.1667 | 0 | 8.0121 | 37.78
2022-12-03 04:30 | 44898.1875 | 0 | 7.9427 | 37.78
2022-12-03 05:00 | 44898.2083 | 0 | 7.9133 | 37.78
2022-12-03 05:30 | 44898.2292 | 0 | 7.7578 | 37.78
2022-12-03 06:00 | 44898.25 | 0 | 7.2751 | 37.78
2022-12-03 06:30 | 44898.2708 | 0 | 7.1789 | 37.78
2022-12-03 07:00 | 44898.2917 | 0 | 6.3848 | 37.78
2022-12-03 07:30 | 44898.3125 | 0 | 6.0926 | 37.78
2022-12-03 08:00 | 44898.3333 | 0 | 6.9174 | 37.78
2022-12-03 08:30 | 44898.3542 | 0 | 7.7242 | 37.78
2022-12-03 09:00 | 44898.375 | 0 | 7.7637 | 37.78
2022-12-03 09:30 | 44898.3958 | 0 | 7.4112 | 37.78
2022-12-03 10:00 | 44898.4167 | 0 | 8.1615 | 37.78
2022-12-03 10:30 | 44898.4375 | 0 | 6.5616 | 37.78
2022-12-03 11:00 | 44898.4583 | 0 | 6.2963 | 37.78
2022-12-03 11:30 | 44898.4792 | 0 | 8.1242 | 37.78
2022-12-03 12:00 | 44898.5 | 0 | 5.585 | 37.78
2022-12-03 12:30 | 44898.5208 | 0 | 5.6194 | 37.78
2022-12-03 13:00 | 44898.5417 | 0 | 7.354 | 37.78
2022-12-03 13:30 | 44898.5625 | 0 | 8.7703 | 37.78
2022-12-03 14:00 | 44898.5833 | 0 | 8.3969 | 37.78
2022-12-03 14:30 | 44898.6042 | 0 | 7.6467 | 37.78
2022-12-03 15:00 | 44898.625 | 0 | 7.3756 | 37.78
2022-12-03 15:30 | 44898.6458 | 0 | 7.145 | 37.78
2022-12-03 16:00 | 44898.6667 | 0 | 8.2089 | 37.78
2022-12-03 16:30 | 44898.6875 | 0 | 9.0687 | 37.78
2022-12-03 17:00 | 44898.7083 | 0 | 9.7556 | 37.78
2022-12-03 17:30 | 44898.7292 | 0 | 10.2187 | 37.78
2022-12-03 18:00 | 44898.75 | 0 | 10.6854 | 37.78
2022-12-03 18:30 | 44898.7708 | 0 | 10.8141 | 37.78
2022-12-03 19:00 | 44898.7917 | 0 | 10.9975 | 37.78
2022-12-03 19:30 | 44898.8125 | 0 | 10.7956 | 37.78
2022-12-03 20:00 | 44898.8333 | 0 | 10.5261 | 37.78
2022-12-03 20:30 | 44898.8542 | 0 | 10.2257 | 37.78
2022-12-03 21:00 | 44898.875 | 0 | 9.9928 | 37.78
2022-12-03 21:30 | 44898.8958 | 0 | 9.6382 | 37.78
2022-12-03 22:00 | 44898.9167 | 0 | 9.4712 | 37.78
2022-12-03 22:30 | 44898.9375 | 0 | 8.9831 | 37.78
2022-12-03 23:00 | 44898.9583 | 0 | 8.5282 | 37.78
2022-12-03 23:30 | 44898.9792 | 0 | 8.1923 | 37.78
2022-12-04 | 44899 | 0 | 7.7596 | 37.78
2022-12-04 00:30 | 44899.0208 | 0 | 7.5133 | 37.78
2022-12-04 01:00 | 44899.0417 | 0 | 7.4925 | 37.78
2022-12-04 01:30 | 44899.0625 | 0 | 7.1573 | 37.78
2022-12-04 02:00 | 44899.0833 | 0 | 7.1402 | 37.78
2022-12-04 02:30 | 44899.1042 | 0 | 7.159 | 37.78
2022-12-04 03:00 | 44899.125 | 0 | 7.0717 | 37.78
2022-12-04 03:30 | 44899.1458 | 0 | 7.0857 | 37.78
2022-12-04 04:00 | 44899.1667 | 0 | 7.0163 | 37.78
2022-12-04 04:30 | 44899.1875 | 0 | 6.9913 | 37.78
2022-12-04 05:00 | 44899.2083 | 0 | 6.9726 | 37.78
2022-12-04 05:30 | 44899.2292 | 0 | 6.9592 | 37.78
2022-12-04 06:00 | 44899.25 | 0 | 6.668 | 37.78
2022-12-04 06:30 | 44899.2708 | 0 | 5.791 | 37.78
2022-12-04 07:00 | 44899.2917 | 0 | 5.9707 | 37.78
2022-12-04 07:30 | 44899.3125 | 0 | 4.5221 | 37.78
2022-12-04 08:00 | 44899.3333 | 0 | 4.7933 | 37.78
2022-12-04 08:30 | 44899.3542 | 0 | 5.2208 | 37.78
2022-12-04 09:00 | 44899.375 | 0 | 6.0893 | 37.78
2022-12-04 09:30 | 44899.3958 | 0 | 6.6107 | 37.78
2022-12-04 10:00 | 44899.4167 | 0 | 5.7702 | 37.78
2022-12-04 10:30 | 44899.4375 | 0 | 6.1792 | 37.78
2022-12-04 11:00 | 44899.4583 | 0 | 6.073 | 37.78
2022-12-04 11:30 | 44899.4792 | 0 | 7.4598 | 37.78
2022-12-04 12:00 | 44899.5 | 0 | 8.3478 | 37.78
2022-12-04 12:30 | 44899.5208 | 0 | 8.8973 | 37.78
2022-12-04 13:00 | 44899.5417 | 0 | 7.7785 | 37.78
2022-12-04 13:30 | 44899.5625 | 0 | 7.6267 | 37.78
2022-12-04 14:00 | 44899.5833 | 0 | 7.7059 | 37.78
2022-12-04 14:30 | 44899.6042 | 0 | 8.5203 | 37.78
2022-12-04 15:00 | 44899.625 | 0 | 8.4457 | 37.78
2022-12-04 15:30 | 44899.6458 | 0 | 8.6463 | 37.78
2022-12-04 16:00 | 44899.6667 | 0 | 9.4014 | 37.78
2022-12-04 16:30 | 44899.6875 | 0 | 9.1704 | 37.78
2022-12-04 17:00 | 44899.7083 | 0 | 9.9433 | 37.78
2022-12-04 17:30 | 44899.7292 | 0 | 10.585 | 37.78
2022-12-04 18:00 | 44899.75 | 0 | 10.8096 | 37.78
2022-12-04 18:30 | 44899.7708 | 0 | 11.3352 | 37.78
2022-12-04 19:00 | 44899.7917 | 0 | 11.3186 | 37.78
2022-12-04 19:30 | 44899.8125 | 0 | 11.0174 | 37.78
2022-12-04 20:00 | 44899.8333 | 0 | 10.9328 | 37.78
2022-12-04 20:30 | 44899.8542 | 0 | 10.4296 | 37.78
2022-12-04 21:00 | 44899.875 | 0 | 10.0885 | 37.78
2022-12-04 21:30 | 44899.8958 | 0 | 9.7198 | 37.78
2022-12-04 22:00 | 44899.9167 | 0 | 9.228 | 37.78
2022-12-04 22:30 | 44899.9375 | 0 | 8.761 | 37.78
2022-12-04 23:00 | 44899.9583 | 0 | 8.3902 | 37.78
2022-12-04 23:30 | 44899.9792 | 0 | 7.9966 | 37.78
2022-12-05 | 44900 | 0 | 7.7837 | 37.78
2022-12-05 00:30 | 44900.0208 | 0 | 7.6289 | 37.78
2022-12-05 01:00 | 44900.0417 | 0 | 7.4674 | 37.78
2022-12-05 01:30 | 44900.0625 | 0 | 7.3933 | 37.78
2022-12-05 02:00 | 44900.0833 | 0 | 7.4591 | 37.78
2022-12-05 02:30 | 44900.1042 | 0 | 7.5484 | 37.78
2022-12-05 03:00 | 44900.125 | 0 | 7.4564 | 37.78
2022-12-05 03:30 | 44900.1458 | 0 | 7.5865 | 37.78
2022-12-05 04:00 | 44900.1667 | 0 | 7.9775 | 37.78
2022-12-05 04:30 | 44900.1875 | 0 | 8.2014 | 37.78
2022-12-05 05:00 | 44900.2083 | 0 | 8.6279 | 37.78
2022-12-05 05:30 | 44900.2292 | 0 | 8.7175 | 37.78
2022-12-05 06:00 | 44900.25 | 0 | 8.9348 | 37.78
2022-12-05 06:30 | 44900.2708 | 0 | 9.1093 | 37.78
2022-12-05 07:00 | 44900.2917 | 0 | 9.2028 | 37.78
2022-12-05 07:30 | 44900.3125 | 0 | 3.028 | 37.78
2022-12-05 08:00 | 44900.3333 | 0 | 0.022333 | 37.78
2022-12-05 08:30 | 44900.3542 | 0 | 0.022333 | 37.78
2022-12-05 09:00 | 44900.375 | 0 | 0.022333 | 37.78
2022-12-05 09:30 | 44900.3958 | 0 | 0.022333 | 37.78
2022-12-05 10:00 | 44900.4167 | 0 | 0.022333 | 37.78
2022-12-05 10:30 | 44900.4375 | 0 | 0.022333 | 37.78
2022-12-05 11:00 | 44900.4583 | 0 | 0.022333 | 37.78
2022-12-05 11:30 | 44900.4792 | 0 | 0.022333 | 37.78
2022-12-05 12:00 | 44900.5 | 0 | 0.022333 | 37.78
2022-12-05 12:30 | 44900.5208 | 0 | 0.022333 | 37.78
2022-12-05 13:00 | 44900.5417 | 0 | 0.022333 | 37.78
2022-12-05 13:30 | 44900.5625 | 0 | 0.022333 | 37.78
2022-12-05 14:00 | 44900.5833 | 0 | 0.022333 | 37.78
2022-12-05 14:30 | 44900.6042 | 0 | 0.022333 | 37.78
2022-12-05 15:00 | 44900.625 | 0 | 0.022333 | 37.78
2022-12-05 15:30 | 44900.6458 | 0 | 0.022333 | 37.78
2022-12-05 16:00 | 44900.6667 | 0 | 0.022333 | 37.78
2022-12-05 16:30 | 44900.6875 | 0 | 0.022333 | 37.78
2022-12-05 17:00 | 44900.7083 | 0 | 0.022333 | 37.78
2022-12-05 17:30 | 44900.7292 | 0 | 0.022333 | 37.78
2022-12-05 18:00 | 44900.75 | 0 | 0.022333 | 37.78
2022-12-05 18:30 | 44900.7708 | 0 | 0.022333 | 37.78
2022-12-05 19:00 | 44900.7917 | 0 | 0.022333 | 37.78
2022-12-05 19:30 | 44900.8125 | 0 | 0.022333 | 37.78
2022-12-05 20:00 | 44900.8333 | 0 | 0.022333 | 37.78
2022-12-05 20:30 | 44900.8542 | 0 | 0.022333 | 37.78
2022-12-05 21:00 | 44900.875 | 0 | 0.022333 | 37.78
2022-12-05 21:30 | 44900.8958 | 0 | 0.022333 | 37.78
2022-12-05 22:00 | 44900.9167 | 0 | 0.022333 | 37.78
2022-12-05 22:30 | 44900.9375 | 0 | 0.022333 | 37.78
2022-12-05 23:00 | 44900.9583 | 0 | 0.022333 | 37.78
2022-12-05 23:30 | 44900.9792 | 0 | 0.022333 | 37.78
2022-12-06 | 44901 | 0 | 0.022333 | 37.78
2022-12-06 00:30 | 44901.0208 | 0 | 0.022333 | 37.78
2022-12-06 01:00 | 44901.0417 | 0 | 0.022333 | 37.78
2022-12-06 01:30 | 44901.0625 | 0 | 0.022333 | 37.78
2022-12-06 02:00 | 44901.0833 | 0 | 0.022333 | 37.78
2022-12-06 02:30 | 44901.1042 | 0 | 0.022333 | 37.78
2022-12-06 03:00 | 44901.125 | 0 | 0.022333 | 37.78
2022-12-06 03:30 | 44901.1458 | 0 | 0.022333 | 37.78
2022-12-06 04:00 | 44901.1667 | 0 | 0.022333 | 37.78
2022-12-06 04:30 | 44901.1875 | 0 | 0.022333 | 37.78
2022-12-06 05:00 | 44901.2083 | 0 | 0.022333 | 37.78
2022-12-06 05:30 | 44901.2292 | 0 | 0.022333 | 37.78
2022-12-06 06:00 | 44901.25 | 0 | 0.022333 | 37.78
2022-12-06 06:30 | 44901.2708 | 0 | 0.022333 | 37.78
2022-12-06 07:00 | 44901.2917 | 0 | 0.022333 | 37.78
2022-12-06 07:30 | 44901.3125 | 0 | 0.022333 | 37.78
2022-12-06 08:00 | 44901.3333 | 0 | 0.022333 | 37.78
2022-12-06 08:30 | 44901.3542 | 0 | 0.022333 | 37.78
2022-12-06 09:00 | 44901.375 | 0 | 0.022333 | 37.78
2022-12-06 09:30 | 44901.3958 | 0 | 0.022333 | 37.78
2022-12-06 10:00 | 44901.4167 | 0 | 0.022333 | 37.78
2022-12-06 10:30 | 44901.4375 | 0 | 0.022333 | 37.78
2022-12-06 11:00 | 44901.4583 | 0 | 0.022333 | 37.78
2022-12-06 11:30 | 44901.4792 | 0 | 0.022333 | 37.78
2022-12-06 12:00 | 44901.5 | 0 | 0.022333 | 37.78
2022-12-06 12:30 | 44901.5208 | 0 | 0.022333 | 37.78
2022-12-06 13:00 | 44901.5417 | 0 | 11.3691 | 37.78
2022-12-06 13:30 | 44901.5625 | 0 | 15.6275 | 37.78
2022-12-06 14:00 | 44901.5833 | 0 | 16.688 | 37.78
2022-12-06 14:30 | 44901.6042 | 0 | 16.8647 | 37.78
2022-12-06 15:00 | 44901.625 | 0 | 17.3616 | 37.78
2022-12-06 15:30 | 44901.6458 | 0 | 19.0856 | 37.78
2022-12-06 16:00 | 44901.6667 | 0 | 18.7789 | 37.78
2022-12-06 16:30 | 44901.6875 | 0 | 19.8009 | 37.78
2022-12-06 17:00 | 44901.7083 | 0 | 19.3966 | 37.78
2022-12-06 17:30 | 44901.7292 | 0 | 19.5336 | 37.78
2022-12-06 18:00 | 44901.75 | 0 | 19.3806 | 37.78
2022-12-06 18:30 | 44901.7708 | 0 | 19.2288 | 37.78
2022-12-06 19:00 | 44901.7917 | 0 | 18.8556 | 37.78
2022-12-06 19:30 | 44901.8125 | 0 | 18.7943 | 37.78
2022-12-06 20:00 | 44901.8333 | 0 | 18.2691 | 37.78
2022-12-06 20:30 | 44901.8542 | 0 | 17.3109 | 37.78
2022-12-06 21:00 | 44901.875 | 0 | 16.5134 | 37.78
2022-12-06 21:30 | 44901.8958 | 0 | 15.5473 | 37.78
2022-12-06 22:00 | 44901.9167 | 0 | 14.4723 | 37.78
2022-12-06 22:30 | 44901.9375 | 0 | 13.4394 | 37.78
2022-12-06 23:00 | 44901.9583 | 0 | 12.6973 | 37.78
2022-12-06 23:30 | 44901.9792 | 0 | 12.0041 | 37.78
2022-12-07 | 44902 | 0 | 11.2516 | 37.78
2022-12-07 00:30 | 44902.0208 | 0 | 10.7399 | 37.78
2022-12-07 01:00 | 44902.0417 | 0 | 10.5137 | 37.78
2022-12-07 01:30 | 44902.0625 | 0 | 10.0628 | 37.78
2022-12-07 02:00 | 44902.0833 | 0 | 9.9577 | 37.78
2022-12-07 02:30 | 44902.1042 | 0 | 9.7389 | 37.78
2022-12-07 03:00 | 44902.125 | 0 | 9.603 | 37.78
2022-12-07 03:30 | 44902.1458 | 0 | 9.4661 | 37.78
2022-12-07 04:00 | 44902.1667 | 0 | 9.6808 | 37.78
2022-12-07 04:30 | 44902.1875 | 0 | 9.7406 | 37.78
2022-12-07 05:00 | 44902.2083 | 0 | 10.108 | 37.78
2022-12-07 05:30 | 44902.2292 | 0 | 10.2796 | 37.78
2022-12-07 06:00 | 44902.25 | 0 | 10.5653 | 37.78
2022-12-07 06:30 | 44902.2708 | 0 | 10.7615 | 37.78
2022-12-07 07:00 | 44902.2917 | 0 | 11.1827 | 37.78
2022-12-07 07:30 | 44902.3125 | 0 | 11.0743 | 37.78
2022-12-07 08:00 | 44902.3333 | 0 | 11.2869 | 37.78
2022-12-07 08:30 | 44902.3542 | 0 | 11.3757 | 37.78
2022-12-07 09:00 | 44902.375 | 0 | 11.5026 | 37.78
2022-12-07 09:30 | 44902.3958 | 0 | 11.342 | 37.78
2022-12-07 10:00 | 44902.4167 | 0 | 11.8016 | 37.78
2022-12-07 10:30 | 44902.4375 | 0 | 11.9422 | 37.78
2022-12-07 11:00 | 44902.4583 | 0 | 12.2091 | 37.78
2022-12-07 11:30 | 44902.4792 | 0 | 12.4002 | 37.78
2022-12-07 12:00 | 44902.5 | 0 | 12.8139 | 37.78
2022-12-07 12:30 | 44902.5208 | 0 | 13.5256 | 37.78
2022-12-07 13:00 | 44902.5417 | 0 | 13.3026 | 37.78
2022-12-07 13:30 | 44902.5625 | 0 | 13.7186 | 37.78
2022-12-07 14:00 | 44902.5833 | 0 | 14.385 | 37.78
2022-12-07 14:30 | 44902.6042 | 0 | 14.881 | 37.78
2022-12-07 15:00 | 44902.625 | 0 | 15.5996 | 37.78
2022-12-07 15:30 | 44902.6458 | 0 | 16.4347 | 37.78
2022-12-07 16:00 | 44902.6667 | 0 | 17.0729 | 37.78
2022-12-07 16:30 | 44902.6875 | 0 | 17.4789 | 37.78
2022-12-07 17:00 | 44902.7083 | 0 | 17.7485 | 37.78
2022-12-07 17:30 | 44902.7292 | 0 | 17.8645 | 37.78
2022-12-07 18:00 | 44902.75 | 0 | 17.7126 | 37.78
2022-12-07 18:30 | 44902.7708 | 0 | 17.6267 | 37.78
2022-12-07 19:00 | 44902.7917 | 0 | 17.7015 | 37.78
2022-12-07 19:30 | 44902.8125 | 0 | 17.0988 | 37.78
2022-12-07 20:00 | 44902.8333 | 0 | 16.8542 | 37.78
2022-12-07 20:30 | 44902.8542 | 0 | 16.101 | 37.78
2022-12-07 21:00 | 44902.875 | 0 | 15.5281 | 37.78
2022-12-07 21:30 | 44902.8958 | 0 | 14.9593 | 37.78
2022-12-07 22:00 | 44902.9167 | 0 | 14.1965 | 37.78
2022-12-07 22:30 | 44902.9375 | 0 | 13.3209 | 37.78
2022-12-07 23:00 | 44902.9583 | 0 | 12.7813 | 37.78
2022-12-07 23:30 | 44902.9792 | 0 | 12.2296 | 37.78
2022-12-08 | 44903 | 0 | 11.3748 | 37.78
2022-12-08 00:30 | 44903.0208 | 0 | 10.8629 | 37.78
2022-12-08 01:00 | 44903.0417 | 0 | 10.5688 | 37.78
2022-12-08 01:30 | 44903.0625 | 0 | 10.3996 | 37.78
2022-12-08 02:00 | 44903.0833 | 0 | 10.2948 | 37.78
2022-12-08 02:30 | 44903.1042 | 0 | 10.1724 | 37.78
2022-12-08 03:00 | 44903.125 | 0 | 10.0157 | 37.78
2022-12-08 03:30 | 44903.1458 | 0 | 9.9279 | 37.78
2022-12-08 04:00 | 44903.1667 | 0 | 9.9544 | 37.78
2022-12-08 04:30 | 44903.1875 | 0 | 10.2429 | 37.78
2022-12-08 05:00 | 44903.2083 | 0 | 11.1594 | 37.78
2022-12-08 05:30 | 44903.2292 | 0 | 11.6467 | 37.78
2022-12-08 06:00 | 44903.25 | 0 | 11.9215 | 37.78
2022-12-08 06:30 | 44903.2708 | 0 | 11.0234 | 37.78
2022-12-08 07:00 | 44903.2917 | 0 | 11.9383 | 37.78
2022-12-08 07:30 | 44903.3125 | 0 | 11.1348 | 37.78
2022-12-08 08:00 | 44903.3333 | 0 | 11.7221 | 37.78
2022-12-08 08:30 | 44903.3542 | 0 | 11.6869 | 37.78
2022-12-08 09:00 | 44903.375 | 0 | 13.1902 | 37.78
2022-12-08 09:30 | 44903.3958 | 0 | 13.0479 | 37.78
2022-12-08 10:00 | 44903.4167 | 0 | 13.9542 | 37.78
2022-12-08 10:30 | 44903.4375 | 0 | 12.9483 | 37.78
2022-12-08 11:00 | 44903.4583 | 0 | 12.6176 | 37.78
2022-12-08 11:30 | 44903.4792 | 0 | 12.1638 | 37.78
2022-12-08 12:00 | 44903.5 | 0 | 12.1878 | 37.78
2022-12-08 12:30 | 44903.5208 | 0 | 12.5638 | 37.78
2022-12-08 13:00 | 44903.5417 | 0 | 13.5168 | 37.78
2022-12-08 13:30 | 44903.5625 | 0 | 13.8645 | 37.78
2022-12-08 14:00 | 44903.5833 | 0 | 14.6827 | 37.78
2022-12-08 14:30 | 44903.6042 | 0 | 15.042 | 37.78
2022-12-08 15:00 | 44903.625 | 0 | 15.955 | 37.78
2022-12-08 15:30 | 44903.6458 | 0 | 16.967 | 37.78
2022-12-08 16:00 | 44903.6667 | 0 | 17.6277 | 37.78
2022-12-08 16:30 | 44903.6875 | 0 | 18.4457 | 37.78
2022-12-08 17:00 | 44903.7083 | 0 | 18.7692 | 37.78
2022-12-08 17:30 | 44903.7292 | 0 | 19.0503 | 37.78
2022-12-08 18:00 | 44903.75 | 0 | 19.2496 | 37.78
2022-12-08 18:30 | 44903.7708 | 0 | 19.251 | 37.78
2022-12-08 19:00 | 44903.7917 | 0 | 19.1336 | 37.78
2022-12-08 19:30 | 44903.8125 | 0 | 18.3376 | 37.78
2022-12-08 20:00 | 44903.8333 | 0 | 17.2106 | 37.78
2022-12-08 20:30 | 44903.8542 | 0 | 16.3485 | 37.78
2022-12-08 21:00 | 44903.875 | 0 | 15.6759 | 37.78
2022-12-08 21:30 | 44903.8958 | 0 | 15.2359 | 37.78
2022-12-08 22:00 | 44903.9167 | 0 | 14.1782 | 37.78
2022-12-08 22:30 | 44903.9375 | 0 | 13.0982 | 37.78
2022-12-08 23:00 | 44903.9583 | 0 | 12.3061 | 37.78
2022-12-08 23:30 | 44903.9792 | 0 | 11.7675 | 37.78
2022-12-09 | 44904 | 0 | 11.409 | 37.78
2022-12-09 00:30 | 44904.0208 | 0 | 10.7243 | 37.78
2022-12-09 01:00 | 44904.0417 | 0 | 10.4166 | 37.78
2022-12-09 01:30 | 44904.0625 | 0 | 10.2278 | 37.78
2022-12-09 02:00 | 44904.0833 | 0 | 10.0036 | 37.78
2022-12-09 02:30 | 44904.1042 | 0 | 9.8547 | 37.78
2022-12-09 03:00 | 44904.125 | 0 | 9.7552 | 37.78
2022-12-09 03:30 | 44904.1458 | 0 | 9.8716 | 37.78
2022-12-09 04:00 | 44904.1667 | 0 | 10.0184 | 37.78
2022-12-09 04:30 | 44904.1875 | 0 | 10.1031 | 37.78
2022-12-09 05:00 | 44904.2083 | 0 | 10.2994 | 37.78
2022-12-09 05:30 | 44904.2292 | 0 | 10.519 | 37.78
2022-12-09 06:00 | 44904.25 | 0 | 10.8674 | 37.78
2022-12-09 06:30 | 44904.2708 | 0 | 11.0203 | 37.78
2022-12-09 07:00 | 44904.2917 | 0 | 11.9411 | 37.78
2022-12-09 07:30 | 44904.3125 | 0 | 13.1223 | 37.78
2022-12-09 08:00 | 44904.3333 | 0 | 12.2047 | 37.78
2022-12-09 08:30 | 44904.3542 | 0 | 11.9861 | 37.78
2022-12-09 09:00 | 44904.375 | 0 | 11.2135 | 37.78
2022-12-09 09:30 | 44904.3958 | 0 | 10.6915 | 37.78
2022-12-09 10:00 | 44904.4167 | 0 | 11.7661 | 37.78
2022-12-09 10:30 | 44904.4375 | 0 | 11.4854 | 37.78
2022-12-09 11:00 | 44904.4583 | 0 | 11.0735 | 37.78
2022-12-09 11:30 | 44904.4792 | 0 | 11.4091 | 37.78
2022-12-09 12:00 | 44904.5 | 0 | 10.3566 | 37.78
2022-12-09 12:30 | 44904.5208 | 0 | 11.1981 | 37.78
2022-12-09 13:00 | 44904.5417 | 0 | 12.4441 | 37.78
2022-12-09 13:30 | 44904.5625 | 0 | 10.435 | 37.78
2022-12-09 14:00 | 44904.5833 | 0 | 11.9753 | 37.78
2022-12-09 14:30 | 44904.6042 | 0 | 11.7897 | 37.78
2022-12-09 15:00 | 44904.625 | 0 | 10.771 | 37.78
2022-12-09 15:30 | 44904.6458 | 0 | 12.2511 | 37.78
2022-12-09 16:00 | 44904.6667 | 0 | 13.1943 | 37.78
2022-12-09 16:30 | 44904.6875 | 0 | 12.3412 | 37.78
2022-12-09 17:00 | 44904.7083 | 0 | 12.8148 | 37.78
2022-12-09 17:30 | 44904.7292 | 0 | 12.8743 | 37.78
2022-12-09 18:00 | 44904.75 | 0 | 13.0384 | 37.78
2022-12-09 18:30 | 44904.7708 | 0 | 13.3301 | 37.78
2022-12-09 19:00 | 44904.7917 | 0 | 13.2885 | 37.78
2022-12-09 19:30 | 44904.8125 | 0 | 13.0414 | 37.78
2022-12-09 20:00 | 44904.8333 | 0 | 13.1387 | 37.78
2022-12-09 20:30 | 44904.8542 | 0 | 12.6498 | 37.78
2022-12-09 21:00 | 44904.875 | 0 | 12.3333 | 37.78
2022-12-09 21:30 | 44904.8958 | 0 | 11.91 | 37.78
2022-12-09 22:00 | 44904.9167 | 0 | 11.5812 | 37.78
2022-12-09 22:30 | 44904.9375 | 0 | 11.038 | 37.78
2022-12-09 23:00 | 44904.9583 | 0 | 10.555 | 37.78
2022-12-09 23:30 | 44904.9792 | 0 | 10.1235 | 37.78
2022-12-10 | 44905 | 0 | 9.6746 | 37.78
2022-12-10 00:30 | 44905.0208 | 0 | 9.1688 | 37.78
2022-12-10 01:00 | 44905.0417 | 0 | 9.0378 | 37.78
2022-12-10 01:30 | 44905.0625 | 0 | 8.7931 | 37.78
2022-12-10 02:00 | 44905.0833 | 0 | 8.7231 | 37.78
2022-12-10 02:30 | 44905.1042 | 0 | 8.7275 | 37.78
2022-12-10 03:00 | 44905.125 | 0 | 8.5057 | 37.78
2022-12-10 03:30 | 44905.1458 | 0 | 8.5588 | 37.78
2022-12-10 04:00 | 44905.1667 | 0 | 8.7598 | 37.78
2022-12-10 04:30 | 44905.1875 | 0 | 8.9664 | 37.78
2022-12-10 05:00 | 44905.2083 | 0 | 8.9503 | 37.78
2022-12-10 05:30 | 44905.2292 | 0 | 9.056 | 37.78
2022-12-10 06:00 | 44905.25 | 0 | 8.7935 | 37.78
2022-12-10 06:30 | 44905.2708 | 0 | 8.6549 | 37.78
2022-12-10 07:00 | 44905.2917 | 0 | 8.7821 | 37.78
2022-12-10 07:30 | 44905.3125 | 0 | 9.5336 | 37.78
2022-12-10 08:00 | 44905.3333 | 0 | 9.7019 | 37.78
2022-12-10 08:30 | 44905.3542 | 0 | 9.8868 | 37.78
2022-12-10 09:00 | 44905.375 | 0 | 9.6467 | 37.78
2022-12-10 09:30 | 44905.3958 | 0 | 9.5489 | 37.78
2022-12-10 10:00 | 44905.4167 | 0 | 8.5359 | 37.78
2022-12-10 10:30 | 44905.4375 | 0 | 7.4286 | 37.78
2022-12-10 11:00 | 44905.4583 | 0 | 7.3874 | 37.78
2022-12-10 11:30 | 44905.4792 | 0 | 7.5565 | 37.78
2022-12-10 12:00 | 44905.5 | 0 | 9.2805 | 37.78
2022-12-10 12:30 | 44905.5208 | 0 | 9.8207 | 37.78
2022-12-10 13:00 | 44905.5417 | 0 | 8.0332 | 37.78
2022-12-10 13:30 | 44905.5625 | 0 | 6.5679 | 37.78
2022-12-10 14:00 | 44905.5833 | 0 | 6.9991 | 37.78
2022-12-10 14:30 | 44905.6042 | 0 | 7.186 | 37.78
2022-12-10 15:00 | 44905.625 | 0 | 8.0759 | 37.78
2022-12-10 15:30 | 44905.6458 | 0 | 8.9226 | 37.78
2022-12-10 16:00 | 44905.6667 | 0 | 9.5302 | 37.78
2022-12-10 16:30 | 44905.6875 | 0 | 10.4383 | 37.78
2022-12-10 17:00 | 44905.7083 | 0 | 10.9936 | 37.78
2022-12-10 17:30 | 44905.7292 | 0 | 11.3919 | 37.78
2022-12-10 18:00 | 44905.75 | 0 | 11.7118 | 37.78
2022-12-10 18:30 | 44905.7708 | 0 | 11.7548 | 37.78
2022-12-10 19:00 | 44905.7917 | 0 | 11.9081 | 37.78
2022-12-10 19:30 | 44905.8125 | 0 | 11.6538 | 37.78
2022-12-10 20:00 | 44905.8333 | 0 | 11.4837 | 37.78
2022-12-10 20:30 | 44905.8542 | 0 | 11.1202 | 37.78
2022-12-10 21:00 | 44905.875 | 0 | 10.7694 | 37.78
2022-12-10 21:30 | 44905.8958 | 0 | 10.4757 | 37.78
2022-12-10 22:00 | 44905.9167 | 0 | 10.2041 | 37.78
2022-12-10 22:30 | 44905.9375 | 0 | 9.4997 | 37.78
2022-12-10 23:00 | 44905.9583 | 0 | 9.199 | 37.78
2022-12-10 23:30 | 44905.9792 | 0 | 8.858 | 37.78
2022-12-11 | 44906 | 0 | 8.3919 | 37.78
2022-12-11 00:30 | 44906.0208 | 0 | 8.0737 | 37.78
2022-12-11 01:00 | 44906.0417 | 0 | 7.8605 | 37.78
2022-12-11 01:30 | 44906.0625 | 0 | 7.6451 | 37.78
2022-12-11 02:00 | 44906.0833 | 0 | 7.5979 | 37.78
2022-12-11 02:30 | 44906.1042 | 0 | 7.4651 | 37.78
2022-12-11 03:00 | 44906.125 | 0 | 7.4764 | 37.78
2022-12-11 03:30 | 44906.1458 | 0 | 7.4567 | 37.78
2022-12-11 04:00 | 44906.1667 | 0 | 7.4007 | 37.78
2022-12-11 04:30 | 44906.1875 | 0 | 7.2587 | 37.78
2022-12-11 05:00 | 44906.2083 | 0 | 7.1813 | 37.78
2022-12-11 05:30 | 44906.2292 | 0 | 7.1039 | 37.78
2022-12-11 06:00 | 44906.25 | 0 | 7.0236 | 37.78
2022-12-11 06:30 | 44906.2708 | 0 | 6.7117 | 37.78
2022-12-11 07:00 | 44906.2917 | 0 | 11.3582 | 37.78
2022-12-11 07:30 | 44906.3125 | 0 | 12.6057 | 37.78
2022-12-11 08:00 | 44906.3333 | 0 | 12.3589 | 37.78
2022-12-11 08:30 | 44906.3542 | 0 | 11.4505 | 37.78
2022-12-11 09:00 | 44906.375 | 0 | 11.9405 | 37.78
2022-12-11 09:30 | 44906.3958 | 0 | 11.1875 | 37.78
2022-12-11 10:00 | 44906.4167 | 0 | 10.6283 | 37.78
2022-12-11 10:30 | 44906.4375 | 0 | 10.4925 | 37.78
2022-12-11 11:00 | 44906.4583 | 0 | 12.1909 | 37.78
2022-12-11 11:30 | 44906.4792 | 0 | 14.4711 | 37.78
2022-12-11 12:00 | 44906.5 | 0 | 13.3712 | 37.78
2022-12-11 12:30 | 44906.5208 | 0 | 13.3608 | 37.78
2022-12-11 13:00 | 44906.5417 | 0 | 13.7186 | 37.78
2022-12-11 13:30 | 44906.5625 | 0 | 13.7617 | 37.78
2022-12-11 14:00 | 44906.5833 | 0 | 9.7028 | 37.78
2022-12-11 14:30 | 44906.6042 | 0 | 7.915 | 37.78
2022-12-11 15:00 | 44906.625 | 0 | 8.6719 | 37.78
2022-12-11 15:30 | 44906.6458 | 0 | 9.4702 | 37.78
2022-12-11 16:00 | 44906.6667 | 0 | 10.3305 | 37.78
2022-12-11 16:30 | 44906.6875 | 0 | 11.3235 | 37.78
2022-12-11 17:00 | 44906.7083 | 0 | 11.8741 | 37.78
2022-12-11 17:30 | 44906.7292 | 0 | 12.4075 | 37.78
2022-12-11 18:00 | 44906.75 | 0 | 12.6541 | 37.78
2022-12-11 18:30 | 44906.7708 | 0 | 12.693 | 37.78
2022-12-11 19:00 | 44906.7917 | 0 | 12.9678 | 37.78
2022-12-11 19:30 | 44906.8125 | 0 | 12.6153 | 37.78
2022-12-11 20:00 | 44906.8333 | 0 | 12.5533 | 37.78
2022-12-11 20:30 | 44906.8542 | 0 | 11.9276 | 37.78
2022-12-11 21:00 | 44906.875 | 0 | 11.6003 | 37.78
2022-12-11 21:30 | 44906.8958 | 0 | 11.1115 | 37.78
2022-12-11 22:00 | 44906.9167 | 0 | 10.6005 | 37.78
2022-12-11 22:30 | 44906.9375 | 0 | 10.0703 | 37.78
2022-12-11 23:00 | 44906.9583 | 0 | 9.5402 | 37.78
2022-12-11 23:30 | 44906.9792 | 0 | 9.0967 | 37.78
2022-12-12 | 44907 | 0 | 8.816 | 37.78
2022-12-12 00:30 | 44907.0208 | 0 | 8.4582 | 37.78
2022-12-12 01:00 | 44907.0417 | 0 | 8.3107 | 37.78
2022-12-12 01:30 | 44907.0625 | 0 | 8.1464 | 37.78
2022-12-12 02:00 | 44907.0833 | 0 | 8.088 | 37.78
2022-12-12 02:30 | 44907.1042 | 0 | 8.1517 | 37.78
2022-12-12 03:00 | 44907.125 | 0 | 7.9734 | 37.78
2022-12-12 03:30 | 44907.1458 | 0 | 8.1997 | 37.78
2022-12-12 04:00 | 44907.1667 | 0 | 8.6412 | 37.78
2022-12-12 04:30 | 44907.1875 | 0 | 8.8508 | 37.78
2022-12-12 05:00 | 44907.2083 | 0 | 9.2652 | 37.78
2022-12-12 05:30 | 44907.2292 | 0 | 9.6612 | 37.78
2022-12-12 06:00 | 44907.25 | 0 | 10.0706 | 37.78
2022-12-12 06:30 | 44907.2708 | 0 | 10.2653 | 37.78
2022-12-12 07:00 | 44907.2917 | 0 | 10.9371 | 37.78
2022-12-12 07:30 | 44907.3125 | 0 | 10.6642 | 37.78
2022-12-12 08:00 | 44907.3333 | 0 | 10.6952 | 37.78
2022-12-12 08:30 | 44907.3542 | 0 | 10.9118 | 37.78
2022-12-12 09:00 | 44907.375 | 0 | 12.1054 | 37.78
2022-12-12 09:30 | 44907.3958 | 0 | 12.042 | 37.78
2022-12-12 10:00 | 44907.4167 | 0 | 12.6747 | 37.78
2022-12-12 10:30 | 44907.4375 | 0 | 11.5408 | 37.78
2022-12-12 11:00 | 44907.4583 | 0 | 11.3929 | 37.78
2022-12-12 11:30 | 44907.4792 | 0 | 12.5771 | 37.78
2022-12-12 12:00 | 44907.5 | 0 | 11.6594 | 37.78
2022-12-12 12:30 | 44907.5208 | 0 | 12.233 | 37.78
2022-12-12 13:00 | 44907.5417 | 0 | 13.2114 | 37.78
2022-12-12 13:30 | 44907.5625 | 0 | 15.8637 | 37.78
2022-12-12 14:00 | 44907.5833 | 0 | 14.3635 | 37.78
2022-12-12 14:30 | 44907.6042 | 0 | 16.8274 | 37.78
2022-12-12 15:00 | 44907.625 | 0 | 15.4323 | 37.78
2022-12-12 15:30 | 44907.6458 | 0 | 16.6797 | 37.78
2022-12-12 16:00 | 44907.6667 | 0 | 16.513 | 37.78
2022-12-12 16:30 | 44907.6875 | 0 | 16.7912 | 37.78
2022-12-12 17:00 | 44907.7083 | 0 | 16.5541 | 37.78
2022-12-12 17:30 | 44907.7292 | 0 | 16.9618 | 37.78
2022-12-12 18:00 | 44907.75 | 0 | 16.844 | 37.78
2022-12-12 18:30 | 44907.7708 | 0 | 17.3564 | 37.78
2022-12-12 19:00 | 44907.7917 | 0 | 17.4367 | 37.78
2022-12-12 19:30 | 44907.8125 | 0 | 17.0118 | 37.78
2022-12-12 20:00 | 44907.8333 | 0 | 16.9786 | 37.78
2022-12-12 20:30 | 44907.8542 | 0 | 16.1463 | 37.78
2022-12-12 21:00 | 44907.875 | 0 | 15.7889 | 37.78
2022-12-12 21:30 | 44907.8958 | 0 | 15.1216 | 37.78
2022-12-12 22:00 | 44907.9167 | 0 | 14.0248 | 37.78
2022-12-12 22:30 | 44907.9375 | 0 | 13.0992 | 37.78
2022-12-12 23:00 | 44907.9583 | 0 | 12.4602 | 37.78
2022-12-12 23:30 | 44907.9792 | 0 | 12.1219 | 37.78
2022-12-13 | 44908 | 0 | 11.5054 | 37.78
2022-12-13 00:30 | 44908.0208 | 0 | 10.8742 | 37.78
2022-12-13 01:00 | 44908.0417 | 0 | 10.4502 | 37.78
2022-12-13 01:30 | 44908.0625 | 0 | 10.2021 | 37.78
2022-12-13 02:00 | 44908.0833 | 0 | 9.975 | 37.78
2022-12-13 02:30 | 44908.1042 | 0 | 10.0074 | 37.78
2022-12-13 03:00 | 44908.125 | 0 | 9.7054 | 37.78
2022-12-13 03:30 | 44908.1458 | 0 | 9.704 | 37.78
2022-12-13 04:00 | 44908.1667 | 0 | 9.9202 | 37.78
2022-12-13 04:30 | 44908.1875 | 0 | 10.3186 | 37.78
2022-12-13 05:00 | 44908.2083 | 0 | 10.5166 | 37.78
2022-12-13 05:30 | 44908.2292 | 0 | 10.6634 | 37.78
2022-12-13 06:00 | 44908.25 | 0 | 11.4846 | 37.78
2022-12-13 06:30 | 44908.2708 | 0 | 11.5509 | 37.78
2022-12-13 07:00 | 44908.2917 | 0 | 11.9192 | 37.78
2022-12-13 07:30 | 44908.3125 | 0 | 11.9376 | 37.78
2022-12-13 08:00 | 44908.3333 | 0 | 12.501 | 37.78
2022-12-13 08:30 | 44908.3542 | 0 | 12.8659 | 37.78
2022-12-13 09:00 | 44908.375 | 0 | 13.4189 | 37.78
2022-12-13 09:30 | 44908.3958 | 0 | 13.4345 | 37.78
2022-12-13 10:00 | 44908.4167 | 0 | 13.9898 | 37.78
2022-12-13 10:30 | 44908.4375 | 0 | 17.66 | 37.78
2022-12-13 11:00 | 44908.4583 | 0 | 16.7877 | 37.78
2022-12-13 11:30 | 44908.4792 | 0 | 15.5557 | 37.78
2022-12-13 12:00 | 44908.5 | 0 | 14.4255 | 37.78
2022-12-13 12:30 | 44908.5208 | 0 | 13.3168 | 37.78
2022-12-13 13:00 | 44908.5417 | 0 | 14.0943 | 37.78
2022-12-13 13:30 | 44908.5625 | 0 | 13.0507 | 37.78
2022-12-13 14:00 | 44908.5833 | 0 | 14.5164 | 37.78
2022-12-13 14:30 | 44908.6042 | 0 | 15.0645 | 37.78
2022-12-13 15:00 | 44908.625 | 0 | 14.4281 | 37.78
2022-12-13 15:30 | 44908.6458 | 0 | 14.3039 | 37.78
2022-12-13 16:00 | 44908.6667 | 0 | 14.4898 | 37.78
2022-12-13 16:30 | 44908.6875 | 0 | 14.6761 | 37.78
2022-12-13 17:00 | 44908.7083 | 0 | 14.473 | 37.78
2022-12-13 17:30 | 44908.7292 | 0 | 14.4419 | 37.78
2022-12-13 18:00 | 44908.75 | 0 | 14.518 | 37.78
2022-12-13 18:30 | 44908.7708 | 0 | 14.7955 | 37.78
2022-12-13 19:00 | 44908.7917 | 0 | 15.0549 | 37.78
2022-12-13 19:30 | 44908.8125 | 0 | 14.8929 | 37.78
2022-12-13 20:00 | 44908.8333 | 0 | 14.6409 | 37.78
2022-12-13 20:30 | 44908.8542 | 0 | 14.1672 | 37.78
2022-12-13 21:00 | 44908.875 | 0 | 13.8483 | 37.78
2022-12-13 21:30 | 44908.8958 | 0 | 13.4004 | 37.78
2022-12-13 22:00 | 44908.9167 | 0 | 12.7231 | 37.78
2022-12-13 22:30 | 44908.9375 | 0 | 12.026 | 37.78
2022-12-13 23:00 | 44908.9583 | 0 | 11.4469 | 37.78
2022-12-13 23:30 | 44908.9792 | 0 | 10.8965 | 37.78
2022-12-14 | 44909 | 0 | 10.3633 | 37.78
2022-12-14 00:30 | 44909.0208 | 0 | 9.9792 | 37.78
2022-12-14 01:00 | 44909.0417 | 0 | 9.7411 | 37.78
2022-12-14 01:30 | 44909.0625 | 0 | 9.5456 | 37.78
2022-12-14 02:00 | 44909.0833 | 0 | 9.5165 | 37.78
2022-12-14 02:30 | 44909.1042 | 0 | 9.3866 | 37.78
2022-12-14 03:00 | 44909.125 | 0 | 9.2466 | 37.78
2022-12-14 03:30 | 44909.1458 | 0 | 9.2609 | 37.78
2022-12-14 04:00 | 44909.1667 | 0 | 9.5792 | 37.78
2022-12-14 04:30 | 44909.1875 | 0 | 9.8008 | 37.78
2022-12-14 05:00 | 44909.2083 | 0 | 10.0676 | 37.78
2022-12-14 05:30 | 44909.2292 | 0 | 10.3973 | 37.78
2022-12-14 06:00 | 44909.25 | 0 | 11.3299 | 37.78
2022-12-14 06:30 | 44909.2708 | 0 | 11.6593 | 37.78
2022-12-14 07:00 | 44909.2917 | 0 | 12.3881 | 37.78
2022-12-14 07:30 | 44909.3125 | 0 | 12.1961 | 37.78
2022-12-14 08:00 | 44909.3333 | 0 | 11.3885 | 37.78
2022-12-14 08:30 | 44909.3542 | 0 | 10.7387 | 37.78
2022-12-14 09:00 | 44909.375 | 0 | 11.3058 | 37.78
2022-12-14 09:30 | 44909.3958 | 0 | 11.426 | 37.78
2022-12-14 10:00 | 44909.4167 | 0 | 11.2134 | 37.78
2022-12-14 10:30 | 44909.4375 | 0 | 11.7133 | 37.78
2022-12-14 11:00 | 44909.4583 | 0 | 11.1778 | 37.78
2022-12-14 11:30 | 44909.4792 | 0 | 11.3359 | 37.78
2022-12-14 12:00 | 44909.5 | 0 | 11.6904 | 37.78
2022-12-14 12:30 | 44909.5208 | 0 | 11.7565 | 37.78
2022-12-14 13:00 | 44909.5417 | 0 | 12.0099 | 37.78
2022-12-14 13:30 | 44909.5625 | 0 | 12.6235 | 37.78
2022-12-14 14:00 | 44909.5833 | 0 | 13.2977 | 37.78
2022-12-14 14:30 | 44909.6042 | 0 | 14.0663 | 37.78
2022-12-14 15:00 | 44909.625 | 0 | 14.8383 | 37.78
2022-12-14 15:30 | 44909.6458 | 0 | 15.6639 | 37.78
2022-12-14 16:00 | 44909.6667 | 0 | 16.5063 | 37.78
2022-12-14 16:30 | 44909.6875 | 0 | 17.4067 | 37.78
2022-12-14 17:00 | 44909.7083 | 0 | 17.728 | 37.78
2022-12-14 17:30 | 44909.7292 | 0 | 17.9858 | 37.78
2022-12-14 18:00 | 44909.75 | 0 | 17.7175 | 37.78
2022-12-14 18:30 | 44909.7708 | 0 | 17.7101 | 37.78
2022-12-14 19:00 | 44909.7917 | 0 | 17.7214 | 37.78
2022-12-14 19:30 | 44909.8125 | 0 | 17.4326 | 37.78
2022-12-14 20:00 | 44909.8333 | 0 | 17.1868 | 37.78
2022-12-14 20:30 | 44909.8542 | 0 | 16.3806 | 37.78
2022-12-14 21:00 | 44909.875 | 0 | 15.7761 | 37.78
2022-12-14 21:30 | 44909.8958 | 0 | 15.1585 | 37.78
2022-12-14 22:00 | 44909.9167 | 0 | 14.2801 | 37.78
2022-12-14 22:30 | 44909.9375 | 0 | 13.4221 | 37.78
2022-12-14 23:00 | 44909.9583 | 0 | 12.5291 | 37.78
2022-12-14 23:30 | 44909.9792 | 0 | 11.888 | 37.78
2022-12-15 | 44910 | 0 | 11.1209 | 37.78
2022-12-15 00:30 | 44910.0208 | 0 | 10.4966 | 37.78
2022-12-15 01:00 | 44910.0417 | 0 | 10.2742 | 37.78
2022-12-15 01:30 | 44910.0625 | 0 | 9.9794 | 37.78
2022-12-15 02:00 | 44910.0833 | 0 | 9.5858 | 37.78
2022-12-15 02:30 | 44910.1042 | 0 | 9.5956 | 37.78
2022-12-15 03:00 | 44910.125 | 0 | 9.3639 | 37.78
2022-12-15 03:30 | 44910.1458 | 0 | 9.3455 | 37.78
2022-12-15 04:00 | 44910.1667 | 0 | 9.4744 | 37.78
2022-12-15 04:30 | 44910.1875 | 0 | 9.7373 | 37.78
2022-12-15 05:00 | 44910.2083 | 0 | 10.0133 | 37.78
2022-12-15 05:30 | 44910.2292 | 0 | 10.122 | 37.78
2022-12-15 06:00 | 44910.25 | 0 | 10.1378 | 37.78
2022-12-15 06:30 | 44910.2708 | 0 | 10.955 | 37.78
2022-12-15 07:00 | 44910.2917 | 0 | 11.3179 | 37.78
2022-12-15 07:30 | 44910.3125 | 0 | 11.3359 | 37.78
2022-12-15 08:00 | 44910.3333 | 0 | 12.0679 | 37.78
2022-12-15 08:30 | 44910.3542 | 0 | 11.7621 | 37.78
2022-12-15 09:00 | 44910.375 | 0 | 10.6319 | 37.78
2022-12-15 09:30 | 44910.3958 | 0 | 11.8727 | 37.78
2022-12-15 10:00 | 44910.4167 | 0 | 11.9302 | 37.78
2022-12-15 10:30 | 44910.4375 | 0 | 12.947 | 37.78
2022-12-15 11:00 | 44910.4583 | 0 | 9.9142 | 37.78
2022-12-15 11:30 | 44910.4792 | 0 | 10.0029 | 37.78
2022-12-15 12:00 | 44910.5 | 0 | 9.3952 | 37.78
2022-12-15 12:30 | 44910.5208 | 0 | 9.6228 | 37.78
2022-12-15 13:00 | 44910.5417 | 0 | 10.3589 | 37.78
2022-12-15 13:30 | 44910.5625 | 0 | 11.7972 | 37.78
2022-12-15 14:00 | 44910.5833 | 0 | 12.5556 | 37.78
2022-12-15 14:30 | 44910.6042 | 0 | 12.1544 | 37.78
2022-12-15 15:00 | 44910.625 | 0 | 14.3732 | 37.78
2022-12-15 15:30 | 44910.6458 | 0 | 13.8489 | 37.78
2022-12-15 16:00 | 44910.6667 | 0 | 13.5977 | 37.78
2022-12-15 16:30 | 44910.6875 | 0 | 14.4858 | 37.78
2022-12-15 17:00 | 44910.7083 | 0 | 14.7244 | 37.78
2022-12-15 17:30 | 44910.7292 | 0 | 14.8554 | 37.78
2022-12-15 18:00 | 44910.75 | 0 | 14.7532 | 37.78
2022-12-15 18:30 | 44910.7708 | 0 | 14.8563 | 37.78
2022-12-15 19:00 | 44910.7917 | 0 | 14.9343 | 37.78
2022-12-15 19:30 | 44910.8125 | 0 | 14.7395 | 37.78
2022-12-15 20:00 | 44910.8333 | 0 | 14.6157 | 37.78
2022-12-15 20:30 | 44910.8542 | 0 | 13.9771 | 37.78
2022-12-15 21:00 | 44910.875 | 0 | 13.7 | 37.78
2022-12-15 21:30 | 44910.8958 | 0 | 13.3939 | 37.78
2022-12-15 22:00 | 44910.9167 | 0 | 12.6759 | 37.78
2022-12-15 22:30 | 44910.9375 | 0 | 11.9731 | 37.78
2022-12-15 23:00 | 44910.9583 | 0 | 11.3304 | 37.78
2022-12-15 23:30 | 44910.9792 | 0 | 10.7766 | 37.78
2022-12-16 | 44911 | 0 | 10.3703 | 37.78
2022-12-16 00:30 | 44911.0208 | 0 | 9.9449 | 37.78
2022-12-16 01:00 | 44911.0417 | 0 | 9.754 | 37.78
2022-12-16 01:30 | 44911.0625 | 0 | 9.4633 | 37.78
2022-12-16 02:00 | 44911.0833 | 0 | 9.4032 | 37.78
2022-12-16 02:30 | 44911.1042 | 0 | 9.2493 | 37.78
2022-12-16 03:00 | 44911.125 | 0 | 9.0328 | 37.78
2022-12-16 03:30 | 44911.1458 | 0 | 9.0599 | 37.78
2022-12-16 04:00 | 44911.1667 | 0 | 9.5226 | 37.78
2022-12-16 04:30 | 44911.1875 | 0 | 9.6564 | 37.78
2022-12-16 05:00 | 44911.2083 | 0 | 10.1057 | 37.78
2022-12-16 05:30 | 44911.2292 | 0 | 10.2522 | 37.78
2022-12-16 06:00 | 44911.25 | 0 | 10.2546 | 37.78
2022-12-16 06:30 | 44911.2708 | 0 | 10.1767 | 37.78
2022-12-16 07:00 | 44911.2917 | 0 | 10.885 | 37.78
2022-12-16 07:30 | 44911.3125 | 0 | 11.4289 | 37.78
2022-12-16 08:00 | 44911.3333 | 0 | 12.0265 | 37.78
2022-12-16 08:30 | 44911.3542 | 0 | 10.5236 | 37.78
2022-12-16 09:00 | 44911.375 | 0 | 10.2203 | 37.78
2022-12-16 09:30 | 44911.3958 | 0 | 11.8097 | 37.78
2022-12-16 10:00 | 44911.4167 | 0 | 11.1035 | 37.78
2022-12-16 10:30 | 44911.4375 | 0 | 11.6049 | 37.78
2022-12-16 11:00 | 44911.4583 | 0 | 9.7567 | 37.78
2022-12-16 11:30 | 44911.4792 | 0 | 9.4196 | 37.78
2022-12-16 12:00 | 44911.5 | 0 | 10.6847 | 37.78
2022-12-16 12:30 | 44911.5208 | 0 | 11.4916 | 37.78
2022-12-16 13:00 | 44911.5417 | 0 | 10.0924 | 37.78
2022-12-16 13:30 | 44911.5625 | 0 | 10.0354 | 37.78
2022-12-16 14:00 | 44911.5833 | 0 | 10.9172 | 37.78
2022-12-16 14:30 | 44911.6042 | 0 | 12.8875 | 37.78
2022-12-16 15:00 | 44911.625 | 0 | 13.3533 | 37.78
2022-12-16 15:30 | 44911.6458 | 0 | 11.6134 | 37.78
2022-12-16 16:00 | 44911.6667 | 0 | 12.8706 | 37.78
2022-12-16 16:30 | 44911.6875 | 0 | 13.4148 | 37.78
2022-12-16 17:00 | 44911.7083 | 0 | 13.7355 | 37.78
2022-12-16 17:30 | 44911.7292 | 0 | 13.9722 | 37.78
2022-12-16 18:00 | 44911.75 | 0 | 14.0335 | 37.78
2022-12-16 18:30 | 44911.7708 | 0 | 14.1917 | 37.78
2022-12-16 19:00 | 44911.7917 | 0 | 14.1865 | 37.78
2022-12-16 19:30 | 44911.8125 | 0 | 14.0603 | 37.78
2022-12-16 20:00 | 44911.8333 | 0 | 13.8754 | 37.78
2022-12-16 20:30 | 44911.8542 | 0 | 13.3814 | 37.78
2022-12-16 21:00 | 44911.875 | 0 | 13.3123 | 37.78
2022-12-16 21:30 | 44911.8958 | 0 | 12.8552 | 37.78
2022-12-16 22:00 | 44911.9167 | 0 | 12.2075 | 37.78
2022-12-16 22:30 | 44911.9375 | 0 | 11.5524 | 37.78
2022-12-16 23:00 | 44911.9583 | 0 | 10.8729 | 37.78
2022-12-16 23:30 | 44911.9792 | 0 | 10.4695 | 37.78
2022-12-17 | 44912 | 0 | 9.9126 | 37.78
2022-12-17 00:30 | 44912.0208 | 0 | 9.6697 | 37.78
2022-12-17 01:00 | 44912.0417 | 0 | 9.3093 | 37.78
2022-12-17 01:30 | 44912.0625 | 0 | 9.0766 | 37.78
2022-12-17 02:00 | 44912.0833 | 0 | 8.8485 | 37.78
2022-12-17 02:30 | 44912.1042 | 0 | 8.7678 | 37.78
2022-12-17 03:00 | 44912.125 | 0 | 8.6627 | 37.78
2022-12-17 03:30 | 44912.1458 | 0 | 8.6454 | 37.78
2022-12-17 04:00 | 44912.1667 | 0 | 8.7559 | 37.78
2022-12-17 04:30 | 44912.1875 | 0 | 8.7717 | 37.78
2022-12-17 05:00 | 44912.2083 | 0 | 8.7019 | 37.78
2022-12-17 05:30 | 44912.2292 | 0 | 8.4849 | 37.78
2022-12-17 06:00 | 44912.25 | 0 | 7.9198 | 37.78
2022-12-17 06:30 | 44912.2708 | 0 | 7.4144 | 37.78
2022-12-17 07:00 | 44912.2917 | 0 | 7.1426 | 37.78
2022-12-17 07:30 | 44912.3125 | 0 | 6.854 | 37.78
2022-12-17 08:00 | 44912.3333 | 0 | 6.7915 | 37.78
2022-12-17 08:30 | 44912.3542 | 0 | 8.0259 | 37.78
2022-12-17 09:00 | 44912.375 | 0 | 9.1353 | 37.78
2022-12-17 09:30 | 44912.3958 | 0 | 10.0523 | 37.78
2022-12-17 10:00 | 44912.4167 | 0 | 8.3646 | 37.78
2022-12-17 10:30 | 44912.4375 | 0 | 8.8824 | 37.78
2022-12-17 11:00 | 44912.4583 | 0 | 7.1383 | 37.78
2022-12-17 11:30 | 44912.4792 | 0 | 7.8976 | 37.78
2022-12-17 12:00 | 44912.5 | 0 | 7.5353 | 37.78
2022-12-17 12:30 | 44912.5208 | 0 | 8.0418 | 37.78
2022-12-17 13:00 | 44912.5417 | 0 | 7.7329 | 37.78
2022-12-17 13:30 | 44912.5625 | 0 | 8.6594 | 37.78
2022-12-17 14:00 | 44912.5833 | 0 | 9.0404 | 37.78
2022-12-17 14:30 | 44912.6042 | 0 | 7.7554 | 37.78
2022-12-17 15:00 | 44912.625 | 0 | 7.2904 | 37.78
2022-12-17 15:30 | 44912.6458 | 0 | 8.6015 | 37.78
2022-12-17 16:00 | 44912.6667 | 0 | 9.7374 | 37.78
2022-12-17 16:30 | 44912.6875 | 0 | 10.332 | 37.78
2022-12-17 17:00 | 44912.7083 | 0 | 10.825 | 37.78
2022-12-17 17:30 | 44912.7292 | 0 | 11.1522 | 37.78
2022-12-17 18:00 | 44912.75 | 0 | 11.3798 | 37.78
2022-12-17 18:30 | 44912.7708 | 0 | 11.6591 | 37.78
2022-12-17 19:00 | 44912.7917 | 0 | 11.8073 | 37.78
2022-12-17 19:30 | 44912.8125 | 0 | 11.487 | 37.78
2022-12-17 20:00 | 44912.8333 | 0 | 11.4284 | 37.78
2022-12-17 20:30 | 44912.8542 | 0 | 10.9052 | 37.78
2022-12-17 21:00 | 44912.875 | 0 | 10.6482 | 37.78
2022-12-17 21:30 | 44912.8958 | 0 | 10.4216 | 37.78
2022-12-17 22:00 | 44912.9167 | 0 | 10.0638 | 37.78
2022-12-17 22:30 | 44912.9375 | 0 | 9.5509 | 37.78
2022-12-17 23:00 | 44912.9583 | 0 | 9.2643 | 37.78
2022-12-17 23:30 | 44912.9792 | 0 | 8.7594 | 37.78
2022-12-18 | 44913 | 0 | 8.3476 | 37.78
2022-12-18 00:30 | 44913.0208 | 0 | 8.0509 | 37.78
2022-12-18 01:00 | 44913.0417 | 0 | 7.9151 | 37.78
2022-12-18 01:30 | 44913.0625 | 0 | 7.7581 | 37.78
2022-12-18 02:00 | 44913.0833 | 0 | 7.7482 | 37.78
2022-12-18 02:30 | 44913.1042 | 0 | 7.6077 | 37.78
2022-12-18 03:00 | 44913.125 | 0 | 7.5618 | 37.78
2022-12-18 03:30 | 44913.1458 | 0 | 7.4329 | 37.78
2022-12-18 04:00 | 44913.1667 | 0 | 7.5288 | 37.78
2022-12-18 04:30 | 44913.1875 | 0 | 7.373 | 37.78
2022-12-18 05:00 | 44913.2083 | 0 | 7.2715 | 37.78
2022-12-18 05:30 | 44913.2292 | 0 | 6.9321 | 37.78
2022-12-18 06:00 | 44913.25 | 0 | 6.6297 | 37.78
2022-12-18 06:30 | 44913.2708 | 0 | 5.9887 | 37.78
2022-12-18 07:00 | 44913.2917 | 0 | 5.6558 | 37.78
2022-12-18 07:30 | 44913.3125 | 0 | 5.414 | 37.78
2022-12-18 08:00 | 44913.3333 | 0 | 5.561 | 37.78
2022-12-18 08:30 | 44913.3542 | 0 | 6.1422 | 37.78
2022-12-18 09:00 | 44913.375 | 0 | 5.738 | 37.78
2022-12-18 09:30 | 44913.3958 | 0 | 6.2227 | 37.78
2022-12-18 10:00 | 44913.4167 | 0 | 6.6094 | 37.78
2022-12-18 10:30 | 44913.4375 | 0 | 6.0206 | 37.78
2022-12-18 11:00 | 44913.4583 | 0 | 6.2664 | 37.78
2022-12-18 11:30 | 44913.4792 | 0 | 6.8025 | 37.78
2022-12-18 12:00 | 44913.5 | 0 | 7.5579 | 37.78
2022-12-18 12:30 | 44913.5208 | 0 | 8.646 | 37.78
2022-12-18 13:00 | 44913.5417 | 0 | 8.9127 | 37.78
2022-12-18 13:30 | 44913.5625 | 0 | 7.3514 | 37.78
2022-12-18 14:00 | 44913.5833 | 0 | 8.065 | 37.78
2022-12-18 14:30 | 44913.6042 | 0 | 7.2542 | 37.78
2022-12-18 15:00 | 44913.625 | 0 | 8.1818 | 37.78
2022-12-18 15:30 | 44913.6458 | 0 | 7.5849 | 37.78
2022-12-18 16:00 | 44913.6667 | 0 | 8.1698 | 37.78
2022-12-18 16:30 | 44913.6875 | 0 | 9.1316 | 37.78
2022-12-18 17:00 | 44913.7083 | 0 | 9.8385 | 37.78
2022-12-18 17:30 | 44913.7292 | 0 | 10.2493 | 37.78
2022-12-18 18:00 | 44913.75 | 0 | 10.9597 | 37.78
2022-12-18 18:30 | 44913.7708 | 0 | 11.4256 | 37.78
2022-12-18 19:00 | 44913.7917 | 0 | 11.5719 | 37.78
2022-12-18 19:30 | 44913.8125 | 0 | 11.2991 | 37.78
2022-12-18 20:00 | 44913.8333 | 0 | 11.183 | 37.78
2022-12-18 20:30 | 44913.8542 | 0 | 10.7949 | 37.78
2022-12-18 21:00 | 44913.875 | 0 | 10.4946 | 37.78
2022-12-18 21:30 | 44913.8958 | 0 | 10.2229 | 37.78
2022-12-18 22:00 | 44913.9167 | 0 | 9.775 | 37.78
2022-12-18 22:30 | 44913.9375 | 0 | 9.1332 | 37.78
2022-12-18 23:00 | 44913.9583 | 0 | 8.687 | 37.78
2022-12-18 23:30 | 44913.9792 | 0 | 8.4325 | 37.78
2022-12-19 | 44914 | 0 | 8.2236 | 37.78
2022-12-19 00:30 | 44914.0208 | 0 | 7.9963 | 37.78
2022-12-19 01:00 | 44914.0417 | 0 | 7.9516 | 37.78
2022-12-19 01:30 | 44914.0625 | 0 | 7.8319 | 37.78
2022-12-19 02:00 | 44914.0833 | 0 | 7.7122 | 37.78
2022-12-19 02:30 | 44914.1042 | 0 | 7.8426 | 37.78
2022-12-19 03:00 | 44914.125 | 0 | 7.5615 | 37.78
2022-12-19 03:30 | 44914.1458 | 0 | 7.7253 | 37.78
2022-12-19 04:00 | 44914.1667 | 0 | 8.1166 | 37.78
2022-12-19 04:30 | 44914.1875 | 0 | 8.4331 | 37.78
2022-12-19 05:00 | 44914.2083 | 0 | 8.7242 | 37.78
2022-12-19 05:30 | 44914.2292 | 0 | 8.7249 | 37.78
2022-12-19 06:00 | 44914.25 | 0 | 9.1912 | 37.78
2022-12-19 06:30 | 44914.2708 | 0 | 9.0761 | 37.78
2022-12-19 07:00 | 44914.2917 | 0 | 9.3809 | 37.78
2022-12-19 07:30 | 44914.3125 | 0 | 9.4133 | 37.78
2022-12-19 08:00 | 44914.3333 | 0 | 10.2792 | 37.78
2022-12-19 08:30 | 44914.3542 | 0 | 9.877 | 37.78
2022-12-19 09:00 | 44914.375 | 0 | 9.9621 | 37.78
2022-12-19 09:30 | 44914.3958 | 0 | 9.4012 | 37.78
2022-12-19 10:00 | 44914.4167 | 0 | 9.1562 | 37.78
2022-12-19 10:30 | 44914.4375 | 0 | 10.5769 | 37.78
2022-12-19 11:00 | 44914.4583 | 0 | 10.53 | 37.78
2022-12-19 11:30 | 44914.4792 | 0 | 10.5626 | 37.78
2022-12-19 12:00 | 44914.5 | 0 | 10.7105 | 37.78
2022-12-19 12:30 | 44914.5208 | 0 | 12.2185 | 37.78
2022-12-19 13:00 | 44914.5417 | 0 | 10.1808 | 37.78
2022-12-19 13:30 | 44914.5625 | 0 | 8.7215 | 37.78
2022-12-19 14:00 | 44914.5833 | 0 | 9.673 | 37.78
2022-12-19 14:30 | 44914.6042 | 0 | 11.1472 | 37.78
2022-12-19 15:00 | 44914.625 | 0 | 10.4348 | 37.78
2022-12-19 15:30 | 44914.6458 | 0 | 11.3341 | 37.78
2022-12-19 16:00 | 44914.6667 | 0 | 10.7754 | 37.78
2022-12-19 16:30 | 44914.6875 | 0 | 11.7817 | 37.78
2022-12-19 17:00 | 44914.7083 | 0 | 12.4521 | 37.78
2022-12-19 17:30 | 44914.7292 | 0 | 12.8174 | 37.78
2022-12-19 18:00 | 44914.75 | 0 | 12.8978 | 37.78
2022-12-19 18:30 | 44914.7708 | 0 | 13.0479 | 37.78
2022-12-19 19:00 | 44914.7917 | 0 | 12.989 | 37.78
2022-12-19 19:30 | 44914.8125 | 0 | 12.6986 | 37.78
2022-12-19 20:00 | 44914.8333 | 0 | 12.4214 | 37.78
2022-12-19 20:30 | 44914.8542 | 0 | 11.9905 | 37.78
2022-12-19 21:00 | 44914.875 | 0 | 11.788 | 37.78
2022-12-19 21:30 | 44914.8958 | 0 | 11.3411 | 37.78
2022-12-19 22:00 | 44914.9167 | 0 | 10.9037 | 37.78
2022-12-19 22:30 | 44914.9375 | 0 | 10.3799 | 37.78
2022-12-19 23:00 | 44914.9583 | 0 | 9.94 | 37.78
2022-12-19 23:30 | 44914.9792 | 0 | 9.4402 | 37.78
2022-12-20 | 44915 | 0 | 8.7327 | 37.78
2022-12-20 00:30 | 44915.0208 | 0 | 8.5135 | 37.78
2022-12-20 01:00 | 44915.0417 | 0 | 8.356 | 37.78
2022-12-20 01:30 | 44915.0625 | 0 | 8.1776 | 37.78
2022-12-20 02:00 | 44915.0833 | 0 | 8.0865 | 37.78
2022-12-20 02:30 | 44915.1042 | 0 | 8.0249 | 37.78
2022-12-20 03:00 | 44915.125 | 0 | 7.9215 | 37.78
2022-12-20 03:30 | 44915.1458 | 0 | 7.9805 | 37.78
2022-12-20 04:00 | 44915.1667 | 0 | 8.4751 | 37.78
2022-12-20 04:30 | 44915.1875 | 0 | 8.6234 | 37.78
2022-12-20 05:00 | 44915.2083 | 0 | 8.8043 | 37.78
2022-12-20 05:30 | 44915.2292 | 0 | 8.85 | 37.78
2022-12-20 06:00 | 44915.25 | 0 | 8.9992 | 37.78
2022-12-20 06:30 | 44915.2708 | 0 | 9.1141 | 37.78
2022-12-20 07:00 | 44915.2917 | 0 | 8.9387 | 37.78
2022-12-20 07:30 | 44915.3125 | 0 | 8.3169 | 37.78
2022-12-20 08:00 | 44915.3333 | 0 | 8.2583 | 37.78
2022-12-20 08:30 | 44915.3542 | 0 | 8.1434 | 37.78
2022-12-20 09:00 | 44915.375 | 0 | 7.764 | 37.78
2022-12-20 09:30 | 44915.3958 | 0 | 7.7774 | 37.78
2022-12-20 10:00 | 44915.4167 | 0 | 7.8632 | 37.78
2022-12-20 10:30 | 44915.4375 | 0 | 8.4726 | 37.78
2022-12-20 11:00 | 44915.4583 | 0 | 8.9815 | 37.78
2022-12-20 11:30 | 44915.4792 | 0 | 10.1106 | 37.78
2022-12-20 12:00 | 44915.5 | 0 | 9.9795 | 37.78
2022-12-20 12:30 | 44915.5208 | 0 | 10.361 | 37.78
2022-12-20 13:00 | 44915.5417 | 0 | 10.1642 | 37.78
2022-12-20 13:30 | 44915.5625 | 0 | 11.3127 | 37.78
2022-12-20 14:00 | 44915.5833 | 0 | 10.938 | 37.78
2022-12-20 14:30 | 44915.6042 | 0 | 11.5834 | 37.78
2022-12-20 15:00 | 44915.625 | 0 | 10.304 | 37.78
2022-12-20 15:30 | 44915.6458 | 0 | 9.9469 | 37.78
2022-12-20 16:00 | 44915.6667 | 0 | 10.9371 | 37.78
2022-12-20 16:30 | 44915.6875 | 0 | 11.746 | 37.78
2022-12-20 17:00 | 44915.7083 | 0 | 12.4355 | 37.78
2022-12-20 17:30 | 44915.7292 | 0 | 12.5188 | 37.78
2022-12-20 18:00 | 44915.75 | 0 | 12.7659 | 37.78
2022-12-20 18:30 | 44915.7708 | 0 | 12.9098 | 37.78
2022-12-20 19:00 | 44915.7917 | 0 | 12.8598 | 37.78
2022-12-20 19:30 | 44915.8125 | 0 | 12.5447 | 37.78
2022-12-20 20:00 | 44915.8333 | 0 | 12.5965 | 37.78
2022-12-20 20:30 | 44915.8542 | 0 | 12.2305 | 37.78
2022-12-20 21:00 | 44915.875 | 0 | 12.0727 | 37.78
2022-12-20 21:30 | 44915.8958 | 0 | 11.6663 | 37.78
2022-12-20 22:00 | 44915.9167 | 0 | 11.1368 | 37.78
2022-12-20 22:30 | 44915.9375 | 0 | 10.4015 | 37.78
2022-12-20 23:00 | 44915.9583 | 0 | 9.9846 | 37.78
2022-12-20 23:30 | 44915.9792 | 0 | 9.4988 | 37.78
2022-12-21 | 44916 | 0 | 8.9961 | 37.78
2022-12-21 00:30 | 44916.0208 | 0 | 8.6883 | 37.78
2022-12-21 01:00 | 44916.0417 | 0 | 8.4299 | 37.78
2022-12-21 01:30 | 44916.0625 | 0 | 8.2851 | 37.78
2022-12-21 02:00 | 44916.0833 | 0 | 8.2259 | 37.78
2022-12-21 02:30 | 44916.1042 | 0 | 8.2932 | 37.78
2022-12-21 03:00 | 44916.125 | 0 | 8.0141 | 37.78
2022-12-21 03:30 | 44916.1458 | 0 | 8.2366 | 37.78
2022-12-21 04:00 | 44916.1667 | 0 | 8.4933 | 37.78
2022-12-21 04:30 | 44916.1875 | 0 | 8.6517 | 37.78
2022-12-21 05:00 | 44916.2083 | 0 | 8.9483 | 37.78
2022-12-21 05:30 | 44916.2292 | 0 | 8.939 | 37.78
2022-12-21 06:00 | 44916.25 | 0 | 9.1272 | 37.78
2022-12-21 06:30 | 44916.2708 | 0 | 9.1486 | 37.78
2022-12-21 07:00 | 44916.2917 | 0 | 8.8553 | 37.78
2022-12-21 07:30 | 44916.3125 | 0 | 8.5591 | 37.78
2022-12-21 08:00 | 44916.3333 | 0 | 8.632 | 37.78
2022-12-21 08:30 | 44916.3542 | 0 | 8.4573 | 37.78
2022-12-21 09:00 | 44916.375 | 0 | 8.7361 | 37.78
2022-12-21 09:30 | 44916.3958 | 0 | 9.6809 | 37.78
2022-12-21 10:00 | 44916.4167 | 0 | 10.6922 | 37.78
2022-12-21 10:30 | 44916.4375 | 0 | 10.2845 | 37.78
2022-12-21 11:00 | 44916.4583 | 0 | 10.5292 | 37.78
2022-12-21 11:30 | 44916.4792 | 0 | 10.8368 | 37.78
2022-12-21 12:00 | 44916.5 | 0 | 10.6499 | 37.78
2022-12-21 12:30 | 44916.5208 | 0 | 10.7469 | 37.78
2022-12-21 13:00 | 44916.5417 | 0 | 10.4819 | 37.78
2022-12-21 13:30 | 44916.5625 | 0 | 10.7307 | 37.78
2022-12-21 14:00 | 44916.5833 | 0 | 9.0811 | 37.78
2022-12-21 14:30 | 44916.6042 | 0 | 10.2522 | 37.78
2022-12-21 15:00 | 44916.625 | 0 | 11.4731 | 37.78
2022-12-21 15:30 | 44916.6458 | 0 | 12.8323 | 37.78
2022-12-21 16:00 | 44916.6667 | 0 | 12.5602 | 37.78
2022-12-21 16:30 | 44916.6875 | 0 | 12.7317 | 37.78
2022-12-21 17:00 | 44916.7083 | 0 | 12.2981 | 37.78
2022-12-21 17:30 | 44916.7292 | 0 | 12.8675 | 37.78
2022-12-21 18:00 | 44916.75 | 0 | 12.8106 | 37.78
2022-12-21 18:30 | 44916.7708 | 0 | 13.2522 | 37.78
2022-12-21 19:00 | 44916.7917 | 0 | 13.2656 | 37.78
2022-12-21 19:30 | 44916.8125 | 0 | 13.0432 | 37.78
2022-12-21 20:00 | 44916.8333 | 0 | 12.8629 | 37.78
2022-12-21 20:30 | 44916.8542 | 0 | 12.3878 | 37.78
2022-12-21 21:00 | 44916.875 | 0 | 12.1535 | 37.78
2022-12-21 21:30 | 44916.8958 | 0 | 11.9073 | 37.78
2022-12-21 22:00 | 44916.9167 | 0 | 11.4261 | 37.78
2022-12-21 22:30 | 44916.9375 | 0 | 10.7814 | 37.78
2022-12-21 23:00 | 44916.9583 | 0 | 10.2126 | 37.78
2022-12-21 23:30 | 44916.9792 | 0 | 9.8325 | 37.78
2022-12-22 | 44917 | 0 | 9.3157 | 37.78
2022-12-22 00:30 | 44917.0208 | 0 | 8.8116 | 37.78
2022-12-22 01:00 | 44917.0417 | 0 | 8.7067 | 37.78
2022-12-22 01:30 | 44917.0625 | 0 | 8.4057 | 37.78
2022-12-22 02:00 | 44917.0833 | 0 | 8.4617 | 37.78
2022-12-22 02:30 | 44917.1042 | 0 | 8.4307 | 37.78
2022-12-22 03:00 | 44917.125 | 0 | 8.4129 | 37.78
2022-12-22 03:30 | 44917.1458 | 0 | 8.5799 | 37.78
2022-12-22 04:00 | 44917.1667 | 0 | 8.8058 | 37.78
2022-12-22 04:30 | 44917.1875 | 0 | 9.0572 | 37.78
2022-12-22 05:00 | 44917.2083 | 0 | 9.2859 | 37.78
2022-12-22 05:30 | 44917.2292 | 0 | 9.4955 | 37.78
2022-12-22 06:00 | 44917.25 | 0 | 9.4868 | 37.78
2022-12-22 06:30 | 44917.2708 | 0 | 9.2356 | 37.78
2022-12-22 07:00 | 44917.2917 | 0 | 9.414 | 37.78
2022-12-22 07:30 | 44917.3125 | 0 | 9.3586 | 37.78
2022-12-22 08:00 | 44917.3333 | 0 | 9.858 | 37.78
2022-12-22 08:30 | 44917.3542 | 0 | 10.5705 | 37.78
2022-12-22 09:00 | 44917.375 | 0 | 10.9556 | 37.78
2022-12-22 09:30 | 44917.3958 | 0 | 10.064 | 37.78
2022-12-22 10:00 | 44917.4167 | 0 | 10.0696 | 37.78
2022-12-22 10:30 | 44917.4375 | 0 | 11.3324 | 37.78
2022-12-22 11:00 | 44917.4583 | 0 | 10.4014 | 37.78
2022-12-22 11:30 | 44917.4792 | 0 | 10.3686 | 37.78
2022-12-22 12:00 | 44917.5 | 0 | 9.6585 | 37.78
2022-12-22 12:30 | 44917.5208 | 0 | 9.2133 | 37.78
2022-12-22 13:00 | 44917.5417 | 0 | 9.7488 | 37.78
2022-12-22 13:30 | 44917.5625 | 0 | 10.0341 | 37.78
2022-12-22 14:00 | 44917.5833 | 0 | 9.5376 | 37.78
2022-12-22 14:30 | 44917.6042 | 0 | 9.6303 | 37.78
2022-12-22 15:00 | 44917.625 | 0 | 10.4254 | 37.78
2022-12-22 15:30 | 44917.6458 | 0 | 11.2378 | 37.78
2022-12-22 16:00 | 44917.6667 | 0 | 12.5955 | 37.78
2022-12-22 16:30 | 44917.6875 | 0 | 12.4228 | 37.78
2022-12-22 17:00 | 44917.7083 | 0 | 13.2073 | 37.78
2022-12-22 17:30 | 44917.7292 | 0 | 13.8528 | 37.78
2022-12-22 18:00 | 44917.75 | 0 | 13.5107 | 37.78
2022-12-22 18:30 | 44917.7708 | 0 | 13.5571 | 37.78
2022-12-22 19:00 | 44917.7917 | 0 | 13.6432 | 37.78
2022-12-22 19:30 | 44917.8125 | 0 | 13.3281 | 37.78
2022-12-22 20:00 | 44917.8333 | 0 | 13.2141 | 37.78
2022-12-22 20:30 | 44917.8542 | 0 | 12.9261 | 37.78
2022-12-22 21:00 | 44917.875 | 0 | 12.7296 | 37.78
2022-12-22 21:30 | 44917.8958 | 0 | 12.3949 | 37.78
2022-12-22 22:00 | 44917.9167 | 0 | 12.0069 | 37.78
2022-12-22 22:30 | 44917.9375 | 0 | 11.2393 | 37.78
2022-12-22 23:00 | 44917.9583 | 0 | 10.643 | 37.78
2022-12-22 23:30 | 44917.9792 | 0 | 10.2712 | 37.78
2022-12-23 | 44918 | 0 | 9.6828 | 37.78
2022-12-23 00:30 | 44918.0208 | 0 | 9.341 | 37.78
2022-12-23 01:00 | 44918.0417 | 0 | 9.1961 | 37.78
2022-12-23 01:30 | 44918.0625 | 0 | 9.0108 | 37.78
2022-12-23 02:00 | 44918.0833 | 0 | 8.8913 | 37.78
2022-12-23 02:30 | 44918.1042 | 0 | 8.8967 | 37.78
2022-12-23 03:00 | 44918.125 | 0 | 8.805 | 37.78
2022-12-23 03:30 | 44918.1458 | 0 | 8.8241 | 37.78
2022-12-23 04:00 | 44918.1667 | 0 | 9.0887 | 37.78
2022-12-23 04:30 | 44918.1875 | 0 | 9.2996 | 37.78
2022-12-23 05:00 | 44918.2083 | 0 | 9.5604 | 37.78
2022-12-23 05:30 | 44918.2292 | 0 | 9.6763 | 37.78
2022-12-23 06:00 | 44918.25 | 0 | 9.7257 | 37.78
2022-12-23 06:30 | 44918.2708 | 0 | 9.5441 | 37.78
2022-12-23 07:00 | 44918.2917 | 0 | 9.6361 | 37.78
2022-12-23 07:30 | 44918.3125 | 0 | 9.7331 | 37.78
2022-12-23 08:00 | 44918.3333 | 0 | 9.5786 | 37.78
2022-12-23 08:30 | 44918.3542 | 0 | 9.3041 | 37.78
2022-12-23 09:00 | 44918.375 | 0 | 8.8985 | 37.78
2022-12-23 09:30 | 44918.3958 | 0 | 10.179 | 37.78
2022-12-23 10:00 | 44918.4167 | 0 | 9.1762 | 37.78
2022-12-23 10:30 | 44918.4375 | 0 | 10.494 | 37.78
2022-12-23 11:00 | 44918.4583 | 0 | 9.5591 | 37.78
2022-12-23 11:30 | 44918.4792 | 0 | 9.308 | 37.78
2022-12-23 12:00 | 44918.5 | 0 | 9.0567 | 37.78
2022-12-23 12:30 | 44918.5208 | 0 | 9.4683 | 37.78
2022-12-23 13:00 | 44918.5417 | 0 | 11.6697 | 37.78
2022-12-23 13:30 | 44918.5625 | 0 | 10.4232 | 37.78
2022-12-23 14:00 | 44918.5833 | 0 | 12.1781 | 37.78
2022-12-23 14:30 | 44918.6042 | 0 | 11.4467 | 37.78
2022-12-23 15:00 | 44918.625 | 0 | 11.7784 | 37.78
2022-12-23 15:30 | 44918.6458 | 0 | 13.7137 | 37.78
2022-12-23 16:00 | 44918.6667 | 0 | 14.1884 | 37.78
2022-12-23 16:30 | 44918.6875 | 0 | 14.1556 | 37.78
2022-12-23 17:00 | 44918.7083 | 0 | 14.6851 | 37.78
2022-12-23 17:30 | 44918.7292 | 0 | 14.3703 | 37.78
2022-12-23 18:00 | 44918.75 | 0 | 14.1621 | 37.78
2022-12-23 18:30 | 44918.7708 | 0 | 14.1047 | 37.78
2022-12-23 19:00 | 44918.7917 | 0 | 14.2265 | 37.78
2022-12-23 19:30 | 44918.8125 | 0 | 13.8924 | 37.78
2022-12-23 20:00 | 44918.8333 | 0 | 13.7459 | 37.78
2022-12-23 20:30 | 44918.8542 | 0 | 13.5434 | 37.78
2022-12-23 21:00 | 44918.875 | 0 | 13.2052 | 37.78
2022-12-23 21:30 | 44918.8958 | 0 | 13.0253 | 37.78
2022-12-23 22:00 | 44918.9167 | 0 | 12.4987 | 37.78
2022-12-23 22:30 | 44918.9375 | 0 | 11.7996 | 37.78
2022-12-23 23:00 | 44918.9583 | 0 | 11.1342 | 37.78
2022-12-23 23:30 | 44918.9792 | 0 | 10.7968 | 37.78
2022-12-24 | 44919 | 0 | 10.1657 | 37.78
2022-12-24 00:30 | 44919.0208 | 0 | 9.7308 | 37.78
2022-12-24 01:00 | 44919.0417 | 0 | 9.6051 | 37.78
2022-12-24 01:30 | 44919.0625 | 0 | 9.327 | 37.78
2022-12-24 02:00 | 44919.0833 | 0 | 9.2332 | 37.78
2022-12-24 02:30 | 44919.1042 | 0 | 9.2669 | 37.78
2022-12-24 03:00 | 44919.125 | 0 | 9.0984 | 37.78
2022-12-24 03:30 | 44919.1458 | 0 | 9.1701 | 37.78
2022-12-24 04:00 | 44919.1667 | 0 | 9.0796 | 37.78
2022-12-24 04:30 | 44919.1875 | 0 | 9.0543 | 37.78
2022-12-24 05:00 | 44919.2083 | 0 | 9.0483 | 37.78
2022-12-24 05:30 | 44919.2292 | 0 | 8.9209 | 37.78
2022-12-24 06:00 | 44919.25 | 0 | 8.9801 | 37.78
2022-12-24 06:30 | 44919.2708 | 0 | 8.663 | 37.78
2022-12-24 07:00 | 44919.2917 | 0 | 9.1141 | 37.78
2022-12-24 07:30 | 44919.3125 | 0 | 9.8183 | 37.78
2022-12-24 08:00 | 44919.3333 | 0 | 10.3088 | 37.78
2022-12-24 08:30 | 44919.3542 | 0 | 10.9864 | 37.78
2022-12-24 09:00 | 44919.375 | 0 | 10.0874 | 37.78
2022-12-24 09:30 | 44919.3958 | 0 | 10.2229 | 37.78
2022-12-24 10:00 | 44919.4167 | 0 | 11.7393 | 37.78
2022-12-24 10:30 | 44919.4375 | 0 | 10.611 | 37.78
2022-12-24 11:00 | 44919.4583 | 0 | 10.5147 | 37.78
2022-12-24 11:30 | 44919.4792 | 0 | 11.3979 | 37.78
2022-12-24 12:00 | 44919.5 | 0 | 11.5971 | 37.78
2022-12-24 12:30 | 44919.5208 | 0 | 10.7797 | 37.78
2022-12-24 13:00 | 44919.5417 | 0 | 11.2829 | 37.78
2022-12-24 13:30 | 44919.5625 | 0 | 11.6824 | 37.78
2022-12-24 14:00 | 44919.5833 | 0 | 10.9001 | 37.78
2022-12-24 14:30 | 44919.6042 | 0 | 11.7945 | 37.78
2022-12-24 15:00 | 44919.625 | 0 | 12.2505 | 37.78
2022-12-24 15:30 | 44919.6458 | 0 | 12.5078 | 37.78
2022-12-24 16:00 | 44919.6667 | 0 | 12.0272 | 37.78
2022-12-24 16:30 | 44919.6875 | 0 | 12.2404 | 37.78
2022-12-24 17:00 | 44919.7083 | 0 | 12.4806 | 37.78
2022-12-24 17:30 | 44919.7292 | 0 | 12.1504 | 37.78
2022-12-24 18:00 | 44919.75 | 0 | 12.1835 | 37.78
2022-12-24 18:30 | 44919.7708 | 0 | 12.4359 | 37.78
2022-12-24 19:00 | 44919.7917 | 0 | 12.5209 | 37.78
2022-12-24 19:30 | 44919.8125 | 0 | 12.4178 | 37.78
2022-12-24 20:00 | 44919.8333 | 0 | 12.5167 | 37.78
2022-12-24 20:30 | 44919.8542 | 0 | 12.0403 | 37.78
2022-12-24 21:00 | 44919.875 | 0 | 12.076 | 37.78
2022-12-24 21:30 | 44919.8958 | 0 | 11.7202 | 37.78
2022-12-24 22:00 | 44919.9167 | 0 | 11.1082 | 37.78
2022-12-24 22:30 | 44919.9375 | 0 | 10.6589 | 37.78
2022-12-24 23:00 | 44919.9583 | 0 | 10.1252 | 37.78
2022-12-24 23:30 | 44919.9792 | 0 | 9.5763 | 37.78
2022-12-25 | 44920 | 0 | 9.1602 | 37.78
2022-12-25 00:30 | 44920.0208 | 0 | 8.7687 | 37.78
2022-12-25 01:00 | 44920.0417 | 0 | 8.5696 | 37.78
2022-12-25 01:30 | 44920.0625 | 0 | 8.3214 | 37.78
2022-12-25 02:00 | 44920.0833 | 0 | 8.2893 | 37.78
2022-12-25 02:30 | 44920.1042 | 0 | 8.0462 | 37.78
2022-12-25 03:00 | 44920.125 | 0 | 8.0719 | 37.78
2022-12-25 03:30 | 44920.1458 | 0 | 7.9615 | 37.78
2022-12-25 04:00 | 44920.1667 | 0 | 8.0612 | 37.78
2022-12-25 04:30 | 44920.1875 | 0 | 7.9537 | 37.78
2022-12-25 05:00 | 44920.2083 | 0 | 8.035 | 37.78
2022-12-25 05:30 | 44920.2292 | 0 | 8.0236 | 37.78
2022-12-25 06:00 | 44920.25 | 0 | 8.1255 | 37.78
2022-12-25 06:30 | 44920.2708 | 0 | 8.1496 | 37.78
2022-12-25 07:00 | 44920.2917 | 0 | 8.3101 | 37.78
2022-12-25 07:30 | 44920.3125 | 0 | 8.1439 | 37.78
2022-12-25 08:00 | 44920.3333 | 0 | 7.6429 | 37.78
2022-12-25 08:30 | 44920.3542 | 0 | 7.9789 | 37.78
2022-12-25 09:00 | 44920.375 | 0 | 8.3441 | 37.78
2022-12-25 09:30 | 44920.3958 | 0 | 8.5263 | 37.78
2022-12-25 10:00 | 44920.4167 | 0 | 9.2735 | 37.78
2022-12-25 10:30 | 44920.4375 | 0 | 10.1765 | 37.78
2022-12-25 11:00 | 44920.4583 | 0 | 11.0757 | 37.78
2022-12-25 11:30 | 44920.4792 | 0 | 12.3455 | 37.78
2022-12-25 12:00 | 44920.5 | 0 | 11.3392 | 37.78
2022-12-25 12:30 | 44920.5208 | 0 | 9.9584 | 37.78
2022-12-25 13:00 | 44920.5417 | 0 | 9.7651 | 37.78
2022-12-25 13:30 | 44920.5625 | 0 | 8.0111 | 37.78
2022-12-25 14:00 | 44920.5833 | 0 | 7.0306 | 37.78
2022-12-25 14:30 | 44920.6042 | 0 | 7.9251 | 37.78
2022-12-25 15:00 | 44920.625 | 0 | 7.6984 | 37.78
2022-12-25 15:30 | 44920.6458 | 0 | 8.6847 | 37.78
2022-12-25 16:00 | 44920.6667 | 0 | 10.0045 | 37.78
2022-12-25 16:30 | 44920.6875 | 0 | 10.7185 | 37.78
2022-12-25 17:00 | 44920.7083 | 0 | 10.5137 | 37.78
2022-12-25 17:30 | 44920.7292 | 0 | 10.5379 | 37.78
2022-12-25 18:00 | 44920.75 | 0 | 10.8852 | 37.78
2022-12-25 18:30 | 44920.7708 | 0 | 11.1294 | 37.78
2022-12-25 19:00 | 44920.7917 | 0 | 11.3829 | 37.78
2022-12-25 19:30 | 44920.8125 | 0 | 11.2437 | 37.78
2022-12-25 20:00 | 44920.8333 | 0 | 11.3185 | 37.78
2022-12-25 20:30 | 44920.8542 | 0 | 10.9697 | 37.78
2022-12-25 21:00 | 44920.875 | 0 | 10.9939 | 37.78
2022-12-25 21:30 | 44920.8958 | 0 | 10.6568 | 37.78
2022-12-25 22:00 | 44920.9167 | 0 | 10.3529 | 37.78
2022-12-25 22:30 | 44920.9375 | 0 | 9.9008 | 37.78
2022-12-25 23:00 | 44920.9583 | 0 | 9.3967 | 37.78
2022-12-25 23:30 | 44920.9792 | 0 | 8.9684 | 37.78
2022-12-26 | 44921 | 0 | 8.8044 | 37.78
2022-12-26 00:30 | 44921.0208 | 0 | 8.4426 | 37.78
2022-12-26 01:00 | 44921.0417 | 0 | 8.3561 | 37.78
2022-12-26 01:30 | 44921.0625 | 0 | 8.114 | 37.78
2022-12-26 02:00 | 44921.0833 | 0 | 8.0013 | 37.78
2022-12-26 02:30 | 44921.1042 | 0 | 8.149 | 37.78
2022-12-26 03:00 | 44921.125 | 0 | 7.8145 | 37.78
2022-12-26 03:30 | 44921.1458 | 0 | 7.831 | 37.78
2022-12-26 04:00 | 44921.1667 | 0 | 7.9823 | 37.78
2022-12-26 04:30 | 44921.1875 | 0 | 7.9552 | 37.78
2022-12-26 05:00 | 44921.2083 | 0 | 8.0311 | 37.78
2022-12-26 05:30 | 44921.2292 | 0 | 7.7747 | 37.78
2022-12-26 06:00 | 44921.25 | 0 | 7.558 | 37.78
2022-12-26 06:30 | 44921.2708 | 0 | 7.3215 | 37.78
2022-12-26 07:00 | 44921.2917 | 0 | 7.936 | 37.78
2022-12-26 07:30 | 44921.3125 | 0 | 7.8397 | 37.78
2022-12-26 08:00 | 44921.3333 | 0 | 7.0662 | 37.78
2022-12-26 08:30 | 44921.3542 | 0 | 6.5899 | 37.78
2022-12-26 09:00 | 44921.375 | 0 | 6.5405 | 37.78
2022-12-26 09:30 | 44921.3958 | 0 | 6.249 | 37.78
2022-12-26 10:00 | 44921.4167 | 0 | 6.6273 | 37.78
2022-12-26 10:30 | 44921.4375 | 0 | 7.6215 | 37.78
2022-12-26 11:00 | 44921.4583 | 0 | 8.6136 | 37.78
2022-12-26 11:30 | 44921.4792 | 0 | 8.3876 | 37.78
2022-12-26 12:00 | 44921.5 | 0 | 7.9542 | 37.78
2022-12-26 12:30 | 44921.5208 | 0 | 7.6331 | 37.78
2022-12-26 13:00 | 44921.5417 | 0 | 8.8199 | 37.78
2022-12-26 13:30 | 44921.5625 | 0 | 6.6884 | 37.78
2022-12-26 14:00 | 44921.5833 | 0 | 6.6107 | 37.78
2022-12-26 14:30 | 44921.6042 | 0 | 7.2344 | 37.78
2022-12-26 15:00 | 44921.625 | 0 | 8.2695 | 37.78
2022-12-26 15:30 | 44921.6458 | 0 | 8.7897 | 37.78
2022-12-26 16:00 | 44921.6667 | 0 | 10.2631 | 37.78
2022-12-26 16:30 | 44921.6875 | 0 | 10.7834 | 37.78
2022-12-26 17:00 | 44921.7083 | 0 | 10.8289 | 37.78
2022-12-26 17:30 | 44921.7292 | 0 | 11.5996 | 37.78
2022-12-26 18:00 | 44921.75 | 0 | 11.3596 | 37.78
2022-12-26 18:30 | 44921.7708 | 0 | 11.8857 | 37.78
2022-12-26 19:00 | 44921.7917 | 0 | 11.9445 | 37.78
2022-12-26 19:30 | 44921.8125 | 0 | 11.814 | 37.78
2022-12-26 20:00 | 44921.8333 | 0 | 11.6484 | 37.78
2022-12-26 20:30 | 44921.8542 | 0 | 11.1532 | 37.78
2022-12-26 21:00 | 44921.875 | 0 | 11.0218 | 37.78
2022-12-26 21:30 | 44921.8958 | 0 | 10.7944 | 37.78
2022-12-26 22:00 | 44921.9167 | 0 | 10.5425 | 37.78
2022-12-26 22:30 | 44921.9375 | 0 | 9.7781 | 37.78
2022-12-26 23:00 | 44921.9583 | 0 | 9.3871 | 37.78
2022-12-26 23:30 | 44921.9792 | 0 | 8.9815 | 37.78
2022-12-27 | 44922 | 0 | 8.585 | 37.78
2022-12-27 00:30 | 44922.0208 | 0 | 8.3471 | 37.78
2022-12-27 01:00 | 44922.0417 | 0 | 8.1019 | 37.78
2022-12-27 01:30 | 44922.0625 | 0 | 7.8554 | 37.78
2022-12-27 02:00 | 44922.0833 | 0 | 7.8379 | 37.78
2022-12-27 02:30 | 44922.1042 | 0 | 7.6741 | 37.78
2022-12-27 03:00 | 44922.125 | 0 | 7.7066 | 37.78
2022-12-27 03:30 | 44922.1458 | 0 | 7.6339 | 37.78
2022-12-27 04:00 | 44922.1667 | 0 | 7.8953 | 37.78
2022-12-27 04:30 | 44922.1875 | 0 | 7.9802 | 37.78
2022-12-27 05:00 | 44922.2083 | 0 | 8.0424 | 37.78
2022-12-27 05:30 | 44922.2292 | 0 | 7.6185 | 37.78
2022-12-27 06:00 | 44922.25 | 0 | 7.3808 | 37.78
2022-12-27 06:30 | 44922.2708 | 0 | 8.0658 | 37.78
2022-12-27 07:00 | 44922.2917 | 0 | 7.9981 | 37.78
2022-12-27 07:30 | 44922.3125 | 0 | 7.4334 | 37.78
2022-12-27 08:00 | 44922.3333 | 0 | 9.6617 | 37.78
2022-12-27 08:30 | 44922.3542 | 0 | 10.0947 | 37.78
2022-12-27 09:00 | 44922.375 | 0 | 10.0412 | 37.78
2022-12-27 09:30 | 44922.3958 | 0 | 8.5109 | 37.78
2022-12-27 10:00 | 44922.4167 | 0 | 7.2501 | 37.78
2022-12-27 10:30 | 44922.4375 | 0 | 8.6506 | 37.78
2022-12-27 11:00 | 44922.4583 | 0 | 5.8418 | 37.78
2022-12-27 11:30 | 44922.4792 | 0 | 6.9043 | 37.78
2022-12-27 12:00 | 44922.5 | 0 | 6.0934 | 37.78
2022-12-27 12:30 | 44922.5208 | 0 | 5.9325 | 37.78
2022-12-27 13:00 | 44922.5417 | 0 | 5.4255 | 37.78
2022-12-27 13:30 | 44922.5625 | 0 | 6.0165 | 37.78
2022-12-27 14:00 | 44922.5833 | 0 | 6.3226 | 37.78
2022-12-27 14:30 | 44922.6042 | 0 | 7.3291 | 37.78
2022-12-27 15:00 | 44922.625 | 0 | 7.3434 | 37.78
2022-12-27 15:30 | 44922.6458 | 0 | 8.5843 | 37.78
2022-12-27 16:00 | 44922.6667 | 0 | 9.1067 | 37.78
2022-12-27 16:30 | 44922.6875 | 0 | 10.4282 | 37.78
2022-12-27 17:00 | 44922.7083 | 0 | 10.9943 | 37.78
2022-12-27 17:30 | 44922.7292 | 0 | 10.7422 | 37.78
2022-12-27 18:00 | 44922.75 | 0 | 11.1791 | 37.78
2022-12-27 18:30 | 44922.7708 | 0 | 11.7709 | 37.78
2022-12-27 19:00 | 44922.7917 | 0 | 11.7964 | 37.78
2022-12-27 19:30 | 44922.8125 | 0 | 11.5847 | 37.78
2022-12-27 20:00 | 44922.8333 | 0 | 11.6591 | 37.78
2022-12-27 20:30 | 44922.8542 | 0 | 11.0109 | 37.78
2022-12-27 21:00 | 44922.875 | 0 | 10.8481 | 37.78
2022-12-27 21:30 | 44922.8958 | 0 | 10.4812 | 37.78
2022-12-27 22:00 | 44922.9167 | 0 | 10.1581 | 37.78
2022-12-27 22:30 | 44922.9375 | 0 | 9.6995 | 37.78
2022-12-27 23:00 | 44922.9583 | 0 | 9.1475 | 37.78
2022-12-27 23:30 | 44922.9792 | 0 | 8.843 | 37.78
2022-12-28 | 44923 | 0 | 8.3878 | 37.78
2022-12-28 00:30 | 44923.0208 | 0 | 8.0281 | 37.78
2022-12-28 01:00 | 44923.0417 | 0 | 8.1056 | 37.78
2022-12-28 01:30 | 44923.0625 | 0 | 7.8717 | 37.78
2022-12-28 02:00 | 44923.0833 | 0 | 7.9367 | 37.78
2022-12-28 02:30 | 44923.1042 | 0 | 7.9891 | 37.78
2022-12-28 03:00 | 44923.125 | 0 | 7.9528 | 37.78
2022-12-28 03:30 | 44923.1458 | 0 | 8.0275 | 37.78
2022-12-28 04:00 | 44923.1667 | 0 | 8.2234 | 37.78
2022-12-28 04:30 | 44923.1875 | 0 | 8.3033 | 37.78
2022-12-28 05:00 | 44923.2083 | 0 | 8.5472 | 37.78
2022-12-28 05:30 | 44923.2292 | 0 | 8.4835 | 37.78
2022-12-28 06:00 | 44923.25 | 0 | 8.6355 | 37.78
2022-12-28 06:30 | 44923.2708 | 0 | 8.8526 | 37.78
2022-12-28 07:00 | 44923.2917 | 0 | 8.369 | 37.78
2022-12-28 07:30 | 44923.3125 | 0 | 10.1956 | 37.78
2022-12-28 08:00 | 44923.3333 | 0 | 10.3612 | 37.78
2022-12-28 08:30 | 44923.3542 | 0 | 10.4837 | 37.78
2022-12-28 09:00 | 44923.375 | 0 | 8.289 | 37.78
2022-12-28 09:30 | 44923.3958 | 0 | 9.3195 | 37.78
2022-12-28 10:00 | 44923.4167 | 0 | 9.3548 | 37.78
2022-12-28 10:30 | 44923.4375 | 0 | 8.0821 | 37.78
2022-12-28 11:00 | 44923.4583 | 0 | 8.6128 | 37.78
2022-12-28 11:30 | 44923.4792 | 0 | 8.6514 | 37.78
2022-12-28 12:00 | 44923.5 | 0 | 9.1328 | 37.78
2022-12-28 12:30 | 44923.5208 | 0 | 9.1301 | 37.78
2022-12-28 13:00 | 44923.5417 | 0 | 9.5811 | 37.78
2022-12-28 13:30 | 44923.5625 | 0 | 8.9784 | 37.78
2022-12-28 14:00 | 44923.5833 | 0 | 10.4221 | 37.78
2022-12-28 14:30 | 44923.6042 | 0 | 9.4258 | 37.78
2022-12-28 15:00 | 44923.625 | 0 | 10.1449 | 37.78
2022-12-28 15:30 | 44923.6458 | 0 | 11.162 | 37.78
2022-12-28 16:00 | 44923.6667 | 0 | 11.1674 | 37.78
2022-12-28 16:30 | 44923.6875 | 0 | 12.3473 | 37.78
2022-12-28 17:00 | 44923.7083 | 0 | 12.6817 | 37.78
2022-12-28 17:30 | 44923.7292 | 0 | 13.1888 | 37.78
2022-12-28 18:00 | 44923.75 | 0 | 13.0295 | 37.78
2022-12-28 18:30 | 44923.7708 | 0 | 13.05 | 37.78
2022-12-28 19:00 | 44923.7917 | 0 | 13.2858 | 37.78
2022-12-28 19:30 | 44923.8125 | 0 | 13.109 | 37.78
2022-12-28 20:00 | 44923.8333 | 0 | 13.0726 | 37.78
2022-12-28 20:30 | 44923.8542 | 0 | 12.5923 | 37.78
2022-12-28 21:00 | 44923.875 | 0 | 12.188 | 37.78
2022-12-28 21:30 | 44923.8958 | 0 | 11.9137 | 37.78
2022-12-28 22:00 | 44923.9167 | 0 | 11.3503 | 37.78
2022-12-28 22:30 | 44923.9375 | 0 | 10.7145 | 37.78
2022-12-28 23:00 | 44923.9583 | 0 | 10.0686 | 37.78
2022-12-28 23:30 | 44923.9792 | 0 | 9.7787 | 37.78
2022-12-29 | 44924 | 0 | 9.3412 | 37.78
2022-12-29 00:30 | 44924.0208 | 0 | 8.8589 | 37.78
2022-12-29 01:00 | 44924.0417 | 0 | 8.6954 | 37.78
2022-12-29 01:30 | 44924.0625 | 0 | 8.5793 | 37.78
2022-12-29 02:00 | 44924.0833 | 0 | 8.4539 | 37.78
2022-12-29 02:30 | 44924.1042 | 0 | 8.3497 | 37.78
2022-12-29 03:00 | 44924.125 | 0 | 8.3575 | 37.78
2022-12-29 03:30 | 44924.1458 | 0 | 8.4492 | 37.78
2022-12-29 04:00 | 44924.1667 | 0 | 8.5841 | 37.78
2022-12-29 04:30 | 44924.1875 | 0 | 8.7082 | 37.78
2022-12-29 05:00 | 44924.2083 | 0 | 8.8717 | 37.78
2022-12-29 05:30 | 44924.2292 | 0 | 8.802 | 37.78
2022-12-29 06:00 | 44924.25 | 0 | 8.6683 | 37.78
2022-12-29 06:30 | 44924.2708 | 0 | 8.3646 | 37.78
2022-12-29 07:00 | 44924.2917 | 0 | 8.2302 | 37.78
2022-12-29 07:30 | 44924.3125 | 0 | 7.8604 | 37.78
2022-12-29 08:00 | 44924.3333 | 0 | 9.0171 | 37.78
2022-12-29 08:30 | 44924.3542 | 0 | 11.0236 | 37.78
2022-12-29 09:00 | 44924.375 | 0 | 11.7153 | 37.78
2022-12-29 09:30 | 44924.3958 | 0 | 10.6407 | 37.78
2022-12-29 10:00 | 44924.4167 | 0 | 10.6785 | 37.78
2022-12-29 10:30 | 44924.4375 | 0 | 10.0352 | 37.78
2022-12-29 11:00 | 44924.4583 | 0 | 10.5577 | 37.78
2022-12-29 11:30 | 44924.4792 | 0 | 10.1947 | 37.78
2022-12-29 12:00 | 44924.5 | 0 | 10.6733 | 37.78
2022-12-29 12:30 | 44924.5208 | 0 | 10.8705 | 37.78
2022-12-29 13:00 | 44924.5417 | 0 | 9.9994 | 37.78
2022-12-29 13:30 | 44924.5625 | 0 | 9.8555 | 37.78
2022-12-29 14:00 | 44924.5833 | 0 | 9.123 | 37.78
2022-12-29 14:30 | 44924.6042 | 0 | 10.1997 | 37.78
2022-12-29 15:00 | 44924.625 | 0 | 12.0154 | 37.78
2022-12-29 15:30 | 44924.6458 | 0 | 12.7007 | 37.78
2022-12-29 16:00 | 44924.6667 | 0 | 13.1107 | 37.78
2022-12-29 16:30 | 44924.6875 | 0 | 13.4522 | 37.78
2022-12-29 17:00 | 44924.7083 | 0 | 13.2244 | 37.78
2022-12-29 17:30 | 44924.7292 | 0 | 13.234 | 37.78
2022-12-29 18:00 | 44924.75 | 0 | 13.1912 | 37.78
2022-12-29 18:30 | 44924.7708 | 0 | 13.3987 | 37.78
2022-12-29 19:00 | 44924.7917 | 0 | 13.5477 | 37.78
2022-12-29 19:30 | 44924.8125 | 0 | 13.3302 | 37.78
2022-12-29 20:00 | 44924.8333 | 0 | 13.0827 | 37.78
2022-12-29 20:30 | 44924.8542 | 0 | 12.7303 | 37.78
2022-12-29 21:00 | 44924.875 | 0 | 12.4596 | 37.78
2022-12-29 21:30 | 44924.8958 | 0 | 12.2341 | 37.78
2022-12-29 22:00 | 44924.9167 | 0 | 11.7126 | 37.78
2022-12-29 22:30 | 44924.9375 | 0 | 10.8921 | 37.78
2022-12-29 23:00 | 44924.9583 | 0 | 10.6032 | 37.78
2022-12-29 23:30 | 44924.9792 | 0 | 10.2533 | 37.78
2022-12-30 | 44925 | 0 | 9.7188 | 37.78
2022-12-30 00:30 | 44925.0208 | 0 | 9.4351 | 37.78
2022-12-30 01:00 | 44925.0417 | 0 | 9.2737 | 37.78
2022-12-30 01:30 | 44925.0625 | 0 | 8.9322 | 37.78
2022-12-30 02:00 | 44925.0833 | 0 | 8.9203 | 37.78
2022-12-30 02:30 | 44925.1042 | 0 | 8.8574 | 37.78
2022-12-30 03:00 | 44925.125 | 0 | 8.8276 | 37.78
2022-12-30 03:30 | 44925.1458 | 0 | 8.8811 | 37.78
2022-12-30 04:00 | 44925.1667 | 0 | 9.0039 | 37.78
2022-12-30 04:30 | 44925.1875 | 0 | 9.1394 | 37.78
2022-12-30 05:00 | 44925.2083 | 0 | 9.3978 | 37.78
2022-12-30 05:30 | 44925.2292 | 0 | 9.3636 | 37.78
2022-12-30 06:00 | 44925.25 | 0 | 9.4297 | 37.78
2022-12-30 06:30 | 44925.2708 | 0 | 10.05 | 37.78
2022-12-30 07:00 | 44925.2917 | 0 | 10.0714 | 37.78
2022-12-30 07:30 | 44925.3125 | 0 | 10.6594 | 37.78
2022-12-30 08:00 | 44925.3333 | 0 | 11.792 | 37.78
2022-12-30 08:30 | 44925.3542 | 0 | 11.4287 | 37.78
2022-12-30 09:00 | 44925.375 | 0 | 10.3823 | 37.78
2022-12-30 09:30 | 44925.3958 | 0 | 9.6209 | 37.78
2022-12-30 10:00 | 44925.4167 | 0 | 10.4861 | 37.78
2022-12-30 10:30 | 44925.4375 | 0 | 11.6008 | 37.78
2022-12-30 11:00 | 44925.4583 | 0 | 9.9988 | 37.78
2022-12-30 11:30 | 44925.4792 | 0 | 9.1913 | 37.78
2022-12-30 12:00 | 44925.5 | 0 | 10.6114 | 37.78
2022-12-30 12:30 | 44925.5208 | 0 | 9.0286 | 37.78
2022-12-30 13:00 | 44925.5417 | 0 | 10.1024 | 37.78
2022-12-30 13:30 | 44925.5625 | 0 | 10.7493 | 37.78
2022-12-30 14:00 | 44925.5833 | 0 | 11.442 | 37.78
2022-12-30 14:30 | 44925.6042 | 0 | 11.3535 | 37.78
2022-12-30 15:00 | 44925.625 | 0 | 10.6584 | 37.78
2022-12-30 15:30 | 44925.6458 | 0 | 12.3695 | 37.78
2022-12-30 16:00 | 44925.6667 | 0 | 12.0046 | 37.78
2022-12-30 16:30 | 44925.6875 | 0 | 12.7254 | 37.78
2022-12-30 17:00 | 44925.7083 | 0 | 12.682 | 37.78
2022-12-30 17:30 | 44925.7292 | 0 | 12.6855 | 37.78
2022-12-30 18:00 | 44925.75 | 0 | 12.7257 | 37.78
2022-12-30 18:30 | 44925.7708 | 0 | 12.9108 | 37.78
2022-12-30 19:00 | 44925.7917 | 0 | 12.7382 | 37.78
2022-12-30 19:30 | 44925.8125 | 0 | 12.5721 | 37.78
2022-12-30 20:00 | 44925.8333 | 0 | 12.4622 | 37.78
2022-12-30 20:30 | 44925.8542 | 0 | 12.1424 | 37.78
2022-12-30 21:00 | 44925.875 | 0 | 11.9753 | 37.78
2022-12-30 21:30 | 44925.8958 | 0 | 11.6049 | 37.78
2022-12-30 22:00 | 44925.9167 | 0 | 11.1749 | 37.78
2022-12-30 22:30 | 44925.9375 | 0 | 10.6238 | 37.78
2022-12-30 23:00 | 44925.9583 | 0 | 10.374 | 37.78
2022-12-30 23:30 | 44925.9792 | 0 | 9.951 | 37.78
2022-12-31 | 44926 | 0 | 9.3202 | 37.78
2022-12-31 00:30 | 44926.0208 | 0 | 8.9615 | 37.78
2022-12-31 01:00 | 44926.0417 | 0 | 8.9593 | 37.78
2022-12-31 01:30 | 44926.0625 | 0 | 8.6481 | 37.78
2022-12-31 02:00 | 44926.0833 | 0 | 8.5978 | 37.78
2022-12-31 02:30 | 44926.1042 | 0 | 8.632 | 37.78
2022-12-31 03:00 | 44926.125 | 0 | 8.5978 | 37.78
2022-12-31 03:30 | 44926.1458 | 0 | 8.643 | 37.78
2022-12-31 04:00 | 44926.1667 | 0 | 8.6737 | 37.78
2022-12-31 04:30 | 44926.1875 | 0 | 8.6526 | 37.78
2022-12-31 05:00 | 44926.2083 | 0 | 8.562 | 37.78
2022-12-31 05:30 | 44926.2292 | 0 | 8.417 | 37.78
2022-12-31 06:00 | 44926.25 | 0 | 7.8533 | 37.78
2022-12-31 06:30 | 44926.2708 | 0 | 7.0513 | 37.78
2022-12-31 07:00 | 44926.2917 | 0 | 7.1549 | 37.78
2022-12-31 07:30 | 44926.3125 | 0 | 7.5362 | 37.78
2022-12-31 08:00 | 44926.3333 | 0 | 8.6339 | 37.78
2022-12-31 08:30 | 44926.3542 | 0 | 9.6014 | 37.78
2022-12-31 09:00 | 44926.375 | 0 | 7.3935 | 37.78
2022-12-31 09:30 | 44926.3958 | 0 | 9.5895 | 37.78
2022-12-31 10:00 | 44926.4167 | 0 | 9.9307 | 37.78
2022-12-31 10:30 | 44926.4375 | 0 | 7.3913 | 37.78
2022-12-31 11:00 | 44926.4583 | 0 | 6.9914 | 37.78
2022-12-31 11:30 | 44926.4792 | 0 | 6.8523 | 37.78
2022-12-31 12:00 | 44926.5 | 0 | 6.614 | 37.78
2022-12-31 12:30 | 44926.5208 | 0 | 6.842 | 37.78
2022-12-31 13:00 | 44926.5417 | 0 | 7.7311 | 37.78
2022-12-31 13:30 | 44926.5625 | 0 | 7.9746 | 37.78
2022-12-31 14:00 | 44926.5833 | 0 | 8.861 | 37.78
2022-12-31 14:30 | 44926.6042 | 0 | 9.1849 | 37.78
2022-12-31 15:00 | 44926.625 | 0 | 9.0587 | 37.78
2022-12-31 15:30 | 44926.6458 | 0 | 10.0703 | 37.78
2022-12-31 16:00 | 44926.6667 | 0 | 10.6143 | 37.78
2022-12-31 16:30 | 44926.6875 | 0 | 10.7771 | 37.78
2022-12-31 17:00 | 44926.7083 | 0 | 11.2452 | 37.78
2022-12-31 17:30 | 44926.7292 | 0 | 11.4986 | 37.78
2022-12-31 18:00 | 44926.75 | 0 | 11.7662 | 37.78
2022-12-31 18:30 | 44926.7708 | 0 | 11.7916 | 37.78
2022-12-31 19:00 | 44926.7917 | 0 | 11.5844 | 37.78
2022-12-31 19:30 | 44926.8125 | 0 | 11.4111 | 37.78
2022-12-31 20:00 | 44926.8333 | 0 | 11.2682 | 37.78
2022-12-31 20:30 | 44926.8542 | 0 | 10.6813 | 37.78
2022-12-31 21:00 | 44926.875 | 0 | 10.6417 | 37.78
2022-12-31 21:30 | 44926.8958 | 0 | 10.5214 | 37.78
2022-12-31 22:00 | 44926.9167 | 0 | 10.0834 | 37.78
2022-12-31 22:30 | 44926.9375 | 0 | 9.6468 | 37.78
2022-12-31 23:00 | 44926.9583 | 0 | 9.373 | 37.78
2022-12-31 23:30 | 44926.9792 | 0 | 9.0614 | 37.78
2023-01-01 | 44927 | 0 | 8.7156 | 37.78
2023-01-01 00:30 | 44927.0208 | 0 | 8.4004 | 37.78
2023-01-01 01:00 | 44927.0417 | 0 | 8.387 | 37.78
2023-01-01 01:30 | 44927.0625 | 0 | 8.2428 | 37.78
2023-01-01 02:00 | 44927.0833 | 0 | 8.0917 | 37.78
2023-01-01 02:30 | 44927.1042 | 0 | 7.8682 | 37.78
2023-01-01 03:00 | 44927.125 | 0 | 7.8983 | 37.78
2023-01-01 03:30 | 44927.1458 | 0 | 7.7852 | 37.78
2023-01-01 04:00 | 44927.1667 | 0 | 7.6714 | 37.78
2023-01-01 04:30 | 44927.1875 | 0 | 7.616 | 37.78
2023-01-01 05:00 | 44927.2083 | 0 | 7.434 | 37.78
2023-01-01 05:30 | 44927.2292 | 0 | 7.1152 | 37.78
2023-01-01 06:00 | 44927.25 | 0 | 6.7653 | 37.78
2023-01-01 06:30 | 44927.2708 | 0 | 7.0402 | 37.78
2023-01-01 07:00 | 44927.2917 | 0 | 5.7216 | 37.78
2023-01-01 07:30 | 44927.3125 | 0 | 5.5367 | 37.78
2023-01-01 08:00 | 44927.3333 | 0 | 5.5632 | 37.78
2023-01-01 08:30 | 44927.3542 | 0 | 6.7056 | 37.78
2023-01-01 09:00 | 44927.375 | 0 | 8.2204 | 37.78
2023-01-01 09:30 | 44927.3958 | 0 | 7.3837 | 37.78
2023-01-01 10:00 | 44927.4167 | 0 | 7.7173 | 37.78
2023-01-01 10:30 | 44927.4375 | 0 | 6.423 | 37.78
2023-01-01 11:00 | 44927.4583 | 0 | 6.3216 | 37.78
2023-01-01 11:30 | 44927.4792 | 0 | 8.3676 | 37.78
2023-01-01 12:00 | 44927.5 | 0 | 8.2675 | 37.78
2023-01-01 12:30 | 44927.5208 | 0 | 8.2457 | 37.78
2023-01-01 13:00 | 44927.5417 | 0 | 8.2308 | 37.78
2023-01-01 13:30 | 44927.5625 | 0 | 7.5249 | 37.78
2023-01-01 14:00 | 44927.5833 | 0 | 8.7078 | 37.78
2023-01-01 14:30 | 44927.6042 | 0 | 8.6627 | 37.78
2023-01-01 15:00 | 44927.625 | 0 | 8.5828 | 37.78
2023-01-01 15:30 | 44927.6458 | 0 | 9.4553 | 37.78
2023-01-01 16:00 | 44927.6667 | 0 | 9.7045 | 37.78
2023-01-01 16:30 | 44927.6875 | 0 | 9.0381 | 37.78
2023-01-01 17:00 | 44927.7083 | 0 | 10.162 | 37.78
2023-01-01 17:30 | 44927.7292 | 0 | 10.7429 | 37.78
2023-01-01 18:00 | 44927.75 | 0 | 10.887 | 37.78
2023-01-01 18:30 | 44927.7708 | 0 | 11.1351 | 37.78
2023-01-01 19:00 | 44927.7917 | 0 | 11.3952 | 37.78
2023-01-01 19:30 | 44927.8125 | 0 | 11.3051 | 37.78
2023-01-01 20:00 | 44927.8333 | 0 | 11.0609 | 37.78
2023-01-01 20:30 | 44927.8542 | 0 | 10.7885 | 37.78
2023-01-01 21:00 | 44927.875 | 0 | 10.3646 | 37.78
2023-01-01 21:30 | 44927.8958 | 0 | 10.2423 | 37.78
2023-01-01 22:00 | 44927.9167 | 0 | 9.877 | 37.78
2023-01-01 22:30 | 44927.9375 | 0 | 9.2457 | 37.78
2023-01-01 23:00 | 44927.9583 | 0 | 8.7481 | 37.78
2023-01-01 23:30 | 44927.9792 | 0 | 8.389 | 37.78
2023-01-02 | 44928 | 0 | 8.1114 | 37.78
2023-01-02 00:30 | 44928.0208 | 0 | 7.8659 | 37.78
2023-01-02 01:00 | 44928.0417 | 0 | 7.7229 | 37.78
2023-01-02 01:30 | 44928.0625 | 0 | 7.5374 | 37.78
2023-01-02 02:00 | 44928.0833 | 0 | 7.4665 | 37.78
2023-01-02 02:30 | 44928.1042 | 0 | 7.6023 | 37.78
2023-01-02 03:00 | 44928.125 | 0 | 7.477 | 37.78
2023-01-02 03:30 | 44928.1458 | 0 | 7.457 | 37.78
2023-01-02 04:00 | 44928.1667 | 0 | 7.6795 | 37.78
2023-01-02 04:30 | 44928.1875 | 0 | 7.6783 | 37.78
2023-01-02 05:00 | 44928.2083 | 0 | 7.6911 | 37.78
2023-01-02 05:30 | 44928.2292 | 0 | 7.4526 | 37.78
2023-01-02 06:00 | 44928.25 | 0 | 7.3118 | 37.78
2023-01-02 06:30 | 44928.2708 | 0 | 6.9561 | 37.78
2023-01-02 07:00 | 44928.2917 | 0 | 6.7969 | 37.78
2023-01-02 07:30 | 44928.3125 | 0 | 6.9036 | 37.78
2023-01-02 08:00 | 44928.3333 | 0 | 7.986 | 37.78
2023-01-02 08:30 | 44928.3542 | 0 | 7.3495 | 37.78
2023-01-02 09:00 | 44928.375 | 0 | 7.5348 | 37.78
2023-01-02 09:30 | 44928.3958 | 0 | 7.4308 | 37.78
2023-01-02 10:00 | 44928.4167 | 0 | 6.9078 | 37.78
2023-01-02 10:30 | 44928.4375 | 0 | 6.8838 | 37.78
2023-01-02 11:00 | 44928.4583 | 0 | 6.9844 | 37.78
2023-01-02 11:30 | 44928.4792 | 0 | 8.0904 | 37.78
2023-01-02 12:00 | 44928.5 | 0 | 8.7052 | 37.78
2023-01-02 12:30 | 44928.5208 | 0 | 9.0115 | 37.78
2023-01-02 13:00 | 44928.5417 | 0 | 9.0868 | 37.78
2023-01-02 13:30 | 44928.5625 | 0 | 7.3575 | 37.78
2023-01-02 14:00 | 44928.5833 | 0 | 10.2318 | 37.78
2023-01-02 14:30 | 44928.6042 | 0 | 9.6152 | 37.78
2023-01-02 15:00 | 44928.625 | 0 | 8.609 | 37.78
2023-01-02 15:30 | 44928.6458 | 0 | 8.6905 | 37.78
2023-01-02 16:00 | 44928.6667 | 0 | 9.4435 | 37.78
2023-01-02 16:30 | 44928.6875 | 0 | 10.5869 | 37.78
2023-01-02 17:00 | 44928.7083 | 0 | 11.7477 | 37.78
2023-01-02 17:30 | 44928.7292 | 0 | 11.9334 | 37.78
2023-01-02 18:00 | 44928.75 | 0 | 12.1231 | 37.78
2023-01-02 18:30 | 44928.7708 | 0 | 12.4656 | 37.78
2023-01-02 19:00 | 44928.7917 | 0 | 12.4521 | 37.78
2023-01-02 19:30 | 44928.8125 | 0 | 12.1621 | 37.78
2023-01-02 20:00 | 44928.8333 | 0 | 12.0776 | 37.78
2023-01-02 20:30 | 44928.8542 | 0 | 11.6401 | 37.78
2023-01-02 21:00 | 44928.875 | 0 | 11.161 | 37.78
2023-01-02 21:30 | 44928.8958 | 0 | 10.8403 | 37.78
2023-01-02 22:00 | 44928.9167 | 0 | 10.2763 | 37.78
2023-01-02 22:30 | 44928.9375 | 0 | 9.7453 | 37.78
2023-01-02 23:00 | 44928.9583 | 0 | 9.3749 | 37.78
2023-01-02 23:30 | 44928.9792 | 0 | 9.0281 | 37.78
2023-01-03 | 44929 | 0 | 8.4731 | 37.78
2023-01-03 00:30 | 44929.0208 | 0 | 8.1386 | 37.78
2023-01-03 01:00 | 44929.0417 | 0 | 7.9659 | 37.78
2023-01-03 01:30 | 44929.0625 | 0 | 7.7295 | 37.78
2023-01-03 02:00 | 44929.0833 | 0 | 7.7369 | 37.78
2023-01-03 02:30 | 44929.1042 | 0 | 7.8319 | 37.78
2023-01-03 03:00 | 44929.125 | 0 | 7.6953 | 37.78
2023-01-03 03:30 | 44929.1458 | 0 | 7.9195 | 37.78
2023-01-03 04:00 | 44929.1667 | 0 | 8.1363 | 37.78
2023-01-03 04:30 | 44929.1875 | 0 | 8.4977 | 37.78
2023-01-03 05:00 | 44929.2083 | 0 | 8.7065 | 37.78
2023-01-03 05:30 | 44929.2292 | 0 | 8.855 | 37.78
2023-01-03 06:00 | 44929.25 | 0 | 9.0822 | 37.78
2023-01-03 06:30 | 44929.2708 | 0 | 9.112 | 37.78
2023-01-03 07:00 | 44929.2917 | 0 | 9.1814 | 37.78
2023-01-03 07:30 | 44929.3125 | 0 | 8.9786 | 37.78
2023-01-03 08:00 | 44929.3333 | 0 | 9.2668 | 37.78
2023-01-03 08:30 | 44929.3542 | 0 | 9.0724 | 37.78
2023-01-03 09:00 | 44929.375 | 0 | 8.992 | 37.78
2023-01-03 09:30 | 44929.3958 | 0 | 9.02 | 37.78
2023-01-03 10:00 | 44929.4167 | 0 | 9.0117 | 37.78
2023-01-03 10:30 | 44929.4375 | 0 | 9.3089 | 37.78
2023-01-03 11:00 | 44929.4583 | 0 | 9.8079 | 37.78
2023-01-03 11:30 | 44929.4792 | 0 | 9.7903 | 37.78
2023-01-03 12:00 | 44929.5 | 0 | 9.7808 | 37.78
2023-01-03 12:30 | 44929.5208 | 0 | 9.9374 | 37.78
2023-01-03 13:00 | 44929.5417 | 0 | 13.3474 | 37.78
2023-01-03 13:30 | 44929.5625 | 0 | 13.4611 | 37.78
2023-01-03 14:00 | 44929.5833 | 0 | 11.3109 | 37.78
2023-01-03 14:30 | 44929.6042 | 0 | 11.3217 | 37.78
2023-01-03 15:00 | 44929.625 | 0 | 12.095 | 37.78
2023-01-03 15:30 | 44929.6458 | 0 | 12.7403 | 37.78
2023-01-03 16:00 | 44929.6667 | 0 | 13.3455 | 37.78
2023-01-03 16:30 | 44929.6875 | 0 | 14.1566 | 37.78
2023-01-03 17:00 | 44929.7083 | 0 | 14.4929 | 37.78
2023-01-03 17:30 | 44929.7292 | 0 | 14.9483 | 37.78
2023-01-03 18:00 | 44929.75 | 0 | 15.0281 | 37.78
2023-01-03 18:30 | 44929.7708 | 0 | 15.2763 | 37.78
2023-01-03 19:00 | 44929.7917 | 0 | 15.2496 | 37.78
2023-01-03 19:30 | 44929.8125 | 0 | 15.0981 | 37.78
2023-01-03 20:00 | 44929.8333 | 0 | 14.819 | 37.78
2023-01-03 20:30 | 44929.8542 | 0 | 14.3053 | 37.78
2023-01-03 21:00 | 44929.875 | 0 | 13.8936 | 37.78
2023-01-03 21:30 | 44929.8958 | 0 | 13.4936 | 37.78
2023-01-03 22:00 | 44929.9167 | 0 | 12.837 | 37.78
2023-01-03 22:30 | 44929.9375 | 0 | 12.0153 | 37.78
2023-01-03 23:00 | 44929.9583 | 0 | 11.6171 | 37.78
2023-01-03 23:30 | 44929.9792 | 0 | 10.9853 | 37.78
2023-01-04 | 44930 | 0 | 10.3367 | 37.78
2023-01-04 00:30 | 44930.0208 | 0 | 10.0015 | 37.78
2023-01-04 01:00 | 44930.0417 | 0 | 9.7278 | 37.78
2023-01-04 01:30 | 44930.0625 | 0 | 9.3691 | 37.78
2023-01-04 02:00 | 44930.0833 | 0 | 9.3563 | 37.78
2023-01-04 02:30 | 44930.1042 | 0 | 9.2663 | 37.78
2023-01-04 03:00 | 44930.125 | 0 | 9.1999 | 37.78
2023-01-04 03:30 | 44930.1458 | 0 | 9.3056 | 37.78
2023-01-04 04:00 | 44930.1667 | 0 | 9.3342 | 37.78
2023-01-04 04:30 | 44930.1875 | 0 | 9.4455 | 37.78
2023-01-04 05:00 | 44930.2083 | 0 | 9.8112 | 37.78
2023-01-04 05:30 | 44930.2292 | 0 | 9.8749 | 37.78
2023-01-04 06:00 | 44930.25 | 0 | 10.1736 | 37.78
2023-01-04 06:30 | 44930.2708 | 0 | 10.1509 | 37.78
2023-01-04 07:00 | 44930.2917 | 0 | 10.6087 | 37.78
2023-01-04 07:30 | 44930.3125 | 0 | 10.4094 | 37.78
2023-01-04 08:00 | 44930.3333 | 0 | 10.7637 | 37.78
2023-01-04 08:30 | 44930.3542 | 0 | 10.7917 | 37.78
2023-01-04 09:00 | 44930.375 | 0 | 10.9052 | 37.78
2023-01-04 09:30 | 44930.3958 | 0 | 11.1312 | 37.78
2023-01-04 10:00 | 44930.4167 | 0 | 11.2247 | 37.78
2023-01-04 10:30 | 44930.4375 | 0 | 11.498 | 37.78
2023-01-04 11:00 | 44930.4583 | 0 | 11.5722 | 37.78
2023-01-04 11:30 | 44930.4792 | 0 | 11.8964 | 37.78
2023-01-04 12:00 | 44930.5 | 0 | 12.1484 | 37.78
2023-01-04 12:30 | 44930.5208 | 0 | 12.4486 | 37.78
2023-01-04 13:00 | 44930.5417 | 0 | 13.2845 | 37.78
2023-01-04 13:30 | 44930.5625 | 0 | 14.6171 | 37.78
2023-01-04 14:00 | 44930.5833 | 0 | 15.6378 | 37.78
2023-01-04 14:30 | 44930.6042 | 0 | 14.7085 | 37.78
2023-01-04 15:00 | 44930.625 | 0 | 16.9917 | 37.78
2023-01-04 15:30 | 44930.6458 | 0 | 17.8588 | 37.78
2023-01-04 16:00 | 44930.6667 | 0 | 17.3592 | 37.78
2023-01-04 16:30 | 44930.6875 | 0 | 17.9972 | 37.78
2023-01-04 17:00 | 44930.7083 | 0 | 18.2231 | 37.78
2023-01-04 17:30 | 44930.7292 | 0 | 17.8575 | 37.78
2023-01-04 18:00 | 44930.75 | 0 | 17.5101 | 37.78
2023-01-04 18:30 | 44930.7708 | 0 | 17.5109 | 37.78
2023-01-04 19:00 | 44930.7917 | 0 | 17.5386 | 37.78
2023-01-04 19:30 | 44930.8125 | 0 | 17.4305 | 37.78
2023-01-04 20:00 | 44930.8333 | 0 | 17.1437 | 37.78
2023-01-04 20:30 | 44930.8542 | 0 | 16.5292 | 37.78
2023-01-04 21:00 | 44930.875 | 0 | 15.9147 | 37.78
2023-01-04 21:30 | 44930.8958 | 0 | 14.946 | 37.78
2023-01-04 22:00 | 44930.9167 | 0 | 14.0322 | 37.78
2023-01-04 22:30 | 44930.9375 | 0 | 13.0185 | 37.78
2023-01-04 23:00 | 44930.9583 | 0 | 12.1933 | 37.78
2023-01-04 23:30 | 44930.9792 | 0 | 11.8298 | 37.78
2023-01-05 | 44931 | 0 | 11.0648 | 37.78
2023-01-05 00:30 | 44931.0208 | 0 | 10.4883 | 37.78
2023-01-05 01:00 | 44931.0417 | 0 | 10.3528 | 37.78
2023-01-05 01:30 | 44931.0625 | 0 | 10.1646 | 37.78
2023-01-05 02:00 | 44931.0833 | 0 | 10.0434 | 37.78
2023-01-05 02:30 | 44931.1042 | 0 | 10.0134 | 37.78
2023-01-05 03:00 | 44931.125 | 0 | 9.8633 | 37.78
2023-01-05 03:30 | 44931.1458 | 0 | 9.9074 | 37.78
2023-01-05 04:00 | 44931.1667 | 0 | 10.0926 | 37.78
2023-01-05 04:30 | 44931.1875 | 0 | 10.2745 | 37.78
2023-01-05 05:00 | 44931.2083 | 0 | 10.7784 | 37.78
2023-01-05 05:30 | 44931.2292 | 0 | 10.8215 | 37.78
2023-01-05 06:00 | 44931.25 | 0 | 11.3633 | 37.78
2023-01-05 06:30 | 44931.2708 | 0 | 11.909 | 37.78
2023-01-05 07:00 | 44931.2917 | 0 | 12.4083 | 37.78
2023-01-05 07:30 | 44931.3125 | 0 | 12.1835 | 37.78
2023-01-05 08:00 | 44931.3333 | 0 | 12.9234 | 37.78
2023-01-05 08:30 | 44931.3542 | 0 | 13.4139 | 37.78
2023-01-05 09:00 | 44931.375 | 0 | 13.4548 | 37.78
2023-01-05 09:30 | 44931.3958 | 0 | 13.4927 | 37.78
2023-01-05 10:00 | 44931.4167 | 0 | 13.2998 | 37.78
2023-01-05 10:30 | 44931.4375 | 0 | 13.7096 | 37.78
2023-01-05 11:00 | 44931.4583 | 0 | 13.4386 | 37.78
2023-01-05 11:30 | 44931.4792 | 0 | 13.497 | 37.78
2023-01-05 12:00 | 44931.5 | 0 | 13.9797 | 37.78
2023-01-05 12:30 | 44931.5208 | 0 | 12.7716 | 37.78
2023-01-05 13:00 | 44931.5417 | 0 | 13.0475 | 37.78
2023-01-05 13:30 | 44931.5625 | 0 | 14.0614 | 37.78
2023-01-05 14:00 | 44931.5833 | 0 | 14.2708 | 37.78
2023-01-05 14:30 | 44931.6042 | 0 | 13.818 | 37.78
2023-01-05 15:00 | 44931.625 | 0 | 13.8934 | 37.78
2023-01-05 15:30 | 44931.6458 | 0 | 14.5802 | 37.78
2023-01-05 16:00 | 44931.6667 | 0 | 14.6908 | 37.78
2023-01-05 16:30 | 44931.6875 | 0 | 15.4331 | 37.78
2023-01-05 17:00 | 44931.7083 | 0 | 15.6196 | 37.78
2023-01-05 17:30 | 44931.7292 | 0 | 15.4827 | 37.78
2023-01-05 18:00 | 44931.75 | 0 | 15.1467 | 37.78
2023-01-05 18:30 | 44931.7708 | 0 | 14.8185 | 37.78
2023-01-05 19:00 | 44931.7917 | 0 | 14.7667 | 37.78
2023-01-05 19:30 | 44931.8125 | 0 | 14.3883 | 37.78
2023-01-05 20:00 | 44931.8333 | 0 | 14.0331 | 37.78
2023-01-05 20:30 | 44931.8542 | 0 | 13.4398 | 37.78
2023-01-05 21:00 | 44931.875 | 0 | 13.1438 | 37.78
2023-01-05 21:30 | 44931.8958 | 0 | 12.572 | 37.78
2023-01-05 22:00 | 44931.9167 | 0 | 12.2231 | 37.78
2023-01-05 22:30 | 44931.9375 | 0 | 11.3351 | 37.78
2023-01-05 23:00 | 44931.9583 | 0 | 10.8705 | 37.78
2023-01-05 23:30 | 44931.9792 | 0 | 10.4679 | 37.78
2023-01-06 | 44932 | 0 | 9.863 | 37.78
2023-01-06 00:30 | 44932.0208 | 0 | 9.2957 | 37.78
2023-01-06 01:00 | 44932.0417 | 0 | 9.1275 | 37.78
2023-01-06 01:30 | 44932.0625 | 0 | 8.9594 | 37.78
2023-01-06 02:00 | 44932.0833 | 0 | 8.9158 | 37.78
2023-01-06 02:30 | 44932.1042 | 0 | 8.9229 | 37.78
2023-01-06 03:00 | 44932.125 | 0 | 8.7327 | 37.78
2023-01-06 03:30 | 44932.1458 | 0 | 8.6249 | 37.78
2023-01-06 04:00 | 44932.1667 | 0 | 9.1102 | 37.78
2023-01-06 04:30 | 44932.1875 | 0 | 9.2082 | 37.78
2023-01-06 05:00 | 44932.2083 | 0 | 9.4915 | 37.78
2023-01-06 05:30 | 44932.2292 | 0 | 9.5078 | 37.78
2023-01-06 06:00 | 44932.25 | 0 | 9.7226 | 37.78
2023-01-06 06:30 | 44932.2708 | 0 | 9.6069 | 37.78
2023-01-06 07:00 | 44932.2917 | 0 | 9.7159 | 37.78
2023-01-06 07:30 | 44932.3125 | 0 | 9.5322 | 37.78
2023-01-06 08:00 | 44932.3333 | 0 | 9.7457 | 37.78
2023-01-06 08:30 | 44932.3542 | 0 | 9.5533 | 37.78
2023-01-06 09:00 | 44932.375 | 0 | 9.7685 | 37.78
2023-01-06 09:30 | 44932.3958 | 0 | 10.5104 | 37.78
2023-01-06 10:00 | 44932.4167 | 0 | 10.804 | 37.78
2023-01-06 10:30 | 44932.4375 | 0 | 11.4197 | 37.78
2023-01-06 11:00 | 44932.4583 | 0 | 12.087 | 37.78
2023-01-06 11:30 | 44932.4792 | 0 | 12.1821 | 37.78
2023-01-06 12:00 | 44932.5 | 0 | 13.009 | 37.78
2023-01-06 12:30 | 44932.5208 | 0 | 13.6888 | 37.78
2023-01-06 13:00 | 44932.5417 | 0 | 13.6279 | 37.78
2023-01-06 13:30 | 44932.5625 | 0 | 11.4325 | 37.78
2023-01-06 14:00 | 44932.5833 | 0 | 11.8444 | 37.78
2023-01-06 14:30 | 44932.6042 | 0 | 13.7868 | 37.78
2023-01-06 15:00 | 44932.625 | 0 | 14.9973 | 37.78
2023-01-06 15:30 | 44932.6458 | 0 | 14.2898 | 37.78
2023-01-06 16:00 | 44932.6667 | 0 | 14.1012 | 37.78
2023-01-06 16:30 | 44932.6875 | 0 | 14.2971 | 37.78
2023-01-06 17:00 | 44932.7083 | 0 | 14.2181 | 37.78
2023-01-06 17:30 | 44932.7292 | 0 | 13.5345 | 37.78
2023-01-06 18:00 | 44932.75 | 0 | 13.6402 | 37.78
2023-01-06 18:30 | 44932.7708 | 0 | 13.5586 | 37.78
2023-01-06 19:00 | 44932.7917 | 0 | 13.686 | 37.78
2023-01-06 19:30 | 44932.8125 | 0 | 13.5148 | 37.78
2023-01-06 20:00 | 44932.8333 | 0 | 13.2521 | 37.78
2023-01-06 20:30 | 44932.8542 | 0 | 12.8582 | 37.78
2023-01-06 21:00 | 44932.875 | 0 | 12.4974 | 37.78
2023-01-06 21:30 | 44932.8958 | 0 | 12.0007 | 37.78
2023-01-06 22:00 | 44932.9167 | 0 | 11.5344 | 37.78
2023-01-06 22:30 | 44932.9375 | 0 | 11.0145 | 37.78
2023-01-06 23:00 | 44932.9583 | 0 | 10.5371 | 37.78
2023-01-06 23:30 | 44932.9792 | 0 | 10.2105 | 37.78
2023-01-07 | 44933 | 0 | 9.535 | 37.78
2023-01-07 00:30 | 44933.0208 | 0 | 9.1111 | 37.78
2023-01-07 01:00 | 44933.0417 | 0 | 8.8419 | 37.78
2023-01-07 01:30 | 44933.0625 | 0 | 8.6472 | 37.78
2023-01-07 02:00 | 44933.0833 | 0 | 8.4685 | 37.78
2023-01-07 02:30 | 44933.1042 | 0 | 8.4394 | 37.78
2023-01-07 03:00 | 44933.125 | 0 | 8.357 | 37.78
2023-01-07 03:30 | 44933.1458 | 0 | 8.3316 | 37.78
2023-01-07 04:00 | 44933.1667 | 0 | 8.3872 | 37.78
2023-01-07 04:30 | 44933.1875 | 0 | 8.2551 | 37.78
2023-01-07 05:00 | 44933.2083 | 0 | 8.1577 | 37.78
2023-01-07 05:30 | 44933.2292 | 0 | 7.915 | 37.78
2023-01-07 06:00 | 44933.25 | 0 | 7.7977 | 37.78
2023-01-07 06:30 | 44933.2708 | 0 | 7.3808 | 37.78
2023-01-07 07:00 | 44933.2917 | 0 | 7.3155 | 37.78
2023-01-07 07:30 | 44933.3125 | 0 | 7.1444 | 37.78
2023-01-07 08:00 | 44933.3333 | 0 | 7.2105 | 37.78
2023-01-07 08:30 | 44933.3542 | 0 | 7.3719 | 37.78
2023-01-07 09:00 | 44933.375 | 0 | 8.4112 | 37.78
2023-01-07 09:30 | 44933.3958 | 0 | 8.0417 | 37.78
2023-01-07 10:00 | 44933.4167 | 0 | 7.1482 | 37.78
2023-01-07 10:30 | 44933.4375 | 0 | 8.4246 | 37.78
2023-01-07 11:00 | 44933.4583 | 0 | 8.3977 | 37.78
2023-01-07 11:30 | 44933.4792 | 0 | 9.0288 | 37.78
2023-01-07 12:00 | 44933.5 | 0 | 9.9811 | 37.78
2023-01-07 12:30 | 44933.5208 | 0 | 8.9276 | 37.78
2023-01-07 13:00 | 44933.5417 | 0 | 8.6839 | 37.78
2023-01-07 13:30 | 44933.5625 | 0 | 9.3662 | 37.78
2023-01-07 14:00 | 44933.5833 | 0 | 9.2966 | 37.78
2023-01-07 14:30 | 44933.6042 | 0 | 9.2289 | 37.78
2023-01-07 15:00 | 44933.625 | 0 | 10.7395 | 37.78
2023-01-07 15:30 | 44933.6458 | 0 | 11.943 | 37.78
2023-01-07 16:00 | 44933.6667 | 0 | 12.6031 | 37.78
2023-01-07 16:30 | 44933.6875 | 0 | 12.5146 | 37.78
2023-01-07 17:00 | 44933.7083 | 0 | 12.1254 | 37.78
2023-01-07 17:30 | 44933.7292 | 0 | 12.5705 | 37.78
2023-01-07 18:00 | 44933.75 | 0 | 12.6096 | 37.78
2023-01-07 18:30 | 44933.7708 | 0 | 12.6727 | 37.78
2023-01-07 19:00 | 44933.7917 | 0 | 12.8094 | 37.78
2023-01-07 19:30 | 44933.8125 | 0 | 12.5623 | 37.78
2023-01-07 20:00 | 44933.8333 | 0 | 12.4461 | 37.78
2023-01-07 20:30 | 44933.8542 | 0 | 11.9403 | 37.78
2023-01-07 21:00 | 44933.875 | 0 | 11.7249 | 37.78
2023-01-07 21:30 | 44933.8958 | 0 | 11.0962 | 37.78
2023-01-07 22:00 | 44933.9167 | 0 | 10.8173 | 37.78
2023-01-07 22:30 | 44933.9375 | 0 | 10.2215 | 37.78
2023-01-07 23:00 | 44933.9583 | 0 | 9.6772 | 37.78
2023-01-07 23:30 | 44933.9792 | 0 | 9.2004 | 37.78
2023-01-08 | 44934 | 0 | 8.7684 | 37.78
2023-01-08 00:30 | 44934.0208 | 0 | 8.5116 | 37.78
2023-01-08 01:00 | 44934.0417 | 0 | 8.3703 | 37.78
2023-01-08 01:30 | 44934.0625 | 0 | 8.1526 | 37.78
2023-01-08 02:00 | 44934.0833 | 0 | 7.9388 | 37.78
2023-01-08 02:30 | 44934.1042 | 0 | 7.8885 | 37.78
2023-01-08 03:00 | 44934.125 | 0 | 7.9432 | 37.78
2023-01-08 03:30 | 44934.1458 | 0 | 7.8304 | 37.78
2023-01-08 04:00 | 44934.1667 | 0 | 7.8697 | 37.78
2023-01-08 04:30 | 44934.1875 | 0 | 7.7054 | 37.78
2023-01-08 05:00 | 44934.2083 | 0 | 7.6577 | 37.78
2023-01-08 05:30 | 44934.2292 | 0 | 7.5335 | 37.78
2023-01-08 06:00 | 44934.25 | 0 | 7.3673 | 37.78
2023-01-08 06:30 | 44934.2708 | 0 | 6.9386 | 37.78
2023-01-08 07:00 | 44934.2917 | 0 | 6.5233 | 37.78
2023-01-08 07:30 | 44934.3125 | 0 | 6.1394 | 37.78
2023-01-08 08:00 | 44934.3333 | 0 | 6.0748 | 37.78
2023-01-08 08:30 | 44934.3542 | 0 | 6.7041 | 37.78
2023-01-08 09:00 | 44934.375 | 0 | 7.4966 | 37.78
2023-01-08 09:30 | 44934.3958 | 0 | 7.7643 | 37.78
2023-01-08 10:00 | 44934.4167 | 0 | 8.3067 | 37.78
2023-01-08 10:30 | 44934.4375 | 0 | 8.1327 | 37.78
2023-01-08 11:00 | 44934.4583 | 0 | 8.1291 | 37.78
2023-01-08 11:30 | 44934.4792 | 0 | 8.972 | 37.78
2023-01-08 12:00 | 44934.5 | 0 | 8.5746 | 37.78
2023-01-08 12:30 | 44934.5208 | 0 | 8.6243 | 37.78
2023-01-08 13:00 | 44934.5417 | 0 | 7.9282 | 37.78
2023-01-08 13:30 | 44934.5625 | 0 | 10.7884 | 37.78
2023-01-08 14:00 | 44934.5833 | 0 | 9.287 | 37.78
2023-01-08 14:30 | 44934.6042 | 0 | 8.3289 | 37.78
2023-01-08 15:00 | 44934.625 | 0 | 10.4562 | 37.78
2023-01-08 15:30 | 44934.6458 | 0 | 10.7677 | 37.78
2023-01-08 16:00 | 44934.6667 | 0 | 11.4492 | 37.78
2023-01-08 16:30 | 44934.6875 | 0 | 12.2398 | 37.78
2023-01-08 17:00 | 44934.7083 | 0 | 12.936 | 37.78
2023-01-08 17:30 | 44934.7292 | 0 | 13.2745 | 37.78
2023-01-08 18:00 | 44934.75 | 0 | 13.4419 | 37.78
2023-01-08 18:30 | 44934.7708 | 0 | 13.5151 | 37.78
2023-01-08 19:00 | 44934.7917 | 0 | 13.6741 | 37.78
2023-01-08 19:30 | 44934.8125 | 0 | 13.4154 | 37.78
2023-01-08 20:00 | 44934.8333 | 0 | 13.2847 | 37.78
2023-01-08 20:30 | 44934.8542 | 0 | 12.5224 | 37.78
2023-01-08 21:00 | 44934.875 | 0 | 12.1911 | 37.78
2023-01-08 21:30 | 44934.8958 | 0 | 11.7389 | 37.78
2023-01-08 22:00 | 44934.9167 | 0 | 11.2208 | 37.78
2023-01-08 22:30 | 44934.9375 | 0 | 10.5925 | 37.78
2023-01-08 23:00 | 44934.9583 | 0 | 10.0816 | 37.78
2023-01-08 23:30 | 44934.9792 | 0 | 9.4842 | 37.78
2023-01-09 | 44935 | 0 | 9.1294 | 37.78
2023-01-09 00:30 | 44935.0208 | 0 | 8.9777 | 37.78
2023-01-09 01:00 | 44935.0417 | 0 | 8.8107 | 37.78
2023-01-09 01:30 | 44935.0625 | 0 | 8.6764 | 37.78
2023-01-09 02:00 | 44935.0833 | 0 | 8.6612 | 37.78
2023-01-09 02:30 | 44935.1042 | 0 | 8.7857 | 37.78
2023-01-09 03:00 | 44935.125 | 0 | 8.6737 | 37.78
2023-01-09 03:30 | 44935.1458 | 0 | 8.9077 | 37.78
2023-01-09 04:00 | 44935.1667 | 0 | 9.2898 | 37.78
2023-01-09 04:30 | 44935.1875 | 0 | 9.3261 | 37.78
2023-01-09 05:00 | 44935.2083 | 0 | 9.6562 | 37.78
2023-01-09 05:30 | 44935.2292 | 0 | 9.8925 | 37.78
2023-01-09 06:00 | 44935.25 | 0 | 10.4505 | 37.78
2023-01-09 06:30 | 44935.2708 | 0 | 10.8104 | 37.78
2023-01-09 07:00 | 44935.2917 | 0 | 11.39 | 37.78
2023-01-09 07:30 | 44935.3125 | 0 | 11.5615 | 37.78
2023-01-09 08:00 | 44935.3333 | 0 | 11.0114 | 37.78
2023-01-09 08:30 | 44935.3542 | 0 | 11.142 | 37.78
2023-01-09 09:00 | 44935.375 | 0 | 12.0304 | 37.78
2023-01-09 09:30 | 44935.3958 | 0 | 12.5078 | 37.78
2023-01-09 10:00 | 44935.4167 | 0 | 12.3044 | 37.78
2023-01-09 10:30 | 44935.4375 | 0 | 11.4272 | 37.78
2023-01-09 11:00 | 44935.4583 | 0 | 12.3473 | 37.78
2023-01-09 11:30 | 44935.4792 | 0 | 11.68 | 37.78
2023-01-09 12:00 | 44935.5 | 0 | 11.3452 | 37.78
2023-01-09 12:30 | 44935.5208 | 0 | 11.2938 | 37.78
2023-01-09 13:00 | 44935.5417 | 0 | 11.6783 | 37.78
2023-01-09 13:30 | 44935.5625 | 0 | 12.1708 | 37.78
2023-01-09 14:00 | 44935.5833 | 0 | 12.7332 | 37.78
2023-01-09 14:30 | 44935.6042 | 0 | 13.4535 | 37.78
2023-01-09 15:00 | 44935.625 | 0 | 14.0899 | 37.78
2023-01-09 15:30 | 44935.6458 | 0 | 15.2482 | 37.78
2023-01-09 16:00 | 44935.6667 | 0 | 15.4989 | 37.78
2023-01-09 16:30 | 44935.6875 | 0 | 16.147 | 37.78
2023-01-09 17:00 | 44935.7083 | 0 | 16.4029 | 37.78
2023-01-09 17:30 | 44935.7292 | 0 | 16.2037 | 37.78
2023-01-09 18:00 | 44935.75 | 0 | 16.3139 | 37.78
2023-01-09 18:30 | 44935.7708 | 0 | 16.4213 | 37.78
2023-01-09 19:00 | 44935.7917 | 0 | 16.3692 | 37.78
2023-01-09 19:30 | 44935.8125 | 0 | 16.078 | 37.78
2023-01-09 20:00 | 44935.8333 | 0 | 15.8331 | 37.78
2023-01-09 20:30 | 44935.8542 | 0 | 15.1506 | 37.78
2023-01-09 21:00 | 44935.875 | 0 | 14.3983 | 37.78
2023-01-09 21:30 | 44935.8958 | 0 | 13.91 | 37.78
2023-01-09 22:00 | 44935.9167 | 0 | 13.0629 | 37.78
2023-01-09 22:30 | 44935.9375 | 0 | 12.0645 | 37.78
2023-01-09 23:00 | 44935.9583 | 0 | 11.5026 | 37.78
2023-01-09 23:30 | 44935.9792 | 0 | 11.1145 | 37.78
2023-01-10 | 44936 | 0 | 10.3897 | 37.78
2023-01-10 00:30 | 44936.0208 | 0 | 9.9866 | 37.78
2023-01-10 01:00 | 44936.0417 | 0 | 9.6816 | 37.78
2023-01-10 01:30 | 44936.0625 | 0 | 9.6227 | 37.78
2023-01-10 02:00 | 44936.0833 | 0 | 9.4017 | 37.78
2023-01-10 02:30 | 44936.1042 | 0 | 9.4001 | 37.78
2023-01-10 03:00 | 44936.125 | 0 | 9.1278 | 37.78
2023-01-10 03:30 | 44936.1458 | 0 | 9.4312 | 37.78
2023-01-10 04:00 | 44936.1667 | 0 | 9.5676 | 37.78
2023-01-10 04:30 | 44936.1875 | 0 | 9.7694 | 37.78
2023-01-10 05:00 | 44936.2083 | 0 | 10.2197 | 37.78
2023-01-10 05:30 | 44936.2292 | 0 | 10.1438 | 37.78
2023-01-10 06:00 | 44936.25 | 0 | 10.7892 | 37.78
2023-01-10 06:30 | 44936.2708 | 0 | 10.9463 | 37.78
2023-01-10 07:00 | 44936.2917 | 0 | 11.9401 | 37.78
2023-01-10 07:30 | 44936.3125 | 0 | 11.1977 | 37.78
2023-01-10 08:00 | 44936.3333 | 0 | 10.5196 | 37.78
2023-01-10 08:30 | 44936.3542 | 0 | 11.6016 | 37.78
2023-01-10 09:00 | 44936.375 | 0 | 11.6825 | 37.78
2023-01-10 09:30 | 44936.3958 | 0 | 10.7121 | 37.78
2023-01-10 10:00 | 44936.4167 | 0 | 10.7588 | 37.78
2023-01-10 10:30 | 44936.4375 | 0 | 11.2765 | 37.78
2023-01-10 11:00 | 44936.4583 | 0 | 12.4886 | 37.78
2023-01-10 11:30 | 44936.4792 | 0 | 11.2265 | 37.78
2023-01-10 12:00 | 44936.5 | 0 | 12.2181 | 37.78
2023-01-10 12:30 | 44936.5208 | 0 | 11.8944 | 37.78
2023-01-10 13:00 | 44936.5417 | 0 | 11.6119 | 37.78
2023-01-10 13:30 | 44936.5625 | 0 | 12.1513 | 37.78
2023-01-10 14:00 | 44936.5833 | 0 | 12.3996 | 37.78
2023-01-10 14:30 | 44936.6042 | 0 | 14.1805 | 37.78
2023-01-10 15:00 | 44936.625 | 0 | 13.16 | 37.78
2023-01-10 15:30 | 44936.6458 | 0 | 13.9542 | 37.78
2023-01-10 16:00 | 44936.6667 | 0 | 14.6865 | 37.78
2023-01-10 16:30 | 44936.6875 | 0 | 15.4074 | 37.78
2023-01-10 17:00 | 44936.7083 | 0 | 15.6686 | 37.78
2023-01-10 17:30 | 44936.7292 | 0 | 15.9769 | 37.78
2023-01-10 18:00 | 44936.75 | 0 | 15.7246 | 37.78
2023-01-10 18:30 | 44936.7708 | 0 | 15.8806 | 37.78
2023-01-10 19:00 | 44936.7917 | 0 | 15.9265 | 37.78
2023-01-10 19:30 | 44936.8125 | 0 | 15.5686 | 37.78
2023-01-10 20:00 | 44936.8333 | 0 | 15.0584 | 37.78
2023-01-10 20:30 | 44936.8542 | 0 | 14.5654 | 37.78
2023-01-10 21:00 | 44936.875 | 0 | 14.0501 | 37.78
2023-01-10 21:30 | 44936.8958 | 0 | 13.397 | 37.78
2023-01-10 22:00 | 44936.9167 | 0 | 12.6925 | 37.78
2023-01-10 22:30 | 44936.9375 | 0 | 11.8575 | 37.78
2023-01-10 23:00 | 44936.9583 | 0 | 11.432 | 37.78
2023-01-10 23:30 | 44936.9792 | 0 | 10.6467 | 37.78
2023-01-11 | 44937 | 0 | 10.1724 | 37.78
2023-01-11 00:30 | 44937.0208 | 0 | 9.6206 | 37.78
2023-01-11 01:00 | 44937.0417 | 0 | 9.4679 | 37.78
2023-01-11 01:30 | 44937.0625 | 0 | 9.2037 | 37.78
2023-01-11 02:00 | 44937.0833 | 0 | 9.056 | 37.78
2023-01-11 02:30 | 44937.1042 | 0 | 9.0668 | 37.78
2023-01-11 03:00 | 44937.125 | 0 | 8.9543 | 37.78
2023-01-11 03:30 | 44937.1458 | 0 | 8.9605 | 37.78
2023-01-11 04:00 | 44937.1667 | 0 | 9.2415 | 37.78
2023-01-11 04:30 | 44937.1875 | 0 | 9.5753 | 37.78
2023-01-11 05:00 | 44937.2083 | 0 | 9.9875 | 37.78
2023-01-11 05:30 | 44937.2292 | 0 | 10.1143 | 37.78
2023-01-11 06:00 | 44937.25 | 0 | 10.7914 | 37.78
2023-01-11 06:30 | 44937.2708 | 0 | 10.9582 | 37.78
2023-01-11 07:00 | 44937.2917 | 0 | 11.0168 | 37.78
2023-01-11 07:30 | 44937.3125 | 0 | 10.9372 | 37.78
2023-01-11 08:00 | 44937.3333 | 0 | 11.7716 | 37.78
2023-01-11 08:30 | 44937.3542 | 0 | 11.1243 | 37.78
2023-01-11 09:00 | 44937.375 | 0 | 10.7965 | 37.78
2023-01-11 09:30 | 44937.3958 | 0 | 11.1274 | 37.78
2023-01-11 10:00 | 44937.4167 | 0 | 12.1171 | 37.78
2023-01-11 10:30 | 44937.4375 | 0 | 11.9743 | 37.78
2023-01-11 11:00 | 44937.4583 | 0 | 12.2632 | 37.78
2023-01-11 11:30 | 44937.4792 | 0 | 13.375 | 37.78
2023-01-11 12:00 | 44937.5 | 0 | 13.6234 | 37.78
2023-01-11 12:30 | 44937.5208 | 0 | 11.2734 | 37.78
2023-01-11 13:00 | 44937.5417 | 0 | 11.8426 | 37.78
2023-01-11 13:30 | 44937.5625 | 0 | 12.5266 | 37.78
2023-01-11 14:00 | 44937.5833 | 0 | 14.2656 | 37.78
2023-01-11 14:30 | 44937.6042 | 0 | 15.4377 | 37.78
2023-01-11 15:00 | 44937.625 | 0 | 15.2151 | 37.78
2023-01-11 15:30 | 44937.6458 | 0 | 14.9067 | 37.78
2023-01-11 16:00 | 44937.6667 | 0 | 14.8578 | 37.78
2023-01-11 16:30 | 44937.6875 | 0 | 14.7351 | 37.78
2023-01-11 17:00 | 44937.7083 | 0 | 15.5442 | 37.78
2023-01-11 17:30 | 44937.7292 | 0 | 15.3309 | 37.78
2023-01-11 18:00 | 44937.75 | 0 | 15.1485 | 37.78
2023-01-11 18:30 | 44937.7708 | 0 | 15.6457 | 37.78
2023-01-11 19:00 | 44937.7917 | 0 | 15.563 | 37.78
2023-01-11 19:30 | 44937.8125 | 0 | 15.3675 | 37.78
2023-01-11 20:00 | 44937.8333 | 0 | 14.9963 | 37.78
2023-01-11 20:30 | 44937.8542 | 0 | 14.2883 | 37.78
2023-01-11 21:00 | 44937.875 | 0 | 13.904 | 37.78
2023-01-11 21:30 | 44937.8958 | 0 | 13.3889 | 37.78
2023-01-11 22:00 | 44937.9167 | 0 | 12.7268 | 37.78
2023-01-11 22:30 | 44937.9375 | 0 | 11.9873 | 37.78
2023-01-11 23:00 | 44937.9583 | 0 | 11.3705 | 37.78
2023-01-11 23:30 | 44937.9792 | 0 | 11.0121 | 37.78
2023-01-12 | 44938 | 0 | 10.4371 | 37.78
2023-01-12 00:30 | 44938.0208 | 0 | 9.9999 | 37.78
2023-01-12 01:00 | 44938.0417 | 0 | 9.7799 | 37.78
2023-01-12 01:30 | 44938.0625 | 0 | 9.6018 | 37.78
2023-01-12 02:00 | 44938.0833 | 0 | 9.4238 | 37.78
2023-01-12 02:30 | 44938.1042 | 0 | 9.3719 | 37.78
2023-01-12 03:00 | 44938.125 | 0 | 9.1251 | 37.78
2023-01-12 03:30 | 44938.1458 | 0 | 9.3955 | 37.78
2023-01-12 04:00 | 44938.1667 | 0 | 9.7744 | 37.78
2023-01-12 04:30 | 44938.1875 | 0 | 9.9916 | 37.78
2023-01-12 05:00 | 44938.2083 | 0 | 10.2575 | 37.78
2023-01-12 05:30 | 44938.2292 | 0 | 10.445 | 37.78
2023-01-12 06:00 | 44938.25 | 0 | 11.0028 | 37.78
2023-01-12 06:30 | 44938.2708 | 0 | 11.2735 | 37.78
2023-01-12 07:00 | 44938.2917 | 0 | 11.1222 | 37.78
2023-01-12 07:30 | 44938.3125 | 0 | 10.9187 | 37.78
2023-01-12 08:00 | 44938.3333 | 0 | 11.2877 | 37.78
2023-01-12 08:30 | 44938.3542 | 0 | 12.9021 | 37.78
2023-01-12 09:00 | 44938.375 | 0 | 12.1654 | 37.78
2023-01-12 09:30 | 44938.3958 | 0 | 11.6183 | 37.78
2023-01-12 10:00 | 44938.4167 | 0 | 12.5213 | 37.78
2023-01-12 10:30 | 44938.4375 | 0 | 12.6101 | 37.78
2023-01-12 11:00 | 44938.4583 | 0 | 12.8361 | 37.78
2023-01-12 11:30 | 44938.4792 | 0 | 13.1378 | 37.78
2023-01-12 12:00 | 44938.5 | 0 | 13.7383 | 37.78
2023-01-12 12:30 | 44938.5208 | 0 | 12.2347 | 37.78
2023-01-12 13:00 | 44938.5417 | 0 | 13.0951 | 37.78
2023-01-12 13:30 | 44938.5625 | 0 | 11.9536 | 37.78
2023-01-12 14:00 | 44938.5833 | 0 | 13.5977 | 37.78
2023-01-12 14:30 | 44938.6042 | 0 | 14.0797 | 37.78
2023-01-12 15:00 | 44938.625 | 0 | 13.4587 | 37.78
2023-01-12 15:30 | 44938.6458 | 0 | 14.3004 | 37.78
2023-01-12 16:00 | 44938.6667 | 0 | 14.9614 | 37.78
2023-01-12 16:30 | 44938.6875 | 0 | 14.6651 | 37.78
2023-01-12 17:00 | 44938.7083 | 0 | 14.5688 | 37.78
2023-01-12 17:30 | 44938.7292 | 0 | 14.5954 | 37.78
2023-01-12 18:00 | 44938.75 | 0 | 14.5561 | 37.78
2023-01-12 18:30 | 44938.7708 | 0 | 14.8667 | 37.78
2023-01-12 19:00 | 44938.7917 | 0 | 14.9376 | 37.78
2023-01-12 19:30 | 44938.8125 | 0 | 14.9483 | 37.78
2023-01-12 20:00 | 44938.8333 | 0 | 14.6097 | 37.78
2023-01-12 20:30 | 44938.8542 | 0 | 14.121 | 37.78
2023-01-12 21:00 | 44938.875 | 0 | 13.609 | 37.78
2023-01-12 21:30 | 44938.8958 | 0 | 13.3543 | 37.78
2023-01-12 22:00 | 44938.9167 | 0 | 12.7293 | 37.78
2023-01-12 22:30 | 44938.9375 | 0 | 11.757 | 37.78
2023-01-12 23:00 | 44938.9583 | 0 | 11.071 | 37.78
2023-01-12 23:30 | 44938.9792 | 0 | 10.815 | 37.78
2023-01-13 | 44939 | 0 | 10.2033 | 37.78
2023-01-13 00:30 | 44939.0208 | 0 | 9.7728 | 37.78
2023-01-13 01:00 | 44939.0417 | 0 | 9.5155 | 37.78
2023-01-13 01:30 | 44939.0625 | 0 | 9.3261 | 37.78
2023-01-13 02:00 | 44939.0833 | 0 | 9.2903 | 37.78
2023-01-13 02:30 | 44939.1042 | 0 | 9.3002 | 37.78
2023-01-13 03:00 | 44939.125 | 0 | 9.1311 | 37.78
2023-01-13 03:30 | 44939.1458 | 0 | 9.1317 | 37.78
2023-01-13 04:00 | 44939.1667 | 0 | 9.3321 | 37.78
2023-01-13 04:30 | 44939.1875 | 0 | 9.689 | 37.78
2023-01-13 05:00 | 44939.2083 | 0 | 9.9747 | 37.78
2023-01-13 05:30 | 44939.2292 | 0 | 10.1398 | 37.78
2023-01-13 06:00 | 44939.25 | 0 | 10.447 | 37.78
2023-01-13 06:30 | 44939.2708 | 0 | 10.7515 | 37.78
2023-01-13 07:00 | 44939.2917 | 0 | 10.9957 | 37.78
2023-01-13 07:30 | 44939.3125 | 0 | 11.7353 | 37.78
2023-01-13 08:00 | 44939.3333 | 0 | 11.8563 | 37.78
2023-01-13 08:30 | 44939.3542 | 0 | 12.4139 | 37.78
2023-01-13 09:00 | 44939.375 | 0 | 10.635 | 37.78
2023-01-13 09:30 | 44939.3958 | 0 | 11.0048 | 37.78
2023-01-13 10:00 | 44939.4167 | 0 | 12.0769 | 37.78
2023-01-13 10:30 | 44939.4375 | 0 | 11.6636 | 37.78
2023-01-13 11:00 | 44939.4583 | 0 | 11.2108 | 37.78
2023-01-13 11:30 | 44939.4792 | 0 | 10.5435 | 37.78
2023-01-13 12:00 | 44939.5 | 0 | 11.3474 | 37.78
2023-01-13 12:30 | 44939.5208 | 0 | 11.5386 | 37.78
2023-01-13 13:00 | 44939.5417 | 0 | 11.7705 | 37.78
2023-01-13 13:30 | 44939.5625 | 0 | 11.7182 | 37.78
2023-01-13 14:00 | 44939.5833 | 0 | 12.4899 | 37.78
2023-01-13 14:30 | 44939.6042 | 0 | 13.4954 | 37.78
2023-01-13 15:00 | 44939.625 | 0 | 14.1419 | 37.78
2023-01-13 15:30 | 44939.6458 | 0 | 14.5445 | 37.78
2023-01-13 16:00 | 44939.6667 | 0 | 14.2854 | 37.78
2023-01-13 16:30 | 44939.6875 | 0 | 14.12 | 37.78
2023-01-13 17:00 | 44939.7083 | 0 | 14.1068 | 37.78
2023-01-13 17:30 | 44939.7292 | 0 | 14.0249 | 37.78
2023-01-13 18:00 | 44939.75 | 0 | 14.1065 | 37.78
2023-01-13 18:30 | 44939.7708 | 0 | 14.3134 | 37.78
2023-01-13 19:00 | 44939.7917 | 0 | 14.4336 | 37.78
2023-01-13 19:30 | 44939.8125 | 0 | 14.4245 | 37.78
2023-01-13 20:00 | 44939.8333 | 0 | 14.0747 | 37.78
2023-01-13 20:30 | 44939.8542 | 0 | 13.7295 | 37.78
2023-01-13 21:00 | 44939.875 | 0 | 13.5481 | 37.78
2023-01-13 21:30 | 44939.8958 | 0 | 13.086 | 37.78
2023-01-13 22:00 | 44939.9167 | 0 | 12.6928 | 37.78
2023-01-13 22:30 | 44939.9375 | 0 | 11.9242 | 37.78
2023-01-13 23:00 | 44939.9583 | 0 | 11.37 | 37.78
2023-01-13 23:30 | 44939.9792 | 0 | 10.7406 | 37.78
2023-01-14 | 44940 | 0 | 10.4242 | 37.78
2023-01-14 00:30 | 44940.0208 | 0 | 9.9056 | 37.78
2023-01-14 01:00 | 44940.0417 | 0 | 9.7528 | 37.78
2023-01-14 01:30 | 44940.0625 | 0 | 9.626 | 37.78
2023-01-14 02:00 | 44940.0833 | 0 | 9.5 | 37.78
2023-01-14 02:30 | 44940.1042 | 0 | 9.3869 | 37.78
2023-01-14 03:00 | 44940.125 | 0 | 9.1744 | 37.78
2023-01-14 03:30 | 44940.1458 | 0 | 9.2755 | 37.78
2023-01-14 04:00 | 44940.1667 | 0 | 9.2781 | 37.78
2023-01-14 04:30 | 44940.1875 | 0 | 9.3699 | 37.78
2023-01-14 05:00 | 44940.2083 | 0 | 9.3085 | 37.78
2023-01-14 05:30 | 44940.2292 | 0 | 9.1996 | 37.78
2023-01-14 06:00 | 44940.25 | 0 | 9.1885 | 37.78
2023-01-14 06:30 | 44940.2708 | 0 | 9.1534 | 37.78
2023-01-14 07:00 | 44940.2917 | 0 | 9.436 | 37.78
2023-01-14 07:30 | 44940.3125 | 0 | 9.818 | 37.78
2023-01-14 08:00 | 44940.3333 | 0 | 10.2657 | 37.78
2023-01-14 08:30 | 44940.3542 | 0 | 9.7362 | 37.78
2023-01-14 09:00 | 44940.375 | 0 | 9.1268 | 37.78
2023-01-14 09:30 | 44940.3958 | 0 | 8.276 | 37.78
2023-01-14 10:00 | 44940.4167 | 0 | 8.472 | 37.78
2023-01-14 10:30 | 44940.4375 | 0 | 9.8879 | 37.78
2023-01-14 11:00 | 44940.4583 | 0 | 9.8776 | 37.78
2023-01-14 11:30 | 44940.4792 | 0 | 9.6723 | 37.78
2023-01-14 12:00 | 44940.5 | 0 | 9.7626 | 37.78
2023-01-14 12:30 | 44940.5208 | 0 | 10.693 | 37.78
2023-01-14 13:00 | 44940.5417 | 0 | 10.1887 | 37.78
2023-01-14 13:30 | 44940.5625 | 0 | 9.8576 | 37.78
2023-01-14 14:00 | 44940.5833 | 0 | 10.843 | 37.78
2023-01-14 14:30 | 44940.6042 | 0 | 10.3454 | 37.78
2023-01-14 15:00 | 44940.625 | 0 | 10.8188 | 37.78
2023-01-14 15:30 | 44940.6458 | 0 | 10.6716 | 37.78
2023-01-14 16:00 | 44940.6667 | 0 | 10.628 | 37.78
2023-01-14 16:30 | 44940.6875 | 0 | 10.9543 | 37.78
2023-01-14 17:00 | 44940.7083 | 0 | 11.4102 | 37.78
2023-01-14 17:30 | 44940.7292 | 0 | 11.4724 | 37.78
2023-01-14 18:00 | 44940.75 | 0 | 11.7648 | 37.78
2023-01-14 18:30 | 44940.7708 | 0 | 11.8155 | 37.78
2023-01-14 19:00 | 44940.7917 | 0 | 12.0054 | 37.78
2023-01-14 19:30 | 44940.8125 | 0 | 11.7562 | 37.78
2023-01-14 20:00 | 44940.8333 | 0 | 11.7155 | 37.78
2023-01-14 20:30 | 44940.8542 | 0 | 11.2937 | 37.78
2023-01-14 21:00 | 44940.875 | 0 | 10.9758 | 37.78
2023-01-14 21:30 | 44940.8958 | 0 | 10.7058 | 37.78
2023-01-14 22:00 | 44940.9167 | 0 | 10.396 | 37.78
2023-01-14 22:30 | 44940.9375 | 0 | 9.9006 | 37.78
2023-01-14 23:00 | 44940.9583 | 0 | 9.4908 | 37.78
2023-01-14 23:30 | 44940.9792 | 0 | 9.0587 | 37.78
2023-01-15 | 44941 | 0 | 8.5492 | 37.78
2023-01-15 00:30 | 44941.0208 | 0 | 8.267 | 37.78
2023-01-15 01:00 | 44941.0417 | 0 | 8.1556 | 37.78
2023-01-15 01:30 | 44941.0625 | 0 | 8.0267 | 37.78
2023-01-15 02:00 | 44941.0833 | 0 | 8.0559 | 37.78
2023-01-15 02:30 | 44941.1042 | 0 | 7.7143 | 37.78
2023-01-15 03:00 | 44941.125 | 0 | 7.8402 | 37.78
2023-01-15 03:30 | 44941.1458 | 0 | 7.5767 | 37.78
2023-01-15 04:00 | 44941.1667 | 0 | 7.6452 | 37.78
2023-01-15 04:30 | 44941.1875 | 0 | 7.619 | 37.78
2023-01-15 05:00 | 44941.2083 | 0 | 7.6467 | 37.78
2023-01-15 05:30 | 44941.2292 | 0 | 7.5618 | 37.78
2023-01-15 06:00 | 44941.25 | 0 | 7.4874 | 37.78
2023-01-15 06:30 | 44941.2708 | 0 | 7.4725 | 37.78
2023-01-15 07:00 | 44941.2917 | 0 | 7.5642 | 37.78
2023-01-15 07:30 | 44941.3125 | 0 | 7.3206 | 37.78
2023-01-15 08:00 | 44941.3333 | 0 | 7.2417 | 37.78
2023-01-15 08:30 | 44941.3542 | 0 | 8.1271 | 37.78
2023-01-15 09:00 | 44941.375 | 0 | 8.827 | 37.78
2023-01-15 09:30 | 44941.3958 | 0 | 8.2651 | 37.78
2023-01-15 10:00 | 44941.4167 | 0 | 7.7444 | 37.78
2023-01-15 10:30 | 44941.4375 | 0 | 7.3751 | 37.78
2023-01-15 11:00 | 44941.4583 | 0 | 6.7866 | 37.78
2023-01-15 11:30 | 44941.4792 | 0 | 5.9747 | 37.78
2023-01-15 12:00 | 44941.5 | 0 | 6.0445 | 37.78
2023-01-15 12:30 | 44941.5208 | 0 | 6.8602 | 37.78
2023-01-15 13:00 | 44941.5417 | 0 | 6.7094 | 37.78
2023-01-15 13:30 | 44941.5625 | 0 | 6.9709 | 37.78
2023-01-15 14:00 | 44941.5833 | 0 | 8.4488 | 37.78
2023-01-15 14:30 | 44941.6042 | 0 | 9.3256 | 37.78
2023-01-15 15:00 | 44941.625 | 0 | 8.7955 | 37.78
2023-01-15 15:30 | 44941.6458 | 0 | 8.4414 | 37.78
2023-01-15 16:00 | 44941.6667 | 0 | 10.5069 | 37.78
2023-01-15 16:30 | 44941.6875 | 0 | 10.6693 | 37.78
2023-01-15 17:00 | 44941.7083 | 0 | 11.5208 | 37.78
2023-01-15 17:30 | 44941.7292 | 0 | 12.3569 | 37.78
2023-01-15 18:00 | 44941.75 | 0 | 12.6543 | 37.78
2023-01-15 18:30 | 44941.7708 | 0 | 12.994 | 37.78
2023-01-15 19:00 | 44941.7917 | 0 | 13.2243 | 37.78
2023-01-15 19:30 | 44941.8125 | 0 | 12.9382 | 37.78
2023-01-15 20:00 | 44941.8333 | 0 | 12.859 | 37.78
2023-01-15 20:30 | 44941.8542 | 0 | 12.3291 | 37.78
2023-01-15 21:00 | 44941.875 | 0 | 11.9329 | 37.78
2023-01-15 21:30 | 44941.8958 | 0 | 11.5945 | 37.78
2023-01-15 22:00 | 44941.9167 | 0 | 10.8791 | 37.78
2023-01-15 22:30 | 44941.9375 | 0 | 10.1979 | 37.78
2023-01-15 23:00 | 44941.9583 | 0 | 9.6224 | 37.78
2023-01-15 23:30 | 44941.9792 | 0 | 9.2133 | 37.78
2023-01-16 | 44942 | 0 | 8.9625 | 37.78
2023-01-16 00:30 | 44942.0208 | 0 | 8.7666 | 37.78
2023-01-16 01:00 | 44942.0417 | 0 | 8.6249 | 37.78
2023-01-16 01:30 | 44942.0625 | 0 | 8.5099 | 37.78
2023-01-16 02:00 | 44942.0833 | 0 | 8.5233 | 37.78
2023-01-16 02:30 | 44942.1042 | 0 | 8.6433 | 37.78
2023-01-16 03:00 | 44942.125 | 0 | 8.4815 | 37.78
2023-01-16 03:30 | 44942.1458 | 0 | 8.6597 | 37.78
2023-01-16 04:00 | 44942.1667 | 0 | 9.0298 | 37.78
2023-01-16 04:30 | 44942.1875 | 0 | 9.344 | 37.78
2023-01-16 05:00 | 44942.2083 | 0 | 9.776 | 37.78
2023-01-16 05:30 | 44942.2292 | 0 | 10.3798 | 37.78
2023-01-16 06:00 | 44942.25 | 0 | 11.001 | 37.78
2023-01-16 06:30 | 44942.2708 | 0 | 11.6865 | 37.78
2023-01-16 07:00 | 44942.2917 | 0 | 12.4361 | 37.78
2023-01-16 07:30 | 44942.3125 | 0 | 13.2525 | 37.78
2023-01-16 08:00 | 44942.3333 | 0 | 13.4978 | 37.78
2023-01-16 08:30 | 44942.3542 | 0 | 12.899 | 37.78
2023-01-16 09:00 | 44942.375 | 0 | 13.8888 | 37.78
2023-01-16 09:30 | 44942.3958 | 0 | 12.8757 | 37.78
2023-01-16 10:00 | 44942.4167 | 0 | 12.8037 | 37.78
2023-01-16 10:30 | 44942.4375 | 0 | 14.1276 | 37.78
2023-01-16 11:00 | 44942.4583 | 0 | 13.5245 | 37.78
2023-01-16 11:30 | 44942.4792 | 0 | 13.6115 | 37.78
2023-01-16 12:00 | 44942.5 | 0 | 12.6088 | 37.78
2023-01-16 12:30 | 44942.5208 | 0 | 13.8462 | 37.78
2023-01-16 13:00 | 44942.5417 | 0 | 14.1693 | 37.78
2023-01-16 13:30 | 44942.5625 | 0 | 12.6797 | 37.78
2023-01-16 14:00 | 44942.5833 | 0 | 13.2011 | 37.78
2023-01-16 14:30 | 44942.6042 | 0 | 13.7236 | 37.78
2023-01-16 15:00 | 44942.625 | 0 | 13.9761 | 37.78
2023-01-16 15:30 | 44942.6458 | 0 | 13.6499 | 37.78
2023-01-16 16:00 | 44942.6667 | 0 | 13.8733 | 37.78
2023-01-16 16:30 | 44942.6875 | 0 | 14.0127 | 37.78
2023-01-16 17:00 | 44942.7083 | 0 | 14.1997 | 37.78
2023-01-16 17:30 | 44942.7292 | 0 | 14.2991 | 37.78
2023-01-16 18:00 | 44942.75 | 0 | 14.6648 | 37.78
2023-01-16 18:30 | 44942.7708 | 0 | 14.7655 | 37.78
2023-01-16 19:00 | 44942.7917 | 0 | 14.918 | 37.78
2023-01-16 19:30 | 44942.8125 | 0 | 14.722 | 37.78
2023-01-16 20:00 | 44942.8333 | 0 | 14.3323 | 37.78
2023-01-16 20:30 | 44942.8542 | 0 | 13.934 | 37.78
2023-01-16 21:00 | 44942.875 | 0 | 13.5852 | 37.78
2023-01-16 21:30 | 44942.8958 | 0 | 12.8595 | 37.78
2023-01-16 22:00 | 44942.9167 | 0 | 12.2493 | 37.78
2023-01-16 22:30 | 44942.9375 | 0 | 11.6124 | 37.78
2023-01-16 23:00 | 44942.9583 | 0 | 11.1048 | 37.78
2023-01-16 23:30 | 44942.9792 | 0 | 10.6848 | 37.78
2023-01-17 | 44943 | 0 | 10.05 | 37.78
2023-01-17 00:30 | 44943.0208 | 0 | 9.5948 | 37.78
2023-01-17 01:00 | 44943.0417 | 0 | 9.3848 | 37.78
2023-01-17 01:30 | 44943.0625 | 0 | 9.158 | 37.78
2023-01-17 02:00 | 44943.0833 | 0 | 8.9777 | 37.78
2023-01-17 02:30 | 44943.1042 | 0 | 9.02 | 37.78
2023-01-17 03:00 | 44943.125 | 0 | 8.9625 | 37.78
2023-01-17 03:30 | 44943.1458 | 0 | 9.0976 | 37.78
2023-01-17 04:00 | 44943.1667 | 0 | 9.2223 | 37.78
2023-01-17 04:30 | 44943.1875 | 0 | 9.5315 | 37.78
2023-01-17 05:00 | 44943.2083 | 0 | 9.8838 | 37.78
2023-01-17 05:30 | 44943.2292 | 0 | 10.0253 | 37.78
2023-01-17 06:00 | 44943.25 | 0 | 10.7579 | 37.78
2023-01-17 06:30 | 44943.2708 | 0 | 11.1386 | 37.78
2023-01-17 07:00 | 44943.2917 | 0 | 11.775 | 37.78
2023-01-17 07:30 | 44943.3125 | 0 | 11.7441 | 37.78
2023-01-17 08:00 | 44943.3333 | 0 | 12.2401 | 37.78
2023-01-17 08:30 | 44943.3542 | 0 | 11.4491 | 37.78
2023-01-17 09:00 | 44943.375 | 0 | 12.8483 | 37.78
2023-01-17 09:30 | 44943.3958 | 0 | 12.5539 | 37.78
2023-01-17 10:00 | 44943.4167 | 0 | 12.4699 | 37.78
2023-01-17 10:30 | 44943.4375 | 0 | 11.4196 | 37.78
2023-01-17 11:00 | 44943.4583 | 0 | 12.2138 | 37.78
2023-01-17 11:30 | 44943.4792 | 0 | 12.466 | 37.78
2023-01-17 12:00 | 44943.5 | 0 | 11.5094 | 37.78
2023-01-17 12:30 | 44943.5208 | 0 | 11.6111 | 37.78
2023-01-17 13:00 | 44943.5417 | 0 | 11.9097 | 37.78
2023-01-17 13:30 | 44943.5625 | 0 | 12.0375 | 37.78
2023-01-17 14:00 | 44943.5833 | 0 | 13.5642 | 37.78
2023-01-17 14:30 | 44943.6042 | 0 | 12.1254 | 37.78
2023-01-17 15:00 | 44943.625 | 0 | 12.5425 | 37.78
2023-01-17 15:30 | 44943.6458 | 0 | 13.9287 | 37.78
2023-01-17 16:00 | 44943.6667 | 0 | 14.4237 | 37.78
2023-01-17 16:30 | 44943.6875 | 0 | 14.8455 | 37.78
2023-01-17 17:00 | 44943.7083 | 0 | 15.1207 | 37.78
2023-01-17 17:30 | 44943.7292 | 0 | 15.124 | 37.78
2023-01-17 18:00 | 44943.75 | 0 | 15.1853 | 37.78
2023-01-17 18:30 | 44943.7708 | 0 | 15.5861 | 37.78
2023-01-17 19:00 | 44943.7917 | 0 | 15.7523 | 37.78
2023-01-17 19:30 | 44943.8125 | 0 | 15.5773 | 37.78
2023-01-17 20:00 | 44943.8333 | 0 | 15.3485 | 37.78
2023-01-17 20:30 | 44943.8542 | 0 | 14.5605 | 37.78
2023-01-17 21:00 | 44943.875 | 0 | 13.8149 | 37.78
2023-01-17 21:30 | 44943.8958 | 0 | 13.6557 | 37.78
2023-01-17 22:00 | 44943.9167 | 0 | 12.8609 | 37.78
2023-01-17 22:30 | 44943.9375 | 0 | 12.0935 | 37.78
2023-01-17 23:00 | 44943.9583 | 0 | 11.4961 | 37.78
2023-01-17 23:30 | 44943.9792 | 0 | 10.9964 | 37.78
2023-01-18 | 44944 | 0 | 10.2954 | 37.78
2023-01-18 00:30 | 44944.0208 | 0 | 9.7897 | 37.78
2023-01-18 01:00 | 44944.0417 | 0 | 9.4713 | 37.78
2023-01-18 01:30 | 44944.0625 | 0 | 9.3042 | 37.78
2023-01-18 02:00 | 44944.0833 | 0 | 9.1787 | 37.78
2023-01-18 02:30 | 44944.1042 | 0 | 9.3353 | 37.78
2023-01-18 03:00 | 44944.125 | 0 | 8.9956 | 37.78
2023-01-18 03:30 | 44944.1458 | 0 | 9.1757 | 37.78
2023-01-18 04:00 | 44944.1667 | 0 | 9.3193 | 37.78
2023-01-18 04:30 | 44944.1875 | 0 | 9.7067 | 37.78
2023-01-18 05:00 | 44944.2083 | 0 | 10.1608 | 37.78
2023-01-18 05:30 | 44944.2292 | 0 | 10.4648 | 37.78
2023-01-18 06:00 | 44944.25 | 0 | 10.7049 | 37.78
2023-01-18 06:30 | 44944.2708 | 0 | 11.4739 | 37.78
2023-01-18 07:00 | 44944.2917 | 0 | 11.8312 | 37.78
2023-01-18 07:30 | 44944.3125 | 0 | 12.3798 | 37.78
2023-01-18 08:00 | 44944.3333 | 0 | 13.6463 | 37.78
2023-01-18 08:30 | 44944.3542 | 0 | 13.4381 | 37.78
2023-01-18 09:00 | 44944.375 | 0 | 11.7735 | 37.78
2023-01-18 09:30 | 44944.3958 | 0 | 10.2378 | 37.78
2023-01-18 10:00 | 44944.4167 | 0 | 10.4238 | 37.78
2023-01-18 10:30 | 44944.4375 | 0 | 10.8532 | 37.78
2023-01-18 11:00 | 44944.4583 | 0 | 10.6186 | 37.78
2023-01-18 11:30 | 44944.4792 | 0 | 10.5684 | 37.78
2023-01-18 12:00 | 44944.5 | 0 | 11.4737 | 37.78
2023-01-18 12:30 | 44944.5208 | 0 | 12.2636 | 37.78
2023-01-18 13:00 | 44944.5417 | 0 | 13.3273 | 37.78
2023-01-18 13:30 | 44944.5625 | 0 | 12.8373 | 37.78
2023-01-18 14:00 | 44944.5833 | 0 | 12.9507 | 37.78
2023-01-18 14:30 | 44944.6042 | 0 | 12.2788 | 37.78
2023-01-18 15:00 | 44944.625 | 0 | 14.3939 | 37.78
2023-01-18 15:30 | 44944.6458 | 0 | 13.4531 | 37.78
2023-01-18 16:00 | 44944.6667 | 0 | 13.8293 | 37.78
2023-01-18 16:30 | 44944.6875 | 0 | 14.6217 | 37.78
2023-01-18 17:00 | 44944.7083 | 0 | 15.1235 | 37.78
2023-01-18 17:30 | 44944.7292 | 0 | 15.6481 | 37.78
2023-01-18 18:00 | 44944.75 | 0 | 15.5997 | 37.78
2023-01-18 18:30 | 44944.7708 | 0 | 15.7255 | 37.78
2023-01-18 19:00 | 44944.7917 | 0 | 15.8583 | 37.78
2023-01-18 19:30 | 44944.8125 | 0 | 15.5569 | 37.78
2023-01-18 20:00 | 44944.8333 | 0 | 15.2169 | 37.78
2023-01-18 20:30 | 44944.8542 | 0 | 14.5197 | 37.78
2023-01-18 21:00 | 44944.875 | 0 | 14.0987 | 37.78
2023-01-18 21:30 | 44944.8958 | 0 | 13.5325 | 37.78
2023-01-18 22:00 | 44944.9167 | 0 | 12.7628 | 37.78
2023-01-18 22:30 | 44944.9375 | 0 | 11.6945 | 37.78
2023-01-18 23:00 | 44944.9583 | 0 | 11.0521 | 37.78
2023-01-18 23:30 | 44944.9792 | 0 | 10.371 | 37.78
2023-01-19 | 44945 | 0 | 9.8752 | 37.78
2023-01-19 00:30 | 44945.0208 | 0 | 9.5018 | 37.78
2023-01-19 01:00 | 44945.0417 | 0 | 9.3196 | 37.78
2023-01-19 01:30 | 44945.0625 | 0 | 9.0656 | 37.78
2023-01-19 02:00 | 44945.0833 | 0 | 8.9962 | 37.78
2023-01-19 02:30 | 44945.1042 | 0 | 9.0575 | 37.78
2023-01-19 03:00 | 44945.125 | 0 | 8.8178 | 37.78
2023-01-19 03:30 | 44945.1458 | 0 | 9.0736 | 37.78
2023-01-19 04:00 | 44945.1667 | 0 | 9.3267 | 37.78
2023-01-19 04:30 | 44945.1875 | 0 | 9.5337 | 37.78
2023-01-19 05:00 | 44945.2083 | 0 | 9.8989 | 37.78
2023-01-19 05:30 | 44945.2292 | 0 | 10.2572 | 37.78
2023-01-19 06:00 | 44945.25 | 0 | 10.5557 | 37.78
2023-01-19 06:30 | 44945.2708 | 0 | 10.8138 | 37.78
2023-01-19 07:00 | 44945.2917 | 0 | 10.9758 | 37.78
2023-01-19 07:30 | 44945.3125 | 0 | 10.7429 | 37.78
2023-01-19 08:00 | 44945.3333 | 0 | 10.9421 | 37.78
2023-01-19 08:30 | 44945.3542 | 0 | 11.1962 | 37.78
2023-01-19 09:00 | 44945.375 | 0 | 10.9755 | 37.78
2023-01-19 09:30 | 44945.3958 | 0 | 10.6637 | 37.78
2023-01-19 10:00 | 44945.4167 | 0 | 10.6095 | 37.78
2023-01-19 10:30 | 44945.4375 | 0 | 10.441 | 37.78
2023-01-19 11:00 | 44945.4583 | 0 | 10.427 | 37.78
2023-01-19 11:30 | 44945.4792 | 0 | 10.6624 | 37.78
2023-01-19 12:00 | 44945.5 | 0 | 10.879 | 37.78
2023-01-19 12:30 | 44945.5208 | 0 | 11.0436 | 37.78
2023-01-19 13:00 | 44945.5417 | 0 | 11.7481 | 37.78
2023-01-19 13:30 | 44945.5625 | 0 | 12.3145 | 37.78
2023-01-19 14:00 | 44945.5833 | 0 | 12.6952 | 37.78
2023-01-19 14:30 | 44945.6042 | 0 | 13.384 | 37.78
2023-01-19 15:00 | 44945.625 | 0 | 14.1681 | 37.78
2023-01-19 15:30 | 44945.6458 | 0 | 14.893 | 37.78
2023-01-19 16:00 | 44945.6667 | 0 | 15.5953 | 37.78
2023-01-19 16:30 | 44945.6875 | 0 | 16.2071 | 37.78
2023-01-19 17:00 | 44945.7083 | 0 | 16.3779 | 37.78
2023-01-19 17:30 | 44945.7292 | 0 | 16.7872 | 37.78
2023-01-19 18:00 | 44945.75 | 0 | 16.8927 | 37.78
2023-01-19 18:30 | 44945.7708 | 0 | 16.8156 | 37.78
2023-01-19 19:00 | 44945.7917 | 0 | 16.9937 | 37.78
2023-01-19 19:30 | 44945.8125 | 0 | 16.8427 | 37.78
2023-01-19 20:00 | 44945.8333 | 0 | 16.5981 | 37.78
2023-01-19 20:30 | 44945.8542 | 0 | 15.7367 | 37.78
2023-01-19 21:00 | 44945.875 | 0 | 15.5796 | 37.78
2023-01-19 21:30 | 44945.8958 | 0 | 15.0984 | 37.78
2023-01-19 22:00 | 44945.9167 | 0 | 14.4541 | 37.78
2023-01-19 22:30 | 44945.9375 | 0 | 13.3308 | 37.78
2023-01-19 23:00 | 44945.9583 | 0 | 12.566 | 37.78
2023-01-19 23:30 | 44945.9792 | 0 | 11.8502 | 37.78
2023-01-20 | 44946 | 0 | 11.3212 | 37.78
2023-01-20 00:30 | 44946.0208 | 0 | 10.8088 | 37.78
2023-01-20 01:00 | 44946.0417 | 0 | 10.502 | 37.78
2023-01-20 01:30 | 44946.0625 | 0 | 10.189 | 37.78
2023-01-20 02:00 | 44946.0833 | 0 | 10.1876 | 37.78
2023-01-20 02:30 | 44946.1042 | 0 | 10.1164 | 37.78
2023-01-20 03:00 | 44946.125 | 0 | 9.8779 | 37.78
2023-01-20 03:30 | 44946.1458 | 0 | 9.9088 | 37.78
2023-01-20 04:00 | 44946.1667 | 0 | 10.1804 | 37.78
2023-01-20 04:30 | 44946.1875 | 0 | 10.3281 | 37.78
2023-01-20 05:00 | 44946.2083 | 0 | 10.8861 | 37.78
2023-01-20 05:30 | 44946.2292 | 0 | 11.2595 | 37.78
2023-01-20 06:00 | 44946.25 | 0 | 12.1862 | 37.78
2023-01-20 06:30 | 44946.2708 | 0 | 13.0094 | 37.78
2023-01-20 07:00 | 44946.2917 | 0 | 13.5668 | 37.78
2023-01-20 07:30 | 44946.3125 | 0 | 1.4698 | 37.78
2023-01-20 08:00 | 44946.3333 | 0 | 0.022333 | 37.78
2023-01-20 08:30 | 44946.3542 | 0 | 0.022333 | 37.78
2023-01-20 09:00 | 44946.375 | 0 | 0.022333 | 37.78
2023-01-20 09:30 | 44946.3958 | 0 | 0.022333 | 37.78
2023-01-20 10:00 | 44946.4167 | 0 | 0.022333 | 37.78
2023-01-20 10:30 | 44946.4375 | 0 | 0.03603 | 37.78
2023-01-20 11:00 | 44946.4583 | 0 | 0.044665 | 37.78
2023-01-20 11:30 | 44946.4792 | 0 | 0.030968 | 37.78
2023-01-20 12:00 | 44946.5 | 0 | 0.022333 | 37.78
2023-01-20 12:30 | 44946.5208 | 0 | 0.022333 | 37.78
2023-01-20 13:00 | 44946.5417 | 0 | 0.022333 | 37.78
2023-01-20 13:30 | 44946.5625 | 0 | 4.9659 | 37.78
2023-01-20 14:00 | 44946.5833 | 0 | 12.2545 | 37.78
2023-01-20 14:30 | 44946.6042 | 0 | 12.3475 | 37.78
2023-01-20 15:00 | 44946.625 | 0 | 13.1459 | 37.78
2023-01-20 15:30 | 44946.6458 | 0 | 15.2078 | 37.78
2023-01-20 16:00 | 44946.6667 | 0 | 14.6057 | 37.78
2023-01-20 16:30 | 44946.6875 | 0 | 14.0303 | 37.78
2023-01-20 17:00 | 44946.7083 | 0 | 14.0017 | 37.78
2023-01-20 17:30 | 44946.7292 | 0 | 13.9671 | 37.78
2023-01-20 18:00 | 44946.75 | 0 | 13.9311 | 37.78
2023-01-20 18:30 | 44946.7708 | 0 | 14.3109 | 37.78
2023-01-20 19:00 | 44946.7917 | 0 | 14.3858 | 37.78
2023-01-20 19:30 | 44946.8125 | 0 | 14.2857 | 37.78
2023-01-20 20:00 | 44946.8333 | 0 | 14.0359 | 37.78
2023-01-20 20:30 | 44946.8542 | 0 | 13.5151 | 37.78
2023-01-20 21:00 | 44946.875 | 0 | 13.0825 | 37.78
2023-01-20 21:30 | 44946.8958 | 0 | 12.7393 | 37.78
2023-01-20 22:00 | 44946.9167 | 0 | 12.2843 | 37.78
2023-01-20 22:30 | 44946.9375 | 0 | 11.5345 | 37.78
2023-01-20 23:00 | 44946.9583 | 0 | 10.9064 | 37.78
2023-01-20 23:30 | 44946.9792 | 0 | 10.3254 | 37.78
2023-01-21 | 44947 | 0 | 9.9489 | 37.78
2023-01-21 00:30 | 44947.0208 | 0 | 9.5441 | 37.78
2023-01-21 01:00 | 44947.0417 | 0 | 9.3666 | 37.78
2023-01-21 01:30 | 44947.0625 | 0 | 9.0304 | 37.78
2023-01-21 02:00 | 44947.0833 | 0 | 9.0236 | 37.78
2023-01-21 02:30 | 44947.1042 | 0 | 8.9602 | 37.78
2023-01-21 03:00 | 44947.125 | 0 | 8.7639 | 37.78
2023-01-21 03:30 | 44947.1458 | 0 | 8.758 | 37.78
2023-01-21 04:00 | 44947.1667 | 0 | 8.7246 | 37.78
2023-01-21 04:30 | 44947.1875 | 0 | 8.615 | 37.78
2023-01-21 05:00 | 44947.2083 | 0 | 8.5201 | 37.78
2023-01-21 05:30 | 44947.2292 | 0 | 8.4581 | 37.78
2023-01-21 06:00 | 44947.25 | 0 | 8.398 | 37.78
2023-01-21 06:30 | 44947.2708 | 0 | 7.8443 | 37.78
2023-01-21 07:00 | 44947.2917 | 0 | 7.7608 | 37.78
2023-01-21 07:30 | 44947.3125 | 0 | 7.4079 | 37.78
2023-01-21 08:00 | 44947.3333 | 0 | 7.3668 | 37.78
2023-01-21 08:30 | 44947.3542 | 0 | 7.3716 | 37.78
2023-01-21 09:00 | 44947.375 | 0 | 7.7197 | 37.78
2023-01-21 09:30 | 44947.3958 | 0 | 8.0861 | 37.78
2023-01-21 10:00 | 44947.4167 | 0 | 8.4148 | 37.78
2023-01-21 10:30 | 44947.4375 | 0 | 9.2451 | 37.78
2023-01-21 11:00 | 44947.4583 | 0 | 9.2517 | 37.78
2023-01-21 11:30 | 44947.4792 | 0 | 9.6822 | 37.78
2023-01-21 12:00 | 44947.5 | 0 | 8.3481 | 37.78
2023-01-21 12:30 | 44947.5208 | 0 | 8.3421 | 37.78
2023-01-21 13:00 | 44947.5417 | 0 | 9.1601 | 37.78
2023-01-21 13:30 | 44947.5625 | 0 | 10.9722 | 37.78
2023-01-21 14:00 | 44947.5833 | 0 | 9.1946 | 37.78
2023-01-21 14:30 | 44947.6042 | 0 | 8.5176 | 37.78
2023-01-21 15:00 | 44947.625 | 0 | 9.6204 | 37.78
2023-01-21 15:30 | 44947.6458 | 0 | 10.2018 | 37.78
2023-01-21 16:00 | 44947.6667 | 0 | 11.1384 | 37.78
2023-01-21 16:30 | 44947.6875 | 0 | 11.8437 | 37.78
2023-01-21 17:00 | 44947.7083 | 0 | 12.8763 | 37.78
2023-01-21 17:30 | 44947.7292 | 0 | 12.763 | 37.78
2023-01-21 18:00 | 44947.75 | 0 | 12.9824 | 37.78
2023-01-21 18:30 | 44947.7708 | 0 | 13.1453 | 37.78
2023-01-21 19:00 | 44947.7917 | 0 | 13.2604 | 37.78
2023-01-21 19:30 | 44947.8125 | 0 | 13.03 | 37.78
2023-01-21 20:00 | 44947.8333 | 0 | 12.6881 | 37.78
2023-01-21 20:30 | 44947.8542 | 0 | 12.3049 | 37.78
2023-01-21 21:00 | 44947.875 | 0 | 11.9974 | 37.78
2023-01-21 21:30 | 44947.8958 | 0 | 11.5097 | 37.78
2023-01-21 22:00 | 44947.9167 | 0 | 11.1884 | 37.78
2023-01-21 22:30 | 44947.9375 | 0 | 10.536 | 37.78
2023-01-21 23:00 | 44947.9583 | 0 | 10.113 | 37.78
2023-01-21 23:30 | 44947.9792 | 0 | 9.5503 | 37.78
2023-01-22 | 44948 | 0 | 9.1014 | 37.78
2023-01-22 00:30 | 44948.0208 | 0 | 8.7176 | 37.78
2023-01-22 01:00 | 44948.0417 | 0 | 8.4512 | 37.78
2023-01-22 01:30 | 44948.0625 | 0 | 8.2193 | 37.78
2023-01-22 02:00 | 44948.0833 | 0 | 8.1487 | 37.78
2023-01-22 02:30 | 44948.1042 | 0 | 7.9963 | 37.78
2023-01-22 03:00 | 44948.125 | 0 | 7.8575 | 37.78
2023-01-22 03:30 | 44948.1458 | 0 | 7.8575 | 37.78
2023-01-22 04:00 | 44948.1667 | 0 | 7.8137 | 37.78
2023-01-22 04:30 | 44948.1875 | 0 | 7.7652 | 37.78
2023-01-22 05:00 | 44948.2083 | 0 | 7.6949 | 37.78
2023-01-22 05:30 | 44948.2292 | 0 | 7.7369 | 37.78
2023-01-22 06:00 | 44948.25 | 0 | 7.4668 | 37.78
2023-01-22 06:30 | 44948.2708 | 0 | 7.0557 | 37.78
2023-01-22 07:00 | 44948.2917 | 0 | 7.5949 | 37.78
2023-01-22 07:30 | 44948.3125 | 0 | 7.7589 | 37.78
2023-01-22 08:00 | 44948.3333 | 0 | 6.6222 | 37.78
2023-01-22 08:30 | 44948.3542 | 0 | 5.9822 | 37.78
2023-01-22 09:00 | 44948.375 | 0 | 6.3073 | 37.78
2023-01-22 09:30 | 44948.3958 | 0 | 7.0365 | 37.78
2023-01-22 10:00 | 44948.4167 | 0 | 7.5998 | 37.78
2023-01-22 10:30 | 44948.4375 | 0 | 8.4246 | 37.78
2023-01-22 11:00 | 44948.4583 | 0 | 6.6769 | 37.78
2023-01-22 11:30 | 44948.4792 | 0 | 6.5214 | 37.78
2023-01-22 12:00 | 44948.5 | 0 | 6.5762 | 37.78
2023-01-22 12:30 | 44948.5208 | 0 | 7.1403 | 37.78
2023-01-22 13:00 | 44948.5417 | 0 | 10.0226 | 37.78
2023-01-22 13:30 | 44948.5625 | 0 | 10.175 | 37.78
2023-01-22 14:00 | 44948.5833 | 0 | 8.7108 | 37.78
2023-01-22 14:30 | 44948.6042 | 0 | 10.2178 | 37.78
2023-01-22 15:00 | 44948.625 | 0 | 9.0834 | 37.78
2023-01-22 15:30 | 44948.6458 | 0 | 11.494 | 37.78
2023-01-22 16:00 | 44948.6667 | 0 | 11.0972 | 37.78
2023-01-22 16:30 | 44948.6875 | 0 | 11.8743 | 37.78
2023-01-22 17:00 | 44948.7083 | 0 | 12.888 | 37.78
2023-01-22 17:30 | 44948.7292 | 0 | 13.6495 | 37.78
2023-01-22 18:00 | 44948.75 | 0 | 14.2366 | 37.78
2023-01-22 18:30 | 44948.7708 | 0 | 14.2941 | 37.78
2023-01-22 19:00 | 44948.7917 | 0 | 14.5317 | 37.78
2023-01-22 19:30 | 44948.8125 | 0 | 14.1832 | 37.78
2023-01-22 20:00 | 44948.8333 | 0 | 13.8861 | 37.78
2023-01-22 20:30 | 44948.8542 | 0 | 13.3057 | 37.78
2023-01-22 21:00 | 44948.875 | 0 | 12.8377 | 37.78
2023-01-22 21:30 | 44948.8958 | 0 | 12.0648 | 37.78
2023-01-22 22:00 | 44948.9167 | 0 | 11.4856 | 37.78
2023-01-22 22:30 | 44948.9375 | 0 | 10.5914 | 37.78
2023-01-22 23:00 | 44948.9583 | 0 | 9.9604 | 37.78
2023-01-22 23:30 | 44948.9792 | 0 | 9.5727 | 37.78
2023-01-23 | 44949 | 0 | 9.2407 | 37.78
2023-01-23 00:30 | 44949.0208 | 0 | 8.9697 | 37.78
2023-01-23 01:00 | 44949.0417 | 0 | 8.7298 | 37.78
2023-01-23 01:30 | 44949.0625 | 0 | 8.6978 | 37.78
2023-01-23 02:00 | 44949.0833 | 0 | 8.6311 | 37.78
2023-01-23 02:30 | 44949.1042 | 0 | 8.6228 | 37.78
2023-01-23 03:00 | 44949.125 | 0 | 8.5186 | 37.78
2023-01-23 03:30 | 44949.1458 | 0 | 8.5201 | 37.78
2023-01-23 04:00 | 44949.1667 | 0 | 8.8434 | 37.78
2023-01-23 04:30 | 44949.1875 | 0 | 9.2158 | 37.78
2023-01-23 05:00 | 44949.2083 | 0 | 9.7102 | 37.78
2023-01-23 05:30 | 44949.2292 | 0 | 9.9547 | 37.78
2023-01-23 06:00 | 44949.25 | 0 | 10.8663 | 37.78
2023-01-23 06:30 | 44949.2708 | 0 | 11.237 | 37.78
2023-01-23 07:00 | 44949.2917 | 0 | 12.7872 | 37.78
2023-01-23 07:30 | 44949.3125 | 0 | 22.5956 | 37.78
2023-01-23 08:00 | 44949.3333 | 0 | 23.6767 | 37.78
2023-01-23 08:30 | 44949.3542 | 0 | 24.4665 | 37.78
2023-01-23 09:00 | 44949.375 | 0 | 22.8606 | 37.78
2023-01-23 09:30 | 44949.3958 | 0 | 22.7696 | 37.78
2023-01-23 10:00 | 44949.4167 | 0 | 27.9491 | 37.78
2023-01-23 10:30 | 44949.4375 | 0 | 29.084 | 37.78
2023-01-23 11:00 | 44949.4583 | 0 | 24.815 | 37.78
2023-01-23 11:30 | 44949.4792 | 0 | 22.1899 | 37.78
2023-01-23 12:00 | 44949.5 | 0 | 23.6394 | 37.78
2023-01-23 12:30 | 44949.5208 | 0 | 18.5581 | 37.78
2023-01-23 13:00 | 44949.5417 | 0 | 12.3272 | 37.78
2023-01-23 13:30 | 44949.5625 | 0 | 12.8513 | 37.78
2023-01-23 14:00 | 44949.5833 | 0 | 13.2656 | 37.78
2023-01-23 14:30 | 44949.6042 | 0 | 13.6348 | 37.78
2023-01-23 15:00 | 44949.625 | 0 | 14.4563 | 37.78
2023-01-23 15:30 | 44949.6458 | 0 | 15.4287 | 37.78
2023-01-23 16:00 | 44949.6667 | 0 | 15.9264 | 37.78
2023-01-23 16:30 | 44949.6875 | 0 | 17.0903 | 37.78
2023-01-23 17:00 | 44949.7083 | 0 | 17.1186 | 37.78
2023-01-23 17:30 | 44949.7292 | 0 | 18.086 | 37.78
2023-01-23 18:00 | 44949.75 | 0 | 17.9867 | 37.78
2023-01-23 18:30 | 44949.7708 | 0 | 17.7323 | 37.78
2023-01-23 19:00 | 44949.7917 | 0 | 17.7464 | 37.78
2023-01-23 19:30 | 44949.8125 | 0 | 17.5704 | 37.78
2023-01-23 20:00 | 44949.8333 | 0 | 17.0973 | 37.78
2023-01-23 20:30 | 44949.8542 | 0 | 16.3242 | 37.78
2023-01-23 21:00 | 44949.875 | 0 | 15.7671 | 37.78
2023-01-23 21:30 | 44949.8958 | 0 | 15.0371 | 37.78
2023-01-23 22:00 | 44949.9167 | 0 | 14.0692 | 37.78
2023-01-23 22:30 | 44949.9375 | 0 | 13.0608 | 37.78
2023-01-23 23:00 | 44949.9583 | 0 | 12.478 | 37.78
2023-01-23 23:30 | 44949.9792 | 0 | 12.0976 | 37.78
2023-01-24 | 44950 | 0 | 11.4754 | 37.78
2023-01-24 00:30 | 44950.0208 | 0 | 10.871 | 37.78
2023-01-24 01:00 | 44950.0417 | 0 | 10.5985 | 37.78
2023-01-24 01:30 | 44950.0625 | 0 | 10.4103 | 37.78
2023-01-24 02:00 | 44950.0833 | 0 | 10.1724 | 37.78
2023-01-24 02:30 | 44950.1042 | 0 | 10.2233 | 37.78
2023-01-24 03:00 | 44950.125 | 0 | 10.03 | 37.78
2023-01-24 03:30 | 44950.1458 | 0 | 10.1596 | 37.78
2023-01-24 04:00 | 44950.1667 | 0 | 10.6132 | 37.78
2023-01-24 04:30 | 44950.1875 | 0 | 10.7807 | 37.78
2023-01-24 05:00 | 44950.2083 | 0 | 11.2358 | 37.78
2023-01-24 05:30 | 44950.2292 | 0 | 11.5689 | 37.78
2023-01-24 06:00 | 44950.25 | 0 | 12.3175 | 37.78
2023-01-24 06:30 | 44950.2708 | 0 | 13.7731 | 37.78
2023-01-24 07:00 | 44950.2917 | 0 | 14.8802 | 37.78
2023-01-24 07:30 | 44950.3125 | 0 | 15.2064 | 37.78
2023-01-24 08:00 | 44950.3333 | 0 | 14.8926 | 37.78
2023-01-24 08:30 | 44950.3542 | 0 | 15.0263 | 37.78
2023-01-24 09:00 | 44950.375 | 0 | 15.1589 | 37.78
2023-01-24 09:30 | 44950.3958 | 0 | 15.4503 | 37.78
2023-01-24 10:00 | 44950.4167 | 0 | 14.484 | 37.78
2023-01-24 10:30 | 44950.4375 | 0 | 14.0859 | 37.78
2023-01-24 11:00 | 44950.4583 | 0 | 12.4772 | 37.78
2023-01-24 11:30 | 44950.4792 | 0 | 12.8283 | 37.78
2023-01-24 12:00 | 44950.5 | 0 | 12.1203 | 37.78
2023-01-24 12:30 | 44950.5208 | 0 | 12.8323 | 37.78
2023-01-24 13:00 | 44950.5417 | 0 | 13.6491 | 37.78
2023-01-24 13:30 | 44950.5625 | 0 | 14.9946 | 37.78
2023-01-24 14:00 | 44950.5833 | 0 | 16.3852 | 37.78
2023-01-24 14:30 | 44950.6042 | 0 | 16.6601 | 37.78
2023-01-24 15:00 | 44950.625 | 0 | 16.2523 | 37.78
2023-01-24 15:30 | 44950.6458 | 0 | 16.2359 | 37.78
2023-01-24 16:00 | 44950.6667 | 0 | 18.6854 | 37.78
2023-01-24 16:30 | 44950.6875 | 0 | 18.4976 | 37.78
2023-01-24 17:00 | 44950.7083 | 0 | 17.9547 | 37.78
2023-01-24 17:30 | 44950.7292 | 0 | 18.1761 | 37.78
2023-01-24 18:00 | 44950.75 | 0 | 18.102 | 37.78
2023-01-24 18:30 | 44950.7708 | 0 | 18.8955 | 37.78
2023-01-24 19:00 | 44950.7917 | 0 | 18.4539 | 37.78
2023-01-24 19:30 | 44950.8125 | 0 | 17.085 | 37.78
2023-01-24 20:00 | 44950.8333 | 0 | 16.2691 | 37.78
2023-01-24 20:30 | 44950.8542 | 0 | 15.468 | 37.78
2023-01-24 21:00 | 44950.875 | 0 | 14.8566 | 37.78
2023-01-24 21:30 | 44950.8958 | 0 | 14.18 | 37.78
2023-01-24 22:00 | 44950.9167 | 0 | 13.213 | 37.78
2023-01-24 22:30 | 44950.9375 | 0 | 12.3831 | 37.78
2023-01-24 23:00 | 44950.9583 | 0 | 11.6517 | 37.78
2023-01-24 23:30 | 44950.9792 | 0 | 11.0769 | 37.78
2023-01-25 | 44951 | 0 | 10.5572 | 37.78
2023-01-25 00:30 | 44951.0208 | 0 | 10.3076 | 37.78
2023-01-25 01:00 | 44951.0417 | 0 | 10.1944 | 37.78
2023-01-25 01:30 | 44951.0625 | 0 | 9.8994 | 37.78
2023-01-25 02:00 | 44951.0833 | 0 | 9.8785 | 37.78
2023-01-25 02:30 | 44951.1042 | 0 | 9.8103 | 37.78
2023-01-25 03:00 | 44951.125 | 0 | 9.687 | 37.78
2023-01-25 03:30 | 44951.1458 | 0 | 9.7186 | 37.78
2023-01-25 04:00 | 44951.1667 | 0 | 10.1078 | 37.78
2023-01-25 04:30 | 44951.1875 | 0 | 10.4151 | 37.78
2023-01-25 05:00 | 44951.2083 | 0 | 10.9201 | 37.78
2023-01-25 05:30 | 44951.2292 | 0 | 11.4471 | 37.78
2023-01-25 06:00 | 44951.25 | 0 | 11.3911 | 37.78
2023-01-25 06:30 | 44951.2708 | 0 | 12.3637 | 37.78
2023-01-25 07:00 | 44951.2917 | 0 | 12.7803 | 37.78
2023-01-25 07:30 | 44951.3125 | 0 | 12.6748 | 37.78
2023-01-25 08:00 | 44951.3333 | 0 | 13.3406 | 37.78
2023-01-25 08:30 | 44951.3542 | 0 | 13.1397 | 37.78
2023-01-25 09:00 | 44951.375 | 0 | 13.7632 | 37.78
2023-01-25 09:30 | 44951.3958 | 0 | 12.7313 | 37.78
2023-01-25 10:00 | 44951.4167 | 0 | 13.2382 | 37.78
2023-01-25 10:30 | 44951.4375 | 0 | 14.8281 | 37.78
2023-01-25 11:00 | 44951.4583 | 0 | 14.2577 | 37.78
2023-01-25 11:30 | 44951.4792 | 0 | 15.381 | 37.78
2023-01-25 12:00 | 44951.5 | 0 | 16.5089 | 37.78
2023-01-25 12:30 | 44951.5208 | 0 | 17.0648 | 37.78
2023-01-25 13:00 | 44951.5417 | 0 | 18.495 | 37.78
2023-01-25 13:30 | 44951.5625 | 0 | 18.2476 | 37.78
2023-01-25 14:00 | 44951.5833 | 0 | 17.3459 | 37.78
2023-01-25 14:30 | 44951.6042 | 0 | 16.4309 | 37.78
2023-01-25 15:00 | 44951.625 | 0 | 17.6824 | 37.78
2023-01-25 15:30 | 44951.6458 | 0 | 19.0174 | 37.78
2023-01-25 16:00 | 44951.6667 | 0 | 19.6905 | 37.78
2023-01-25 16:30 | 44951.6875 | 0 | 19.9291 | 37.78
2023-01-25 17:00 | 44951.7083 | 0 | 19.3215 | 37.78
2023-01-25 17:30 | 44951.7292 | 0 | 19.3782 | 37.78
2023-01-25 18:00 | 44951.75 | 0 | 19.4673 | 37.78
2023-01-25 18:30 | 44951.7708 | 0 | 19.4916 | 37.78
2023-01-25 19:00 | 44951.7917 | 0 | 19.6417 | 37.78
2023-01-25 19:30 | 44951.8125 | 0 | 19.3719 | 37.78
2023-01-25 20:00 | 44951.8333 | 0 | 18.8826 | 37.78
2023-01-25 20:30 | 44951.8542 | 0 | 17.9875 | 37.78
2023-01-25 21:00 | 44951.875 | 0 | 17.5006 | 37.78
2023-01-25 21:30 | 44951.8958 | 0 | 16.5895 | 37.78
2023-01-25 22:00 | 44951.9167 | 0 | 15.6438 | 37.78
2023-01-25 22:30 | 44951.9375 | 0 | 14.8783 | 37.78
2023-01-25 23:00 | 44951.9583 | 0 | 14.0573 | 37.78
2023-01-25 23:30 | 44951.9792 | 0 | 13.4781 | 37.78
2023-01-26 | 44952 | 0 | 12.6803 | 37.78
2023-01-26 00:30 | 44952.0208 | 0 | 12.0248 | 37.78
2023-01-26 01:00 | 44952.0417 | 0 | 11.4546 | 37.78
2023-01-26 01:30 | 44952.0625 | 0 | 11.1021 | 37.78
2023-01-26 02:00 | 44952.0833 | 0 | 10.8141 | 37.78
2023-01-26 02:30 | 44952.1042 | 0 | 10.6762 | 37.78
2023-01-26 03:00 | 44952.125 | 0 | 10.4204 | 37.78
2023-01-26 03:30 | 44952.1458 | 0 | 10.3798 | 37.78
2023-01-26 04:00 | 44952.1667 | 0 | 10.3498 | 37.78
2023-01-26 04:30 | 44952.1875 | 0 | 10.3612 | 37.78
2023-01-26 05:00 | 44952.2083 | 0 | 10.3972 | 37.78
2023-01-26 05:30 | 44952.2292 | 0 | 10.3237 | 37.78
2023-01-26 06:00 | 44952.25 | 0 | 10.1274 | 37.78
2023-01-26 06:30 | 44952.2708 | 0 | 10.2729 | 37.78
2023-01-26 07:00 | 44952.2917 | 0 | 10.6255 | 37.78
2023-01-26 07:30 | 44952.3125 | 0 | 10.8685 | 37.78
2023-01-26 08:00 | 44952.3333 | 0 | 11.049 | 37.78
2023-01-26 08:30 | 44952.3542 | 0 | 10.292 | 37.78
2023-01-26 09:00 | 44952.375 | 0 | 10.2544 | 37.78
2023-01-26 09:30 | 44952.3958 | 0 | 11.9889 | 37.78
2023-01-26 10:00 | 44952.4167 | 0 | 11.6236 | 37.78
2023-01-26 10:30 | 44952.4375 | 0 | 11.5212 | 37.78
2023-01-26 11:00 | 44952.4583 | 0 | 11.6088 | 37.78
2023-01-26 11:30 | 44952.4792 | 0 | 12.7411 | 37.78
2023-01-26 12:00 | 44952.5 | 0 | 13.1677 | 37.78
2023-01-26 12:30 | 44952.5208 | 0 | 13.6965 | 37.78
2023-01-26 13:00 | 44952.5417 | 0 | 13.6746 | 37.78
2023-01-26 13:30 | 44952.5625 | 0 | 14.903 | 37.78
2023-01-26 14:00 | 44952.5833 | 0 | 16.1982 | 37.78
2023-01-26 14:30 | 44952.6042 | 0 | 15.6683 | 37.78
2023-01-26 15:00 | 44952.625 | 0 | 14.9834 | 37.78
2023-01-26 15:30 | 44952.6458 | 0 | 16.8213 | 37.78
2023-01-26 16:00 | 44952.6667 | 0 | 17.5107 | 37.78
2023-01-26 16:30 | 44952.6875 | 0 | 17.8701 | 37.78
2023-01-26 17:00 | 44952.7083 | 0 | 17.1389 | 37.78
2023-01-26 17:30 | 44952.7292 | 0 | 18.152 | 37.78
2023-01-26 18:00 | 44952.75 | 0 | 18.3836 | 37.78
2023-01-26 18:30 | 44952.7708 | 0 | 18.7171 | 37.78
2023-01-26 19:00 | 44952.7917 | 0 | 18.6353 | 37.78
2023-01-26 19:30 | 44952.8125 | 0 | 18.5712 | 37.78
2023-01-26 20:00 | 44952.8333 | 0 | 18.1346 | 37.78
2023-01-26 20:30 | 44952.8542 | 0 | 17.3412 | 37.78
2023-01-26 21:00 | 44952.875 | 0 | 16.48 | 37.78
2023-01-26 21:30 | 44952.8958 | 0 | 15.7796 | 37.78
2023-01-26 22:00 | 44952.9167 | 0 | 14.8049 | 37.78
2023-01-26 22:30 | 44952.9375 | 0 | 13.5128 | 37.78
2023-01-26 23:00 | 44952.9583 | 0 | 12.9383 | 37.78
2023-01-26 23:30 | 44952.9792 | 0 | 12.3067 | 37.78
2023-01-27 | 44953 | 0 | 11.8056 | 37.78
2023-01-27 00:30 | 44953.0208 | 0 | 11.5481 | 37.78
2023-01-27 01:00 | 44953.0417 | 0 | 11.2145 | 37.78
2023-01-27 01:30 | 44953.0625 | 0 | 10.9376 | 37.78
2023-01-27 02:00 | 44953.0833 | 0 | 10.822 | 37.78
2023-01-27 02:30 | 44953.1042 | 0 | 10.6527 | 37.78
2023-01-27 03:00 | 44953.125 | 0 | 10.4135 | 37.78
2023-01-27 03:30 | 44953.1458 | 0 | 10.6551 | 37.78
2023-01-27 04:00 | 44953.1667 | 0 | 11.0072 | 37.78
2023-01-27 04:30 | 44953.1875 | 0 | 11.3956 | 37.78
2023-01-27 05:00 | 44953.2083 | 0 | 11.8633 | 37.78
2023-01-27 05:30 | 44953.2292 | 0 | 12.4522 | 37.78
2023-01-27 06:00 | 44953.25 | 0 | 12.8943 | 37.78
2023-01-27 06:30 | 44953.2708 | 0 | 13.6445 | 37.78
2023-01-27 07:00 | 44953.2917 | 0 | 14.4008 | 37.78
2023-01-27 07:30 | 44953.3125 | 0 | 15.0232 | 37.78
2023-01-27 08:00 | 44953.3333 | 0 | 14.8409 | 37.78
2023-01-27 08:30 | 44953.3542 | 0 | 15.6054 | 37.78
2023-01-27 09:00 | 44953.375 | 0 | 16.7391 | 37.78
2023-01-27 09:30 | 44953.3958 | 0 | 16.9577 | 37.78
2023-01-27 10:00 | 44953.4167 | 0 | 16.9724 | 37.78
2023-01-27 10:30 | 44953.4375 | 0 | 15.8658 | 37.78
2023-01-27 11:00 | 44953.4583 | 0 | 13.6868 | 37.78
2023-01-27 11:30 | 44953.4792 | 0 | 14.3925 | 37.78
2023-01-27 12:00 | 44953.5 | 0 | 14.3 | 37.78
2023-01-27 12:30 | 44953.5208 | 0 | 14.6101 | 37.78
2023-01-27 13:00 | 44953.5417 | 0 | 16.674 | 37.78
2023-01-27 13:30 | 44953.5625 | 0 | 20.036 | 37.78
2023-01-27 14:00 | 44953.5833 | 0 | 20.1198 | 37.78
2023-01-27 14:30 | 44953.6042 | 0 | 18.4103 | 37.78
2023-01-27 15:00 | 44953.625 | 0 | 17.9734 | 37.78
2023-01-27 15:30 | 44953.6458 | 0 | 19.4839 | 37.78
2023-01-27 16:00 | 44953.6667 | 0 | 20.3577 | 37.78
2023-01-27 16:30 | 44953.6875 | 0 | 19.6369 | 37.78
2023-01-27 17:00 | 44953.7083 | 0 | 19.4293 | 37.78
2023-01-27 17:30 | 44953.7292 | 0 | 18.9848 | 37.78
2023-01-27 18:00 | 44953.75 | 0 | 19.1543 | 37.78
2023-01-27 18:30 | 44953.7708 | 0 | 19.1319 | 37.78
2023-01-27 19:00 | 44953.7917 | 0 | 19.2978 | 37.78
2023-01-27 19:30 | 44953.8125 | 0 | 19.2138 | 37.78
2023-01-27 20:00 | 44953.8333 | 0 | 19.0658 | 37.78
2023-01-27 20:30 | 44953.8542 | 0 | 18.1889 | 37.78
2023-01-27 21:00 | 44953.875 | 0 | 17.5213 | 37.78
2023-01-27 21:30 | 44953.8958 | 0 | 16.8206 | 37.78
2023-01-27 22:00 | 44953.9167 | 0 | 15.7069 | 37.78
2023-01-27 22:30 | 44953.9375 | 0 | 14.9719 | 37.78
2023-01-27 23:00 | 44953.9583 | 0 | 14.1007 | 37.78
2023-01-27 23:30 | 44953.9792 | 0 | 13.3735 | 37.78
2023-01-28 | 44954 | 0 | 12.4973 | 37.78
2023-01-28 00:30 | 44954.0208 | 0 | 11.8152 | 37.78
2023-01-28 01:00 | 44954.0417 | 0 | 11.6136 | 37.78
2023-01-28 01:30 | 44954.0625 | 0 | 11.2539 | 37.78
2023-01-28 02:00 | 44954.0833 | 0 | 11.0975 | 37.78
2023-01-28 02:30 | 44954.1042 | 0 | 10.819 | 37.78
2023-01-28 03:00 | 44954.125 | 0 | 10.6691 | 37.78
2023-01-28 03:30 | 44954.1458 | 0 | 10.5143 | 37.78
2023-01-28 04:00 | 44954.1667 | 0 | 10.6336 | 37.78
2023-01-28 04:30 | 44954.1875 | 0 | 10.6363 | 37.78
2023-01-28 05:00 | 44954.2083 | 0 | 10.6577 | 37.78
2023-01-28 05:30 | 44954.2292 | 0 | 10.3273 | 37.78
2023-01-28 06:00 | 44954.25 | 0 | 10.0392 | 37.78
2023-01-28 06:30 | 44954.2708 | 0 | 10.2856 | 37.78
2023-01-28 07:00 | 44954.2917 | 0 | 11.126 | 37.78
2023-01-28 07:30 | 44954.3125 | 0 | 10.488 | 37.78
2023-01-28 08:00 | 44954.3333 | 0 | 11.6642 | 37.78
2023-01-28 08:30 | 44954.3542 | 0 | 12.0515 | 37.78
2023-01-28 09:00 | 44954.375 | 0 | 12.1075 | 37.78
2023-01-28 09:30 | 44954.3958 | 0 | 11.0553 | 37.78
2023-01-28 10:00 | 44954.4167 | 0 | 10.6745 | 37.78
2023-01-28 10:30 | 44954.4375 | 0 | 11.6206 | 37.78
2023-01-28 11:00 | 44954.4583 | 0 | 12.0888 | 37.78
2023-01-28 11:30 | 44954.4792 | 0 | 12.6735 | 37.78
2023-01-28 12:00 | 44954.5 | 0 | 12.6902 | 37.78
2023-01-28 12:30 | 44954.5208 | 0 | 12.5156 | 37.78
2023-01-28 13:00 | 44954.5417 | 0 | 15.5353 | 37.78
2023-01-28 13:30 | 44954.5625 | 0 | 17.4364 | 37.78
2023-01-28 14:00 | 44954.5833 | 0 | 18.2726 | 37.78
2023-01-28 14:30 | 44954.6042 | 0 | 17.8123 | 37.78
2023-01-28 15:00 | 44954.625 | 0 | 13.1084 | 37.78
2023-01-28 15:30 | 44954.6458 | 0 | 14.412 | 37.78
2023-01-28 16:00 | 44954.6667 | 0 | 15.7447 | 37.78
2023-01-28 16:30 | 44954.6875 | 0 | 16.1179 | 37.78
2023-01-28 17:00 | 44954.7083 | 0 | 16.9682 | 37.78
2023-01-28 17:30 | 44954.7292 | 0 | 17.3482 | 37.78
2023-01-28 18:00 | 44954.75 | 0 | 17.6527 | 37.78
2023-01-28 18:30 | 44954.7708 | 0 | 17.6246 | 37.78
2023-01-28 19:00 | 44954.7917 | 0 | 17.6836 | 37.78
2023-01-28 19:30 | 44954.8125 | 0 | 17.3511 | 37.78
2023-01-28 20:00 | 44954.8333 | 0 | 17.1844 | 37.78
2023-01-28 20:30 | 44954.8542 | 0 | 16.2413 | 37.78
2023-01-28 21:00 | 44954.875 | 0 | 15.9312 | 37.78
2023-01-28 21:30 | 44954.8958 | 0 | 15.3176 | 37.78
2023-01-28 22:00 | 44954.9167 | 0 | 14.6105 | 37.78
2023-01-28 22:30 | 44954.9375 | 0 | 13.6539 | 37.78
2023-01-28 23:00 | 44954.9583 | 0 | 13.0891 | 37.78
2023-01-28 23:30 | 44954.9792 | 0 | 12.4298 | 37.78
2023-01-29 | 44955 | 0 | 11.6928 | 37.78
2023-01-29 00:30 | 44955.0208 | 0 | 11.3372 | 37.78
2023-01-29 01:00 | 44955.0417 | 0 | 11.1053 | 37.78
2023-01-29 01:30 | 44955.0625 | 0 | 10.8108 | 37.78
2023-01-29 02:00 | 44955.0833 | 0 | 10.5682 | 37.78
2023-01-29 02:30 | 44955.1042 | 0 | 10.3698 | 37.78
2023-01-29 03:00 | 44955.125 | 0 | 10.1128 | 37.78
2023-01-29 03:30 | 44955.1458 | 0 | 10.0018 | 37.78
2023-01-29 04:00 | 44955.1667 | 0 | 10.0494 | 37.78
2023-01-29 04:30 | 44955.1875 | 0 | 9.8988 | 37.78
2023-01-29 05:00 | 44955.2083 | 0 | 9.8159 | 37.78
2023-01-29 05:30 | 44955.2292 | 0 | 9.7233 | 37.78
2023-01-29 06:00 | 44955.25 | 0 | 9.6236 | 37.78
2023-01-29 06:30 | 44955.2708 | 0 | 9.2489 | 37.78
2023-01-29 07:00 | 44955.2917 | 0 | 9.5698 | 37.78
2023-01-29 07:30 | 44955.3125 | 0 | 9.598 | 37.78
2023-01-29 08:00 | 44955.3333 | 0 | 11.3553 | 37.78
2023-01-29 08:30 | 44955.3542 | 0 | 9.9864 | 37.78
2023-01-29 09:00 | 44955.375 | 0 | 10.2507 | 37.78
2023-01-29 09:30 | 44955.3958 | 0 | 11.7392 | 37.78
2023-01-29 10:00 | 44955.4167 | 0 | 10.7921 | 37.78
2023-01-29 10:30 | 44955.4375 | 0 | 11.7969 | 37.78
2023-01-29 11:00 | 44955.4583 | 0 | 11.1414 | 37.78
2023-01-29 11:30 | 44955.4792 | 0 | 11.632 | 37.78
2023-01-29 12:00 | 44955.5 | 0 | 11.2392 | 37.78
2023-01-29 12:30 | 44955.5208 | 0 | 11.5285 | 37.78
2023-01-29 13:00 | 44955.5417 | 0 | 11.8367 | 37.78
2023-01-29 13:30 | 44955.5625 | 0 | 12.5046 | 37.78
2023-01-29 14:00 | 44955.5833 | 0 | 13.074 | 37.78
2023-01-29 14:30 | 44955.6042 | 0 | 14.0746 | 37.78
2023-01-29 15:00 | 44955.625 | 0 | 15.7186 | 37.78
2023-01-29 15:30 | 44955.6458 | 0 | 17.4059 | 37.78
2023-01-29 16:00 | 44955.6667 | 0 | 17.3298 | 37.78
2023-01-29 16:30 | 44955.6875 | 0 | 17.5185 | 37.78
2023-01-29 17:00 | 44955.7083 | 0 | 17.5709 | 37.78
2023-01-29 17:30 | 44955.7292 | 0 | 17.706 | 37.78
2023-01-29 18:00 | 44955.75 | 0 | 17.993 | 37.78
2023-01-29 18:30 | 44955.7708 | 0 | 18.1908 | 37.78
2023-01-29 19:00 | 44955.7917 | 0 | 18.2668 | 37.78
2023-01-29 19:30 | 44955.8125 | 0 | 17.7605 | 37.78
2023-01-29 20:00 | 44955.8333 | 0 | 17.3407 | 37.78
2023-01-29 20:30 | 44955.8542 | 0 | 16.5365 | 37.78
2023-01-29 21:00 | 44955.875 | 0 | 15.9401 | 37.78
2023-01-29 21:30 | 44955.8958 | 0 | 14.862 | 37.78
2023-01-29 22:00 | 44955.9167 | 0 | 13.9605 | 37.78
2023-01-29 22:30 | 44955.9375 | 0 | 12.9285 | 37.78
2023-01-29 23:00 | 44955.9583 | 0 | 12.3718 | 37.78
2023-01-29 23:30 | 44955.9792 | 0 | 11.8215 | 37.78
2023-01-30 | 44956 | 0 | 11.4698 | 37.78
2023-01-30 00:30 | 44956.0208 | 0 | 11.1065 | 37.78
2023-01-30 01:00 | 44956.0417 | 0 | 10.9411 | 37.78
2023-01-30 01:30 | 44956.0625 | 0 | 10.6375 | 37.78
2023-01-30 02:00 | 44956.0833 | 0 | 10.6595 | 37.78
2023-01-30 02:30 | 44956.1042 | 0 | 10.6966 | 37.78
2023-01-30 03:00 | 44956.125 | 0 | 10.4553 | 37.78
2023-01-30 03:30 | 44956.1458 | 0 | 10.5944 | 37.78
2023-01-30 04:00 | 44956.1667 | 0 | 10.8535 | 37.78
2023-01-30 04:30 | 44956.1875 | 0 | 11.2907 | 37.78
2023-01-30 05:00 | 44956.2083 | 0 | 11.8441 | 37.78
2023-01-30 05:30 | 44956.2292 | 0 | 12.5142 | 37.78
2023-01-30 06:00 | 44956.25 | 0 | 13.6051 | 37.78
2023-01-30 06:30 | 44956.2708 | 0 | 14.0413 | 37.78
2023-01-30 07:00 | 44956.2917 | 0 | 15.3295 | 37.78
2023-01-30 07:30 | 44956.3125 | 0 | 14.7366 | 37.78
2023-01-30 08:00 | 44956.3333 | 0 | 13.6567 | 37.78
2023-01-30 08:30 | 44956.3542 | 0 | 16.0349 | 37.78
2023-01-30 09:00 | 44956.375 | 0 | 15.0208 | 37.78
2023-01-30 09:30 | 44956.3958 | 0 | 16.1814 | 37.78
2023-01-30 10:00 | 44956.4167 | 0 | 15.6265 | 37.78
2023-01-30 10:30 | 44956.4375 | 0 | 15.4262 | 37.78
2023-01-30 11:00 | 44956.4583 | 0 | 15.5421 | 37.78
2023-01-30 11:30 | 44956.4792 | 0 | 15.9622 | 37.78
2023-01-30 12:00 | 44956.5 | 0 | 16.9471 | 37.78
2023-01-30 12:30 | 44956.5208 | 0 | 15.9279 | 37.78
2023-01-30 13:00 | 44956.5417 | 0 | 16.1902 | 37.78
2023-01-30 13:30 | 44956.5625 | 0 | 16.3918 | 37.78
2023-01-30 14:00 | 44956.5833 | 0 | 16.0413 | 37.78
2023-01-30 14:30 | 44956.6042 | 0 | 16.7762 | 37.78
2023-01-30 15:00 | 44956.625 | 0 | 19.0362 | 37.78
2023-01-30 15:30 | 44956.6458 | 0 | 18.4321 | 37.78
2023-01-30 16:00 | 44956.6667 | 0 | 19.4179 | 37.78
2023-01-30 16:30 | 44956.6875 | 0 | 20.1868 | 37.78
2023-01-30 17:00 | 44956.7083 | 0 | 19.5674 | 37.78
2023-01-30 17:30 | 44956.7292 | 0 | 19.4785 | 37.78
2023-01-30 18:00 | 44956.75 | 0 | 19.861 | 37.78
2023-01-30 18:30 | 44956.7708 | 0 | 20.5217 | 37.78
2023-01-30 19:00 | 44956.7917 | 0 | 20.385 | 37.78
2023-01-30 19:30 | 44956.8125 | 0 | 20.1857 | 37.78
2023-01-30 20:00 | 44956.8333 | 0 | 19.5492 | 37.78
2023-01-30 20:30 | 44956.8542 | 0 | 18.7959 | 37.78
2023-01-30 21:00 | 44956.875 | 0 | 17.8679 | 37.78
2023-01-30 21:30 | 44956.8958 | 0 | 16.9938 | 37.78
2023-01-30 22:00 | 44956.9167 | 0 | 15.8109 | 37.78
2023-01-30 22:30 | 44956.9375 | 0 | 14.7681 | 37.78
2023-01-30 23:00 | 44956.9583 | 0 | 14.0097 | 37.78
2023-01-30 23:30 | 44956.9792 | 0 | 13.2409 | 37.78
2023-01-31 | 44957 | 0 | 12.3521 | 37.78
2023-01-31 00:30 | 44957.0208 | 0 | 11.9178 | 37.78
2023-01-31 01:00 | 44957.0417 | 0 | 11.6785 | 37.78
2023-01-31 01:30 | 44957.0625 | 0 | 11.5139 | 37.78
2023-01-31 02:00 | 44957.0833 | 0 | 11.1256 | 37.78
2023-01-31 02:30 | 44957.1042 | 0 | 10.9968 | 37.78
2023-01-31 03:00 | 44957.125 | 0 | 10.8265 | 37.78
2023-01-31 03:30 | 44957.1458 | 0 | 10.7361 | 37.78
2023-01-31 04:00 | 44957.1667 | 0 | 11.0091 | 37.78
2023-01-31 04:30 | 44957.1875 | 0 | 11.3708 | 37.78
2023-01-31 05:00 | 44957.2083 | 0 | 12.1604 | 37.78
2023-01-31 05:30 | 44957.2292 | 0 | 12.6525 | 37.78
2023-01-31 06:00 | 44957.25 | 0 | 13.6645 | 37.78
2023-01-31 06:30 | 44957.2708 | 0 | 13.9687 | 37.78
2023-01-31 07:00 | 44957.2917 | 0 | 14.7968 | 37.78
2023-01-31 07:30 | 44957.3125 | 0 | 14.4046 | 37.78
2023-01-31 08:00 | 44957.3333 | 0 | 14.6812 | 37.78
2023-01-31 08:30 | 44957.3542 | 0 | 14.5996 | 37.78
2023-01-31 09:00 | 44957.375 | 0 | 15.2979 | 37.78
2023-01-31 09:30 | 44957.3958 | 0 | 15.4012 | 37.78
2023-01-31 10:00 | 44957.4167 | 0 | 15.7467 | 37.78
2023-01-31 10:30 | 44957.4375 | 0 | 16.8158 | 37.78
2023-01-31 11:00 | 44957.4583 | 0 | 17.0443 | 37.78
2023-01-31 11:30 | 44957.4792 | 0 | 16.6906 | 37.78
2023-01-31 12:00 | 44957.5 | 0 | 15.7125 | 37.78
2023-01-31 12:30 | 44957.5208 | 0 | 17.6534 | 37.78
2023-01-31 13:00 | 44957.5417 | 0 | 18.2406 | 37.78
2023-01-31 13:30 | 44957.5625 | 0 | 19.8374 | 37.78
2023-01-31 14:00 | 44957.5833 | 0 | 21.7127 | 37.78
2023-01-31 14:30 | 44957.6042 | 0 | 21.6084 | 37.78
2023-01-31 15:00 | 44957.625 | 0 | 21.7303 | 37.78
2023-01-31 15:30 | 44957.6458 | 0 | 20.1063 | 37.78
2023-01-31 16:00 | 44957.6667 | 0 | 21.6774 | 37.78
2023-01-31 16:30 | 44957.6875 | 0 | 21.5591 | 37.78
2023-01-31 17:00 | 44957.7083 | 0 | 20.6987 | 37.78
2023-01-31 17:30 | 44957.7292 | 0 | 21.0176 | 37.78
2023-01-31 18:00 | 44957.75 | 0 | 20.946 | 37.78
2023-01-31 18:30 | 44957.7708 | 0 | 21.3535 | 37.78
2023-01-31 19:00 | 44957.7917 | 0 | 21.6414 | 37.78
2023-01-31 19:30 | 44957.8125 | 0 | 21.3002 | 37.78
2023-01-31 20:00 | 44957.8333 | 0 | 21.0005 | 37.78
2023-01-31 20:30 | 44957.8542 | 0 | 20.1258 | 37.78
2023-01-31 21:00 | 44957.875 | 0 | 19.2059 | 37.78
2023-01-31 21:30 | 44957.8958 | 0 | 18.3819 | 37.78
2023-01-31 22:00 | 44957.9167 | 0 | 16.9005 | 37.78
2023-01-31 22:30 | 44957.9375 | 0 | 15.8467 | 37.78
2023-01-31 23:00 | 44957.9583 | 0 | 14.9495 | 37.78
2023-01-31 23:30 | 44957.9792 | 0 | 14.2274 | 37.78
2023-02-01 | 44958 | 0 | 13.6062 | 37.78
2023-02-01 00:30 | 44958.0208 | 0 | 13.0751 | 37.78
2023-02-01 01:00 | 44958.0417 | 0 | 12.7127 | 37.78
2023-02-01 01:30 | 44958.0625 | 0 | 12.3629 | 37.78
2023-02-01 02:00 | 44958.0833 | 0 | 12.1457 | 37.78
2023-02-01 02:30 | 44958.1042 | 0 | 11.9298 | 37.78
2023-02-01 03:00 | 44958.125 | 0 | 11.7264 | 37.78
2023-02-01 03:30 | 44958.1458 | 0 | 11.6706 | 37.78
2023-02-01 04:00 | 44958.1667 | 0 | 12.036 | 37.78
2023-02-01 04:30 | 44958.1875 | 0 | 12.2338 | 37.78
2023-02-01 05:00 | 44958.2083 | 0 | 12.9187 | 37.78
2023-02-01 05:30 | 44958.2292 | 0 | 13.2016 | 37.78
2023-02-01 06:00 | 44958.25 | 0 | 13.7902 | 37.78
2023-02-01 06:30 | 44958.2708 | 0 | 14.8868 | 37.78
2023-02-01 07:00 | 44958.2917 | 0 | 15.9377 | 37.78
2023-02-01 07:30 | 44958.3125 | 0 | 16.5782 | 37.78
2023-02-01 08:00 | 44958.3333 | 0 | 15.9825 | 37.78
2023-02-01 08:30 | 44958.3542 | 0 | 17.2696 | 37.78
2023-02-01 09:00 | 44958.375 | 0 | 18.1476 | 37.78
2023-02-01 09:30 | 44958.3958 | 0 | 18.6455 | 37.78
2023-02-01 10:00 | 44958.4167 | 0 | 17.6204 | 37.78
2023-02-01 10:30 | 44958.4375 | 0 | 16.3939 | 37.78
2023-02-01 11:00 | 44958.4583 | 0 | 16.6889 | 37.78
2023-02-01 11:30 | 44958.4792 | 0 | 17.3311 | 37.78
2023-02-01 12:00 | 44958.5 | 0 | 17.7576 | 37.78
2023-02-01 12:30 | 44958.5208 | 0 | 19.2865 | 37.78
2023-02-01 13:00 | 44958.5417 | 0 | 19.498 | 37.78
2023-02-01 13:30 | 44958.5625 | 0 | 20.4906 | 37.78
2023-02-01 14:00 | 44958.5833 | 0 | 21.7449 | 37.78
2023-02-01 14:30 | 44958.6042 | 0 | 19.1886 | 37.78
2023-02-01 15:00 | 44958.625 | 0 | 19.914 | 37.78
2023-02-01 15:30 | 44958.6458 | 0 | 23.5658 | 37.78
2023-02-01 16:00 | 44958.6667 | 0 | 24.2949 | 37.78
2023-02-01 16:30 | 44958.6875 | 0 | 22.3264 | 37.78
2023-02-01 17:00 | 44958.7083 | 0 | 20.5746 | 37.78
2023-02-01 17:30 | 44958.7292 | 0 | 21.7215 | 37.78
2023-02-01 18:00 | 44958.75 | 0 | 22.0844 | 37.78
2023-02-01 18:30 | 44958.7708 | 0 | 22.2764 | 37.78
2023-02-01 19:00 | 44958.7917 | 0 | 22.143 | 37.78
2023-02-01 19:30 | 44958.8125 | 0 | 21.8905 | 37.78
2023-02-01 20:00 | 44958.8333 | 0 | 21.0224 | 37.78
2023-02-01 20:30 | 44958.8542 | 0 | 20.0675 | 37.78
2023-02-01 21:00 | 44958.875 | 0 | 19.6138 | 37.78
2023-02-01 21:30 | 44958.8958 | 0 | 18.6195 | 37.78
2023-02-01 22:00 | 44958.9167 | 0 | 17.8649 | 37.78
2023-02-01 22:30 | 44958.9375 | 0 | 16.3935 | 37.78
2023-02-01 23:00 | 44958.9583 | 0 | 16.0472 | 37.78
2023-02-01 23:30 | 44958.9792 | 0 | 14.951 | 37.78
2023-02-02 | 44959 | 0 | 13.7867 | 37.78
2023-02-02 00:30 | 44959.0208 | 0 | 13.3866 | 37.78
2023-02-02 01:00 | 44959.0417 | 0 | 12.9995 | 37.78
2023-02-02 01:30 | 44959.0625 | 0 | 12.7636 | 37.78
2023-02-02 02:00 | 44959.0833 | 0 | 12.4065 | 37.78
2023-02-02 02:30 | 44959.1042 | 0 | 12.2311 | 37.78
2023-02-02 03:00 | 44959.125 | 0 | 11.9647 | 37.78
2023-02-02 03:30 | 44959.1458 | 0 | 12.0267 | 37.78
2023-02-02 04:00 | 44959.1667 | 0 | 12.384 | 37.78
2023-02-02 04:30 | 44959.1875 | 0 | 12.6934 | 37.78
2023-02-02 05:00 | 44959.2083 | 0 | 13.1178 | 37.78
2023-02-02 05:30 | 44959.2292 | 0 | 13.309 | 37.78
2023-02-02 06:00 | 44959.25 | 0 | 14.3126 | 37.78
2023-02-02 06:30 | 44959.2708 | 0 | 15.0733 | 37.78
2023-02-02 07:00 | 44959.2917 | 0 | 15.5533 | 37.78
2023-02-02 07:30 | 44959.3125 | 0 | 15.5908 | 37.78
2023-02-02 08:00 | 44959.3333 | 0 | 15.8119 | 37.78
2023-02-02 08:30 | 44959.3542 | 0 | 17.2727 | 37.78
2023-02-02 09:00 | 44959.375 | 0 | 17.4196 | 37.78
2023-02-02 09:30 | 44959.3958 | 0 | 17.6906 | 37.78
2023-02-02 10:00 | 44959.4167 | 0 | 18.2952 | 37.78
2023-02-02 10:30 | 44959.4375 | 0 | 18.4442 | 37.78
2023-02-02 11:00 | 44959.4583 | 0 | 18.7243 | 37.78
2023-02-02 11:30 | 44959.4792 | 0 | 18.0677 | 37.78
2023-02-02 12:00 | 44959.5 | 0 | 18.5361 | 37.78
2023-02-02 12:30 | 44959.5208 | 0 | 17.5168 | 37.78
2023-02-02 13:00 | 44959.5417 | 0 | 19.331 | 37.78
2023-02-02 13:30 | 44959.5625 | 0 | 18.4938 | 37.78
2023-02-02 14:00 | 44959.5833 | 0 | 18.3134 | 37.78
2023-02-02 14:30 | 44959.6042 | 0 | 19.3164 | 37.78
2023-02-02 15:00 | 44959.625 | 0 | 20.8626 | 37.78
2023-02-02 15:30 | 44959.6458 | 0 | 20.2267 | 37.78
2023-02-02 16:00 | 44959.6667 | 0 | 21.2183 | 37.78
2023-02-02 16:30 | 44959.6875 | 0 | 20.6799 | 37.78
2023-02-02 17:00 | 44959.7083 | 0 | 20.881 | 37.78
2023-02-02 17:30 | 44959.7292 | 0 | 21.0396 | 37.78
2023-02-02 18:00 | 44959.75 | 0 | 20.9558 | 37.78
2023-02-02 18:30 | 44959.7708 | 0 | 20.9192 | 37.78
2023-02-02 19:00 | 44959.7917 | 0 | 20.9224 | 37.78
2023-02-02 19:30 | 44959.8125 | 0 | 20.5126 | 37.78
2023-02-02 20:00 | 44959.8333 | 0 | 20.1791 | 37.78
2023-02-02 20:30 | 44959.8542 | 0 | 19.4087 | 37.78
2023-02-02 21:00 | 44959.875 | 0 | 18.8762 | 37.78
2023-02-02 21:30 | 44959.8958 | 0 | 18.2291 | 37.78
2023-02-02 22:00 | 44959.9167 | 0 | 16.9407 | 37.78
2023-02-02 22:30 | 44959.9375 | 0 | 15.7113 | 37.78
2023-02-02 23:00 | 44959.9583 | 0 | 14.7187 | 37.78
2023-02-02 23:30 | 44959.9792 | 0 | 13.9744 | 37.78
2023-02-03 | 44960 | 0 | 13.4582 | 37.78
2023-02-03 00:30 | 44960.0208 | 0 | 13.0745 | 37.78
2023-02-03 01:00 | 44960.0417 | 0 | 12.7187 | 37.78
2023-02-03 01:30 | 44960.0625 | 0 | 12.3777 | 37.78
2023-02-03 02:00 | 44960.0833 | 0 | 12.1036 | 37.78
2023-02-03 02:30 | 44960.1042 | 0 | 11.6995 | 37.78
2023-02-03 03:00 | 44960.125 | 0 | 11.5386 | 37.78
2023-02-03 03:30 | 44960.1458 | 0 | 11.6337 | 37.78
2023-02-03 04:00 | 44960.1667 | 0 | 11.8341 | 37.78
2023-02-03 04:30 | 44960.1875 | 0 | 12.3295 | 37.78
2023-02-03 05:00 | 44960.2083 | 0 | 12.8711 | 37.78
2023-02-03 05:30 | 44960.2292 | 0 | 13.2756 | 37.78
2023-02-03 06:00 | 44960.25 | 0 | 14.0917 | 37.78
2023-02-03 06:30 | 44960.2708 | 0 | 14.8509 | 37.78
2023-02-03 07:00 | 44960.2917 | 0 | 15.7941 | 37.78
2023-02-03 07:30 | 44960.3125 | 0 | 16.0475 | 37.78
2023-02-03 08:00 | 44960.3333 | 0 | 16.7136 | 37.78
2023-02-03 08:30 | 44960.3542 | 0 | 17.1262 | 37.78
2023-02-03 09:00 | 44960.375 | 0 | 17.6002 | 37.78
2023-02-03 09:30 | 44960.3958 | 0 | 17.2595 | 37.78
2023-02-03 10:00 | 44960.4167 | 0 | 17.6229 | 37.78
2023-02-03 10:30 | 44960.4375 | 0 | 18.0632 | 37.78
2023-02-03 11:00 | 44960.4583 | 0 | 18.3991 | 37.78
2023-02-03 11:30 | 44960.4792 | 0 | 18.9904 | 37.78
2023-02-03 12:00 | 44960.5 | 0 | 20.1925 | 37.78
2023-02-03 12:30 | 44960.5208 | 0 | 23.1836 | 37.78
2023-02-03 13:00 | 44960.5417 | 0 | 20.3988 | 37.78
2023-02-03 13:30 | 44960.5625 | 0 | 20.9151 | 37.78
2023-02-03 14:00 | 44960.5833 | 0 | 21.9434 | 37.78
2023-02-03 14:30 | 44960.6042 | 0 | 23.9588 | 37.78
2023-02-03 15:00 | 44960.625 | 0 | 23.6102 | 37.78
2023-02-03 15:30 | 44960.6458 | 0 | 23.8963 | 37.78
2023-02-03 16:00 | 44960.6667 | 0 | 23.9125 | 37.78
2023-02-03 16:30 | 44960.6875 | 0 | 22.4699 | 37.78
2023-02-03 17:00 | 44960.7083 | 0 | 22.5234 | 37.78
2023-02-03 17:30 | 44960.7292 | 0 | 22.498 | 37.78
2023-02-03 18:00 | 44960.75 | 0 | 22.4056 | 37.78
2023-02-03 18:30 | 44960.7708 | 0 | 22.666 | 37.78
2023-02-03 19:00 | 44960.7917 | 0 | 23.1512 | 37.78
2023-02-03 19:30 | 44960.8125 | 0 | 22.861 | 37.78
2023-02-03 20:00 | 44960.8333 | 0 | 22.1981 | 37.78
2023-02-03 20:30 | 44960.8542 | 0 | 21.9523 | 37.78
2023-02-03 21:00 | 44960.875 | 0 | 22.0293 | 37.78
2023-02-03 21:30 | 44960.8958 | 0 | 21.0992 | 37.78
2023-02-03 22:00 | 44960.9167 | 0 | 19.7027 | 37.78
2023-02-03 22:30 | 44960.9375 | 0 | 18.8485 | 37.78
2023-02-03 23:00 | 44960.9583 | 0 | 17.765 | 37.78
2023-02-03 23:30 | 44960.9792 | 0 | 17.0481 | 37.78
2023-02-04 | 44961 | 0 | 16.1912 | 37.78
2023-02-04 00:30 | 44961.0208 | 0 | 14.9218 | 37.78
2023-02-04 01:00 | 44961.0417 | 0 | 14.3672 | 37.78
2023-02-04 01:30 | 44961.0625 | 0 | 13.9936 | 37.78
2023-02-04 02:00 | 44961.0833 | 0 | 14.6381 | 37.78
2023-02-04 02:30 | 44961.1042 | 0 | 14.3333 | 37.78
2023-02-04 03:00 | 44961.125 | 0 | 14.0148 | 37.78
2023-02-04 03:30 | 44961.1458 | 0 | 13.8122 | 37.78
2023-02-04 04:00 | 44961.1667 | 0 | 13.7582 | 37.78
2023-02-04 04:30 | 44961.1875 | 0 | 13.5368 | 37.78
2023-02-04 05:00 | 44961.2083 | 0 | 13.6906 | 37.78
2023-02-04 05:30 | 44961.2292 | 0 | 13.6381 | 37.78
2023-02-04 06:00 | 44961.25 | 0 | 13.8369 | 37.78
2023-02-04 06:30 | 44961.2708 | 0 | 14.476 | 37.78
2023-02-04 07:00 | 44961.2917 | 0 | 14.6003 | 37.78
2023-02-04 07:30 | 44961.3125 | 0 | 14.5975 | 37.78
2023-02-04 08:00 | 44961.3333 | 0 | 15.0949 | 37.78
2023-02-04 08:30 | 44961.3542 | 0 | 15.867 | 37.78
2023-02-04 09:00 | 44961.375 | 0 | 16.0056 | 37.78
2023-02-04 09:30 | 44961.3958 | 0 | 16.7132 | 37.78
2023-02-04 10:00 | 44961.4167 | 0 | 15.8946 | 37.78
2023-02-04 10:30 | 44961.4375 | 0 | 16.3127 | 37.78
2023-02-04 11:00 | 44961.4583 | 0 | 15.532 | 37.78
2023-02-04 11:30 | 44961.4792 | 0 | 14.1346 | 37.78
2023-02-04 12:00 | 44961.5 | 0 | 14.0977 | 37.78
2023-02-04 12:30 | 44961.5208 | 0 | 13.8341 | 37.78
2023-02-04 13:00 | 44961.5417 | 0 | 13.9465 | 37.78
2023-02-04 13:30 | 44961.5625 | 0 | 13.8442 | 37.78
2023-02-04 14:00 | 44961.5833 | 0 | 13.6545 | 37.78
2023-02-04 14:30 | 44961.6042 | 0 | 11.6746 | 37.78
2023-02-04 15:00 | 44961.625 | 0 | 11.8018 | 37.78
2023-02-04 15:30 | 44961.6458 | 0 | 11.2269 | 37.78
2023-02-04 16:00 | 44961.6667 | 0 | 12.7302 | 37.78
2023-02-04 16:30 | 44961.6875 | 0 | 12.9214 | 37.78
2023-02-04 17:00 | 44961.7083 | 0 | 14.2635 | 37.78
2023-02-04 17:30 | 44961.7292 | 0 | 14.2459 | 37.78
2023-02-04 18:00 | 44961.75 | 0 | 14.2547 | 37.78
2023-02-04 18:30 | 44961.7708 | 0 | 14.6371 | 37.78
2023-02-04 19:00 | 44961.7917 | 0 | 14.7036 | 37.78
2023-02-04 19:30 | 44961.8125 | 0 | 14.6431 | 37.78
2023-02-04 20:00 | 44961.8333 | 0 | 14.3764 | 37.78
2023-02-04 20:30 | 44961.8542 | 0 | 13.7167 | 37.78
2023-02-04 21:00 | 44961.875 | 0 | 13.7019 | 37.78
2023-02-04 21:30 | 44961.8958 | 0 | 13.1335 | 37.78
2023-02-04 22:00 | 44961.9167 | 0 | 12.6396 | 37.78
2023-02-04 22:30 | 44961.9375 | 0 | 11.7949 | 37.78
2023-02-04 23:00 | 44961.9583 | 0 | 11.3343 | 37.78
2023-02-04 23:30 | 44961.9792 | 0 | 10.8115 | 37.78
2023-02-05 | 44962 | 0 | 10.2981 | 37.78
2023-02-05 00:30 | 44962.0208 | 0 | 9.9455 | 37.78
2023-02-05 01:00 | 44962.0417 | 0 | 9.7292 | 37.78
2023-02-05 01:30 | 44962.0625 | 0 | 9.4418 | 37.78
2023-02-05 02:00 | 44962.0833 | 0 | 9.3826 | 37.78
2023-02-05 02:30 | 44962.1042 | 0 | 9.3114 | 37.78
2023-02-05 03:00 | 44962.125 | 0 | 9.1505 | 37.78
2023-02-05 03:30 | 44962.1458 | 0 | 9.0486 | 37.78
2023-02-05 04:00 | 44962.1667 | 0 | 9.1347 | 37.78
2023-02-05 04:30 | 44962.1875 | 0 | 9.0651 | 37.78
2023-02-05 05:00 | 44962.2083 | 0 | 9.0706 | 37.78
2023-02-05 05:30 | 44962.2292 | 0 | 9.0075 | 37.78
2023-02-05 06:00 | 44962.25 | 0 | 8.9398 | 37.78
2023-02-05 06:30 | 44962.2708 | 0 | 8.8191 | 37.78
2023-02-05 07:00 | 44962.2917 | 0 | 8.6733 | 37.78
2023-02-05 07:30 | 44962.3125 | 0 | 8.6845 | 37.78
2023-02-05 08:00 | 44962.3333 | 0 | 9.2724 | 37.78
2023-02-05 08:30 | 44962.3542 | 0 | 9.8522 | 37.78
2023-02-05 09:00 | 44962.375 | 0 | 10.3084 | 37.78
2023-02-05 09:30 | 44962.3958 | 0 | 12.3038 | 37.78
2023-02-05 10:00 | 44962.4167 | 0 | 11.7687 | 37.78
2023-02-05 10:30 | 44962.4375 | 0 | 10.8608 | 37.78
2023-02-05 11:00 | 44962.4583 | 0 | 11.1152 | 37.78
2023-02-05 11:30 | 44962.4792 | 0 | 11.6328 | 37.78
2023-02-05 12:00 | 44962.5 | 0 | 11.8898 | 37.78
2023-02-05 12:30 | 44962.5208 | 0 | 12.2635 | 37.78
2023-02-05 13:00 | 44962.5417 | 0 | 12.6953 | 37.78
2023-02-05 13:30 | 44962.5625 | 0 | 12.3188 | 37.78
2023-02-05 14:00 | 44962.5833 | 0 | 12.5467 | 37.78
2023-02-05 14:30 | 44962.6042 | 0 | 13.3113 | 37.78
2023-02-05 15:00 | 44962.625 | 0 | 14.1447 | 37.78
2023-02-05 15:30 | 44962.6458 | 0 | 14.8119 | 37.78
2023-02-05 16:00 | 44962.6667 | 0 | 15.4536 | 37.78
2023-02-05 16:30 | 44962.6875 | 0 | 16.3621 | 37.78
2023-02-05 17:00 | 44962.7083 | 0 | 16.9761 | 37.78
2023-02-05 17:30 | 44962.7292 | 0 | 17.3846 | 37.78
2023-02-05 18:00 | 44962.75 | 0 | 17.3887 | 37.78
2023-02-05 18:30 | 44962.7708 | 0 | 17.11 | 37.78
2023-02-05 19:00 | 44962.7917 | 0 | 16.9005 | 37.78
2023-02-05 19:30 | 44962.8125 | 0 | 16.2919 | 37.78
2023-02-05 20:00 | 44962.8333 | 0 | 16.2279 | 37.78
2023-02-05 20:30 | 44962.8542 | 0 | 15.3766 | 37.78
2023-02-05 21:00 | 44962.875 | 0 | 14.5509 | 37.78
2023-02-05 21:30 | 44962.8958 | 0 | 13.7971 | 37.78
2023-02-05 22:00 | 44962.9167 | 0 | 12.8877 | 37.78
2023-02-05 22:30 | 44962.9375 | 0 | 11.9594 | 37.78
2023-02-05 23:00 | 44962.9583 | 0 | 11.2169 | 37.78
2023-02-05 23:30 | 44962.9792 | 0 | 10.5587 | 37.78
2023-02-06 | 44963 | 0 | 10.1487 | 37.78
2023-02-06 00:30 | 44963.0208 | 0 | 9.8622 | 37.78
2023-02-06 01:00 | 44963.0417 | 0 | 9.7266 | 37.78
2023-02-06 01:30 | 44963.0625 | 0 | 9.4862 | 37.78
2023-02-06 02:00 | 44963.0833 | 0 | 9.4668 | 37.78
2023-02-06 02:30 | 44963.1042 | 0 | 9.4745 | 37.78
2023-02-06 03:00 | 44963.125 | 0 | 9.3088 | 37.78
2023-02-06 03:30 | 44963.1458 | 0 | 9.4636 | 37.78
2023-02-06 04:00 | 44963.1667 | 0 | 9.8922 | 37.78
2023-02-06 04:30 | 44963.1875 | 0 | 10.1818 | 37.78
2023-02-06 05:00 | 44963.2083 | 0 | 10.6669 | 37.78
2023-02-06 05:30 | 44963.2292 | 0 | 11.1375 | 37.78
2023-02-06 06:00 | 44963.25 | 0 | 11.823 | 37.78
2023-02-06 06:30 | 44963.2708 | 0 | 12.0609 | 37.78
2023-02-06 07:00 | 44963.2917 | 0 | 13.6875 | 37.78
2023-02-06 07:30 | 44963.3125 | 0 | 12.8392 | 37.78
2023-02-06 08:00 | 44963.3333 | 0 | 13.0444 | 37.78
2023-02-06 08:30 | 44963.3542 | 0 | 12.9618 | 37.78
2023-02-06 09:00 | 44963.375 | 0 | 13.0504 | 37.78
2023-02-06 09:30 | 44963.3958 | 0 | 12.8508 | 37.78
2023-02-06 10:00 | 44963.4167 | 0 | 12.5455 | 37.78
2023-02-06 10:30 | 44963.4375 | 0 | 12.5416 | 37.78
2023-02-06 11:00 | 44963.4583 | 0 | 13.2393 | 37.78
2023-02-06 11:30 | 44963.4792 | 0 | 13.2828 | 37.78
2023-02-06 12:00 | 44963.5 | 0 | 13.652 | 37.78
2023-02-06 12:30 | 44963.5208 | 0 | 13.3359 | 37.78
2023-02-06 13:00 | 44963.5417 | 0 | 13.6594 | 37.78
2023-02-06 13:30 | 44963.5625 | 0 | 14.2025 | 37.78
2023-02-06 14:00 | 44963.5833 | 0 | 15.1982 | 37.78
2023-02-06 14:30 | 44963.6042 | 0 | 15.5251 | 37.78
2023-02-06 15:00 | 44963.625 | 0 | 16.0724 | 37.78
2023-02-06 15:30 | 44963.6458 | 0 | 16.7344 | 37.78
2023-02-06 16:00 | 44963.6667 | 0 | 17.2732 | 37.78
2023-02-06 16:30 | 44963.6875 | 0 | 17.9295 | 37.78
2023-02-06 17:00 | 44963.7083 | 0 | 18.2844 | 37.78
2023-02-06 17:30 | 44963.7292 | 0 | 18.7532 | 37.78
2023-02-06 18:00 | 44963.75 | 0 | 18.5422 | 37.78
2023-02-06 18:30 | 44963.7708 | 0 | 18.4301 | 37.78
2023-02-06 19:00 | 44963.7917 | 0 | 18.228 | 37.78
2023-02-06 19:30 | 44963.8125 | 0 | 17.8288 | 37.78
2023-02-06 20:00 | 44963.8333 | 0 | 17.3723 | 37.78
2023-02-06 20:30 | 44963.8542 | 0 | 16.4661 | 37.78
2023-02-06 21:00 | 44963.875 | 0 | 15.8498 | 37.78
2023-02-06 21:30 | 44963.8958 | 0 | 14.9428 | 37.78
2023-02-06 22:00 | 44963.9167 | 0 | 14.0782 | 37.78
2023-02-06 22:30 | 44963.9375 | 0 | 13.1067 | 37.78
2023-02-06 23:00 | 44963.9583 | 0 | 12.4162 | 37.78
2023-02-06 23:30 | 44963.9792 | 0 | 11.7898 | 37.78
2023-02-07 | 44964 | 0 | 11.1629 | 37.78
2023-02-07 00:30 | 44964.0208 | 0 | 10.924 | 37.78
2023-02-07 01:00 | 44964.0417 | 0 | 10.4944 | 37.78
2023-02-07 01:30 | 44964.0625 | 0 | 10.1534 | 37.78
2023-02-07 02:00 | 44964.0833 | 0 | 10.2274 | 37.78
2023-02-07 02:30 | 44964.1042 | 0 | 9.9638 | 37.78
2023-02-07 03:00 | 44964.125 | 0 | 9.7638 | 37.78
2023-02-07 03:30 | 44964.1458 | 0 | 9.941 | 37.78
2023-02-07 04:00 | 44964.1667 | 0 | 10.1133 | 37.78
2023-02-07 04:30 | 44964.1875 | 0 | 10.4377 | 37.78
2023-02-07 05:00 | 44964.2083 | 0 | 11.0558 | 37.78
2023-02-07 05:30 | 44964.2292 | 0 | 11.4112 | 37.78
2023-02-07 06:00 | 44964.25 | 0 | 11.9827 | 37.78
2023-02-07 06:30 | 44964.2708 | 0 | 12.4553 | 37.78
2023-02-07 07:00 | 44964.2917 | 0 | 12.5734 | 37.78
2023-02-07 07:30 | 44964.3125 | 0 | 13.4006 | 37.78
2023-02-07 08:00 | 44964.3333 | 0 | 12.8768 | 37.78
2023-02-07 08:30 | 44964.3542 | 0 | 13.6412 | 37.78
2023-02-07 09:00 | 44964.375 | 0 | 13.8601 | 37.78
2023-02-07 09:30 | 44964.3958 | 0 | 13.1962 | 37.78
2023-02-07 10:00 | 44964.4167 | 0 | 13.0241 | 37.78
2023-02-07 10:30 | 44964.4375 | 0 | 12.8355 | 37.78
2023-02-07 11:00 | 44964.4583 | 0 | 13.8016 | 37.78
2023-02-07 11:30 | 44964.4792 | 0 | 14.7595 | 37.78
2023-02-07 12:00 | 44964.5 | 0 | 14.9836 | 37.78
2023-02-07 12:30 | 44964.5208 | 0 | 14.3096 | 37.78
2023-02-07 13:00 | 44964.5417 | 0 | 14.6898 | 37.78
2023-02-07 13:30 | 44964.5625 | 0 | 15.2153 | 37.78
2023-02-07 14:00 | 44964.5833 | 0 | 15.2341 | 37.78
2023-02-07 14:30 | 44964.6042 | 0 | 16.3447 | 37.78
2023-02-07 15:00 | 44964.625 | 0 | 14.9661 | 37.78
2023-02-07 15:30 | 44964.6458 | 0 | 15.0585 | 37.78
2023-02-07 16:00 | 44964.6667 | 0 | 16.9201 | 37.78
2023-02-07 16:30 | 44964.6875 | 0 | 16.3006 | 37.78
2023-02-07 17:00 | 44964.7083 | 0 | 16.5189 | 37.78
2023-02-07 17:30 | 44964.7292 | 0 | 16.377 | 37.78
2023-02-07 18:00 | 44964.75 | 0 | 16.4608 | 37.78
2023-02-07 18:30 | 44964.7708 | 0 | 16.6586 | 37.78
2023-02-07 19:00 | 44964.7917 | 0 | 16.7003 | 37.78
2023-02-07 19:30 | 44964.8125 | 0 | 16.4569 | 37.78
2023-02-07 20:00 | 44964.8333 | 0 | 16.2063 | 37.78
2023-02-07 20:30 | 44964.8542 | 0 | 15.6676 | 37.78
2023-02-07 21:00 | 44964.875 | 0 | 15.2024 | 37.78
2023-02-07 21:30 | 44964.8958 | 0 | 14.5636 | 37.78
2023-02-07 22:00 | 44964.9167 | 0 | 13.6358 | 37.78
2023-02-07 22:30 | 44964.9375 | 0 | 12.6781 | 37.78
2023-02-07 23:00 | 44964.9583 | 0 | 12.1376 | 37.78
2023-02-07 23:30 | 44964.9792 | 0 | 11.6334 | 37.78
2023-02-08 | 44965 | 0 | 11.1935 | 37.78
2023-02-08 00:30 | 44965.0208 | 0 | 10.7957 | 37.78
2023-02-08 01:00 | 44965.0417 | 0 | 10.4648 | 37.78
2023-02-08 01:30 | 44965.0625 | 0 | 10.1403 | 37.78
2023-02-08 02:00 | 44965.0833 | 0 | 10.0937 | 37.78
2023-02-08 02:30 | 44965.1042 | 0 | 9.9607 | 37.78
2023-02-08 03:00 | 44965.125 | 0 | 9.8314 | 37.78
2023-02-08 03:30 | 44965.1458 | 0 | 9.9637 | 37.78
2023-02-08 04:00 | 44965.1667 | 0 | 10.2435 | 37.78
2023-02-08 04:30 | 44965.1875 | 0 | 10.262 | 37.78
2023-02-08 05:00 | 44965.2083 | 0 | 10.69 | 37.78
2023-02-08 05:30 | 44965.2292 | 0 | 11.2478 | 37.78
2023-02-08 06:00 | 44965.25 | 0 | 11.8267 | 37.78
2023-02-08 06:30 | 44965.2708 | 0 | 12.332 | 37.78
2023-02-08 07:00 | 44965.2917 | 0 | 12.6947 | 37.78
2023-02-08 07:30 | 44965.3125 | 0 | 12.574 | 37.78
2023-02-08 08:00 | 44965.3333 | 0 | 13.4151 | 37.78
2023-02-08 08:30 | 44965.3542 | 0 | 14.3269 | 37.78
2023-02-08 09:00 | 44965.375 | 0 | 14.6103 | 37.78
2023-02-08 09:30 | 44965.3958 | 0 | 12.7481 | 37.78
2023-02-08 10:00 | 44965.4167 | 0 | 13.368 | 37.78
2023-02-08 10:30 | 44965.4375 | 0 | 13.0072 | 37.78
2023-02-08 11:00 | 44965.4583 | 0 | 13.0438 | 37.78
2023-02-08 11:30 | 44965.4792 | 0 | 12.8375 | 37.78
2023-02-08 12:00 | 44965.5 | 0 | 12.2496 | 37.78
2023-02-08 12:30 | 44965.5208 | 0 | 13.0123 | 37.78
2023-02-08 13:00 | 44965.5417 | 0 | 15.0295 | 37.78
2023-02-08 13:30 | 44965.5625 | 0 | 14.492 | 37.78
2023-02-08 14:00 | 44965.5833 | 0 | 15.2565 | 37.78
2023-02-08 14:30 | 44965.6042 | 0 | 15.9075 | 37.78
2023-02-08 15:00 | 44965.625 | 0 | 15.6495 | 37.78
2023-02-08 15:30 | 44965.6458 | 0 | 15.5542 | 37.78
2023-02-08 16:00 | 44965.6667 | 0 | 16.2836 | 37.78
2023-02-08 16:30 | 44965.6875 | 0 | 16.7734 | 37.78
2023-02-08 17:00 | 44965.7083 | 0 | 16.2801 | 37.78
2023-02-08 17:30 | 44965.7292 | 0 | 16.4696 | 37.78
2023-02-08 18:00 | 44965.75 | 0 | 16.7543 | 37.78
2023-02-08 18:30 | 44965.7708 | 0 | 16.8464 | 37.78
2023-02-08 19:00 | 44965.7917 | 0 | 16.8879 | 37.78
2023-02-08 19:30 | 44965.8125 | 0 | 16.7359 | 37.78
2023-02-08 20:00 | 44965.8333 | 0 | 16.5328 | 37.78
2023-02-08 20:30 | 44965.8542 | 0 | 15.914 | 37.78
2023-02-08 21:00 | 44965.875 | 0 | 15.3114 | 37.78
2023-02-08 21:30 | 44965.8958 | 0 | 14.8958 | 37.78
2023-02-08 22:00 | 44965.9167 | 0 | 13.876 | 37.78
2023-02-08 22:30 | 44965.9375 | 0 | 13.128 | 37.78
2023-02-08 23:00 | 44965.9583 | 0 | 12.4924 | 37.78
2023-02-08 23:30 | 44965.9792 | 0 | 11.8754 | 37.78
2023-02-09 | 44966 | 0 | 11.5106 | 37.78
2023-02-09 00:30 | 44966.0208 | 0 | 10.8784 | 37.78
2023-02-09 01:00 | 44966.0417 | 0 | 10.5131 | 37.78
2023-02-09 01:30 | 44966.0625 | 0 | 10.3706 | 37.78
2023-02-09 02:00 | 44966.0833 | 0 | 10.0792 | 37.78
2023-02-09 02:30 | 44966.1042 | 0 | 10.0626 | 37.78
2023-02-09 03:00 | 44966.125 | 0 | 9.8998 | 37.78
2023-02-09 03:30 | 44966.1458 | 0 | 10.0106 | 37.78
2023-02-09 04:00 | 44966.1667 | 0 | 10.2708 | 37.78
2023-02-09 04:30 | 44966.1875 | 0 | 10.5946 | 37.78
2023-02-09 05:00 | 44966.2083 | 0 | 11.1627 | 37.78
2023-02-09 05:30 | 44966.2292 | 0 | 11.3939 | 37.78
2023-02-09 06:00 | 44966.25 | 0 | 11.9145 | 37.78
2023-02-09 06:30 | 44966.2708 | 0 | 12.5371 | 37.78
2023-02-09 07:00 | 44966.2917 | 0 | 12.5844 | 37.78
2023-02-09 07:30 | 44966.3125 | 0 | 12.7117 | 37.78
2023-02-09 08:00 | 44966.3333 | 0 | 12.9869 | 37.78
2023-02-09 08:30 | 44966.3542 | 0 | 12.8269 | 37.78
2023-02-09 09:00 | 44966.375 | 0 | 14.1015 | 37.78
2023-02-09 09:30 | 44966.3958 | 0 | 14.31 | 37.78
2023-02-09 10:00 | 44966.4167 | 0 | 13.2536 | 37.78
2023-02-09 10:30 | 44966.4375 | 0 | 15.1548 | 37.78
2023-02-09 11:00 | 44966.4583 | 0 | 16.7359 | 37.78
2023-02-09 11:30 | 44966.4792 | 0 | 14.0085 | 37.78
2023-02-09 12:00 | 44966.5 | 0 | 14.8785 | 37.78
2023-02-09 12:30 | 44966.5208 | 0 | 13.6507 | 37.78
2023-02-09 13:00 | 44966.5417 | 0 | 11.9903 | 37.78
2023-02-09 13:30 | 44966.5625 | 0 | 13.8097 | 37.78
2023-02-09 14:00 | 44966.5833 | 0 | 15.2294 | 37.78
2023-02-09 14:30 | 44966.6042 | 0 | 15.8527 | 37.78
2023-02-09 15:00 | 44966.625 | 0 | 14.6265 | 37.78
2023-02-09 15:30 | 44966.6458 | 0 | 13.9707 | 37.78
2023-02-09 16:00 | 44966.6667 | 0 | 14.8244 | 37.78
2023-02-09 16:30 | 44966.6875 | 0 | 15.1568 | 37.78
2023-02-09 17:00 | 44966.7083 | 0 | 15.1693 | 37.78
2023-02-09 17:30 | 44966.7292 | 0 | 15.7272 | 37.78
2023-02-09 18:00 | 44966.75 | 0 | 15.648 | 37.78
2023-02-09 18:30 | 44966.7708 | 0 | 16.0094 | 37.78
2023-02-09 19:00 | 44966.7917 | 0 | 15.9536 | 37.78
2023-02-09 19:30 | 44966.8125 | 0 | 15.7992 | 37.78
2023-02-09 20:00 | 44966.8333 | 0 | 15.6682 | 37.78
2023-02-09 20:30 | 44966.8542 | 0 | 15.0945 | 37.78
2023-02-09 21:00 | 44966.875 | 0 | 14.56 | 37.78
2023-02-09 21:30 | 44966.8958 | 0 | 14.0258 | 37.78
2023-02-09 22:00 | 44966.9167 | 0 | 13.3638 | 37.78
2023-02-09 22:30 | 44966.9375 | 0 | 12.5322 | 37.78
2023-02-09 23:00 | 44966.9583 | 0 | 11.934 | 37.78
2023-02-09 23:30 | 44966.9792 | 0 | 11.2448 | 37.78
2023-02-10 | 44967 | 0 | 10.5905 | 37.78
2023-02-10 00:30 | 44967.0208 | 0 | 10.4799 | 37.78
2023-02-10 01:00 | 44967.0417 | 0 | 10.1276 | 37.78
2023-02-10 01:30 | 44967.0625 | 0 | 9.9189 | 37.78
2023-02-10 02:00 | 44967.0833 | 0 | 9.8613 | 37.78
2023-02-10 02:30 | 44967.1042 | 0 | 9.658 | 37.78
2023-02-10 03:00 | 44967.125 | 0 | 9.4511 | 37.78
2023-02-10 03:30 | 44967.1458 | 0 | 9.604 | 37.78
2023-02-10 04:00 | 44967.1667 | 0 | 9.7403 | 37.78
2023-02-10 04:30 | 44967.1875 | 0 | 10.0033 | 37.78
2023-02-10 05:00 | 44967.2083 | 0 | 10.5477 | 37.78
2023-02-10 05:30 | 44967.2292 | 0 | 10.8939 | 37.78
2023-02-10 06:00 | 44967.25 | 0 | 11.4046 | 37.78
2023-02-10 06:30 | 44967.2708 | 0 | 11.959 | 37.78
2023-02-10 07:00 | 44967.2917 | 0 | 12.6299 | 37.78
2023-02-10 07:30 | 44967.3125 | 0 | 12.6573 | 37.78
2023-02-10 08:00 | 44967.3333 | 0 | 12.0155 | 37.78
2023-02-10 08:30 | 44967.3542 | 0 | 11.8609 | 37.78
2023-02-10 09:00 | 44967.375 | 0 | 11.7951 | 37.78
2023-02-10 09:30 | 44967.3958 | 0 | 12.1589 | 37.78
2023-02-10 10:00 | 44967.4167 | 0 | 12.4965 | 37.78
2023-02-10 10:30 | 44967.4375 | 0 | 12.6945 | 37.78
2023-02-10 11:00 | 44967.4583 | 0 | 12.174 | 37.78
2023-02-10 11:30 | 44967.4792 | 0 | 13.31 | 37.78
2023-02-10 12:00 | 44967.5 | 0 | 13.0779 | 37.78
2023-02-10 12:30 | 44967.5208 | 0 | 12.879 | 37.78
2023-02-10 13:00 | 44967.5417 | 0 | 13.0528 | 37.78
2023-02-10 13:30 | 44967.5625 | 0 | 13.8613 | 37.78
2023-02-10 14:00 | 44967.5833 | 0 | 15.78 | 37.78
2023-02-10 14:30 | 44967.6042 | 0 | 14.0159 | 37.78
2023-02-10 15:00 | 44967.625 | 0 | 13.9602 | 37.78
2023-02-10 15:30 | 44967.6458 | 0 | 14.6317 | 37.78
2023-02-10 16:00 | 44967.6667 | 0 | 15.4647 | 37.78
2023-02-10 16:30 | 44967.6875 | 0 | 16.2903 | 37.78
2023-02-10 17:00 | 44967.7083 | 0 | 16.6123 | 37.78
2023-02-10 17:30 | 44967.7292 | 0 | 16.9107 | 37.78
2023-02-10 18:00 | 44967.75 | 0 | 16.6854 | 37.78
2023-02-10 18:30 | 44967.7708 | 0 | 16.5452 | 37.78
2023-02-10 19:00 | 44967.7917 | 0 | 16.5781 | 37.78
2023-02-10 19:30 | 44967.8125 | 0 | 16.2076 | 37.78
2023-02-10 20:00 | 44967.8333 | 0 | 15.9045 | 37.78
2023-02-10 20:30 | 44967.8542 | 0 | 15.4146 | 37.78
2023-02-10 21:00 | 44967.875 | 0 | 14.9367 | 37.78
2023-02-10 21:30 | 44967.8958 | 0 | 14.4258 | 37.78
2023-02-10 22:00 | 44967.9167 | 0 | 13.6085 | 37.78
2023-02-10 22:30 | 44967.9375 | 0 | 12.7622 | 37.78
2023-02-10 23:00 | 44967.9583 | 0 | 12.1798 | 37.78
2023-02-10 23:30 | 44967.9792 | 0 | 11.7005 | 37.78
2023-02-11 | 44968 | 0 | 11.2478 | 37.78
2023-02-11 00:30 | 44968.0208 | 0 | 10.802 | 37.78
2023-02-11 01:00 | 44968.0417 | 0 | 10.2546 | 37.78
2023-02-11 01:30 | 44968.0625 | 0 | 10.1866 | 37.78
2023-02-11 02:00 | 44968.0833 | 0 | 9.9989 | 37.78
2023-02-11 02:30 | 44968.1042 | 0 | 9.8603 | 37.78
2023-02-11 03:00 | 44968.125 | 0 | 9.539 | 37.78
2023-02-11 03:30 | 44968.1458 | 0 | 9.605 | 37.78
2023-02-11 04:00 | 44968.1667 | 0 | 9.6144 | 37.78
2023-02-11 04:30 | 44968.1875 | 0 | 9.5995 | 37.78
2023-02-11 05:00 | 44968.2083 | 0 | 9.5684 | 37.78
2023-02-11 05:30 | 44968.2292 | 0 | 9.4962 | 37.78
2023-02-11 06:00 | 44968.25 | 0 | 9.5771 | 37.78
2023-02-11 06:30 | 44968.2708 | 0 | 9.4201 | 37.78
2023-02-11 07:00 | 44968.2917 | 0 | 9.3163 | 37.78
2023-02-11 07:30 | 44968.3125 | 0 | 8.8704 | 37.78
2023-02-11 08:00 | 44968.3333 | 0 | 8.7945 | 37.78
2023-02-11 08:30 | 44968.3542 | 0 | 8.7618 | 37.78
2023-02-11 09:00 | 44968.375 | 0 | 8.7411 | 37.78
2023-02-11 09:30 | 44968.3958 | 0 | 8.7638 | 37.78
2023-02-11 10:00 | 44968.4167 | 0 | 8.8304 | 37.78
2023-02-11 10:30 | 44968.4375 | 0 | 8.8839 | 37.78
2023-02-11 11:00 | 44968.4583 | 0 | 9.3242 | 37.78
2023-02-11 11:30 | 44968.4792 | 0 | 9.6024 | 37.78
2023-02-11 12:00 | 44968.5 | 0 | 9.9228 | 37.78
2023-02-11 12:30 | 44968.5208 | 0 | 10.401 | 37.78
2023-02-11 13:00 | 44968.5417 | 0 | 10.9614 | 37.78
2023-02-11 13:30 | 44968.5625 | 0 | 11.4717 | 37.78
2023-02-11 14:00 | 44968.5833 | 0 | 12.0176 | 37.78
2023-02-11 14:30 | 44968.6042 | 0 | 12.7968 | 37.78
2023-02-11 15:00 | 44968.625 | 0 | 13.5384 | 37.78
2023-02-11 15:30 | 44968.6458 | 0 | 14.3534 | 37.78
2023-02-11 16:00 | 44968.6667 | 0 | 15.09 | 37.78
2023-02-11 16:30 | 44968.6875 | 0 | 15.9333 | 37.78
2023-02-11 17:00 | 44968.7083 | 0 | 16.4628 | 37.78
2023-02-11 17:30 | 44968.7292 | 0 | 16.6991 | 37.78
2023-02-11 18:00 | 44968.75 | 0 | 16.652 | 37.78
2023-02-11 18:30 | 44968.7708 | 0 | 16.5239 | 37.78
2023-02-11 19:00 | 44968.7917 | 0 | 16.4908 | 37.78
2023-02-11 19:30 | 44968.8125 | 0 | 15.9987 | 37.78
2023-02-11 20:00 | 44968.8333 | 0 | 15.3991 | 37.78
2023-02-11 20:30 | 44968.8542 | 0 | 14.8554 | 37.78
2023-02-11 21:00 | 44968.875 | 0 | 14.444 | 37.78
2023-02-11 21:30 | 44968.8958 | 0 | 14.0986 | 37.78
2023-02-11 22:00 | 44968.9167 | 0 | 13.3907 | 37.78
2023-02-11 22:30 | 44968.9375 | 0 | 12.5539 | 37.78
2023-02-11 23:00 | 44968.9583 | 0 | 11.8093 | 37.78
2023-02-11 23:30 | 44968.9792 | 0 | 11.0592 | 37.78
2023-02-12 | 44969 | 0 | 10.5248 | 37.78
2023-02-12 00:30 | 44969.0208 | 0 | 10.0775 | 37.78
2023-02-12 01:00 | 44969.0417 | 0 | 9.8428 | 37.78
2023-02-12 01:30 | 44969.0625 | 0 | 9.7168 | 37.78
2023-02-12 02:00 | 44969.0833 | 0 | 9.4881 | 37.78
2023-02-12 02:30 | 44969.1042 | 0 | 9.3839 | 37.78
2023-02-12 03:00 | 44969.125 | 0 | 9.2434 | 37.78
2023-02-12 03:30 | 44969.1458 | 0 | 9.1849 | 37.78
2023-02-12 04:00 | 44969.1667 | 0 | 9.1315 | 37.78
2023-02-12 04:30 | 44969.1875 | 0 | 9.0958 | 37.78
2023-02-12 05:00 | 44969.2083 | 0 | 9.0071 | 37.78
2023-02-12 05:30 | 44969.2292 | 0 | 8.9227 | 37.78
2023-02-12 06:00 | 44969.25 | 0 | 9.0532 | 37.78
2023-02-12 06:30 | 44969.2708 | 0 | 9.1428 | 37.78
2023-02-12 07:00 | 44969.2917 | 0 | 9.22 | 37.78
2023-02-12 07:30 | 44969.3125 | 0 | 7.9115 | 37.78
2023-02-12 08:00 | 44969.3333 | 0 | 7.7861 | 37.78
2023-02-12 08:30 | 44969.3542 | 0 | 8.1366 | 37.78
2023-02-12 09:00 | 44969.375 | 0 | 8.5328 | 37.78
2023-02-12 09:30 | 44969.3958 | 0 | 8.8677 | 37.78
2023-02-12 10:00 | 44969.4167 | 0 | 9.4996 | 37.78
2023-02-12 10:30 | 44969.4375 | 0 | 10.0408 | 37.78
2023-02-12 11:00 | 44969.4583 | 0 | 10.6296 | 37.78
2023-02-12 11:30 | 44969.4792 | 0 | 11.1811 | 37.78
2023-02-12 12:00 | 44969.5 | 0 | 11.7836 | 37.78
2023-02-12 12:30 | 44969.5208 | 0 | 12.3499 | 37.78
2023-02-12 13:00 | 44969.5417 | 0 | 13.1027 | 37.78
2023-02-12 13:30 | 44969.5625 | 0 | 13.9217 | 37.78
2023-02-12 14:00 | 44969.5833 | 0 | 14.4881 | 37.78
2023-02-12 14:30 | 44969.6042 | 0 | 15.3238 | 37.78
2023-02-12 15:00 | 44969.625 | 0 | 16.2305 | 37.78
2023-02-12 15:30 | 44969.6458 | 0 | 17.0227 | 37.78
2023-02-12 16:00 | 44969.6667 | 0 | 17.8786 | 37.78
2023-02-12 16:30 | 44969.6875 | 0 | 18.8435 | 37.78
2023-02-12 17:00 | 44969.7083 | 0 | 19.6078 | 37.78
2023-02-12 17:30 | 44969.7292 | 0 | 19.9419 | 37.78
2023-02-12 18:00 | 44969.75 | 0 | 20.1292 | 37.78
2023-02-12 18:30 | 44969.7708 | 0 | 20.3147 | 37.78
2023-02-12 19:00 | 44969.7917 | 0 | 20.3426 | 37.78
2023-02-12 19:30 | 44969.8125 | 0 | 19.6843 | 37.78
2023-02-12 20:00 | 44969.8333 | 0 | 18.9985 | 37.78
2023-02-12 20:30 | 44969.8542 | 0 | 18.1408 | 37.78
2023-02-12 21:00 | 44969.875 | 0 | 17.5175 | 37.78
2023-02-12 21:30 | 44969.8958 | 0 | 16.5595 | 37.78
2023-02-12 22:00 | 44969.9167 | 0 | 15.5118 | 37.78
2023-02-12 22:30 | 44969.9375 | 0 | 14.1171 | 37.78
2023-02-12 23:00 | 44969.9583 | 0 | 13.2834 | 37.78
2023-02-12 23:30 | 44969.9792 | 0 | 12.6068 | 37.78
2023-02-13 | 44970 | 0 | 12.177 | 37.78
2023-02-13 00:30 | 44970.0208 | 0 | 11.7682 | 37.78
2023-02-13 01:00 | 44970.0417 | 0 | 11.7162 | 37.78
2023-02-13 01:30 | 44970.0625 | 0 | 11.4097 | 37.78
2023-02-13 02:00 | 44970.0833 | 0 | 11.3699 | 37.78
2023-02-13 02:30 | 44970.1042 | 0 | 11.3086 | 37.78
2023-02-13 03:00 | 44970.125 | 0 | 11.1582 | 37.78
2023-02-13 03:30 | 44970.1458 | 0 | 11.3541 | 37.78
2023-02-13 04:00 | 44970.1667 | 0 | 11.5791 | 37.78
2023-02-13 04:30 | 44970.1875 | 0 | 11.9341 | 37.78
2023-02-13 05:00 | 44970.2083 | 0 | 12.3128 | 37.78
2023-02-13 05:30 | 44970.2292 | 0 | 12.5624 | 37.78
2023-02-13 06:00 | 44970.25 | 0 | 13.5707 | 37.78
2023-02-13 06:30 | 44970.2708 | 0 | 14.2843 | 37.78
2023-02-13 07:00 | 44970.2917 | 0 | 14.9068 | 37.78
2023-02-13 07:30 | 44970.3125 | 0 | 15.2782 | 37.78
2023-02-13 08:00 | 44970.3333 | 0 | 16.5913 | 37.78
2023-02-13 08:30 | 44970.3542 | 0 | 17.0542 | 37.78
2023-02-13 09:00 | 44970.375 | 0 | 17.4968 | 37.78
2023-02-13 09:30 | 44970.3958 | 0 | 18.181 | 37.78
2023-02-13 10:00 | 44970.4167 | 0 | 17.9867 | 37.78
2023-02-13 10:30 | 44970.4375 | 0 | 17.7194 | 37.78
2023-02-13 11:00 | 44970.4583 | 0 | 18.2886 | 37.78
2023-02-13 11:30 | 44970.4792 | 0 | 19.0368 | 37.78
2023-02-13 12:00 | 44970.5 | 0 | 17.0711 | 37.78
2023-02-13 12:30 | 44970.5208 | 0 | 17.1322 | 37.78
2023-02-13 13:00 | 44970.5417 | 0 | 17.6484 | 37.78
2023-02-13 13:30 | 44970.5625 | 0 | 18.3484 | 37.78
2023-02-13 14:00 | 44970.5833 | 0 | 18.8857 | 37.78
2023-02-13 14:30 | 44970.6042 | 0 | 19.329 | 37.78
2023-02-13 15:00 | 44970.625 | 0 | 20.3681 | 37.78
2023-02-13 15:30 | 44970.6458 | 0 | 21.856 | 37.78
2023-02-13 16:00 | 44970.6667 | 0 | 22.3974 | 37.78
2023-02-13 16:30 | 44970.6875 | 0 | 22.9247 | 37.78
2023-02-13 17:00 | 44970.7083 | 0 | 22.9427 | 37.78
2023-02-13 17:30 | 44970.7292 | 0 | 22.8781 | 37.78
2023-02-13 18:00 | 44970.75 | 0 | 22.8067 | 37.78
2023-02-13 18:30 | 44970.7708 | 0 | 22.6835 | 37.78
2023-02-13 19:00 | 44970.7917 | 0 | 22.2573 | 37.78
2023-02-13 19:30 | 44970.8125 | 0 | 21.752 | 37.78
2023-02-13 20:00 | 44970.8333 | 0 | 20.6461 | 37.78
2023-02-13 20:30 | 44970.8542 | 0 | 19.5445 | 37.78
2023-02-13 21:00 | 44970.875 | 0 | 18.4571 | 37.78
2023-02-13 21:30 | 44970.8958 | 0 | 17.8257 | 37.78
2023-02-13 22:00 | 44970.9167 | 0 | 16.5934 | 37.78
2023-02-13 22:30 | 44970.9375 | 0 | 15.4665 | 37.78
2023-02-13 23:00 | 44970.9583 | 0 | 14.5856 | 37.78
2023-02-13 23:30 | 44970.9792 | 0 | 13.9499 | 37.78
2023-02-14 | 44971 | 0 | 13.0795 | 37.78
2023-02-14 00:30 | 44971.0208 | 0 | 12.4713 | 37.78
2023-02-14 01:00 | 44971.0417 | 0 | 12.2545 | 37.78
2023-02-14 01:30 | 44971.0625 | 0 | 11.8995 | 37.78
2023-02-14 02:00 | 44971.0833 | 0 | 11.746 | 37.78
2023-02-14 02:30 | 44971.1042 | 0 | 11.4624 | 37.78
2023-02-14 03:00 | 44971.125 | 0 | 11.2758 | 37.78
2023-02-14 03:30 | 44971.1458 | 0 | 11.2521 | 37.78
2023-02-14 04:00 | 44971.1667 | 0 | 11.6399 | 37.78
2023-02-14 04:30 | 44971.1875 | 0 | 12.0028 | 37.78
2023-02-14 05:00 | 44971.2083 | 0 | 12.5759 | 37.78
2023-02-14 05:30 | 44971.2292 | 0 | 12.8716 | 37.78
2023-02-14 06:00 | 44971.25 | 0 | 13.7235 | 37.78
2023-02-14 06:30 | 44971.2708 | 0 | 14.2636 | 37.78
2023-02-14 07:00 | 44971.2917 | 0 | 14.856 | 37.78
2023-02-14 07:30 | 44971.3125 | 0 | 14.9986 | 37.78
2023-02-14 08:00 | 44971.3333 | 0 | 15.9207 | 37.78
2023-02-14 08:30 | 44971.3542 | 0 | 16.8697 | 37.78
2023-02-14 09:00 | 44971.375 | 0 | 17.9254 | 37.78
2023-02-14 09:30 | 44971.3958 | 0 | 18.4922 | 37.78
2023-02-14 10:00 | 44971.4167 | 0 | 18.8225 | 37.78
2023-02-14 10:30 | 44971.4375 | 0 | 18.4463 | 37.78
2023-02-14 11:00 | 44971.4583 | 0 | 16.3692 | 37.78
2023-02-14 11:30 | 44971.4792 | 0 | 13.7747 | 37.78
2023-02-14 12:00 | 44971.5 | 0 | 17.0854 | 37.78
2023-02-14 12:30 | 44971.5208 | 0 | 16.6573 | 37.78
2023-02-14 13:00 | 44971.5417 | 0 | 15.6442 | 37.78
2023-02-14 13:30 | 44971.5625 | 0 | 16.7861 | 37.78
2023-02-14 14:00 | 44971.5833 | 0 | 19.5123 | 37.78
2023-02-14 14:30 | 44971.6042 | 0 | 20.3245 | 37.78
2023-02-14 15:00 | 44971.625 | 0 | 19.0122 | 37.78
2023-02-14 15:30 | 44971.6458 | 0 | 18.316 | 37.78
2023-02-14 16:00 | 44971.6667 | 0 | 17.1236 | 37.78
2023-02-14 16:30 | 44971.6875 | 0 | 16.8783 | 37.78
2023-02-14 17:00 | 44971.7083 | 0 | 16.598 | 37.78
2023-02-14 17:30 | 44971.7292 | 0 | 16.0133 | 37.78
2023-02-14 18:00 | 44971.75 | 0 | 15.7198 | 37.78
2023-02-14 18:30 | 44971.7708 | 0 | 15.8949 | 37.78
2023-02-14 19:00 | 44971.7917 | 0 | 16.0095 | 37.78
2023-02-14 19:30 | 44971.8125 | 0 | 15.8783 | 37.78
2023-02-14 20:00 | 44971.8333 | 0 | 15.5896 | 37.78
2023-02-14 20:30 | 44971.8542 | 0 | 15.1306 | 37.78
2023-02-14 21:00 | 44971.875 | 0 | 14.9206 | 37.78
2023-02-14 21:30 | 44971.8958 | 0 | 14.2977 | 37.78
2023-02-14 22:00 | 44971.9167 | 0 | 13.4968 | 37.78
2023-02-14 22:30 | 44971.9375 | 0 | 12.3314 | 37.78
2023-02-14 23:00 | 44971.9583 | 0 | 11.7002 | 37.78
2023-02-14 23:30 | 44971.9792 | 0 | 11.1084 | 37.78
2023-02-15 | 44972 | 0 | 10.5799 | 37.78
2023-02-15 00:30 | 44972.0208 | 0 | 10.1653 | 37.78
2023-02-15 01:00 | 44972.0417 | 0 | 9.9687 | 37.78
2023-02-15 01:30 | 44972.0625 | 0 | 9.9514 | 37.78
2023-02-15 02:00 | 44972.0833 | 0 | 9.7529 | 37.78
2023-02-15 02:30 | 44972.1042 | 0 | 9.5839 | 37.78
2023-02-15 03:00 | 44972.125 | 0 | 9.5435 | 37.78
2023-02-15 03:30 | 44972.1458 | 0 | 9.6499 | 37.78
2023-02-15 04:00 | 44972.1667 | 0 | 9.7819 | 37.78
2023-02-15 04:30 | 44972.1875 | 0 | 10.136 | 37.78
2023-02-15 05:00 | 44972.2083 | 0 | 10.4953 | 37.78
2023-02-15 05:30 | 44972.2292 | 0 | 11.0588 | 37.78
2023-02-15 06:00 | 44972.25 | 0 | 11.614 | 37.78
2023-02-15 06:30 | 44972.2708 | 0 | 11.7315 | 37.78
2023-02-15 07:00 | 44972.2917 | 0 | 12.4274 | 37.78
2023-02-15 07:30 | 44972.3125 | 0 | 11.4253 | 37.78
2023-02-15 08:00 | 44972.3333 | 0 | 12.2018 | 37.78
2023-02-15 08:30 | 44972.3542 | 0 | 12.4806 | 37.78
2023-02-15 09:00 | 44972.375 | 0 | 12.5801 | 37.78
2023-02-15 09:30 | 44972.3958 | 0 | 13.7268 | 37.78
2023-02-15 10:00 | 44972.4167 | 0 | 13.683 | 37.78
2023-02-15 10:30 | 44972.4375 | 0 | 13.1162 | 37.78
2023-02-15 11:00 | 44972.4583 | 0 | 14.4597 | 37.78
2023-02-15 11:30 | 44972.4792 | 0 | 13.6972 | 37.78
2023-02-15 12:00 | 44972.5 | 0 | 12.7598 | 37.78
2023-02-15 12:30 | 44972.5208 | 0 | 13.927 | 37.78
2023-02-15 13:00 | 44972.5417 | 0 | 13.8346 | 37.78
2023-02-15 13:30 | 44972.5625 | 0 | 13.7984 | 37.78
2023-02-15 14:00 | 44972.5833 | 0 | 14.3769 | 37.78
2023-02-15 14:30 | 44972.6042 | 0 | 14.9963 | 37.78
2023-02-15 15:00 | 44972.625 | 0 | 13.4985 | 37.78
2023-02-15 15:30 | 44972.6458 | 0 | 14.5576 | 37.78
2023-02-15 16:00 | 44972.6667 | 0 | 14.921 | 37.78
2023-02-15 16:30 | 44972.6875 | 0 | 15.315 | 37.78
2023-02-15 17:00 | 44972.7083 | 0 | 15.2201 | 37.78
2023-02-15 17:30 | 44972.7292 | 0 | 15.4142 | 37.78
2023-02-15 18:00 | 44972.75 | 0 | 15.3783 | 37.78
2023-02-15 18:30 | 44972.7708 | 0 | 15.6001 | 37.78
2023-02-15 19:00 | 44972.7917 | 0 | 15.7454 | 37.78
2023-02-15 19:30 | 44972.8125 | 0 | 15.3119 | 37.78
2023-02-15 20:00 | 44972.8333 | 0 | 15.0321 | 37.78
2023-02-15 20:30 | 44972.8542 | 0 | 14.2773 | 37.78
2023-02-15 21:00 | 44972.875 | 0 | 13.804 | 37.78
2023-02-15 21:30 | 44972.8958 | 0 | 13.33 | 37.78
2023-02-15 22:00 | 44972.9167 | 0 | 12.6732 | 37.78
2023-02-15 22:30 | 44972.9375 | 0 | 11.689 | 37.78
2023-02-15 23:00 | 44972.9583 | 0 | 11.2591 | 37.78
2023-02-15 23:30 | 44972.9792 | 0 | 10.7671 | 37.78
2023-02-16 | 44973 | 0 | 10.1486 | 37.78
2023-02-16 00:30 | 44973.0208 | 0 | 9.8091 | 37.78
2023-02-16 01:00 | 44973.0417 | 0 | 9.5475 | 37.78
2023-02-16 01:30 | 44973.0625 | 0 | 9.2401 | 37.78
2023-02-16 02:00 | 44973.0833 | 0 | 9.1169 | 37.78
2023-02-16 02:30 | 44973.1042 | 0 | 9.1585 | 37.78
2023-02-16 03:00 | 44973.125 | 0 | 9.0777 | 37.78
2023-02-16 03:30 | 44973.1458 | 0 | 9.1426 | 37.78
2023-02-16 04:00 | 44973.1667 | 0 | 9.3354 | 37.78
2023-02-16 04:30 | 44973.1875 | 0 | 9.598 | 37.78
2023-02-16 05:00 | 44973.2083 | 0 | 10.0389 | 37.78
2023-02-16 05:30 | 44973.2292 | 0 | 10.4159 | 37.78
2023-02-16 06:00 | 44973.25 | 0 | 11.0989 | 37.78
2023-02-16 06:30 | 44973.2708 | 0 | 11.2837 | 37.78
2023-02-16 07:00 | 44973.2917 | 0 | 11.424 | 37.78
2023-02-16 07:30 | 44973.3125 | 0 | 10.8967 | 37.78
2023-02-16 08:00 | 44973.3333 | 0 | 10.753 | 37.78
2023-02-16 08:30 | 44973.3542 | 0 | 10.7949 | 37.78
2023-02-16 09:00 | 44973.375 | 0 | 11.6253 | 37.78
2023-02-16 09:30 | 44973.3958 | 0 | 12.3361 | 37.78
2023-02-16 10:00 | 44973.4167 | 0 | 12.6246 | 37.78
2023-02-16 10:30 | 44973.4375 | 0 | 13.0416 | 37.78
2023-02-16 11:00 | 44973.4583 | 0 | 12.6499 | 37.78
2023-02-16 11:30 | 44973.4792 | 0 | 12.4773 | 37.78
2023-02-16 12:00 | 44973.5 | 0 | 12.1764 | 37.78
2023-02-16 12:30 | 44973.5208 | 0 | 11.8144 | 37.78
2023-02-16 13:00 | 44973.5417 | 0 | 13.1211 | 37.78
2023-02-16 13:30 | 44973.5625 | 0 | 12.7485 | 37.78
2023-02-16 14:00 | 44973.5833 | 0 | 13.216 | 37.78
2023-02-16 14:30 | 44973.6042 | 0 | 14.0945 | 37.78
2023-02-16 15:00 | 44973.625 | 0 | 13.4728 | 37.78
2023-02-16 15:30 | 44973.6458 | 0 | 14.2286 | 37.78
2023-02-16 16:00 | 44973.6667 | 0 | 14.0183 | 37.78
2023-02-16 16:30 | 44973.6875 | 0 | 14.7856 | 37.78
2023-02-16 17:00 | 44973.7083 | 0 | 15.0611 | 37.78
2023-02-16 17:30 | 44973.7292 | 0 | 15.6339 | 37.78
2023-02-16 18:00 | 44973.75 | 0 | 15.7133 | 37.78
2023-02-16 18:30 | 44973.7708 | 0 | 15.732 | 37.78
2023-02-16 19:00 | 44973.7917 | 0 | 15.7667 | 37.78
2023-02-16 19:30 | 44973.8125 | 0 | 15.3427 | 37.78
2023-02-16 20:00 | 44973.8333 | 0 | 15.1847 | 37.78
2023-02-16 20:30 | 44973.8542 | 0 | 14.5727 | 37.78
2023-02-16 21:00 | 44973.875 | 0 | 14.0225 | 37.78
2023-02-16 21:30 | 44973.8958 | 0 | 13.1664 | 37.78
2023-02-16 22:00 | 44973.9167 | 0 | 12.447 | 37.78
2023-02-16 22:30 | 44973.9375 | 0 | 11.376 | 37.78
2023-02-16 23:00 | 44973.9583 | 0 | 10.9203 | 37.78
2023-02-16 23:30 | 44973.9792 | 0 | 10.4719 | 37.78
2023-02-17 | 44974 | 0 | 9.9767 | 37.78
2023-02-17 00:30 | 44974.0208 | 0 | 9.6169 | 37.78
2023-02-17 01:00 | 44974.0417 | 0 | 9.4696 | 37.78
2023-02-17 01:30 | 44974.0625 | 0 | 9.234 | 37.78
2023-02-17 02:00 | 44974.0833 | 0 | 9.1638 | 37.78
2023-02-17 02:30 | 44974.1042 | 0 | 9.1285 | 37.78
2023-02-17 03:00 | 44974.125 | 0 | 8.9658 | 37.78
2023-02-17 03:30 | 44974.1458 | 0 | 9.0972 | 37.78
2023-02-17 04:00 | 44974.1667 | 0 | 9.3785 | 37.78
2023-02-17 04:30 | 44974.1875 | 0 | 9.5574 | 37.78
2023-02-17 05:00 | 44974.2083 | 0 | 10.0672 | 37.78
2023-02-17 05:30 | 44974.2292 | 0 | 10.4081 | 37.78
2023-02-17 06:00 | 44974.25 | 0 | 10.9417 | 37.78
2023-02-17 06:30 | 44974.2708 | 0 | 11.3338 | 37.78
2023-02-17 07:00 | 44974.2917 | 0 | 11.4401 | 37.78
2023-02-17 07:30 | 44974.3125 | 0 | 10.8515 | 37.78
2023-02-17 08:00 | 44974.3333 | 0 | 10.924 | 37.78
2023-02-17 08:30 | 44974.3542 | 0 | 10.8991 | 37.78
2023-02-17 09:00 | 44974.375 | 0 | 11.3883 | 37.78
2023-02-17 09:30 | 44974.3958 | 0 | 10.8698 | 37.78
2023-02-17 10:00 | 44974.4167 | 0 | 10.8012 | 37.78
2023-02-17 10:30 | 44974.4375 | 0 | 10.6612 | 37.78
2023-02-17 11:00 | 44974.4583 | 0 | 11.0166 | 37.78
2023-02-17 11:30 | 44974.4792 | 0 | 11.3441 | 37.78
2023-02-17 12:00 | 44974.5 | 0 | 11.2148 | 37.78
2023-02-17 12:30 | 44974.5208 | 0 | 11.6048 | 37.78
2023-02-17 13:00 | 44974.5417 | 0 | 11.7464 | 37.78
2023-02-17 13:30 | 44974.5625 | 0 | 11.6738 | 37.78
2023-02-17 14:00 | 44974.5833 | 0 | 14.0879 | 37.78
2023-02-17 14:30 | 44974.6042 | 0 | 13.0929 | 37.78
2023-02-17 15:00 | 44974.625 | 0 | 14.1564 | 37.78
2023-02-17 15:30 | 44974.6458 | 0 | 16.3699 | 37.78
2023-02-17 16:00 | 44974.6667 | 0 | 15.0556 | 37.78
2023-02-17 16:30 | 44974.6875 | 0 | 15.6216 | 37.78
2023-02-17 17:00 | 44974.7083 | 0 | 16.0713 | 37.78
2023-02-17 17:30 | 44974.7292 | 0 | 16.2837 | 37.78
2023-02-17 18:00 | 44974.75 | 0 | 16.0129 | 37.78
2023-02-17 18:30 | 44974.7708 | 0 | 16.0201 | 37.78
2023-02-17 19:00 | 44974.7917 | 0 | 15.9475 | 37.78
2023-02-17 19:30 | 44974.8125 | 0 | 15.7833 | 37.78
2023-02-17 20:00 | 44974.8333 | 0 | 15.4445 | 37.78
2023-02-17 20:30 | 44974.8542 | 0 | 14.9858 | 37.78
2023-02-17 21:00 | 44974.875 | 0 | 14.4144 | 37.78
2023-02-17 21:30 | 44974.8958 | 0 | 13.8462 | 37.78
2023-02-17 22:00 | 44974.9167 | 0 | 13.0166 | 37.78
2023-02-17 22:30 | 44974.9375 | 0 | 12.3248 | 37.78
2023-02-17 23:00 | 44974.9583 | 0 | 11.7464 | 37.78
2023-02-17 23:30 | 44974.9792 | 0 | 11.0358 | 37.78
2023-02-18 | 44975 | 0 | 0.022333 | 37.78
2023-02-18 00:30 | 44975.0208 | 0 | 0.022333 | 37.78
2023-02-18 01:00 | 44975.0417 | 0 | 0.022333 | 37.78
2023-02-18 01:30 | 44975.0625 | 0 | 0.022333 | 37.78
2023-02-18 02:00 | 44975.0833 | 0 | 0.022333 | 37.78
2023-02-18 02:30 | 44975.1042 | 0 | 0.022333 | 37.78
2023-02-18 03:00 | 44975.125 | 0 | 0.022333 | 37.78
2023-02-18 03:30 | 44975.1458 | 0 | 0.022333 | 37.78
2023-02-18 04:00 | 44975.1667 | 0 | 5.6297 | 37.78
2023-02-18 04:30 | 44975.1875 | 0 | 9.2223 | 37.78
2023-02-18 05:00 | 44975.2083 | 0 | 9.3319 | 37.78
2023-02-18 05:30 | 44975.2292 | 0 | 9.383 | 37.78
2023-02-18 06:00 | 44975.25 | 0 | 9.4452 | 37.78
2023-02-18 06:30 | 44975.2708 | 0 | 9.3004 | 37.78
2023-02-18 07:00 | 44975.2917 | 0 | 9.0823 | 37.78
2023-02-18 07:30 | 44975.3125 | 0 | 8.7857 | 37.78
2023-02-18 08:00 | 44975.3333 | 0 | 9.0602 | 37.78
2023-02-18 08:30 | 44975.3542 | 0 | 9.2683 | 37.78
2023-02-18 09:00 | 44975.375 | 0 | 9.9594 | 37.78
2023-02-18 09:30 | 44975.3958 | 0 | 9.4954 | 37.78
2023-02-18 10:00 | 44975.4167 | 0 | 9.6606 | 37.78
2023-02-18 10:30 | 44975.4375 | 0 | 9.4901 | 37.78
2023-02-18 11:00 | 44975.4583 | 0 | 10.956 | 37.78
2023-02-18 11:30 | 44975.4792 | 0 | 10.5949 | 37.78
2023-02-18 12:00 | 44975.5 | 0 | 10.3654 | 37.78
2023-02-18 12:30 | 44975.5208 | 0 | 9.9455 | 37.78
2023-02-18 13:00 | 44975.5417 | 0 | 9.8072 | 37.78
2023-02-18 13:30 | 44975.5625 | 0 | 10.1189 | 37.78
2023-02-18 14:00 | 44975.5833 | 0 | 10.6298 | 37.78
2023-02-18 14:30 | 44975.6042 | 0 | 11.4665 | 37.78
2023-02-18 15:00 | 44975.625 | 0 | 12.1176 | 37.78
2023-02-18 15:30 | 44975.6458 | 0 | 12.9064 | 37.78
2023-02-18 16:00 | 44975.6667 | 0 | 13.7582 | 37.78
2023-02-18 16:30 | 44975.6875 | 0 | 14.5541 | 37.78
2023-02-18 17:00 | 44975.7083 | 0 | 14.7498 | 37.78
2023-02-18 17:30 | 44975.7292 | 0 | 15.2236 | 37.78
2023-02-18 18:00 | 44975.75 | 0 | 15.0933 | 37.78
2023-02-18 18:30 | 44975.7708 | 0 | 14.8564 | 37.78
2023-02-18 19:00 | 44975.7917 | 0 | 14.7742 | 37.78
2023-02-18 19:30 | 44975.8125 | 0 | 14.3318 | 37.78
2023-02-18 20:00 | 44975.8333 | 0 | 14.1148 | 37.78
2023-02-18 20:30 | 44975.8542 | 0 | 13.7421 | 37.78
2023-02-18 21:00 | 44975.875 | 0 | 13.5111 | 37.78
2023-02-18 21:30 | 44975.8958 | 0 | 12.5294 | 37.78
2023-02-18 22:00 | 44975.9167 | 0 | 12.0152 | 37.78
2023-02-18 22:30 | 44975.9375 | 0 | 11.3778 | 37.78
2023-02-18 23:00 | 44975.9583 | 0 | 10.7103 | 37.78
2023-02-18 23:30 | 44975.9792 | 0 | 10.244 | 37.78
2023-02-19 | 44976 | 0 | 9.8652 | 37.78
2023-02-19 00:30 | 44976.0208 | 0 | 9.4919 | 37.78
2023-02-19 01:00 | 44976.0417 | 0 | 9.2612 | 37.78
2023-02-19 01:30 | 44976.0625 | 0 | 9.0561 | 37.78
2023-02-19 02:00 | 44976.0833 | 0 | 8.9225 | 37.78
2023-02-19 02:30 | 44976.1042 | 0 | 8.9265 | 37.78
2023-02-19 03:00 | 44976.125 | 0 | 8.7849 | 37.78
2023-02-19 03:30 | 44976.1458 | 0 | 8.6556 | 37.78
2023-02-19 04:00 | 44976.1667 | 0 | 8.532 | 37.78
2023-02-19 04:30 | 44976.1875 | 0 | 8.5875 | 37.78
2023-02-19 05:00 | 44976.2083 | 0 | 8.628 | 37.78
2023-02-19 05:30 | 44976.2292 | 0 | 8.5352 | 37.78
2023-02-19 06:00 | 44976.25 | 0 | 8.3264 | 37.78
2023-02-19 06:30 | 44976.2708 | 0 | 8.1732 | 37.78
2023-02-19 07:00 | 44976.2917 | 0 | 8.4174 | 37.78
2023-02-19 07:30 | 44976.3125 | 0 | 8.328 | 37.78
2023-02-19 08:00 | 44976.3333 | 0 | 7.4511 | 37.78
2023-02-19 08:30 | 44976.3542 | 0 | 8.2268 | 37.78
2023-02-19 09:00 | 44976.375 | 0 | 9.4218 | 37.78
2023-02-19 09:30 | 44976.3958 | 0 | 8.5042 | 37.78
2023-02-19 10:00 | 44976.4167 | 0 | 8.982 | 37.78
2023-02-19 10:30 | 44976.4375 | 0 | 9.1635 | 37.78
2023-02-19 11:00 | 44976.4583 | 0 | 8.15 | 37.78
2023-02-19 11:30 | 44976.4792 | 0 | 9.2611 | 37.78
2023-02-19 12:00 | 44976.5 | 0 | 8.3224 | 37.78
2023-02-19 12:30 | 44976.5208 | 0 | 8.0715 | 37.78
2023-02-19 13:00 | 44976.5417 | 0 | 9.3775 | 37.78
2023-02-19 13:30 | 44976.5625 | 0 | 11.0941 | 37.78
2023-02-19 14:00 | 44976.5833 | 0 | 11.1475 | 37.78
2023-02-19 14:30 | 44976.6042 | 0 | 12.0079 | 37.78
2023-02-19 15:00 | 44976.625 | 0 | 12.8971 | 37.78
2023-02-19 15:30 | 44976.6458 | 0 | 13.0016 | 37.78
2023-02-19 16:00 | 44976.6667 | 0 | 13.4952 | 37.78
2023-02-19 16:30 | 44976.6875 | 0 | 13.8699 | 37.78
2023-02-19 17:00 | 44976.7083 | 0 | 14.2097 | 37.78
2023-02-19 17:30 | 44976.7292 | 0 | 14.3936 | 37.78
2023-02-19 18:00 | 44976.75 | 0 | 14.7384 | 37.78
2023-02-19 18:30 | 44976.7708 | 0 | 14.9798 | 37.78
2023-02-19 19:00 | 44976.7917 | 0 | 14.9612 | 37.78
2023-02-19 19:30 | 44976.8125 | 0 | 14.6716 | 37.78
2023-02-19 20:00 | 44976.8333 | 0 | 14.353 | 37.78
2023-02-19 20:30 | 44976.8542 | 0 | 13.7345 | 37.78
2023-02-19 21:00 | 44976.875 | 0 | 13.2825 | 37.78
2023-02-19 21:30 | 44976.8958 | 0 | 12.4407 | 37.78
2023-02-19 22:00 | 44976.9167 | 0 | 11.69 | 37.78
2023-02-19 22:30 | 44976.9375 | 0 | 10.9807 | 37.78
2023-02-19 23:00 | 44976.9583 | 0 | 10.5068 | 37.78
2023-02-19 23:30 | 44976.9792 | 0 | 10.1602 | 37.78
2023-02-20 | 44977 | 0 | 9.7992 | 37.78
2023-02-20 00:30 | 44977.0208 | 0 | 9.5266 | 37.78
2023-02-20 01:00 | 44977.0417 | 0 | 9.4646 | 37.78
2023-02-20 01:30 | 44977.0625 | 0 | 9.2923 | 37.78
2023-02-20 02:00 | 44977.0833 | 0 | 9.1458 | 37.78
2023-02-20 02:30 | 44977.1042 | 0 | 9.1916 | 37.78
2023-02-20 03:00 | 44977.125 | 0 | 8.9392 | 37.78
2023-02-20 03:30 | 44977.1458 | 0 | 9.1984 | 37.78
2023-02-20 04:00 | 44977.1667 | 0 | 9.678 | 37.78
2023-02-20 04:30 | 44977.1875 | 0 | 9.9504 | 37.78
2023-02-20 05:00 | 44977.2083 | 0 | 10.4671 | 37.78
2023-02-20 05:30 | 44977.2292 | 0 | 10.7954 | 37.78
2023-02-20 06:00 | 44977.25 | 0 | 11.5908 | 37.78
2023-02-20 06:30 | 44977.2708 | 0 | 12.0509 | 37.78
2023-02-20 07:00 | 44977.2917 | 0 | 12.3825 | 37.78
2023-02-20 07:30 | 44977.3125 | 0 | 12.5802 | 37.78
2023-02-20 08:00 | 44977.3333 | 0 | 12.8059 | 37.78
2023-02-20 08:30 | 44977.3542 | 0 | 14.1098 | 37.78
2023-02-20 09:00 | 44977.375 | 0 | 13.5096 | 37.78
2023-02-20 09:30 | 44977.3958 | 0 | 13.3821 | 37.78
2023-02-20 10:00 | 44977.4167 | 0 | 13.7577 | 37.78
2023-02-20 10:30 | 44977.4375 | 0 | 14.1268 | 37.78
2023-02-20 11:00 | 44977.4583 | 0 | 14.598 | 37.78
2023-02-20 11:30 | 44977.4792 | 0 | 15.9673 | 37.78
2023-02-20 12:00 | 44977.5 | 0 | 14.7268 | 37.78
2023-02-20 12:30 | 44977.5208 | 0 | 14.1007 | 37.78
2023-02-20 13:00 | 44977.5417 | 0 | 13.2258 | 37.78
2023-02-20 13:30 | 44977.5625 | 0 | 13.6204 | 37.78
2023-02-20 14:00 | 44977.5833 | 0 | 13.0413 | 37.78
2023-02-20 14:30 | 44977.6042 | 0 | 14.4273 | 37.78
2023-02-20 15:00 | 44977.625 | 0 | 15.1557 | 37.78
2023-02-20 15:30 | 44977.6458 | 0 | 15.2914 | 37.78
2023-02-20 16:00 | 44977.6667 | 0 | 15.6278 | 37.78
2023-02-20 16:30 | 44977.6875 | 0 | 15.6758 | 37.78
2023-02-20 17:00 | 44977.7083 | 0 | 15.2878 | 37.78
2023-02-20 17:30 | 44977.7292 | 0 | 15.7647 | 37.78
2023-02-20 18:00 | 44977.75 | 0 | 15.8627 | 37.78
2023-02-20 18:30 | 44977.7708 | 0 | 16.4543 | 37.78
2023-02-20 19:00 | 44977.7917 | 0 | 16.2546 | 37.78
2023-02-20 19:30 | 44977.8125 | 0 | 15.9188 | 37.78
2023-02-20 20:00 | 44977.8333 | 0 | 15.6107 | 37.78
2023-02-20 20:30 | 44977.8542 | 0 | 14.9283 | 37.78
2023-02-20 21:00 | 44977.875 | 0 | 14.2772 | 37.78
2023-02-20 21:30 | 44977.8958 | 0 | 13.5729 | 37.78
2023-02-20 22:00 | 44977.9167 | 0 | 12.8108 | 37.78
2023-02-20 22:30 | 44977.9375 | 0 | 11.8888 | 37.78
2023-02-20 23:00 | 44977.9583 | 0 | 11.3508 | 37.78
2023-02-20 23:30 | 44977.9792 | 0 | 10.809 | 37.78
2023-02-21 | 44978 | 0 | 10.1296 | 37.78
2023-02-21 00:30 | 44978.0208 | 0 | 9.9886 | 37.78
2023-02-21 01:00 | 44978.0417 | 0 | 9.7826 | 37.78
2023-02-21 01:30 | 44978.0625 | 0 | 9.624 | 37.78
2023-02-21 02:00 | 44978.0833 | 0 | 9.5085 | 37.78
2023-02-21 02:30 | 44978.1042 | 0 | 9.4385 | 37.78
2023-02-21 03:00 | 44978.125 | 0 | 9.4529 | 37.78
2023-02-21 03:30 | 44978.1458 | 0 | 9.6023 | 37.78
2023-02-21 04:00 | 44978.1667 | 0 | 9.8182 | 37.78
2023-02-21 04:30 | 44978.1875 | 0 | 10.1147 | 37.78
2023-02-21 05:00 | 44978.2083 | 0 | 10.6622 | 37.78
2023-02-21 05:30 | 44978.2292 | 0 | 11.1909 | 37.78
2023-02-21 06:00 | 44978.25 | 0 | 12.0347 | 37.78
2023-02-21 06:30 | 44978.2708 | 0 | 12.5745 | 37.78
2023-02-21 07:00 | 44978.2917 | 0 | 12.677 | 37.78
2023-02-21 07:30 | 44978.3125 | 0 | 12.9455 | 37.78
2023-02-21 08:00 | 44978.3333 | 0 | 11.793 | 37.78
2023-02-21 08:30 | 44978.3542 | 0 | 14.3823 | 37.78
2023-02-21 09:00 | 44978.375 | 0 | 14.9338 | 37.78
2023-02-21 09:30 | 44978.3958 | 0 | 14.6234 | 37.78
2023-02-21 10:00 | 44978.4167 | 0 | 13.0139 | 37.78
2023-02-21 10:30 | 44978.4375 | 0 | 13.5495 | 37.78
2023-02-21 11:00 | 44978.4583 | 0 | 14.273 | 37.78
2023-02-21 11:30 | 44978.4792 | 0 | 13.8238 | 37.78
2023-02-21 12:00 | 44978.5 | 0 | 11.3257 | 37.78
2023-02-21 12:30 | 44978.5208 | 0 | 11.1445 | 37.78
2023-02-21 13:00 | 44978.5417 | 0 | 11.8799 | 37.78
2023-02-21 13:30 | 44978.5625 | 0 | 13.0217 | 37.78
2023-02-21 14:00 | 44978.5833 | 0 | 13.1579 | 37.78
2023-02-21 14:30 | 44978.6042 | 0 | 13.5338 | 37.78
2023-02-21 15:00 | 44978.625 | 0 | 14.6141 | 37.78
2023-02-21 15:30 | 44978.6458 | 0 | 15.2451 | 37.78
2023-02-21 16:00 | 44978.6667 | 0 | 15.2073 | 37.78
2023-02-21 16:30 | 44978.6875 | 0 | 15.9919 | 37.78
2023-02-21 17:00 | 44978.7083 | 0 | 15.8971 | 37.78
2023-02-21 17:30 | 44978.7292 | 0 | 16.289 | 37.78
2023-02-21 18:00 | 44978.75 | 0 | 16.1912 | 37.78
2023-02-21 18:30 | 44978.7708 | 0 | 16.8553 | 37.78
2023-02-21 19:00 | 44978.7917 | 0 | 16.8682 | 37.78
2023-02-21 19:30 | 44978.8125 | 0 | 16.255 | 37.78
2023-02-21 20:00 | 44978.8333 | 0 | 15.9151 | 37.78
2023-02-21 20:30 | 44978.8542 | 0 | 15.259 | 37.78
2023-02-21 21:00 | 44978.875 | 0 | 14.6513 | 37.78
2023-02-21 21:30 | 44978.8958 | 0 | 13.9551 | 37.78
2023-02-21 22:00 | 44978.9167 | 0 | 13.1439 | 37.78
2023-02-21 22:30 | 44978.9375 | 0 | 12.2116 | 37.78
2023-02-21 23:00 | 44978.9583 | 0 | 11.5663 | 37.78
2023-02-21 23:30 | 44978.9792 | 0 | 11.0617 | 37.78
2023-02-22 | 44979 | 0 | 10.572 | 37.78
2023-02-22 00:30 | 44979.0208 | 0 | 10.1231 | 37.78
2023-02-22 01:00 | 44979.0417 | 0 | 9.8656 | 37.78
2023-02-22 01:30 | 44979.0625 | 0 | 9.6326 | 37.78
2023-02-22 02:00 | 44979.0833 | 0 | 9.4882 | 37.78
2023-02-22 02:30 | 44979.1042 | 0 | 9.418 | 37.78
2023-02-22 03:00 | 44979.125 | 0 | 9.2248 | 37.78
2023-02-22 03:30 | 44979.1458 | 0 | 9.4151 | 37.78
2023-02-22 04:00 | 44979.1667 | 0 | 9.7878 | 37.78
2023-02-22 04:30 | 44979.1875 | 0 | 10.065 | 37.78
2023-02-22 05:00 | 44979.2083 | 0 | 10.6065 | 37.78
2023-02-22 05:30 | 44979.2292 | 0 | 11.1686 | 37.78
2023-02-22 06:00 | 44979.25 | 0 | 11.7283 | 37.78
2023-02-22 06:30 | 44979.2708 | 0 | 12.4884 | 37.78
2023-02-22 07:00 | 44979.2917 | 0 | 13.6138 | 37.78
2023-02-22 07:30 | 44979.3125 | 0 | 13.3392 | 37.78
2023-02-22 08:00 | 44979.3333 | 0 | 12.6112 | 37.78
2023-02-22 08:30 | 44979.3542 | 0 | 12.1769 | 37.78
2023-02-22 09:00 | 44979.375 | 0 | 13.0285 | 37.78
2023-02-22 09:30 | 44979.3958 | 0 | 12.7692 | 37.78
2023-02-22 10:00 | 44979.4167 | 0 | 11.9738 | 37.78
2023-02-22 10:30 | 44979.4375 | 0 | 11.3673 | 37.78
2023-02-22 11:00 | 44979.4583 | 0 | 10.4425 | 37.78
2023-02-22 11:30 | 44979.4792 | 0 | 10.8947 | 37.78
2023-02-22 12:00 | 44979.5 | 0 | 11.0131 | 37.78
2023-02-22 12:30 | 44979.5208 | 0 | 10.7883 | 37.78
2023-02-22 13:00 | 44979.5417 | 0 | 10.7171 | 37.78
2023-02-22 13:30 | 44979.5625 | 0 | 10.868 | 37.78
2023-02-22 14:00 | 44979.5833 | 0 | 12.2708 | 37.78
2023-02-22 14:30 | 44979.6042 | 0 | 13.6618 | 37.78
2023-02-22 15:00 | 44979.625 | 0 | 12.9597 | 37.78
2023-02-22 15:30 | 44979.6458 | 0 | 14.4218 | 37.78
2023-02-22 16:00 | 44979.6667 | 0 | 15.5842 | 37.78
2023-02-22 16:30 | 44979.6875 | 0 | 15.3337 | 37.78
2023-02-22 17:00 | 44979.7083 | 0 | 15.7264 | 37.78
2023-02-22 17:30 | 44979.7292 | 0 | 15.9121 | 37.78
2023-02-22 18:00 | 44979.75 | 0 | 15.648 | 37.78
2023-02-22 18:30 | 44979.7708 | 0 | 16.1897 | 37.78
2023-02-22 19:00 | 44979.7917 | 0 | 16.1171 | 37.78
2023-02-22 19:30 | 44979.8125 | 0 | 15.5311 | 37.78
2023-02-22 20:00 | 44979.8333 | 0 | 15.278 | 37.78
2023-02-22 20:30 | 44979.8542 | 0 | 14.7022 | 37.78
2023-02-22 21:00 | 44979.875 | 0 | 14.1526 | 37.78
2023-02-22 21:30 | 44979.8958 | 0 | 13.2432 | 37.78
2023-02-22 22:00 | 44979.9167 | 0 | 12.4018 | 37.78
2023-02-22 22:30 | 44979.9375 | 0 | 11.7617 | 37.78
2023-02-22 23:00 | 44979.9583 | 0 | 11.208 | 37.78
2023-02-22 23:30 | 44979.9792 | 0 | 10.732 | 37.78
2023-02-23 | 44980 | 0 | 10.2001 | 37.78
2023-02-23 00:30 | 44980.0208 | 0 | 9.7316 | 37.78
2023-02-23 01:00 | 44980.0417 | 0 | 9.6164 | 37.78
2023-02-23 01:30 | 44980.0625 | 0 | 9.4225 | 37.78
2023-02-23 02:00 | 44980.0833 | 0 | 9.4061 | 37.78
2023-02-23 02:30 | 44980.1042 | 0 | 9.2095 | 37.78
2023-02-23 03:00 | 44980.125 | 0 | 9.1201 | 37.78
2023-02-23 03:30 | 44980.1458 | 0 | 9.2772 | 37.78
2023-02-23 04:00 | 44980.1667 | 0 | 9.6439 | 37.78
2023-02-23 04:30 | 44980.1875 | 0 | 9.931 | 37.78
2023-02-23 05:00 | 44980.2083 | 0 | 10.4181 | 37.78
2023-02-23 05:30 | 44980.2292 | 0 | 10.8597 | 37.78
2023-02-23 06:00 | 44980.25 | 0 | 11.6099 | 37.78
2023-02-23 06:30 | 44980.2708 | 0 | 11.9454 | 37.78
2023-02-23 07:00 | 44980.2917 | 0 | 12.1398 | 37.78
2023-02-23 07:30 | 44980.3125 | 0 | 12.1674 | 37.78
2023-02-23 08:00 | 44980.3333 | 0 | 13.4231 | 37.78
2023-02-23 08:30 | 44980.3542 | 0 | 13.0866 | 37.78
2023-02-23 09:00 | 44980.375 | 0 | 12.1364 | 37.78
2023-02-23 09:30 | 44980.3958 | 0 | 12.8991 | 37.78
2023-02-23 10:00 | 44980.4167 | 0 | 13.8734 | 37.78
2023-02-23 10:30 | 44980.4375 | 0 | 13.5991 | 37.78
2023-02-23 11:00 | 44980.4583 | 0 | 13.3573 | 37.78
2023-02-23 11:30 | 44980.4792 | 0 | 12.5045 | 37.78
2023-02-23 12:00 | 44980.5 | 0 | 12.1987 | 37.78
2023-02-23 12:30 | 44980.5208 | 0 | 11.2356 | 37.78
2023-02-23 13:00 | 44980.5417 | 0 | 10.9555 | 37.78
2023-02-23 13:30 | 44980.5625 | 0 | 11.3797 | 37.78
2023-02-23 14:00 | 44980.5833 | 0 | 11.6503 | 37.78
2023-02-23 14:30 | 44980.6042 | 0 | 12.1187 | 37.78
2023-02-23 15:00 | 44980.625 | 0 | 12.5051 | 37.78
2023-02-23 15:30 | 44980.6458 | 0 | 13.8892 | 37.78
2023-02-23 16:00 | 44980.6667 | 0 | 13.7813 | 37.78
2023-02-23 16:30 | 44980.6875 | 0 | 15.738 | 37.78
2023-02-23 17:00 | 44980.7083 | 0 | 15.3784 | 37.78
2023-02-23 17:30 | 44980.7292 | 0 | 15.1501 | 37.78
2023-02-23 18:00 | 44980.75 | 0 | 14.831 | 37.78
2023-02-23 18:30 | 44980.7708 | 0 | 15.2793 | 37.78
2023-02-23 19:00 | 44980.7917 | 0 | 15.146 | 37.78
2023-02-23 19:30 | 44980.8125 | 0 | 14.8214 | 37.78
2023-02-23 20:00 | 44980.8333 | 0 | 14.6249 | 37.78
2023-02-23 20:30 | 44980.8542 | 0 | 14.0604 | 37.78
2023-02-23 21:00 | 44980.875 | 0 | 13.5012 | 37.78
2023-02-23 21:30 | 44980.8958 | 0 | 12.9506 | 37.78
2023-02-23 22:00 | 44980.9167 | 0 | 12.2076 | 37.78
2023-02-23 22:30 | 44980.9375 | 0 | 11.4137 | 37.78
2023-02-23 23:00 | 44980.9583 | 0 | 10.9174 | 37.78
2023-02-23 23:30 | 44980.9792 | 0 | 10.5336 | 37.78
2023-02-24 | 44981 | 0 | 9.8608 | 37.78
2023-02-24 00:30 | 44981.0208 | 0 | 9.5259 | 37.78
2023-02-24 01:00 | 44981.0417 | 0 | 9.3123 | 37.78
2023-02-24 01:30 | 44981.0625 | 0 | 9.14 | 37.78
2023-02-24 02:00 | 44981.0833 | 0 | 8.9863 | 37.78
2023-02-24 02:30 | 44981.1042 | 0 | 9.0321 | 37.78
2023-02-24 03:00 | 44981.125 | 0 | 8.9319 | 37.78
2023-02-24 03:30 | 44981.1458 | 0 | 9.1374 | 37.78
2023-02-24 04:00 | 44981.1667 | 0 | 9.4601 | 37.78
2023-02-24 04:30 | 44981.1875 | 0 | 9.7138 | 37.78
2023-02-24 05:00 | 44981.2083 | 0 | 10.2205 | 37.78
2023-02-24 05:30 | 44981.2292 | 0 | 10.8127 | 37.78
2023-02-24 06:00 | 44981.25 | 0 | 11.5813 | 37.78
2023-02-24 06:30 | 44981.2708 | 0 | 11.9196 | 37.78
2023-02-24 07:00 | 44981.2917 | 0 | 11.8755 | 37.78
2023-02-24 07:30 | 44981.3125 | 0 | 12.1291 | 37.78
2023-02-24 08:00 | 44981.3333 | 0 | 12.1256 | 37.78
2023-02-24 08:30 | 44981.3542 | 0 | 13.5766 | 37.78
2023-02-24 09:00 | 44981.375 | 0 | 12.5304 | 37.78
2023-02-24 09:30 | 44981.3958 | 0 | 11.6676 | 37.78
2023-02-24 10:00 | 44981.4167 | 0 | 11.3971 | 37.78
2023-02-24 10:30 | 44981.4375 | 0 | 12.8534 | 37.78
2023-02-24 11:00 | 44981.4583 | 0 | 12.3134 | 37.78
2023-02-24 11:30 | 44981.4792 | 0 | 12.8258 | 37.78
2023-02-24 12:00 | 44981.5 | 0 | 13.0721 | 37.78
2023-02-24 12:30 | 44981.5208 | 0 | 12.418 | 37.78
2023-02-24 13:00 | 44981.5417 | 0 | 10.5747 | 37.78
2023-02-24 13:30 | 44981.5625 | 0 | 11.425 | 37.78
2023-02-24 14:00 | 44981.5833 | 0 | 12.4512 | 37.78
2023-02-24 14:30 | 44981.6042 | 0 | 12.53 | 37.78
2023-02-24 15:00 | 44981.625 | 0 | 12.6777 | 37.78
2023-02-24 15:30 | 44981.6458 | 0 | 12.853 | 37.78
2023-02-24 16:00 | 44981.6667 | 0 | 12.077 | 37.78
2023-02-24 16:30 | 44981.6875 | 0 | 12.7195 | 37.78
2023-02-24 17:00 | 44981.7083 | 0 | 13.3177 | 37.78
2023-02-24 17:30 | 44981.7292 | 0 | 13.1848 | 37.78
2023-02-24 18:00 | 44981.75 | 0 | 13.3199 | 37.78
2023-02-24 18:30 | 44981.7708 | 0 | 13.6594 | 37.78
2023-02-24 19:00 | 44981.7917 | 0 | 13.6348 | 37.78
2023-02-24 19:30 | 44981.8125 | 0 | 13.5155 | 37.78
2023-02-24 20:00 | 44981.8333 | 0 | 13.4493 | 37.78
2023-02-24 20:30 | 44981.8542 | 0 | 13.0223 | 37.78
2023-02-24 21:00 | 44981.875 | 0 | 12.507 | 37.78
2023-02-24 21:30 | 44981.8958 | 0 | 12.2316 | 37.78
2023-02-24 22:00 | 44981.9167 | 0 | 11.6527 | 37.78
2023-02-24 22:30 | 44981.9375 | 0 | 10.9765 | 37.78
2023-02-24 23:00 | 44981.9583 | 0 | 10.479 | 37.78
2023-02-24 23:30 | 44981.9792 | 0 | 9.9967 | 37.78
2023-02-25 | 44982 | 0 | 9.6952 | 37.78
2023-02-25 00:30 | 44982.0208 | 0 | 9.2712 | 37.78
2023-02-25 01:00 | 44982.0417 | 0 | 9.1702 | 37.78
2023-02-25 01:30 | 44982.0625 | 0 | 8.9359 | 37.78
2023-02-25 02:00 | 44982.0833 | 0 | 8.818 | 37.78
2023-02-25 02:30 | 44982.1042 | 0 | 8.7289 | 37.78
2023-02-25 03:00 | 44982.125 | 0 | 8.5277 | 37.78
2023-02-25 03:30 | 44982.1458 | 0 | 8.7589 | 37.78
2023-02-25 04:00 | 44982.1667 | 0 | 8.73 | 37.78
2023-02-25 04:30 | 44982.1875 | 0 | 8.5828 | 37.78
2023-02-25 05:00 | 44982.2083 | 0 | 8.5728 | 37.78
2023-02-25 05:30 | 44982.2292 | 0 | 8.8826 | 37.78
2023-02-25 06:00 | 44982.25 | 0 | 8.8458 | 37.78
2023-02-25 06:30 | 44982.2708 | 0 | 9.1707 | 37.78
2023-02-25 07:00 | 44982.2917 | 0 | 8.5549 | 37.78
2023-02-25 07:30 | 44982.3125 | 0 | 7.879 | 37.78
2023-02-25 08:00 | 44982.3333 | 0 | 8.1803 | 37.78
2023-02-25 08:30 | 44982.3542 | 0 | 7.8528 | 37.78
2023-02-25 09:00 | 44982.375 | 0 | 7.5384 | 37.78
2023-02-25 09:30 | 44982.3958 | 0 | 7.4772 | 37.78
2023-02-25 10:00 | 44982.4167 | 0 | 7.2408 | 37.78
2023-02-25 10:30 | 44982.4375 | 0 | 7.2701 | 37.78
2023-02-25 11:00 | 44982.4583 | 0 | 8.3902 | 37.78
2023-02-25 11:30 | 44982.4792 | 0 | 8.709 | 37.78
2023-02-25 12:00 | 44982.5 | 0 | 8.7406 | 37.78
2023-02-25 12:30 | 44982.5208 | 0 | 8.9566 | 37.78
2023-02-25 13:00 | 44982.5417 | 0 | 7.625 | 37.78
2023-02-25 13:30 | 44982.5625 | 0 | 8.448 | 37.78
2023-02-25 14:00 | 44982.5833 | 0 | 8.9074 | 37.78
2023-02-25 14:30 | 44982.6042 | 0 | 9.5564 | 37.78
2023-02-25 15:00 | 44982.625 | 0 | 9.813 | 37.78
2023-02-25 15:30 | 44982.6458 | 0 | 10.6069 | 37.78
2023-02-25 16:00 | 44982.6667 | 0 | 11.1438 | 37.78
2023-02-25 16:30 | 44982.6875 | 0 | 11.8517 | 37.78
2023-02-25 17:00 | 44982.7083 | 0 | 12.636 | 37.78
2023-02-25 17:30 | 44982.7292 | 0 | 12.9235 | 37.78
2023-02-25 18:00 | 44982.75 | 0 | 12.9708 | 37.78
2023-02-25 18:30 | 44982.7708 | 0 | 13.1178 | 37.78
2023-02-25 19:00 | 44982.7917 | 0 | 12.9697 | 37.78
2023-02-25 19:30 | 44982.8125 | 0 | 12.6516 | 37.78
2023-02-25 20:00 | 44982.8333 | 0 | 12.6693 | 37.78
2023-02-25 20:30 | 44982.8542 | 0 | 12.5461 | 37.78
2023-02-25 21:00 | 44982.875 | 0 | 11.9515 | 37.78
2023-02-25 21:30 | 44982.8958 | 0 | 11.4227 | 37.78
2023-02-25 22:00 | 44982.9167 | 0 | 11.07 | 37.78
2023-02-25 22:30 | 44982.9375 | 0 | 10.5007 | 37.78
2023-02-25 23:00 | 44982.9583 | 0 | 9.9397 | 37.78
2023-02-25 23:30 | 44982.9792 | 0 | 9.4814 | 37.78
2023-02-26 | 44983 | 0 | 8.9697 | 37.78
2023-02-26 00:30 | 44983.0208 | 0 | 8.6031 | 37.78
2023-02-26 01:00 | 44983.0417 | 0 | 8.5333 | 37.78
2023-02-26 01:30 | 44983.0625 | 0 | 8.4531 | 37.78
2023-02-26 02:00 | 44983.0833 | 0 | 8.2002 | 37.78
2023-02-26 02:30 | 44983.1042 | 0 | 8.2707 | 37.78
2023-02-26 03:00 | 44983.125 | 0 | 8.1609 | 37.78
2023-02-26 03:30 | 44983.1458 | 0 | 8.1492 | 37.78
2023-02-26 04:00 | 44983.1667 | 0 | 8.1803 | 37.78
2023-02-26 04:30 | 44983.1875 | 0 | 8.195 | 37.78
2023-02-26 05:00 | 44983.2083 | 0 | 8.1961 | 37.78
2023-02-26 05:30 | 44983.2292 | 0 | 8.2919 | 37.78
2023-02-26 06:00 | 44983.25 | 0 | 8.1613 | 37.78
2023-02-26 06:30 | 44983.2708 | 0 | 7.7813 | 37.78
2023-02-26 07:00 | 44983.2917 | 0 | 7.4289 | 37.78
2023-02-26 07:30 | 44983.3125 | 0 | 7.138 | 37.78
2023-02-26 08:00 | 44983.3333 | 0 | 7.1643 | 37.78
2023-02-26 08:30 | 44983.3542 | 0 | 7.0232 | 37.78
2023-02-26 09:00 | 44983.375 | 0 | 7.6077 | 37.78
2023-02-26 09:30 | 44983.3958 | 0 | 8.1347 | 37.78
2023-02-26 10:00 | 44983.4167 | 0 | 7.945 | 37.78
2023-02-26 10:30 | 44983.4375 | 0 | 7.4 | 37.78
2023-02-26 11:00 | 44983.4583 | 0 | 6.989 | 37.78
2023-02-26 11:30 | 44983.4792 | 0 | 7.2386 | 37.78
2023-02-26 12:00 | 44983.5 | 0 | 7.6143 | 37.78
2023-02-26 12:30 | 44983.5208 | 0 | 7.896 | 37.78
2023-02-26 13:00 | 44983.5417 | 0 | 8.3917 | 37.78
2023-02-26 13:30 | 44983.5625 | 0 | 8.6494 | 37.78
2023-02-26 14:00 | 44983.5833 | 0 | 9.4131 | 37.78
2023-02-26 14:30 | 44983.6042 | 0 | 10.273 | 37.78
2023-02-26 15:00 | 44983.625 | 0 | 11.4417 | 37.78
2023-02-26 15:30 | 44983.6458 | 0 | 11.5482 | 37.78
2023-02-26 16:00 | 44983.6667 | 0 | 13.0112 | 37.78
2023-02-26 16:30 | 44983.6875 | 0 | 14.4583 | 37.78
2023-02-26 17:00 | 44983.7083 | 0 | 14.8172 | 37.78
2023-02-26 17:30 | 44983.7292 | 0 | 15.1196 | 37.78
2023-02-26 18:00 | 44983.75 | 0 | 15.2636 | 37.78
2023-02-26 18:30 | 44983.7708 | 0 | 15.4308 | 37.78
2023-02-26 19:00 | 44983.7917 | 0 | 15.3558 | 37.78
2023-02-26 19:30 | 44983.8125 | 0 | 14.8936 | 37.78
2023-02-26 20:00 | 44983.8333 | 0 | 14.7412 | 37.78
2023-02-26 20:30 | 44983.8542 | 0 | 14.0138 | 37.78
2023-02-26 21:00 | 44983.875 | 0 | 13.4484 | 37.78
2023-02-26 21:30 | 44983.8958 | 0 | 12.7879 | 37.78
2023-02-26 22:00 | 44983.9167 | 0 | 12.1298 | 37.78
2023-02-26 22:30 | 44983.9375 | 0 | 11.3341 | 37.78
2023-02-26 23:00 | 44983.9583 | 0 | 10.6575 | 37.78
2023-02-26 23:30 | 44983.9792 | 0 | 10.1439 | 37.78
2023-02-27 | 44984 | 0 | 9.962 | 37.78
2023-02-27 00:30 | 44984.0208 | 0 | 9.5832 | 37.78
2023-02-27 01:00 | 44984.0417 | 0 | 9.4176 | 37.78
2023-02-27 01:30 | 44984.0625 | 0 | 9.2498 | 37.78
2023-02-27 02:00 | 44984.0833 | 0 | 9.1032 | 37.78
2023-02-27 02:30 | 44984.1042 | 0 | 9.3361 | 37.78
2023-02-27 03:00 | 44984.125 | 0 | 8.8884 | 37.78
2023-02-27 03:30 | 44984.1458 | 0 | 9.4651 | 37.78
2023-02-27 04:00 | 44984.1667 | 0 | 9.7263 | 37.78
2023-02-27 04:30 | 44984.1875 | 0 | 9.9693 | 37.78
2023-02-27 05:00 | 44984.2083 | 0 | 10.6171 | 37.78
2023-02-27 05:30 | 44984.2292 | 0 | 11.1633 | 37.78
2023-02-27 06:00 | 44984.25 | 0 | 11.921 | 37.78
2023-02-27 06:30 | 44984.2708 | 0 | 12.105 | 37.78
2023-02-27 07:00 | 44984.2917 | 0 | 12.5707 | 37.78
2023-02-27 07:30 | 44984.3125 | 0 | 12.1059 | 37.78
2023-02-27 08:00 | 44984.3333 | 0 | 12.3995 | 37.78
2023-02-27 08:30 | 44984.3542 | 0 | 13.3054 | 37.78
2023-02-27 09:00 | 44984.375 | 0 | 13.0321 | 37.78
2023-02-27 09:30 | 44984.3958 | 0 | 13.2147 | 37.78
2023-02-27 10:00 | 44984.4167 | 0 | 13.4264 | 37.78
2023-02-27 10:30 | 44984.4375 | 0 | 12.9179 | 37.78
2023-02-27 11:00 | 44984.4583 | 0 | 12.6269 | 37.78
2023-02-27 11:30 | 44984.4792 | 0 | 13.2861 | 37.78
2023-02-27 12:00 | 44984.5 | 0 | 13.2265 | 37.78
2023-02-27 12:30 | 44984.5208 | 0 | 13.2318 | 37.78
2023-02-27 13:00 | 44984.5417 | 0 | 13.7258 | 37.78
2023-02-27 13:30 | 44984.5625 | 0 | 14.2642 | 37.78
2023-02-27 14:00 | 44984.5833 | 0 | 14.8871 | 37.78
2023-02-27 14:30 | 44984.6042 | 0 | 15.3454 | 37.78
2023-02-27 15:00 | 44984.625 | 0 | 15.8588 | 37.78
2023-02-27 15:30 | 44984.6458 | 0 | 16.6541 | 37.78
2023-02-27 16:00 | 44984.6667 | 0 | 17.6481 | 37.78
2023-02-27 16:30 | 44984.6875 | 0 | 18.1538 | 37.78
2023-02-27 17:00 | 44984.7083 | 0 | 18.1754 | 37.78
2023-02-27 17:30 | 44984.7292 | 0 | 18.3438 | 37.78
2023-02-27 18:00 | 44984.75 | 0 | 18.4587 | 37.78
2023-02-27 18:30 | 44984.7708 | 0 | 18.8322 | 37.78
2023-02-27 19:00 | 44984.7917 | 0 | 18.5277 | 37.78
2023-02-27 19:30 | 44984.8125 | 0 | 18.1146 | 37.78
2023-02-27 20:00 | 44984.8333 | 0 | 17.5134 | 37.78
2023-02-27 20:30 | 44984.8542 | 0 | 16.7262 | 37.78
2023-02-27 21:00 | 44984.875 | 0 | 16.1001 | 37.78
2023-02-27 21:30 | 44984.8958 | 0 | 15.1691 | 37.78
2023-02-27 22:00 | 44984.9167 | 0 | 14.365 | 37.78
2023-02-27 22:30 | 44984.9375 | 0 | 13.5616 | 37.78
2023-02-27 23:00 | 44984.9583 | 0 | 12.8343 | 37.78
2023-02-27 23:30 | 44984.9792 | 0 | 12.1201 | 37.78
2023-02-28 | 44985 | 0 | 11.8366 | 37.78
2023-02-28 00:30 | 44985.0208 | 0 | 11.3052 | 37.78
2023-02-28 01:00 | 44985.0417 | 0 | 11.1034 | 37.78
2023-02-28 01:30 | 44985.0625 | 0 | 10.7911 | 37.78
2023-02-28 02:00 | 44985.0833 | 0 | 10.7534 | 37.78
2023-02-28 02:30 | 44985.1042 | 0 | 10.5942 | 37.78
2023-02-28 03:00 | 44985.125 | 0 | 10.4708 | 37.78
2023-02-28 03:30 | 44985.1458 | 0 | 10.5464 | 37.78
2023-02-28 04:00 | 44985.1667 | 0 | 10.7264 | 37.78
2023-02-28 04:30 | 44985.1875 | 0 | 10.9497 | 37.78
2023-02-28 05:00 | 44985.2083 | 0 | 11.6912 | 37.78
2023-02-28 05:30 | 44985.2292 | 0 | 12.0207 | 37.78
2023-02-28 06:00 | 44985.25 | 0 | 12.934 | 37.78
2023-02-28 06:30 | 44985.2708 | 0 | 13.3892 | 37.78
2023-02-28 07:00 | 44985.2917 | 0 | 13.8394 | 37.78
2023-02-28 07:30 | 44985.3125 | 0 | 13.5981 | 37.78
2023-02-28 08:00 | 44985.3333 | 0 | 14.4467 | 37.78
2023-02-28 08:30 | 44985.3542 | 0 | 13.7805 | 37.78
2023-02-28 09:00 | 44985.375 | 0 | 13.5366 | 37.78
2023-02-28 09:30 | 44985.3958 | 0 | 13.593 | 37.78
2023-02-28 10:00 | 44985.4167 | 0 | 14.8326 | 37.78
2023-02-28 10:30 | 44985.4375 | 0 | 13.9948 | 37.78
2023-02-28 11:00 | 44985.4583 | 0 | 13.7439 | 37.78
2023-02-28 11:30 | 44985.4792 | 0 | 13.5632 | 37.78
2023-02-28 12:00 | 44985.5 | 0 | 13.9694 | 37.78
2023-02-28 12:30 | 44985.5208 | 0 | 13.9396 | 37.78
2023-02-28 13:00 | 44985.5417 | 0 | 14.3734 | 37.78
2023-02-28 13:30 | 44985.5625 | 0 | 14.7724 | 37.78
2023-02-28 14:00 | 44985.5833 | 0 | 15.3329 | 37.78
2023-02-28 14:30 | 44985.6042 | 0 | 15.9889 | 37.78
2023-02-28 15:00 | 44985.625 | 0 | 16.5324 | 37.78
2023-02-28 15:30 | 44985.6458 | 0 | 17.9463 | 37.78
2023-02-28 16:00 | 44985.6667 | 0 | 17.9719 | 37.78
2023-02-28 16:30 | 44985.6875 | 0 | 19.3974 | 37.78
2023-02-28 17:00 | 44985.7083 | 0 | 18.4929 | 37.78
2023-02-28 17:30 | 44985.7292 | 0 | 17.8045 | 37.78
2023-02-28 18:00 | 44985.75 | 0 | 17.7416 | 37.78
2023-02-28 18:30 | 44985.7708 | 0 | 17.8931 | 37.78
2023-02-28 19:00 | 44985.7917 | 0 | 17.7561 | 37.78
2023-02-28 19:30 | 44985.8125 | 0 | 17.2799 | 37.78
2023-02-28 20:00 | 44985.8333 | 0 | 17.0108 | 37.78
2023-02-28 20:30 | 44985.8542 | 0 | 16.1825 | 37.78
2023-02-28 21:00 | 44985.875 | 0 | 15.5745 | 37.78
2023-02-28 21:30 | 44985.8958 | 0 | 14.7768 | 37.78
2023-02-28 22:00 | 44985.9167 | 0 | 14.0301 | 37.78
2023-02-28 22:30 | 44985.9375 | 0 | 13.1183 | 37.78
2023-02-28 23:00 | 44985.9583 | 0 | 12.3969 | 37.78
2023-02-28 23:30 | 44985.9792 | 0 | 11.815 | 37.78
2023-03-01 | 44986 | 0 | 11.2499 | 37.78
2023-03-01 00:30 | 44986.0208 | 0 | 10.7707 | 37.78
2023-03-01 01:00 | 44986.0417 | 0 | 10.5458 | 37.78
2023-03-01 01:30 | 44986.0625 | 0 | 10.324 | 37.78
2023-03-01 02:00 | 44986.0833 | 0 | 10.2793 | 37.78
2023-03-01 02:30 | 44986.1042 | 0 | 9.9777 | 37.78
2023-03-01 03:00 | 44986.125 | 0 | 9.9231 | 37.78
2023-03-01 03:30 | 44986.1458 | 0 | 10.0383 | 37.78
2023-03-01 04:00 | 44986.1667 | 0 | 10.5522 | 37.78
2023-03-01 04:30 | 44986.1875 | 0 | 10.8368 | 37.78
2023-03-01 05:00 | 44986.2083 | 0 | 11.3817 | 37.78
2023-03-01 05:30 | 44986.2292 | 0 | 11.7944 | 37.78
2023-03-01 06:00 | 44986.25 | 0 | 12.0861 | 37.78
2023-03-01 06:30 | 44986.2708 | 0 | 12.381 | 37.78
2023-03-01 07:00 | 44986.2917 | 0 | 12.6263 | 37.78
2023-03-01 07:30 | 44986.3125 | 0 | 12.796 | 37.78
2023-03-01 08:00 | 44986.3333 | 0 | 12.8273 | 37.78
2023-03-01 08:30 | 44986.3542 | 0 | 12.6434 | 37.78
2023-03-01 09:00 | 44986.375 | 0 | 13.2726 | 37.78
2023-03-01 09:30 | 44986.3958 | 0 | 13.0607 | 37.78
2023-03-01 10:00 | 44986.4167 | 0 | 12.9401 | 37.78
2023-03-01 10:30 | 44986.4375 | 0 | 13.0938 | 37.78
2023-03-01 11:00 | 44986.4583 | 0 | 13.4102 | 37.78
2023-03-01 11:30 | 44986.4792 | 0 | 13.6882 | 37.78
2023-03-01 12:00 | 44986.5 | 0 | 14.0283 | 37.78
2023-03-01 12:30 | 44986.5208 | 0 | 14.1474 | 37.78
2023-03-01 13:00 | 44986.5417 | 0 | 14.4159 | 37.78
2023-03-01 13:30 | 44986.5625 | 0 | 14.4157 | 37.78
2023-03-01 14:00 | 44986.5833 | 0 | 15.2428 | 37.78
2023-03-01 14:30 | 44986.6042 | 0 | 15.678 | 37.78
2023-03-01 15:00 | 44986.625 | 0 | 16.395 | 37.78
2023-03-01 15:30 | 44986.6458 | 0 | 17.2971 | 37.78
2023-03-01 16:00 | 44986.6667 | 0 | 18.2433 | 37.78
2023-03-01 16:30 | 44986.6875 | 0 | 18.4961 | 37.78
2023-03-01 17:00 | 44986.7083 | 0 | 18.7291 | 37.78
2023-03-01 17:30 | 44986.7292 | 0 | 18.8019 | 37.78
2023-03-01 18:00 | 44986.75 | 0 | 18.6509 | 37.78
2023-03-01 18:30 | 44986.7708 | 0 | 19.1597 | 37.78
2023-03-01 19:00 | 44986.7917 | 0 | 18.8502 | 37.78
2023-03-01 19:30 | 44986.8125 | 0 | 18.8002 | 37.78
2023-03-01 20:00 | 44986.8333 | 0 | 18.336 | 37.78
2023-03-01 20:30 | 44986.8542 | 0 | 17.8081 | 37.78
2023-03-01 21:00 | 44986.875 | 0 | 17.0724 | 37.78
2023-03-01 21:30 | 44986.8958 | 0 | 16.1508 | 37.78
2023-03-01 22:00 | 44986.9167 | 0 | 15.1338 | 37.78
2023-03-01 22:30 | 44986.9375 | 0 | 14.1301 | 37.78
2023-03-01 23:00 | 44986.9583 | 0 | 13.2866 | 37.78
2023-03-01 23:30 | 44986.9792 | 0 | 12.5537 | 37.78
2023-03-02 | 44987 | 0 | 11.9066 | 37.78
2023-03-02 00:30 | 44987.0208 | 0 | 11.4244 | 37.78
2023-03-02 01:00 | 44987.0417 | 0 | 11.1723 | 37.78
2023-03-02 01:30 | 44987.0625 | 0 | 10.9735 | 37.78
2023-03-02 02:00 | 44987.0833 | 0 | 10.9197 | 37.78
2023-03-02 02:30 | 44987.1042 | 0 | 10.8014 | 37.78
2023-03-02 03:00 | 44987.125 | 0 | 10.6017 | 37.78
2023-03-02 03:30 | 44987.1458 | 0 | 10.8678 | 37.78
2023-03-02 04:00 | 44987.1667 | 0 | 11.2615 | 37.78
2023-03-02 04:30 | 44987.1875 | 0 | 11.6685 | 37.78
2023-03-02 05:00 | 44987.2083 | 0 | 12.3254 | 37.78
2023-03-02 05:30 | 44987.2292 | 0 | 12.7631 | 37.78
2023-03-02 06:00 | 44987.25 | 0 | 13.6809 | 37.78
2023-03-02 06:30 | 44987.2708 | 0 | 14.4617 | 37.78
2023-03-02 07:00 | 44987.2917 | 0 | 15.2993 | 37.78
2023-03-02 07:30 | 44987.3125 | 0 | 16.0503 | 37.78
2023-03-02 08:00 | 44987.3333 | 0 | 16.5381 | 37.78
2023-03-02 08:30 | 44987.3542 | 0 | 16.0337 | 37.78
2023-03-02 09:00 | 44987.375 | 0 | 15.9817 | 37.78
2023-03-02 09:30 | 44987.3958 | 0 | 16.44 | 37.78
2023-03-02 10:00 | 44987.4167 | 0 | 17.0456 | 37.78
2023-03-02 10:30 | 44987.4375 | 0 | 16.7146 | 37.78
2023-03-02 11:00 | 44987.4583 | 0 | 16.3959 | 37.78
2023-03-02 11:30 | 44987.4792 | 0 | 15.9047 | 37.78
2023-03-02 12:00 | 44987.5 | 0 | 13.3238 | 37.78
2023-03-02 12:30 | 44987.5208 | 0 | 13.9989 | 37.78
2023-03-02 13:00 | 44987.5417 | 0 | 13.48 | 37.78
2023-03-02 13:30 | 44987.5625 | 0 | 16.1231 | 37.78
2023-03-02 14:00 | 44987.5833 | 0 | 18.3259 | 37.78
2023-03-02 14:30 | 44987.6042 | 0 | 18.2293 | 37.78
2023-03-02 15:00 | 44987.625 | 0 | 16.0817 | 37.78
2023-03-02 15:30 | 44987.6458 | 0 | 15.466 | 37.78
2023-03-02 16:00 | 44987.6667 | 0 | 16.3768 | 37.78
2023-03-02 16:30 | 44987.6875 | 0 | 15.7497 | 37.78
2023-03-02 17:00 | 44987.7083 | 0 | 16.5314 | 37.78
2023-03-02 17:30 | 44987.7292 | 0 | 17.0819 | 37.78
2023-03-02 18:00 | 44987.75 | 0 | 17.128 | 37.78
2023-03-02 18:30 | 44987.7708 | 0 | 17.5483 | 37.78
2023-03-02 19:00 | 44987.7917 | 0 | 17.3306 | 37.78
2023-03-02 19:30 | 44987.8125 | 0 | 16.9823 | 37.78
2023-03-02 20:00 | 44987.8333 | 0 | 16.7604 | 37.78
2023-03-02 20:30 | 44987.8542 | 0 | 16.1387 | 37.78
2023-03-02 21:00 | 44987.875 | 0 | 15.8797 | 37.78
2023-03-02 21:30 | 44987.8958 | 0 | 15.1916 | 37.78
2023-03-02 22:00 | 44987.9167 | 0 | 13.9325 | 37.78
2023-03-02 22:30 | 44987.9375 | 0 | 13.1562 | 37.78
2023-03-02 23:00 | 44987.9583 | 0 | 12.4729 | 37.78
2023-03-02 23:30 | 44987.9792 | 0 | 11.9245 | 37.78
2023-03-03 | 44988 | 0 | 11.3575 | 37.78
2023-03-03 00:30 | 44988.0208 | 0 | 10.9643 | 37.78
2023-03-03 01:00 | 44988.0417 | 0 | 10.745 | 37.78
2023-03-03 01:30 | 44988.0625 | 0 | 10.4001 | 37.78
2023-03-03 02:00 | 44988.0833 | 0 | 10.2418 | 37.78
2023-03-03 02:30 | 44988.1042 | 0 | 10.0274 | 37.78
2023-03-03 03:00 | 44988.125 | 0 | 9.9782 | 37.78
2023-03-03 03:30 | 44988.1458 | 0 | 10.0086 | 37.78
2023-03-03 04:00 | 44988.1667 | 0 | 10.535 | 37.78
2023-03-03 04:30 | 44988.1875 | 0 | 10.7307 | 37.78
2023-03-03 05:00 | 44988.2083 | 0 | 11.4381 | 37.78
2023-03-03 05:30 | 44988.2292 | 0 | 11.9603 | 37.78
2023-03-03 06:00 | 44988.25 | 0 | 12.7683 | 37.78
2023-03-03 06:30 | 44988.2708 | 0 | 12.8087 | 37.78
2023-03-03 07:00 | 44988.2917 | 0 | 13.2862 | 37.78
2023-03-03 07:30 | 44988.3125 | 0 | 13.6839 | 37.78
2023-03-03 08:00 | 44988.3333 | 0 | 13.4432 | 37.78
2023-03-03 08:30 | 44988.3542 | 0 | 13.7247 | 37.78
2023-03-03 09:00 | 44988.375 | 0 | 14.5135 | 37.78
2023-03-03 09:30 | 44988.3958 | 0 | 14.6378 | 37.78
2023-03-03 10:00 | 44988.4167 | 0 | 15.2078 | 37.78
2023-03-03 10:30 | 44988.4375 | 0 | 12.8502 | 37.78
2023-03-03 11:00 | 44988.4583 | 0 | 15.0877 | 37.78
2023-03-03 11:30 | 44988.4792 | 0 | 14.6172 | 37.78
2023-03-03 12:00 | 44988.5 | 0 | 13.9306 | 37.78
2023-03-03 12:30 | 44988.5208 | 0 | 13.2846 | 37.78
2023-03-03 13:00 | 44988.5417 | 0 | 14.1506 | 37.78
2023-03-03 13:30 | 44988.5625 | 0 | 13.8409 | 37.78
2023-03-03 14:00 | 44988.5833 | 0 | 14.0595 | 37.78
2023-03-03 14:30 | 44988.6042 | 0 | 14.9923 | 37.78
2023-03-03 15:00 | 44988.625 | 0 | 15.5691 | 37.78
2023-03-03 15:30 | 44988.6458 | 0 | 16.1002 | 37.78
2023-03-03 16:00 | 44988.6667 | 0 | 16.3511 | 37.78
2023-03-03 16:30 | 44988.6875 | 0 | 16.426 | 37.78
2023-03-03 17:00 | 44988.7083 | 0 | 16.4657 | 37.78
2023-03-03 17:30 | 44988.7292 | 0 | 16.1973 | 37.78
2023-03-03 18:00 | 44988.75 | 0 | 15.7694 | 37.78
2023-03-03 18:30 | 44988.7708 | 0 | 16.1225 | 37.78
2023-03-03 19:00 | 44988.7917 | 0 | 16.0119 | 37.78
2023-03-03 19:30 | 44988.8125 | 0 | 15.4101 | 37.78
2023-03-03 20:00 | 44988.8333 | 0 | 15.2398 | 37.78
2023-03-03 20:30 | 44988.8542 | 0 | 14.7422 | 37.78
2023-03-03 21:00 | 44988.875 | 0 | 14.3708 | 37.78
2023-03-03 21:30 | 44988.8958 | 0 | 13.8783 | 37.78
2023-03-03 22:00 | 44988.9167 | 0 | 13.2725 | 37.78
2023-03-03 22:30 | 44988.9375 | 0 | 12.5443 | 37.78
2023-03-03 23:00 | 44988.9583 | 0 | 12.0188 | 37.78
2023-03-03 23:30 | 44988.9792 | 0 | 11.1814 | 37.78
2023-03-04 | 44989 | 0 | 10.8174 | 37.78
2023-03-04 00:30 | 44989.0208 | 0 | 10.2578 | 37.78
2023-03-04 01:00 | 44989.0417 | 0 | 10.0156 | 37.78
2023-03-04 01:30 | 44989.0625 | 0 | 9.7568 | 37.78
2023-03-04 02:00 | 44989.0833 | 0 | 9.6016 | 37.78
2023-03-04 02:30 | 44989.1042 | 0 | 9.6457 | 37.78
2023-03-04 03:00 | 44989.125 | 0 | 9.4984 | 37.78
2023-03-04 03:30 | 44989.1458 | 0 | 9.3042 | 37.78
2023-03-04 04:00 | 44989.1667 | 0 | 9.3512 | 37.78
2023-03-04 04:30 | 44989.1875 | 0 | 9.2935 | 37.78
2023-03-04 05:00 | 44989.2083 | 0 | 9.5967 | 37.78
2023-03-04 05:30 | 44989.2292 | 0 | 9.5563 | 37.78
2023-03-04 06:00 | 44989.25 | 0 | 9.4048 | 37.78
2023-03-04 06:30 | 44989.2708 | 0 | 9.2051 | 37.78
2023-03-04 07:00 | 44989.2917 | 0 | 8.9905 | 37.78
2023-03-04 07:30 | 44989.3125 | 0 | 8.8136 | 37.78
2023-03-04 08:00 | 44989.3333 | 0 | 8.768 | 37.78
2023-03-04 08:30 | 44989.3542 | 0 | 8.6857 | 37.78
2023-03-04 09:00 | 44989.375 | 0 | 9.8358 | 37.78
2023-03-04 09:30 | 44989.3958 | 0 | 11.4389 | 37.78
2023-03-04 10:00 | 44989.4167 | 0 | 10.4256 | 37.78
2023-03-04 10:30 | 44989.4375 | 0 | 9.8724 | 37.78
2023-03-04 11:00 | 44989.4583 | 0 | 11.1073 | 37.78
2023-03-04 11:30 | 44989.4792 | 0 | 11.2597 | 37.78
2023-03-04 12:00 | 44989.5 | 0 | 8.4973 | 37.78
2023-03-04 12:30 | 44989.5208 | 0 | 10.8666 | 37.78
2023-03-04 13:00 | 44989.5417 | 0 | 9.4473 | 37.78
2023-03-04 13:30 | 44989.5625 | 0 | 10.4965 | 37.78
2023-03-04 14:00 | 44989.5833 | 0 | 10.5003 | 37.78
2023-03-04 14:30 | 44989.6042 | 0 | 9.4067 | 37.78
2023-03-04 15:00 | 44989.625 | 0 | 10.5387 | 37.78
2023-03-04 15:30 | 44989.6458 | 0 | 11.4681 | 37.78
2023-03-04 16:00 | 44989.6667 | 0 | 12.0024 | 37.78
2023-03-04 16:30 | 44989.6875 | 0 | 12.8169 | 37.78
2023-03-04 17:00 | 44989.7083 | 0 | 13.3093 | 37.78
2023-03-04 17:30 | 44989.7292 | 0 | 13.6415 | 37.78
2023-03-04 18:00 | 44989.75 | 0 | 13.6493 | 37.78
2023-03-04 18:30 | 44989.7708 | 0 | 13.7804 | 37.78
2023-03-04 19:00 | 44989.7917 | 0 | 13.6171 | 37.78
2023-03-04 19:30 | 44989.8125 | 0 | 13.1998 | 37.78
2023-03-04 20:00 | 44989.8333 | 0 | 12.9675 | 37.78
2023-03-04 20:30 | 44989.8542 | 0 | 12.6561 | 37.78
2023-03-04 21:00 | 44989.875 | 0 | 12.3983 | 37.78
2023-03-04 21:30 | 44989.8958 | 0 | 11.8523 | 37.78
2023-03-04 22:00 | 44989.9167 | 0 | 11.259 | 37.78
2023-03-04 22:30 | 44989.9375 | 0 | 10.6195 | 37.78
2023-03-04 23:00 | 44989.9583 | 0 | 10.3064 | 37.78
2023-03-04 23:30 | 44989.9792 | 0 | 9.7947 | 37.78
2023-03-05 | 44990 | 0 | 9.3057 | 37.78
2023-03-05 00:30 | 44990.0208 | 0 | 8.8564 | 37.78
2023-03-05 01:00 | 44990.0417 | 0 | 8.6766 | 37.78
2023-03-05 01:30 | 44990.0625 | 0 | 8.4064 | 37.78
2023-03-05 02:00 | 44990.0833 | 0 | 8.4174 | 37.78
2023-03-05 02:30 | 44990.1042 | 0 | 8.3321 | 37.78
2023-03-05 03:00 | 44990.125 | 0 | 8.3234 | 37.78
2023-03-05 03:30 | 44990.1458 | 0 | 8.3314 | 37.78
2023-03-05 04:00 | 44990.1667 | 0 | 8.326 | 37.78
2023-03-05 04:30 | 44990.1875 | 0 | 8.2651 | 37.78
2023-03-05 05:00 | 44990.2083 | 0 | 8.3545 | 37.78
2023-03-05 05:30 | 44990.2292 | 0 | 8.3706 | 37.78
2023-03-05 06:00 | 44990.25 | 0 | 8.3083 | 37.78
2023-03-05 06:30 | 44990.2708 | 0 | 8.0003 | 37.78
2023-03-05 07:00 | 44990.2917 | 0 | 7.8375 | 37.78
2023-03-05 07:30 | 44990.3125 | 0 | 7.4095 | 37.78
2023-03-05 08:00 | 44990.3333 | 0 | 7.3943 | 37.78
2023-03-05 08:30 | 44990.3542 | 0 | 7.1792 | 37.78
2023-03-05 09:00 | 44990.375 | 0 | 7.877 | 37.78
2023-03-05 09:30 | 44990.3958 | 0 | 8.6497 | 37.78
2023-03-05 10:00 | 44990.4167 | 0 | 8.963 | 37.78
2023-03-05 10:30 | 44990.4375 | 0 | 8.8028 | 37.78
2023-03-05 11:00 | 44990.4583 | 0 | 8.0839 | 37.78
2023-03-05 11:30 | 44990.4792 | 0 | 7.5685 | 37.78
2023-03-05 12:00 | 44990.5 | 0 | 7.609 | 37.78
2023-03-05 12:30 | 44990.5208 | 0 | 8.1048 | 37.78
2023-03-05 13:00 | 44990.5417 | 0 | 10.0699 | 37.78
2023-03-05 13:30 | 44990.5625 | 0 | 9.0952 | 37.78
2023-03-05 14:00 | 44990.5833 | 0 | 9.3298 | 37.78
2023-03-05 14:30 | 44990.6042 | 0 | 9.9435 | 37.78
2023-03-05 15:00 | 44990.625 | 0 | 10.8679 | 37.78
2023-03-05 15:30 | 44990.6458 | 0 | 11.9649 | 37.78
2023-03-05 16:00 | 44990.6667 | 0 | 12.8336 | 37.78
2023-03-05 16:30 | 44990.6875 | 0 | 13.918 | 37.78
2023-03-05 17:00 | 44990.7083 | 0 | 14.719 | 37.78
2023-03-05 17:30 | 44990.7292 | 0 | 15.2292 | 37.78
2023-03-05 18:00 | 44990.75 | 0 | 15.0446 | 37.78
2023-03-05 18:30 | 44990.7708 | 0 | 15.4548 | 37.78
2023-03-05 19:00 | 44990.7917 | 0 | 15.4132 | 37.78
2023-03-05 19:30 | 44990.8125 | 0 | 14.9028 | 37.78
2023-03-05 20:00 | 44990.8333 | 0 | 14.471 | 37.78
2023-03-05 20:30 | 44990.8542 | 0 | 14.0359 | 37.78
2023-03-05 21:00 | 44990.875 | 0 | 13.3445 | 37.78
2023-03-05 21:30 | 44990.8958 | 0 | 12.5048 | 37.78
2023-03-05 22:00 | 44990.9167 | 0 | 11.7219 | 37.78
2023-03-05 22:30 | 44990.9375 | 0 | 11.0471 | 37.78
2023-03-05 23:00 | 44990.9583 | 0 | 10.5354 | 37.78
2023-03-05 23:30 | 44990.9792 | 0 | 10.0281 | 37.78
2023-03-06 | 44991 | 0 | 9.6858 | 37.78
2023-03-06 00:30 | 44991.0208 | 0 | 9.4539 | 37.78
2023-03-06 01:00 | 44991.0417 | 0 | 9.22 | 37.78
2023-03-06 01:30 | 44991.0625 | 0 | 9.2003 | 37.78
2023-03-06 02:00 | 44991.0833 | 0 | 9.386 | 37.78
2023-03-06 02:30 | 44991.1042 | 0 | 9.4916 | 37.78
2023-03-06 03:00 | 44991.125 | 0 | 9.3466 | 37.78
2023-03-06 03:30 | 44991.1458 | 0 | 9.3873 | 37.78
2023-03-06 04:00 | 44991.1667 | 0 | 9.6684 | 37.78
2023-03-06 04:30 | 44991.1875 | 0 | 9.8583 | 37.78
2023-03-06 05:00 | 44991.2083 | 0 | 10.5137 | 37.78
2023-03-06 05:30 | 44991.2292 | 0 | 11.0173 | 37.78
2023-03-06 06:00 | 44991.25 | 0 | 11.8675 | 37.78
2023-03-06 06:30 | 44991.2708 | 0 | 12.3072 | 37.78
2023-03-06 07:00 | 44991.2917 | 0 | 12.5523 | 37.78
2023-03-06 07:30 | 44991.3125 | 0 | 12.2388 | 37.78
2023-03-06 08:00 | 44991.3333 | 0 | 12.4471 | 37.78
2023-03-06 08:30 | 44991.3542 | 0 | 13.2963 | 37.78
2023-03-06 09:00 | 44991.375 | 0 | 13.4508 | 37.78
2023-03-06 09:30 | 44991.3958 | 0 | 12.9232 | 37.78
2023-03-06 10:00 | 44991.4167 | 0 | 11.9141 | 37.78
2023-03-06 10:30 | 44991.4375 | 0 | 12.1037 | 37.78
2023-03-06 11:00 | 44991.4583 | 0 | 11.7937 | 37.78
2023-03-06 11:30 | 44991.4792 | 0 | 12.2619 | 37.78
2023-03-06 12:00 | 44991.5 | 0 | 12.5394 | 37.78
2023-03-06 12:30 | 44991.5208 | 0 | 12.9086 | 37.78
2023-03-06 13:00 | 44991.5417 | 0 | 13.4523 | 37.78
2023-03-06 13:30 | 44991.5625 | 0 | 14.0905 | 37.78
2023-03-06 14:00 | 44991.5833 | 0 | 14.5833 | 37.78
2023-03-06 14:30 | 44991.6042 | 0 | 15.0046 | 37.78
2023-03-06 15:00 | 44991.625 | 0 | 15.3876 | 37.78
2023-03-06 15:30 | 44991.6458 | 0 | 16.2133 | 37.78
2023-03-06 16:00 | 44991.6667 | 0 | 16.8976 | 37.78
2023-03-06 16:30 | 44991.6875 | 0 | 17.5786 | 37.78
2023-03-06 17:00 | 44991.7083 | 0 | 18.0161 | 37.78
2023-03-06 17:30 | 44991.7292 | 0 | 18.2949 | 37.78
2023-03-06 18:00 | 44991.75 | 0 | 18.017 | 37.78
2023-03-06 18:30 | 44991.7708 | 0 | 18.4034 | 37.78
2023-03-06 19:00 | 44991.7917 | 0 | 17.9755 | 37.78
2023-03-06 19:30 | 44991.8125 | 0 | 17.3056 | 37.78
2023-03-06 20:00 | 44991.8333 | 0 | 17.036 | 37.78
2023-03-06 20:30 | 44991.8542 | 0 | 16.3861 | 37.78
2023-03-06 21:00 | 44991.875 | 0 | 15.7959 | 37.78
2023-03-06 21:30 | 44991.8958 | 0 | 14.9265 | 37.78
2023-03-06 22:00 | 44991.9167 | 0 | 13.87 | 37.78
2023-03-06 22:30 | 44991.9375 | 0 | 13.1563 | 37.78
2023-03-06 23:00 | 44991.9583 | 0 | 12.3819 | 37.78
2023-03-06 23:30 | 44991.9792 | 0 | 11.7967 | 37.78
2023-03-07 | 44992 | 0 | 11.2882 | 37.78
2023-03-07 00:30 | 44992.0208 | 0 | 10.8723 | 37.78
2023-03-07 01:00 | 44992.0417 | 0 | 10.4931 | 37.78
2023-03-07 01:30 | 44992.0625 | 0 | 10.2526 | 37.78
2023-03-07 02:00 | 44992.0833 | 0 | 10.1495 | 37.78
2023-03-07 02:30 | 44992.1042 | 0 | 9.9699 | 37.78
2023-03-07 03:00 | 44992.125 | 0 | 9.8608 | 37.78
2023-03-07 03:30 | 44992.1458 | 0 | 10.0744 | 37.78
2023-03-07 04:00 | 44992.1667 | 0 | 10.2105 | 37.78
2023-03-07 04:30 | 44992.1875 | 0 | 10.5778 | 37.78
2023-03-07 05:00 | 44992.2083 | 0 | 10.9717 | 37.78
2023-03-07 05:30 | 44992.2292 | 0 | 11.5447 | 37.78
2023-03-07 06:00 | 44992.25 | 0 | 12.252 | 37.78
2023-03-07 06:30 | 44992.2708 | 0 | 12.564 | 37.78
2023-03-07 07:00 | 44992.2917 | 0 | 13.0927 | 37.78
2023-03-07 07:30 | 44992.3125 | 0 | 12.6873 | 37.78
2023-03-07 08:00 | 44992.3333 | 0 | 12.9624 | 37.78
2023-03-07 08:30 | 44992.3542 | 0 | 12.9862 | 37.78
2023-03-07 09:00 | 44992.375 | 0 | 13.1345 | 37.78
2023-03-07 09:30 | 44992.3958 | 0 | 13.037 | 37.78
2023-03-07 10:00 | 44992.4167 | 0 | 12.8578 | 37.78
2023-03-07 10:30 | 44992.4375 | 0 | 12.8785 | 37.78
2023-03-07 11:00 | 44992.4583 | 0 | 13.3853 | 37.78
2023-03-07 11:30 | 44992.4792 | 0 | 14.0246 | 37.78
2023-03-07 12:00 | 44992.5 | 0 | 13.9787 | 37.78
2023-03-07 12:30 | 44992.5208 | 0 | 14.8965 | 37.78
2023-03-07 13:00 | 44992.5417 | 0 | 15.6851 | 37.78
2023-03-07 13:30 | 44992.5625 | 0 | 15.1917 | 37.78
2023-03-07 14:00 | 44992.5833 | 0 | 16.072 | 37.78
2023-03-07 14:30 | 44992.6042 | 0 | 17.153 | 37.78
2023-03-07 15:00 | 44992.625 | 0 | 17.6745 | 37.78
2023-03-07 15:30 | 44992.6458 | 0 | 18.5291 | 37.78
2023-03-07 16:00 | 44992.6667 | 0 | 19.419 | 37.78
2023-03-07 16:30 | 44992.6875 | 0 | 19.3419 | 37.78
2023-03-07 17:00 | 44992.7083 | 0 | 18.9843 | 37.78
2023-03-07 17:30 | 44992.7292 | 0 | 18.7792 | 37.78
2023-03-07 18:00 | 44992.75 | 0 | 19.0306 | 37.78
2023-03-07 18:30 | 44992.7708 | 0 | 19.3235 | 37.78
2023-03-07 19:00 | 44992.7917 | 0 | 19.2788 | 37.78
2023-03-07 19:30 | 44992.8125 | 0 | 18.9647 | 37.78
2023-03-07 20:00 | 44992.8333 | 0 | 18.4743 | 37.78
2023-03-07 20:30 | 44992.8542 | 0 | 18.0943 | 37.78
2023-03-07 21:00 | 44992.875 | 0 | 17.5434 | 37.78
2023-03-07 21:30 | 44992.8958 | 0 | 16.7416 | 37.78
2023-03-07 22:00 | 44992.9167 | 0 | 15.782 | 37.78
2023-03-07 22:30 | 44992.9375 | 0 | 14.669 | 37.78
2023-03-07 23:00 | 44992.9583 | 0 | 13.9482 | 37.78
2023-03-07 23:30 | 44992.9792 | 0 | 13.4195 | 37.78
2023-03-08 | 44993 | 0 | 12.7235 | 37.78
2023-03-08 00:30 | 44993.0208 | 0 | 12.0484 | 37.78
2023-03-08 01:00 | 44993.0417 | 0 | 11.9478 | 37.78
2023-03-08 01:30 | 44993.0625 | 0 | 11.715 | 37.78
2023-03-08 02:00 | 44993.0833 | 0 | 11.5608 | 37.78
2023-03-08 02:30 | 44993.1042 | 0 | 11.2681 | 37.78
2023-03-08 03:00 | 44993.125 | 0 | 11.1855 | 37.78
2023-03-08 03:30 | 44993.1458 | 0 | 11.2676 | 37.78
2023-03-08 04:00 | 44993.1667 | 0 | 11.4782 | 37.78
2023-03-08 04:30 | 44993.1875 | 0 | 11.8884 | 37.78
2023-03-08 05:00 | 44993.2083 | 0 | 12.3259 | 37.78
2023-03-08 05:30 | 44993.2292 | 0 | 12.9028 | 37.78
2023-03-08 06:00 | 44993.25 | 0 | 13.7009 | 37.78
2023-03-08 06:30 | 44993.2708 | 0 | 14.3178 | 37.78
2023-03-08 07:00 | 44993.2917 | 0 | 14.9288 | 37.78
2023-03-08 07:30 | 44993.3125 | 0 | 15.2543 | 37.78
2023-03-08 08:00 | 44993.3333 | 0 | 15.2341 | 37.78
2023-03-08 08:30 | 44993.3542 | 0 | 15.8483 | 37.78
2023-03-08 09:00 | 44993.375 | 0 | 16.0213 | 37.78
2023-03-08 09:30 | 44993.3958 | 0 | 15.4455 | 37.78
2023-03-08 10:00 | 44993.4167 | 0 | 16.8972 | 37.78
2023-03-08 10:30 | 44993.4375 | 0 | 17.5171 | 37.78
2023-03-08 11:00 | 44993.4583 | 0 | 17.4965 | 37.78
2023-03-08 11:30 | 44993.4792 | 0 | 16.9213 | 37.78
2023-03-08 12:00 | 44993.5 | 0 | 16.0767 | 37.78
2023-03-08 12:30 | 44993.5208 | 0 | 17.5672 | 37.78
2023-03-08 13:00 | 44993.5417 | 0 | 18.0712 | 37.78
2023-03-08 13:30 | 44993.5625 | 0 | 16.9282 | 37.78
2023-03-08 14:00 | 44993.5833 | 0 | 18.5648 | 37.78
2023-03-08 14:30 | 44993.6042 | 0 | 18.9192 | 37.78
2023-03-08 15:00 | 44993.625 | 0 | 18.292 | 37.78
2023-03-08 15:30 | 44993.6458 | 0 | 19.634 | 37.78
2023-03-08 16:00 | 44993.6667 | 0 | 19.5302 | 37.78
2023-03-08 16:30 | 44993.6875 | 0 | 19.7438 | 37.78
2023-03-08 17:00 | 44993.7083 | 0 | 19.4553 | 37.78
2023-03-08 17:30 | 44993.7292 | 0 | 19.5989 | 37.78
2023-03-08 18:00 | 44993.75 | 0 | 19.5875 | 37.78
2023-03-08 18:30 | 44993.7708 | 0 | 20.1565 | 37.78
2023-03-08 19:00 | 44993.7917 | 0 | 19.9106 | 37.78
2023-03-08 19:30 | 44993.8125 | 0 | 19.6991 | 37.78
2023-03-08 20:00 | 44993.8333 | 0 | 19.1687 | 37.78
2023-03-08 20:30 | 44993.8542 | 0 | 18.5719 | 37.78
2023-03-08 21:00 | 44993.875 | 0 | 17.92 | 37.78
2023-03-08 21:30 | 44993.8958 | 0 | 16.9913 | 37.78
2023-03-08 22:00 | 44993.9167 | 0 | 15.8251 | 37.78
2023-03-08 22:30 | 44993.9375 | 0 | 15.0549 | 37.78
2023-03-08 23:00 | 44993.9583 | 0 | 14.2087 | 37.78
2023-03-08 23:30 | 44993.9792 | 0 | 13.7341 | 37.78
2023-03-09 | 44994 | 0 | 12.9018 | 37.78
2023-03-09 00:30 | 44994.0208 | 0 | 12.5471 | 37.78
2023-03-09 01:00 | 44994.0417 | 0 | 12.1415 | 37.78
2023-03-09 01:30 | 44994.0625 | 0 | 11.8287 | 37.78
2023-03-09 02:00 | 44994.0833 | 0 | 11.6669 | 37.78
2023-03-09 02:30 | 44994.1042 | 0 | 11.3911 | 37.78
2023-03-09 03:00 | 44994.125 | 0 | 11.3133 | 37.78
2023-03-09 03:30 | 44994.1458 | 0 | 11.33 | 37.78
2023-03-09 04:00 | 44994.1667 | 0 | 11.5182 | 37.78
2023-03-09 04:30 | 44994.1875 | 0 | 11.8468 | 37.78
2023-03-09 05:00 | 44994.2083 | 0 | 12.4979 | 37.78
2023-03-09 05:30 | 44994.2292 | 0 | 12.9137 | 37.78
2023-03-09 06:00 | 44994.25 | 0 | 14.0076 | 37.78
2023-03-09 06:30 | 44994.2708 | 0 | 14.9238 | 37.78
2023-03-09 07:00 | 44994.2917 | 0 | 15.3947 | 37.78
2023-03-09 07:30 | 44994.3125 | 0 | 15.8385 | 37.78
2023-03-09 08:00 | 44994.3333 | 0 | 15.3104 | 37.78
2023-03-09 08:30 | 44994.3542 | 0 | 16.2358 | 37.78
2023-03-09 09:00 | 44994.375 | 0 | 17.2047 | 37.78
2023-03-09 09:30 | 44994.3958 | 0 | 17.8591 | 37.78
2023-03-09 10:00 | 44994.4167 | 0 | 17.8209 | 37.78
2023-03-09 10:30 | 44994.4375 | 0 | 17.5851 | 37.78
2023-03-09 11:00 | 44994.4583 | 0 | 17.295 | 37.78
2023-03-09 11:30 | 44994.4792 | 0 | 16.6814 | 37.78
2023-03-09 12:00 | 44994.5 | 0 | 17.2638 | 37.78
2023-03-09 12:30 | 44994.5208 | 0 | 17.3508 | 37.78
2023-03-09 13:00 | 44994.5417 | 0 | 17.2747 | 37.78
2023-03-09 13:30 | 44994.5625 | 0 | 16.8511 | 37.78
2023-03-09 14:00 | 44994.5833 | 0 | 16.8227 | 37.78
2023-03-09 14:30 | 44994.6042 | 0 | 16.1545 | 37.78
2023-03-09 15:00 | 44994.625 | 0 | 16.0163 | 37.78
2023-03-09 15:30 | 44994.6458 | 0 | 16.914 | 37.78
2023-03-09 16:00 | 44994.6667 | 0 | 16.9058 | 37.78
2023-03-09 16:30 | 44994.6875 | 0 | 16.6303 | 37.78
2023-03-09 17:00 | 44994.7083 | 0 | 16.5707 | 37.78
2023-03-09 17:30 | 44994.7292 | 0 | 16.8111 | 37.78
2023-03-09 18:00 | 44994.75 | 0 | 16.8965 | 37.78
2023-03-09 18:30 | 44994.7708 | 0 | 17.0677 | 37.78
2023-03-09 19:00 | 44994.7917 | 0 | 16.9002 | 37.78
2023-03-09 19:30 | 44994.8125 | 0 | 16.6768 | 37.78
2023-03-09 20:00 | 44994.8333 | 0 | 16.4552 | 37.78
2023-03-09 20:30 | 44994.8542 | 0 | 16.0831 | 37.78
2023-03-09 21:00 | 44994.875 | 0 | 15.6165 | 37.78
2023-03-09 21:30 | 44994.8958 | 0 | 14.7449 | 37.78
2023-03-09 22:00 | 44994.9167 | 0 | 13.9528 | 37.78
2023-03-09 22:30 | 44994.9375 | 0 | 13.0602 | 37.78
2023-03-09 23:00 | 44994.9583 | 0 | 12.526 | 37.78
2023-03-09 23:30 | 44994.9792 | 0 | 11.8435 | 37.78
2023-03-10 | 44995 | 0 | 11.2963 | 37.78
2023-03-10 00:30 | 44995.0208 | 0 | 10.853 | 37.78
2023-03-10 01:00 | 44995.0417 | 0 | 10.5631 | 37.78
2023-03-10 01:30 | 44995.0625 | 0 | 10.3232 | 37.78
2023-03-10 02:00 | 44995.0833 | 0 | 10.1934 | 37.78
2023-03-10 02:30 | 44995.1042 | 0 | 10.1056 | 37.78
2023-03-10 03:00 | 44995.125 | 0 | 9.9081 | 37.78
2023-03-10 03:30 | 44995.1458 | 0 | 9.8451 | 37.78
2023-03-10 04:00 | 44995.1667 | 0 | 10.0983 | 37.78
2023-03-10 04:30 | 44995.1875 | 0 | 10.4602 | 37.78
2023-03-10 05:00 | 44995.2083 | 0 | 11.0761 | 37.78
2023-03-10 05:30 | 44995.2292 | 0 | 11.6003 | 37.78
2023-03-10 06:00 | 44995.25 | 0 | 12.4206 | 37.78
2023-03-10 06:30 | 44995.2708 | 0 | 13.0618 | 37.78
2023-03-10 07:00 | 44995.2917 | 0 | 13.6695 | 37.78
2023-03-10 07:30 | 44995.3125 | 0 | 13.6155 | 37.78
2023-03-10 08:00 | 44995.3333 | 0 | 13.2968 | 37.78
2023-03-10 08:30 | 44995.3542 | 0 | 13.7874 | 37.78
2023-03-10 09:00 | 44995.375 | 0 | 14.0516 | 37.78
2023-03-10 09:30 | 44995.3958 | 0 | 15.5229 | 37.78
2023-03-10 10:00 | 44995.4167 | 0 | 14.9959 | 37.78
2023-03-10 10:30 | 44995.4375 | 0 | 14.438 | 37.78
2023-03-10 11:00 | 44995.4583 | 0 | 15.0026 | 37.78
2023-03-10 11:30 | 44995.4792 | 0 | 15.6224 | 37.78
2023-03-10 12:00 | 44995.5 | 0 | 16.3452 | 37.78
2023-03-10 12:30 | 44995.5208 | 0 | 16.6087 | 37.78
2023-03-10 13:00 | 44995.5417 | 0 | 17.2801 | 37.78
2023-03-10 13:30 | 44995.5625 | 0 | 17.3394 | 37.78
2023-03-10 14:00 | 44995.5833 | 0 | 16.2508 | 37.78
2023-03-10 14:30 | 44995.6042 | 0 | 16.1544 | 37.78
2023-03-10 15:00 | 44995.625 | 0 | 15.5974 | 37.78
2023-03-10 15:30 | 44995.6458 | 0 | 15.9159 | 37.78
2023-03-10 16:00 | 44995.6667 | 0 | 15.8637 | 37.78
2023-03-10 16:30 | 44995.6875 | 0 | 15.9475 | 37.78
2023-03-10 17:00 | 44995.7083 | 0 | 15.6821 | 37.78
2023-03-10 17:30 | 44995.7292 | 0 | 15.2383 | 37.78
2023-03-10 18:00 | 44995.75 | 0 | 15.1768 | 37.78
2023-03-10 18:30 | 44995.7708 | 0 | 15.3797 | 37.78
2023-03-10 19:00 | 44995.7917 | 0 | 15.188 | 37.78
2023-03-10 19:30 | 44995.8125 | 0 | 15.0206 | 37.78
2023-03-10 20:00 | 44995.8333 | 0 | 14.8264 | 37.78
2023-03-10 20:30 | 44995.8542 | 0 | 14.3578 | 37.78
2023-03-10 21:00 | 44995.875 | 0 | 14.1069 | 37.78
2023-03-10 21:30 | 44995.8958 | 0 | 13.82 | 37.78
2023-03-10 22:00 | 44995.9167 | 0 | 13.2072 | 37.78
2023-03-10 22:30 | 44995.9375 | 0 | 12.4632 | 37.78
2023-03-10 23:00 | 44995.9583 | 0 | 11.797 | 37.78
2023-03-10 23:30 | 44995.9792 | 0 | 11.4032 | 37.78
2023-03-11 | 44996 | 0 | 10.9409 | 37.78
2023-03-11 00:30 | 44996.0208 | 0 | 10.5871 | 37.78
2023-03-11 01:00 | 44996.0417 | 0 | 10.1798 | 37.78
2023-03-11 01:30 | 44996.0625 | 0 | 10.0608 | 37.78
2023-03-11 02:00 | 44996.0833 | 0 | 9.9294 | 37.78
2023-03-11 02:30 | 44996.1042 | 0 | 9.6642 | 37.78
2023-03-11 03:00 | 44996.125 | 0 | 9.6384 | 37.78
2023-03-11 03:30 | 44996.1458 | 0 | 9.6532 | 37.78
2023-03-11 04:00 | 44996.1667 | 0 | 9.698 | 37.78
2023-03-11 04:30 | 44996.1875 | 0 | 9.5542 | 37.78
2023-03-11 05:00 | 44996.2083 | 0 | 9.5733 | 37.78
2023-03-11 05:30 | 44996.2292 | 0 | 9.793 | 37.78
2023-03-11 06:00 | 44996.25 | 0 | 9.8245 | 37.78
2023-03-11 06:30 | 44996.2708 | 0 | 10.2274 | 37.78
2023-03-11 07:00 | 44996.2917 | 0 | 10.1612 | 37.78
2023-03-11 07:30 | 44996.3125 | 0 | 10.7814 | 37.78
2023-03-11 08:00 | 44996.3333 | 0 | 11.6078 | 37.78
2023-03-11 08:30 | 44996.3542 | 0 | 12.3885 | 37.78
2023-03-11 09:00 | 44996.375 | 0 | 11.9537 | 37.78
2023-03-11 09:30 | 44996.3958 | 0 | 12.6251 | 37.78
2023-03-11 10:00 | 44996.4167 | 0 | 11.55 | 37.78
2023-03-11 10:30 | 44996.4375 | 0 | 11.4696 | 37.78
2023-03-11 11:00 | 44996.4583 | 0 | 12.6479 | 37.78
2023-03-11 11:30 | 44996.4792 | 0 | 13.0566 | 37.78
2023-03-11 12:00 | 44996.5 | 0 | 12.7677 | 37.78
2023-03-11 12:30 | 44996.5208 | 0 | 13.7597 | 37.78
2023-03-11 13:00 | 44996.5417 | 0 | 12.6972 | 37.78
2023-03-11 13:30 | 44996.5625 | 0 | 13.2431 | 37.78
2023-03-11 14:00 | 44996.5833 | 0 | 12.9514 | 37.78
2023-03-11 14:30 | 44996.6042 | 0 | 12.7684 | 37.78
2023-03-11 15:00 | 44996.625 | 0 | 13.9084 | 37.78
2023-03-11 15:30 | 44996.6458 | 0 | 14.39 | 37.78
2023-03-11 16:00 | 44996.6667 | 0 | 14.3654 | 37.78
2023-03-11 16:30 | 44996.6875 | 0 | 14.0154 | 37.78
2023-03-11 17:00 | 44996.7083 | 0 | 13.7923 | 37.78
2023-03-11 17:30 | 44996.7292 | 0 | 13.8238 | 37.78
2023-03-11 18:00 | 44996.75 | 0 | 13.9077 | 37.78
2023-03-11 18:30 | 44996.7708 | 0 | 14.2447 | 37.78
2023-03-11 19:00 | 44996.7917 | 0 | 14.4064 | 37.78
2023-03-11 19:30 | 44996.8125 | 0 | 13.9893 | 37.78
2023-03-11 20:00 | 44996.8333 | 0 | 13.7442 | 37.78
2023-03-11 20:30 | 44996.8542 | 0 | 13.418 | 37.78
2023-03-11 21:00 | 44996.875 | 0 | 13.1259 | 37.78
2023-03-11 21:30 | 44996.8958 | 0 | 12.9996 | 37.78
2023-03-11 22:00 | 44996.9167 | 0 | 12.4438 | 37.78
2023-03-11 22:30 | 44996.9375 | 0 | 11.8007 | 37.78
2023-03-11 23:00 | 44996.9583 | 0 | 11.3782 | 37.78
2023-03-11 23:30 | 44996.9792 | 0 | 10.9372 | 37.78
2023-03-12 | 44997 | 0 | 10.4951 | 37.78
2023-03-12 00:30 | 44997.0208 | 0 | 10.0747 | 37.78
2023-03-12 01:00 | 44997.0417 | 0 | 9.9062 | 37.78
2023-03-12 01:30 | 44997.0625 | 0 | 9.6905 | 37.78
2023-03-12 02:00 | 44997.0833 | 0 | 9.6086 | 37.78
2023-03-12 02:30 | 44997.1042 | 0 | 9.5546 | 37.78
2023-03-12 03:00 | 44997.125 | 0 | 9.4931 | 37.78
2023-03-12 03:30 | 44997.1458 | 0 | 9.3723 | 37.78
2023-03-12 04:00 | 44997.1667 | 0 | 9.1501 | 37.78
2023-03-12 04:30 | 44997.1875 | 0 | 9.0893 | 37.78
2023-03-12 05:00 | 44997.2083 | 0 | 9.1024 | 37.78
2023-03-12 05:30 | 44997.2292 | 0 | 9.2681 | 37.78
2023-03-12 06:00 | 44997.25 | 0 | 9.0891 | 37.78
2023-03-12 06:30 | 44997.2708 | 0 | 9.0914 | 37.78
2023-03-12 07:00 | 44997.2917 | 0 | 9.2191 | 37.78
2023-03-12 07:30 | 44997.3125 | 0 | 9.8451 | 37.78
2023-03-12 08:00 | 44997.3333 | 0 | 10.1786 | 37.78
2023-03-12 08:30 | 44997.3542 | 0 | 10.6023 | 37.78
2023-03-12 09:00 | 44997.375 | 0 | 9.3545 | 37.78
2023-03-12 09:30 | 44997.3958 | 0 | 10.327 | 37.78
2023-03-12 10:00 | 44997.4167 | 0 | 11.3562 | 37.78
2023-03-12 10:30 | 44997.4375 | 0 | 13.2797 | 37.78
2023-03-12 11:00 | 44997.4583 | 0 | 13.5279 | 37.78
2023-03-12 11:30 | 44997.4792 | 0 | 10.9467 | 37.78
2023-03-12 12:00 | 44997.5 | 0 | 12.6643 | 37.78
2023-03-12 12:30 | 44997.5208 | 0 | 13.2953 | 37.78
2023-03-12 13:00 | 44997.5417 | 0 | 13.5801 | 37.78
2023-03-12 13:30 | 44997.5625 | 0 | 17.0566 | 37.78
2023-03-12 14:00 | 44997.5833 | 0 | 17.2334 | 37.78
2023-03-12 14:30 | 44997.6042 | 0 | 16.5345 | 37.78
2023-03-12 15:00 | 44997.625 | 0 | 15.3991 | 37.78
2023-03-12 15:30 | 44997.6458 | 0 | 14.86 | 37.78
2023-03-12 16:00 | 44997.6667 | 0 | 14.1873 | 37.78
2023-03-12 16:30 | 44997.6875 | 0 | 14.0565 | 37.78
2023-03-12 17:00 | 44997.7083 | 0 | 13.7895 | 37.78
2023-03-12 17:30 | 44997.7292 | 0 | 13.7091 | 37.78
2023-03-12 18:00 | 44997.75 | 0 | 14.1069 | 37.78
2023-03-12 18:30 | 44997.7708 | 0 | 14.4213 | 37.78
2023-03-12 19:00 | 44997.7917 | 0 | 14.3226 | 37.78
2023-03-12 19:30 | 44997.8125 | 0 | 14.0304 | 37.78
2023-03-12 20:00 | 44997.8333 | 0 | 13.6667 | 37.78
2023-03-12 20:30 | 44997.8542 | 0 | 13.286 | 37.78
2023-03-12 21:00 | 44997.875 | 0 | 12.7587 | 37.78
2023-03-12 21:30 | 44997.8958 | 0 | 12.2083 | 37.78
2023-03-12 22:00 | 44997.9167 | 0 | 11.5793 | 37.78
2023-03-12 22:30 | 44997.9375 | 0 | 10.8625 | 37.78
2023-03-12 23:00 | 44997.9583 | 0 | 10.3938 | 37.78
2023-03-12 23:30 | 44997.9792 | 0 | 9.9311 | 37.78
2023-03-13 | 44998 | 0 | 9.763 | 37.78
2023-03-13 00:30 | 44998.0208 | 0 | 9.603 | 37.78
2023-03-13 01:00 | 44998.0417 | 0 | 9.7202 | 37.78
2023-03-13 01:30 | 44998.0625 | 0 | 9.5086 | 37.78
2023-03-13 02:00 | 44998.0833 | 0 | 9.6125 | 37.78
2023-03-13 02:30 | 44998.1042 | 0 | 9.6012 | 37.78
2023-03-13 03:00 | 44998.125 | 0 | 9.5714 | 37.78
2023-03-13 03:30 | 44998.1458 | 0 | 9.78 | 37.78
2023-03-13 04:00 | 44998.1667 | 0 | 10.0144 | 37.78
2023-03-13 04:30 | 44998.1875 | 0 | 10.1172 | 37.78
2023-03-13 05:00 | 44998.2083 | 0 | 11.0415 | 37.78
2023-03-13 05:30 | 44998.2292 | 0 | 11.5175 | 37.78
2023-03-13 06:00 | 44998.25 | 0 | 12.6593 | 37.78
2023-03-13 06:30 | 44998.2708 | 0 | 13.3974 | 37.78
2023-03-13 07:00 | 44998.2917 | 0 | 14.0358 | 37.78
2023-03-13 07:30 | 44998.3125 | 0 | 14.2449 | 37.78
2023-03-13 08:00 | 44998.3333 | 0 | 14.3097 | 37.78
2023-03-13 08:30 | 44998.3542 | 0 | 15.0309 | 37.78
2023-03-13 09:00 | 44998.375 | 0 | 14.2036 | 37.78
2023-03-13 09:30 | 44998.3958 | 0 | 14.5165 | 37.78
2023-03-13 10:00 | 44998.4167 | 0 | 14.22 | 37.78
2023-03-13 10:30 | 44998.4375 | 0 | 13.9381 | 37.78
2023-03-13 11:00 | 44998.4583 | 0 | 14.8924 | 37.78
2023-03-13 11:30 | 44998.4792 | 0 | 15.613 | 37.78
2023-03-13 12:00 | 44998.5 | 0 | 15.1311 | 37.78
2023-03-13 12:30 | 44998.5208 | 0 | 14.597 | 37.78
2023-03-13 13:00 | 44998.5417 | 0 | 16.2981 | 37.78
2023-03-13 13:30 | 44998.5625 | 0 | 16.7241 | 37.78
2023-03-13 14:00 | 44998.5833 | 0 | 15.5176 | 37.78
2023-03-13 14:30 | 44998.6042 | 0 | 15.6218 | 37.78
2023-03-13 15:00 | 44998.625 | 0 | 17.7564 | 37.78
2023-03-13 15:30 | 44998.6458 | 0 | 17.7744 | 37.78
2023-03-13 16:00 | 44998.6667 | 0 | 17.4039 | 37.78
2023-03-13 16:30 | 44998.6875 | 0 | 18.6293 | 37.78
2023-03-13 17:00 | 44998.7083 | 0 | 18.791 | 37.78
2023-03-13 17:30 | 44998.7292 | 0 | 18.9308 | 37.78
2023-03-13 18:00 | 44998.75 | 0 | 19.2193 | 37.78
2023-03-13 18:30 | 44998.7708 | 0 | 19.6458 | 37.78
2023-03-13 19:00 | 44998.7917 | 0 | 19.1032 | 37.78
2023-03-13 19:30 | 44998.8125 | 0 | 18.4566 | 37.78
2023-03-13 20:00 | 44998.8333 | 0 | 17.7862 | 37.78
2023-03-13 20:30 | 44998.8542 | 0 | 17.1237 | 37.78
2023-03-13 21:00 | 44998.875 | 0 | 16.1576 | 37.78
2023-03-13 21:30 | 44998.8958 | 0 | 15.295 | 37.78
2023-03-13 22:00 | 44998.9167 | 0 | 14.182 | 37.78
2023-03-13 22:30 | 44998.9375 | 0 | 13.259 | 37.78
2023-03-13 23:00 | 44998.9583 | 0 | 12.5028 | 37.78
2023-03-13 23:30 | 44998.9792 | 0 | 11.8398 | 37.78
2023-03-14 | 44999 | 0 | 11.3502 | 37.78
2023-03-14 00:30 | 44999.0208 | 0 | 11.1699 | 37.78
2023-03-14 01:00 | 44999.0417 | 0 | 10.9206 | 37.78
2023-03-14 01:30 | 44999.0625 | 0 | 10.59 | 37.78
2023-03-14 02:00 | 44999.0833 | 0 | 10.4163 | 37.78
2023-03-14 02:30 | 44999.1042 | 0 | 10.1948 | 37.78
2023-03-14 03:00 | 44999.125 | 0 | 10.1018 | 37.78
2023-03-14 03:30 | 44999.1458 | 0 | 10.167 | 37.78
2023-03-14 04:00 | 44999.1667 | 0 | 10.4295 | 37.78
2023-03-14 04:30 | 44999.1875 | 0 | 10.7255 | 37.78
2023-03-14 05:00 | 44999.2083 | 0 | 11.3372 | 37.78
2023-03-14 05:30 | 44999.2292 | 0 | 11.774 | 37.78
2023-03-14 06:00 | 44999.25 | 0 | 12.5129 | 37.78
2023-03-14 06:30 | 44999.2708 | 0 | 12.7706 | 37.78
2023-03-14 07:00 | 44999.2917 | 0 | 13.2355 | 37.78
2023-03-14 07:30 | 44999.3125 | 0 | 13.0573 | 37.78
2023-03-14 08:00 | 44999.3333 | 0 | 12.8784 | 37.78
2023-03-14 08:30 | 44999.3542 | 0 | 12.8117 | 37.78
2023-03-14 09:00 | 44999.375 | 0 | 12.8207 | 37.78
2023-03-14 09:30 | 44999.3958 | 0 | 12.7961 | 37.78
2023-03-14 10:00 | 44999.4167 | 0 | 13.3885 | 37.78
2023-03-14 10:30 | 44999.4375 | 0 | 13.6694 | 37.78
2023-03-14 11:00 | 44999.4583 | 0 | 14.2104 | 37.78
2023-03-14 11:30 | 44999.4792 | 0 | 14.7676 | 37.78
2023-03-14 12:00 | 44999.5 | 0 | 15.042 | 37.78
2023-03-14 12:30 | 44999.5208 | 0 | 15.2176 | 37.78
2023-03-14 13:00 | 44999.5417 | 0 | 13.898 | 37.78
2023-03-14 13:30 | 44999.5625 | 0 | 14.6796 | 37.78
2023-03-14 14:00 | 44999.5833 | 0 | 16.5576 | 37.78
2023-03-14 14:30 | 44999.6042 | 0 | 16.1906 | 37.78
2023-03-14 15:00 | 44999.625 | 0 | 16.1791 | 37.78
2023-03-14 15:30 | 44999.6458 | 0 | 17.2335 | 37.78
2023-03-14 16:00 | 44999.6667 | 0 | 17.8806 | 37.78
2023-03-14 16:30 | 44999.6875 | 0 | 18.7782 | 37.78
2023-03-14 17:00 | 44999.7083 | 0 | 18.6996 | 37.78
2023-03-14 17:30 | 44999.7292 | 0 | 18.7707 | 37.78
2023-03-14 18:00 | 44999.75 | 0 | 18.6627 | 37.78
2023-03-14 18:30 | 44999.7708 | 0 | 19.2164 | 37.78
2023-03-14 19:00 | 44999.7917 | 0 | 18.7183 | 37.78
2023-03-14 19:30 | 44999.8125 | 0 | 18.276 | 37.78
2023-03-14 20:00 | 44999.8333 | 0 | 17.7232 | 37.78
2023-03-14 20:30 | 44999.8542 | 0 | 17.0183 | 37.78
2023-03-14 21:00 | 44999.875 | 0 | 16.35 | 37.78
2023-03-14 21:30 | 44999.8958 | 0 | 15.5061 | 37.78
2023-03-14 22:00 | 44999.9167 | 0 | 14.7216 | 37.78
2023-03-14 22:30 | 44999.9375 | 0 | 13.8742 | 37.78
2023-03-14 23:00 | 44999.9583 | 0 | 13.288 | 37.78
2023-03-14 23:30 | 44999.9792 | 0 | 12.5627 | 37.78
2023-03-15 | 45000 | 0 | 11.9653 | 37.78
2023-03-15 00:30 | 45000.0208 | 0 | 11.3026 | 37.78
2023-03-15 01:00 | 45000.0417 | 0 | 11.09 | 37.78
2023-03-15 01:30 | 45000.0625 | 0 | 10.7678 | 37.78
2023-03-15 02:00 | 45000.0833 | 0 | 10.5193 | 37.78
2023-03-15 02:30 | 45000.1042 | 0 | 9.9652 | 37.78
2023-03-15 03:00 | 45000.125 | 0 | 10.2436 | 37.78
2023-03-15 03:30 | 45000.1458 | 0 | 10.716 | 37.78
2023-03-15 04:00 | 45000.1667 | 0 | 10.9162 | 37.78
2023-03-15 04:30 | 45000.1875 | 0 | 11.0697 | 37.78
2023-03-15 05:00 | 45000.2083 | 0 | 11.699 | 37.78
2023-03-15 05:30 | 45000.2292 | 0 | 12.1027 | 37.78
2023-03-15 06:00 | 45000.25 | 0 | 12.999 | 37.78
2023-03-15 06:30 | 45000.2708 | 0 | 13.4722 | 37.78
2023-03-15 07:00 | 45000.2917 | 0 | 13.7546 | 37.78
2023-03-15 07:30 | 45000.3125 | 0 | 13.5651 | 37.78
2023-03-15 08:00 | 45000.3333 | 0 | 13.7272 | 37.78
2023-03-15 08:30 | 45000.3542 | 0 | 13.759 | 37.78
2023-03-15 09:00 | 45000.375 | 0 | 14.3184 | 37.78
2023-03-15 09:30 | 45000.3958 | 0 | 14.4118 | 37.78
2023-03-15 10:00 | 45000.4167 | 0 | 13.7733 | 37.78
2023-03-15 10:30 | 45000.4375 | 0 | 13.5849 | 37.78
2023-03-15 11:00 | 45000.4583 | 0 | 13.8387 | 37.78
2023-03-15 11:30 | 45000.4792 | 0 | 13.9206 | 37.78
2023-03-15 12:00 | 45000.5 | 0 | 14.2405 | 37.78
2023-03-15 12:30 | 45000.5208 | 0 | 17.0641 | 37.78
2023-03-15 13:00 | 45000.5417 | 0 | 20.062 | 37.78
2023-03-15 13:30 | 45000.5625 | 0 | 19.5413 | 37.78
2023-03-15 14:00 | 45000.5833 | 0 | 14.8789 | 37.78
2023-03-15 14:30 | 45000.6042 | 0 | 15.5436 | 37.78
2023-03-15 15:00 | 45000.625 | 0 | 16.485 | 37.78
2023-03-15 15:30 | 45000.6458 | 0 | 17.9896 | 37.78
2023-03-15 16:00 | 45000.6667 | 0 | 19.2621 | 37.78
2023-03-15 16:30 | 45000.6875 | 0 | 20.0299 | 37.78
2023-03-15 17:00 | 45000.7083 | 0 | 19.2417 | 37.78
2023-03-15 17:30 | 45000.7292 | 0 | 19.3882 | 37.78
2023-03-15 18:00 | 45000.75 | 0 | 19.4535 | 37.78
2023-03-15 18:30 | 45000.7708 | 0 | 19.8837 | 37.78
2023-03-15 19:00 | 45000.7917 | 0 | 19.6458 | 37.78
2023-03-15 19:30 | 45000.8125 | 0 | 19.3199 | 37.78
2023-03-15 20:00 | 45000.8333 | 0 | 19.2783 | 37.78
2023-03-15 20:30 | 45000.8542 | 0 | 18.4682 | 37.78
2023-03-15 21:00 | 45000.875 | 0 | 17.4656 | 37.78
2023-03-15 21:30 | 45000.8958 | 0 | 16.8051 | 37.78
2023-03-15 22:00 | 45000.9167 | 0 | 15.8649 | 37.78
2023-03-15 22:30 | 45000.9375 | 0 | 14.8382 | 37.78
2023-03-15 23:00 | 45000.9583 | 0 | 13.644 | 37.78
2023-03-15 23:30 | 45000.9792 | 0 | 13.0849 | 37.78
2023-03-16 | 45001 | 0 | 12.677 | 37.78
2023-03-16 00:30 | 45001.0208 | 0 | 12.1054 | 37.78
2023-03-16 01:00 | 45001.0417 | 0 | 11.5494 | 37.78
2023-03-16 01:30 | 45001.0625 | 0 | 11.3102 | 37.78
2023-03-16 02:00 | 45001.0833 | 0 | 11.0769 | 37.78
2023-03-16 02:30 | 45001.1042 | 0 | 10.8314 | 37.78
2023-03-16 03:00 | 45001.125 | 0 | 10.7459 | 37.78
2023-03-16 03:30 | 45001.1458 | 0 | 10.6193 | 37.78
2023-03-16 04:00 | 45001.1667 | 0 | 10.9887 | 37.78
2023-03-16 04:30 | 45001.1875 | 0 | 11.3712 | 37.78
2023-03-16 05:00 | 45001.2083 | 0 | 11.8937 | 37.78
2023-03-16 05:30 | 45001.2292 | 0 | 11.9108 | 37.78
2023-03-16 06:00 | 45001.25 | 0 | 12.8483 | 37.78
2023-03-16 06:30 | 45001.2708 | 0 | 13.9225 | 37.78
2023-03-16 07:00 | 45001.2917 | 0 | 14.7769 | 37.78
2023-03-16 07:30 | 45001.3125 | 0 | 14.6707 | 37.78
2023-03-16 08:00 | 45001.3333 | 0 | 14.8401 | 37.78
2023-03-16 08:30 | 45001.3542 | 0 | 15.0384 | 37.78
2023-03-16 09:00 | 45001.375 | 0 | 15.4355 | 37.78
2023-03-16 09:30 | 45001.3958 | 0 | 15.2006 | 37.78
2023-03-16 10:00 | 45001.4167 | 0 | 14.8475 | 37.78
2023-03-16 10:30 | 45001.4375 | 0 | 15.0022 | 37.78
2023-03-16 11:00 | 45001.4583 | 0 | 15.3891 | 37.78
2023-03-16 11:30 | 45001.4792 | 0 | 16.1344 | 37.78
2023-03-16 12:00 | 45001.5 | 0 | 17.2258 | 37.78
2023-03-16 12:30 | 45001.5208 | 0 | 19.5205 | 37.78
2023-03-16 13:00 | 45001.5417 | 0 | 20.7179 | 37.78
2023-03-16 13:30 | 45001.5625 | 0 | 18.7761 | 37.78
2023-03-16 14:00 | 45001.5833 | 0 | 19.219 | 37.78
2023-03-16 14:30 | 45001.6042 | 0 | 19.8994 | 37.78
2023-03-16 15:00 | 45001.625 | 0 | 20.7738 | 37.78
2023-03-16 15:30 | 45001.6458 | 0 | 21.8109 | 37.78
2023-03-16 16:00 | 45001.6667 | 0 | 22.7118 | 37.78
2023-03-16 16:30 | 45001.6875 | 0 | 23.2875 | 37.78
2023-03-16 17:00 | 45001.7083 | 0 | 23.2555 | 37.78
2023-03-16 17:30 | 45001.7292 | 0 | 22.8794 | 37.78
2023-03-16 18:00 | 45001.75 | 0 | 22.6209 | 37.78
2023-03-16 18:30 | 45001.7708 | 0 | 22.7776 | 37.78
2023-03-16 19:00 | 45001.7917 | 0 | 22.3425 | 37.78
2023-03-16 19:30 | 45001.8125 | 0 | 21.7404 | 37.78
2023-03-16 20:00 | 45001.8333 | 0 | 20.9804 | 37.78
2023-03-16 20:30 | 45001.8542 | 0 | 20.4711 | 37.78
2023-03-16 21:00 | 45001.875 | 0 | 19.7287 | 37.78
2023-03-16 21:30 | 45001.8958 | 0 | 19.0254 | 37.78
2023-03-16 22:00 | 45001.9167 | 0 | 17.6203 | 37.78
2023-03-16 22:30 | 45001.9375 | 0 | 16.7833 | 37.78
2023-03-16 23:00 | 45001.9583 | 0 | 15.8373 | 37.78
2023-03-16 23:30 | 45001.9792 | 0 | 14.778 | 37.78
2023-03-17 | 45002 | 0 | 14.0303 | 37.78
2023-03-17 00:30 | 45002.0208 | 0 | 13.6057 | 37.78
2023-03-17 01:00 | 45002.0417 | 0 | 13.1568 | 37.78
2023-03-17 01:30 | 45002.0625 | 0 | 12.7051 | 37.78
2023-03-17 02:00 | 45002.0833 | 0 | 12.4635 | 37.78
2023-03-17 02:30 | 45002.1042 | 0 | 12.3332 | 37.78
2023-03-17 03:00 | 45002.125 | 0 | 12.2011 | 37.78
2023-03-17 03:30 | 45002.1458 | 0 | 12.2141 | 37.78
2023-03-17 04:00 | 45002.1667 | 0 | 12.2587 | 37.78
2023-03-17 04:30 | 45002.1875 | 0 | 12.0856 | 37.78
2023-03-17 05:00 | 45002.2083 | 0 | 12.5451 | 37.78
2023-03-17 05:30 | 45002.2292 | 0 | 13.0684 | 37.78
2023-03-17 06:00 | 45002.25 | 0 | 13.8762 | 37.78
2023-03-17 06:30 | 45002.2708 | 0 | 15.1779 | 37.78
2023-03-17 07:00 | 45002.2917 | 0 | 15.6419 | 37.78
2023-03-17 07:30 | 45002.3125 | 0 | 15.7185 | 37.78
2023-03-17 08:00 | 45002.3333 | 0 | 16.504 | 37.78
2023-03-17 08:30 | 45002.3542 | 0 | 16.9154 | 37.78
2023-03-17 09:00 | 45002.375 | 0 | 17.0751 | 37.78
2023-03-17 09:30 | 45002.3958 | 0 | 16.716 | 37.78
2023-03-17 10:00 | 45002.4167 | 0 | 16.8388 | 37.78
2023-03-17 10:30 | 45002.4375 | 0 | 17.0039 | 37.78
2023-03-17 11:00 | 45002.4583 | 0 | 17.8422 | 37.78
2023-03-17 11:30 | 45002.4792 | 0 | 18.4098 | 37.78
2023-03-17 12:00 | 45002.5 | 0 | 18.296 | 37.78
2023-03-17 12:30 | 45002.5208 | 0 | 18.7529 | 37.78
2023-03-17 13:00 | 45002.5417 | 0 | 19.5065 | 37.78
2023-03-17 13:30 | 45002.5625 | 0 | 20.4497 | 37.78
2023-03-17 14:00 | 45002.5833 | 0 | 21.3077 | 37.78
2023-03-17 14:30 | 45002.6042 | 0 | 21.7405 | 37.78
2023-03-17 15:00 | 45002.625 | 0 | 22.4576 | 37.78
2023-03-17 15:30 | 45002.6458 | 0 | 23.5379 | 37.78
2023-03-17 16:00 | 45002.6667 | 0 | 24.5017 | 37.78
2023-03-17 16:30 | 45002.6875 | 0 | 24.7317 | 37.78
2023-03-17 17:00 | 45002.7083 | 0 | 23.9609 | 37.78
2023-03-17 17:30 | 45002.7292 | 0 | 23.8028 | 37.78
2023-03-17 18:00 | 45002.75 | 0 | 23.3284 | 37.78
2023-03-17 18:30 | 45002.7708 | 0 | 22.6552 | 37.78
2023-03-17 19:00 | 45002.7917 | 0 | 22.5054 | 37.78
2023-03-17 19:30 | 45002.8125 | 0 | 21.71 | 37.78
2023-03-17 20:00 | 45002.8333 | 0 | 21.0387 | 37.78
2023-03-17 20:30 | 45002.8542 | 0 | 20.1958 | 37.78
2023-03-17 21:00 | 45002.875 | 0 | 19.2864 | 37.78
2023-03-17 21:30 | 45002.8958 | 0 | 18.3343 | 37.78
2023-03-17 22:00 | 45002.9167 | 0 | 17.5346 | 37.78
2023-03-17 22:30 | 45002.9375 | 0 | 15.9368 | 37.78
2023-03-17 23:00 | 45002.9583 | 0 | 15.7994 | 37.78
2023-03-17 23:30 | 45002.9792 | 0 | 14.9627 | 37.78
2023-03-18 | 45003 | 0 | 14.3235 | 37.78
2023-03-18 00:30 | 45003.0208 | 0 | 13.6585 | 37.78
2023-03-18 01:00 | 45003.0417 | 0 | 13.4496 | 37.78
2023-03-18 01:30 | 45003.0625 | 0 | 13.0259 | 37.78
2023-03-18 02:00 | 45003.0833 | 0 | 12.7684 | 37.78
2023-03-18 02:30 | 45003.1042 | 0 | 12.3705 | 37.78
2023-03-18 03:00 | 45003.125 | 0 | 12.2381 | 37.78
2023-03-18 03:30 | 45003.1458 | 0 | 12.1844 | 37.78
2023-03-18 04:00 | 45003.1667 | 0 | 12.1321 | 37.78
2023-03-18 04:30 | 45003.1875 | 0 | 11.6547 | 37.78
2023-03-18 05:00 | 45003.2083 | 0 | 11.5887 | 37.78
2023-03-18 05:30 | 45003.2292 | 0 | 11.5218 | 37.78
2023-03-18 06:00 | 45003.25 | 0 | 11.4062 | 37.78
2023-03-18 06:30 | 45003.2708 | 0 | 11.3371 | 37.78
2023-03-18 07:00 | 45003.2917 | 0 | 11.3171 | 37.78
2023-03-18 07:30 | 45003.3125 | 0 | 11.4977 | 37.78
2023-03-18 08:00 | 45003.3333 | 0 | 11.7608 | 37.78
2023-03-18 08:30 | 45003.3542 | 0 | 11.9488 | 37.78
2023-03-18 09:00 | 45003.375 | 0 | 12.7679 | 37.78
2023-03-18 09:30 | 45003.3958 | 0 | 13.4874 | 37.78
2023-03-18 10:00 | 45003.4167 | 0 | 13.9752 | 37.78
2023-03-18 10:30 | 45003.4375 | 0 | 14.4917 | 37.78
2023-03-18 11:00 | 45003.4583 | 0 | 14.4806 | 37.78
2023-03-18 11:30 | 45003.4792 | 0 | 14.122 | 37.78
2023-03-18 12:00 | 45003.5 | 0 | 14.1656 | 37.78
2023-03-18 12:30 | 45003.5208 | 0 | 14.4232 | 37.78
2023-03-18 13:00 | 45003.5417 | 0 | 14.9303 | 37.78
2023-03-18 13:30 | 45003.5625 | 0 | 15.3828 | 37.78
2023-03-18 14:00 | 45003.5833 | 0 | 16.1906 | 37.78
2023-03-18 14:30 | 45003.6042 | 0 | 16.7968 | 37.78
2023-03-18 15:00 | 45003.625 | 0 | 17.7753 | 37.78
2023-03-18 15:30 | 45003.6458 | 0 | 18.6097 | 37.78
2023-03-18 16:00 | 45003.6667 | 0 | 19.4278 | 37.78
2023-03-18 16:30 | 45003.6875 | 0 | 19.8831 | 37.78
2023-03-18 17:00 | 45003.7083 | 0 | 20.3515 | 37.78
2023-03-18 17:30 | 45003.7292 | 0 | 19.9988 | 37.78
2023-03-18 18:00 | 45003.75 | 0 | 20.2969 | 37.78
2023-03-18 18:30 | 45003.7708 | 0 | 20.1718 | 37.78
2023-03-18 19:00 | 45003.7917 | 0 | 19.6628 | 37.78
2023-03-18 19:30 | 45003.8125 | 0 | 19.0113 | 37.78
2023-03-18 20:00 | 45003.8333 | 0 | 18.534 | 37.78
2023-03-18 20:30 | 45003.8542 | 0 | 17.7221 | 37.78
2023-03-18 21:00 | 45003.875 | 0 | 17.3606 | 37.78
2023-03-18 21:30 | 45003.8958 | 0 | 16.6408 | 37.78
2023-03-18 22:00 | 45003.9167 | 0 | 15.5423 | 37.78
2023-03-18 22:30 | 45003.9375 | 0 | 14.6116 | 37.78
2023-03-18 23:00 | 45003.9583 | 0 | 13.9816 | 37.78
2023-03-18 23:30 | 45003.9792 | 0 | 13.167 | 37.78
2023-03-19 | 45004 | 0 | 12.2901 | 37.78
2023-03-19 00:30 | 45004.0208 | 0 | 11.8772 | 37.78
2023-03-19 01:00 | 45004.0417 | 0 | 11.5901 | 37.78
2023-03-19 01:30 | 45004.0625 | 0 | 9.9591 | 37.78
2023-03-19 02:00 | 45004.0833 | 0 | 10.0534 | 37.78
2023-03-19 02:30 | 45004.1042 | 0 | 9.9864 | 37.78
2023-03-19 03:00 | 45004.125 | 0 | 9.9696 | 37.78
2023-03-19 03:30 | 45004.1458 | 0 | 10.8374 | 37.78
2023-03-19 04:00 | 45004.1667 | 0 | 10.766 | 37.78
2023-03-19 04:30 | 45004.1875 | 0 | 10.256 | 37.78
2023-03-19 05:00 | 45004.2083 | 0 | 10.2545 | 37.78
2023-03-19 05:30 | 45004.2292 | 0 | 10.2506 | 37.78
2023-03-19 06:00 | 45004.25 | 0 | 10.2357 | 37.78
2023-03-19 06:30 | 45004.2708 | 0 | 10.3142 | 37.78
2023-03-19 07:00 | 45004.2917 | 0 | 10.2054 | 37.78
2023-03-19 07:30 | 45004.3125 | 0 | 10.0253 | 37.78
2023-03-19 08:00 | 45004.3333 | 0 | 11.2176 | 37.78
2023-03-19 08:30 | 45004.3542 | 0 | 12.0652 | 37.78
2023-03-19 09:00 | 45004.375 | 0 | 11.7495 | 37.78
2023-03-19 09:30 | 45004.3958 | 0 | 11.5832 | 37.78
2023-03-19 10:00 | 45004.4167 | 0 | 11.7793 | 37.78
2023-03-19 10:30 | 45004.4375 | 0 | 10.5845 | 37.78
2023-03-19 11:00 | 45004.4583 | 0 | 10.8129 | 37.78
2023-03-19 11:30 | 45004.4792 | 0 | 11.2332 | 37.78
2023-03-19 12:00 | 45004.5 | 0 | 11.6253 | 37.78
2023-03-19 12:30 | 45004.5208 | 0 | 12.0456 | 37.78
2023-03-19 13:00 | 45004.5417 | 0 | 12.5572 | 37.78
2023-03-19 13:30 | 45004.5625 | 0 | 13.0294 | 37.78
2023-03-19 14:00 | 45004.5833 | 0 | 13.8255 | 37.78
2023-03-19 14:30 | 45004.6042 | 0 | 14.4329 | 37.78
2023-03-19 15:00 | 45004.625 | 0 | 15.5465 | 37.78
2023-03-19 15:30 | 45004.6458 | 0 | 16.3824 | 37.78
2023-03-19 16:00 | 45004.6667 | 0 | 17.2241 | 37.78
2023-03-19 16:30 | 45004.6875 | 0 | 17.9263 | 37.78
2023-03-19 17:00 | 45004.7083 | 0 | 18.4799 | 37.78
2023-03-19 17:30 | 45004.7292 | 0 | 18.4357 | 37.78
2023-03-19 18:00 | 45004.75 | 0 | 18.3611 | 37.78
2023-03-19 18:30 | 45004.7708 | 0 | 18.7096 | 37.78
2023-03-19 19:00 | 45004.7917 | 0 | 18.3085 | 37.78
2023-03-19 19:30 | 45004.8125 | 0 | 17.5639 | 37.78
2023-03-19 20:00 | 45004.8333 | 0 | 16.8917 | 37.78
2023-03-19 20:30 | 45004.8542 | 0 | 16.4136 | 37.78
2023-03-19 21:00 | 45004.875 | 0 | 15.6618 | 37.78
2023-03-19 21:30 | 45004.8958 | 0 | 14.4963 | 37.78
2023-03-19 22:00 | 45004.9167 | 0 | 13.555 | 37.78
2023-03-19 22:30 | 45004.9375 | 0 | 12.7217 | 37.78
2023-03-19 23:00 | 45004.9583 | 0 | 12.2604 | 37.78
2023-03-19 23:30 | 45004.9792 | 0 | 11.5284 | 37.78
2023-03-20 | 45005 | 0 | 11.0657 | 37.78
2023-03-20 00:30 | 45005.0208 | 0 | 10.7586 | 37.78
2023-03-20 01:00 | 45005.0417 | 0 | 10.4553 | 37.78
2023-03-20 01:30 | 45005.0625 | 0 | 10.2003 | 37.78
2023-03-20 02:00 | 45005.0833 | 0 | 9.8851 | 37.78
2023-03-20 02:30 | 45005.1042 | 0 | 9.9046 | 37.78
2023-03-20 03:00 | 45005.125 | 0 | 9.7389 | 37.78
2023-03-20 03:30 | 45005.1458 | 0 | 9.9493 | 37.78
2023-03-20 04:00 | 45005.1667 | 0 | 10.0553 | 37.78
2023-03-20 04:30 | 45005.1875 | 0 | 10.4043 | 37.78
2023-03-20 05:00 | 45005.2083 | 0 | 11.0272 | 37.78
2023-03-20 05:30 | 45005.2292 | 0 | 11.55 | 37.78
2023-03-20 06:00 | 45005.25 | 0 | 12.59 | 37.78
2023-03-20 06:30 | 45005.2708 | 0 | 13.1568 | 37.78
2023-03-20 07:00 | 45005.2917 | 0 | 13.8292 | 37.78
2023-03-20 07:30 | 45005.3125 | 0 | 13.3573 | 37.78
2023-03-20 08:00 | 45005.3333 | 0 | 13.1093 | 37.78
2023-03-20 08:30 | 45005.3542 | 0 | 13.2768 | 37.78
2023-03-20 09:00 | 45005.375 | 0 | 13.5336 | 37.78
2023-03-20 09:30 | 45005.3958 | 0 | 13.5351 | 37.78
2023-03-20 10:00 | 45005.4167 | 0 | 14.5673 | 37.78
2023-03-20 10:30 | 45005.4375 | 0 | 15.3381 | 37.78
2023-03-20 11:00 | 45005.4583 | 0 | 15.1224 | 37.78
2023-03-20 11:30 | 45005.4792 | 0 | 14.8968 | 37.78
2023-03-20 12:00 | 45005.5 | 0 | 13.9046 | 37.78
2023-03-20 12:30 | 45005.5208 | 0 | 14.2467 | 37.78
2023-03-20 13:00 | 45005.5417 | 0 | 14.8623 | 37.78
2023-03-20 13:30 | 45005.5625 | 0 | 15.3907 | 37.78
2023-03-20 14:00 | 45005.5833 | 0 | 16.0787 | 37.78
2023-03-20 14:30 | 45005.6042 | 0 | 16.5899 | 37.78
2023-03-20 15:00 | 45005.625 | 0 | 17.5006 | 37.78
2023-03-20 15:30 | 45005.6458 | 0 | 18.6175 | 37.78
2023-03-20 16:00 | 45005.6667 | 0 | 19.3158 | 37.78
2023-03-20 16:30 | 45005.6875 | 0 | 20.0373 | 37.78
2023-03-20 17:00 | 45005.7083 | 0 | 20.1365 | 37.78
2023-03-20 17:30 | 45005.7292 | 0 | 20.4102 | 37.78
2023-03-20 18:00 | 45005.75 | 0 | 20.3508 | 37.78
2023-03-20 18:30 | 45005.7708 | 0 | 20.6075 | 37.78
2023-03-20 19:00 | 45005.7917 | 0 | 20.1411 | 37.78
2023-03-20 19:30 | 45005.8125 | 0 | 19.6606 | 37.78
2023-03-20 20:00 | 45005.8333 | 0 | 18.927 | 37.78
2023-03-20 20:30 | 45005.8542 | 0 | 18.3163 | 37.78
2023-03-20 21:00 | 45005.875 | 0 | 17.5174 | 37.78
2023-03-20 21:30 | 45005.8958 | 0 | 16.6349 | 37.78
2023-03-20 22:00 | 45005.9167 | 0 | 15.4687 | 37.78
2023-03-20 22:30 | 45005.9375 | 0 | 14.3416 | 37.78
2023-03-20 23:00 | 45005.9583 | 0 | 13.6714 | 37.78
2023-03-20 23:30 | 45005.9792 | 0 | 12.8529 | 37.78
2023-03-21 | 45006 | 0 | 12.3071 | 37.78
2023-03-21 00:30 | 45006.0208 | 0 | 11.7265 | 37.78
2023-03-21 01:00 | 45006.0417 | 0 | 11.3653 | 37.78
2023-03-21 01:30 | 45006.0625 | 0 | 11.0396 | 37.78
2023-03-21 02:00 | 45006.0833 | 0 | 10.8393 | 37.78
2023-03-21 02:30 | 45006.1042 | 0 | 10.7103 | 37.78
2023-03-21 03:00 | 45006.125 | 0 | 10.5448 | 37.78
2023-03-21 03:30 | 45006.1458 | 0 | 10.7328 | 37.78
2023-03-21 04:00 | 45006.1667 | 0 | 10.8388 | 37.78
2023-03-21 04:30 | 45006.1875 | 0 | 11.1241 | 37.78
2023-03-21 05:00 | 45006.2083 | 0 | 11.6895 | 37.78
2023-03-21 05:30 | 45006.2292 | 0 | 12.3178 | 37.78
2023-03-21 06:00 | 45006.25 | 0 | 13.4766 | 37.78
2023-03-21 06:30 | 45006.2708 | 0 | 13.8362 | 37.78
2023-03-21 07:00 | 45006.2917 | 0 | 14.8464 | 37.78
2023-03-21 07:30 | 45006.3125 | 0 | 14.3842 | 37.78
2023-03-21 08:00 | 45006.3333 | 0 | 15.1245 | 37.78
2023-03-21 08:30 | 45006.3542 | 0 | 14.1702 | 37.78
2023-03-21 09:00 | 45006.375 | 0 | 14.7986 | 37.78
2023-03-21 09:30 | 45006.3958 | 0 | 14.5396 | 37.78
2023-03-21 10:00 | 45006.4167 | 0 | 13.641 | 37.78
2023-03-21 10:30 | 45006.4375 | 0 | 14.4391 | 37.78
2023-03-21 11:00 | 45006.4583 | 0 | 13.47 | 37.78
2023-03-21 11:30 | 45006.4792 | 0 | 13.2569 | 37.78
2023-03-21 12:00 | 45006.5 | 0 | 13.351 | 37.78
2023-03-21 12:30 | 45006.5208 | 0 | 13.138 | 37.78
2023-03-21 13:00 | 45006.5417 | 0 | 13.5614 | 37.78
2023-03-21 13:30 | 45006.5625 | 0 | 14.0459 | 37.78
2023-03-21 14:00 | 45006.5833 | 0 | 14.6949 | 37.78
2023-03-21 14:30 | 45006.6042 | 0 | 15.4129 | 37.78
2023-03-21 15:00 | 45006.625 | 0 | 16.0927 | 37.78
2023-03-21 15:30 | 45006.6458 | 0 | 16.6139 | 37.78
2023-03-21 16:00 | 45006.6667 | 0 | 17.506 | 37.78
2023-03-21 16:30 | 45006.6875 | 0 | 18.3499 | 37.78
2023-03-21 17:00 | 45006.7083 | 0 | 17.9348 | 37.78
2023-03-21 17:30 | 45006.7292 | 0 | 18.0672 | 37.78
2023-03-21 18:00 | 45006.75 | 0 | 18.1764 | 37.78
2023-03-21 18:30 | 45006.7708 | 0 | 18.3833 | 37.78
2023-03-21 19:00 | 45006.7917 | 0 | 18.0185 | 37.78
2023-03-21 19:30 | 45006.8125 | 0 | 17.6557 | 37.78
2023-03-21 20:00 | 45006.8333 | 0 | 17.5154 | 37.78
2023-03-21 20:30 | 45006.8542 | 0 | 16.727 | 37.78
2023-03-21 21:00 | 45006.875 | 0 | 16.1514 | 37.78
2023-03-21 21:30 | 45006.8958 | 0 | 15.6294 | 37.78
2023-03-21 22:00 | 45006.9167 | 0 | 14.6673 | 37.78
2023-03-21 22:30 | 45006.9375 | 0 | 13.5354 | 37.78
2023-03-21 23:00 | 45006.9583 | 0 | 12.8571 | 37.78
2023-03-21 23:30 | 45006.9792 | 0 | 12.3397 | 37.78
2023-03-22 | 45007 | 0 | 11.8342 | 37.78
2023-03-22 00:30 | 45007.0208 | 0 | 11.3829 | 37.78
2023-03-22 01:00 | 45007.0417 | 0 | 11.17 | 37.78
2023-03-22 01:30 | 45007.0625 | 0 | 10.9559 | 37.78
2023-03-22 02:00 | 45007.0833 | 0 | 10.6983 | 37.78
2023-03-22 02:30 | 45007.1042 | 0 | 10.6415 | 37.78
2023-03-22 03:00 | 45007.125 | 0 | 10.6173 | 37.78
2023-03-22 03:30 | 45007.1458 | 0 | 10.7495 | 37.78
2023-03-22 04:00 | 45007.1667 | 0 | 10.9302 | 37.78
2023-03-22 04:30 | 45007.1875 | 0 | 11.2169 | 37.78
2023-03-22 05:00 | 45007.2083 | 0 | 11.8341 | 37.78
2023-03-22 05:30 | 45007.2292 | 0 | 12.5015 | 37.78
2023-03-22 06:00 | 45007.25 | 0 | 13.3772 | 37.78
2023-03-22 06:30 | 45007.2708 | 0 | 13.773 | 37.78
2023-03-22 07:00 | 45007.2917 | 0 | 14.6197 | 37.78
2023-03-22 07:30 | 45007.3125 | 0 | 14.0082 | 37.78
2023-03-22 08:00 | 45007.3333 | 0 | 14.5859 | 37.78
2023-03-22 08:30 | 45007.3542 | 0 | 13.3131 | 37.78
2023-03-22 09:00 | 45007.375 | 0 | 13.845 | 37.78
2023-03-22 09:30 | 45007.3958 | 0 | 13.4984 | 37.78
2023-03-22 10:00 | 45007.4167 | 0 | 14.569 | 37.78
2023-03-22 10:30 | 45007.4375 | 0 | 14.397 | 37.78
2023-03-22 11:00 | 45007.4583 | 0 | 14.0503 | 37.78
2023-03-22 11:30 | 45007.4792 | 0 | 13.0201 | 37.78
2023-03-22 12:00 | 45007.5 | 0 | 13.0526 | 37.78
2023-03-22 12:30 | 45007.5208 | 0 | 13.2214 | 37.78
2023-03-22 13:00 | 45007.5417 | 0 | 13.4999 | 37.78
2023-03-22 13:30 | 45007.5625 | 0 | 13.0599 | 37.78
2023-03-22 14:00 | 45007.5833 | 0 | 12.7015 | 37.78
2023-03-22 14:30 | 45007.6042 | 0 | 13.6284 | 37.78
2023-03-22 15:00 | 45007.625 | 0 | 14.0057 | 37.78
2023-03-22 15:30 | 45007.6458 | 0 | 14.978 | 37.78
2023-03-22 16:00 | 45007.6667 | 0 | 14.9124 | 37.78
2023-03-22 16:30 | 45007.6875 | 0 | 15.7351 | 37.78
2023-03-22 17:00 | 45007.7083 | 0 | 15.3535 | 37.78
2023-03-22 17:30 | 45007.7292 | 0 | 15.5886 | 37.78
2023-03-22 18:00 | 45007.75 | 0 | 15.8575 | 37.78
2023-03-22 18:30 | 45007.7708 | 0 | 16.2302 | 37.78
2023-03-22 19:00 | 45007.7917 | 0 | 15.9343 | 37.78
2023-03-22 19:30 | 45007.8125 | 0 | 15.593 | 37.78
2023-03-22 20:00 | 45007.8333 | 0 | 15.2785 | 37.78
2023-03-22 20:30 | 45007.8542 | 0 | 14.7581 | 37.78
2023-03-22 21:00 | 45007.875 | 0 | 14.1917 | 37.78
2023-03-22 21:30 | 45007.8958 | 0 | 13.7097 | 37.78
2023-03-22 22:00 | 45007.9167 | 0 | 12.9415 | 37.78
2023-03-22 22:30 | 45007.9375 | 0 | 12.2571 | 37.78
2023-03-22 23:00 | 45007.9583 | 0 | 11.7915 | 37.78
2023-03-22 23:30 | 45007.9792 | 0 | 11.2094 | 37.78
2023-03-23 | 45008 | 0 | 10.7018 | 37.78
2023-03-23 00:30 | 45008.0208 | 0 | 10.3697 | 37.78
2023-03-23 01:00 | 45008.0417 | 0 | 10.0773 | 37.78
2023-03-23 01:30 | 45008.0625 | 0 | 9.869 | 37.78
2023-03-23 02:00 | 45008.0833 | 0 | 9.8376 | 37.78
2023-03-23 02:30 | 45008.1042 | 0 | 9.698 | 37.78
2023-03-23 03:00 | 45008.125 | 0 | 9.7556 | 37.78
2023-03-23 03:30 | 45008.1458 | 0 | 9.8357 | 37.78
2023-03-23 04:00 | 45008.1667 | 0 | 9.8618 | 37.78
2023-03-23 04:30 | 45008.1875 | 0 | 9.9623 | 37.78
2023-03-23 05:00 | 45008.2083 | 0 | 10.7093 | 37.78
2023-03-23 05:30 | 45008.2292 | 0 | 11.2695 | 37.78
2023-03-23 06:00 | 45008.25 | 0 | 12.2095 | 37.78
2023-03-23 06:30 | 45008.2708 | 0 | 12.5176 | 37.78
2023-03-23 07:00 | 45008.2917 | 0 | 12.8862 | 37.78
2023-03-23 07:30 | 45008.3125 | 0 | 12.7069 | 37.78
2023-03-23 08:00 | 45008.3333 | 0 | 12.5919 | 37.78
2023-03-23 08:30 | 45008.3542 | 0 | 13.0708 | 37.78
2023-03-23 09:00 | 45008.375 | 0 | 13.1725 | 37.78
2023-03-23 09:30 | 45008.3958 | 0 | 14.6503 | 37.78
2023-03-23 10:00 | 45008.4167 | 0 | 13.8815 | 37.78
2023-03-23 10:30 | 45008.4375 | 0 | 14.3759 | 37.78
2023-03-23 11:00 | 45008.4583 | 0 | 12.7928 | 37.78
2023-03-23 11:30 | 45008.4792 | 0 | 13.8991 | 37.78
2023-03-23 12:00 | 45008.5 | 0 | 13.5983 | 37.78
2023-03-23 12:30 | 45008.5208 | 0 | 13.4782 | 37.78
2023-03-23 13:00 | 45008.5417 | 0 | 14.3812 | 37.78
2023-03-23 13:30 | 45008.5625 | 0 | 14.625 | 37.78
2023-03-23 14:00 | 45008.5833 | 0 | 13.9051 | 37.78
2023-03-23 14:30 | 45008.6042 | 0 | 13.2625 | 37.78
2023-03-23 15:00 | 45008.625 | 0 | 13.7269 | 37.78
2023-03-23 15:30 | 45008.6458 | 0 | 15.2927 | 37.78
2023-03-23 16:00 | 45008.6667 | 0 | 15.4332 | 37.78
2023-03-23 16:30 | 45008.6875 | 0 | 16.0164 | 37.78
2023-03-23 17:00 | 45008.7083 | 0 | 15.7649 | 37.78
2023-03-23 17:30 | 45008.7292 | 0 | 15.9531 | 37.78
2023-03-23 18:00 | 45008.75 | 0 | 15.8077 | 37.78
2023-03-23 18:30 | 45008.7708 | 0 | 16.2018 | 37.78
2023-03-23 19:00 | 45008.7917 | 0 | 15.8134 | 37.78
2023-03-23 19:30 | 45008.8125 | 0 | 15.5805 | 37.78
2023-03-23 20:00 | 45008.8333 | 0 | 15.0723 | 37.78
2023-03-23 20:30 | 45008.8542 | 0 | 14.5462 | 37.78
2023-03-23 21:00 | 45008.875 | 0 | 14.0701 | 37.78
2023-03-23 21:30 | 45008.8958 | 0 | 13.4362 | 37.78
2023-03-23 22:00 | 45008.9167 | 0 | 12.6729 | 37.78
2023-03-23 22:30 | 45008.9375 | 0 | 11.9 | 37.78
2023-03-23 23:00 | 45008.9583 | 0 | 11.2578 | 37.78
2023-03-23 23:30 | 45008.9792 | 0 | 10.6655 | 37.78
2023-03-24 | 45009 | 0 | 10.0293 | 37.78
2023-03-24 00:30 | 45009.0208 | 0 | 9.7351 | 37.78
2023-03-24 01:00 | 45009.0417 | 0 | 9.5134 | 37.78
2023-03-24 01:30 | 45009.0625 | 0 | 9.3274 | 37.78
2023-03-24 02:00 | 45009.0833 | 0 | 9.2941 | 37.78
2023-03-24 02:30 | 45009.1042 | 0 | 9.1153 | 37.78
2023-03-24 03:00 | 45009.125 | 0 | 9.082 | 37.78
2023-03-24 03:30 | 45009.1458 | 0 | 9.2551 | 37.78
2023-03-24 04:00 | 45009.1667 | 0 | 9.4469 | 37.78
2023-03-24 04:30 | 45009.1875 | 0 | 9.7283 | 37.78
2023-03-24 05:00 | 45009.2083 | 0 | 10.3309 | 37.78
2023-03-24 05:30 | 45009.2292 | 0 | 10.8595 | 37.78
2023-03-24 06:00 | 45009.25 | 0 | 11.3832 | 37.78
2023-03-24 06:30 | 45009.2708 | 0 | 11.7362 | 37.78
2023-03-24 07:00 | 45009.2917 | 0 | 11.9907 | 37.78
2023-03-24 07:30 | 45009.3125 | 0 | 11.9905 | 37.78
2023-03-24 08:00 | 45009.3333 | 0 | 12.4273 | 37.78
2023-03-24 08:30 | 45009.3542 | 0 | 11.201 | 37.78
2023-03-24 09:00 | 45009.375 | 0 | 11.198 | 37.78
2023-03-24 09:30 | 45009.3958 | 0 | 11.2259 | 37.78
2023-03-24 10:00 | 45009.4167 | 0 | 11.3562 | 37.78
2023-03-24 10:30 | 45009.4375 | 0 | 11.4456 | 37.78
2023-03-24 11:00 | 45009.4583 | 0 | 11.8202 | 37.78
2023-03-24 11:30 | 45009.4792 | 0 | 12.0745 | 37.78
2023-03-24 12:00 | 45009.5 | 0 | 12.1435 | 37.78
2023-03-24 12:30 | 45009.5208 | 0 | 12.471 | 37.78
2023-03-24 13:00 | 45009.5417 | 0 | 13.0873 | 37.78
2023-03-24 13:30 | 45009.5625 | 0 | 13.6861 | 37.78
2023-03-24 14:00 | 45009.5833 | 0 | 14.2376 | 37.78
2023-03-24 14:30 | 45009.6042 | 0 | 14.8856 | 37.78
2023-03-24 15:00 | 45009.625 | 0 | 15.8243 | 37.78
2023-03-24 15:30 | 45009.6458 | 0 | 16.9646 | 37.78
2023-03-24 16:00 | 45009.6667 | 0 | 17.8079 | 37.78
2023-03-24 16:30 | 45009.6875 | 0 | 18.3281 | 37.78
2023-03-24 17:00 | 45009.7083 | 0 | 18.1528 | 37.78
2023-03-24 17:30 | 45009.7292 | 0 | 17.6688 | 37.78
2023-03-24 18:00 | 45009.75 | 0 | 17.371 | 37.78
2023-03-24 18:30 | 45009.7708 | 0 | 17.2985 | 37.78
2023-03-24 19:00 | 45009.7917 | 0 | 17.3208 | 37.78
2023-03-24 19:30 | 45009.8125 | 0 | 17.0081 | 37.78
2023-03-24 20:00 | 45009.8333 | 0 | 16.6456 | 37.78
2023-03-24 20:30 | 45009.8542 | 0 | 16.0885 | 37.78
2023-03-24 21:00 | 45009.875 | 0 | 15.6736 | 37.78
2023-03-24 21:30 | 45009.8958 | 0 | 15.1199 | 37.78
2023-03-24 22:00 | 45009.9167 | 0 | 14.54 | 37.78
2023-03-24 22:30 | 45009.9375 | 0 | 13.6898 | 37.78
2023-03-24 23:00 | 45009.9583 | 0 | 13.2134 | 37.78
2023-03-24 23:30 | 45009.9792 | 0 | 12.5814 | 37.78
2023-03-25 | 45010 | 0 | 12.0706 | 37.78
2023-03-25 00:30 | 45010.0208 | 0 | 11.5136 | 37.78
2023-03-25 01:00 | 45010.0417 | 0 | 11.2345 | 37.78
2023-03-25 01:30 | 45010.0625 | 0 | 10.8928 | 37.78
2023-03-25 02:00 | 45010.0833 | 0 | 10.6619 | 37.78
2023-03-25 02:30 | 45010.1042 | 0 | 10.3001 | 37.78
2023-03-25 03:00 | 45010.125 | 0 | 10.3661 | 37.78
2023-03-25 03:30 | 45010.1458 | 0 | 10.3864 | 37.78
2023-03-25 04:00 | 45010.1667 | 0 | 10.2414 | 37.78
2023-03-25 04:30 | 45010.1875 | 0 | 10.2489 | 37.78
2023-03-25 05:00 | 45010.2083 | 0 | 10.3085 | 37.78
2023-03-25 05:30 | 45010.2292 | 0 | 10.4033 | 37.78
2023-03-25 06:00 | 45010.25 | 0 | 10.4982 | 37.78
2023-03-25 06:30 | 45010.2708 | 0 | 10.1873 | 37.78
2023-03-25 07:00 | 45010.2917 | 0 | 10.2006 | 37.78
2023-03-25 07:30 | 45010.3125 | 0 | 9.8889 | 37.78
2023-03-25 08:00 | 45010.3333 | 0 | 10.5761 | 37.78
2023-03-25 08:30 | 45010.3542 | 0 | 10.0241 | 37.78
2023-03-25 09:00 | 45010.375 | 0 | 11.2312 | 37.78
2023-03-25 09:30 | 45010.3958 | 0 | 10.9932 | 37.78
2023-03-25 10:00 | 45010.4167 | 0 | 11.6714 | 37.78
2023-03-25 10:30 | 45010.4375 | 0 | 12.0007 | 37.78
2023-03-25 11:00 | 45010.4583 | 0 | 11.4277 | 37.78
2023-03-25 11:30 | 45010.4792 | 0 | 12.5413 | 37.78
2023-03-25 12:00 | 45010.5 | 0 | 13.4385 | 37.78
2023-03-25 12:30 | 45010.5208 | 0 | 12.2371 | 37.78
2023-03-25 13:00 | 45010.5417 | 0 | 11.4614 | 37.78
2023-03-25 13:30 | 45010.5625 | 0 | 14.8246 | 37.78
2023-03-25 14:00 | 45010.5833 | 0 | 16.0553 | 37.78
2023-03-25 14:30 | 45010.6042 | 0 | 14.8267 | 37.78
2023-03-25 15:00 | 45010.625 | 0 | 13.6984 | 37.78
2023-03-25 15:30 | 45010.6458 | 0 | 14.3646 | 37.78
2023-03-25 16:00 | 45010.6667 | 0 | 15.2607 | 37.78
2023-03-25 16:30 | 45010.6875 | 0 | 14.6527 | 37.78
2023-03-25 17:00 | 45010.7083 | 0 | 15.1991 | 37.78
2023-03-25 17:30 | 45010.7292 | 0 | 15.0038 | 37.78
2023-03-25 18:00 | 45010.75 | 0 | 14.9052 | 37.78
2023-03-25 18:30 | 45010.7708 | 0 | 15.1061 | 37.78
2023-03-25 19:00 | 45010.7917 | 0 | 14.9609 | 37.78
2023-03-25 19:30 | 45010.8125 | 0 | 14.6679 | 37.78
2023-03-25 20:00 | 45010.8333 | 0 | 14.5683 | 37.78
2023-03-25 20:30 | 45010.8542 | 0 | 13.9825 | 37.78
2023-03-25 21:00 | 45010.875 | 0 | 13.8497 | 37.78
2023-03-25 21:30 | 45010.8958 | 0 | 13.2629 | 37.78
2023-03-25 22:00 | 45010.9167 | 0 | 12.6376 | 37.78
2023-03-25 22:30 | 45010.9375 | 0 | 12.1153 | 37.78
2023-03-25 23:00 | 45010.9583 | 0 | 11.5215 | 37.78
2023-03-25 23:30 | 45010.9792 | 0 | 11.0313 | 37.78
2023-03-26 | 45011 | 0 | 10.4137 | 37.78
2023-03-26 00:30 | 45011.0208 | 0 | 10.0235 | 37.78
2023-03-26 01:00 | 45011.0417 | 0 | 9.7799 | 37.78
2023-03-26 01:30 | 45011.0625 | 0 | 9.5061 | 37.78
2023-03-26 02:00 | 45011.0833 | 0 | 9.3945 | 37.78
2023-03-26 02:30 | 45011.1042 | 0 | 9.2271 | 37.78
2023-03-26 03:00 | 45011.125 | 0 | 9.2494 | 37.78
2023-03-26 03:30 | 45011.1458 | 0 | 9.1548 | 37.78
2023-03-26 04:00 | 45011.1667 | 0 | 8.9461 | 37.78
2023-03-26 04:30 | 45011.1875 | 0 | 8.881 | 37.78
2023-03-26 05:00 | 45011.2083 | 0 | 8.8624 | 37.78
2023-03-26 05:30 | 45011.2292 | 0 | 8.9126 | 37.78
2023-03-26 06:00 | 45011.25 | 0 | 11.0248 | 37.78
2023-03-26 06:30 | 45011.2708 | 0 | 16.8071 | 37.78
2023-03-26 07:00 | 45011.2917 | 0 | 16.2899 | 37.78
2023-03-26 07:30 | 45011.3125 | 0 | 15.7402 | 37.78
2023-03-26 08:00 | 45011.3333 | 0 | 15.6049 | 37.78
2023-03-26 08:30 | 45011.3542 | 0 | 15.4076 | 37.78
2023-03-26 09:00 | 45011.375 | 0 | 16.2174 | 37.78
2023-03-26 09:30 | 45011.3958 | 0 | 17.4384 | 37.78
2023-03-26 10:00 | 45011.4167 | 0 | 22.0656 | 37.78
2023-03-26 10:30 | 45011.4375 | 0 | 25.6868 | 37.78
2023-03-26 11:00 | 45011.4583 | 0 | 25.5113 | 37.78
2023-03-26 11:30 | 45011.4792 | 0 | 24.5548 | 37.78
2023-03-26 12:00 | 45011.5 | 0 | 23.3554 | 37.78
2023-03-26 12:30 | 45011.5208 | 0 | 21.9289 | 37.78
2023-03-26 13:00 | 45011.5417 | 0 | 18.7322 | 37.78
2023-03-26 13:30 | 45011.5625 | 0 | 17.7142 | 37.78
2023-03-26 14:00 | 45011.5833 | 0 | 19.2999 | 37.78
2023-03-26 14:30 | 45011.6042 | 0 | 21.814 | 37.78
2023-03-26 15:00 | 45011.625 | 0 | 19.7643 | 37.78
2023-03-26 15:30 | 45011.6458 | 0 | 20.7866 | 37.78
2023-03-26 16:00 | 45011.6667 | 0 | 12.9861 | 37.78
2023-03-26 16:30 | 45011.6875 | 0 | 13.0275 | 37.78
2023-03-26 17:00 | 45011.7083 | 0 | 13.7921 | 37.78
2023-03-26 17:30 | 45011.7292 | 0 | 14.4252 | 37.78
2023-03-26 18:00 | 45011.75 | 0 | 14.6056 | 37.78
2023-03-26 18:30 | 45011.7708 | 0 | 14.8717 | 37.78
2023-03-26 19:00 | 45011.7917 | 0 | 14.5476 | 37.78
2023-03-26 19:30 | 45011.8125 | 0 | 14.0005 | 37.78
2023-03-26 20:00 | 45011.8333 | 0 | 13.7549 | 37.78
2023-03-26 20:30 | 45011.8542 | 0 | 13.1131 | 37.78
2023-03-26 21:00 | 45011.875 | 0 | 12.7934 | 37.78
2023-03-26 21:30 | 45011.8958 | 0 | 12.037 | 37.78
2023-03-26 22:00 | 45011.9167 | 0 | 11.6687 | 37.78
2023-03-26 22:30 | 45011.9375 | 0 | 10.8926 | 37.78
2023-03-26 23:00 | 45011.9583 | 0 | 10.5359 | 37.78
2023-03-26 23:30 | 45011.9792 | 0 | 9.9786 | 37.78
2023-03-27 | 45012 | 0 | 9.6239 | 37.78
2023-03-27 00:30 | 45012.0208 | 0 | 9.5415 | 37.78
2023-03-27 01:00 | 45012.0417 | 0 | 9.3052 | 37.78
2023-03-27 01:30 | 45012.0625 | 0 | 9.2662 | 37.78
2023-03-27 02:00 | 45012.0833 | 0 | 9.0366 | 37.78
2023-03-27 02:30 | 45012.1042 | 0 | 8.9684 | 37.78
2023-03-27 03:00 | 45012.125 | 0 | 8.9515 | 37.78
2023-03-27 03:30 | 45012.1458 | 0 | 9.0392 | 37.78
2023-03-27 04:00 | 45012.1667 | 0 | 9.4809 | 37.78
2023-03-27 04:30 | 45012.1875 | 0 | 9.8415 | 37.78
2023-03-27 05:00 | 45012.2083 | 0 | 10.5719 | 37.78
2023-03-27 05:30 | 45012.2292 | 0 | 11.0977 | 37.78
2023-03-27 06:00 | 45012.25 | 0 | 11.9732 | 37.78
2023-03-27 06:30 | 45012.2708 | 0 | 12.5065 | 37.78
2023-03-27 07:00 | 45012.2917 | 0 | 12.7482 | 37.78
2023-03-27 07:30 | 45012.3125 | 0 | 12.6308 | 37.78
2023-03-27 08:00 | 45012.3333 | 0 | 12.6925 | 37.78
2023-03-27 08:30 | 45012.3542 | 0 | 12.8427 | 37.78
2023-03-27 09:00 | 45012.375 | 0 | 12.8336 | 37.78
2023-03-27 09:30 | 45012.3958 | 0 | 12.748 | 37.78
2023-03-27 10:00 | 45012.4167 | 0 | 14.1477 | 37.78
2023-03-27 10:30 | 45012.4375 | 0 | 14.1204 | 37.78
2023-03-27 11:00 | 45012.4583 | 0 | 13.689 | 37.78
2023-03-27 11:30 | 45012.4792 | 0 | 13.7666 | 37.78
2023-03-27 12:00 | 45012.5 | 0 | 13.3031 | 37.78
2023-03-27 12:30 | 45012.5208 | 0 | 15.0808 | 37.78
2023-03-27 13:00 | 45012.5417 | 0 | 14.3647 | 37.78
2023-03-27 13:30 | 45012.5625 | 0 | 14.2817 | 37.78
2023-03-27 14:00 | 45012.5833 | 0 | 14.7858 | 37.78
2023-03-27 14:30 | 45012.6042 | 0 | 16.2438 | 37.78
2023-03-27 15:00 | 45012.625 | 0 | 16.45 | 37.78
2023-03-27 15:30 | 45012.6458 | 0 | 17.7223 | 37.78
2023-03-27 16:00 | 45012.6667 | 0 | 18.46 | 37.78
2023-03-27 16:30 | 45012.6875 | 0 | 18.7633 | 37.78
2023-03-27 17:00 | 45012.7083 | 0 | 18.7689 | 37.78
2023-03-27 17:30 | 45012.7292 | 0 | 18.5289 | 37.78
2023-03-27 18:00 | 45012.75 | 0 | 18.4708 | 37.78
2023-03-27 18:30 | 45012.7708 | 0 | 18.7092 | 37.78
2023-03-27 19:00 | 45012.7917 | 0 | 18.5231 | 37.78
2023-03-27 19:30 | 45012.8125 | 0 | 18.127 | 37.78
2023-03-27 20:00 | 45012.8333 | 0 | 17.4096 | 37.78
2023-03-27 20:30 | 45012.8542 | 0 | 16.8446 | 37.78
2023-03-27 21:00 | 45012.875 | 0 | 16.234 | 37.78
2023-03-27 21:30 | 45012.8958 | 0 | 15.4852 | 37.78
2023-03-27 22:00 | 45012.9167 | 0 | 14.5534 | 37.78
2023-03-27 22:30 | 45012.9375 | 0 | 13.4477 | 37.78
2023-03-27 23:00 | 45012.9583 | 0 | 12.8335 | 37.78
2023-03-27 23:30 | 45012.9792 | 0 | 12.2201 | 37.78
2023-03-28 | 45013 | 0 | 11.7606 | 37.78
2023-03-28 00:30 | 45013.0208 | 0 | 11.1445 | 37.78
2023-03-28 01:00 | 45013.0417 | 0 | 10.9186 | 37.78
2023-03-28 01:30 | 45013.0625 | 0 | 10.6005 | 37.78
2023-03-28 02:00 | 45013.0833 | 0 | 10.3656 | 37.78
2023-03-28 02:30 | 45013.1042 | 0 | 10.1967 | 37.78
2023-03-28 03:00 | 45013.125 | 0 | 10.2078 | 37.78
2023-03-28 03:30 | 45013.1458 | 0 | 10.2546 | 37.78
2023-03-28 04:00 | 45013.1667 | 0 | 10.5226 | 37.78
2023-03-28 04:30 | 45013.1875 | 0 | 10.7904 | 37.78
2023-03-28 05:00 | 45013.2083 | 0 | 11.321 | 37.78
2023-03-28 05:30 | 45013.2292 | 0 | 11.8589 | 37.78
2023-03-28 06:00 | 45013.25 | 0 | 12.3943 | 37.78
2023-03-28 06:30 | 45013.2708 | 0 | 13.2991 | 37.78
2023-03-28 07:00 | 45013.2917 | 0 | 13.8277 | 37.78
2023-03-28 07:30 | 45013.3125 | 0 | 13.5869 | 37.78
2023-03-28 08:00 | 45013.3333 | 0 | 14.5962 | 37.78
2023-03-28 08:30 | 45013.3542 | 0 | 15.1889 | 37.78
2023-03-28 09:00 | 45013.375 | 0 | 12.4449 | 37.78
2023-03-28 09:30 | 45013.3958 | 0 | 13.6483 | 37.78
2023-03-28 10:00 | 45013.4167 | 0 | 14.0137 | 37.78
2023-03-28 10:30 | 45013.4375 | 0 | 13.9092 | 37.78
2023-03-28 11:00 | 45013.4583 | 0 | 15.9844 | 37.78
2023-03-28 11:30 | 45013.4792 | 0 | 15.854 | 37.78
2023-03-28 12:00 | 45013.5 | 0 | 14.5028 | 37.78
2023-03-28 12:30 | 45013.5208 | 0 | 16.2333 | 37.78
2023-03-28 13:00 | 45013.5417 | 0 | 16.9067 | 37.78
2023-03-28 13:30 | 45013.5625 | 0 | 16.9771 | 37.78
2023-03-28 14:00 | 45013.5833 | 0 | 16.9252 | 37.78
2023-03-28 14:30 | 45013.6042 | 0 | 16.6298 | 37.78
2023-03-28 15:00 | 45013.625 | 0 | 18.4762 | 37.78
2023-03-28 15:30 | 45013.6458 | 0 | 18.581 | 37.78
2023-03-28 16:00 | 45013.6667 | 0 | 18.1036 | 37.78
2023-03-28 16:30 | 45013.6875 | 0 | 17.8577 | 37.78
2023-03-28 17:00 | 45013.7083 | 0 | 18.646 | 37.78
2023-03-28 17:30 | 45013.7292 | 0 | 18.9809 | 37.78
2023-03-28 18:00 | 45013.75 | 0 | 19.1127 | 37.78
2023-03-28 18:30 | 45013.7708 | 0 | 19.4534 | 37.78
2023-03-28 19:00 | 45013.7917 | 0 | 19.2824 | 37.78
2023-03-28 19:30 | 45013.8125 | 0 | 18.7662 | 37.78
2023-03-28 20:00 | 45013.8333 | 0 | 18.5669 | 37.78
2023-03-28 20:30 | 45013.8542 | 0 | 17.6604 | 37.78
2023-03-28 21:00 | 45013.875 | 0 | 17.0678 | 37.78
2023-03-28 21:30 | 45013.8958 | 0 | 15.9974 | 37.78
2023-03-28 22:00 | 45013.9167 | 0 | 14.9569 | 37.78
2023-03-28 22:30 | 45013.9375 | 0 | 13.946 | 37.78
2023-03-28 23:00 | 45013.9583 | 0 | 13.0149 | 37.78
2023-03-28 23:30 | 45013.9792 | 0 | 12.6329 | 37.78
2023-03-29 | 45014 | 0 | 12.0119 | 37.78
2023-03-29 00:30 | 45014.0208 | 0 | 11.5813 | 37.78
2023-03-29 01:00 | 45014.0417 | 0 | 11.3597 | 37.78
2023-03-29 01:30 | 45014.0625 | 0 | 11.0427 | 37.78
2023-03-29 02:00 | 45014.0833 | 0 | 10.9876 | 37.78
2023-03-29 02:30 | 45014.1042 | 0 | 10.7569 | 37.78
2023-03-29 03:00 | 45014.125 | 0 | 10.8089 | 37.78
2023-03-29 03:30 | 45014.1458 | 0 | 10.9562 | 37.78
2023-03-29 04:00 | 45014.1667 | 0 | 11.2056 | 37.78
2023-03-29 04:30 | 45014.1875 | 0 | 11.7067 | 37.78
2023-03-29 05:00 | 45014.2083 | 0 | 12.2179 | 37.78
2023-03-29 05:30 | 45014.2292 | 0 | 12.7019 | 37.78
2023-03-29 06:00 | 45014.25 | 0 | 13.6665 | 37.78
2023-03-29 06:30 | 45014.2708 | 0 | 14.4177 | 37.78
2023-03-29 07:00 | 45014.2917 | 0 | 15.3829 | 37.78
2023-03-29 07:30 | 45014.3125 | 0 | 15.7822 | 37.78
2023-03-29 08:00 | 45014.3333 | 0 | 15.8265 | 37.78
2023-03-29 08:30 | 45014.3542 | 0 | 15.8468 | 37.78
2023-03-29 09:00 | 45014.375 | 0 | 15.7437 | 37.78
2023-03-29 09:30 | 45014.3958 | 0 | 15.4223 | 37.78
2023-03-29 10:00 | 45014.4167 | 0 | 16.579 | 37.78
2023-03-29 10:30 | 45014.4375 | 0 | 16.4004 | 37.78
2023-03-29 11:00 | 45014.4583 | 0 | 16.0855 | 37.78
2023-03-29 11:30 | 45014.4792 | 0 | 14.5399 | 37.78
2023-03-29 12:00 | 45014.5 | 0 | 14.9254 | 37.78
2023-03-29 12:30 | 45014.5208 | 0 | 16.3953 | 37.78
2023-03-29 13:00 | 45014.5417 | 0 | 16.092 | 37.78
2023-03-29 13:30 | 45014.5625 | 0 | 16.1039 | 37.78
2023-03-29 14:00 | 45014.5833 | 0 | 16.0291 | 37.78
2023-03-29 14:30 | 45014.6042 | 0 | 15.376 | 37.78
2023-03-29 15:00 | 45014.625 | 0 | 15.2215 | 37.78
2023-03-29 15:30 | 45014.6458 | 0 | 16.1163 | 37.78
2023-03-29 16:00 | 45014.6667 | 0 | 16.0535 | 37.78
2023-03-29 16:30 | 45014.6875 | 0 | 16.2694 | 37.78
2023-03-29 17:00 | 45014.7083 | 0 | 15.9509 | 37.78
2023-03-29 17:30 | 45014.7292 | 0 | 16.26 | 37.78
2023-03-29 18:00 | 45014.75 | 0 | 16.5374 | 37.78
2023-03-29 18:30 | 45014.7708 | 0 | 17.0084 | 37.78
2023-03-29 19:00 | 45014.7917 | 0 | 17.0005 | 37.78
2023-03-29 19:30 | 45014.8125 | 0 | 16.7253 | 37.78
2023-03-29 20:00 | 45014.8333 | 0 | 16.2819 | 37.78
2023-03-29 20:30 | 45014.8542 | 0 | 15.6682 | 37.78
2023-03-29 21:00 | 45014.875 | 0 | 15.296 | 37.78
2023-03-29 21:30 | 45014.8958 | 0 | 14.6744 | 37.78
2023-03-29 22:00 | 45014.9167 | 0 | 13.8749 | 37.78
2023-03-29 22:30 | 45014.9375 | 0 | 13.1584 | 37.78
2023-03-29 23:00 | 45014.9583 | 0 | 12.5413 | 37.78
2023-03-29 23:30 | 45014.9792 | 0 | 12.0107 | 37.78
2023-03-30 | 45015 | 0 | 11.3837 | 37.78
2023-03-30 00:30 | 45015.0208 | 0 | 10.8833 | 37.78
2023-03-30 01:00 | 45015.0417 | 0 | 10.8499 | 37.78
2023-03-30 01:30 | 45015.0625 | 0 | 10.498 | 37.78
2023-03-30 02:00 | 45015.0833 | 0 | 10.4584 | 37.78
2023-03-30 02:30 | 45015.1042 | 0 | 10.3213 | 37.78
2023-03-30 03:00 | 45015.125 | 0 | 10.3458 | 37.78
2023-03-30 03:30 | 45015.1458 | 0 | 10.4963 | 37.78
2023-03-30 04:00 | 45015.1667 | 0 | 10.4181 | 37.78
2023-03-30 04:30 | 45015.1875 | 0 | 10.4425 | 37.78
2023-03-30 05:00 | 45015.2083 | 0 | 10.9052 | 37.78
2023-03-30 05:30 | 45015.2292 | 0 | 11.4779 | 37.78
2023-03-30 06:00 | 45015.25 | 0 | 12.7157 | 37.78
2023-03-30 06:30 | 45015.2708 | 0 | 13.248 | 37.78
2023-03-30 07:00 | 45015.2917 | 0 | 14.2149 | 37.78
2023-03-30 07:30 | 45015.3125 | 0 | 13.5288 | 37.78
2023-03-30 08:00 | 45015.3333 | 0 | 12.9021 | 37.78
2023-03-30 08:30 | 45015.3542 | 0 | 13.2678 | 37.78
2023-03-30 09:00 | 45015.375 | 0 | 11.4728 | 37.78
2023-03-30 09:30 | 45015.3958 | 0 | 11.5548 | 37.78
2023-03-30 10:00 | 45015.4167 | 0 | 13.9966 | 37.78
2023-03-30 10:30 | 45015.4375 | 0 | 12.1805 | 37.78
2023-03-30 11:00 | 45015.4583 | 0 | 11.5534 | 37.78
2023-03-30 11:30 | 45015.4792 | 0 | 11.4921 | 37.78
2023-03-30 12:00 | 45015.5 | 0 | 12.4645 | 37.78
2023-03-30 12:30 | 45015.5208 | 0 | 13.8338 | 37.78
2023-03-30 13:00 | 45015.5417 | 0 | 12.5214 | 37.78
2023-03-30 13:30 | 45015.5625 | 0 | 12.7912 | 37.78
2023-03-30 14:00 | 45015.5833 | 0 | 14.6096 | 37.78
2023-03-30 14:30 | 45015.6042 | 0 | 15.7115 | 37.78
2023-03-30 15:00 | 45015.625 | 0 | 15.9306 | 37.78
2023-03-30 15:30 | 45015.6458 | 0 | 15.7886 | 37.78
2023-03-30 16:00 | 45015.6667 | 0 | 16.4625 | 37.78
2023-03-30 16:30 | 45015.6875 | 0 | 16.7104 | 37.78
2023-03-30 17:00 | 45015.7083 | 0 | 16.6062 | 37.78
2023-03-30 17:30 | 45015.7292 | 0 | 16.5446 | 37.78
2023-03-30 18:00 | 45015.75 | 0 | 16.2935 | 37.78
2023-03-30 18:30 | 45015.7708 | 0 | 16.3885 | 37.78
2023-03-30 19:00 | 45015.7917 | 0 | 16.0534 | 37.78
2023-03-30 19:30 | 45015.8125 | 0 | 15.4639 | 37.78
2023-03-30 20:00 | 45015.8333 | 0 | 15.1914 | 37.78
2023-03-30 20:30 | 45015.8542 | 0 | 14.5234 | 37.78
2023-03-30 21:00 | 45015.875 | 0 | 13.9559 | 37.78
2023-03-30 21:30 | 45015.8958 | 0 | 13.2052 | 37.78
2023-03-30 22:00 | 45015.9167 | 0 | 12.25 | 37.78
2023-03-30 22:30 | 45015.9375 | 0 | 11.4973 | 37.78
2023-03-30 23:00 | 45015.9583 | 0 | 11.0251 | 37.78
2023-03-30 23:30 | 45015.9792 | 0 | 10.5168 | 37.78
2023-03-31 | 45016 | 0 | 9.9788 | 37.78
2023-03-31 00:30 | 45016.0208 | 0 | 9.5769 | 37.78
2023-03-31 01:00 | 45016.0417 | 0 | 9.3591 | 37.78
2023-03-31 01:30 | 45016.0625 | 0 | 9.0334 | 37.78
2023-03-31 02:00 | 45016.0833 | 0 | 8.9534 | 37.78
2023-03-31 02:30 | 45016.1042 | 0 | 8.8213 | 37.78
2023-03-31 03:00 | 45016.125 | 0 | 8.8717 | 37.78
2023-03-31 03:30 | 45016.1458 | 0 | 8.9312 | 37.78
2023-03-31 04:00 | 45016.1667 | 0 | 9.1119 | 37.78
2023-03-31 04:30 | 45016.1875 | 0 | 9.2309 | 37.78
2023-03-31 05:00 | 45016.2083 | 0 | 9.8689 | 37.78
2023-03-31 05:30 | 45016.2292 | 0 | 10.473 | 37.78
2023-03-31 06:00 | 45016.25 | 0 | 11.0769 | 37.78
2023-03-31 06:30 | 45016.2708 | 0 | 11.3135 | 37.78
2023-03-31 07:00 | 45016.2917 | 0 | 11.2592 | 37.78
2023-03-31 07:30 | 45016.3125 | 0 | 10.6773 | 37.78
2023-03-31 08:00 | 45016.3333 | 0 | 10.4329 | 37.78
2023-03-31 08:30 | 45016.3542 | 0 | 10.2561 | 37.78
2023-03-31 09:00 | 45016.375 | 0 | 10.5529 | 37.78
2023-03-31 09:30 | 45016.3958 | 0 | 10.3129 | 37.78
2023-03-31 10:00 | 45016.4167 | 0 | 9.5775 | 37.78
2023-03-31 10:30 | 45016.4375 | 0 | 9.5632 | 37.78
2023-03-31 11:00 | 45016.4583 | 0 | 9.5321 | 37.78
2023-03-31 11:30 | 45016.4792 | 0 | 10.01 | 37.78
2023-03-31 12:00 | 45016.5 | 0 | 9.267 | 37.78
2023-03-31 12:30 | 45016.5208 | 0 | 9.5332 | 37.78
2023-03-31 13:00 | 45016.5417 | 0 | 9.5605 | 37.78
2023-03-31 13:30 | 45016.5625 | 0 | 10.211 | 37.78
2023-03-31 14:00 | 45016.5833 | 0 | 10.9359 | 37.78
2023-03-31 14:30 | 45016.6042 | 0 | 11.4728 | 37.78
2023-03-31 15:00 | 45016.625 | 0 | 12.441 | 37.78
2023-03-31 15:30 | 45016.6458 | 0 | 13.047 | 37.78
2023-03-31 16:00 | 45016.6667 | 0 | 13.7835 | 37.78
2023-03-31 16:30 | 45016.6875 | 0 | 14.7661 | 37.78
2023-03-31 17:00 | 45016.7083 | 0 | 14.7064 | 37.78
2023-03-31 17:30 | 45016.7292 | 0 | 14.3711 | 37.78
2023-03-31 18:00 | 45016.75 | 0 | 14.2332 | 37.78
2023-03-31 18:30 | 45016.7708 | 0 | 14.223 | 37.78
2023-03-31 19:00 | 45016.7917 | 0 | 14.1851 | 37.78
2023-03-31 19:30 | 45016.8125 | 0 | 13.9521 | 37.78
2023-03-31 20:00 | 45016.8333 | 0 | 13.5985 | 37.78
2023-03-31 20:30 | 45016.8542 | 0 | 13.261 | 37.78
2023-03-31 21:00 | 45016.875 | 0 | 13.0164 | 37.78
2023-03-31 21:30 | 45016.8958 | 0 | 12.387 | 37.78
2023-03-31 22:00 | 45016.9167 | 0 | 11.7549 | 37.78
2023-03-31 22:30 | 45016.9375 | 0 | 11.0049 | 37.78
2023-03-31 23:00 | 45016.9583 | 0 | 10.7866 | 37.78
2023-03-31 23:30 | 45016.9792 | 0 | 10.4215 | 37.78
2023-04-01 | 45017 | 0 | 9.9123 | 37.78
2023-04-01 00:30 | 45017.0208 | 0 | 9.7129 | 37.78
2023-04-01 01:00 | 45017.0417 | 0 | 9.5601 | 37.78
2023-04-01 01:30 | 45017.0625 | 0 | 9.19 | 37.78
2023-04-01 02:00 | 45017.0833 | 0 | 9.0372 | 37.78
2023-04-01 02:30 | 45017.1042 | 0 | 8.8864 | 37.78
2023-04-01 03:00 | 45017.125 | 0 | 8.8251 | 37.78
2023-04-01 03:30 | 45017.1458 | 0 | 8.7599 | 37.78
2023-04-01 04:00 | 45017.1667 | 0 | 8.7359 | 37.78
2023-04-01 04:30 | 45017.1875 | 0 | 8.7711 | 37.78
2023-04-01 05:00 | 45017.2083 | 0 | 8.881 | 37.78
2023-04-01 05:30 | 45017.2292 | 0 | 9.1026 | 37.78
2023-04-01 06:00 | 45017.25 | 0 | 9.3574 | 37.78
2023-04-01 06:30 | 45017.2708 | 0 | 9.4709 | 37.78
2023-04-01 07:00 | 45017.2917 | 0 | 9.8226 | 37.78
2023-04-01 07:30 | 45017.3125 | 0 | 9.9026 | 37.78
2023-04-01 08:00 | 45017.3333 | 0 | 9.7257 | 37.78
2023-04-01 08:30 | 45017.3542 | 0 | 9.4775 | 37.78
2023-04-01 09:00 | 45017.375 | 0 | 9.6781 | 37.78
2023-04-01 09:30 | 45017.3958 | 0 | 9.4262 | 37.78
2023-04-01 10:00 | 45017.4167 | 0 | 9.6491 | 37.78
2023-04-01 10:30 | 45017.4375 | 0 | 10.4421 | 37.78
2023-04-01 11:00 | 45017.4583 | 0 | 8.9037 | 37.78
2023-04-01 11:30 | 45017.4792 | 0 | 9.3811 | 37.78
2023-04-01 12:00 | 45017.5 | 0 | 9.2962 | 37.78
2023-04-01 12:30 | 45017.5208 | 0 | 9.6427 | 37.78
2023-04-01 13:00 | 45017.5417 | 0 | 9.0723 | 37.78
2023-04-01 13:30 | 45017.5625 | 0 | 9.2534 | 37.78
2023-04-01 14:00 | 45017.5833 | 0 | 9.3962 | 37.78
2023-04-01 14:30 | 45017.6042 | 0 | 9.7997 | 37.78
2023-04-01 15:00 | 45017.625 | 0 | 10.6229 | 37.78
2023-04-01 15:30 | 45017.6458 | 0 | 10.4873 | 37.78
2023-04-01 16:00 | 45017.6667 | 0 | 10.8861 | 37.78
2023-04-01 16:30 | 45017.6875 | 0 | 11.1049 | 37.78
2023-04-01 17:00 | 45017.7083 | 0 | 11.4919 | 37.78
2023-04-01 17:30 | 45017.7292 | 0 | 11.7211 | 37.78
2023-04-01 18:00 | 45017.75 | 0 | 11.8755 | 37.78
2023-04-01 18:30 | 45017.7708 | 0 | 11.892 | 37.78
2023-04-01 19:00 | 45017.7917 | 0 | 11.5515 | 37.78
2023-04-01 19:30 | 45017.8125 | 0 | 11.559 | 37.78
2023-04-01 20:00 | 45017.8333 | 0 | 11.3638 | 37.78
2023-04-01 20:30 | 45017.8542 | 0 | 10.9559 | 37.78
2023-04-01 21:00 | 45017.875 | 0 | 10.7542 | 37.78
2023-04-01 21:30 | 45017.8958 | 0 | 10.5167 | 37.78
2023-04-01 22:00 | 45017.9167 | 0 | 9.9815 | 37.78
2023-04-01 22:30 | 45017.9375 | 0 | 9.495 | 37.78
2023-04-01 23:00 | 45017.9583 | 0 | 9.1173 | 37.78
2023-04-01 23:30 | 45017.9792 | 0 | 8.6959 | 37.78
2023-04-02 | 45018 | 0 | 8.3187 | 37.78
2023-04-02 00:30 | 45018.0208 | 0 | 8.0639 | 37.78
2023-04-02 01:00 | 45018.0417 | 0 | 7.9895 | 37.78
2023-04-02 01:30 | 45018.0625 | 0 | 7.749 | 37.78
2023-04-02 02:00 | 45018.0833 | 0 | 7.7736 | 37.78
2023-04-02 02:30 | 45018.1042 | 0 | 7.7345 | 37.78
2023-04-02 03:00 | 45018.125 | 0 | 7.7066 | 37.78
2023-04-02 03:30 | 45018.1458 | 0 | 7.6359 | 37.78
2023-04-02 04:00 | 45018.1667 | 0 | 7.6955 | 37.78
2023-04-02 04:30 | 45018.1875 | 0 | 7.6601 | 37.78
2023-04-02 05:00 | 45018.2083 | 0 | 7.6824 | 37.78
2023-04-02 05:30 | 45018.2292 | 0 | 7.7922 | 37.78
2023-04-02 06:00 | 45018.25 | 0 | 8.134 | 37.78
2023-04-02 06:30 | 45018.2708 | 0 | 14.6638 | 37.78
2023-04-02 07:00 | 45018.2917 | 0 | 14.2941 | 37.78
2023-04-02 07:30 | 45018.3125 | 0 | 13.6256 | 37.78
2023-04-02 08:00 | 45018.3333 | 0 | 12.8232 | 37.78
2023-04-02 08:30 | 45018.3542 | 0 | 12.9865 | 37.78
2023-04-02 09:00 | 45018.375 | 0 | 12.1379 | 37.78
2023-04-02 09:30 | 45018.3958 | 0 | 10.2059 | 37.78
2023-04-02 10:00 | 45018.4167 | 0 | 10.7733 | 37.78
2023-04-02 10:30 | 45018.4375 | 0 | 11.0603 | 37.78
2023-04-02 11:00 | 45018.4583 | 0 | 13.4509 | 37.78
2023-04-02 11:30 | 45018.4792 | 0 | 15.5783 | 37.78
2023-04-02 12:00 | 45018.5 | 0 | 16.2268 | 37.78
2023-04-02 12:30 | 45018.5208 | 0 | 13.3241 | 37.78
2023-04-02 13:00 | 45018.5417 | 0 | 10.6879 | 37.78
2023-04-02 13:30 | 45018.5625 | 0 | 14.2085 | 37.78
2023-04-02 14:00 | 45018.5833 | 0 | 14.5315 | 37.78
2023-04-02 14:30 | 45018.6042 | 0 | 15.0278 | 37.78
2023-04-02 15:00 | 45018.625 | 0 | 16.9333 | 37.78
2023-04-02 15:30 | 45018.6458 | 0 | 21.4444 | 37.78
2023-04-02 16:00 | 45018.6667 | 0 | 21.5786 | 37.78
2023-04-02 16:30 | 45018.6875 | 0 | 15.6985 | 37.78
2023-04-02 17:00 | 45018.7083 | 0 | 11.9368 | 37.78
2023-04-02 17:30 | 45018.7292 | 0 | 12.0247 | 37.78
2023-04-02 18:00 | 45018.75 | 0 | 12.4953 | 37.78
2023-04-02 18:30 | 45018.7708 | 0 | 12.5525 | 37.78
2023-04-02 19:00 | 45018.7917 | 0 | 12.2419 | 37.78
2023-04-02 19:30 | 45018.8125 | 0 | 11.8405 | 37.78
2023-04-02 20:00 | 45018.8333 | 0 | 11.4963 | 37.78
2023-04-02 20:30 | 45018.8542 | 0 | 11.0473 | 37.78
2023-04-02 21:00 | 45018.875 | 0 | 10.8814 | 37.78
2023-04-02 21:30 | 45018.8958 | 0 | 10.5594 | 37.78
2023-04-02 22:00 | 45018.9167 | 0 | 9.996 | 37.78
2023-04-02 22:30 | 45018.9375 | 0 | 9.3552 | 37.78
2023-04-02 23:00 | 45018.9583 | 0 | 8.8355 | 37.78
2023-04-02 23:30 | 45018.9792 | 0 | 8.4858 | 37.78
2023-04-03 | 45019 | 0 | 8.2184 | 37.78
2023-04-03 00:30 | 45019.0208 | 0 | 8.0713 | 37.78
2023-04-03 01:00 | 45019.0417 | 0 | 7.9857 | 37.78
2023-04-03 01:30 | 45019.0625 | 0 | 8.0155 | 37.78
2023-04-03 02:00 | 45019.0833 | 0 | 7.8592 | 37.78
2023-04-03 02:30 | 45019.1042 | 0 | 7.9095 | 37.78
2023-04-03 03:00 | 45019.125 | 0 | 7.9299 | 37.78
2023-04-03 03:30 | 45019.1458 | 0 | 8.0603 | 37.78
2023-04-03 04:00 | 45019.1667 | 0 | 8.4997 | 37.78
2023-04-03 04:30 | 45019.1875 | 0 | 8.7411 | 37.78
2023-04-03 05:00 | 45019.2083 | 0 | 9.3382 | 37.78
2023-04-03 05:30 | 45019.2292 | 0 | 9.8255 | 37.78
2023-04-03 06:00 | 45019.25 | 0 | 10.8084 | 37.78
2023-04-03 06:30 | 45019.2708 | 0 | 11.0492 | 37.78
2023-04-03 07:00 | 45019.2917 | 0 | 11.0731 | 37.78
2023-04-03 07:30 | 45019.3125 | 0 | 10.5557 | 37.78
2023-04-03 08:00 | 45019.3333 | 0 | 10.2935 | 37.78
2023-04-03 08:30 | 45019.3542 | 0 | 10.0924 | 37.78
2023-04-03 09:00 | 45019.375 | 0 | 9.6664 | 37.78
2023-04-03 09:30 | 45019.3958 | 0 | 9.6874 | 37.78
2023-04-03 10:00 | 45019.4167 | 0 | 9.4558 | 37.78
2023-04-03 10:30 | 45019.4375 | 0 | 10.0381 | 37.78
2023-04-03 11:00 | 45019.4583 | 0 | 10.7682 | 37.78
2023-04-03 11:30 | 45019.4792 | 0 | 12.4101 | 37.78
2023-04-03 12:00 | 45019.5 | 0 | 11.6651 | 37.78
2023-04-03 12:30 | 45019.5208 | 0 | 11.4563 | 37.78
2023-04-03 13:00 | 45019.5417 | 0 | 11.3694 | 37.78
2023-04-03 13:30 | 45019.5625 | 0 | 9.8791 | 37.78
2023-04-03 14:00 | 45019.5833 | 0 | 11.0675 | 37.78
2023-04-03 14:30 | 45019.6042 | 0 | 11.8865 | 37.78
2023-04-03 15:00 | 45019.625 | 0 | 12.5434 | 37.78
2023-04-03 15:30 | 45019.6458 | 0 | 12.782 | 37.78
2023-04-03 16:00 | 45019.6667 | 0 | 14.048 | 37.78
2023-04-03 16:30 | 45019.6875 | 0 | 13.9633 | 37.78
2023-04-03 17:00 | 45019.7083 | 0 | 13.9452 | 37.78
2023-04-03 17:30 | 45019.7292 | 0 | 14.3079 | 37.78
2023-04-03 18:00 | 45019.75 | 0 | 14.3655 | 37.78
2023-04-03 18:30 | 45019.7708 | 0 | 14.5292 | 37.78
2023-04-03 19:00 | 45019.7917 | 0 | 14.1104 | 37.78
2023-04-03 19:30 | 45019.8125 | 0 | 13.9168 | 37.78
2023-04-03 20:00 | 45019.8333 | 0 | 13.6489 | 37.78
2023-04-03 20:30 | 45019.8542 | 0 | 12.9643 | 37.78
2023-04-03 21:00 | 45019.875 | 0 | 12.6495 | 37.78
2023-04-03 21:30 | 45019.8958 | 0 | 12.2946 | 37.78
2023-04-03 22:00 | 45019.9167 | 0 | 11.7541 | 37.78
2023-04-03 22:30 | 45019.9375 | 0 | 11.0453 | 37.78
2023-04-03 23:00 | 45019.9583 | 0 | 10.6005 | 37.78
2023-04-03 23:30 | 45019.9792 | 0 | 10.176 | 37.78
2023-04-04 | 45020 | 0 | 9.7436 | 37.78
2023-04-04 00:30 | 45020.0208 | 0 | 9.2495 | 37.78
2023-04-04 01:00 | 45020.0417 | 0 | 9.1004 | 37.78
2023-04-04 01:30 | 45020.0625 | 0 | 8.9274 | 37.78
2023-04-04 02:00 | 45020.0833 | 0 | 8.8921 | 37.78
2023-04-04 02:30 | 45020.1042 | 0 | 8.8102 | 37.78
2023-04-04 03:00 | 45020.125 | 0 | 8.8158 | 37.78
2023-04-04 03:30 | 45020.1458 | 0 | 8.8382 | 37.78
2023-04-04 04:00 | 45020.1667 | 0 | 9.1211 | 37.78
2023-04-04 04:30 | 45020.1875 | 0 | 9.3315 | 37.78
2023-04-04 05:00 | 45020.2083 | 0 | 9.8003 | 37.78
2023-04-04 05:30 | 45020.2292 | 0 | 10.3321 | 37.78
2023-04-04 06:00 | 45020.25 | 0 | 11.0647 | 37.78
2023-04-04 06:30 | 45020.2708 | 0 | 11.2411 | 37.78
2023-04-04 07:00 | 45020.2917 | 0 | 11.6581 | 37.78
2023-04-04 07:30 | 45020.3125 | 0 | 11.1519 | 37.78
2023-04-04 08:00 | 45020.3333 | 0 | 11.1264 | 37.78
2023-04-04 08:30 | 45020.3542 | 0 | 9.9622 | 37.78
2023-04-04 09:00 | 45020.375 | 0 | 9.4662 | 37.78
2023-04-04 09:30 | 45020.3958 | 0 | 9.7536 | 37.78
2023-04-04 10:00 | 45020.4167 | 0 | 9.9026 | 37.78
2023-04-04 10:30 | 45020.4375 | 0 | 10.1221 | 37.78
2023-04-04 11:00 | 45020.4583 | 0 | 11.5013 | 37.78
2023-04-04 11:30 | 45020.4792 | 0 | 12.8918 | 37.78
2023-04-04 12:00 | 45020.5 | 0 | 11.736 | 37.78
2023-04-04 12:30 | 45020.5208 | 0 | 11.8866 | 37.78
2023-04-04 13:00 | 45020.5417 | 0 | 12.3935 | 37.78
2023-04-04 13:30 | 45020.5625 | 0 | 12.1953 | 37.78
2023-04-04 14:00 | 45020.5833 | 0 | 14.381 | 37.78
2023-04-04 14:30 | 45020.6042 | 0 | 15.8899 | 37.78
2023-04-04 15:00 | 45020.625 | 0 | 13.9791 | 37.78
2023-04-04 15:30 | 45020.6458 | 0 | 12.5076 | 37.78
2023-04-04 16:00 | 45020.6667 | 0 | 14.0645 | 37.78
2023-04-04 16:30 | 45020.6875 | 0 | 14.3111 | 37.78
2023-04-04 17:00 | 45020.7083 | 0 | 14.3154 | 37.78
2023-04-04 17:30 | 45020.7292 | 0 | 14.84 | 37.78
2023-04-04 18:00 | 45020.75 | 0 | 14.909 | 37.78
2023-04-04 18:30 | 45020.7708 | 0 | 14.9387 | 37.78
2023-04-04 19:00 | 45020.7917 | 0 | 14.5313 | 37.78
2023-04-04 19:30 | 45020.8125 | 0 | 14.1253 | 37.78
2023-04-04 20:00 | 45020.8333 | 0 | 13.7401 | 37.78
2023-04-04 20:30 | 45020.8542 | 0 | 13.163 | 37.78
2023-04-04 21:00 | 45020.875 | 0 | 12.8596 | 37.78
2023-04-04 21:30 | 45020.8958 | 0 | 12.2682 | 37.78
2023-04-04 22:00 | 45020.9167 | 0 | 11.5162 | 37.78
2023-04-04 22:30 | 45020.9375 | 0 | 11.0237 | 37.78
2023-04-04 23:00 | 45020.9583 | 0 | 10.7028 | 37.78
2023-04-04 23:30 | 45020.9792 | 0 | 10.3536 | 37.78
2023-04-05 | 45021 | 0 | 9.8168 | 37.78
2023-04-05 00:30 | 45021.0208 | 0 | 9.4255 | 37.78
2023-04-05 01:00 | 45021.0417 | 0 | 9.3014 | 37.78
2023-04-05 01:30 | 45021.0625 | 0 | 9.0855 | 37.78
2023-04-05 02:00 | 45021.0833 | 0 | 8.9926 | 37.78
2023-04-05 02:30 | 45021.1042 | 0 | 8.8736 | 37.78
2023-04-05 03:00 | 45021.125 | 0 | 8.8095 | 37.78
2023-04-05 03:30 | 45021.1458 | 0 | 8.9127 | 37.78
2023-04-05 04:00 | 45021.1667 | 0 | 9.2249 | 37.78
2023-04-05 04:30 | 45021.1875 | 0 | 9.566 | 37.78
2023-04-05 05:00 | 45021.2083 | 0 | 10.0645 | 37.78
2023-04-05 05:30 | 45021.2292 | 0 | 10.5478 | 37.78
2023-04-05 06:00 | 45021.25 | 0 | 11.0679 | 37.78
2023-04-05 06:30 | 45021.2708 | 0 | 11.0847 | 37.78
2023-04-05 07:00 | 45021.2917 | 0 | 11.3843 | 37.78
2023-04-05 07:30 | 45021.3125 | 0 | 10.7927 | 37.78
2023-04-05 08:00 | 45021.3333 | 0 | 10.1487 | 37.78
2023-04-05 08:30 | 45021.3542 | 0 | 9.9714 | 37.78
2023-04-05 09:00 | 45021.375 | 0 | 9.6701 | 37.78
2023-04-05 09:30 | 45021.3958 | 0 | 9.3608 | 37.78
2023-04-05 10:00 | 45021.4167 | 0 | 9.0688 | 37.78
2023-04-05 10:30 | 45021.4375 | 0 | 9.4583 | 37.78
2023-04-05 11:00 | 45021.4583 | 0 | 10.1274 | 37.78
2023-04-05 11:30 | 45021.4792 | 0 | 10.5161 | 37.78
2023-04-05 12:00 | 45021.5 | 0 | 10.621 | 37.78
2023-04-05 12:30 | 45021.5208 | 0 | 11.4922 | 37.78
2023-04-05 13:00 | 45021.5417 | 0 | 12.9194 | 37.78
2023-04-05 13:30 | 45021.5625 | 0 | 12.6949 | 37.78
2023-04-05 14:00 | 45021.5833 | 0 | 12.7055 | 37.78
2023-04-05 14:30 | 45021.6042 | 0 | 12.8985 | 37.78
2023-04-05 15:00 | 45021.625 | 0 | 13.7285 | 37.78
2023-04-05 15:30 | 45021.6458 | 0 | 13.7607 | 37.78
2023-04-05 16:00 | 45021.6667 | 0 | 14.6492 | 37.78
2023-04-05 16:30 | 45021.6875 | 0 | 15.4631 | 37.78
2023-04-05 17:00 | 45021.7083 | 0 | 15.5507 | 37.78
2023-04-05 17:30 | 45021.7292 | 0 | 15.3986 | 37.78
2023-04-05 18:00 | 45021.75 | 0 | 15.497 | 37.78
2023-04-05 18:30 | 45021.7708 | 0 | 15.4838 | 37.78
2023-04-05 19:00 | 45021.7917 | 0 | 15.1545 | 37.78
2023-04-05 19:30 | 45021.8125 | 0 | 14.7932 | 37.78
2023-04-05 20:00 | 45021.8333 | 0 | 14.2537 | 37.78
2023-04-05 20:30 | 45021.8542 | 0 | 13.597 | 37.78
2023-04-05 21:00 | 45021.875 | 0 | 13.32 | 37.78
2023-04-05 21:30 | 45021.8958 | 0 | 12.5438 | 37.78
2023-04-05 22:00 | 45021.9167 | 0 | 11.6022 | 37.78
2023-04-05 22:30 | 45021.9375 | 0 | 11.0035 | 37.78
2023-04-05 23:00 | 45021.9583 | 0 | 10.6808 | 37.78
2023-04-05 23:30 | 45021.9792 | 0 | 10.3083 | 37.78
2023-04-06 | 45022 | 0 | 9.8253 | 37.78
2023-04-06 00:30 | 45022.0208 | 0 | 9.3888 | 37.78
2023-04-06 01:00 | 45022.0417 | 0 | 9.1325 | 37.78
2023-04-06 01:30 | 45022.0625 | 0 | 8.9424 | 37.78
2023-04-06 02:00 | 45022.0833 | 0 | 8.8269 | 37.78
2023-04-06 02:30 | 45022.1042 | 0 | 8.7507 | 37.78
2023-04-06 03:00 | 45022.125 | 0 | 8.8921 | 37.78
2023-04-06 03:30 | 45022.1458 | 0 | 8.8122 | 37.78
2023-04-06 04:00 | 45022.1667 | 0 | 9.1136 | 37.78
2023-04-06 04:30 | 45022.1875 | 0 | 9.3128 | 37.78
2023-04-06 05:00 | 45022.2083 | 0 | 9.7979 | 37.78
2023-04-06 05:30 | 45022.2292 | 0 | 10.247 | 37.78
2023-04-06 06:00 | 45022.25 | 0 | 10.9751 | 37.78
2023-04-06 06:30 | 45022.2708 | 0 | 10.9261 | 37.78
2023-04-06 07:00 | 45022.2917 | 0 | 10.8164 | 37.78
2023-04-06 07:30 | 45022.3125 | 0 | 10.454 | 37.78
2023-04-06 08:00 | 45022.3333 | 0 | 10.446 | 37.78
2023-04-06 08:30 | 45022.3542 | 0 | 10.2247 | 37.78
2023-04-06 09:00 | 45022.375 | 0 | 9.8677 | 37.78
2023-04-06 09:30 | 45022.3958 | 0 | 9.5981 | 37.78
2023-04-06 10:00 | 45022.4167 | 0 | 9.6057 | 37.78
2023-04-06 10:30 | 45022.4375 | 0 | 9.6816 | 37.78
2023-04-06 11:00 | 45022.4583 | 0 | 11.1725 | 37.78
2023-04-06 11:30 | 45022.4792 | 0 | 12.0811 | 37.78
2023-04-06 12:00 | 45022.5 | 0 | 11.9973 | 37.78
2023-04-06 12:30 | 45022.5208 | 0 | 12.3036 | 37.78
2023-04-06 13:00 | 45022.5417 | 0 | 12.6389 | 37.78
2023-04-06 13:30 | 45022.5625 | 0 | 12.3157 | 37.78
2023-04-06 14:00 | 45022.5833 | 0 | 13.1243 | 37.78
2023-04-06 14:30 | 45022.6042 | 0 | 12.8609 | 37.78
2023-04-06 15:00 | 45022.625 | 0 | 13.5976 | 37.78
2023-04-06 15:30 | 45022.6458 | 0 | 14.1678 | 37.78
2023-04-06 16:00 | 45022.6667 | 0 | 14.2648 | 37.78
2023-04-06 16:30 | 45022.6875 | 0 | 13.9038 | 37.78
2023-04-06 17:00 | 45022.7083 | 0 | 13.7349 | 37.78
2023-04-06 17:30 | 45022.7292 | 0 | 13.8649 | 37.78
2023-04-06 18:00 | 45022.75 | 0 | 13.7548 | 37.78
2023-04-06 18:30 | 45022.7708 | 0 | 13.6266 | 37.78
2023-04-06 19:00 | 45022.7917 | 0 | 13.3716 | 37.78
2023-04-06 19:30 | 45022.8125 | 0 | 13.1893 | 37.78
2023-04-06 20:00 | 45022.8333 | 0 | 12.8002 | 37.78
2023-04-06 20:30 | 45022.8542 | 0 | 12.3021 | 37.78
2023-04-06 21:00 | 45022.875 | 0 | 12.2455 | 37.78
2023-04-06 21:30 | 45022.8958 | 0 | 11.5496 | 37.78
2023-04-06 22:00 | 45022.9167 | 0 | 11.1058 | 37.78
2023-04-06 22:30 | 45022.9375 | 0 | 10.7215 | 37.78
2023-04-06 23:00 | 45022.9583 | 0 | 10.4489 | 37.78
2023-04-06 23:30 | 45022.9792 | 0 | 10.1484 | 37.78
2023-04-07 | 45023 | 0 | 9.6209 | 37.78
2023-04-07 00:30 | 45023.0208 | 0 | 9.1209 | 37.78
2023-04-07 01:00 | 45023.0417 | 0 | 8.875 | 37.78
2023-04-07 01:30 | 45023.0625 | 0 | 8.747 | 37.78
2023-04-07 02:00 | 45023.0833 | 0 | 8.5644 | 37.78
2023-04-07 02:30 | 45023.1042 | 0 | 8.5123 | 37.78
2023-04-07 03:00 | 45023.125 | 0 | 8.4027 | 37.78
2023-04-07 03:30 | 45023.1458 | 0 | 8.4213 | 37.78
2023-04-07 04:00 | 45023.1667 | 0 | 8.3375 | 37.78
2023-04-07 04:30 | 45023.1875 | 0 | 8.3952 | 37.78
2023-04-07 05:00 | 45023.2083 | 0 | 8.3804 | 37.78
2023-04-07 05:30 | 45023.2292 | 0 | 8.5386 | 37.78
2023-04-07 06:00 | 45023.25 | 0 | 8.6445 | 37.78
2023-04-07 06:30 | 45023.2708 | 0 | 8.7472 | 37.78
2023-04-07 07:00 | 45023.2917 | 0 | 8.9313 | 37.78
2023-04-07 07:30 | 45023.3125 | 0 | 9.3537 | 37.78
2023-04-07 08:00 | 45023.3333 | 0 | 9.7968 | 37.78
2023-04-07 08:30 | 45023.3542 | 0 | 10.0492 | 37.78
2023-04-07 09:00 | 45023.375 | 0 | 8.9226 | 37.78
2023-04-07 09:30 | 45023.3958 | 0 | 9.4416 | 37.78
2023-04-07 10:00 | 45023.4167 | 0 | 9.1043 | 37.78
2023-04-07 10:30 | 45023.4375 | 0 | 9.2749 | 37.78
2023-04-07 11:00 | 45023.4583 | 0 | 10.3195 | 37.78
2023-04-07 11:30 | 45023.4792 | 0 | 10.8385 | 37.78
2023-04-07 12:00 | 45023.5 | 0 | 10.0838 | 37.78
2023-04-07 12:30 | 45023.5208 | 0 | 7.2471 | 37.78
2023-04-07 13:00 | 45023.5417 | 0 | 8.3209 | 37.78
2023-04-07 13:30 | 45023.5625 | 0 | 7.8447 | 37.78
2023-04-07 14:00 | 45023.5833 | 0 | 9.3892 | 37.78
2023-04-07 14:30 | 45023.6042 | 0 | 9.7751 | 37.78
2023-04-07 15:00 | 45023.625 | 0 | 9.2836 | 37.78
2023-04-07 15:30 | 45023.6458 | 0 | 9.8066 | 37.78
2023-04-07 16:00 | 45023.6667 | 0 | 11.0286 | 37.78
2023-04-07 16:30 | 45023.6875 | 0 | 11.6298 | 37.78
2023-04-07 17:00 | 45023.7083 | 0 | 11.6204 | 37.78
2023-04-07 17:30 | 45023.7292 | 0 | 11.7824 | 37.78
2023-04-07 18:00 | 45023.75 | 0 | 11.5476 | 37.78
2023-04-07 18:30 | 45023.7708 | 0 | 11.3745 | 37.78
2023-04-07 19:00 | 45023.7917 | 0 | 11.1776 | 37.78
2023-04-07 19:30 | 45023.8125 | 0 | 11.0918 | 37.78
2023-04-07 20:00 | 45023.8333 | 0 | 11.0565 | 37.78
2023-04-07 20:30 | 45023.8542 | 0 | 10.6599 | 37.78
2023-04-07 21:00 | 45023.875 | 0 | 10.3353 | 37.78
2023-04-07 21:30 | 45023.8958 | 0 | 10.0346 | 37.78
2023-04-07 22:00 | 45023.9167 | 0 | 9.5872 | 37.78
2023-04-07 22:30 | 45023.9375 | 0 | 9.2231 | 37.78
2023-04-07 23:00 | 45023.9583 | 0 | 8.9933 | 37.78
2023-04-07 23:30 | 45023.9792 | 0 | 8.5513 | 37.78
2023-04-08 | 45024 | 0 | 8.2363 | 37.78
2023-04-08 00:30 | 45024.0208 | 0 | 8.021 | 37.78
2023-04-08 01:00 | 45024.0417 | 0 | 7.7902 | 37.78
2023-04-08 01:30 | 45024.0625 | 0 | 7.6061 | 37.78
2023-04-08 02:00 | 45024.0833 | 0 | 7.5614 | 37.78
2023-04-08 02:30 | 45024.1042 | 0 | 7.4461 | 37.78
2023-04-08 03:00 | 45024.125 | 0 | 7.5187 | 37.78
2023-04-08 03:30 | 45024.1458 | 0 | 7.5503 | 37.78
2023-04-08 04:00 | 45024.1667 | 0 | 7.5206 | 37.78
2023-04-08 04:30 | 45024.1875 | 0 | 7.6341 | 37.78
2023-04-08 05:00 | 45024.2083 | 0 | 7.7234 | 37.78
2023-04-08 05:30 | 45024.2292 | 0 | 7.9363 | 37.78
2023-04-08 06:00 | 45024.25 | 0 | 7.9429 | 37.78
2023-04-08 06:30 | 45024.2708 | 0 | 7.8219 | 37.78
2023-04-08 07:00 | 45024.2917 | 0 | 7.6812 | 37.78
2023-04-08 07:30 | 45024.3125 | 0 | 7.2692 | 37.78
2023-04-08 08:00 | 45024.3333 | 0 | 6.8655 | 37.78
2023-04-08 08:30 | 45024.3542 | 0 | 6.3447 | 37.78
2023-04-08 09:00 | 45024.375 | 0 | 5.9105 | 37.78
2023-04-08 09:30 | 45024.3958 | 0 | 5.3248 | 37.78
2023-04-08 10:00 | 45024.4167 | 0 | 4.8802 | 37.78
2023-04-08 10:30 | 45024.4375 | 0 | 4.4888 | 37.78
2023-04-08 11:00 | 45024.4583 | 0 | 4.3623 | 37.78
2023-04-08 11:30 | 45024.4792 | 0 | 4.2916 | 37.78
2023-04-08 12:00 | 45024.5 | 0 | 4.2263 | 37.78
2023-04-08 12:30 | 45024.5208 | 0 | 4.1596 | 37.78
2023-04-08 13:00 | 45024.5417 | 0 | 4.4798 | 37.78
2023-04-08 13:30 | 45024.5625 | 0 | 4.811 | 37.78
2023-04-08 14:00 | 45024.5833 | 0 | 5.7065 | 37.78
2023-04-08 14:30 | 45024.6042 | 0 | 6.4481 | 37.78
2023-04-08 15:00 | 45024.625 | 0 | 7.5137 | 37.78
2023-04-08 15:30 | 45024.6458 | 0 | 8.4019 | 37.78
2023-04-08 16:00 | 45024.6667 | 0 | 9.2596 | 37.78
2023-04-08 16:30 | 45024.6875 | 0 | 10.1976 | 37.78
2023-04-08 17:00 | 45024.7083 | 0 | 10.7172 | 37.78
2023-04-08 17:30 | 45024.7292 | 0 | 10.9749 | 37.78
2023-04-08 18:00 | 45024.75 | 0 | 11.1384 | 37.78
2023-04-08 18:30 | 45024.7708 | 0 | 10.941 | 37.78
2023-04-08 19:00 | 45024.7917 | 0 | 10.8145 | 37.78
2023-04-08 19:30 | 45024.8125 | 0 | 10.6544 | 37.78
2023-04-08 20:00 | 45024.8333 | 0 | 10.3825 | 37.78
2023-04-08 20:30 | 45024.8542 | 0 | 10.1203 | 37.78
2023-04-08 21:00 | 45024.875 | 0 | 9.8989 | 37.78
2023-04-08 21:30 | 45024.8958 | 0 | 9.5905 | 37.78
2023-04-08 22:00 | 45024.9167 | 0 | 9.199 | 37.78
2023-04-08 22:30 | 45024.9375 | 0 | 8.7575 | 37.78
2023-04-08 23:00 | 45024.9583 | 0 | 8.3382 | 37.78
2023-04-08 23:30 | 45024.9792 | 0 | 8.0341 | 37.78
2023-04-09 | 45025 | 0 | 7.7646 | 37.78
2023-04-09 00:30 | 45025.0208 | 0 | 7.5019 | 37.78
2023-04-09 01:00 | 45025.0417 | 0 | 7.353 | 37.78
2023-04-09 01:30 | 45025.0625 | 0 | 7.245 | 37.78
2023-04-09 02:00 | 45025.0833 | 0 | 7.0794 | 37.78
2023-04-09 02:30 | 45025.1042 | 0 | 7.046 | 37.78
2023-04-09 03:00 | 45025.125 | 0 | 7.1595 | 37.78
2023-04-09 03:30 | 45025.1458 | 0 | 7.0999 | 37.78
2023-04-09 04:00 | 45025.1667 | 0 | 7.1203 | 37.78
2023-04-09 04:30 | 45025.1875 | 0 | 7.1353 | 37.78
2023-04-09 05:00 | 45025.2083 | 0 | 7.1 | 37.78
2023-04-09 05:30 | 45025.2292 | 0 | 7.2804 | 37.78
2023-04-09 06:00 | 45025.25 | 0 | 7.3214 | 37.78
2023-04-09 06:30 | 45025.2708 | 0 | 7.1333 | 37.78
2023-04-09 07:00 | 45025.2917 | 0 | 6.6918 | 37.78
2023-04-09 07:30 | 45025.3125 | 0 | 6.1499 | 37.78
2023-04-09 08:00 | 45025.3333 | 0 | 5.7114 | 37.78
2023-04-09 08:30 | 45025.3542 | 0 | 5.3304 | 37.78
2023-04-09 09:00 | 45025.375 | 0 | 4.9011 | 37.78
2023-04-09 09:30 | 45025.3958 | 0 | 4.2664 | 37.78
2023-04-09 10:00 | 45025.4167 | 0 | 3.9025 | 37.78
2023-04-09 10:30 | 45025.4375 | 0 | 3.5374 | 37.78
2023-04-09 11:00 | 45025.4583 | 0 | 3.2476 | 37.78
2023-04-09 11:30 | 45025.4792 | 0 | 3.2103 | 37.78
2023-04-09 12:00 | 45025.5 | 0 | 3.2606 | 37.78
2023-04-09 12:30 | 45025.5208 | 0 | 3.1228 | 37.78
2023-04-09 13:00 | 45025.5417 | 0 | 3.4914 | 37.78
2023-04-09 13:30 | 45025.5625 | 0 | 3.9065 | 37.78
2023-04-09 14:00 | 45025.5833 | 0 | 4.7006 | 37.78
2023-04-09 14:30 | 45025.6042 | 0 | 5.562 | 37.78
2023-04-09 15:00 | 45025.625 | 0 | 6.5987 | 37.78
2023-04-09 15:30 | 45025.6458 | 0 | 7.5577 | 37.78
2023-04-09 16:00 | 45025.6667 | 0 | 8.6104 | 37.78
2023-04-09 16:30 | 45025.6875 | 0 | 9.5443 | 37.78
2023-04-09 17:00 | 45025.7083 | 0 | 10.0568 | 37.78
2023-04-09 17:30 | 45025.7292 | 0 | 10.1838 | 37.78
2023-04-09 18:00 | 45025.75 | 0 | 10.4741 | 37.78
2023-04-09 18:30 | 45025.7708 | 0 | 10.7452 | 37.78
2023-04-09 19:00 | 45025.7917 | 0 | 10.4684 | 37.78
2023-04-09 19:30 | 45025.8125 | 0 | 10.1738 | 37.78
2023-04-09 20:00 | 45025.8333 | 0 | 9.9937 | 37.78
2023-04-09 20:30 | 45025.8542 | 0 | 9.6415 | 37.78
2023-04-09 21:00 | 45025.875 | 0 | 9.4578 | 37.78
2023-04-09 21:30 | 45025.8958 | 0 | 9.1321 | 37.78
2023-04-09 22:00 | 45025.9167 | 0 | 8.8297 | 37.78
2023-04-09 22:30 | 45025.9375 | 0 | 8.4491 | 37.78
2023-04-09 23:00 | 45025.9583 | 0 | 8.1137 | 37.78
2023-04-09 23:30 | 45025.9792 | 0 | 7.8442 | 37.78
2023-04-10 | 45026 | 0 | 7.5426 | 37.78
2023-04-10 00:30 | 45026.0208 | 0 | 7.2655 | 37.78
2023-04-10 01:00 | 45026.0417 | 0 | 7.1632 | 37.78
2023-04-10 01:30 | 45026.0625 | 0 | 7.1091 | 37.78
2023-04-10 02:00 | 45026.0833 | 0 | 6.9324 | 37.78
2023-04-10 02:30 | 45026.1042 | 0 | 6.964 | 37.78
2023-04-10 03:00 | 45026.125 | 0 | 6.9474 | 37.78
2023-04-10 03:30 | 45026.1458 | 0 | 6.9864 | 37.78
2023-04-10 04:00 | 45026.1667 | 0 | 7.0516 | 37.78
2023-04-10 04:30 | 45026.1875 | 0 | 7.1912 | 37.78
2023-04-10 05:00 | 45026.2083 | 0 | 7.3512 | 37.78
2023-04-10 05:30 | 45026.2292 | 0 | 7.5988 | 37.78
2023-04-10 06:00 | 45026.25 | 0 | 7.7923 | 37.78
2023-04-10 06:30 | 45026.2708 | 0 | 7.5128 | 37.78
2023-04-10 07:00 | 45026.2917 | 0 | 7.2432 | 37.78
2023-04-10 07:30 | 45026.3125 | 0 | 6.7147 | 37.78
2023-04-10 08:00 | 45026.3333 | 0 | 6.3477 | 37.78
2023-04-10 08:30 | 45026.3542 | 0 | 5.8993 | 37.78
2023-04-10 09:00 | 45026.375 | 0 | 5.2995 | 37.78
2023-04-10 09:30 | 45026.3958 | 0 | 4.9532 | 37.78
2023-04-10 10:00 | 45026.4167 | 0 | 4.4254 | 37.78
2023-04-10 10:30 | 45026.4375 | 0 | 4.2245 | 37.78
2023-04-10 11:00 | 45026.4583 | 0 | 3.9105 | 37.78
2023-04-10 11:30 | 45026.4792 | 0 | 3.9027 | 37.78
2023-04-10 12:00 | 45026.5 | 0 | 4.1089 | 37.78
2023-04-10 12:30 | 45026.5208 | 0 | 4.5433 | 37.78
2023-04-10 13:00 | 45026.5417 | 0 | 5.414 | 37.78
2023-04-10 13:30 | 45026.5625 | 0 | 5.4663 | 37.78
2023-04-10 14:00 | 45026.5833 | 0 | 8.1527 | 37.78
2023-04-10 14:30 | 45026.6042 | 0 | 7.5477 | 37.78
2023-04-10 15:00 | 45026.625 | 0 | 8.5051 | 37.78
2023-04-10 15:30 | 45026.6458 | 0 | 8.8457 | 37.78
2023-04-10 16:00 | 45026.6667 | 0 | 9.1034 | 37.78
2023-04-10 16:30 | 45026.6875 | 0 | 9.9769 | 37.78
2023-04-10 17:00 | 45026.7083 | 0 | 10.8128 | 37.78
2023-04-10 17:30 | 45026.7292 | 0 | 11.3804 | 37.78
2023-04-10 18:00 | 45026.75 | 0 | 11.7471 | 37.78
2023-04-10 18:30 | 45026.7708 | 0 | 11.6557 | 37.78
2023-04-10 19:00 | 45026.7917 | 0 | 11.2573 | 37.78
2023-04-10 19:30 | 45026.8125 | 0 | 11.0007 | 37.78
2023-04-10 20:00 | 45026.8333 | 0 | 10.7511 | 37.78
2023-04-10 20:30 | 45026.8542 | 0 | 10.2912 | 37.78
2023-04-10 21:00 | 45026.875 | 0 | 9.9753 | 37.78
2023-04-10 21:30 | 45026.8958 | 0 | 9.4597 | 37.78
2023-04-10 22:00 | 45026.9167 | 0 | 9.0146 | 37.78
2023-04-10 22:30 | 45026.9375 | 0 | 8.6297 | 37.78
2023-04-10 23:00 | 45026.9583 | 0 | 8.4046 | 37.78
2023-04-10 23:30 | 45026.9792 | 0 | 8.0638 | 37.78
2023-04-11 | 45027 | 0 | 7.7755 | 37.78
2023-04-11 00:30 | 45027.0208 | 0 | 7.6743 | 37.78
2023-04-11 01:00 | 45027.0417 | 0 | 7.565 | 37.78
2023-04-11 01:30 | 45027.0625 | 0 | 7.2859 | 37.78
2023-04-11 02:00 | 45027.0833 | 0 | 7.3196 | 37.78
2023-04-11 02:30 | 45027.1042 | 0 | 7.3754 | 37.78
2023-04-11 03:00 | 45027.125 | 0 | 7.4014 | 37.78
2023-04-11 03:30 | 45027.1458 | 0 | 7.5206 | 37.78
2023-04-11 04:00 | 45027.1667 | 0 | 7.8556 | 37.78
2023-04-11 04:30 | 45027.1875 | 0 | 8.0673 | 37.78
2023-04-11 05:00 | 45027.2083 | 0 | 8.601 | 37.78
2023-04-11 05:30 | 45027.2292 | 0 | 8.9632 | 37.78
2023-04-11 06:00 | 45027.25 | 0 | 9.77 | 37.78
2023-04-11 06:30 | 45027.2708 | 0 | 10.0707 | 37.78
2023-04-11 07:00 | 45027.2917 | 0 | 9.953 | 37.78
2023-04-11 07:30 | 45027.3125 | 0 | 9.4083 | 37.78
2023-04-11 08:00 | 45027.3333 | 0 | 8.984 | 37.78
2023-04-11 08:30 | 45027.3542 | 0 | 8.5346 | 37.78
2023-04-11 09:00 | 45027.375 | 0 | 8.1309 | 37.78
2023-04-11 09:30 | 45027.3958 | 0 | 7.5429 | 37.78
2023-04-11 10:00 | 45027.4167 | 0 | 7.1208 | 37.78
2023-04-11 10:30 | 45027.4375 | 0 | 6.8599 | 37.78
2023-04-11 11:00 | 45027.4583 | 0 | 6.7351 | 37.78
2023-04-11 11:30 | 45027.4792 | 0 | 6.8302 | 37.78
2023-04-11 12:00 | 45027.5 | 0 | 6.9194 | 37.78
2023-04-11 12:30 | 45027.5208 | 0 | 7.1251 | 37.78
2023-04-11 13:00 | 45027.5417 | 0 | 7.6342 | 37.78
2023-04-11 13:30 | 45027.5625 | 0 | 8.0416 | 37.78
2023-04-11 14:00 | 45027.5833 | 0 | 8.8033 | 37.78
2023-04-11 14:30 | 45027.6042 | 0 | 9.4445 | 37.78
2023-04-11 15:00 | 45027.625 | 0 | 10.3441 | 37.78
2023-04-11 15:30 | 45027.6458 | 0 | 11.184 | 37.78
2023-04-11 16:00 | 45027.6667 | 0 | 11.9171 | 37.78
2023-04-11 16:30 | 45027.6875 | 0 | 12.4869 | 37.78
2023-04-11 17:00 | 45027.7083 | 0 | 13.0087 | 37.78
2023-04-11 17:30 | 45027.7292 | 0 | 13.1037 | 37.78
2023-04-11 18:00 | 45027.75 | 0 | 13.368 | 37.78
2023-04-11 18:30 | 45027.7708 | 0 | 13.4556 | 37.78
2023-04-11 19:00 | 45027.7917 | 0 | 13.1148 | 37.78
2023-04-11 19:30 | 45027.8125 | 0 | 12.6881 | 37.78
2023-04-11 20:00 | 45027.8333 | 0 | 12.5135 | 37.78
2023-04-11 20:30 | 45027.8542 | 0 | 12.0676 | 37.78
2023-04-11 21:00 | 45027.875 | 0 | 11.7264 | 37.78
2023-04-11 21:30 | 45027.8958 | 0 | 11.2435 | 37.78
2023-04-11 22:00 | 45027.9167 | 0 | 10.6186 | 37.78
2023-04-11 22:30 | 45027.9375 | 0 | 9.9788 | 37.78
2023-04-11 23:00 | 45027.9583 | 0 | 9.6706 | 37.78
2023-04-11 23:30 | 45027.9792 | 0 | 9.161 | 37.78
2023-04-12 | 45028 | 0 | 8.5922 | 37.78
2023-04-12 00:30 | 45028.0208 | 0 | 8.1982 | 37.78
2023-04-12 01:00 | 45028.0417 | 0 | 8.209 | 37.78
2023-04-12 01:30 | 45028.0625 | 0 | 8.0024 | 37.78
2023-04-12 02:00 | 45028.0833 | 0 | 7.9114 | 37.78
2023-04-12 02:30 | 45028.1042 | 0 | 7.9262 | 37.78
2023-04-12 03:00 | 45028.125 | 0 | 7.9096 | 37.78
2023-04-12 03:30 | 45028.1458 | 0 | 7.969 | 37.78
2023-04-12 04:00 | 45028.1667 | 0 | 8.1926 | 37.78
2023-04-12 04:30 | 45028.1875 | 0 | 8.6562 | 37.78
2023-04-12 05:00 | 45028.2083 | 0 | 9.1045 | 37.78
2023-04-12 05:30 | 45028.2292 | 0 | 9.6984 | 37.78
2023-04-12 06:00 | 45028.25 | 0 | 10.4759 | 37.78
2023-04-12 06:30 | 45028.2708 | 0 | 10.6893 | 37.78
2023-04-12 07:00 | 45028.2917 | 0 | 10.5128 | 37.78
2023-04-12 07:30 | 45028.3125 | 0 | 10.0028 | 37.78
2023-04-12 08:00 | 45028.3333 | 0 | 9.8557 | 37.78
2023-04-12 08:30 | 45028.3542 | 0 | 9.2692 | 37.78
2023-04-12 09:00 | 45028.375 | 0 | 8.9155 | 37.78
2023-04-12 09:30 | 45028.3958 | 0 | 8.4464 | 37.78
2023-04-12 10:00 | 45028.4167 | 0 | 8.2813 | 37.78
2023-04-12 10:30 | 45028.4375 | 0 | 7.9322 | 37.78
2023-04-12 11:00 | 45028.4583 | 0 | 8.7604 | 37.78
2023-04-12 11:30 | 45028.4792 | 0 | 9.4492 | 37.78
2023-04-12 12:00 | 45028.5 | 0 | 8.6327 | 37.78
2023-04-12 12:30 | 45028.5208 | 0 | 7.6359 | 37.78
2023-04-12 13:00 | 45028.5417 | 0 | 9.4244 | 37.78
2023-04-12 13:30 | 45028.5625 | 0 | 9.841 | 37.78
2023-04-12 14:00 | 45028.5833 | 0 | 9.0906 | 37.78
2023-04-12 14:30 | 45028.6042 | 0 | 9.5328 | 37.78
2023-04-12 15:00 | 45028.625 | 0 | 10.3772 | 37.78
2023-04-12 15:30 | 45028.6458 | 0 | 11.2403 | 37.78
2023-04-12 16:00 | 45028.6667 | 0 | 12.0891 | 37.78
2023-04-12 16:30 | 45028.6875 | 0 | 12.8527 | 37.78
2023-04-12 17:00 | 45028.7083 | 0 | 13.1763 | 37.78
2023-04-12 17:30 | 45028.7292 | 0 | 13.186 | 37.78
2023-04-12 18:00 | 45028.75 | 0 | 13.513 | 37.78
2023-04-12 18:30 | 45028.7708 | 0 | 13.5356 | 37.78
2023-04-12 19:00 | 45028.7917 | 0 | 13.2265 | 37.78
2023-04-12 19:30 | 45028.8125 | 0 | 13.0199 | 37.78
2023-04-12 20:00 | 45028.8333 | 0 | 12.5471 | 37.78
2023-04-12 20:30 | 45028.8542 | 0 | 11.8998 | 37.78
2023-04-12 21:00 | 45028.875 | 0 | 11.7564 | 37.78
2023-04-12 21:30 | 45028.8958 | 0 | 11.3634 | 37.78
2023-04-12 22:00 | 45028.9167 | 0 | 10.6927 | 37.78
2023-04-12 22:30 | 45028.9375 | 0 | 10.0309 | 37.78
2023-04-12 23:00 | 45028.9583 | 0 | 9.6236 | 37.78
2023-04-12 23:30 | 45028.9792 | 0 | 9.3404 | 37.78
2023-04-13 | 45029 | 0 | 8.9185 | 37.78
2023-04-13 00:30 | 45029.0208 | 0 | 8.5217 | 37.78
2023-04-13 01:00 | 45029.0417 | 0 | 8.4322 | 37.78
2023-04-13 01:30 | 45029.0625 | 0 | 8.1141 | 37.78
2023-04-13 02:00 | 45029.0833 | 0 | 8.0788 | 37.78
2023-04-13 02:30 | 45029.1042 | 0 | 7.9634 | 37.78
2023-04-13 03:00 | 45029.125 | 0 | 8.1123 | 37.78
2023-04-13 03:30 | 45029.1458 | 0 | 8.131 | 37.78
2023-04-13 04:00 | 45029.1667 | 0 | 8.3208 | 37.78
2023-04-13 04:30 | 45029.1875 | 0 | 8.6174 | 37.78
2023-04-13 05:00 | 45029.2083 | 0 | 9.2552 | 37.78
2023-04-13 05:30 | 45029.2292 | 0 | 9.852 | 37.78
2023-04-13 06:00 | 45029.25 | 0 | 10.5809 | 37.78
2023-04-13 06:30 | 45029.2708 | 0 | 10.8649 | 37.78
2023-04-13 07:00 | 45029.2917 | 0 | 10.8684 | 37.78
2023-04-13 07:30 | 45029.3125 | 0 | 10.3599 | 37.78
2023-04-13 08:00 | 45029.3333 | 0 | 10.273 | 37.78
2023-04-13 08:30 | 45029.3542 | 0 | 9.7583 | 37.78
2023-04-13 09:00 | 45029.375 | 0 | 9.4038 | 37.78
2023-04-13 09:30 | 45029.3958 | 0 | 9.0252 | 37.78
2023-04-13 10:00 | 45029.4167 | 0 | 8.3944 | 37.78
2023-04-13 10:30 | 45029.4375 | 0 | 8.1309 | 37.78
2023-04-13 11:00 | 45029.4583 | 0 | 8.0826 | 37.78
2023-04-13 11:30 | 45029.4792 | 0 | 8.1012 | 37.78
2023-04-13 12:00 | 45029.5 | 0 | 8.2056 | 37.78
2023-04-13 12:30 | 45029.5208 | 0 | 8.2389 | 37.78
2023-04-13 13:00 | 45029.5417 | 0 | 8.6174 | 37.78
2023-04-13 13:30 | 45029.5625 | 0 | 8.9351 | 37.78
2023-04-13 14:00 | 45029.5833 | 0 | 9.591 | 37.78
2023-04-13 14:30 | 45029.6042 | 0 | 10.1958 | 37.78
2023-04-13 15:00 | 45029.625 | 0 | 11.0586 | 37.78
2023-04-13 15:30 | 45029.6458 | 0 | 11.897 | 37.78
2023-04-13 16:00 | 45029.6667 | 0 | 12.5717 | 37.78
2023-04-13 16:30 | 45029.6875 | 0 | 13.1828 | 37.78
2023-04-13 17:00 | 45029.7083 | 0 | 13.4331 | 37.78
2023-04-13 17:30 | 45029.7292 | 0 | 13.7264 | 37.78
2023-04-13 18:00 | 45029.75 | 0 | 13.5846 | 37.78
2023-04-13 18:30 | 45029.7708 | 0 | 13.3792 | 37.78
2023-04-13 19:00 | 45029.7917 | 0 | 13.3661 | 37.78
2023-04-13 19:30 | 45029.8125 | 0 | 13.232 | 37.78
2023-04-13 20:00 | 45029.8333 | 0 | 13.0012 | 37.78
2023-04-13 20:30 | 45029.8542 | 0 | 12.5401 | 37.78
2023-04-13 21:00 | 45029.875 | 0 | 12.1916 | 37.78
2023-04-13 21:30 | 45029.8958 | 0 | 11.7856 | 37.78
2023-04-13 22:00 | 45029.9167 | 0 | 11.2587 | 37.78
2023-04-13 22:30 | 45029.9375 | 0 | 10.6234 | 37.78
2023-04-13 23:00 | 45029.9583 | 0 | 10.297 | 37.78
2023-04-13 23:30 | 45029.9792 | 0 | 9.6371 | 37.78
2023-04-14 | 45030 | 0 | 9.063 | 37.78
2023-04-14 00:30 | 45030.0208 | 0 | 8.8101 | 37.78
2023-04-14 01:00 | 45030.0417 | 0 | 8.6426 | 37.78
2023-04-14 01:30 | 45030.0625 | 0 | 8.3815 | 37.78
2023-04-14 02:00 | 45030.0833 | 0 | 8.2575 | 37.78
2023-04-14 02:30 | 45030.1042 | 0 | 8.2258 | 37.78
2023-04-14 03:00 | 45030.125 | 0 | 8.2164 | 37.78
2023-04-14 03:30 | 45030.1458 | 0 | 8.2297 | 37.78
2023-04-14 04:00 | 45030.1667 | 0 | 8.4437 | 37.78
2023-04-14 04:30 | 45030.1875 | 0 | 8.6684 | 37.78
2023-04-14 05:00 | 45030.2083 | 0 | 9.244 | 37.78
2023-04-14 05:30 | 45030.2292 | 0 | 9.763 | 37.78
2023-04-14 06:00 | 45030.25 | 0 | 10.323 | 37.78
2023-04-14 06:30 | 45030.2708 | 0 | 10.6603 | 37.78
2023-04-14 07:00 | 45030.2917 | 0 | 10.809 | 37.78
2023-04-14 07:30 | 45030.3125 | 0 | 10.3509 | 37.78
2023-04-14 08:00 | 45030.3333 | 0 | 9.9413 | 37.78
2023-04-14 08:30 | 45030.3542 | 0 | 9.56 | 37.78
2023-04-14 09:00 | 45030.375 | 0 | 9.2878 | 37.78
2023-04-14 09:30 | 45030.3958 | 0 | 8.7894 | 37.78
2023-04-14 10:00 | 45030.4167 | 0 | 8.3271 | 37.78
2023-04-14 10:30 | 45030.4375 | 0 | 8.1366 | 37.78
2023-04-14 11:00 | 45030.4583 | 0 | 8.196 | 37.78
2023-04-14 11:30 | 45030.4792 | 0 | 8.1439 | 37.78
2023-04-14 12:00 | 45030.5 | 0 | 8.2758 | 37.78
2023-04-14 12:30 | 45030.5208 | 0 | 8.9408 | 37.78
2023-04-14 13:00 | 45030.5417 | 0 | 9.0207 | 37.78
2023-04-14 13:30 | 45030.5625 | 0 | 9.7962 | 37.78
2023-04-14 14:00 | 45030.5833 | 0 | 11.0786 | 37.78
2023-04-14 14:30 | 45030.6042 | 0 | 13.0328 | 37.78
2023-04-14 15:00 | 45030.625 | 0 | 12.7556 | 37.78
2023-04-14 15:30 | 45030.6458 | 0 | 12.1459 | 37.78
2023-04-14 16:00 | 45030.6667 | 0 | 13.2173 | 37.78
2023-04-14 16:30 | 45030.6875 | 0 | 13.312 | 37.78
2023-04-14 17:00 | 45030.7083 | 0 | 13.2767 | 37.78
2023-04-14 17:30 | 45030.7292 | 0 | 13.1894 | 37.78
2023-04-14 18:00 | 45030.75 | 0 | 13.1911 | 37.78
2023-04-14 18:30 | 45030.7708 | 0 | 13.206 | 37.78
2023-04-14 19:00 | 45030.7917 | 0 | 13.1428 | 37.78
2023-04-14 19:30 | 45030.8125 | 0 | 13.0756 | 37.78
2023-04-14 20:00 | 45030.8333 | 0 | 12.6477 | 37.78
2023-04-14 20:30 | 45030.8542 | 0 | 12.3646 | 37.78
2023-04-14 21:00 | 45030.875 | 0 | 12.0534 | 37.78
2023-04-14 21:30 | 45030.8958 | 0 | 11.4581 | 37.78
2023-04-14 22:00 | 45030.9167 | 0 | 11.0428 | 37.78
2023-04-14 22:30 | 45030.9375 | 0 | 10.4013 | 37.78
2023-04-14 23:00 | 45030.9583 | 0 | 9.9803 | 37.78
2023-04-14 23:30 | 45030.9792 | 0 | 9.5712 | 37.78
2023-04-15 | 45031 | 0 | 9.1214 | 37.78
2023-04-15 00:30 | 45031.0208 | 0 | 8.7971 | 37.78
2023-04-15 01:00 | 45031.0417 | 0 | 8.6653 | 37.78
2023-04-15 01:30 | 45031.0625 | 0 | 8.4584 | 37.78
2023-04-15 02:00 | 45031.0833 | 0 | 8.2817 | 37.78
2023-04-15 02:30 | 45031.1042 | 0 | 8.2649 | 37.78
2023-04-15 03:00 | 45031.125 | 0 | 8.3784 | 37.78
2023-04-15 03:30 | 45031.1458 | 0 | 8.1662 | 37.78
2023-04-15 04:00 | 45031.1667 | 0 | 8.2259 | 37.78
2023-04-15 04:30 | 45031.1875 | 0 | 8.2948 | 37.78
2023-04-15 05:00 | 45031.2083 | 0 | 8.5368 | 37.78
2023-04-15 05:30 | 45031.2292 | 0 | 8.6409 | 37.78
2023-04-15 06:00 | 45031.25 | 0 | 8.8568 | 37.78
2023-04-15 06:30 | 45031.2708 | 0 | 8.4732 | 37.78
2023-04-15 07:00 | 45031.2917 | 0 | 8.3765 | 37.78
2023-04-15 07:30 | 45031.3125 | 0 | 7.8247 | 37.78
2023-04-15 08:00 | 45031.3333 | 0 | 7.539 | 37.78
2023-04-15 08:30 | 45031.3542 | 0 | 7.3022 | 37.78
2023-04-15 09:00 | 45031.375 | 0 | 7.0775 | 37.78
2023-04-15 09:30 | 45031.3958 | 0 | 6.7342 | 37.78
2023-04-15 10:00 | 45031.4167 | 0 | 6.4691 | 37.78
2023-04-15 10:30 | 45031.4375 | 0 | 6.974 | 37.78
2023-04-15 11:00 | 45031.4583 | 0 | 6.7551 | 37.78
2023-04-15 11:30 | 45031.4792 | 0 | 6.1956 | 37.78
2023-04-15 12:00 | 45031.5 | 0 | 6.3203 | 37.78
2023-04-15 12:30 | 45031.5208 | 0 | 6.1694 | 37.78
2023-04-15 13:00 | 45031.5417 | 0 | 6.6182 | 37.78
2023-04-15 13:30 | 45031.5625 | 0 | 6.9741 | 37.78
2023-04-15 14:00 | 45031.5833 | 0 | 7.5246 | 37.78
2023-04-15 14:30 | 45031.6042 | 0 | 8.2657 | 37.78
2023-04-15 15:00 | 45031.625 | 0 | 9.0812 | 37.78
2023-04-15 15:30 | 45031.6458 | 0 | 9.9771 | 37.78
2023-04-15 16:00 | 45031.6667 | 0 | 10.9004 | 37.78
2023-04-15 16:30 | 45031.6875 | 0 | 11.5856 | 37.78
2023-04-15 17:00 | 45031.7083 | 0 | 11.8753 | 37.78
2023-04-15 17:30 | 45031.7292 | 0 | 12.0339 | 37.78
2023-04-15 18:00 | 45031.75 | 0 | 12.1228 | 37.78
2023-04-15 18:30 | 45031.7708 | 0 | 12.0262 | 37.78
2023-04-15 19:00 | 45031.7917 | 0 | 11.9125 | 37.78
2023-04-15 19:30 | 45031.8125 | 0 | 11.8513 | 37.78
2023-04-15 20:00 | 45031.8333 | 0 | 11.5029 | 37.78
2023-04-15 20:30 | 45031.8542 | 0 | 11.1493 | 37.78
2023-04-15 21:00 | 45031.875 | 0 | 10.7128 | 37.78
2023-04-15 21:30 | 45031.8958 | 0 | 10.4329 | 37.78
2023-04-15 22:00 | 45031.9167 | 0 | 10.0198 | 37.78
2023-04-15 22:30 | 45031.9375 | 0 | 9.5228 | 37.78
2023-04-15 23:00 | 45031.9583 | 0 | 9.1119 | 37.78
2023-04-15 23:30 | 45031.9792 | 0 | 8.5912 | 37.78
2023-04-16 | 45032 | 0 | 8.1735 | 37.78
2023-04-16 00:30 | 45032.0208 | 0 | 7.8474 | 37.78
2023-04-16 01:00 | 45032.0417 | 0 | 7.6376 | 37.78
2023-04-16 01:30 | 45032.0625 | 0 | 7.554 | 37.78
2023-04-16 02:00 | 45032.0833 | 0 | 7.5037 | 37.78
2023-04-16 02:30 | 45032.1042 | 0 | 7.474 | 37.78
2023-04-16 03:00 | 45032.125 | 0 | 7.4702 | 37.78
2023-04-16 03:30 | 45032.1458 | 0 | 7.353 | 37.78
2023-04-16 04:00 | 45032.1667 | 0 | 7.3661 | 37.78
2023-04-16 04:30 | 45032.1875 | 0 | 7.4852 | 37.78
2023-04-16 05:00 | 45032.2083 | 0 | 7.4666 | 37.78
2023-04-16 05:30 | 45032.2292 | 0 | 7.6397 | 37.78
2023-04-16 06:00 | 45032.25 | 0 | 7.7978 | 37.78
2023-04-16 06:30 | 45032.2708 | 0 | 7.5669 | 37.78
2023-04-16 07:00 | 45032.2917 | 0 | 7.4832 | 37.78
2023-04-16 07:30 | 45032.3125 | 0 | 6.9161 | 37.78
2023-04-16 08:00 | 45032.3333 | 0 | 6.7352 | 37.78
2023-04-16 08:30 | 45032.3542 | 0 | 6.3988 | 37.78
2023-04-16 09:00 | 45032.375 | 0 | 6.3833 | 37.78
2023-04-16 09:30 | 45032.3958 | 0 | 6.283 | 37.78
2023-04-16 10:00 | 45032.4167 | 0 | 6.0538 | 37.78
2023-04-16 10:30 | 45032.4375 | 0 | 6.0319 | 37.78
2023-04-16 11:00 | 45032.4583 | 0 | 6.0818 | 37.78
2023-04-16 11:30 | 45032.4792 | 0 | 6.1918 | 37.78
2023-04-16 12:00 | 45032.5 | 0 | 6.1824 | 37.78
2023-04-16 12:30 | 45032.5208 | 0 | 6.9087 | 37.78
2023-04-16 13:00 | 45032.5417 | 0 | 6.7761 | 37.78
2023-04-16 13:30 | 45032.5625 | 0 | 7.3516 | 37.78
2023-04-16 14:00 | 45032.5833 | 0 | 8.1781 | 37.78
2023-04-16 14:30 | 45032.6042 | 0 | 9.1124 | 37.78
2023-04-16 15:00 | 45032.625 | 0 | 10.1234 | 37.78
2023-04-16 15:30 | 45032.6458 | 0 | 11.1243 | 37.78
2023-04-16 16:00 | 45032.6667 | 0 | 12.7482 | 37.78
2023-04-16 16:30 | 45032.6875 | 0 | 12.7112 | 37.78
2023-04-16 17:00 | 45032.7083 | 0 | 13.1006 | 37.78
2023-04-16 17:30 | 45032.7292 | 0 | 13.3441 | 37.78
2023-04-16 18:00 | 45032.75 | 0 | 13.8401 | 37.78
2023-04-16 18:30 | 45032.7708 | 0 | 14.2496 | 37.78
2023-04-16 19:00 | 45032.7917 | 0 | 14.0286 | 37.78
2023-04-16 19:30 | 45032.8125 | 0 | 13.606 | 37.78
2023-04-16 20:00 | 45032.8333 | 0 | 13.206 | 37.78
2023-04-16 20:30 | 45032.8542 | 0 | 12.569 | 37.78
2023-04-16 21:00 | 45032.875 | 0 | 12.162 | 37.78
2023-04-16 21:30 | 45032.8958 | 0 | 11.4747 | 37.78
2023-04-16 22:00 | 45032.9167 | 0 | 10.9877 | 37.78
2023-04-16 22:30 | 45032.9375 | 0 | 10.4198 | 37.78
2023-04-16 23:00 | 45032.9583 | 0 | 9.7569 | 37.78
2023-04-16 23:30 | 45032.9792 | 0 | 9.4131 | 37.78
2023-04-17 | 45033 | 0 | 9.2192 | 37.78
2023-04-17 00:30 | 45033.0208 | 0 | 9.0502 | 37.78
2023-04-17 01:00 | 45033.0417 | 0 | 8.9776 | 37.78
2023-04-17 01:30 | 45033.0625 | 0 | 8.8233 | 37.78
2023-04-17 02:00 | 45033.0833 | 0 | 8.84 | 37.78
2023-04-17 02:30 | 45033.1042 | 0 | 8.8158 | 37.78
2023-04-17 03:00 | 45033.125 | 0 | 8.8289 | 37.78
2023-04-17 03:30 | 45033.1458 | 0 | 8.9612 | 37.78
2023-04-17 04:00 | 45033.1667 | 0 | 9.2011 | 37.78
2023-04-17 04:30 | 45033.1875 | 0 | 9.5464 | 37.78
2023-04-17 05:00 | 45033.2083 | 0 | 10.0824 | 37.78
2023-04-17 05:30 | 45033.2292 | 0 | 10.7292 | 37.78
2023-04-17 06:00 | 45033.25 | 0 | 11.6872 | 37.78
2023-04-17 06:30 | 45033.2708 | 0 | 12.2683 | 37.78
2023-04-17 07:00 | 45033.2917 | 0 | 12.8277 | 37.78
2023-04-17 07:30 | 45033.3125 | 0 | 13.4929 | 37.78
2023-04-17 08:00 | 45033.3333 | 0 | 13.3602 | 37.78
2023-04-17 08:30 | 45033.3542 | 0 | 12.6686 | 37.78
2023-04-17 09:00 | 45033.375 | 0 | 11.7074 | 37.78
2023-04-17 09:30 | 45033.3958 | 0 | 11.6346 | 37.78
2023-04-17 10:00 | 45033.4167 | 0 | 11.2244 | 37.78
2023-04-17 10:30 | 45033.4375 | 0 | 11.1813 | 37.78
2023-04-17 11:00 | 45033.4583 | 0 | 11.9972 | 37.78
2023-04-17 11:30 | 45033.4792 | 0 | 12.4055 | 37.78
2023-04-17 12:00 | 45033.5 | 0 | 12.1689 | 37.78
2023-04-17 12:30 | 45033.5208 | 0 | 12.6824 | 37.78
2023-04-17 13:00 | 45033.5417 | 0 | 12.6012 | 37.78
2023-04-17 13:30 | 45033.5625 | 0 | 14.3353 | 37.78
2023-04-17 14:00 | 45033.5833 | 0 | 15.6082 | 37.78
2023-04-17 14:30 | 45033.6042 | 0 | 15.2299 | 37.78
2023-04-17 15:00 | 45033.625 | 0 | 13.8185 | 37.78
2023-04-17 15:30 | 45033.6458 | 0 | 15.3107 | 37.78
2023-04-17 16:00 | 45033.6667 | 0 | 15.5675 | 37.78
2023-04-17 16:30 | 45033.6875 | 0 | 15.4169 | 37.78
2023-04-17 17:00 | 45033.7083 | 0 | 15.1267 | 37.78
2023-04-17 17:30 | 45033.7292 | 0 | 15.3172 | 37.78
2023-04-17 18:00 | 45033.75 | 0 | 15.3424 | 37.78
2023-04-17 18:30 | 45033.7708 | 0 | 15.2322 | 37.78
2023-04-17 19:00 | 45033.7917 | 0 | 14.9015 | 37.78
2023-04-17 19:30 | 45033.8125 | 0 | 14.6351 | 37.78
2023-04-17 20:00 | 45033.8333 | 0 | 14.2366 | 37.78
2023-04-17 20:30 | 45033.8542 | 0 | 13.6874 | 37.78
2023-04-17 21:00 | 45033.875 | 0 | 13.3623 | 37.78
2023-04-17 21:30 | 45033.8958 | 0 | 12.889 | 37.78
2023-04-17 22:00 | 45033.9167 | 0 | 12.0777 | 37.78
2023-04-17 22:30 | 45033.9375 | 0 | 11.2891 | 37.78
2023-04-17 23:00 | 45033.9583 | 0 | 10.6731 | 37.78
2023-04-17 23:30 | 45033.9792 | 0 | 10.109 | 37.78
2023-04-18 | 45034 | 0 | 9.7762 | 37.78
2023-04-18 00:30 | 45034.0208 | 0 | 9.445 | 37.78
2023-04-18 01:00 | 45034.0417 | 0 | 9.1507 | 37.78
2023-04-18 01:30 | 45034.0625 | 0 | 8.8901 | 37.78
2023-04-18 02:00 | 45034.0833 | 0 | 8.7562 | 37.78
2023-04-18 02:30 | 45034.1042 | 0 | 8.6402 | 37.78
2023-04-18 03:00 | 45034.125 | 0 | 8.7785 | 37.78
2023-04-18 03:30 | 45034.1458 | 0 | 8.9015 | 37.78
2023-04-18 04:00 | 45034.1667 | 0 | 9.0289 | 37.78
2023-04-18 04:30 | 45034.1875 | 0 | 9.132 | 37.78
2023-04-18 05:00 | 45034.2083 | 0 | 9.3076 | 37.78
2023-04-18 05:30 | 45034.2292 | 0 | 10.4446 | 37.78
2023-04-18 06:00 | 45034.25 | 0 | 12.0814 | 37.78
2023-04-18 06:30 | 45034.2708 | 0 | 12.6336 | 37.78
2023-04-18 07:00 | 45034.2917 | 0 | 12.6793 | 37.78
2023-04-18 07:30 | 45034.3125 | 0 | 12.1594 | 37.78
2023-04-18 08:00 | 45034.3333 | 0 | 11.7095 | 37.78
2023-04-18 08:30 | 45034.3542 | 0 | 11.3094 | 37.78
2023-04-18 09:00 | 45034.375 | 0 | 10.7736 | 37.78
2023-04-18 09:30 | 45034.3958 | 0 | 10.2702 | 37.78
2023-04-18 10:00 | 45034.4167 | 0 | 9.8354 | 37.78
2023-04-18 10:30 | 45034.4375 | 0 | 9.9484 | 37.78
2023-04-18 11:00 | 45034.4583 | 0 | 9.9164 | 37.78
2023-04-18 11:30 | 45034.4792 | 0 | 10.9482 | 37.78
2023-04-18 12:00 | 45034.5 | 0 | 10.9093 | 37.78
2023-04-18 12:30 | 45034.5208 | 0 | 10.3745 | 37.78
2023-04-18 13:00 | 45034.5417 | 0 | 10.8929 | 37.78
2023-04-18 13:30 | 45034.5625 | 0 | 10.7518 | 37.78
2023-04-18 14:00 | 45034.5833 | 0 | 11.7964 | 37.78
2023-04-18 14:30 | 45034.6042 | 0 | 11.9381 | 37.78
2023-04-18 15:00 | 45034.625 | 0 | 12.6592 | 37.78
2023-04-18 15:30 | 45034.6458 | 0 | 13.4143 | 37.78
2023-04-18 16:00 | 45034.6667 | 0 | 13.4662 | 37.78
2023-04-18 16:30 | 45034.6875 | 0 | 13.9021 | 37.78
2023-04-18 17:00 | 45034.7083 | 0 | 14.0174 | 37.78
2023-04-18 17:30 | 45034.7292 | 0 | 14.2087 | 37.78
2023-04-18 18:00 | 45034.75 | 0 | 14.2554 | 37.78
2023-04-18 18:30 | 45034.7708 | 0 | 14.2587 | 37.78
2023-04-18 19:00 | 45034.7917 | 0 | 14.0843 | 37.78
2023-04-18 19:30 | 45034.8125 | 0 | 13.7735 | 37.78
2023-04-18 20:00 | 45034.8333 | 0 | 13.3764 | 37.78
2023-04-18 20:30 | 45034.8542 | 0 | 12.8298 | 37.78
2023-04-18 21:00 | 45034.875 | 0 | 12.4302 | 37.78
2023-04-18 21:30 | 45034.8958 | 0 | 11.9321 | 37.78
2023-04-18 22:00 | 45034.9167 | 0 | 11.2917 | 37.78
2023-04-18 22:30 | 45034.9375 | 0 | 10.7027 | 37.78
2023-04-18 23:00 | 45034.9583 | 0 | 10.2391 | 37.78
2023-04-18 23:30 | 45034.9792 | 0 | 9.7353 | 37.78
2023-04-19 | 45035 | 0 | 9.3385 | 37.78
2023-04-19 00:30 | 45035.0208 | 0 | 8.9736 | 37.78
2023-04-19 01:00 | 45035.0417 | 0 | 8.9107 | 37.78
2023-04-19 01:30 | 45035.0625 | 0 | 8.691 | 37.78
2023-04-19 02:00 | 45035.0833 | 0 | 8.6092 | 37.78
2023-04-19 02:30 | 45035.1042 | 0 | 8.4826 | 37.78
2023-04-19 03:00 | 45035.125 | 0 | 8.5944 | 37.78
2023-04-19 03:30 | 45035.1458 | 0 | 8.7024 | 37.78
2023-04-19 04:00 | 45035.1667 | 0 | 8.9723 | 37.78
2023-04-19 04:30 | 45035.1875 | 0 | 9.1863 | 37.78
2023-04-19 05:00 | 45035.2083 | 0 | 9.7409 | 37.78
2023-04-19 05:30 | 45035.2292 | 0 | 10.4392 | 37.78
2023-04-19 06:00 | 45035.25 | 0 | 11.4033 | 37.78
2023-04-19 06:30 | 45035.2708 | 0 | 12.1646 | 37.78
2023-04-19 07:00 | 45035.2917 | 0 | 12.3411 | 37.78
2023-04-19 07:30 | 45035.3125 | 0 | 11.7154 | 37.78
2023-04-19 08:00 | 45035.3333 | 0 | 12.3906 | 37.78
2023-04-19 08:30 | 45035.3542 | 0 | 11.5369 | 37.78
2023-04-19 09:00 | 45035.375 | 0 | 11.1979 | 37.78
2023-04-19 09:30 | 45035.3958 | 0 | 10.6047 | 37.78
2023-04-19 10:00 | 45035.4167 | 0 | 9.4675 | 37.78
2023-04-19 10:30 | 45035.4375 | 0 | 10.2048 | 37.78
2023-04-19 11:00 | 45035.4583 | 0 | 10.962 | 37.78
2023-04-19 11:30 | 45035.4792 | 0 | 11.5652 | 37.78
2023-04-19 12:00 | 45035.5 | 0 | 10.2254 | 37.78
2023-04-19 12:30 | 45035.5208 | 0 | 9.2655 | 37.78
2023-04-19 13:00 | 45035.5417 | 0 | 8.8517 | 37.78
2023-04-19 13:30 | 45035.5625 | 0 | 10.3265 | 37.78
2023-04-19 14:00 | 45035.5833 | 0 | 10.8395 | 37.78
2023-04-19 14:30 | 45035.6042 | 0 | 10.6986 | 37.78
2023-04-19 15:00 | 45035.625 | 0 | 12.0302 | 37.78
2023-04-19 15:30 | 45035.6458 | 0 | 11.7668 | 37.78
2023-04-19 16:00 | 45035.6667 | 0 | 13.2416 | 37.78
2023-04-19 16:30 | 45035.6875 | 0 | 13.6786 | 37.78
2023-04-19 17:00 | 45035.7083 | 0 | 13.5152 | 37.78
2023-04-19 17:30 | 45035.7292 | 0 | 13.8859 | 37.78
2023-04-19 18:00 | 45035.75 | 0 | 14.0456 | 37.78
2023-04-19 18:30 | 45035.7708 | 0 | 14.0087 | 37.78
2023-04-19 19:00 | 45035.7917 | 0 | 13.8371 | 37.78
2023-04-19 19:30 | 45035.8125 | 0 | 13.5693 | 37.78
2023-04-19 20:00 | 45035.8333 | 0 | 13.2351 | 37.78
2023-04-19 20:30 | 45035.8542 | 0 | 12.7463 | 37.78
2023-04-19 21:00 | 45035.875 | 0 | 12.3545 | 37.78
2023-04-19 21:30 | 45035.8958 | 0 | 11.7486 | 37.78
2023-04-19 22:00 | 45035.9167 | 0 | 11.0471 | 37.78
2023-04-19 22:30 | 45035.9375 | 0 | 10.3334 | 37.78
2023-04-19 23:00 | 45035.9583 | 0 | 9.8345 | 37.78
2023-04-19 23:30 | 45035.9792 | 0 | 9.4625 | 37.78
2023-04-20 | 45036 | 0 | 9.1611 | 37.78
2023-04-20 00:30 | 45036.0208 | 0 | 8.715 | 37.78
2023-04-20 01:00 | 45036.0417 | 0 | 8.6164 | 37.78
2023-04-20 01:30 | 45036.0625 | 0 | 8.3754 | 37.78
2023-04-20 02:00 | 45036.0833 | 0 | 8.3072 | 37.78
2023-04-20 02:30 | 45036.1042 | 0 | 8.3266 | 37.78
2023-04-20 03:00 | 45036.125 | 0 | 8.3936 | 37.78
2023-04-20 03:30 | 45036.1458 | 0 | 8.3616 | 37.78
2023-04-20 04:00 | 45036.1667 | 0 | 8.5178 | 37.78
2023-04-20 04:30 | 45036.1875 | 0 | 8.811 | 37.78
2023-04-20 05:00 | 45036.2083 | 0 | 9.2363 | 37.78
2023-04-20 05:30 | 45036.2292 | 0 | 10.0084 | 37.78
2023-04-20 06:00 | 45036.25 | 0 | 10.8113 | 37.78
2023-04-20 06:30 | 45036.2708 | 0 | 11.3317 | 37.78
2023-04-20 07:00 | 45036.2917 | 0 | 11.3949 | 37.78
2023-04-20 07:30 | 45036.3125 | 0 | 11.7839 | 37.78
2023-04-20 08:00 | 45036.3333 | 0 | 10.8426 | 37.78
2023-04-20 08:30 | 45036.3542 | 0 | 9.4593 | 37.78
2023-04-20 09:00 | 45036.375 | 0 | 9.752 | 37.78
2023-04-20 09:30 | 45036.3958 | 0 | 8.4275 | 37.78
2023-04-20 10:00 | 45036.4167 | 0 | 8.3244 | 37.78
2023-04-20 10:30 | 45036.4375 | 0 | 8.5057 | 37.78
2023-04-20 11:00 | 45036.4583 | 0 | 8.7169 | 37.78
2023-04-20 11:30 | 45036.4792 | 0 | 9.8531 | 37.78
2023-04-20 12:00 | 45036.5 | 0 | 9.347 | 37.78
2023-04-20 12:30 | 45036.5208 | 0 | 10.1884 | 37.78
2023-04-20 13:00 | 45036.5417 | 0 | 12.0938 | 37.78
2023-04-20 13:30 | 45036.5625 | 0 | 11.9084 | 37.78
2023-04-20 14:00 | 45036.5833 | 0 | 12.369 | 37.78
2023-04-20 14:30 | 45036.6042 | 0 | 12.9917 | 37.78
2023-04-20 15:00 | 45036.625 | 0 | 12.4865 | 37.78
2023-04-20 15:30 | 45036.6458 | 0 | 12.6967 | 37.78
2023-04-20 16:00 | 45036.6667 | 0 | 13.1942 | 37.78
2023-04-20 16:30 | 45036.6875 | 0 | 13.2547 | 37.78
2023-04-20 17:00 | 45036.7083 | 0 | 13.3892 | 37.78
2023-04-20 17:30 | 45036.7292 | 0 | 14.0847 | 37.78
2023-04-20 18:00 | 45036.75 | 0 | 14.1807 | 37.78
2023-04-20 18:30 | 45036.7708 | 0 | 13.9071 | 37.78
2023-04-20 19:00 | 45036.7917 | 0 | 13.5802 | 37.78
2023-04-20 19:30 | 45036.8125 | 0 | 13.4764 | 37.78
2023-04-20 20:00 | 45036.8333 | 0 | 12.9407 | 37.78
2023-04-20 20:30 | 45036.8542 | 0 | 12.6712 | 37.78
2023-04-20 21:00 | 45036.875 | 0 | 12.409 | 37.78
2023-04-20 21:30 | 45036.8958 | 0 | 11.7805 | 37.78
2023-04-20 22:00 | 45036.9167 | 0 | 10.9087 | 37.78
2023-04-20 22:30 | 45036.9375 | 0 | 10.4351 | 37.78
2023-04-20 23:00 | 45036.9583 | 0 | 10.0538 | 37.78
2023-04-20 23:30 | 45036.9792 | 0 | 9.6151 | 37.78
2023-04-21 | 45037 | 0 | 9.2239 | 37.78
2023-04-21 00:30 | 45037.0208 | 0 | 8.7112 | 37.78
2023-04-21 01:00 | 45037.0417 | 0 | 8.6193 | 37.78
2023-04-21 01:30 | 45037.0625 | 0 | 8.3805 | 37.78
2023-04-21 02:00 | 45037.0833 | 0 | 8.1864 | 37.78
2023-04-21 02:30 | 45037.1042 | 0 | 8.093 | 37.78
2023-04-21 03:00 | 45037.125 | 0 | 8.1651 | 37.78
2023-04-21 03:30 | 45037.1458 | 0 | 8.3111 | 37.78
2023-04-21 04:00 | 45037.1667 | 0 | 8.5224 | 37.78
2023-04-21 04:30 | 45037.1875 | 0 | 8.689 | 37.78
2023-04-21 05:00 | 45037.2083 | 0 | 9.4896 | 37.78
2023-04-21 05:30 | 45037.2292 | 0 | 10.0605 | 37.78
2023-04-21 06:00 | 45037.25 | 0 | 10.7737 | 37.78
2023-04-21 06:30 | 45037.2708 | 0 | 11.1305 | 37.78
2023-04-21 07:00 | 45037.2917 | 0 | 11.2373 | 37.78
2023-04-21 07:30 | 45037.3125 | 0 | 11.1336 | 37.78
2023-04-21 08:00 | 45037.3333 | 0 | 10.5179 | 37.78
2023-04-21 08:30 | 45037.3542 | 0 | 9.9303 | 37.78
2023-04-21 09:00 | 45037.375 | 0 | 9.6364 | 37.78
2023-04-21 09:30 | 45037.3958 | 0 | 10.4637 | 37.78
2023-04-21 10:00 | 45037.4167 | 0 | 11.0145 | 37.78
2023-04-21 10:30 | 45037.4375 | 0 | 11.7226 | 37.78
2023-04-21 11:00 | 45037.4583 | 0 | 9.7936 | 37.78
2023-04-21 11:30 | 45037.4792 | 0 | 11.1561 | 37.78
2023-04-21 12:00 | 45037.5 | 0 | 10.6728 | 37.78
2023-04-21 12:30 | 45037.5208 | 0 | 9.3861 | 37.78
2023-04-21 13:00 | 45037.5417 | 0 | 11.8051 | 37.78
2023-04-21 13:30 | 45037.5625 | 0 | 10.6403 | 37.78
2023-04-21 14:00 | 45037.5833 | 0 | 12.4832 | 37.78
2023-04-21 14:30 | 45037.6042 | 0 | 12.5101 | 37.78
2023-04-21 15:00 | 45037.625 | 0 | 11.1305 | 37.78
2023-04-21 15:30 | 45037.6458 | 0 | 13.1196 | 37.78
2023-04-21 16:00 | 45037.6667 | 0 | 12.9779 | 37.78
2023-04-21 16:30 | 45037.6875 | 0 | 13.1888 | 37.78
2023-04-21 17:00 | 45037.7083 | 0 | 13.3814 | 37.78
2023-04-21 17:30 | 45037.7292 | 0 | 13.774 | 37.78
2023-04-21 18:00 | 45037.75 | 0 | 13.6265 | 37.78
2023-04-21 18:30 | 45037.7708 | 0 | 13.3172 | 37.78
2023-04-21 19:00 | 45037.7917 | 0 | 13.0029 | 37.78
2023-04-21 19:30 | 45037.8125 | 0 | 12.7092 | 37.78
2023-04-21 20:00 | 45037.8333 | 0 | 12.4037 | 37.78
2023-04-21 20:30 | 45037.8542 | 0 | 12.0208 | 37.78
2023-04-21 21:00 | 45037.875 | 0 | 11.8871 | 37.78
2023-04-21 21:30 | 45037.8958 | 0 | 11.1429 | 37.78
2023-04-21 22:00 | 45037.9167 | 0 | 10.4201 | 37.78
2023-04-21 22:30 | 45037.9375 | 0 | 10.0606 | 37.78
2023-04-21 23:00 | 45037.9583 | 0 | 9.7961 | 37.78
2023-04-21 23:30 | 45037.9792 | 0 | 9.4043 | 37.78
2023-04-22 | 45038 | 0 | 9.0345 | 37.78
2023-04-22 00:30 | 45038.0208 | 0 | 8.625 | 37.78
2023-04-22 01:00 | 45038.0417 | 0 | 8.4063 | 37.78
2023-04-22 01:30 | 45038.0625 | 0 | 8.1519 | 37.78
2023-04-22 02:00 | 45038.0833 | 0 | 8.0684 | 37.78
2023-04-22 02:30 | 45038.1042 | 0 | 8.0541 | 37.78
2023-04-22 03:00 | 45038.125 | 0 | 8.0048 | 37.78
2023-04-22 03:30 | 45038.1458 | 0 | 8.1806 | 37.78
2023-04-22 04:00 | 45038.1667 | 0 | 8.1177 | 37.78
2023-04-22 04:30 | 45038.1875 | 0 | 7.9521 | 37.78
2023-04-22 05:00 | 45038.2083 | 0 | 8.2257 | 37.78
2023-04-22 05:30 | 45038.2292 | 0 | 8.5073 | 37.78
2023-04-22 06:00 | 45038.25 | 0 | 8.7727 | 37.78
2023-04-22 06:30 | 45038.2708 | 0 | 10.8753 | 37.78
2023-04-22 07:00 | 45038.2917 | 0 | 17.5549 | 37.78
2023-04-22 07:30 | 45038.3125 | 0 | 16.9751 | 37.78
2023-04-22 08:00 | 45038.3333 | 0 | 13.8903 | 37.78
2023-04-22 08:30 | 45038.3542 | 0 | 13.6314 | 37.78
2023-04-22 09:00 | 45038.375 | 0 | 14.4682 | 37.78
2023-04-22 09:30 | 45038.3958 | 0 | 14.5646 | 37.78
2023-04-22 10:00 | 45038.4167 | 0 | 14.8856 | 37.78
2023-04-22 10:30 | 45038.4375 | 0 | 13.1146 | 37.78
2023-04-22 11:00 | 45038.4583 | 0 | 13.3901 | 37.78
2023-04-22 11:30 | 45038.4792 | 0 | 14.0301 | 37.78
2023-04-22 12:00 | 45038.5 | 0 | 16.7718 | 37.78
2023-04-22 12:30 | 45038.5208 | 0 | 13.3714 | 37.78
2023-04-22 13:00 | 45038.5417 | 0 | 13.8536 | 37.78
2023-04-22 13:30 | 45038.5625 | 0 | 9.5501 | 37.78
2023-04-22 14:00 | 45038.5833 | 0 | 9.5074 | 37.78
2023-04-22 14:30 | 45038.6042 | 0 | 9.3423 | 37.78
2023-04-22 15:00 | 45038.625 | 0 | 9.3694 | 37.78
2023-04-22 15:30 | 45038.6458 | 0 | 10.7198 | 37.78
2023-04-22 16:00 | 45038.6667 | 0 | 10.8249 | 37.78
2023-04-22 16:30 | 45038.6875 | 0 | 11.0048 | 37.78
2023-04-22 17:00 | 45038.7083 | 0 | 11.0226 | 37.78
2023-04-22 17:30 | 45038.7292 | 0 | 11.4207 | 37.78
2023-04-22 18:00 | 45038.75 | 0 | 11.5009 | 37.78
2023-04-22 18:30 | 45038.7708 | 0 | 11.2533 | 37.78
2023-04-22 19:00 | 45038.7917 | 0 | 10.9417 | 37.78
2023-04-22 19:30 | 45038.8125 | 0 | 10.8159 | 37.78
2023-04-22 20:00 | 45038.8333 | 0 | 10.4174 | 37.78
2023-04-22 20:30 | 45038.8542 | 0 | 10.2037 | 37.78
2023-04-22 21:00 | 45038.875 | 0 | 10.1568 | 37.78
2023-04-22 21:30 | 45038.8958 | 0 | 9.4707 | 37.78
2023-04-22 22:00 | 45038.9167 | 0 | 9.1107 | 37.78
2023-04-22 22:30 | 45038.9375 | 0 | 8.8031 | 37.78
2023-04-22 23:00 | 45038.9583 | 0 | 8.6366 | 37.78
2023-04-22 23:30 | 45038.9792 | 0 | 8.2191 | 37.78
2023-04-23 | 45039 | 0 | 7.9117 | 37.78
2023-04-23 00:30 | 45039.0208 | 0 | 7.5964 | 37.78
2023-04-23 01:00 | 45039.0417 | 0 | 7.3703 | 37.78
2023-04-23 01:30 | 45039.0625 | 0 | 7.324 | 37.78
2023-04-23 02:00 | 45039.0833 | 0 | 7.2134 | 37.78
2023-04-23 02:30 | 45039.1042 | 0 | 7.238 | 37.78
2023-04-23 03:00 | 45039.125 | 0 | 7.2662 | 37.78
2023-04-23 03:30 | 45039.1458 | 0 | 7.2174 | 37.78
2023-04-23 04:00 | 45039.1667 | 0 | 7.1373 | 37.78
2023-04-23 04:30 | 45039.1875 | 0 | 7.111 | 37.78
2023-04-23 05:00 | 45039.2083 | 0 | 7.2529 | 37.78
2023-04-23 05:30 | 45039.2292 | 0 | 7.4538 | 37.78
2023-04-23 06:00 | 45039.25 | 0 | 7.6452 | 37.78
2023-04-23 06:30 | 45039.2708 | 0 | 7.5148 | 37.78
2023-04-23 07:00 | 45039.2917 | 0 | 7.2931 | 37.78
2023-04-23 07:30 | 45039.3125 | 0 | 6.8447 | 37.78
2023-04-23 08:00 | 45039.3333 | 0 | 6.5699 | 37.78
2023-04-23 08:30 | 45039.3542 | 0 | 5.8358 | 37.78
2023-04-23 09:00 | 45039.375 | 0 | 5.5075 | 37.78
2023-04-23 09:30 | 45039.3958 | 0 | 5.2293 | 37.78
2023-04-23 10:00 | 45039.4167 | 0 | 5.3864 | 37.78
2023-04-23 10:30 | 45039.4375 | 0 | 4.9211 | 37.78
2023-04-23 11:00 | 45039.4583 | 0 | 4.6761 | 37.78
2023-04-23 11:30 | 45039.4792 | 0 | 6.5458 | 37.78
2023-04-23 12:00 | 45039.5 | 0 | 5.588 | 37.78
2023-04-23 12:30 | 45039.5208 | 0 | 5.7406 | 37.78
2023-04-23 13:00 | 45039.5417 | 0 | 5.9436 | 37.78
2023-04-23 13:30 | 45039.5625 | 0 | 5.4247 | 37.78
2023-04-23 14:00 | 45039.5833 | 0 | 6.676 | 37.78
2023-04-23 14:30 | 45039.6042 | 0 | 7.9247 | 37.78
2023-04-23 15:00 | 45039.625 | 0 | 8.643 | 37.78
2023-04-23 15:30 | 45039.6458 | 0 | 8.8126 | 37.78
2023-04-23 16:00 | 45039.6667 | 0 | 9.6393 | 37.78
2023-04-23 16:30 | 45039.6875 | 0 | 10.7456 | 37.78
2023-04-23 17:00 | 45039.7083 | 0 | 11.2396 | 37.78
2023-04-23 17:30 | 45039.7292 | 0 | 11.7712 | 37.78
2023-04-23 18:00 | 45039.75 | 0 | 11.9485 | 37.78
2023-04-23 18:30 | 45039.7708 | 0 | 11.7688 | 37.78
2023-04-23 19:00 | 45039.7917 | 0 | 11.3035 | 37.78
2023-04-23 19:30 | 45039.8125 | 0 | 11.0246 | 37.78
2023-04-23 20:00 | 45039.8333 | 0 | 10.6581 | 37.78
2023-04-23 20:30 | 45039.8542 | 0 | 10.1746 | 37.78
2023-04-23 21:00 | 45039.875 | 0 | 10.2032 | 37.78
2023-04-23 21:30 | 45039.8958 | 0 | 9.6402 | 37.78
2023-04-23 22:00 | 45039.9167 | 0 | 9.0374 | 37.78
2023-04-23 22:30 | 45039.9375 | 0 | 8.6456 | 37.78
2023-04-23 23:00 | 45039.9583 | 0 | 8.394 | 37.78
2023-04-23 23:30 | 45039.9792 | 0 | 8.3357 | 37.78
2023-04-24 | 45040 | 0 | 8.0102 | 37.78
2023-04-24 00:30 | 45040.0208 | 0 | 7.8548 | 37.78
2023-04-24 01:00 | 45040.0417 | 0 | 7.6436 | 37.78
2023-04-24 01:30 | 45040.0625 | 0 | 7.5776 | 37.78
2023-04-24 02:00 | 45040.0833 | 0 | 7.5805 | 37.78
2023-04-24 02:30 | 45040.1042 | 0 | 7.6968 | 37.78
2023-04-24 03:00 | 45040.125 | 0 | 7.7356 | 37.78
2023-04-24 03:30 | 45040.1458 | 0 | 7.8519 | 37.78
2023-04-24 04:00 | 45040.1667 | 0 | 8.1092 | 37.78
2023-04-24 04:30 | 45040.1875 | 0 | 8.4302 | 37.78
2023-04-24 05:00 | 45040.2083 | 0 | 8.9177 | 37.78
2023-04-24 05:30 | 45040.2292 | 0 | 9.768 | 37.78
2023-04-24 06:00 | 45040.25 | 0 | 10.5712 | 37.78
2023-04-24 06:30 | 45040.2708 | 0 | 11.2158 | 37.78
2023-04-24 07:00 | 45040.2917 | 0 | 11.4307 | 37.78
2023-04-24 07:30 | 45040.3125 | 0 | 10.9282 | 37.78
2023-04-24 08:00 | 45040.3333 | 0 | 10.2404 | 37.78
2023-04-24 08:30 | 45040.3542 | 0 | 10.0558 | 37.78
2023-04-24 09:00 | 45040.375 | 0 | 10.2566 | 37.78
2023-04-24 09:30 | 45040.3958 | 0 | 11.1737 | 37.78
2023-04-24 10:00 | 45040.4167 | 0 | 11.4949 | 37.78
2023-04-24 10:30 | 45040.4375 | 0 | 12.0602 | 37.78
2023-04-24 11:00 | 45040.4583 | 0 | 11.6087 | 37.78
2023-04-24 11:30 | 45040.4792 | 0 | 11.9369 | 37.78
2023-04-24 12:00 | 45040.5 | 0 | 10.1633 | 37.78
2023-04-24 12:30 | 45040.5208 | 0 | 7.7481 | 37.78
2023-04-24 13:00 | 45040.5417 | 0 | 10.5725 | 37.78
2023-04-24 13:30 | 45040.5625 | 0 | 11.645 | 37.78
2023-04-24 14:00 | 45040.5833 | 0 | 9.424 | 37.78
2023-04-24 14:30 | 45040.6042 | 0 | 12.3026 | 37.78
2023-04-24 15:00 | 45040.625 | 0 | 11.9516 | 37.78
2023-04-24 15:30 | 45040.6458 | 0 | 12.2538 | 37.78
2023-04-24 16:00 | 45040.6667 | 0 | 12.1387 | 37.78
2023-04-24 16:30 | 45040.6875 | 0 | 12.5383 | 37.78
2023-04-24 17:00 | 45040.7083 | 0 | 13.1023 | 37.78
2023-04-24 17:30 | 45040.7292 | 0 | 13.6021 | 37.78
2023-04-24 18:00 | 45040.75 | 0 | 13.7049 | 37.78
2023-04-24 18:30 | 45040.7708 | 0 | 13.4792 | 37.78
2023-04-24 19:00 | 45040.7917 | 0 | 12.8739 | 37.78
2023-04-24 19:30 | 45040.8125 | 0 | 12.5474 | 37.78
2023-04-24 20:00 | 45040.8333 | 0 | 11.9868 | 37.78
2023-04-24 20:30 | 45040.8542 | 0 | 11.5592 | 37.78
2023-04-24 21:00 | 45040.875 | 0 | 11.4343 | 37.78
2023-04-24 21:30 | 45040.8958 | 0 | 10.8363 | 37.78
2023-04-24 22:00 | 45040.9167 | 0 | 10.1814 | 37.78
2023-04-24 22:30 | 45040.9375 | 0 | 9.8413 | 37.78
2023-04-24 23:00 | 45040.9583 | 0 | 9.5909 | 37.78
2023-04-24 23:30 | 45040.9792 | 0 | 9.2578 | 37.78
2023-04-25 | 45041 | 0 | 8.7908 | 37.78
2023-04-25 00:30 | 45041.0208 | 0 | 8.5191 | 37.78
2023-04-25 01:00 | 45041.0417 | 0 | 8.2667 | 37.78
2023-04-25 01:30 | 45041.0625 | 0 | 8.0564 | 37.78
2023-04-25 02:00 | 45041.0833 | 0 | 7.9608 | 37.78
2023-04-25 02:30 | 45041.1042 | 0 | 7.8851 | 37.78
2023-04-25 03:00 | 45041.125 | 0 | 7.7816 | 37.78
2023-04-25 03:30 | 45041.1458 | 0 | 7.7294 | 37.78
2023-04-25 04:00 | 45041.1667 | 0 | 7.774 | 37.78
2023-04-25 04:30 | 45041.1875 | 0 | 7.9257 | 37.78
2023-04-25 05:00 | 45041.2083 | 0 | 8.0146 | 37.78
2023-04-25 05:30 | 45041.2292 | 0 | 8.0861 | 37.78
2023-04-25 06:00 | 45041.25 | 0 | 8.2728 | 37.78
2023-04-25 06:30 | 45041.2708 | 0 | 8.2345 | 37.78
2023-04-25 07:00 | 45041.2917 | 0 | 8.2596 | 37.78
2023-04-25 07:30 | 45041.3125 | 0 | 7.7794 | 37.78
2023-04-25 08:00 | 45041.3333 | 0 | 7.4676 | 37.78
2023-04-25 08:30 | 45041.3542 | 0 | 6.769 | 37.78
2023-04-25 09:00 | 45041.375 | 0 | 6.5189 | 37.78
2023-04-25 09:30 | 45041.3958 | 0 | 7.0481 | 37.78
2023-04-25 10:00 | 45041.4167 | 0 | 8.8939 | 37.78
2023-04-25 10:30 | 45041.4375 | 0 | 6.325 | 37.78
2023-04-25 11:00 | 45041.4583 | 0 | 6.3001 | 37.78
2023-04-25 11:30 | 45041.4792 | 0 | 9.221 | 37.78
2023-04-25 12:00 | 45041.5 | 0 | 6.5857 | 37.78
2023-04-25 12:30 | 45041.5208 | 0 | 7.4406 | 37.78
2023-04-25 13:00 | 45041.5417 | 0 | 9.1278 | 37.78
2023-04-25 13:30 | 45041.5625 | 0 | 9.3468 | 37.78
2023-04-25 14:00 | 45041.5833 | 0 | 9.4523 | 37.78
2023-04-25 14:30 | 45041.6042 | 0 | 8.4977 | 37.78
2023-04-25 15:00 | 45041.625 | 0 | 9.8617 | 37.78
2023-04-25 15:30 | 45041.6458 | 0 | 9.8513 | 37.78
2023-04-25 16:00 | 45041.6667 | 0 | 10.6789 | 37.78
2023-04-25 16:30 | 45041.6875 | 0 | 11.1144 | 37.78
2023-04-25 17:00 | 45041.7083 | 0 | 11.5011 | 37.78
2023-04-25 17:30 | 45041.7292 | 0 | 12.1943 | 37.78
2023-04-25 18:00 | 45041.75 | 0 | 12.216 | 37.78
2023-04-25 18:30 | 45041.7708 | 0 | 11.8444 | 37.78
2023-04-25 19:00 | 45041.7917 | 0 | 11.3356 | 37.78
2023-04-25 19:30 | 45041.8125 | 0 | 10.9706 | 37.78
2023-04-25 20:00 | 45041.8333 | 0 | 10.6182 | 37.78
2023-04-25 20:30 | 45041.8542 | 0 | 10.181 | 37.78
2023-04-25 21:00 | 45041.875 | 0 | 10.0325 | 37.78
2023-04-25 21:30 | 45041.8958 | 0 | 9.4836 | 37.78
2023-04-25 22:00 | 45041.9167 | 0 | 8.9402 | 37.78
2023-04-25 22:30 | 45041.9375 | 0 | 8.4687 | 37.78
2023-04-25 23:00 | 45041.9583 | 0 | 8.1579 | 37.78
2023-04-25 23:30 | 45041.9792 | 0 | 8.0557 | 37.78
2023-04-26 | 45042 | 0 | 7.871 | 37.78
2023-04-26 00:30 | 45042.0208 | 0 | 7.5299 | 37.78
2023-04-26 01:00 | 45042.0417 | 0 | 7.4162 | 37.78
2023-04-26 01:30 | 45042.0625 | 0 | 7.233 | 37.78
2023-04-26 02:00 | 45042.0833 | 0 | 7.2341 | 37.78
2023-04-26 02:30 | 45042.1042 | 0 | 7.2564 | 37.78
2023-04-26 03:00 | 45042.125 | 0 | 7.3165 | 37.78
2023-04-26 03:30 | 45042.1458 | 0 | 7.5769 | 37.78
2023-04-26 04:00 | 45042.1667 | 0 | 7.9494 | 37.78
2023-04-26 04:30 | 45042.1875 | 0 | 8.3448 | 37.78
2023-04-26 05:00 | 45042.2083 | 0 | 8.9434 | 37.78
2023-04-26 05:30 | 45042.2292 | 0 | 9.563 | 37.78
2023-04-26 06:00 | 45042.25 | 0 | 10.7147 | 37.78
2023-04-26 06:30 | 45042.2708 | 0 | 11.4863 | 37.78
2023-04-26 07:00 | 45042.2917 | 0 | 11.5821 | 37.78
2023-04-26 07:30 | 45042.3125 | 0 | 12.0565 | 37.78
2023-04-26 08:00 | 45042.3333 | 0 | 10.5578 | 37.78
2023-04-26 08:30 | 45042.3542 | 0 | 11.363 | 37.78
2023-04-26 09:00 | 45042.375 | 0 | 8.9389 | 37.78
2023-04-26 09:30 | 45042.3958 | 0 | 9.6819 | 37.78
2023-04-26 10:00 | 45042.4167 | 0 | 9.2244 | 37.78
2023-04-26 10:30 | 45042.4375 | 0 | 9.2137 | 37.78
2023-04-26 11:00 | 45042.4583 | 0 | 10.1785 | 37.78
2023-04-26 11:30 | 45042.4792 | 0 | 10.5774 | 37.78
2023-04-26 12:00 | 45042.5 | 0 | 10.3648 | 37.78
2023-04-26 12:30 | 45042.5208 | 0 | 11.1322 | 37.78
2023-04-26 13:00 | 45042.5417 | 0 | 10.6854 | 37.78
2023-04-26 13:30 | 45042.5625 | 0 | 10.8749 | 37.78
2023-04-26 14:00 | 45042.5833 | 0 | 11.3103 | 37.78
2023-04-26 14:30 | 45042.6042 | 0 | 12.6847 | 37.78
2023-04-26 15:00 | 45042.625 | 0 | 11.3107 | 37.78
2023-04-26 15:30 | 45042.6458 | 0 | 11.3183 | 37.78
2023-04-26 16:00 | 45042.6667 | 0 | 12.3105 | 37.78
2023-04-26 16:30 | 45042.6875 | 0 | 12.8512 | 37.78
2023-04-26 17:00 | 45042.7083 | 0 | 13.271 | 37.78
2023-04-26 17:30 | 45042.7292 | 0 | 13.8908 | 37.78
2023-04-26 18:00 | 45042.75 | 0 | 14.0994 | 37.78
2023-04-26 18:30 | 45042.7708 | 0 | 13.8658 | 37.78
2023-04-26 19:00 | 45042.7917 | 0 | 13.7501 | 37.78
2023-04-26 19:30 | 45042.8125 | 0 | 13.3969 | 37.78
2023-04-26 20:00 | 45042.8333 | 0 | 12.7722 | 37.78
2023-04-26 20:30 | 45042.8542 | 0 | 12.2402 | 37.78
2023-04-26 21:00 | 45042.875 | 0 | 11.9475 | 37.78
2023-04-26 21:30 | 45042.8958 | 0 | 11.1766 | 37.78
2023-04-26 22:00 | 45042.9167 | 0 | 10.4244 | 37.78
2023-04-26 22:30 | 45042.9375 | 0 | 9.9946 | 37.78
2023-04-26 23:00 | 45042.9583 | 0 | 9.6363 | 37.78
2023-04-26 23:30 | 45042.9792 | 0 | 9.5429 | 37.78
2023-04-27 | 45043 | 0 | 9.1021 | 37.78
2023-04-27 00:30 | 45043.0208 | 0 | 8.7367 | 37.78
2023-04-27 01:00 | 45043.0417 | 0 | 8.4001 | 37.78
2023-04-27 01:30 | 45043.0625 | 0 | 8.2213 | 37.78
2023-04-27 02:00 | 45043.0833 | 0 | 8.2064 | 37.78
2023-04-27 02:30 | 45043.1042 | 0 | 8.1984 | 37.78
2023-04-27 03:00 | 45043.125 | 0 | 8.1194 | 37.78
2023-04-27 03:30 | 45043.1458 | 0 | 8.1817 | 37.78
2023-04-27 04:00 | 45043.1667 | 0 | 8.4514 | 37.78
2023-04-27 04:30 | 45043.1875 | 0 | 8.9374 | 37.78
2023-04-27 05:00 | 45043.2083 | 0 | 9.4783 | 37.78
2023-04-27 05:30 | 45043.2292 | 0 | 10.0633 | 37.78
2023-04-27 06:00 | 45043.25 | 0 | 11.0825 | 37.78
2023-04-27 06:30 | 45043.2708 | 0 | 11.7311 | 37.78
2023-04-27 07:00 | 45043.2917 | 0 | 11.9622 | 37.78
2023-04-27 07:30 | 45043.3125 | 0 | 11.2157 | 37.78
2023-04-27 08:00 | 45043.3333 | 0 | 10.9654 | 37.78
2023-04-27 08:30 | 45043.3542 | 0 | 10.4278 | 37.78
2023-04-27 09:00 | 45043.375 | 0 | 9.8917 | 37.78
2023-04-27 09:30 | 45043.3958 | 0 | 10.1392 | 37.78
2023-04-27 10:00 | 45043.4167 | 0 | 9.4908 | 37.78
2023-04-27 10:30 | 45043.4375 | 0 | 10.9129 | 37.78
2023-04-27 11:00 | 45043.4583 | 0 | 11.2786 | 37.78
2023-04-27 11:30 | 45043.4792 | 0 | 12.1813 | 37.78
2023-04-27 12:00 | 45043.5 | 0 | 10.9759 | 37.78
2023-04-27 12:30 | 45043.5208 | 0 | 12.2005 | 37.78
2023-04-27 13:00 | 45043.5417 | 0 | 8.0439 | 37.78
2023-04-27 13:30 | 45043.5625 | 0 | 10.2454 | 37.78
2023-04-27 14:00 | 45043.5833 | 0 | 10.9476 | 37.78
2023-04-27 14:30 | 45043.6042 | 0 | 12.0318 | 37.78
2023-04-27 15:00 | 45043.625 | 0 | 11.7719 | 37.78
2023-04-27 15:30 | 45043.6458 | 0 | 11.8912 | 37.78
2023-04-27 16:00 | 45043.6667 | 0 | 12.7105 | 37.78
2023-04-27 16:30 | 45043.6875 | 0 | 13.1539 | 37.78
2023-04-27 17:00 | 45043.7083 | 0 | 13.4783 | 37.78
2023-04-27 17:30 | 45043.7292 | 0 | 13.8333 | 37.78
2023-04-27 18:00 | 45043.75 | 0 | 13.8497 | 37.78
2023-04-27 18:30 | 45043.7708 | 0 | 13.7002 | 37.78
2023-04-27 19:00 | 45043.7917 | 0 | 13.1253 | 37.78
2023-04-27 19:30 | 45043.8125 | 0 | 12.6232 | 37.78
2023-04-27 20:00 | 45043.8333 | 0 | 12.8063 | 37.78
2023-04-27 20:30 | 45043.8542 | 0 | 12.3341 | 37.78
2023-04-27 21:00 | 45043.875 | 0 | 12.1266 | 37.78
2023-04-27 21:30 | 45043.8958 | 0 | 11.3138 | 37.78
2023-04-27 22:00 | 45043.9167 | 0 | 10.6922 | 37.78
2023-04-27 22:30 | 45043.9375 | 0 | 10.2627 | 37.78
2023-04-27 23:00 | 45043.9583 | 0 | 9.9424 | 37.78
2023-04-27 23:30 | 45043.9792 | 0 | 9.5653 | 37.78
2023-04-28 | 45044 | 0 | 9.2718 | 37.78
2023-04-28 00:30 | 45044.0208 | 0 | 8.7487 | 37.78
2023-04-28 01:00 | 45044.0417 | 0 | 8.5878 | 37.78
2023-04-28 01:30 | 45044.0625 | 0 | 8.4612 | 37.78
2023-04-28 02:00 | 45044.0833 | 0 | 8.1864 | 37.78
2023-04-28 02:30 | 45044.1042 | 0 | 8.2836 | 37.78
2023-04-28 03:00 | 45044.125 | 0 | 8.353 | 37.78
2023-04-28 03:30 | 45044.1458 | 0 | 8.4274 | 37.78
2023-04-28 04:00 | 45044.1667 | 0 | 8.8373 | 37.78
2023-04-28 04:30 | 45044.1875 | 0 | 8.9938 | 37.78
2023-04-28 05:00 | 45044.2083 | 0 | 9.5666 | 37.78
2023-04-28 05:30 | 45044.2292 | 0 | 10.1618 | 37.78
2023-04-28 06:00 | 45044.25 | 0 | 11.1146 | 37.78
2023-04-28 06:30 | 45044.2708 | 0 | 11.5459 | 37.78
2023-04-28 07:00 | 45044.2917 | 0 | 11.873 | 37.78
2023-04-28 07:30 | 45044.3125 | 0 | 11.5243 | 37.78
2023-04-28 08:00 | 45044.3333 | 0 | 10.9825 | 37.78
2023-04-28 08:30 | 45044.3542 | 0 | 10.1028 | 37.78
2023-04-28 09:00 | 45044.375 | 0 | 10.356 | 37.78
2023-04-28 09:30 | 45044.3958 | 0 | 9.6255 | 37.78
2023-04-28 10:00 | 45044.4167 | 0 | 11.006 | 37.78
2023-04-28 10:30 | 45044.4375 | 0 | 11.1521 | 37.78
2023-04-28 11:00 | 45044.4583 | 0 | 11.6309 | 37.78
2023-04-28 11:30 | 45044.4792 | 0 | 9.9947 | 37.78
2023-04-28 12:00 | 45044.5 | 0 | 8.8752 | 37.78
2023-04-28 12:30 | 45044.5208 | 0 | 8.3953 | 37.78
2023-04-28 13:00 | 45044.5417 | 0 | 10.6596 | 37.78
2023-04-28 13:30 | 45044.5625 | 0 | 10.9325 | 37.78
2023-04-28 14:00 | 45044.5833 | 0 | 10.375 | 37.78
2023-04-28 14:30 | 45044.6042 | 0 | 11.0287 | 37.78
2023-04-28 15:00 | 45044.625 | 0 | 12.7262 | 37.78
2023-04-28 15:30 | 45044.6458 | 0 | 12.3519 | 37.78
2023-04-28 16:00 | 45044.6667 | 0 | 12.3618 | 37.78
2023-04-28 16:30 | 45044.6875 | 0 | 12.9526 | 37.78
2023-04-28 17:00 | 45044.7083 | 0 | 13.3555 | 37.78
2023-04-28 17:30 | 45044.7292 | 0 | 13.5147 | 37.78
2023-04-28 18:00 | 45044.75 | 0 | 13.2091 | 37.78
2023-04-28 18:30 | 45044.7708 | 0 | 12.9278 | 37.78
2023-04-28 19:00 | 45044.7917 | 0 | 12.657 | 37.78
2023-04-28 19:30 | 45044.8125 | 0 | 12.4628 | 37.78
2023-04-28 20:00 | 45044.8333 | 0 | 12.1156 | 37.78
2023-04-28 20:30 | 45044.8542 | 0 | 11.6383 | 37.78
2023-04-28 21:00 | 45044.875 | 0 | 11.4125 | 37.78
2023-04-28 21:30 | 45044.8958 | 0 | 10.7304 | 37.78
2023-04-28 22:00 | 45044.9167 | 0 | 10.2273 | 37.78
2023-04-28 22:30 | 45044.9375 | 0 | 10.0031 | 37.78
2023-04-28 23:00 | 45044.9583 | 0 | 9.59 | 37.78
2023-04-28 23:30 | 45044.9792 | 0 | 9.2733 | 37.78
2023-04-29 | 45045 | 0 | 8.8236 | 37.78
2023-04-29 00:30 | 45045.0208 | 0 | 8.3565 | 37.78
2023-04-29 01:00 | 45045.0417 | 0 | 8.2025 | 37.78
2023-04-29 01:30 | 45045.0625 | 0 | 8.0347 | 37.78
2023-04-29 02:00 | 45045.0833 | 0 | 7.932 | 37.78
2023-04-29 02:30 | 45045.1042 | 0 | 7.896 | 37.78
2023-04-29 03:00 | 45045.125 | 0 | 7.8033 | 37.78
2023-04-29 03:30 | 45045.1458 | 0 | 7.884 | 37.78
2023-04-29 04:00 | 45045.1667 | 0 | 7.9825 | 37.78
2023-04-29 04:30 | 45045.1875 | 0 | 7.8983 | 37.78
2023-04-29 05:00 | 45045.2083 | 0 | 8.054 | 37.78
2023-04-29 05:30 | 45045.2292 | 0 | 8.3448 | 37.78
2023-04-29 06:00 | 45045.25 | 0 | 8.5311 | 37.78
2023-04-29 06:30 | 45045.2708 | 0 | 8.8058 | 37.78
2023-04-29 07:00 | 45045.2917 | 0 | 8.7298 | 37.78
2023-04-29 07:30 | 45045.3125 | 0 | 8.8169 | 37.78
2023-04-29 08:00 | 45045.3333 | 0 | 9.3462 | 37.78
2023-04-29 08:30 | 45045.3542 | 0 | 8.325 | 37.78
2023-04-29 09:00 | 45045.375 | 0 | 7.0215 | 37.78
2023-04-29 09:30 | 45045.3958 | 0 | 6.5881 | 37.78
2023-04-29 10:00 | 45045.4167 | 0 | 5.888 | 37.78
2023-04-29 10:30 | 45045.4375 | 0 | 6.6869 | 37.78
2023-04-29 11:00 | 45045.4583 | 0 | 7.3497 | 37.78
2023-04-29 11:30 | 45045.4792 | 0 | 8.006 | 37.78
2023-04-29 12:00 | 45045.5 | 0 | 7.5909 | 37.78
2023-04-29 12:30 | 45045.5208 | 0 | 8.5312 | 37.78
2023-04-29 13:00 | 45045.5417 | 0 | 8.5414 | 37.78
2023-04-29 13:30 | 45045.5625 | 0 | 9.5945 | 37.78
2023-04-29 14:00 | 45045.5833 | 0 | 9.8625 | 37.78
2023-04-29 14:30 | 45045.6042 | 0 | 9.7215 | 37.78
2023-04-29 15:00 | 45045.625 | 0 | 10.3594 | 37.78
2023-04-29 15:30 | 45045.6458 | 0 | 10.4758 | 37.78
2023-04-29 16:00 | 45045.6667 | 0 | 10.5811 | 37.78
2023-04-29 16:30 | 45045.6875 | 0 | 10.7534 | 37.78
2023-04-29 17:00 | 45045.7083 | 0 | 11.1297 | 37.78
2023-04-29 17:30 | 45045.7292 | 0 | 11.419 | 37.78
2023-04-29 18:00 | 45045.75 | 0 | 11.5414 | 37.78
2023-04-29 18:30 | 45045.7708 | 0 | 11.1882 | 37.78
2023-04-29 19:00 | 45045.7917 | 0 | 10.8899 | 37.78
2023-04-29 19:30 | 45045.8125 | 0 | 10.6793 | 37.78
2023-04-29 20:00 | 45045.8333 | 0 | 10.4106 | 37.78
2023-04-29 20:30 | 45045.8542 | 0 | 10.0269 | 37.78
2023-04-29 21:00 | 45045.875 | 0 | 10.0635 | 37.78
2023-04-29 21:30 | 45045.8958 | 0 | 9.5654 | 37.78
2023-04-29 22:00 | 45045.9167 | 0 | 9.0607 | 37.78
2023-04-29 22:30 | 45045.9375 | 0 | 8.8255 | 37.78
2023-04-29 23:00 | 45045.9583 | 0 | 8.5045 | 37.78
2023-04-29 23:30 | 45045.9792 | 0 | 8.3192 | 37.78
2023-04-30 | 45046 | 0 | 7.8542 | 37.78
2023-04-30 00:30 | 45046.0208 | 0 | 7.5553 | 37.78
2023-04-30 01:00 | 45046.0417 | 0 | 7.4454 | 37.78
2023-04-30 01:30 | 45046.0625 | 0 | 7.3687 | 37.78
2023-04-30 02:00 | 45046.0833 | 0 | 7.2713 | 37.78
2023-04-30 02:30 | 45046.1042 | 0 | 7.1832 | 37.78
2023-04-30 03:00 | 45046.125 | 0 | 7.2375 | 37.78
2023-04-30 03:30 | 45046.1458 | 0 | 7.1722 | 37.78
2023-04-30 04:00 | 45046.1667 | 0 | 7.0938 | 37.78
2023-04-30 04:30 | 45046.1875 | 0 | 7.112 | 37.78
2023-04-30 05:00 | 45046.2083 | 0 | 7.2323 | 37.78
2023-04-30 05:30 | 45046.2292 | 0 | 7.2947 | 37.78
2023-04-30 06:00 | 45046.25 | 0 | 7.5509 | 37.78
2023-04-30 06:30 | 45046.2708 | 0 | 7.6915 | 37.78
2023-04-30 07:00 | 45046.2917 | 0 | 7.0786 | 37.78
2023-04-30 07:30 | 45046.3125 | 0 | 7.5323 | 37.78
2023-04-30 08:00 | 45046.3333 | 0 | 6.9554 | 37.78
2023-04-30 08:30 | 45046.3542 | 0 | 5.0787 | 37.78
2023-04-30 09:00 | 45046.375 | 0 | 5.2934 | 37.78
2023-04-30 09:30 | 45046.3958 | 0 | 5.9775 | 37.78
2023-04-30 10:00 | 45046.4167 | 0 | 4.5602 | 37.78
2023-04-30 10:30 | 45046.4375 | 0 | 4.5416 | 37.78
2023-04-30 11:00 | 45046.4583 | 0 | 4.659 | 37.78
2023-04-30 11:30 | 45046.4792 | 0 | 4.6348 | 37.78
2023-04-30 12:00 | 45046.5 | 0 | 4.4363 | 37.78
2023-04-30 12:30 | 45046.5208 | 0 | 4.542 | 37.78
2023-04-30 13:00 | 45046.5417 | 0 | 4.9736 | 37.78
2023-04-30 13:30 | 45046.5625 | 0 | 5.3966 | 37.78
2023-04-30 14:00 | 45046.5833 | 0 | 5.8688 | 37.78
2023-04-30 14:30 | 45046.6042 | 0 | 6.7554 | 37.78
2023-04-30 15:00 | 45046.625 | 0 | 7.427 | 37.78
2023-04-30 15:30 | 45046.6458 | 0 | 8.2427 | 37.78
2023-04-30 16:00 | 45046.6667 | 0 | 9 | 37.78
2023-04-30 16:30 | 45046.6875 | 0 | 10.0586 | 37.78
2023-04-30 17:00 | 45046.7083 | 0 | 10.6658 | 37.78
2023-04-30 17:30 | 45046.7292 | 0 | 11.0388 | 37.78
2023-04-30 18:00 | 45046.75 | 0 | 11.0897 | 37.78
2023-04-30 18:30 | 45046.7708 | 0 | 10.7979 | 37.78
2023-04-30 19:00 | 45046.7917 | 0 | 10.5342 | 37.78
2023-04-30 19:30 | 45046.8125 | 0 | 10.2731 | 37.78
2023-04-30 20:00 | 45046.8333 | 0 | 9.916 | 37.78
2023-04-30 20:30 | 45046.8542 | 0 | 9.6146 | 37.78
2023-04-30 21:00 | 45046.875 | 0 | 9.5672 | 37.78
2023-04-30 21:30 | 45046.8958 | 0 | 9.0265 | 37.78
2023-04-30 22:00 | 45046.9167 | 0 | 8.6108 | 37.78
2023-04-30 22:30 | 45046.9375 | 0 | 8.4126 | 37.78
2023-04-30 23:00 | 45046.9583 | 0 | 7.9661 | 37.78
2023-04-30 23:30 | 45046.9792 | 0 | 8.0058 | 37.78
2023-05-01 | 45047 | 0 | 7.5561 | 39.95
2023-05-01 00:30 | 45047.0208 | 0 | 7.2033 | 39.95
2023-05-01 01:00 | 45047.0417 | 0 | 7.1636 | 39.95
2023-05-01 01:30 | 45047.0625 | 0 | 6.9558 | 39.95
2023-05-01 02:00 | 45047.0833 | 0 | 6.9958 | 39.95
2023-05-01 02:30 | 45047.1042 | 0 | 6.8705 | 39.95
2023-05-01 03:00 | 45047.125 | 0 | 6.9552 | 39.95
2023-05-01 03:30 | 45047.1458 | 0 | 7.0181 | 39.95
2023-05-01 04:00 | 45047.1667 | 0 | 7.099 | 39.95
2023-05-01 04:30 | 45047.1875 | 0 | 7.1693 | 39.95
2023-05-01 05:00 | 45047.2083 | 0 | 7.3468 | 39.95
2023-05-01 05:30 | 45047.2292 | 0 | 7.5466 | 39.95
2023-05-01 06:00 | 45047.25 | 0 | 7.8053 | 39.95
2023-05-01 06:30 | 45047.2708 | 0 | 7.7363 | 39.95
2023-05-01 07:00 | 45047.2917 | 0 | 7.6458 | 39.95
2023-05-01 07:30 | 45047.3125 | 0 | 7.1158 | 39.95
2023-05-01 08:00 | 45047.3333 | 0 | 6.6337 | 39.95
2023-05-01 08:30 | 45047.3542 | 0 | 5.8946 | 39.95
2023-05-01 09:00 | 45047.375 | 0 | 5.4505 | 39.95
2023-05-01 09:30 | 45047.3958 | 0 | 4.8411 | 39.95
2023-05-01 10:00 | 45047.4167 | 0 | 4.4581 | 39.95
2023-05-01 10:30 | 45047.4375 | 0 | 4.4619 | 39.95
2023-05-01 11:00 | 45047.4583 | 0 | 4.3944 | 39.95
2023-05-01 11:30 | 45047.4792 | 0 | 4.5128 | 39.95
2023-05-01 12:00 | 45047.5 | 0 | 4.4911 | 39.95
2023-05-01 12:30 | 45047.5208 | 0 | 4.6956 | 39.95
2023-05-01 13:00 | 45047.5417 | 0 | 4.9846 | 39.95
2023-05-01 13:30 | 45047.5625 | 0 | 5.2039 | 39.95
2023-05-01 14:00 | 45047.5833 | 0 | 6.6833 | 39.95
2023-05-01 14:30 | 45047.6042 | 0 | 6.8808 | 39.95
2023-05-01 15:00 | 45047.625 | 0 | 8.4424 | 39.95
2023-05-01 15:30 | 45047.6458 | 0 | 9.53 | 39.95
2023-05-01 16:00 | 45047.6667 | 0 | 9.4658 | 39.95
2023-05-01 16:30 | 45047.6875 | 0 | 10.6567 | 39.95
2023-05-01 17:00 | 45047.7083 | 0 | 11.4064 | 39.95
2023-05-01 17:30 | 45047.7292 | 0 | 11.9093 | 39.95
2023-05-01 18:00 | 45047.75 | 0 | 11.9618 | 39.95
2023-05-01 18:30 | 45047.7708 | 0 | 11.6121 | 39.95
2023-05-01 19:00 | 45047.7917 | 0 | 11.0951 | 39.95
2023-05-01 19:30 | 45047.8125 | 0 | 10.7094 | 39.95
2023-05-01 20:00 | 45047.8333 | 0 | 10.2036 | 39.95
2023-05-01 20:30 | 45047.8542 | 0 | 9.7778 | 39.95
2023-05-01 21:00 | 45047.875 | 0 | 9.6272 | 39.95
2023-05-01 21:30 | 45047.8958 | 0 | 8.9756 | 39.95
2023-05-01 22:00 | 45047.9167 | 0 | 8.2587 | 39.95
2023-05-01 22:30 | 45047.9375 | 0 | 8.0053 | 39.95
2023-05-01 23:00 | 45047.9583 | 0 | 7.8011 | 39.95
2023-05-01 23:30 | 45047.9792 | 0 | 7.6114 | 39.95
2023-05-02 | 45048 | 0 | 7.4534 | 39.95
2023-05-02 00:30 | 45048.0208 | 0 | 7.2627 | 39.95
2023-05-02 01:00 | 45048.0417 | 0 | 7.2891 | 39.95
2023-05-02 01:30 | 45048.0625 | 0 | 7.1888 | 39.95
2023-05-02 02:00 | 45048.0833 | 0 | 7.1504 | 39.95
2023-05-02 02:30 | 45048.1042 | 0 | 7.0314 | 39.95
2023-05-02 03:00 | 45048.125 | 0 | 7.2655 | 39.95
2023-05-02 03:30 | 45048.1458 | 0 | 7.5081 | 39.95
2023-05-02 04:00 | 45048.1667 | 0 | 7.7006 | 39.95
2023-05-02 04:30 | 45048.1875 | 0 | 7.8988 | 39.95
2023-05-02 05:00 | 45048.2083 | 0 | 8.5012 | 39.95
2023-05-02 05:30 | 45048.2292 | 0 | 9.3564 | 39.95
2023-05-02 06:00 | 45048.25 | 0 | 10.5484 | 39.95
2023-05-02 06:30 | 45048.2708 | 0 | 11.4438 | 39.95
2023-05-02 07:00 | 45048.2917 | 0 | 11.5591 | 39.95
2023-05-02 07:30 | 45048.3125 | 0 | 11.1839 | 39.95
2023-05-02 08:00 | 45048.3333 | 0 | 11.4704 | 39.95
2023-05-02 08:30 | 45048.3542 | 0 | 11.0226 | 39.95
2023-05-02 09:00 | 45048.375 | 0 | 11.2629 | 39.95
2023-05-02 09:30 | 45048.3958 | 0 | 10.0069 | 39.95
2023-05-02 10:00 | 45048.4167 | 0 | 8.3232 | 39.95
2023-05-02 10:30 | 45048.4375 | 0 | 7.3764 | 39.95
2023-05-02 11:00 | 45048.4583 | 0 | 8.5774 | 39.95
2023-05-02 11:30 | 45048.4792 | 0 | 7.696 | 39.95
2023-05-02 12:00 | 45048.5 | 0 | 6.4485 | 39.95
2023-05-02 12:30 | 45048.5208 | 0 | 7.323 | 39.95
2023-05-02 13:00 | 45048.5417 | 0 | 7.9766 | 39.95
2023-05-02 13:30 | 45048.5625 | 0 | 7.0257 | 39.95
2023-05-02 14:00 | 45048.5833 | 0 | 8.1372 | 39.95
2023-05-02 14:30 | 45048.6042 | 0 | 9.5331 | 39.95
2023-05-02 15:00 | 45048.625 | 0 | 10.5508 | 39.95
2023-05-02 15:30 | 45048.6458 | 0 | 10.8928 | 39.95
2023-05-02 16:00 | 45048.6667 | 0 | 12.0383 | 39.95
2023-05-02 16:30 | 45048.6875 | 0 | 12.1917 | 39.95
2023-05-02 17:00 | 45048.7083 | 0 | 12.6768 | 39.95
2023-05-02 17:30 | 45048.7292 | 0 | 13.5126 | 39.95
2023-05-02 18:00 | 45048.75 | 0 | 13.7444 | 39.95
2023-05-02 18:30 | 45048.7708 | 0 | 13.6395 | 39.95
2023-05-02 19:00 | 45048.7917 | 0 | 13.2188 | 39.95
2023-05-02 19:30 | 45048.8125 | 0 | 12.7001 | 39.95
2023-05-02 20:00 | 45048.8333 | 0 | 12.112 | 39.95
2023-05-02 20:30 | 45048.8542 | 0 | 11.7934 | 39.95
2023-05-02 21:00 | 45048.875 | 0 | 11.5992 | 39.95
2023-05-02 21:30 | 45048.8958 | 0 | 10.7586 | 39.95
2023-05-02 22:00 | 45048.9167 | 0 | 10.1031 | 39.95
2023-05-02 22:30 | 45048.9375 | 0 | 9.6502 | 39.95
2023-05-02 23:00 | 45048.9583 | 0 | 9.221 | 39.95
2023-05-02 23:30 | 45048.9792 | 0 | 8.8655 | 39.95
2023-05-03 | 45049 | 0 | 8.6142 | 39.95
2023-05-03 00:30 | 45049.0208 | 0 | 8.1354 | 39.95
2023-05-03 01:00 | 45049.0417 | 0 | 8.002 | 39.95
2023-05-03 01:30 | 45049.0625 | 0 | 7.8171 | 39.95
2023-05-03 02:00 | 45049.0833 | 0 | 7.655 | 39.95
2023-05-03 02:30 | 45049.1042 | 0 | 7.7591 | 39.95
2023-05-03 03:00 | 45049.125 | 0 | 7.7747 | 39.95
2023-05-03 03:30 | 45049.1458 | 0 | 7.9498 | 39.95
2023-05-03 04:00 | 45049.1667 | 0 | 8.2292 | 39.95
2023-05-03 04:30 | 45049.1875 | 0 | 8.5837 | 39.95
2023-05-03 05:00 | 45049.2083 | 0 | 9.0183 | 39.95
2023-05-03 05:30 | 45049.2292 | 0 | 9.8154 | 39.95
2023-05-03 06:00 | 45049.25 | 0 | 10.8109 | 39.95
2023-05-03 06:30 | 45049.2708 | 0 | 11.3093 | 39.95
2023-05-03 07:00 | 45049.2917 | 0 | 11.5975 | 39.95
2023-05-03 07:30 | 45049.3125 | 0 | 11.007 | 39.95
2023-05-03 08:00 | 45049.3333 | 0 | 10.097 | 39.95
2023-05-03 08:30 | 45049.3542 | 0 | 9.2167 | 39.95
2023-05-03 09:00 | 45049.375 | 0 | 8.4972 | 39.95
2023-05-03 09:30 | 45049.3958 | 0 | 8.1326 | 39.95
2023-05-03 10:00 | 45049.4167 | 0 | 7.778 | 39.95
2023-05-03 10:30 | 45049.4375 | 0 | 7.9137 | 39.95
2023-05-03 11:00 | 45049.4583 | 0 | 8.1146 | 39.95
2023-05-03 11:30 | 45049.4792 | 0 | 8.0346 | 39.95
2023-05-03 12:00 | 45049.5 | 0 | 8.1022 | 39.95
2023-05-03 12:30 | 45049.5208 | 0 | 8.2985 | 39.95
2023-05-03 13:00 | 45049.5417 | 0 | 8.5706 | 39.95
2023-05-03 13:30 | 45049.5625 | 0 | 8.9384 | 39.95
2023-05-03 14:00 | 45049.5833 | 0 | 9.6639 | 39.95
2023-05-03 14:30 | 45049.6042 | 0 | 10.1633 | 39.95
2023-05-03 15:00 | 45049.625 | 0 | 10.7891 | 39.95
2023-05-03 15:30 | 45049.6458 | 0 | 11.6603 | 39.95
2023-05-03 16:00 | 45049.6667 | 0 | 12.3451 | 39.95
2023-05-03 16:30 | 45049.6875 | 0 | 12.6975 | 39.95
2023-05-03 17:00 | 45049.7083 | 0 | 12.8929 | 39.95
2023-05-03 17:30 | 45049.7292 | 0 | 13.772 | 39.95
2023-05-03 18:00 | 45049.75 | 0 | 14.0616 | 39.95
2023-05-03 18:30 | 45049.7708 | 0 | 13.5904 | 39.95
2023-05-03 19:00 | 45049.7917 | 0 | 13.2942 | 39.95
2023-05-03 19:30 | 45049.8125 | 0 | 13.0624 | 39.95
2023-05-03 20:00 | 45049.8333 | 0 | 12.4284 | 39.95
2023-05-03 20:30 | 45049.8542 | 0 | 12.0992 | 39.95
2023-05-03 21:00 | 45049.875 | 0 | 11.7505 | 39.95
2023-05-03 21:30 | 45049.8958 | 0 | 11.0619 | 39.95
2023-05-03 22:00 | 45049.9167 | 0 | 10.2412 | 39.95
2023-05-03 22:30 | 45049.9375 | 0 | 9.8786 | 39.95
2023-05-03 23:00 | 45049.9583 | 0 | 9.5981 | 39.95
2023-05-03 23:30 | 45049.9792 | 0 | 9.2553 | 39.95
2023-05-04 | 45050 | 0 | 8.8364 | 39.95
2023-05-04 00:30 | 45050.0208 | 0 | 8.3207 | 39.95
2023-05-04 01:00 | 45050.0417 | 0 | 8.2151 | 39.95
2023-05-04 01:30 | 45050.0625 | 0 | 8.0564 | 39.95
2023-05-04 02:00 | 45050.0833 | 0 | 7.9105 | 39.95
2023-05-04 02:30 | 45050.1042 | 0 | 7.8777 | 39.95
2023-05-04 03:00 | 45050.125 | 0 | 7.9749 | 39.95
2023-05-04 03:30 | 45050.1458 | 0 | 8.1743 | 39.95
2023-05-04 04:00 | 45050.1667 | 0 | 8.3741 | 39.95
2023-05-04 04:30 | 45050.1875 | 0 | 8.5554 | 39.95
2023-05-04 05:00 | 45050.2083 | 0 | 9.1895 | 39.95
2023-05-04 05:30 | 45050.2292 | 0 | 9.9184 | 39.95
2023-05-04 06:00 | 45050.25 | 0 | 10.803 | 39.95
2023-05-04 06:30 | 45050.2708 | 0 | 11.7665 | 39.95
2023-05-04 07:00 | 45050.2917 | 0 | 12.1364 | 39.95
2023-05-04 07:30 | 45050.3125 | 0 | 11.3755 | 39.95
2023-05-04 08:00 | 45050.3333 | 0 | 10.5542 | 39.95
2023-05-04 08:30 | 45050.3542 | 0 | 9.8503 | 39.95
2023-05-04 09:00 | 45050.375 | 0 | 9.3546 | 39.95
2023-05-04 09:30 | 45050.3958 | 0 | 8.9341 | 39.95
2023-05-04 10:00 | 45050.4167 | 0 | 8.4232 | 39.95
2023-05-04 10:30 | 45050.4375 | 0 | 8.2795 | 39.95
2023-05-04 11:00 | 45050.4583 | 0 | 8.4893 | 39.95
2023-05-04 11:30 | 45050.4792 | 0 | 8.7084 | 39.95
2023-05-04 12:00 | 45050.5 | 0 | 8.6232 | 39.95
2023-05-04 12:30 | 45050.5208 | 0 | 8.9973 | 39.95
2023-05-04 13:00 | 45050.5417 | 0 | 9.3379 | 39.95
2023-05-04 13:30 | 45050.5625 | 0 | 9.6962 | 39.95
2023-05-04 14:00 | 45050.5833 | 0 | 9.4778 | 39.95
2023-05-04 14:30 | 45050.6042 | 0 | 9.841 | 39.95
2023-05-04 15:00 | 45050.625 | 0 | 10.7011 | 39.95
2023-05-04 15:30 | 45050.6458 | 0 | 11.4297 | 39.95
2023-05-04 16:00 | 45050.6667 | 0 | 12.059 | 39.95
2023-05-04 16:30 | 45050.6875 | 0 | 12.7644 | 39.95
2023-05-04 17:00 | 45050.7083 | 0 | 12.9362 | 39.95
2023-05-04 17:30 | 45050.7292 | 0 | 13.5882 | 39.95
2023-05-04 18:00 | 45050.75 | 0 | 13.5491 | 39.95
2023-05-04 18:30 | 45050.7708 | 0 | 13.414 | 39.95
2023-05-04 19:00 | 45050.7917 | 0 | 13.1797 | 39.95
2023-05-04 19:30 | 45050.8125 | 0 | 12.8676 | 39.95
2023-05-04 20:00 | 45050.8333 | 0 | 12.5685 | 39.95
2023-05-04 20:30 | 45050.8542 | 0 | 12.0551 | 39.95
2023-05-04 21:00 | 45050.875 | 0 | 11.8354 | 39.95
2023-05-04 21:30 | 45050.8958 | 0 | 10.9814 | 39.95
2023-05-04 22:00 | 45050.9167 | 0 | 10.4064 | 39.95
2023-05-04 22:30 | 45050.9375 | 0 | 10.0223 | 39.95
2023-05-04 23:00 | 45050.9583 | 0 | 9.6386 | 39.95
2023-05-04 23:30 | 45050.9792 | 0 | 9.291 | 39.95
2023-05-05 | 45051 | 0 | 8.8151 | 39.95
2023-05-05 00:30 | 45051.0208 | 0 | 8.4092 | 39.95
2023-05-05 01:00 | 45051.0417 | 0 | 8.3026 | 39.95
2023-05-05 01:30 | 45051.0625 | 0 | 8.0491 | 39.95
2023-05-05 02:00 | 45051.0833 | 0 | 8.0363 | 39.95
2023-05-05 02:30 | 45051.1042 | 0 | 8.0186 | 39.95
2023-05-05 03:00 | 45051.125 | 0 | 8.1279 | 39.95
2023-05-05 03:30 | 45051.1458 | 0 | 8.2412 | 39.95
2023-05-05 04:00 | 45051.1667 | 0 | 8.5738 | 39.95
2023-05-05 04:30 | 45051.1875 | 0 | 8.657 | 39.95
2023-05-05 05:00 | 45051.2083 | 0 | 9.311 | 39.95
2023-05-05 05:30 | 45051.2292 | 0 | 9.9738 | 39.95
2023-05-05 06:00 | 45051.25 | 0 | 10.6603 | 39.95
2023-05-05 06:30 | 45051.2708 | 0 | 11.5075 | 39.95
2023-05-05 07:00 | 45051.2917 | 0 | 12.0112 | 39.95
2023-05-05 07:30 | 45051.3125 | 0 | 11.2883 | 39.95
2023-05-05 08:00 | 45051.3333 | 0 | 10.3434 | 39.95
2023-05-05 08:30 | 45051.3542 | 0 | 10.5817 | 39.95
2023-05-05 09:00 | 45051.375 | 0 | 9.9527 | 39.95
2023-05-05 09:30 | 45051.3958 | 0 | 9.0424 | 39.95
2023-05-05 10:00 | 45051.4167 | 0 | 8.046 | 39.95
2023-05-05 10:30 | 45051.4375 | 0 | 9.7458 | 39.95
2023-05-05 11:00 | 45051.4583 | 0 | 10.2411 | 39.95
2023-05-05 11:30 | 45051.4792 | 0 | 9.4384 | 39.95
2023-05-05 12:00 | 45051.5 | 0 | 11.0442 | 39.95
2023-05-05 12:30 | 45051.5208 | 0 | 9.2277 | 39.95
2023-05-05 13:00 | 45051.5417 | 0 | 10.4832 | 39.95
2023-05-05 13:30 | 45051.5625 | 0 | 8.6245 | 39.95
2023-05-05 14:00 | 45051.5833 | 0 | 9.0623 | 39.95
2023-05-05 14:30 | 45051.6042 | 0 | 9.5182 | 39.95
2023-05-05 15:00 | 45051.625 | 0 | 10.3324 | 39.95
2023-05-05 15:30 | 45051.6458 | 0 | 11.2356 | 39.95
2023-05-05 16:00 | 45051.6667 | 0 | 11.9606 | 39.95
2023-05-05 16:30 | 45051.6875 | 0 | 12.4473 | 39.95
2023-05-05 17:00 | 45051.7083 | 0 | 12.6631 | 39.95
2023-05-05 17:30 | 45051.7292 | 0 | 13.2292 | 39.95
2023-05-05 18:00 | 45051.75 | 0 | 13.2056 | 39.95
2023-05-05 18:30 | 45051.7708 | 0 | 12.857 | 39.95
2023-05-05 19:00 | 45051.7917 | 0 | 12.7657 | 39.95
2023-05-05 19:30 | 45051.8125 | 0 | 12.4141 | 39.95
2023-05-05 20:00 | 45051.8333 | 0 | 12.0355 | 39.95
2023-05-05 20:30 | 45051.8542 | 0 | 11.7298 | 39.95
2023-05-05 21:00 | 45051.875 | 0 | 11.5206 | 39.95
2023-05-05 21:30 | 45051.8958 | 0 | 10.939 | 39.95
2023-05-05 22:00 | 45051.9167 | 0 | 10.3055 | 39.95
2023-05-05 22:30 | 45051.9375 | 0 | 9.7853 | 39.95
2023-05-05 23:00 | 45051.9583 | 0 | 9.5123 | 39.95
2023-05-05 23:30 | 45051.9792 | 0 | 9.2125 | 39.95
2023-05-06 | 45052 | 0 | 8.8873 | 39.95
2023-05-06 00:30 | 45052.0208 | 0 | 8.4623 | 39.95
2023-05-06 01:00 | 45052.0417 | 0 | 8.3165 | 39.95
2023-05-06 01:30 | 45052.0625 | 0 | 8.0521 | 39.95
2023-05-06 02:00 | 45052.0833 | 0 | 7.9642 | 39.95
2023-05-06 02:30 | 45052.1042 | 0 | 7.8405 | 39.95
2023-05-06 03:00 | 45052.125 | 0 | 7.7414 | 39.95
2023-05-06 03:30 | 45052.1458 | 0 | 7.8497 | 39.95
2023-05-06 04:00 | 45052.1667 | 0 | 7.9504 | 39.95
2023-05-06 04:30 | 45052.1875 | 0 | 7.9859 | 39.95
2023-05-06 05:00 | 45052.2083 | 0 | 8.1016 | 39.95
2023-05-06 05:30 | 45052.2292 | 0 | 8.4656 | 39.95
2023-05-06 06:00 | 45052.25 | 0 | 8.59 | 39.95
2023-05-06 06:30 | 45052.2708 | 0 | 8.7322 | 39.95
2023-05-06 07:00 | 45052.2917 | 0 | 8.6422 | 39.95
2023-05-06 07:30 | 45052.3125 | 0 | 8.1333 | 39.95
2023-05-06 08:00 | 45052.3333 | 0 | 7.7599 | 39.95
2023-05-06 08:30 | 45052.3542 | 0 | 7.2801 | 39.95
2023-05-06 09:00 | 45052.375 | 0 | 6.7432 | 39.95
2023-05-06 09:30 | 45052.3958 | 0 | 6.1628 | 39.95
2023-05-06 10:00 | 45052.4167 | 0 | 5.7321 | 39.95
2023-05-06 10:30 | 45052.4375 | 0 | 5.7675 | 39.95
2023-05-06 11:00 | 45052.4583 | 0 | 5.9033 | 39.95
2023-05-06 11:30 | 45052.4792 | 0 | 5.909 | 39.95
2023-05-06 12:00 | 45052.5 | 0 | 5.8185 | 39.95
2023-05-06 12:30 | 45052.5208 | 0 | 6.1003 | 39.95
2023-05-06 13:00 | 45052.5417 | 0 | 6.001 | 39.95
2023-05-06 13:30 | 45052.5625 | 0 | 6.323 | 39.95
2023-05-06 14:00 | 45052.5833 | 0 | 6.7902 | 39.95
2023-05-06 14:30 | 45052.6042 | 0 | 7.793 | 39.95
2023-05-06 15:00 | 45052.625 | 0 | 8.705 | 39.95
2023-05-06 15:30 | 45052.6458 | 0 | 9.5359 | 39.95
2023-05-06 16:00 | 45052.6667 | 0 | 10.2219 | 39.95
2023-05-06 16:30 | 45052.6875 | 0 | 10.7514 | 39.95
2023-05-06 17:00 | 45052.7083 | 0 | 11.0346 | 39.95
2023-05-06 17:30 | 45052.7292 | 0 | 11.7122 | 39.95
2023-05-06 18:00 | 45052.75 | 0 | 11.5902 | 39.95
2023-05-06 18:30 | 45052.7708 | 0 | 11.2786 | 39.95
2023-05-06 19:00 | 45052.7917 | 0 | 10.885 | 39.95
2023-05-06 19:30 | 45052.8125 | 0 | 10.6425 | 39.95
2023-05-06 20:00 | 45052.8333 | 0 | 10.2361 | 39.95
2023-05-06 20:30 | 45052.8542 | 0 | 9.9861 | 39.95
2023-05-06 21:00 | 45052.875 | 0 | 9.7667 | 39.95
2023-05-06 21:30 | 45052.8958 | 0 | 9.3822 | 39.95
2023-05-06 22:00 | 45052.9167 | 0 | 8.8805 | 39.95
2023-05-06 22:30 | 45052.9375 | 0 | 8.6422 | 39.95
2023-05-06 23:00 | 45052.9583 | 0 | 8.5077 | 39.95
2023-05-06 23:30 | 45052.9792 | 0 | 8.0419 | 39.95
2023-05-07 | 45053 | 0 | 7.7284 | 39.95
2023-05-07 00:30 | 45053.0208 | 0 | 7.4846 | 39.95
2023-05-07 01:00 | 45053.0417 | 0 | 7.3343 | 39.95
2023-05-07 01:30 | 45053.0625 | 0 | 7.162 | 39.95
2023-05-07 02:00 | 45053.0833 | 0 | 7.0903 | 39.95
2023-05-07 02:30 | 45053.1042 | 0 | 6.9924 | 39.95
2023-05-07 03:00 | 45053.125 | 0 | 7.0503 | 39.95
2023-05-07 03:30 | 45053.1458 | 0 | 6.9437 | 39.95
2023-05-07 04:00 | 45053.1667 | 0 | 7.0239 | 39.95
2023-05-07 04:30 | 45053.1875 | 0 | 7.0559 | 39.95
2023-05-07 05:00 | 45053.2083 | 0 | 7.1063 | 39.95
2023-05-07 05:30 | 45053.2292 | 0 | 7.2907 | 39.95
2023-05-07 06:00 | 45053.25 | 0 | 7.3767 | 39.95
2023-05-07 06:30 | 45053.2708 | 0 | 7.4127 | 39.95
2023-05-07 07:00 | 45053.2917 | 0 | 7.2942 | 39.95
2023-05-07 07:30 | 45053.3125 | 0 | 7.4739 | 39.95
2023-05-07 08:00 | 45053.3333 | 0 | 7.2833 | 39.95
2023-05-07 08:30 | 45053.3542 | 0 | 6.6601 | 39.95
2023-05-07 09:00 | 45053.375 | 0 | 7.1985 | 39.95
2023-05-07 09:30 | 45053.3958 | 0 | 5.7393 | 39.95
2023-05-07 10:00 | 45053.4167 | 0 | 5.4238 | 39.95
2023-05-07 10:30 | 45053.4375 | 0 | 7.494 | 39.95
2023-05-07 11:00 | 45053.4583 | 0 | 7.7022 | 39.95
2023-05-07 11:30 | 45053.4792 | 0 | 8.6651 | 39.95
2023-05-07 12:00 | 45053.5 | 0 | 8.137 | 39.95
2023-05-07 12:30 | 45053.5208 | 0 | 6.6083 | 39.95
2023-05-07 13:00 | 45053.5417 | 0 | 7.3502 | 39.95
2023-05-07 13:30 | 45053.5625 | 0 | 6.4104 | 39.95
2023-05-07 14:00 | 45053.5833 | 0 | 6.3356 | 39.95
2023-05-07 14:30 | 45053.6042 | 0 | 7.8585 | 39.95
2023-05-07 15:00 | 45053.625 | 0 | 9.3358 | 39.95
2023-05-07 15:30 | 45053.6458 | 0 | 10.7614 | 39.95
2023-05-07 16:00 | 45053.6667 | 0 | 11.1294 | 39.95
2023-05-07 16:30 | 45053.6875 | 0 | 10.9848 | 39.95
2023-05-07 17:00 | 45053.7083 | 0 | 11.2922 | 39.95
2023-05-07 17:30 | 45053.7292 | 0 | 11.993 | 39.95
2023-05-07 18:00 | 45053.75 | 0 | 12.291 | 39.95
2023-05-07 18:30 | 45053.7708 | 0 | 11.9265 | 39.95
2023-05-07 19:00 | 45053.7917 | 0 | 11.5707 | 39.95
2023-05-07 19:30 | 45053.8125 | 0 | 11.0086 | 39.95
2023-05-07 20:00 | 45053.8333 | 0 | 10.3804 | 39.95
2023-05-07 20:30 | 45053.8542 | 0 | 10.0366 | 39.95
2023-05-07 21:00 | 45053.875 | 0 | 9.9933 | 39.95
2023-05-07 21:30 | 45053.8958 | 0 | 9.3508 | 39.95
2023-05-07 22:00 | 45053.9167 | 0 | 8.6657 | 39.95
2023-05-07 22:30 | 45053.9375 | 0 | 8.3856 | 39.95
2023-05-07 23:00 | 45053.9583 | 0 | 8.0765 | 39.95
2023-05-07 23:30 | 45053.9792 | 0 | 7.9692 | 39.95
2023-05-08 | 45054 | 0 | 7.7327 | 39.95
2023-05-08 00:30 | 45054.0208 | 0 | 7.5043 | 39.95
2023-05-08 01:00 | 45054.0417 | 0 | 7.4168 | 39.95
2023-05-08 01:30 | 45054.0625 | 0 | 7.3503 | 39.95
2023-05-08 02:00 | 45054.0833 | 0 | 7.3217 | 39.95
2023-05-08 02:30 | 45054.1042 | 0 | 7.2678 | 39.95
2023-05-08 03:00 | 45054.125 | 0 | 7.4333 | 39.95
2023-05-08 03:30 | 45054.1458 | 0 | 7.4756 | 39.95
2023-05-08 04:00 | 45054.1667 | 0 | 7.7758 | 39.95
2023-05-08 04:30 | 45054.1875 | 0 | 8.1407 | 39.95
2023-05-08 05:00 | 45054.2083 | 0 | 8.6857 | 39.95
2023-05-08 05:30 | 45054.2292 | 0 | 9.6208 | 39.95
2023-05-08 06:00 | 45054.25 | 0 | 10.7948 | 39.95
2023-05-08 06:30 | 45054.2708 | 0 | 11.7253 | 39.95
2023-05-08 07:00 | 45054.2917 | 0 | 11.8604 | 39.95
2023-05-08 07:30 | 45054.3125 | 0 | 11.2446 | 39.95
2023-05-08 08:00 | 45054.3333 | 0 | 9.8751 | 39.95
2023-05-08 08:30 | 45054.3542 | 0 | 8.9093 | 39.95
2023-05-08 09:00 | 45054.375 | 0 | 8.1589 | 39.95
2023-05-08 09:30 | 45054.3958 | 0 | 7.6813 | 39.95
2023-05-08 10:00 | 45054.4167 | 0 | 6.8152 | 39.95
2023-05-08 10:30 | 45054.4375 | 0 | 6.686 | 39.95
2023-05-08 11:00 | 45054.4583 | 0 | 6.7404 | 39.95
2023-05-08 11:30 | 45054.4792 | 0 | 6.8882 | 39.95
2023-05-08 12:00 | 45054.5 | 0 | 6.4558 | 39.95
2023-05-08 12:30 | 45054.5208 | 0 | 6.6414 | 39.95
2023-05-08 13:00 | 45054.5417 | 0 | 7.1435 | 39.95
2023-05-08 13:30 | 45054.5625 | 0 | 7.3975 | 39.95
2023-05-08 14:00 | 45054.5833 | 0 | 7.9716 | 39.95
2023-05-08 14:30 | 45054.6042 | 0 | 8.4717 | 39.95
2023-05-08 15:00 | 45054.625 | 0 | 9.3771 | 39.95
2023-05-08 15:30 | 45054.6458 | 0 | 10.4226 | 39.95
2023-05-08 16:00 | 45054.6667 | 0 | 11.3704 | 39.95
2023-05-08 16:30 | 45054.6875 | 0 | 12.2912 | 39.95
2023-05-08 17:00 | 45054.7083 | 0 | 12.9592 | 39.95
2023-05-08 17:30 | 45054.7292 | 0 | 14.0265 | 39.95
2023-05-08 18:00 | 45054.75 | 0 | 14.4498 | 39.95
2023-05-08 18:30 | 45054.7708 | 0 | 14.2136 | 39.95
2023-05-08 19:00 | 45054.7917 | 0 | 13.8389 | 39.95
2023-05-08 19:30 | 45054.8125 | 0 | 13.3369 | 39.95
2023-05-08 20:00 | 45054.8333 | 0 | 12.8232 | 39.95
2023-05-08 20:30 | 45054.8542 | 0 | 12.4326 | 39.95
2023-05-08 21:00 | 45054.875 | 0 | 12.0792 | 39.95
2023-05-08 21:30 | 45054.8958 | 0 | 11.4425 | 39.95
2023-05-08 22:00 | 45054.9167 | 0 | 10.5002 | 39.95
2023-05-08 22:30 | 45054.9375 | 0 | 9.9887 | 39.95
2023-05-08 23:00 | 45054.9583 | 0 | 9.6816 | 39.95
2023-05-08 23:30 | 45054.9792 | 0 | 9.3242 | 39.95
2023-05-09 | 45055 | 0 | 8.9144 | 39.95
2023-05-09 00:30 | 45055.0208 | 0 | 8.574 | 39.95
2023-05-09 01:00 | 45055.0417 | 0 | 8.4715 | 39.95
2023-05-09 01:30 | 45055.0625 | 0 | 8.3553 | 39.95
2023-05-09 02:00 | 45055.0833 | 0 | 8.2585 | 39.95
2023-05-09 02:30 | 45055.1042 | 0 | 8.2373 | 39.95
2023-05-09 03:00 | 45055.125 | 0 | 8.2676 | 39.95
2023-05-09 03:30 | 45055.1458 | 0 | 8.5274 | 39.95
2023-05-09 04:00 | 45055.1667 | 0 | 8.8705 | 39.95
2023-05-09 04:30 | 45055.1875 | 0 | 9.1849 | 39.95
2023-05-09 05:00 | 45055.2083 | 0 | 9.826 | 39.95
2023-05-09 05:30 | 45055.2292 | 0 | 10.7142 | 39.95
2023-05-09 06:00 | 45055.25 | 0 | 12.1289 | 39.95
2023-05-09 06:30 | 45055.2708 | 0 | 13.185 | 39.95
2023-05-09 07:00 | 45055.2917 | 0 | 13.673 | 39.95
2023-05-09 07:30 | 45055.3125 | 0 | 12.5619 | 39.95
2023-05-09 08:00 | 45055.3333 | 0 | 11.2417 | 39.95
2023-05-09 08:30 | 45055.3542 | 0 | 10.1784 | 39.95
2023-05-09 09:00 | 45055.375 | 0 | 9.313 | 39.95
2023-05-09 09:30 | 45055.3958 | 0 | 8.5292 | 39.95
2023-05-09 10:00 | 45055.4167 | 0 | 7.7782 | 39.95
2023-05-09 10:30 | 45055.4375 | 0 | 7.6223 | 39.95
2023-05-09 11:00 | 45055.4583 | 0 | 7.5095 | 39.95
2023-05-09 11:30 | 45055.4792 | 0 | 7.6 | 39.95
2023-05-09 12:00 | 45055.5 | 0 | 7.3618 | 39.95
2023-05-09 12:30 | 45055.5208 | 0 | 7.4098 | 39.95
2023-05-09 13:00 | 45055.5417 | 0 | 7.7739 | 39.95
2023-05-09 13:30 | 45055.5625 | 0 | 8.0214 | 39.95
2023-05-09 14:00 | 45055.5833 | 0 | 8.6584 | 39.95
2023-05-09 14:30 | 45055.6042 | 0 | 9.3063 | 39.95
2023-05-09 15:00 | 45055.625 | 0 | 10.0942 | 39.95
2023-05-09 15:30 | 45055.6458 | 0 | 11.0725 | 39.95
2023-05-09 16:00 | 45055.6667 | 0 | 11.8443 | 39.95
2023-05-09 16:30 | 45055.6875 | 0 | 12.2759 | 39.95
2023-05-09 17:00 | 45055.7083 | 0 | 13.0039 | 39.95
2023-05-09 17:30 | 45055.7292 | 0 | 14.1725 | 39.95
2023-05-09 18:00 | 45055.75 | 0 | 14.38 | 39.95
2023-05-09 18:30 | 45055.7708 | 0 | 14.3015 | 39.95
2023-05-09 19:00 | 45055.7917 | 0 | 14.0038 | 39.95
2023-05-09 19:30 | 45055.8125 | 0 | 13.7947 | 39.95
2023-05-09 20:00 | 45055.8333 | 0 | 13.1237 | 39.95
2023-05-09 20:30 | 45055.8542 | 0 | 12.5459 | 39.95
2023-05-09 21:00 | 45055.875 | 0 | 12.3152 | 39.95
2023-05-09 21:30 | 45055.8958 | 0 | 11.5848 | 39.95
2023-05-09 22:00 | 45055.9167 | 0 | 10.6417 | 39.95
2023-05-09 22:30 | 45055.9375 | 0 | 10.0709 | 39.95
2023-05-09 23:00 | 45055.9583 | 0 | 9.6244 | 39.95
2023-05-09 23:30 | 45055.9792 | 0 | 9.3356 | 39.95
2023-05-10 | 45056 | 0 | 8.9538 | 39.95
2023-05-10 00:30 | 45056.0208 | 0 | 8.491 | 39.95
2023-05-10 01:00 | 45056.0417 | 0 | 8.3118 | 39.95
2023-05-10 01:30 | 45056.0625 | 0 | 8.1647 | 39.95
2023-05-10 02:00 | 45056.0833 | 0 | 8.0254 | 39.95
2023-05-10 02:30 | 45056.1042 | 0 | 8.1679 | 39.95
2023-05-10 03:00 | 45056.125 | 0 | 8.1619 | 39.95
2023-05-10 03:30 | 45056.1458 | 0 | 8.2997 | 39.95
2023-05-10 04:00 | 45056.1667 | 0 | 8.7638 | 39.95
2023-05-10 04:30 | 45056.1875 | 0 | 9.0395 | 39.95
2023-05-10 05:00 | 45056.2083 | 0 | 9.6411 | 39.95
2023-05-10 05:30 | 45056.2292 | 0 | 10.6718 | 39.95
2023-05-10 06:00 | 45056.25 | 0 | 11.7638 | 39.95
2023-05-10 06:30 | 45056.2708 | 0 | 12.7019 | 39.95
2023-05-10 07:00 | 45056.2917 | 0 | 12.8982 | 39.95
2023-05-10 07:30 | 45056.3125 | 0 | 12.2217 | 39.95
2023-05-10 08:00 | 45056.3333 | 0 | 10.9871 | 39.95
2023-05-10 08:30 | 45056.3542 | 0 | 10.1331 | 39.95
2023-05-10 09:00 | 45056.375 | 0 | 9.1661 | 39.95
2023-05-10 09:30 | 45056.3958 | 0 | 8.4095 | 39.95
2023-05-10 10:00 | 45056.4167 | 0 | 7.8656 | 39.95
2023-05-10 10:30 | 45056.4375 | 0 | 7.8591 | 39.95
2023-05-10 11:00 | 45056.4583 | 0 | 7.9183 | 39.95
2023-05-10 11:30 | 45056.4792 | 0 | 7.8284 | 39.95
2023-05-10 12:00 | 45056.5 | 0 | 7.7295 | 39.95
2023-05-10 12:30 | 45056.5208 | 0 | 9.5016 | 39.95
2023-05-10 13:00 | 45056.5417 | 0 | 8.9981 | 39.95
2023-05-10 13:30 | 45056.5625 | 0 | 9.9166 | 39.95
2023-05-10 14:00 | 45056.5833 | 0 | 9.6826 | 39.95
2023-05-10 14:30 | 45056.6042 | 0 | 10.0828 | 39.95
2023-05-10 15:00 | 45056.625 | 0 | 10.4241 | 39.95
2023-05-10 15:30 | 45056.6458 | 0 | 11.16 | 39.95
2023-05-10 16:00 | 45056.6667 | 0 | 11.7711 | 39.95
2023-05-10 16:30 | 45056.6875 | 0 | 12.5936 | 39.95
2023-05-10 17:00 | 45056.7083 | 0 | 12.942 | 39.95
2023-05-10 17:30 | 45056.7292 | 0 | 13.8052 | 39.95
2023-05-10 18:00 | 45056.75 | 0 | 14.1572 | 39.95
2023-05-10 18:30 | 45056.7708 | 0 | 13.5 | 39.95
2023-05-10 19:00 | 45056.7917 | 0 | 13.2902 | 39.95
2023-05-10 19:30 | 45056.8125 | 0 | 13.1025 | 39.95
2023-05-10 20:00 | 45056.8333 | 0 | 12.7722 | 39.95
2023-05-10 20:30 | 45056.8542 | 0 | 12.2336 | 39.95
2023-05-10 21:00 | 45056.875 | 0 | 11.9028 | 39.95
2023-05-10 21:30 | 45056.8958 | 0 | 11.0736 | 39.95
2023-05-10 22:00 | 45056.9167 | 0 | 10.3877 | 39.95
2023-05-10 22:30 | 45056.9375 | 0 | 9.9402 | 39.95
2023-05-10 23:00 | 45056.9583 | 0 | 9.5659 | 39.95
2023-05-10 23:30 | 45056.9792 | 0 | 9.3149 | 39.95
2023-05-11 | 45057 | 0 | 8.8988 | 39.95
2023-05-11 00:30 | 45057.0208 | 0 | 8.502 | 39.95
2023-05-11 01:00 | 45057.0417 | 0 | 8.2826 | 39.95
2023-05-11 01:30 | 45057.0625 | 0 | 8.1228 | 39.95
2023-05-11 02:00 | 45057.0833 | 0 | 8.0506 | 39.95
2023-05-11 02:30 | 45057.1042 | 0 | 7.9968 | 39.95
2023-05-11 03:00 | 45057.125 | 0 | 8.1239 | 39.95
2023-05-11 03:30 | 45057.1458 | 0 | 8.1743 | 39.95
2023-05-11 04:00 | 45057.1667 | 0 | 8.5281 | 39.95
2023-05-11 04:30 | 45057.1875 | 0 | 8.8139 | 39.95
2023-05-11 05:00 | 45057.2083 | 0 | 9.3675 | 39.95
2023-05-11 05:30 | 45057.2292 | 0 | 10.0756 | 39.95
2023-05-11 06:00 | 45057.25 | 0 | 11.2369 | 39.95
2023-05-11 06:30 | 45057.2708 | 0 | 12.1008 | 39.95
2023-05-11 07:00 | 45057.2917 | 0 | 12.2509 | 39.95
2023-05-11 07:30 | 45057.3125 | 0 | 11.8136 | 39.95
2023-05-11 08:00 | 45057.3333 | 0 | 10.7005 | 39.95
2023-05-11 08:30 | 45057.3542 | 0 | 10.0573 | 39.95
2023-05-11 09:00 | 45057.375 | 0 | 9.2799 | 39.95
2023-05-11 09:30 | 45057.3958 | 0 | 8.5517 | 39.95
2023-05-11 10:00 | 45057.4167 | 0 | 9.2632 | 39.95
2023-05-11 10:30 | 45057.4375 | 0 | 10.7392 | 39.95
2023-05-11 11:00 | 45057.4583 | 0 | 11.5555 | 39.95
2023-05-11 11:30 | 45057.4792 | 0 | 10.0595 | 39.95
2023-05-11 12:00 | 45057.5 | 0 | 9.3997 | 39.95
2023-05-11 12:30 | 45057.5208 | 0 | 10.6582 | 39.95
2023-05-11 13:00 | 45057.5417 | 0 | 11.1022 | 39.95
2023-05-11 13:30 | 45057.5625 | 0 | 9.9102 | 39.95
2023-05-11 14:00 | 45057.5833 | 0 | 9.3085 | 39.95
2023-05-11 14:30 | 45057.6042 | 0 | 9.6698 | 39.95
2023-05-11 15:00 | 45057.625 | 0 | 10.2096 | 39.95
2023-05-11 15:30 | 45057.6458 | 0 | 10.8772 | 39.95
2023-05-11 16:00 | 45057.6667 | 0 | 11.584 | 39.95
2023-05-11 16:30 | 45057.6875 | 0 | 12.5446 | 39.95
2023-05-11 17:00 | 45057.7083 | 0 | 13.0871 | 39.95
2023-05-11 17:30 | 45057.7292 | 0 | 13.7783 | 39.95
2023-05-11 18:00 | 45057.75 | 0 | 13.8366 | 39.95
2023-05-11 18:30 | 45057.7708 | 0 | 13.6452 | 39.95
2023-05-11 19:00 | 45057.7917 | 0 | 13.4031 | 39.95
2023-05-11 19:30 | 45057.8125 | 0 | 13.0085 | 39.95
2023-05-11 20:00 | 45057.8333 | 0 | 12.5727 | 39.95
2023-05-11 20:30 | 45057.8542 | 0 | 12.0832 | 39.95
2023-05-11 21:00 | 45057.875 | 0 | 11.866 | 39.95
2023-05-11 21:30 | 45057.8958 | 0 | 11.2428 | 39.95
2023-05-11 22:00 | 45057.9167 | 0 | 10.5414 | 39.95
2023-05-11 22:30 | 45057.9375 | 0 | 10.0217 | 39.95
2023-05-11 23:00 | 45057.9583 | 0 | 9.6871 | 39.95
2023-05-11 23:30 | 45057.9792 | 0 | 9.2728 | 39.95
2023-05-12 | 45058 | 0 | 8.79 | 39.95
2023-05-12 00:30 | 45058.0208 | 0 | 8.4499 | 39.95
2023-05-12 01:00 | 45058.0417 | 0 | 8.4636 | 39.95
2023-05-12 01:30 | 45058.0625 | 0 | 8.2574 | 39.95
2023-05-12 02:00 | 45058.0833 | 0 | 8.2476 | 39.95
2023-05-12 02:30 | 45058.1042 | 0 | 7.9871 | 39.95
2023-05-12 03:00 | 45058.125 | 0 | 8.0901 | 39.95
2023-05-12 03:30 | 45058.1458 | 0 | 8.2086 | 39.95
2023-05-12 04:00 | 45058.1667 | 0 | 8.4354 | 39.95
2023-05-12 04:30 | 45058.1875 | 0 | 8.8958 | 39.95
2023-05-12 05:00 | 45058.2083 | 0 | 9.3215 | 39.95
2023-05-12 05:30 | 45058.2292 | 0 | 9.9956 | 39.95
2023-05-12 06:00 | 45058.25 | 0 | 10.8342 | 39.95
2023-05-12 06:30 | 45058.2708 | 0 | 11.7607 | 39.95
2023-05-12 07:00 | 45058.2917 | 0 | 11.8598 | 39.95
2023-05-12 07:30 | 45058.3125 | 0 | 11.4053 | 39.95
2023-05-12 08:00 | 45058.3333 | 0 | 10.5684 | 39.95
2023-05-12 08:30 | 45058.3542 | 0 | 9.959 | 39.95
2023-05-12 09:00 | 45058.375 | 0 | 9.6719 | 39.95
2023-05-12 09:30 | 45058.3958 | 0 | 9.2771 | 39.95
2023-05-12 10:00 | 45058.4167 | 0 | 9.4501 | 39.95
2023-05-12 10:30 | 45058.4375 | 0 | 9.6901 | 39.95
2023-05-12 11:00 | 45058.4583 | 0 | 12.259 | 39.95
2023-05-12 11:30 | 45058.4792 | 0 | 9.4997 | 39.95
2023-05-12 12:00 | 45058.5 | 0 | 9.5523 | 39.95
2023-05-12 12:30 | 45058.5208 | 0 | 8.7874 | 39.95
2023-05-12 13:00 | 45058.5417 | 0 | 8.4216 | 39.95
2023-05-12 13:30 | 45058.5625 | 0 | 8.4875 | 39.95
2023-05-12 14:00 | 45058.5833 | 0 | 8.8393 | 39.95
2023-05-12 14:30 | 45058.6042 | 0 | 9.6278 | 39.95
2023-05-12 15:00 | 45058.625 | 0 | 10.8486 | 39.95
2023-05-12 15:30 | 45058.6458 | 0 | 11.1249 | 39.95
2023-05-12 16:00 | 45058.6667 | 0 | 11.8087 | 39.95
2023-05-12 16:30 | 45058.6875 | 0 | 12.2941 | 39.95
2023-05-12 17:00 | 45058.7083 | 0 | 12.4724 | 39.95
2023-05-12 17:30 | 45058.7292 | 0 | 13.0253 | 39.95
2023-05-12 18:00 | 45058.75 | 0 | 12.7007 | 39.95
2023-05-12 18:30 | 45058.7708 | 0 | 12.5287 | 39.95
2023-05-12 19:00 | 45058.7917 | 0 | 12.2601 | 39.95
2023-05-12 19:30 | 45058.8125 | 0 | 12.3688 | 39.95
2023-05-12 20:00 | 45058.8333 | 0 | 12.1444 | 39.95
2023-05-12 20:30 | 45058.8542 | 0 | 11.6268 | 39.95
2023-05-12 21:00 | 45058.875 | 0 | 11.5169 | 39.95
2023-05-12 21:30 | 45058.8958 | 0 | 10.8922 | 39.95
2023-05-12 22:00 | 45058.9167 | 0 | 10.2721 | 39.95
2023-05-12 22:30 | 45058.9375 | 0 | 9.7565 | 39.95
2023-05-12 23:00 | 45058.9583 | 0 | 9.4675 | 39.95
2023-05-12 23:30 | 45058.9792 | 0 | 9.1549 | 39.95
2023-05-13 | 45059 | 0 | 8.7539 | 39.95
2023-05-13 00:30 | 45059.0208 | 0 | 8.6068 | 39.95
2023-05-13 01:00 | 45059.0417 | 0 | 8.4013 | 39.95
2023-05-13 01:30 | 45059.0625 | 0 | 8.2362 | 39.95
2023-05-13 02:00 | 45059.0833 | 0 | 8.16 | 39.95
2023-05-13 02:30 | 45059.1042 | 0 | 8.0249 | 39.95
2023-05-13 03:00 | 45059.125 | 0 | 8.0043 | 39.95
2023-05-13 03:30 | 45059.1458 | 0 | 8.0197 | 39.95
2023-05-13 04:00 | 45059.1667 | 0 | 8.1033 | 39.95
2023-05-13 04:30 | 45059.1875 | 0 | 7.9602 | 39.95
2023-05-13 05:00 | 45059.2083 | 0 | 8.2682 | 39.95
2023-05-13 05:30 | 45059.2292 | 0 | 8.3592 | 39.95
2023-05-13 06:00 | 45059.25 | 0 | 8.6099 | 39.95
2023-05-13 06:30 | 45059.2708 | 0 | 8.6351 | 39.95
2023-05-13 07:00 | 45059.2917 | 0 | 8.3318 | 39.95
2023-05-13 07:30 | 45059.3125 | 0 | 8.1309 | 39.95
2023-05-13 08:00 | 45059.3333 | 0 | 7.9052 | 39.95
2023-05-13 08:30 | 45059.3542 | 0 | 8.7363 | 39.95
2023-05-13 09:00 | 45059.375 | 0 | 7.7701 | 39.95
2023-05-13 09:30 | 45059.3958 | 0 | 6.1437 | 39.95
2023-05-13 10:00 | 45059.4167 | 0 | 8.1914 | 39.95
2023-05-13 10:30 | 45059.4375 | 0 | 8.5948 | 39.95
2023-05-13 11:00 | 45059.4583 | 0 | 6.6257 | 39.95
2023-05-13 11:30 | 45059.4792 | 0 | 6.2709 | 39.95
2023-05-13 12:00 | 45059.5 | 0 | 5.7964 | 39.95
2023-05-13 12:30 | 45059.5208 | 0 | 5.8051 | 39.95
2023-05-13 13:00 | 45059.5417 | 0 | 5.885 | 39.95
2023-05-13 13:30 | 45059.5625 | 0 | 5.951 | 39.95
2023-05-13 14:00 | 45059.5833 | 0 | 6.4516 | 39.95
2023-05-13 14:30 | 45059.6042 | 0 | 7.6558 | 39.95
2023-05-13 15:00 | 45059.625 | 0 | 8.1233 | 39.95
2023-05-13 15:30 | 45059.6458 | 0 | 8.9138 | 39.95
2023-05-13 16:00 | 45059.6667 | 0 | 10.2967 | 39.95
2023-05-13 16:30 | 45059.6875 | 0 | 10.7929 | 39.95
2023-05-13 17:00 | 45059.7083 | 0 | 11.0043 | 39.95
2023-05-13 17:30 | 45059.7292 | 0 | 11.4982 | 39.95
2023-05-13 18:00 | 45059.75 | 0 | 11.4041 | 39.95
2023-05-13 18:30 | 45059.7708 | 0 | 11.1166 | 39.95
2023-05-13 19:00 | 45059.7917 | 0 | 10.9717 | 39.95
2023-05-13 19:30 | 45059.8125 | 0 | 10.8021 | 39.95
2023-05-13 20:00 | 45059.8333 | 0 | 10.2926 | 39.95
2023-05-13 20:30 | 45059.8542 | 0 | 10.0274 | 39.95
2023-05-13 21:00 | 45059.875 | 0 | 9.8643 | 39.95
2023-05-13 21:30 | 45059.8958 | 0 | 9.4392 | 39.95
2023-05-13 22:00 | 45059.9167 | 0 | 8.9629 | 39.95
2023-05-13 22:30 | 45059.9375 | 0 | 8.5991 | 39.95
2023-05-13 23:00 | 45059.9583 | 0 | 8.3084 | 39.95
2023-05-13 23:30 | 45059.9792 | 0 | 8.0421 | 39.95
2023-05-14 | 45060 | 0 | 7.6947 | 39.95
2023-05-14 00:30 | 45060.0208 | 0 | 7.3704 | 39.95
2023-05-14 01:00 | 45060.0417 | 0 | 7.2238 | 39.95
2023-05-14 01:30 | 45060.0625 | 0 | 7.0507 | 39.95
2023-05-14 02:00 | 45060.0833 | 0 | 6.9981 | 39.95
2023-05-14 02:30 | 45060.1042 | 0 | 7.0812 | 39.95
2023-05-14 03:00 | 45060.125 | 0 | 7.0256 | 39.95
2023-05-14 03:30 | 45060.1458 | 0 | 7.0834 | 39.95
2023-05-14 04:00 | 45060.1667 | 0 | 7.0193 | 39.95
2023-05-14 04:30 | 45060.1875 | 0 | 7.0296 | 39.95
2023-05-14 05:00 | 45060.2083 | 0 | 7.3169 | 39.95
2023-05-14 05:30 | 45060.2292 | 0 | 7.3651 | 39.95
2023-05-14 06:00 | 45060.25 | 0 | 7.621 | 39.95
2023-05-14 06:30 | 45060.2708 | 0 | 7.6911 | 39.95
2023-05-14 07:00 | 45060.2917 | 0 | 7.7529 | 39.95
2023-05-14 07:30 | 45060.3125 | 0 | 8.2694 | 39.95
2023-05-14 08:00 | 45060.3333 | 0 | 7.8497 | 39.95
2023-05-14 08:30 | 45060.3542 | 0 | 7.8763 | 39.95
2023-05-14 09:00 | 45060.375 | 0 | 6.7158 | 39.95
2023-05-14 09:30 | 45060.3958 | 0 | 7.4566 | 39.95
2023-05-14 10:00 | 45060.4167 | 0 | 8.5424 | 39.95
2023-05-14 10:30 | 45060.4375 | 0 | 7.6953 | 39.95
2023-05-14 11:00 | 45060.4583 | 0 | 8.5003 | 39.95
2023-05-14 11:30 | 45060.4792 | 0 | 8.9853 | 39.95
2023-05-14 12:00 | 45060.5 | 0 | 9.7155 | 39.95
2023-05-14 12:30 | 45060.5208 | 0 | 9.2471 | 39.95
2023-05-14 13:00 | 45060.5417 | 0 | 8.4435 | 39.95
2023-05-14 13:30 | 45060.5625 | 0 | 8.4041 | 39.95
2023-05-14 14:00 | 45060.5833 | 0 | 8.9818 | 39.95
2023-05-14 14:30 | 45060.6042 | 0 | 10.0537 | 39.95
2023-05-14 15:00 | 45060.625 | 0 | 10.5308 | 39.95
2023-05-14 15:30 | 45060.6458 | 0 | 10.7052 | 39.95
2023-05-14 16:00 | 45060.6667 | 0 | 11.0493 | 39.95
2023-05-14 16:30 | 45060.6875 | 0 | 11.2173 | 39.95
2023-05-14 17:00 | 45060.7083 | 0 | 11.3425 | 39.95
2023-05-14 17:30 | 45060.7292 | 0 | 11.8616 | 39.95
2023-05-14 18:00 | 45060.75 | 0 | 12.0597 | 39.95
2023-05-14 18:30 | 45060.7708 | 0 | 11.6314 | 39.95
2023-05-14 19:00 | 45060.7917 | 0 | 11.3874 | 39.95
2023-05-14 19:30 | 45060.8125 | 0 | 11.0989 | 39.95
2023-05-14 20:00 | 45060.8333 | 0 | 10.5702 | 39.95
2023-05-14 20:30 | 45060.8542 | 0 | 10.2733 | 39.95
2023-05-14 21:00 | 45060.875 | 0 | 10.1597 | 39.95
2023-05-14 21:30 | 45060.8958 | 0 | 9.4052 | 39.95
2023-05-14 22:00 | 45060.9167 | 0 | 8.8269 | 39.95
2023-05-14 22:30 | 45060.9375 | 0 | 8.4218 | 39.95
2023-05-14 23:00 | 45060.9583 | 0 | 8.1985 | 39.95
2023-05-14 23:30 | 45060.9792 | 0 | 7.9887 | 39.95
2023-05-15 | 45061 | 0 | 7.7393 | 39.95
2023-05-15 00:30 | 45061.0208 | 0 | 7.525 | 39.95
2023-05-15 01:00 | 45061.0417 | 0 | 7.4482 | 39.95
2023-05-15 01:30 | 45061.0625 | 0 | 7.2023 | 39.95
2023-05-15 02:00 | 45061.0833 | 0 | 7.2558 | 39.95
2023-05-15 02:30 | 45061.1042 | 0 | 7.2576 | 39.95
2023-05-15 03:00 | 45061.125 | 0 | 7.3651 | 39.95
2023-05-15 03:30 | 45061.1458 | 0 | 7.5552 | 39.95
2023-05-15 04:00 | 45061.1667 | 0 | 7.9212 | 39.95
2023-05-15 04:30 | 45061.1875 | 0 | 8.2209 | 39.95
2023-05-15 05:00 | 45061.2083 | 0 | 8.9764 | 39.95
2023-05-15 05:30 | 45061.2292 | 0 | 9.5675 | 39.95
2023-05-15 06:00 | 45061.25 | 0 | 10.7219 | 39.95
2023-05-15 06:30 | 45061.2708 | 0 | 11.4904 | 39.95
2023-05-15 07:00 | 45061.2917 | 0 | 11.7284 | 39.95
2023-05-15 07:30 | 45061.3125 | 0 | 11.2375 | 39.95
2023-05-15 08:00 | 45061.3333 | 0 | 10.719 | 39.95
2023-05-15 08:30 | 45061.3542 | 0 | 9.8898 | 39.95
2023-05-15 09:00 | 45061.375 | 0 | 11.4803 | 39.95
2023-05-15 09:30 | 45061.3958 | 0 | 10.9908 | 39.95
2023-05-15 10:00 | 45061.4167 | 0 | 10.1528 | 39.95
2023-05-15 10:30 | 45061.4375 | 0 | 12.1133 | 39.95
2023-05-15 11:00 | 45061.4583 | 0 | 12.0186 | 39.95
2023-05-15 11:30 | 45061.4792 | 0 | 9.3414 | 39.95
2023-05-15 12:00 | 45061.5 | 0 | 8.5103 | 39.95
2023-05-15 12:30 | 45061.5208 | 0 | 10.5424 | 39.95
2023-05-15 13:00 | 45061.5417 | 0 | 10.4462 | 39.95
2023-05-15 13:30 | 45061.5625 | 0 | 10.8832 | 39.95
2023-05-15 14:00 | 45061.5833 | 0 | 11.2747 | 39.95
2023-05-15 14:30 | 45061.6042 | 0 | 12.3208 | 39.95
2023-05-15 15:00 | 45061.625 | 0 | 12.1005 | 39.95
2023-05-15 15:30 | 45061.6458 | 0 | 12.6178 | 39.95
2023-05-15 16:00 | 45061.6667 | 0 | 13.0908 | 39.95
2023-05-15 16:30 | 45061.6875 | 0 | 13.6408 | 39.95
2023-05-15 17:00 | 45061.7083 | 0 | 13.6434 | 39.95
2023-05-15 17:30 | 45061.7292 | 0 | 14.2278 | 39.95
2023-05-15 18:00 | 45061.75 | 0 | 14.1446 | 39.95
2023-05-15 18:30 | 45061.7708 | 0 | 14.0223 | 39.95
2023-05-15 19:00 | 45061.7917 | 0 | 13.745 | 39.95
2023-05-15 19:30 | 45061.8125 | 0 | 13.3768 | 39.95
2023-05-15 20:00 | 45061.8333 | 0 | 12.812 | 39.95
2023-05-15 20:30 | 45061.8542 | 0 | 12.2647 | 39.95
2023-05-15 21:00 | 45061.875 | 0 | 11.9002 | 39.95
2023-05-15 21:30 | 45061.8958 | 0 | 11.187 | 39.95
2023-05-15 22:00 | 45061.9167 | 0 | 10.4916 | 39.95
2023-05-15 22:30 | 45061.9375 | 0 | 9.9811 | 39.95
2023-05-15 23:00 | 45061.9583 | 0 | 9.6142 | 39.95
2023-05-15 23:30 | 45061.9792 | 0 | 9.2968 | 39.95
2023-05-16 | 45062 | 0 | 8.9321 | 39.95
2023-05-16 00:30 | 45062.0208 | 0 | 8.621 | 39.95
2023-05-16 01:00 | 45062.0417 | 0 | 8.4501 | 39.95
2023-05-16 01:30 | 45062.0625 | 0 | 8.2043 | 39.95
2023-05-16 02:00 | 45062.0833 | 0 | 8.1411 | 39.95
2023-05-16 02:30 | 45062.1042 | 0 | 8.227 | 39.95
2023-05-16 03:00 | 45062.125 | 0 | 8.2643 | 39.95
2023-05-16 03:30 | 45062.1458 | 0 | 8.3477 | 39.95
2023-05-16 04:00 | 45062.1667 | 0 | 8.5778 | 39.95
2023-05-16 04:30 | 45062.1875 | 0 | 8.9175 | 39.95
2023-05-16 05:00 | 45062.2083 | 0 | 9.6334 | 39.95
2023-05-16 05:30 | 45062.2292 | 0 | 10.5334 | 39.95
2023-05-16 06:00 | 45062.25 | 0 | 11.3122 | 39.95
2023-05-16 06:30 | 45062.2708 | 0 | 12.2052 | 39.95
2023-05-16 07:00 | 45062.2917 | 0 | 13.0238 | 39.95
2023-05-16 07:30 | 45062.3125 | 0 | 12.9691 | 39.95
2023-05-16 08:00 | 45062.3333 | 0 | 12.9205 | 39.95
2023-05-16 08:30 | 45062.3542 | 0 | 12.8545 | 39.95
2023-05-16 09:00 | 45062.375 | 0 | 12.5324 | 39.95
2023-05-16 09:30 | 45062.3958 | 0 | 12.3924 | 39.95
2023-05-16 10:00 | 45062.4167 | 0 | 12.0853 | 39.95
2023-05-16 10:30 | 45062.4375 | 0 | 11.5038 | 39.95
2023-05-16 11:00 | 45062.4583 | 0 | 11.5737 | 39.95
2023-05-16 11:30 | 45062.4792 | 0 | 11.3704 | 39.95
2023-05-16 12:00 | 45062.5 | 0 | 11.797 | 39.95
2023-05-16 12:30 | 45062.5208 | 0 | 11.2383 | 39.95
2023-05-16 13:00 | 45062.5417 | 0 | 9.6511 | 39.95
2023-05-16 13:30 | 45062.5625 | 0 | 10.8211 | 39.95
2023-05-16 14:00 | 45062.5833 | 0 | 11.2387 | 39.95
2023-05-16 14:30 | 45062.6042 | 0 | 11.5364 | 39.95
2023-05-16 15:00 | 45062.625 | 0 | 11.8106 | 39.95
2023-05-16 15:30 | 45062.6458 | 0 | 12.0709 | 39.95
2023-05-16 16:00 | 45062.6667 | 0 | 12.4847 | 39.95
2023-05-16 16:30 | 45062.6875 | 0 | 12.7529 | 39.95
2023-05-16 17:00 | 45062.7083 | 0 | 13.2519 | 39.95
2023-05-16 17:30 | 45062.7292 | 0 | 14.3345 | 39.95
2023-05-16 18:00 | 45062.75 | 0 | 14.4287 | 39.95
2023-05-16 18:30 | 45062.7708 | 0 | 14.3593 | 39.95
2023-05-16 19:00 | 45062.7917 | 0 | 13.8533 | 39.95
2023-05-16 19:30 | 45062.8125 | 0 | 13.5423 | 39.95
2023-05-16 20:00 | 45062.8333 | 0 | 12.8924 | 39.95
2023-05-16 20:30 | 45062.8542 | 0 | 12.406 | 39.95
2023-05-16 21:00 | 45062.875 | 0 | 12.08 | 39.95
2023-05-16 21:30 | 45062.8958 | 0 | 11.4376 | 39.95
2023-05-16 22:00 | 45062.9167 | 0 | 10.6576 | 39.95
2023-05-16 22:30 | 45062.9375 | 0 | 10.0236 | 39.95
2023-05-16 23:00 | 45062.9583 | 0 | 9.6518 | 39.95
2023-05-16 23:30 | 45062.9792 | 0 | 9.3125 | 39.95
2023-05-17 | 45063 | 0 | 8.9887 | 39.95
2023-05-17 00:30 | 45063.0208 | 0 | 8.4993 | 39.95
2023-05-17 01:00 | 45063.0417 | 0 | 8.3799 | 39.95
2023-05-17 01:30 | 45063.0625 | 0 | 8.2202 | 39.95
2023-05-17 02:00 | 45063.0833 | 0 | 8.2029 | 39.95
2023-05-17 02:30 | 45063.1042 | 0 | 8.1623 | 39.95
2023-05-17 03:00 | 45063.125 | 0 | 8.1784 | 39.95
2023-05-17 03:30 | 45063.1458 | 0 | 8.2876 | 39.95
2023-05-17 04:00 | 45063.1667 | 0 | 8.5379 | 39.95
2023-05-17 04:30 | 45063.1875 | 0 | 8.8 | 39.95
2023-05-17 05:00 | 45063.2083 | 0 | 9.4358 | 39.95
2023-05-17 05:30 | 45063.2292 | 0 | 10.1726 | 39.95
2023-05-17 06:00 | 45063.25 | 0 | 11.2733 | 39.95
2023-05-17 06:30 | 45063.2708 | 0 | 12.2682 | 39.95
2023-05-17 07:00 | 45063.2917 | 0 | 12.5979 | 39.95
2023-05-17 07:30 | 45063.3125 | 0 | 11.4429 | 39.95
2023-05-17 08:00 | 45063.3333 | 0 | 10.6145 | 39.95
2023-05-17 08:30 | 45063.3542 | 0 | 9.6611 | 39.95
2023-05-17 09:00 | 45063.375 | 0 | 8.9975 | 39.95
2023-05-17 09:30 | 45063.3958 | 0 | 8.4262 | 39.95
2023-05-17 10:00 | 45063.4167 | 0 | 7.954 | 39.95
2023-05-17 10:30 | 45063.4375 | 0 | 7.9159 | 39.95
2023-05-17 11:00 | 45063.4583 | 0 | 8.1604 | 39.95
2023-05-17 11:30 | 45063.4792 | 0 | 8.1978 | 39.95
2023-05-17 12:00 | 45063.5 | 0 | 9.1594 | 39.95
2023-05-17 12:30 | 45063.5208 | 0 | 9.1577 | 39.95
2023-05-17 13:00 | 45063.5417 | 0 | 10.0431 | 39.95
2023-05-17 13:30 | 45063.5625 | 0 | 8.9642 | 39.95
2023-05-17 14:00 | 45063.5833 | 0 | 9.7607 | 39.95
2023-05-17 14:30 | 45063.6042 | 0 | 10.4078 | 39.95
2023-05-17 15:00 | 45063.625 | 0 | 10.1369 | 39.95
2023-05-17 15:30 | 45063.6458 | 0 | 11.0007 | 39.95
2023-05-17 16:00 | 45063.6667 | 0 | 12.0461 | 39.95
2023-05-17 16:30 | 45063.6875 | 0 | 12.433 | 39.95
2023-05-17 17:00 | 45063.7083 | 0 | 12.8028 | 39.95
2023-05-17 17:30 | 45063.7292 | 0 | 13.5524 | 39.95
2023-05-17 18:00 | 45063.75 | 0 | 13.6572 | 39.95
2023-05-17 18:30 | 45063.7708 | 0 | 13.438 | 39.95
2023-05-17 19:00 | 45063.7917 | 0 | 13.4437 | 39.95
2023-05-17 19:30 | 45063.8125 | 0 | 13.0322 | 39.95
2023-05-17 20:00 | 45063.8333 | 0 | 12.5307 | 39.95
2023-05-17 20:30 | 45063.8542 | 0 | 12.3431 | 39.95
2023-05-17 21:00 | 45063.875 | 0 | 12.134 | 39.95
2023-05-17 21:30 | 45063.8958 | 0 | 11.2686 | 39.95
2023-05-17 22:00 | 45063.9167 | 0 | 10.6197 | 39.95
2023-05-17 22:30 | 45063.9375 | 0 | 10.1111 | 39.95
2023-05-17 23:00 | 45063.9583 | 0 | 9.7511 | 39.95
2023-05-17 23:30 | 45063.9792 | 0 | 9.3696 | 39.95
2023-05-18 | 45064 | 0 | 8.9234 | 39.95
2023-05-18 00:30 | 45064.0208 | 0 | 8.5322 | 39.95
2023-05-18 01:00 | 45064.0417 | 0 | 8.4069 | 39.95
2023-05-18 01:30 | 45064.0625 | 0 | 8.1881 | 39.95
2023-05-18 02:00 | 45064.0833 | 0 | 8.1383 | 39.95
2023-05-18 02:30 | 45064.1042 | 0 | 8.0003 | 39.95
2023-05-18 03:00 | 45064.125 | 0 | 8.0437 | 39.95
2023-05-18 03:30 | 45064.1458 | 0 | 8.1324 | 39.95
2023-05-18 04:00 | 45064.1667 | 0 | 8.4898 | 39.95
2023-05-18 04:30 | 45064.1875 | 0 | 8.7417 | 39.95
2023-05-18 05:00 | 45064.2083 | 0 | 9.2691 | 39.95
2023-05-18 05:30 | 45064.2292 | 0 | 10.0495 | 39.95
2023-05-18 06:00 | 45064.25 | 0 | 11.261 | 39.95
2023-05-18 06:30 | 45064.2708 | 0 | 12.1249 | 39.95
2023-05-18 07:00 | 45064.2917 | 0 | 12.5774 | 39.95
2023-05-18 07:30 | 45064.3125 | 0 | 11.3372 | 39.95
2023-05-18 08:00 | 45064.3333 | 0 | 10.6323 | 39.95
2023-05-18 08:30 | 45064.3542 | 0 | 9.7872 | 39.95
2023-05-18 09:00 | 45064.375 | 0 | 9.2232 | 39.95
2023-05-18 09:30 | 45064.3958 | 0 | 8.285 | 39.95
2023-05-18 10:00 | 45064.4167 | 0 | 7.7989 | 39.95
2023-05-18 10:30 | 45064.4375 | 0 | 7.9194 | 39.95
2023-05-18 11:00 | 45064.4583 | 0 | 7.935 | 39.95
2023-05-18 11:30 | 45064.4792 | 0 | 7.9023 | 39.95
2023-05-18 12:00 | 45064.5 | 0 | 7.4999 | 39.95
2023-05-18 12:30 | 45064.5208 | 0 | 7.3864 | 39.95
2023-05-18 13:00 | 45064.5417 | 0 | 8.7979 | 39.95
2023-05-18 13:30 | 45064.5625 | 0 | 10.167 | 39.95
2023-05-18 14:00 | 45064.5833 | 0 | 9.4556 | 39.95
2023-05-18 14:30 | 45064.6042 | 0 | 9.1489 | 39.95
2023-05-18 15:00 | 45064.625 | 0 | 10.1003 | 39.95
2023-05-18 15:30 | 45064.6458 | 0 | 10.8644 | 39.95
2023-05-18 16:00 | 45064.6667 | 0 | 11.4068 | 39.95
2023-05-18 16:30 | 45064.6875 | 0 | 12.3319 | 39.95
2023-05-18 17:00 | 45064.7083 | 0 | 12.8201 | 39.95
2023-05-18 17:30 | 45064.7292 | 0 | 13.5003 | 39.95
2023-05-18 18:00 | 45064.75 | 0 | 13.5153 | 39.95
2023-05-18 18:30 | 45064.7708 | 0 | 13.3916 | 39.95
2023-05-18 19:00 | 45064.7917 | 0 | 13.1758 | 39.95
2023-05-18 19:30 | 45064.8125 | 0 | 13.1116 | 39.95
2023-05-18 20:00 | 45064.8333 | 0 | 12.5102 | 39.95
2023-05-18 20:30 | 45064.8542 | 0 | 12.2144 | 39.95
2023-05-18 21:00 | 45064.875 | 0 | 11.8536 | 39.95
2023-05-18 21:30 | 45064.8958 | 0 | 11.2111 | 39.95
2023-05-18 22:00 | 45064.9167 | 0 | 10.4672 | 39.95
2023-05-18 22:30 | 45064.9375 | 0 | 9.9474 | 39.95
2023-05-18 23:00 | 45064.9583 | 0 | 9.8138 | 39.95
2023-05-18 23:30 | 45064.9792 | 0 | 9.3659 | 39.95
2023-05-19 | 45065 | 0 | 9.0465 | 39.95
2023-05-19 00:30 | 45065.0208 | 0 | 8.5128 | 39.95
2023-05-19 01:00 | 45065.0417 | 0 | 8.3835 | 39.95
2023-05-19 01:30 | 45065.0625 | 0 | 8.1023 | 39.95
2023-05-19 02:00 | 45065.0833 | 0 | 8.1388 | 39.95
2023-05-19 02:30 | 45065.1042 | 0 | 8.1445 | 39.95
2023-05-19 03:00 | 45065.125 | 0 | 8.1176 | 39.95
2023-05-19 03:30 | 45065.1458 | 0 | 8.4147 | 39.95
2023-05-19 04:00 | 45065.1667 | 0 | 8.752 | 39.95
2023-05-19 04:30 | 45065.1875 | 0 | 8.9649 | 39.95
2023-05-19 05:00 | 45065.2083 | 0 | 9.4205 | 39.95
2023-05-19 05:30 | 45065.2292 | 0 | 10.1252 | 39.95
2023-05-19 06:00 | 45065.25 | 0 | 11.2823 | 39.95
2023-05-19 06:30 | 45065.2708 | 0 | 12.4599 | 39.95
2023-05-19 07:00 | 45065.2917 | 0 | 12.8356 | 39.95
2023-05-19 07:30 | 45065.3125 | 0 | 11.7615 | 39.95
2023-05-19 08:00 | 45065.3333 | 0 | 11.1795 | 39.95
2023-05-19 08:30 | 45065.3542 | 0 | 10.245 | 39.95
2023-05-19 09:00 | 45065.375 | 0 | 9.2118 | 39.95
2023-05-19 09:30 | 45065.3958 | 0 | 8.4194 | 39.95
2023-05-19 10:00 | 45065.4167 | 0 | 7.8525 | 39.95
2023-05-19 10:30 | 45065.4375 | 0 | 7.9337 | 39.95
2023-05-19 11:00 | 45065.4583 | 0 | 7.7553 | 39.95
2023-05-19 11:30 | 45065.4792 | 0 | 7.75 | 39.95
2023-05-19 12:00 | 45065.5 | 0 | 7.4622 | 39.95
2023-05-19 12:30 | 45065.5208 | 0 | 7.4049 | 39.95
2023-05-19 13:00 | 45065.5417 | 0 | 8.7841 | 39.95
2023-05-19 13:30 | 45065.5625 | 0 | 8.5565 | 39.95
2023-05-19 14:00 | 45065.5833 | 0 | 9.3188 | 39.95
2023-05-19 14:30 | 45065.6042 | 0 | 9.3075 | 39.95
2023-05-19 15:00 | 45065.625 | 0 | 10.0119 | 39.95
2023-05-19 15:30 | 45065.6458 | 0 | 10.8097 | 39.95
2023-05-19 16:00 | 45065.6667 | 0 | 11.4731 | 39.95
2023-05-19 16:30 | 45065.6875 | 0 | 12.1544 | 39.95
2023-05-19 17:00 | 45065.7083 | 0 | 12.6881 | 39.95
2023-05-19 17:30 | 45065.7292 | 0 | 13.3771 | 39.95
2023-05-19 18:00 | 45065.75 | 0 | 13.3143 | 39.95
2023-05-19 18:30 | 45065.7708 | 0 | 13.2055 | 39.95
2023-05-19 19:00 | 45065.7917 | 0 | 12.961 | 39.95
2023-05-19 19:30 | 45065.8125 | 0 | 12.7047 | 39.95
2023-05-19 20:00 | 45065.8333 | 0 | 12.4503 | 39.95
2023-05-19 20:30 | 45065.8542 | 0 | 12.0828 | 39.95
2023-05-19 21:00 | 45065.875 | 0 | 11.9108 | 39.95
2023-05-19 21:30 | 45065.8958 | 0 | 11.2608 | 39.95
2023-05-19 22:00 | 45065.9167 | 0 | 10.6538 | 39.95
2023-05-19 22:30 | 45065.9375 | 0 | 10.0795 | 39.95
2023-05-19 23:00 | 45065.9583 | 0 | 9.5232 | 39.95
2023-05-19 23:30 | 45065.9792 | 0 | 9.1587 | 39.95
2023-05-20 | 45066 | 0 | 8.9452 | 39.95
2023-05-20 00:30 | 45066.0208 | 0 | 8.6646 | 39.95
2023-05-20 01:00 | 45066.0417 | 0 | 8.3845 | 39.95
2023-05-20 01:30 | 45066.0625 | 0 | 8.1343 | 39.95
2023-05-20 02:00 | 45066.0833 | 0 | 7.983 | 39.95
2023-05-20 02:30 | 45066.1042 | 0 | 7.865 | 39.95
2023-05-20 03:00 | 45066.125 | 0 | 7.8113 | 39.95
2023-05-20 03:30 | 45066.1458 | 0 | 7.8663 | 39.95
2023-05-20 04:00 | 45066.1667 | 0 | 7.9744 | 39.95
2023-05-20 04:30 | 45066.1875 | 0 | 8.0271 | 39.95
2023-05-20 05:00 | 45066.2083 | 0 | 8.4672 | 39.95
2023-05-20 05:30 | 45066.2292 | 0 | 8.6249 | 39.95
2023-05-20 06:00 | 45066.25 | 0 | 8.9004 | 39.95
2023-05-20 06:30 | 45066.2708 | 0 | 9.4408 | 39.95
2023-05-20 07:00 | 45066.2917 | 0 | 9.6477 | 39.95
2023-05-20 07:30 | 45066.3125 | 0 | 9.0392 | 39.95
2023-05-20 08:00 | 45066.3333 | 0 | 8.6734 | 39.95
2023-05-20 08:30 | 45066.3542 | 0 | 8.0646 | 39.95
2023-05-20 09:00 | 45066.375 | 0 | 7.3216 | 39.95
2023-05-20 09:30 | 45066.3958 | 0 | 6.5445 | 39.95
2023-05-20 10:00 | 45066.4167 | 0 | 5.8051 | 39.95
2023-05-20 10:30 | 45066.4375 | 0 | 5.7892 | 39.95
2023-05-20 11:00 | 45066.4583 | 0 | 5.8002 | 39.95
2023-05-20 11:30 | 45066.4792 | 0 | 5.6879 | 39.95
2023-05-20 12:00 | 45066.5 | 0 | 5.4493 | 39.95
2023-05-20 12:30 | 45066.5208 | 0 | 5.3157 | 39.95
2023-05-20 13:00 | 45066.5417 | 0 | 5.7319 | 39.95
2023-05-20 13:30 | 45066.5625 | 0 | 5.9176 | 39.95
2023-05-20 14:00 | 45066.5833 | 0 | 6.3221 | 39.95
2023-05-20 14:30 | 45066.6042 | 0 | 7.0463 | 39.95
2023-05-20 15:00 | 45066.625 | 0 | 8.0863 | 39.95
2023-05-20 15:30 | 45066.6458 | 0 | 8.9413 | 39.95
2023-05-20 16:00 | 45066.6667 | 0 | 9.7768 | 39.95
2023-05-20 16:30 | 45066.6875 | 0 | 10.5942 | 39.95
2023-05-20 17:00 | 45066.7083 | 0 | 11.1441 | 39.95
2023-05-20 17:30 | 45066.7292 | 0 | 11.6894 | 39.95
2023-05-20 18:00 | 45066.75 | 0 | 11.593 | 39.95
2023-05-20 18:30 | 45066.7708 | 0 | 11.3233 | 39.95
2023-05-20 19:00 | 45066.7917 | 0 | 11.2396 | 39.95
2023-05-20 19:30 | 45066.8125 | 0 | 11.1739 | 39.95
2023-05-20 20:00 | 45066.8333 | 0 | 10.8349 | 39.95
2023-05-20 20:30 | 45066.8542 | 0 | 10.6192 | 39.95
2023-05-20 21:00 | 45066.875 | 0 | 10.3715 | 39.95
2023-05-20 21:30 | 45066.8958 | 0 | 9.7903 | 39.95
2023-05-20 22:00 | 45066.9167 | 0 | 9.1926 | 39.95
2023-05-20 22:30 | 45066.9375 | 0 | 8.8581 | 39.95
2023-05-20 23:00 | 45066.9583 | 0 | 8.5927 | 39.95
2023-05-20 23:30 | 45066.9792 | 0 | 8.2082 | 39.95
2023-05-21 | 45067 | 0 | 7.9207 | 39.95
2023-05-21 00:30 | 45067.0208 | 0 | 7.5411 | 39.95
2023-05-21 01:00 | 45067.0417 | 0 | 7.4551 | 39.95
2023-05-21 01:30 | 45067.0625 | 0 | 7.2885 | 39.95
2023-05-21 02:00 | 45067.0833 | 0 | 7.2259 | 39.95
2023-05-21 02:30 | 45067.1042 | 0 | 7.1018 | 39.95
2023-05-21 03:00 | 45067.125 | 0 | 7.1092 | 39.95
2023-05-21 03:30 | 45067.1458 | 0 | 7.143 | 39.95
2023-05-21 04:00 | 45067.1667 | 0 | 7.0869 | 39.95
2023-05-21 04:30 | 45067.1875 | 0 | 7.1974 | 39.95
2023-05-21 05:00 | 45067.2083 | 0 | 7.3016 | 39.95
2023-05-21 05:30 | 45067.2292 | 0 | 7.6317 | 39.95
2023-05-21 06:00 | 45067.25 | 0 | 7.9057 | 39.95
2023-05-21 06:30 | 45067.2708 | 0 | 8.3099 | 39.95
2023-05-21 07:00 | 45067.2917 | 0 | 8.4131 | 39.95
2023-05-21 07:30 | 45067.3125 | 0 | 7.8332 | 39.95
2023-05-21 08:00 | 45067.3333 | 0 | 7.5548 | 39.95
2023-05-21 08:30 | 45067.3542 | 0 | 6.9059 | 39.95
2023-05-21 09:00 | 45067.375 | 0 | 6.2506 | 39.95
2023-05-21 09:30 | 45067.3958 | 0 | 5.632 | 39.95
2023-05-21 10:00 | 45067.4167 | 0 | 5.0057 | 39.95
2023-05-21 10:30 | 45067.4375 | 0 | 5.0431 | 39.95
2023-05-21 11:00 | 45067.4583 | 0 | 5.0162 | 39.95
2023-05-21 11:30 | 45067.4792 | 0 | 5.0489 | 39.95
2023-05-21 12:00 | 45067.5 | 0 | 4.8905 | 39.95
2023-05-21 12:30 | 45067.5208 | 0 | 4.7311 | 39.95
2023-05-21 13:00 | 45067.5417 | 0 | 5.0464 | 39.95
2023-05-21 13:30 | 45067.5625 | 0 | 5.3863 | 39.95
2023-05-21 14:00 | 45067.5833 | 0 | 5.986 | 39.95
2023-05-21 14:30 | 45067.6042 | 0 | 6.8445 | 39.95
2023-05-21 15:00 | 45067.625 | 0 | 7.6732 | 39.95
2023-05-21 15:30 | 45067.6458 | 0 | 8.676 | 39.95
2023-05-21 16:00 | 45067.6667 | 0 | 9.6583 | 39.95
2023-05-21 16:30 | 45067.6875 | 0 | 10.7118 | 39.95
2023-05-21 17:00 | 45067.7083 | 0 | 11.7464 | 39.95
2023-05-21 17:30 | 45067.7292 | 0 | 12.6357 | 39.95
2023-05-21 18:00 | 45067.75 | 0 | 12.7468 | 39.95
2023-05-21 18:30 | 45067.7708 | 0 | 12.393 | 39.95
2023-05-21 19:00 | 45067.7917 | 0 | 12.0262 | 39.95
2023-05-21 19:30 | 45067.8125 | 0 | 11.7053 | 39.95
2023-05-21 20:00 | 45067.8333 | 0 | 11.096 | 39.95
2023-05-21 20:30 | 45067.8542 | 0 | 10.7779 | 39.95
2023-05-21 21:00 | 45067.875 | 0 | 10.4587 | 39.95
2023-05-21 21:30 | 45067.8958 | 0 | 9.5419 | 39.95
2023-05-21 22:00 | 45067.9167 | 0 | 9.0907 | 39.95
2023-05-21 22:30 | 45067.9375 | 0 | 8.62 | 39.95
2023-05-21 23:00 | 45067.9583 | 0 | 8.3978 | 39.95
2023-05-21 23:30 | 45067.9792 | 0 | 8.0832 | 39.95
2023-05-22 | 45068 | 0 | 7.8251 | 39.95
2023-05-22 00:30 | 45068.0208 | 0 | 7.5296 | 39.95
2023-05-22 01:00 | 45068.0417 | 0 | 7.439 | 39.95
2023-05-22 01:30 | 45068.0625 | 0 | 7.2123 | 39.95
2023-05-22 02:00 | 45068.0833 | 0 | 7.3394 | 39.95
2023-05-22 02:30 | 45068.1042 | 0 | 7.5009 | 39.95
2023-05-22 03:00 | 45068.125 | 0 | 7.486 | 39.95
2023-05-22 03:30 | 45068.1458 | 0 | 7.7127 | 39.95
2023-05-22 04:00 | 45068.1667 | 0 | 8.1645 | 39.95
2023-05-22 04:30 | 45068.1875 | 0 | 8.4117 | 39.95
2023-05-22 05:00 | 45068.2083 | 0 | 9.1481 | 39.95
2023-05-22 05:30 | 45068.2292 | 0 | 10.256 | 39.95
2023-05-22 06:00 | 45068.25 | 0 | 11.6391 | 39.95
2023-05-22 06:30 | 45068.2708 | 0 | 12.9944 | 39.95
2023-05-22 07:00 | 45068.2917 | 0 | 13.3292 | 39.95
2023-05-22 07:30 | 45068.3125 | 0 | 12.0567 | 39.95
2023-05-22 08:00 | 45068.3333 | 0 | 11.136 | 39.95
2023-05-22 08:30 | 45068.3542 | 0 | 10.2392 | 39.95
2023-05-22 09:00 | 45068.375 | 0 | 9.3589 | 39.95
2023-05-22 09:30 | 45068.3958 | 0 | 8.4379 | 39.95
2023-05-22 10:00 | 45068.4167 | 0 | 7.7287 | 39.95
2023-05-22 10:30 | 45068.4375 | 0 | 7.7591 | 39.95
2023-05-22 11:00 | 45068.4583 | 0 | 7.8337 | 39.95
2023-05-22 11:30 | 45068.4792 | 0 | 7.746 | 39.95
2023-05-22 12:00 | 45068.5 | 0 | 7.3696 | 39.95
2023-05-22 12:30 | 45068.5208 | 0 | 7.5271 | 39.95
2023-05-22 13:00 | 45068.5417 | 0 | 7.9234 | 39.95
2023-05-22 13:30 | 45068.5625 | 0 | 8.1798 | 39.95
2023-05-22 14:00 | 45068.5833 | 0 | 8.5286 | 39.95
2023-05-22 14:30 | 45068.6042 | 0 | 9.2333 | 39.95
2023-05-22 15:00 | 45068.625 | 0 | 10.1118 | 39.95
2023-05-22 15:30 | 45068.6458 | 0 | 11.0547 | 39.95
2023-05-22 16:00 | 45068.6667 | 0 | 11.8132 | 39.95
2023-05-22 16:30 | 45068.6875 | 0 | 12.5151 | 39.95
2023-05-22 17:00 | 45068.7083 | 0 | 13.1412 | 39.95
2023-05-22 17:30 | 45068.7292 | 0 | 14.1338 | 39.95
2023-05-22 18:00 | 45068.75 | 0 | 14.234 | 39.95
2023-05-22 18:30 | 45068.7708 | 0 | 14.1275 | 39.95
2023-05-22 19:00 | 45068.7917 | 0 | 14.0054 | 39.95
2023-05-22 19:30 | 45068.8125 | 0 | 13.5274 | 39.95
2023-05-22 20:00 | 45068.8333 | 0 | 13.0659 | 39.95
2023-05-22 20:30 | 45068.8542 | 0 | 12.5682 | 39.95
2023-05-22 21:00 | 45068.875 | 0 | 12.4004 | 39.95
2023-05-22 21:30 | 45068.8958 | 0 | 11.5495 | 39.95
2023-05-22 22:00 | 45068.9167 | 0 | 10.6135 | 39.95
2023-05-22 22:30 | 45068.9375 | 0 | 10.1502 | 39.95
2023-05-22 23:00 | 45068.9583 | 0 | 9.8308 | 39.95
2023-05-22 23:30 | 45068.9792 | 0 | 9.3926 | 39.95
2023-05-23 | 45069 | 0 | 8.9284 | 39.95
2023-05-23 00:30 | 45069.0208 | 0 | 8.5654 | 39.95
2023-05-23 01:00 | 45069.0417 | 0 | 8.333 | 39.95
2023-05-23 01:30 | 45069.0625 | 0 | 8.2904 | 39.95
2023-05-23 02:00 | 45069.0833 | 0 | 8.148 | 39.95
2023-05-23 02:30 | 45069.1042 | 0 | 8.1514 | 39.95
2023-05-23 03:00 | 45069.125 | 0 | 8.2172 | 39.95
2023-05-23 03:30 | 45069.1458 | 0 | 8.4823 | 39.95
2023-05-23 04:00 | 45069.1667 | 0 | 8.7228 | 39.95
2023-05-23 04:30 | 45069.1875 | 0 | 9.0914 | 39.95
2023-05-23 05:00 | 45069.2083 | 0 | 9.9401 | 39.95
2023-05-23 05:30 | 45069.2292 | 0 | 10.7266 | 39.95
2023-05-23 06:00 | 45069.25 | 0 | 12.2956 | 39.95
2023-05-23 06:30 | 45069.2708 | 0 | 13.7526 | 39.95
2023-05-23 07:00 | 45069.2917 | 0 | 13.9546 | 39.95
2023-05-23 07:30 | 45069.3125 | 0 | 12.7411 | 39.95
2023-05-23 08:00 | 45069.3333 | 0 | 11.5976 | 39.95
2023-05-23 08:30 | 45069.3542 | 0 | 10.7028 | 39.95
2023-05-23 09:00 | 45069.375 | 0 | 9.6499 | 39.95
2023-05-23 09:30 | 45069.3958 | 0 | 8.9675 | 39.95
2023-05-23 10:00 | 45069.4167 | 0 | 8.1997 | 39.95
2023-05-23 10:30 | 45069.4375 | 0 | 8.24 | 39.95
2023-05-23 11:00 | 45069.4583 | 0 | 8.3146 | 39.95
2023-05-23 11:30 | 45069.4792 | 0 | 8.1349 | 39.95
2023-05-23 12:00 | 45069.5 | 0 | 7.7501 | 39.95
2023-05-23 12:30 | 45069.5208 | 0 | 7.8811 | 39.95
2023-05-23 13:00 | 45069.5417 | 0 | 8.0546 | 39.95
2023-05-23 13:30 | 45069.5625 | 0 | 8.3801 | 39.95
2023-05-23 14:00 | 45069.5833 | 0 | 8.9208 | 39.95
2023-05-23 14:30 | 45069.6042 | 0 | 9.4907 | 39.95
2023-05-23 15:00 | 45069.625 | 0 | 10.1773 | 39.95
2023-05-23 15:30 | 45069.6458 | 0 | 11.0826 | 39.95
2023-05-23 16:00 | 45069.6667 | 0 | 11.8955 | 39.95
2023-05-23 16:30 | 45069.6875 | 0 | 12.52 | 39.95
2023-05-23 17:00 | 45069.7083 | 0 | 13.2816 | 39.95
2023-05-23 17:30 | 45069.7292 | 0 | 14.2863 | 39.95
2023-05-23 18:00 | 45069.75 | 0 | 14.451 | 39.95
2023-05-23 18:30 | 45069.7708 | 0 | 14.1 | 39.95
2023-05-23 19:00 | 45069.7917 | 0 | 13.8148 | 39.95
2023-05-23 19:30 | 45069.8125 | 0 | 13.6826 | 39.95
2023-05-23 20:00 | 45069.8333 | 0 | 13.2612 | 39.95
2023-05-23 20:30 | 45069.8542 | 0 | 12.8546 | 39.95
2023-05-23 21:00 | 45069.875 | 0 | 12.5123 | 39.95
2023-05-23 21:30 | 45069.8958 | 0 | 11.6986 | 39.95
2023-05-23 22:00 | 45069.9167 | 0 | 10.9855 | 39.95
2023-05-23 22:30 | 45069.9375 | 0 | 10.2983 | 39.95
2023-05-23 23:00 | 45069.9583 | 0 | 9.785 | 39.95
2023-05-23 23:30 | 45069.9792 | 0 | 9.4588 | 39.95
2023-05-24 | 45070 | 0 | 8.9587 | 39.95
2023-05-24 00:30 | 45070.0208 | 0 | 8.6124 | 39.95
2023-05-24 01:00 | 45070.0417 | 0 | 8.3207 | 39.95
2023-05-24 01:30 | 45070.0625 | 0 | 8.2447 | 39.95
2023-05-24 02:00 | 45070.0833 | 0 | 8.2534 | 39.95
2023-05-24 02:30 | 45070.1042 | 0 | 8.2127 | 39.95
2023-05-24 03:00 | 45070.125 | 0 | 8.1468 | 39.95
2023-05-24 03:30 | 45070.1458 | 0 | 8.4685 | 39.95
2023-05-24 04:00 | 45070.1667 | 0 | 8.712 | 39.95
2023-05-24 04:30 | 45070.1875 | 0 | 8.9858 | 39.95
2023-05-24 05:00 | 45070.2083 | 0 | 9.827 | 39.95
2023-05-24 05:30 | 45070.2292 | 0 | 10.7616 | 39.95
2023-05-24 06:00 | 45070.25 | 0 | 12.4042 | 39.95
2023-05-24 06:30 | 45070.2708 | 0 | 13.4082 | 39.95
2023-05-24 07:00 | 45070.2917 | 0 | 13.8514 | 39.95
2023-05-24 07:30 | 45070.3125 | 0 | 12.7859 | 39.95
2023-05-24 08:00 | 45070.3333 | 0 | 11.8984 | 39.95
2023-05-24 08:30 | 45070.3542 | 0 | 11.314 | 39.95
2023-05-24 09:00 | 45070.375 | 0 | 10.2104 | 39.95
2023-05-24 09:30 | 45070.3958 | 0 | 9.518 | 39.95
2023-05-24 10:00 | 45070.4167 | 0 | 8.8346 | 39.95
2023-05-24 10:30 | 45070.4375 | 0 | 8.7778 | 39.95
2023-05-24 11:00 | 45070.4583 | 0 | 8.8172 | 39.95
2023-05-24 11:30 | 45070.4792 | 0 | 8.9675 | 39.95
2023-05-24 12:00 | 45070.5 | 0 | 8.6481 | 39.95
2023-05-24 12:30 | 45070.5208 | 0 | 8.6013 | 39.95
2023-05-24 13:00 | 45070.5417 | 0 | 8.8386 | 39.95
2023-05-24 13:30 | 45070.5625 | 0 | 9.1544 | 39.95
2023-05-24 14:00 | 45070.5833 | 0 | 9.6569 | 39.95
2023-05-24 14:30 | 45070.6042 | 0 | 10.056 | 39.95
2023-05-24 15:00 | 45070.625 | 0 | 10.7051 | 39.95
2023-05-24 15:30 | 45070.6458 | 0 | 11.7773 | 39.95
2023-05-24 16:00 | 45070.6667 | 0 | 12.414 | 39.95
2023-05-24 16:30 | 45070.6875 | 0 | 13.0544 | 39.95
2023-05-24 17:00 | 45070.7083 | 0 | 13.6401 | 39.95
2023-05-24 17:30 | 45070.7292 | 0 | 14.5305 | 39.95
2023-05-24 18:00 | 45070.75 | 0 | 14.6519 | 39.95
2023-05-24 18:30 | 45070.7708 | 0 | 14.656 | 39.95
2023-05-24 19:00 | 45070.7917 | 0 | 14.4469 | 39.95
2023-05-24 19:30 | 45070.8125 | 0 | 14.067 | 39.95
2023-05-24 20:00 | 45070.8333 | 0 | 13.6591 | 39.95
2023-05-24 20:30 | 45070.8542 | 0 | 13.0798 | 39.95
2023-05-24 21:00 | 45070.875 | 0 | 12.9839 | 39.95
2023-05-24 21:30 | 45070.8958 | 0 | 12.3667 | 39.95
2023-05-24 22:00 | 45070.9167 | 0 | 11.3789 | 39.95
2023-05-24 22:30 | 45070.9375 | 0 | 10.8331 | 39.95
2023-05-24 23:00 | 45070.9583 | 0 | 10.4347 | 39.95
2023-05-24 23:30 | 45070.9792 | 0 | 9.968 | 39.95
2023-05-25 | 45071 | 0 | 9.578 | 39.95
2023-05-25 00:30 | 45071.0208 | 0 | 9.2463 | 39.95
2023-05-25 01:00 | 45071.0417 | 0 | 9.0657 | 39.95
2023-05-25 01:30 | 45071.0625 | 0 | 8.9119 | 39.95
2023-05-25 02:00 | 45071.0833 | 0 | 8.5745 | 39.95
2023-05-25 02:30 | 45071.1042 | 0 | 8.2631 | 39.95
2023-05-25 03:00 | 45071.125 | 0 | 8.2367 | 39.95
2023-05-25 03:30 | 45071.1458 | 0 | 8.5023 | 39.95
2023-05-25 04:00 | 45071.1667 | 0 | 9.1403 | 39.95
2023-05-25 04:30 | 45071.1875 | 0 | 9.4916 | 39.95
2023-05-25 05:00 | 45071.2083 | 0 | 10.0152 | 39.95
2023-05-25 05:30 | 45071.2292 | 0 | 10.9886 | 39.95
2023-05-25 06:00 | 45071.25 | 0 | 12.3768 | 39.95
2023-05-25 06:30 | 45071.2708 | 0 | 13.5548 | 39.95
2023-05-25 07:00 | 45071.2917 | 0 | 13.4024 | 39.95
2023-05-25 07:30 | 45071.3125 | 0 | 12.7782 | 39.95
2023-05-25 08:00 | 45071.3333 | 0 | 11.977 | 39.95
2023-05-25 08:30 | 45071.3542 | 0 | 10.6837 | 39.95
2023-05-25 09:00 | 45071.375 | 0 | 9.9079 | 39.95
2023-05-25 09:30 | 45071.3958 | 0 | 9.2289 | 39.95
2023-05-25 10:00 | 45071.4167 | 0 | 8.5319 | 39.95
2023-05-25 10:30 | 45071.4375 | 0 | 8.4507 | 39.95
2023-05-25 11:00 | 45071.4583 | 0 | 8.5952 | 39.95
2023-05-25 11:30 | 45071.4792 | 0 | 8.8471 | 39.95
2023-05-25 12:00 | 45071.5 | 0 | 8.1153 | 39.95
2023-05-25 12:30 | 45071.5208 | 0 | 8.2343 | 39.95
2023-05-25 13:00 | 45071.5417 | 0 | 8.3536 | 39.95
2023-05-25 13:30 | 45071.5625 | 0 | 8.7101 | 39.95
2023-05-25 14:00 | 45071.5833 | 0 | 9.2618 | 39.95
2023-05-25 14:30 | 45071.6042 | 0 | 9.7209 | 39.95
2023-05-25 15:00 | 45071.625 | 0 | 10.6679 | 39.95
2023-05-25 15:30 | 45071.6458 | 0 | 11.506 | 39.95
2023-05-25 16:00 | 45071.6667 | 0 | 12.296 | 39.95
2023-05-25 16:30 | 45071.6875 | 0 | 12.7291 | 39.95
2023-05-25 17:00 | 45071.7083 | 0 | 13.1769 | 39.95
2023-05-25 17:30 | 45071.7292 | 0 | 14.0071 | 39.95
2023-05-25 18:00 | 45071.75 | 0 | 14.0312 | 39.95
2023-05-25 18:30 | 45071.7708 | 0 | 14.0101 | 39.95
2023-05-25 19:00 | 45071.7917 | 0 | 13.7037 | 39.95
2023-05-25 19:30 | 45071.8125 | 0 | 13.3672 | 39.95
2023-05-25 20:00 | 45071.8333 | 0 | 13.0115 | 39.95
2023-05-25 20:30 | 45071.8542 | 0 | 12.545 | 39.95
2023-05-25 21:00 | 45071.875 | 0 | 12.2734 | 39.95
2023-05-25 21:30 | 45071.8958 | 0 | 11.6298 | 39.95
2023-05-25 22:00 | 45071.9167 | 0 | 10.7966 | 39.95
2023-05-25 22:30 | 45071.9375 | 0 | 10.0819 | 39.95
2023-05-25 23:00 | 45071.9583 | 0 | 9.6795 | 39.95
2023-05-25 23:30 | 45071.9792 | 0 | 9.2424 | 39.95
2023-05-26 | 45072 | 0 | 8.7792 | 39.95
2023-05-26 00:30 | 45072.0208 | 0 | 8.5063 | 39.95
2023-05-26 01:00 | 45072.0417 | 0 | 8.3181 | 39.95
2023-05-26 01:30 | 45072.0625 | 0 | 8.1526 | 39.95
2023-05-26 02:00 | 45072.0833 | 0 | 8.0577 | 39.95
2023-05-26 02:30 | 45072.1042 | 0 | 8.1176 | 39.95
2023-05-26 03:00 | 45072.125 | 0 | 7.9802 | 39.95
2023-05-26 03:30 | 45072.1458 | 0 | 8.3303 | 39.95
2023-05-26 04:00 | 45072.1667 | 0 | 8.6025 | 39.95
2023-05-26 04:30 | 45072.1875 | 0 | 8.9427 | 39.95
2023-05-26 05:00 | 45072.2083 | 0 | 9.575 | 39.95
2023-05-26 05:30 | 45072.2292 | 0 | 10.3405 | 39.95
2023-05-26 06:00 | 45072.25 | 0 | 11.4305 | 39.95
2023-05-26 06:30 | 45072.2708 | 0 | 12.681 | 39.95
2023-05-26 07:00 | 45072.2917 | 0 | 12.8437 | 39.95
2023-05-26 07:30 | 45072.3125 | 0 | 12.5046 | 39.95
2023-05-26 08:00 | 45072.3333 | 0 | 11.7697 | 39.95
2023-05-26 08:30 | 45072.3542 | 0 | 10.8168 | 39.95
2023-05-26 09:00 | 45072.375 | 0 | 9.9188 | 39.95
2023-05-26 09:30 | 45072.3958 | 0 | 8.9828 | 39.95
2023-05-26 10:00 | 45072.4167 | 0 | 8.3598 | 39.95
2023-05-26 10:30 | 45072.4375 | 0 | 8.4223 | 39.95
2023-05-26 11:00 | 45072.4583 | 0 | 8.6329 | 39.95
2023-05-26 11:30 | 45072.4792 | 0 | 8.4407 | 39.95
2023-05-26 12:00 | 45072.5 | 0 | 7.8558 | 39.95
2023-05-26 12:30 | 45072.5208 | 0 | 8.1022 | 39.95
2023-05-26 13:00 | 45072.5417 | 0 | 10.6106 | 39.95
2023-05-26 13:30 | 45072.5625 | 0 | 9.3998 | 39.95
2023-05-26 14:00 | 45072.5833 | 0 | 9.659 | 39.95
2023-05-26 14:30 | 45072.6042 | 0 | 9.5249 | 39.95
2023-05-26 15:00 | 45072.625 | 0 | 10.2438 | 39.95
2023-05-26 15:30 | 45072.6458 | 0 | 11.1162 | 39.95
2023-05-26 16:00 | 45072.6667 | 0 | 11.7706 | 39.95
2023-05-26 16:30 | 45072.6875 | 0 | 12.2538 | 39.95
2023-05-26 17:00 | 45072.7083 | 0 | 12.5249 | 39.95
2023-05-26 17:30 | 45072.7292 | 0 | 13.1578 | 39.95
2023-05-26 18:00 | 45072.75 | 0 | 13.1831 | 39.95
2023-05-26 18:30 | 45072.7708 | 0 | 12.9739 | 39.95
2023-05-26 19:00 | 45072.7917 | 0 | 12.7279 | 39.95
2023-05-26 19:30 | 45072.8125 | 0 | 12.5436 | 39.95
2023-05-26 20:00 | 45072.8333 | 0 | 12.2969 | 39.95
2023-05-26 20:30 | 45072.8542 | 0 | 11.9183 | 39.95
2023-05-26 21:00 | 45072.875 | 0 | 11.6989 | 39.95
2023-05-26 21:30 | 45072.8958 | 0 | 11.187 | 39.95
2023-05-26 22:00 | 45072.9167 | 0 | 10.5726 | 39.95
2023-05-26 22:30 | 45072.9375 | 0 | 10.028 | 39.95
2023-05-26 23:00 | 45072.9583 | 0 | 9.5894 | 39.95
2023-05-26 23:30 | 45072.9792 | 0 | 9.224 | 39.95
2023-05-27 | 45073 | 0 | 8.7656 | 39.95
2023-05-27 00:30 | 45073.0208 | 0 | 8.4081 | 39.95
2023-05-27 01:00 | 45073.0417 | 0 | 8.2328 | 39.95
2023-05-27 01:30 | 45073.0625 | 0 | 7.9716 | 39.95
2023-05-27 02:00 | 45073.0833 | 0 | 7.9264 | 39.95
2023-05-27 02:30 | 45073.1042 | 0 | 7.7558 | 39.95
2023-05-27 03:00 | 45073.125 | 0 | 7.7214 | 39.95
2023-05-27 03:30 | 45073.1458 | 0 | 7.6338 | 39.95
2023-05-27 04:00 | 45073.1667 | 0 | 7.758 | 39.95
2023-05-27 04:30 | 45073.1875 | 0 | 7.8485 | 39.95
2023-05-27 05:00 | 45073.2083 | 0 | 8.1009 | 39.95
2023-05-27 05:30 | 45073.2292 | 0 | 8.3177 | 39.95
2023-05-27 06:00 | 45073.25 | 0 | 8.7434 | 39.95
2023-05-27 06:30 | 45073.2708 | 0 | 9.2916 | 39.95
2023-05-27 07:00 | 45073.2917 | 0 | 9.3746 | 39.95
2023-05-27 07:30 | 45073.3125 | 0 | 8.9302 | 39.95
2023-05-27 08:00 | 45073.3333 | 0 | 8.7714 | 39.95
2023-05-27 08:30 | 45073.3542 | 0 | 8.0589 | 39.95
2023-05-27 09:00 | 45073.375 | 0 | 7.392 | 39.95
2023-05-27 09:30 | 45073.3958 | 0 | 6.7008 | 39.95
2023-05-27 10:00 | 45073.4167 | 0 | 6.7789 | 39.95
2023-05-27 10:30 | 45073.4375 | 0 | 6.4831 | 39.95
2023-05-27 11:00 | 45073.4583 | 0 | 5.9946 | 39.95
2023-05-27 11:30 | 45073.4792 | 0 | 5.4341 | 39.95
2023-05-27 12:00 | 45073.5 | 0 | 5.286 | 39.95
2023-05-27 12:30 | 45073.5208 | 0 | 5.519 | 39.95
2023-05-27 13:00 | 45073.5417 | 0 | 5.9584 | 39.95
2023-05-27 13:30 | 45073.5625 | 0 | 6.083 | 39.95
2023-05-27 14:00 | 45073.5833 | 0 | 6.5311 | 39.95
2023-05-27 14:30 | 45073.6042 | 0 | 7.1718 | 39.95
2023-05-27 15:00 | 45073.625 | 0 | 8.0301 | 39.95
2023-05-27 15:30 | 45073.6458 | 0 | 8.9543 | 39.95
2023-05-27 16:00 | 45073.6667 | 0 | 9.6795 | 39.95
2023-05-27 16:30 | 45073.6875 | 0 | 10.552 | 39.95
2023-05-27 17:00 | 45073.7083 | 0 | 11.0153 | 39.95
2023-05-27 17:30 | 45073.7292 | 0 | 11.704 | 39.95
2023-05-27 18:00 | 45073.75 | 0 | 11.6543 | 39.95
2023-05-27 18:30 | 45073.7708 | 0 | 11.3282 | 39.95
2023-05-27 19:00 | 45073.7917 | 0 | 11.0753 | 39.95
2023-05-27 19:30 | 45073.8125 | 0 | 10.824 | 39.95
2023-05-27 20:00 | 45073.8333 | 0 | 10.5831 | 39.95
2023-05-27 20:30 | 45073.8542 | 0 | 10.3616 | 39.95
2023-05-27 21:00 | 45073.875 | 0 | 10.1786 | 39.95
2023-05-27 21:30 | 45073.8958 | 0 | 9.7562 | 39.95
2023-05-27 22:00 | 45073.9167 | 0 | 9.1275 | 39.95
2023-05-27 22:30 | 45073.9375 | 0 | 8.664 | 39.95
2023-05-27 23:00 | 45073.9583 | 0 | 8.5346 | 39.95
2023-05-27 23:30 | 45073.9792 | 0 | 8.1347 | 39.95
2023-05-28 | 45074 | 0 | 7.7985 | 39.95
2023-05-28 00:30 | 45074.0208 | 0 | 7.4212 | 39.95
2023-05-28 01:00 | 45074.0417 | 0 | 7.2992 | 39.95
2023-05-28 01:30 | 45074.0625 | 0 | 7.228 | 39.95
2023-05-28 02:00 | 45074.0833 | 0 | 7.1252 | 39.95
2023-05-28 02:30 | 45074.1042 | 0 | 7.1524 | 39.95
2023-05-28 03:00 | 45074.125 | 0 | 7.0942 | 39.95
2023-05-28 03:30 | 45074.1458 | 0 | 7.0882 | 39.95
2023-05-28 04:00 | 45074.1667 | 0 | 7.1686 | 39.95
2023-05-28 04:30 | 45074.1875 | 0 | 7.125 | 39.95
2023-05-28 05:00 | 45074.2083 | 0 | 7.3266 | 39.95
2023-05-28 05:30 | 45074.2292 | 0 | 7.5965 | 39.95
2023-05-28 06:00 | 45074.25 | 0 | 7.9701 | 39.95
2023-05-28 06:30 | 45074.2708 | 0 | 8.1039 | 39.95
2023-05-28 07:00 | 45074.2917 | 0 | 8.3338 | 39.95
2023-05-28 07:30 | 45074.3125 | 0 | 7.8721 | 39.95
2023-05-28 08:00 | 45074.3333 | 0 | 7.4492 | 39.95
2023-05-28 08:30 | 45074.3542 | 0 | 7.0314 | 39.95
2023-05-28 09:00 | 45074.375 | 0 | 6.4745 | 39.95
2023-05-28 09:30 | 45074.3958 | 0 | 5.7537 | 39.95
2023-05-28 10:00 | 45074.4167 | 0 | 5.1431 | 39.95
2023-05-28 10:30 | 45074.4375 | 0 | 5.0872 | 39.95
2023-05-28 11:00 | 45074.4583 | 0 | 5.106 | 39.95
2023-05-28 11:30 | 45074.4792 | 0 | 5.0855 | 39.95
2023-05-28 12:00 | 45074.5 | 0 | 4.9627 | 39.95
2023-05-28 12:30 | 45074.5208 | 0 | 4.9545 | 39.95
2023-05-28 13:00 | 45074.5417 | 0 | 5.2848 | 39.95
2023-05-28 13:30 | 45074.5625 | 0 | 5.4886 | 39.95
2023-05-28 14:00 | 45074.5833 | 0 | 5.9563 | 39.95
2023-05-28 14:30 | 45074.6042 | 0 | 6.9034 | 39.95
2023-05-28 15:00 | 45074.625 | 0 | 7.9101 | 39.95
2023-05-28 15:30 | 45074.6458 | 0 | 8.9336 | 39.95
2023-05-28 16:00 | 45074.6667 | 0 | 9.8248 | 39.95
2023-05-28 16:30 | 45074.6875 | 0 | 10.6957 | 39.95
2023-05-28 17:00 | 45074.7083 | 0 | 11.6883 | 39.95
2023-05-28 17:30 | 45074.7292 | 0 | 12.5791 | 39.95
2023-05-28 18:00 | 45074.75 | 0 | 12.69 | 39.95
2023-05-28 18:30 | 45074.7708 | 0 | 12.3462 | 39.95
2023-05-28 19:00 | 45074.7917 | 0 | 12.0486 | 39.95
2023-05-28 19:30 | 45074.8125 | 0 | 11.6113 | 39.95
2023-05-28 20:00 | 45074.8333 | 0 | 11.2523 | 39.95
2023-05-28 20:30 | 45074.8542 | 0 | 10.8179 | 39.95
2023-05-28 21:00 | 45074.875 | 0 | 10.3708 | 39.95
2023-05-28 21:30 | 45074.8958 | 0 | 9.7312 | 39.95
2023-05-28 22:00 | 45074.9167 | 0 | 9.04 | 39.95
2023-05-28 22:30 | 45074.9375 | 0 | 8.5971 | 39.95
2023-05-28 23:00 | 45074.9583 | 0 | 8.3124 | 39.95
2023-05-28 23:30 | 45074.9792 | 0 | 8.1786 | 39.95
2023-05-29 | 45075 | 0 | 7.8581 | 39.95
2023-05-29 00:30 | 45075.0208 | 0 | 7.5994 | 39.95
2023-05-29 01:00 | 45075.0417 | 0 | 7.5637 | 39.95
2023-05-29 01:30 | 45075.0625 | 0 | 7.4338 | 39.95
2023-05-29 02:00 | 45075.0833 | 0 | 7.3333 | 39.95
2023-05-29 02:30 | 45075.1042 | 0 | 7.335 | 39.95
2023-05-29 03:00 | 45075.125 | 0 | 7.5994 | 39.95
2023-05-29 03:30 | 45075.1458 | 0 | 7.736 | 39.95
2023-05-29 04:00 | 45075.1667 | 0 | 7.9465 | 39.95
2023-05-29 04:30 | 45075.1875 | 0 | 8.4305 | 39.95
2023-05-29 05:00 | 45075.2083 | 0 | 9.2 | 39.95
2023-05-29 05:30 | 45075.2292 | 0 | 10.1895 | 39.95
2023-05-29 06:00 | 45075.25 | 0 | 11.7024 | 39.95
2023-05-29 06:30 | 45075.2708 | 0 | 13.1513 | 39.95
2023-05-29 07:00 | 45075.2917 | 0 | 13.2541 | 39.95
2023-05-29 07:30 | 45075.3125 | 0 | 12.562 | 39.95
2023-05-29 08:00 | 45075.3333 | 0 | 11.5151 | 39.95
2023-05-29 08:30 | 45075.3542 | 0 | 10.5697 | 39.95
2023-05-29 09:00 | 45075.375 | 0 | 9.5304 | 39.95
2023-05-29 09:30 | 45075.3958 | 0 | 8.7434 | 39.95
2023-05-29 10:00 | 45075.4167 | 0 | 7.9599 | 39.95
2023-05-29 10:30 | 45075.4375 | 0 | 7.6175 | 39.95
2023-05-29 11:00 | 45075.4583 | 0 | 7.5786 | 39.95
2023-05-29 11:30 | 45075.4792 | 0 | 7.5036 | 39.95
2023-05-29 12:00 | 45075.5 | 0 | 7.2272 | 39.95
2023-05-29 12:30 | 45075.5208 | 0 | 7.3819 | 39.95
2023-05-29 13:00 | 45075.5417 | 0 | 7.8297 | 39.95
2023-05-29 13:30 | 45075.5625 | 0 | 8.2914 | 39.95
2023-05-29 14:00 | 45075.5833 | 0 | 8.712 | 39.95
2023-05-29 14:30 | 45075.6042 | 0 | 9.1547 | 39.95
2023-05-29 15:00 | 45075.625 | 0 | 9.8537 | 39.95
2023-05-29 15:30 | 45075.6458 | 0 | 10.8715 | 39.95
2023-05-29 16:00 | 45075.6667 | 0 | 11.6606 | 39.95
2023-05-29 16:30 | 45075.6875 | 0 | 12.4986 | 39.95
2023-05-29 17:00 | 45075.7083 | 0 | 13.3906 | 39.95
2023-05-29 17:30 | 45075.7292 | 0 | 14.3346 | 39.95
2023-05-29 18:00 | 45075.75 | 0 | 14.7927 | 39.95
2023-05-29 18:30 | 45075.7708 | 0 | 14.8424 | 39.95
2023-05-29 19:00 | 45075.7917 | 0 | 14.6844 | 39.95
2023-05-29 19:30 | 45075.8125 | 0 | 14.1672 | 39.95
2023-05-29 20:00 | 45075.8333 | 0 | 13.7973 | 39.95
2023-05-29 20:30 | 45075.8542 | 0 | 13.1958 | 39.95
2023-05-29 21:00 | 45075.875 | 0 | 12.815 | 39.95
2023-05-29 21:30 | 45075.8958 | 0 | 11.8422 | 39.95
2023-05-29 22:00 | 45075.9167 | 0 | 10.8635 | 39.95
2023-05-29 22:30 | 45075.9375 | 0 | 10.0835 | 39.95
2023-05-29 23:00 | 45075.9583 | 0 | 9.7497 | 39.95
2023-05-29 23:30 | 45075.9792 | 0 | 9.3267 | 39.95
2023-05-30 | 45076 | 0 | 9.0511 | 39.95
2023-05-30 00:30 | 45076.0208 | 0 | 8.5504 | 39.95
2023-05-30 01:00 | 45076.0417 | 0 | 8.2731 | 39.95
2023-05-30 01:30 | 45076.0625 | 0 | 8.0924 | 39.95
2023-05-30 02:00 | 45076.0833 | 0 | 8.1436 | 39.95
2023-05-30 02:30 | 45076.1042 | 0 | 8.0768 | 39.95
2023-05-30 03:00 | 45076.125 | 0 | 8.205 | 39.95
2023-05-30 03:30 | 45076.1458 | 0 | 8.3821 | 39.95
2023-05-30 04:00 | 45076.1667 | 0 | 8.8617 | 39.95
2023-05-30 04:30 | 45076.1875 | 0 | 9.3595 | 39.95
2023-05-30 05:00 | 45076.2083 | 0 | 10.0109 | 39.95
2023-05-30 05:30 | 45076.2292 | 0 | 11.0616 | 39.95
2023-05-30 06:00 | 45076.25 | 0 | 12.4187 | 39.95
2023-05-30 06:30 | 45076.2708 | 0 | 13.9761 | 39.95
2023-05-30 07:00 | 45076.2917 | 0 | 14.149 | 39.95
2023-05-30 07:30 | 45076.3125 | 0 | 13.3415 | 39.95
2023-05-30 08:00 | 45076.3333 | 0 | 12.3239 | 39.95
2023-05-30 08:30 | 45076.3542 | 0 | 11.3117 | 39.95
2023-05-30 09:00 | 45076.375 | 0 | 10.2085 | 39.95
2023-05-30 09:30 | 45076.3958 | 0 | 9.2844 | 39.95
2023-05-30 10:00 | 45076.4167 | 0 | 8.5138 | 39.95
2023-05-30 10:30 | 45076.4375 | 0 | 8.5409 | 39.95
2023-05-30 11:00 | 45076.4583 | 0 | 8.3033 | 39.95
2023-05-30 11:30 | 45076.4792 | 0 | 8.2773 | 39.95
2023-05-30 12:00 | 45076.5 | 0 | 7.8728 | 39.95
2023-05-30 12:30 | 45076.5208 | 0 | 7.8878 | 39.95
2023-05-30 13:00 | 45076.5417 | 0 | 8.1639 | 39.95
2023-05-30 13:30 | 45076.5625 | 0 | 8.4824 | 39.95
2023-05-30 14:00 | 45076.5833 | 0 | 9.0832 | 39.95
2023-05-30 14:30 | 45076.6042 | 0 | 9.8215 | 39.95
2023-05-30 15:00 | 45076.625 | 0 | 10.5256 | 39.95
2023-05-30 15:30 | 45076.6458 | 0 | 11.306 | 39.95
2023-05-30 16:00 | 45076.6667 | 0 | 12.1265 | 39.95
2023-05-30 16:30 | 45076.6875 | 0 | 12.6934 | 39.95
2023-05-30 17:00 | 45076.7083 | 0 | 13.3816 | 39.95
2023-05-30 17:30 | 45076.7292 | 0 | 14.5959 | 39.95
2023-05-30 18:00 | 45076.75 | 0 | 14.6853 | 39.95
2023-05-30 18:30 | 45076.7708 | 0 | 14.753 | 39.95
2023-05-30 19:00 | 45076.7917 | 0 | 14.3868 | 39.95
2023-05-30 19:30 | 45076.8125 | 0 | 14.1123 | 39.95
2023-05-30 20:00 | 45076.8333 | 0 | 13.6677 | 39.95
2023-05-30 20:30 | 45076.8542 | 0 | 13.1049 | 39.95
2023-05-30 21:00 | 45076.875 | 0 | 12.6321 | 39.95
2023-05-30 21:30 | 45076.8958 | 0 | 11.8889 | 39.95
2023-05-30 22:00 | 45076.9167 | 0 | 10.8743 | 39.95
2023-05-30 22:30 | 45076.9375 | 0 | 10.1988 | 39.95
2023-05-30 23:00 | 45076.9583 | 0 | 9.724 | 39.95
2023-05-30 23:30 | 45076.9792 | 0 | 9.4639 | 39.95
2023-05-31 | 45077 | 0 | 8.9508 | 39.95
2023-05-31 00:30 | 45077.0208 | 0 | 8.5557 | 39.95
2023-05-31 01:00 | 45077.0417 | 0 | 8.3555 | 39.95
2023-05-31 01:30 | 45077.0625 | 0 | 8.2564 | 39.95
2023-05-31 02:00 | 45077.0833 | 0 | 8.2177 | 39.95
2023-05-31 02:30 | 45077.1042 | 0 | 8.2354 | 39.95
2023-05-31 03:00 | 45077.125 | 0 | 8.1768 | 39.95
2023-05-31 03:30 | 45077.1458 | 0 | 8.4028 | 39.95
2023-05-31 04:00 | 45077.1667 | 0 | 8.7365 | 39.95
2023-05-31 04:30 | 45077.1875 | 0 | 9.1536 | 39.95
2023-05-31 05:00 | 45077.2083 | 0 | 9.9193 | 39.95
2023-05-31 05:30 | 45077.2292 | 0 | 11.0425 | 39.95
2023-05-31 06:00 | 45077.25 | 0 | 12.3406 | 39.95
2023-05-31 06:30 | 45077.2708 | 0 | 13.7301 | 39.95
2023-05-31 07:00 | 45077.2917 | 0 | 14.1329 | 39.95
2023-05-31 07:30 | 45077.3125 | 0 | 13.3324 | 39.95
2023-05-31 08:00 | 45077.3333 | 0 | 12.6806 | 39.95
2023-05-31 08:30 | 45077.3542 | 0 | 11.6403 | 39.95
2023-05-31 09:00 | 45077.375 | 0 | 10.5545 | 39.95
2023-05-31 09:30 | 45077.3958 | 0 | 9.7304 | 39.95
2023-05-31 10:00 | 45077.4167 | 0 | 9.0136 | 39.95
2023-05-31 10:30 | 45077.4375 | 0 | 8.9188 | 39.95
2023-05-31 11:00 | 45077.4583 | 0 | 8.8267 | 39.95
2023-05-31 11:30 | 45077.4792 | 0 | 8.5495 | 39.95
2023-05-31 12:00 | 45077.5 | 0 | 8.051 | 39.95
2023-05-31 12:30 | 45077.5208 | 0 | 8.3008 | 39.95
2023-05-31 13:00 | 45077.5417 | 0 | 8.6233 | 39.95
2023-05-31 13:30 | 45077.5625 | 0 | 8.5867 | 39.95
2023-05-31 14:00 | 45077.5833 | 0 | 9.3066 | 39.95
2023-05-31 14:30 | 45077.6042 | 0 | 9.7702 | 39.95
2023-05-31 15:00 | 45077.625 | 0 | 10.4318 | 39.95
2023-05-31 15:30 | 45077.6458 | 0 | 11.1437 | 39.95
2023-05-31 16:00 | 45077.6667 | 0 | 12.0195 | 39.95
2023-05-31 16:30 | 45077.6875 | 0 | 12.5955 | 39.95
2023-05-31 17:00 | 45077.7083 | 0 | 13.3522 | 39.95
2023-05-31 17:30 | 45077.7292 | 0 | 14.2214 | 39.95
2023-05-31 18:00 | 45077.75 | 0 | 14.5563 | 39.95
2023-05-31 18:30 | 45077.7708 | 0 | 14.6487 | 39.95
2023-05-31 19:00 | 45077.7917 | 0 | 14.3415 | 39.95
2023-05-31 19:30 | 45077.8125 | 0 | 14.0477 | 39.95
2023-05-31 20:00 | 45077.8333 | 0 | 13.5918 | 39.95
2023-05-31 20:30 | 45077.8542 | 0 | 12.9027 | 39.95
2023-05-31 21:00 | 45077.875 | 0 | 12.4563 | 39.95
2023-05-31 21:30 | 45077.8958 | 0 | 11.7347 | 39.95
2023-05-31 22:00 | 45077.9167 | 0 | 10.8776 | 39.95
2023-05-31 22:30 | 45077.9375 | 0 | 10.5452 | 39.95
2023-05-31 23:00 | 45077.9583 | 0 | 10.1294 | 39.95
2023-05-31 23:30 | 45077.9792 | 0 | 9.4967 | 39.95
2023-06-01 | 45078 | 0 | 9.1206 | 39.95
2023-06-01 00:30 | 45078.0208 | 0 | 8.6437 | 39.95
2023-06-01 01:00 | 45078.0417 | 0 | 8.4001 | 39.95
2023-06-01 01:30 | 45078.0625 | 0 | 8.1931 | 39.95
2023-06-01 02:00 | 45078.0833 | 0 | 8.2482 | 39.95
2023-06-01 02:30 | 45078.1042 | 0 | 8.1797 | 39.95
2023-06-01 03:00 | 45078.125 | 0 | 8.0502 | 39.95
2023-06-01 03:30 | 45078.1458 | 0 | 8.3552 | 39.95
2023-06-01 04:00 | 45078.1667 | 0 | 8.839 | 39.95
2023-06-01 04:30 | 45078.1875 | 0 | 8.9442 | 39.95
2023-06-01 05:00 | 45078.2083 | 0 | 9.6347 | 39.95
2023-06-01 05:30 | 45078.2292 | 0 | 10.5722 | 39.95
2023-06-01 06:00 | 45078.25 | 0 | 11.9238 | 39.95
2023-06-01 06:30 | 45078.2708 | 0 | 13.3189 | 39.95
2023-06-01 07:00 | 45078.2917 | 0 | 13.6438 | 39.95
2023-06-01 07:30 | 45078.3125 | 0 | 12.6432 | 39.95
2023-06-01 08:00 | 45078.3333 | 0 | 11.7816 | 39.95
2023-06-01 08:30 | 45078.3542 | 0 | 10.8049 | 39.95
2023-06-01 09:00 | 45078.375 | 0 | 9.8604 | 39.95
2023-06-01 09:30 | 45078.3958 | 0 | 9.2371 | 39.95
2023-06-01 10:00 | 45078.4167 | 0 | 8.7411 | 39.95
2023-06-01 10:30 | 45078.4375 | 0 | 8.5068 | 39.95
2023-06-01 11:00 | 45078.4583 | 0 | 8.6122 | 39.95
2023-06-01 11:30 | 45078.4792 | 0 | 8.5345 | 39.95
2023-06-01 12:00 | 45078.5 | 0 | 8.0987 | 39.95
2023-06-01 12:30 | 45078.5208 | 0 | 8.1885 | 39.95
2023-06-01 13:00 | 45078.5417 | 0 | 8.5091 | 39.95
2023-06-01 13:30 | 45078.5625 | 0 | 8.6228 | 39.95
2023-06-01 14:00 | 45078.5833 | 0 | 10.7756 | 39.95
2023-06-01 14:30 | 45078.6042 | 0 | 10.072 | 39.95
2023-06-01 15:00 | 45078.625 | 0 | 10.5852 | 39.95
2023-06-01 15:30 | 45078.6458 | 0 | 11.7132 | 39.95
2023-06-01 16:00 | 45078.6667 | 0 | 11.9664 | 39.95
2023-06-01 16:30 | 45078.6875 | 0 | 12.4916 | 39.95
2023-06-01 17:00 | 45078.7083 | 0 | 13.0155 | 39.95
2023-06-01 17:30 | 45078.7292 | 0 | 13.736 | 39.95
2023-06-01 18:00 | 45078.75 | 0 | 13.9214 | 39.95
2023-06-01 18:30 | 45078.7708 | 0 | 13.6855 | 39.95
2023-06-01 19:00 | 45078.7917 | 0 | 13.5679 | 39.95
2023-06-01 19:30 | 45078.8125 | 0 | 13.2749 | 39.95
2023-06-01 20:00 | 45078.8333 | 0 | 12.9971 | 39.95
2023-06-01 20:30 | 45078.8542 | 0 | 12.4475 | 39.95
2023-06-01 21:00 | 45078.875 | 0 | 12.1938 | 39.95
2023-06-01 21:30 | 45078.8958 | 0 | 11.3586 | 39.95
2023-06-01 22:00 | 45078.9167 | 0 | 10.6305 | 39.95
2023-06-01 22:30 | 45078.9375 | 0 | 10.0493 | 39.95
2023-06-01 23:00 | 45078.9583 | 0 | 9.6329 | 39.95
2023-06-01 23:30 | 45078.9792 | 0 | 9.3054 | 39.95
2023-06-02 | 45079 | 0 | 8.9693 | 39.95
2023-06-02 00:30 | 45079.0208 | 0 | 8.631 | 39.95
2023-06-02 01:00 | 45079.0417 | 0 | 8.3663 | 39.95
2023-06-02 01:30 | 45079.0625 | 0 | 8.1724 | 39.95
2023-06-02 02:00 | 45079.0833 | 0 | 8.202 | 39.95
2023-06-02 02:30 | 45079.1042 | 0 | 8.1582 | 39.95
2023-06-02 03:00 | 45079.125 | 0 | 8.0331 | 39.95
2023-06-02 03:30 | 45079.1458 | 0 | 8.2235 | 39.95
2023-06-02 04:00 | 45079.1667 | 0 | 8.5287 | 39.95
2023-06-02 04:30 | 45079.1875 | 0 | 8.9947 | 39.95
2023-06-02 05:00 | 45079.2083 | 0 | 9.7504 | 39.95
2023-06-02 05:30 | 45079.2292 | 0 | 10.4663 | 39.95
2023-06-02 06:00 | 45079.25 | 0 | 11.5309 | 39.95
2023-06-02 06:30 | 45079.2708 | 0 | 12.768 | 39.95
2023-06-02 07:00 | 45079.2917 | 0 | 13.0009 | 39.95
2023-06-02 07:30 | 45079.3125 | 0 | 12.3204 | 39.95
2023-06-02 08:00 | 45079.3333 | 0 | 11.5112 | 39.95
2023-06-02 08:30 | 45079.3542 | 0 | 10.5521 | 39.95
2023-06-02 09:00 | 45079.375 | 0 | 9.8583 | 39.95
2023-06-02 09:30 | 45079.3958 | 0 | 9.4104 | 39.95
2023-06-02 10:00 | 45079.4167 | 0 | 8.7805 | 39.95
2023-06-02 10:30 | 45079.4375 | 0 | 8.9373 | 39.95
2023-06-02 11:00 | 45079.4583 | 0 | 9.6811 | 39.95
2023-06-02 11:30 | 45079.4792 | 0 | 10.5621 | 39.95
2023-06-02 12:00 | 45079.5 | 0 | 11.3671 | 39.95
2023-06-02 12:30 | 45079.5208 | 0 | 10.0822 | 39.95
2023-06-02 13:00 | 45079.5417 | 0 | 11.438 | 39.95
2023-06-02 13:30 | 45079.5625 | 0 | 9.6685 | 39.95
2023-06-02 14:00 | 45079.5833 | 0 | 9.3412 | 39.95
2023-06-02 14:30 | 45079.6042 | 0 | 9.9256 | 39.95
2023-06-02 15:00 | 45079.625 | 0 | 10.5517 | 39.95
2023-06-02 15:30 | 45079.6458 | 0 | 11.4939 | 39.95
2023-06-02 16:00 | 45079.6667 | 0 | 12.0054 | 39.95
2023-06-02 16:30 | 45079.6875 | 0 | 12.4128 | 39.95
2023-06-02 17:00 | 45079.7083 | 0 | 12.8021 | 39.95
2023-06-02 17:30 | 45079.7292 | 0 | 13.5658 | 39.95
2023-06-02 18:00 | 45079.75 | 0 | 13.566 | 39.95
2023-06-02 18:30 | 45079.7708 | 0 | 13.1002 | 39.95
2023-06-02 19:00 | 45079.7917 | 0 | 12.9768 | 39.95
2023-06-02 19:30 | 45079.8125 | 0 | 12.7347 | 39.95
2023-06-02 20:00 | 45079.8333 | 0 | 12.3547 | 39.95
2023-06-02 20:30 | 45079.8542 | 0 | 11.9947 | 39.95
2023-06-02 21:00 | 45079.875 | 0 | 11.6982 | 39.95
2023-06-02 21:30 | 45079.8958 | 0 | 11.1186 | 39.95
2023-06-02 22:00 | 45079.9167 | 0 | 10.4975 | 39.95
2023-06-02 22:30 | 45079.9375 | 0 | 10.0406 | 39.95
2023-06-02 23:00 | 45079.9583 | 0 | 9.6362 | 39.95
2023-06-02 23:30 | 45079.9792 | 0 | 9.2858 | 39.95
2023-06-03 | 45080 | 0 | 8.908 | 39.95
2023-06-03 00:30 | 45080.0208 | 0 | 8.5265 | 39.95
2023-06-03 01:00 | 45080.0417 | 0 | 8.3099 | 39.95
2023-06-03 01:30 | 45080.0625 | 0 | 8.1744 | 39.95
2023-06-03 02:00 | 45080.0833 | 0 | 7.9749 | 39.95
2023-06-03 02:30 | 45080.1042 | 0 | 7.9579 | 39.95
2023-06-03 03:00 | 45080.125 | 0 | 7.888 | 39.95
2023-06-03 03:30 | 45080.1458 | 0 | 8.068 | 39.95
2023-06-03 04:00 | 45080.1667 | 0 | 8.0189 | 39.95
2023-06-03 04:30 | 45080.1875 | 0 | 8.0823 | 39.95
2023-06-03 05:00 | 45080.2083 | 0 | 8.404 | 39.95
2023-06-03 05:30 | 45080.2292 | 0 | 8.6571 | 39.95
2023-06-03 06:00 | 45080.25 | 0 | 8.9443 | 39.95
2023-06-03 06:30 | 45080.2708 | 0 | 9.1801 | 39.95
2023-06-03 07:00 | 45080.2917 | 0 | 9.6352 | 39.95
2023-06-03 07:30 | 45080.3125 | 0 | 10.1058 | 39.95
2023-06-03 08:00 | 45080.3333 | 0 | 9.8605 | 39.95
2023-06-03 08:30 | 45080.3542 | 0 | 8.767 | 39.95
2023-06-03 09:00 | 45080.375 | 0 | 7.6683 | 39.95
2023-06-03 09:30 | 45080.3958 | 0 | 7.5097 | 39.95
2023-06-03 10:00 | 45080.4167 | 0 | 7.0293 | 39.95
2023-06-03 10:30 | 45080.4375 | 0 | 6.957 | 39.95
2023-06-03 11:00 | 45080.4583 | 0 | 8.561 | 39.95
2023-06-03 11:30 | 45080.4792 | 0 | 10.6012 | 39.95
2023-06-03 12:00 | 45080.5 | 0 | 11.5592 | 39.95
2023-06-03 12:30 | 45080.5208 | 0 | 10.8593 | 39.95
2023-06-03 13:00 | 45080.5417 | 0 | 9.5946 | 39.95
2023-06-03 13:30 | 45080.5625 | 0 | 8.8729 | 39.95
2023-06-03 14:00 | 45080.5833 | 0 | 8.2124 | 39.95
2023-06-03 14:30 | 45080.6042 | 0 | 8.4313 | 39.95
2023-06-03 15:00 | 45080.625 | 0 | 9.7337 | 39.95
2023-06-03 15:30 | 45080.6458 | 0 | 10.6391 | 39.95
2023-06-03 16:00 | 45080.6667 | 0 | 11.1026 | 39.95
2023-06-03 16:30 | 45080.6875 | 0 | 11.383 | 39.95
2023-06-03 17:00 | 45080.7083 | 0 | 11.7135 | 39.95
2023-06-03 17:30 | 45080.7292 | 0 | 12.0248 | 39.95
2023-06-03 18:00 | 45080.75 | 0 | 11.9372 | 39.95
2023-06-03 18:30 | 45080.7708 | 0 | 11.6515 | 39.95
2023-06-03 19:00 | 45080.7917 | 0 | 11.2244 | 39.95
2023-06-03 19:30 | 45080.8125 | 0 | 10.9945 | 39.95
2023-06-03 20:00 | 45080.8333 | 0 | 10.4988 | 39.95
2023-06-03 20:30 | 45080.8542 | 0 | 10.1658 | 39.95
2023-06-03 21:00 | 45080.875 | 0 | 9.9788 | 39.95
2023-06-03 21:30 | 45080.8958 | 0 | 9.7441 | 39.95
2023-06-03 22:00 | 45080.9167 | 0 | 9.1057 | 39.95
2023-06-03 22:30 | 45080.9375 | 0 | 8.7529 | 39.95
2023-06-03 23:00 | 45080.9583 | 0 | 8.5333 | 39.95
2023-06-03 23:30 | 45080.9792 | 0 | 8.144 | 39.95
2023-06-04 | 45081 | 0 | 8.0529 | 39.95
2023-06-04 00:30 | 45081.0208 | 0 | 7.5437 | 39.95
2023-06-04 01:00 | 45081.0417 | 0 | 7.3988 | 39.95
2023-06-04 01:30 | 45081.0625 | 0 | 7.2646 | 39.95
2023-06-04 02:00 | 45081.0833 | 0 | 7.0609 | 39.95
2023-06-04 02:30 | 45081.1042 | 0 | 7.1472 | 39.95
2023-06-04 03:00 | 45081.125 | 0 | 7.0222 | 39.95
2023-06-04 03:30 | 45081.1458 | 0 | 7.1717 | 39.95
2023-06-04 04:00 | 45081.1667 | 0 | 7.0623 | 39.95
2023-06-04 04:30 | 45081.1875 | 0 | 7.1755 | 39.95
2023-06-04 05:00 | 45081.2083 | 0 | 7.2083 | 39.95
2023-06-04 05:30 | 45081.2292 | 0 | 7.2977 | 39.95
2023-06-04 06:00 | 45081.25 | 0 | 7.4383 | 39.95
2023-06-04 06:30 | 45081.2708 | 0 | 7.676 | 39.95
2023-06-04 07:00 | 45081.2917 | 0 | 7.9326 | 39.95
2023-06-04 07:30 | 45081.3125 | 0 | 8.0518 | 39.95
2023-06-04 08:00 | 45081.3333 | 0 | 8.4486 | 39.95
2023-06-04 08:30 | 45081.3542 | 0 | 8.1505 | 39.95
2023-06-04 09:00 | 45081.375 | 0 | 8.6183 | 39.95
2023-06-04 09:30 | 45081.3958 | 0 | 8.9159 | 39.95
2023-06-04 10:00 | 45081.4167 | 0 | 9.2948 | 39.95
2023-06-04 10:30 | 45081.4375 | 0 | 9.6909 | 39.95
2023-06-04 11:00 | 45081.4583 | 0 | 9.7249 | 39.95
2023-06-04 11:30 | 45081.4792 | 0 | 10.869 | 39.95
2023-06-04 12:00 | 45081.5 | 0 | 9.9769 | 39.95
2023-06-04 12:30 | 45081.5208 | 0 | 10.8125 | 39.95
2023-06-04 13:00 | 45081.5417 | 0 | 10.2277 | 39.95
2023-06-04 13:30 | 45081.5625 | 0 | 9.0172 | 39.95
2023-06-04 14:00 | 45081.5833 | 0 | 9.2318 | 39.95
2023-06-04 14:30 | 45081.6042 | 0 | 9.6331 | 39.95
2023-06-04 15:00 | 45081.625 | 0 | 9.9427 | 39.95
2023-06-04 15:30 | 45081.6458 | 0 | 10.4194 | 39.95
2023-06-04 16:00 | 45081.6667 | 0 | 10.8778 | 39.95
2023-06-04 16:30 | 45081.6875 | 0 | 11.3909 | 39.95
2023-06-04 17:00 | 45081.7083 | 0 | 11.9677 | 39.95
2023-06-04 17:30 | 45081.7292 | 0 | 12.5925 | 39.95
2023-06-04 18:00 | 45081.75 | 0 | 12.6915 | 39.95
2023-06-04 18:30 | 45081.7708 | 0 | 12.4137 | 39.95
2023-06-04 19:00 | 45081.7917 | 0 | 11.9073 | 39.95
2023-06-04 19:30 | 45081.8125 | 0 | 11.382 | 39.95
2023-06-04 20:00 | 45081.8333 | 0 | 10.9615 | 39.95
2023-06-04 20:30 | 45081.8542 | 0 | 10.5008 | 39.95
2023-06-04 21:00 | 45081.875 | 0 | 10.2624 | 39.95
2023-06-04 21:30 | 45081.8958 | 0 | 9.6441 | 39.95
2023-06-04 22:00 | 45081.9167 | 0 | 8.993 | 39.95
2023-06-04 22:30 | 45081.9375 | 0 | 8.5778 | 39.95
2023-06-04 23:00 | 45081.9583 | 0 | 8.2311 | 39.95
2023-06-04 23:30 | 45081.9792 | 0 | 8.13 | 39.95
2023-06-05 | 45082 | 0 | 7.8935 | 39.95
2023-06-05 00:30 | 45082.0208 | 0 | 7.5791 | 39.95
2023-06-05 01:00 | 45082.0417 | 0 | 7.5387 | 39.95
2023-06-05 01:30 | 45082.0625 | 0 | 7.3809 | 39.95
2023-06-05 02:00 | 45082.0833 | 0 | 7.3512 | 39.95
2023-06-05 02:30 | 45082.1042 | 0 | 7.3861 | 39.95
2023-06-05 03:00 | 45082.125 | 0 | 7.3327 | 39.95
2023-06-05 03:30 | 45082.1458 | 0 | 7.5665 | 39.95
2023-06-05 04:00 | 45082.1667 | 0 | 7.9685 | 39.95
2023-06-05 04:30 | 45082.1875 | 0 | 8.2441 | 39.95
2023-06-05 05:00 | 45082.2083 | 0 | 8.931 | 39.95
2023-06-05 05:30 | 45082.2292 | 0 | 9.6519 | 39.95
2023-06-05 06:00 | 45082.25 | 0 | 10.8507 | 39.95
2023-06-05 06:30 | 45082.2708 | 0 | 11.8687 | 39.95
2023-06-05 07:00 | 45082.2917 | 0 | 12.1661 | 39.95
2023-06-05 07:30 | 45082.3125 | 0 | 12.0732 | 39.95
2023-06-05 08:00 | 45082.3333 | 0 | 10.8578 | 39.95
2023-06-05 08:30 | 45082.3542 | 0 | 10.7659 | 39.95
2023-06-05 09:00 | 45082.375 | 0 | 12.3847 | 39.95
2023-06-05 09:30 | 45082.3958 | 0 | 10.7915 | 39.95
2023-06-05 10:00 | 45082.4167 | 0 | 10.3319 | 39.95
2023-06-05 10:30 | 45082.4375 | 0 | 11.6143 | 39.95
2023-06-05 11:00 | 45082.4583 | 0 | 11.7226 | 39.95
2023-06-05 11:30 | 45082.4792 | 0 | 10.9677 | 39.95
2023-06-05 12:00 | 45082.5 | 0 | 10.137 | 39.95
2023-06-05 12:30 | 45082.5208 | 0 | 11.2397 | 39.95
2023-06-05 13:00 | 45082.5417 | 0 | 11.9049 | 39.95
2023-06-05 13:30 | 45082.5625 | 0 | 11.1409 | 39.95
2023-06-05 14:00 | 45082.5833 | 0 | 11.4003 | 39.95
2023-06-05 14:30 | 45082.6042 | 0 | 11.9484 | 39.95
2023-06-05 15:00 | 45082.625 | 0 | 11.4907 | 39.95
2023-06-05 15:30 | 45082.6458 | 0 | 11.7144 | 39.95
2023-06-05 16:00 | 45082.6667 | 0 | 12.4295 | 39.95
2023-06-05 16:30 | 45082.6875 | 0 | 12.9166 | 39.95
2023-06-05 17:00 | 45082.7083 | 0 | 13.408 | 39.95
2023-06-05 17:30 | 45082.7292 | 0 | 14.3393 | 39.95
2023-06-05 18:00 | 45082.75 | 0 | 14.4386 | 39.95
2023-06-05 18:30 | 45082.7708 | 0 | 14.1915 | 39.95
2023-06-05 19:00 | 45082.7917 | 0 | 13.9286 | 39.95
2023-06-05 19:30 | 45082.8125 | 0 | 13.4733 | 39.95
2023-06-05 20:00 | 45082.8333 | 0 | 12.9789 | 39.95
2023-06-05 20:30 | 45082.8542 | 0 | 12.3549 | 39.95
2023-06-05 21:00 | 45082.875 | 0 | 12.0493 | 39.95
2023-06-05 21:30 | 45082.8958 | 0 | 11.4638 | 39.95
2023-06-05 22:00 | 45082.9167 | 0 | 10.5641 | 39.95
2023-06-05 22:30 | 45082.9375 | 0 | 9.9433 | 39.95
2023-06-05 23:00 | 45082.9583 | 0 | 9.5477 | 39.95
2023-06-05 23:30 | 45082.9792 | 0 | 9.1973 | 39.95
2023-06-06 | 45083 | 0 | 8.9231 | 39.95
2023-06-06 00:30 | 45083.0208 | 0 | 8.5429 | 39.95
2023-06-06 01:00 | 45083.0417 | 0 | 8.4185 | 39.95
2023-06-06 01:30 | 45083.0625 | 0 | 8.2459 | 39.95
2023-06-06 02:00 | 45083.0833 | 0 | 8.1432 | 39.95
2023-06-06 02:30 | 45083.1042 | 0 | 8.1462 | 39.95
2023-06-06 03:00 | 45083.125 | 0 | 8.202 | 39.95
2023-06-06 03:30 | 45083.1458 | 0 | 8.3987 | 39.95
2023-06-06 04:00 | 45083.1667 | 0 | 8.6348 | 39.95
2023-06-06 04:30 | 45083.1875 | 0 | 9.069 | 39.95
2023-06-06 05:00 | 45083.2083 | 0 | 9.6539 | 39.95
2023-06-06 05:30 | 45083.2292 | 0 | 10.1778 | 39.95
2023-06-06 06:00 | 45083.25 | 0 | 11.3258 | 39.95
2023-06-06 06:30 | 45083.2708 | 0 | 12.4542 | 39.95
2023-06-06 07:00 | 45083.2917 | 0 | 12.4307 | 39.95
2023-06-06 07:30 | 45083.3125 | 0 | 12.0815 | 39.95
2023-06-06 08:00 | 45083.3333 | 0 | 11.1396 | 39.95
2023-06-06 08:30 | 45083.3542 | 0 | 10.3851 | 39.95
2023-06-06 09:00 | 45083.375 | 0 | 10.8682 | 39.95
2023-06-06 09:30 | 45083.3958 | 0 | 11.1416 | 39.95
2023-06-06 10:00 | 45083.4167 | 0 | 10.3497 | 39.95
2023-06-06 10:30 | 45083.4375 | 0 | 9.0371 | 39.95
2023-06-06 11:00 | 45083.4583 | 0 | 9.94 | 39.95
2023-06-06 11:30 | 45083.4792 | 0 | 10.6952 | 39.95
2023-06-06 12:00 | 45083.5 | 0 | 9.8483 | 39.95
2023-06-06 12:30 | 45083.5208 | 0 | 10.1697 | 39.95
2023-06-06 13:00 | 45083.5417 | 0 | 10.6955 | 39.95
2023-06-06 13:30 | 45083.5625 | 0 | 10.8381 | 39.95
2023-06-06 14:00 | 45083.5833 | 0 | 8.9321 | 39.95
2023-06-06 14:30 | 45083.6042 | 0 | 9.4639 | 39.95
2023-06-06 15:00 | 45083.625 | 0 | 10.2415 | 39.95
2023-06-06 15:30 | 45083.6458 | 0 | 11.8582 | 39.95
2023-06-06 16:00 | 45083.6667 | 0 | 12.1403 | 39.95
2023-06-06 16:30 | 45083.6875 | 0 | 12.5984 | 39.95
2023-06-06 17:00 | 45083.7083 | 0 | 13.201 | 39.95
2023-06-06 17:30 | 45083.7292 | 0 | 13.926 | 39.95
2023-06-06 18:00 | 45083.75 | 0 | 14.2943 | 39.95
2023-06-06 18:30 | 45083.7708 | 0 | 14.0262 | 39.95
2023-06-06 19:00 | 45083.7917 | 0 | 13.5391 | 39.95
2023-06-06 19:30 | 45083.8125 | 0 | 13.2439 | 39.95
2023-06-06 20:00 | 45083.8333 | 0 | 12.8684 | 39.95
2023-06-06 20:30 | 45083.8542 | 0 | 12.3487 | 39.95
2023-06-06 21:00 | 45083.875 | 0 | 12.1287 | 39.95
2023-06-06 21:30 | 45083.8958 | 0 | 11.4968 | 39.95
2023-06-06 22:00 | 45083.9167 | 0 | 10.695 | 39.95
2023-06-06 22:30 | 45083.9375 | 0 | 10.0487 | 39.95
2023-06-06 23:00 | 45083.9583 | 0 | 9.6002 | 39.95
2023-06-06 23:30 | 45083.9792 | 0 | 9.3044 | 39.95
2023-06-07 | 45084 | 0 | 8.9002 | 39.95
2023-06-07 00:30 | 45084.0208 | 0 | 8.438 | 39.95
2023-06-07 01:00 | 45084.0417 | 0 | 8.2748 | 39.95
2023-06-07 01:30 | 45084.0625 | 0 | 8.0575 | 39.95
2023-06-07 02:00 | 45084.0833 | 0 | 8.0777 | 39.95
2023-06-07 02:30 | 45084.1042 | 0 | 8.1194 | 39.95
2023-06-07 03:00 | 45084.125 | 0 | 8.1321 | 39.95
2023-06-07 03:30 | 45084.1458 | 0 | 8.3413 | 39.95
2023-06-07 04:00 | 45084.1667 | 0 | 8.6057 | 39.95
2023-06-07 04:30 | 45084.1875 | 0 | 8.9079 | 39.95
2023-06-07 05:00 | 45084.2083 | 0 | 9.5935 | 39.95
2023-06-07 05:30 | 45084.2292 | 0 | 10.0282 | 39.95
2023-06-07 06:00 | 45084.25 | 0 | 11.2651 | 39.95
2023-06-07 06:30 | 45084.2708 | 0 | 12.2618 | 39.95
2023-06-07 07:00 | 45084.2917 | 0 | 12.6243 | 39.95
2023-06-07 07:30 | 45084.3125 | 0 | 11.9712 | 39.95
2023-06-07 08:00 | 45084.3333 | 0 | 11.0468 | 39.95
2023-06-07 08:30 | 45084.3542 | 0 | 10.2117 | 39.95
2023-06-07 09:00 | 45084.375 | 0 | 10.7606 | 39.95
2023-06-07 09:30 | 45084.3958 | 0 | 9.6706 | 39.95
2023-06-07 10:00 | 45084.4167 | 0 | 8.9789 | 39.95
2023-06-07 10:30 | 45084.4375 | 0 | 10.7828 | 39.95
2023-06-07 11:00 | 45084.4583 | 0 | 8.9849 | 39.95
2023-06-07 11:30 | 45084.4792 | 0 | 11.53 | 39.95
2023-06-07 12:00 | 45084.5 | 0 | 10.6782 | 39.95
2023-06-07 12:30 | 45084.5208 | 0 | 9.5832 | 39.95
2023-06-07 13:00 | 45084.5417 | 0 | 9.509 | 39.95
2023-06-07 13:30 | 45084.5625 | 0 | 9.0979 | 39.95
2023-06-07 14:00 | 45084.5833 | 0 | 9.6316 | 39.95
2023-06-07 14:30 | 45084.6042 | 0 | 10.4529 | 39.95
2023-06-07 15:00 | 45084.625 | 0 | 10.686 | 39.95
2023-06-07 15:30 | 45084.6458 | 0 | 11.8829 | 39.95
2023-06-07 16:00 | 45084.6667 | 0 | 11.9372 | 39.95
2023-06-07 16:30 | 45084.6875 | 0 | 12.5008 | 39.95
2023-06-07 17:00 | 45084.7083 | 0 | 13.2917 | 39.95
2023-06-07 17:30 | 45084.7292 | 0 | 13.9477 | 39.95
2023-06-07 18:00 | 45084.75 | 0 | 14.152 | 39.95
2023-06-07 18:30 | 45084.7708 | 0 | 13.7665 | 39.95
2023-06-07 19:00 | 45084.7917 | 0 | 13.6392 | 39.95
2023-06-07 19:30 | 45084.8125 | 0 | 13.3969 | 39.95
2023-06-07 20:00 | 45084.8333 | 0 | 12.9682 | 39.95
2023-06-07 20:30 | 45084.8542 | 0 | 12.4332 | 39.95
2023-06-07 21:00 | 45084.875 | 0 | 12.1642 | 39.95
2023-06-07 21:30 | 45084.8958 | 0 | 11.4909 | 39.95
2023-06-07 22:00 | 45084.9167 | 0 | 10.6861 | 39.95
2023-06-07 22:30 | 45084.9375 | 0 | 10.1717 | 39.95
2023-06-07 23:00 | 45084.9583 | 0 | 9.7849 | 39.95
2023-06-07 23:30 | 45084.9792 | 0 | 9.4302 | 39.95
2023-06-08 | 45085 | 0 | 8.9573 | 39.95
2023-06-08 00:30 | 45085.0208 | 0 | 8.5405 | 39.95
2023-06-08 01:00 | 45085.0417 | 0 | 8.3143 | 39.95
2023-06-08 01:30 | 45085.0625 | 0 | 8.1075 | 39.95
2023-06-08 02:00 | 45085.0833 | 0 | 8.1068 | 39.95
2023-06-08 02:30 | 45085.1042 | 0 | 8.103 | 39.95
2023-06-08 03:00 | 45085.125 | 0 | 8.0495 | 39.95
2023-06-08 03:30 | 45085.1458 | 0 | 8.3653 | 39.95
2023-06-08 04:00 | 45085.1667 | 0 | 8.6295 | 39.95
2023-06-08 04:30 | 45085.1875 | 0 | 8.955 | 39.95
2023-06-08 05:00 | 45085.2083 | 0 | 9.7491 | 39.95
2023-06-08 05:30 | 45085.2292 | 0 | 10.3607 | 39.95
2023-06-08 06:00 | 45085.25 | 0 | 11.4876 | 39.95
2023-06-08 06:30 | 45085.2708 | 0 | 12.3478 | 39.95
2023-06-08 07:00 | 45085.2917 | 0 | 12.984 | 39.95
2023-06-08 07:30 | 45085.3125 | 0 | 12.4112 | 39.95
2023-06-08 08:00 | 45085.3333 | 0 | 11.9655 | 39.95
2023-06-08 08:30 | 45085.3542 | 0 | 11.4461 | 39.95
2023-06-08 09:00 | 45085.375 | 0 | 11.2155 | 39.95
2023-06-08 09:30 | 45085.3958 | 0 | 10.8103 | 39.95
2023-06-08 10:00 | 45085.4167 | 0 | 9.9711 | 39.95
2023-06-08 10:30 | 45085.4375 | 0 | 9.6043 | 39.95
2023-06-08 11:00 | 45085.4583 | 0 | 9.123 | 39.95
2023-06-08 11:30 | 45085.4792 | 0 | 8.818 | 39.95
2023-06-08 12:00 | 45085.5 | 0 | 8.6427 | 39.95
2023-06-08 12:30 | 45085.5208 | 0 | 9.9591 | 39.95
2023-06-08 13:00 | 45085.5417 | 0 | 11.433 | 39.95
2023-06-08 13:30 | 45085.5625 | 0 | 9.9241 | 39.95
2023-06-08 14:00 | 45085.5833 | 0 | 10.1764 | 39.95
2023-06-08 14:30 | 45085.6042 | 0 | 10.8275 | 39.95
2023-06-08 15:00 | 45085.625 | 0 | 12.239 | 39.95
2023-06-08 15:30 | 45085.6458 | 0 | 11.9356 | 39.95
2023-06-08 16:00 | 45085.6667 | 0 | 12.1877 | 39.95
2023-06-08 16:30 | 45085.6875 | 0 | 12.607 | 39.95
2023-06-08 17:00 | 45085.7083 | 0 | 13.0371 | 39.95
2023-06-08 17:30 | 45085.7292 | 0 | 13.723 | 39.95
2023-06-08 18:00 | 45085.75 | 0 | 13.8282 | 39.95
2023-06-08 18:30 | 45085.7708 | 0 | 13.7214 | 39.95
2023-06-08 19:00 | 45085.7917 | 0 | 13.5061 | 39.95
2023-06-08 19:30 | 45085.8125 | 0 | 13.3525 | 39.95
2023-06-08 20:00 | 45085.8333 | 0 | 12.9064 | 39.95
2023-06-08 20:30 | 45085.8542 | 0 | 12.4681 | 39.95
2023-06-08 21:00 | 45085.875 | 0 | 12.1056 | 39.95
2023-06-08 21:30 | 45085.8958 | 0 | 11.4491 | 39.95
2023-06-08 22:00 | 45085.9167 | 0 | 10.6589 | 39.95
2023-06-08 22:30 | 45085.9375 | 0 | 10.0946 | 39.95
2023-06-08 23:00 | 45085.9583 | 0 | 9.6311 | 39.95
2023-06-08 23:30 | 45085.9792 | 0 | 9.2234 | 39.95
2023-06-09 | 45086 | 0 | 9.0288 | 39.95
2023-06-09 00:30 | 45086.0208 | 0 | 8.5632 | 39.95
2023-06-09 01:00 | 45086.0417 | 0 | 8.3292 | 39.95
2023-06-09 01:30 | 45086.0625 | 0 | 8.1312 | 39.95
2023-06-09 02:00 | 45086.0833 | 0 | 8.0949 | 39.95
2023-06-09 02:30 | 45086.1042 | 0 | 8.1194 | 39.95
2023-06-09 03:00 | 45086.125 | 0 | 8.0785 | 39.95
2023-06-09 03:30 | 45086.1458 | 0 | 8.261 | 39.95
2023-06-09 04:00 | 45086.1667 | 0 | 8.6861 | 39.95
2023-06-09 04:30 | 45086.1875 | 0 | 9.012 | 39.95
2023-06-09 05:00 | 45086.2083 | 0 | 9.5722 | 39.95
2023-06-09 05:30 | 45086.2292 | 0 | 10.2002 | 39.95
2023-06-09 06:00 | 45086.25 | 0 | 11.1033 | 39.95
2023-06-09 06:30 | 45086.2708 | 0 | 12.0174 | 39.95
2023-06-09 07:00 | 45086.2917 | 0 | 12.0749 | 39.95
2023-06-09 07:30 | 45086.3125 | 0 | 11.5345 | 39.95
2023-06-09 08:00 | 45086.3333 | 0 | 11.2516 | 39.95
2023-06-09 08:30 | 45086.3542 | 0 | 10.5209 | 39.95
2023-06-09 09:00 | 45086.375 | 0 | 9.7863 | 39.95
2023-06-09 09:30 | 45086.3958 | 0 | 9.0598 | 39.95
2023-06-09 10:00 | 45086.4167 | 0 | 8.4617 | 39.95
2023-06-09 10:30 | 45086.4375 | 0 | 8.6124 | 39.95
2023-06-09 11:00 | 45086.4583 | 0 | 8.723 | 39.95
2023-06-09 11:30 | 45086.4792 | 0 | 8.6077 | 39.95
2023-06-09 12:00 | 45086.5 | 0 | 8.0549 | 39.95
2023-06-09 12:30 | 45086.5208 | 0 | 8.0457 | 39.95
2023-06-09 13:00 | 45086.5417 | 0 | 8.2569 | 39.95
2023-06-09 13:30 | 45086.5625 | 0 | 8.396 | 39.95
2023-06-09 14:00 | 45086.5833 | 0 | 8.7182 | 39.95
2023-06-09 14:30 | 45086.6042 | 0 | 9.3673 | 39.95
2023-06-09 15:00 | 45086.625 | 0 | 10.0969 | 39.95
2023-06-09 15:30 | 45086.6458 | 0 | 10.9866 | 39.95
2023-06-09 16:00 | 45086.6667 | 0 | 11.9253 | 39.95
2023-06-09 16:30 | 45086.6875 | 0 | 12.4031 | 39.95
2023-06-09 17:00 | 45086.7083 | 0 | 12.7069 | 39.95
2023-06-09 17:30 | 45086.7292 | 0 | 13.2857 | 39.95
2023-06-09 18:00 | 45086.75 | 0 | 13.1739 | 39.95
2023-06-09 18:30 | 45086.7708 | 0 | 12.9 | 39.95
2023-06-09 19:00 | 45086.7917 | 0 | 12.8138 | 39.95
2023-06-09 19:30 | 45086.8125 | 0 | 12.6393 | 39.95
2023-06-09 20:00 | 45086.8333 | 0 | 12.2582 | 39.95
2023-06-09 20:30 | 45086.8542 | 0 | 11.8655 | 39.95
2023-06-09 21:00 | 45086.875 | 0 | 11.8003 | 39.95
2023-06-09 21:30 | 45086.8958 | 0 | 11.2296 | 39.95
2023-06-09 22:00 | 45086.9167 | 0 | 10.5611 | 39.95
2023-06-09 22:30 | 45086.9375 | 0 | 10.0124 | 39.95
2023-06-09 23:00 | 45086.9583 | 0 | 9.6472 | 39.95
2023-06-09 23:30 | 45086.9792 | 0 | 9.2196 | 39.95
2023-06-10 | 45087 | 0 | 9.0489 | 39.95
2023-06-10 00:30 | 45087.0208 | 0 | 8.5873 | 39.95
2023-06-10 01:00 | 45087.0417 | 0 | 8.2696 | 39.95
2023-06-10 01:30 | 45087.0625 | 0 | 8.0066 | 39.95
2023-06-10 02:00 | 45087.0833 | 0 | 7.981 | 39.95
2023-06-10 02:30 | 45087.1042 | 0 | 7.9556 | 39.95
2023-06-10 03:00 | 45087.125 | 0 | 7.8991 | 39.95
2023-06-10 03:30 | 45087.1458 | 0 | 8.0599 | 39.95
2023-06-10 04:00 | 45087.1667 | 0 | 8.1098 | 39.95
2023-06-10 04:30 | 45087.1875 | 0 | 8.179 | 39.95
2023-06-10 05:00 | 45087.2083 | 0 | 8.4904 | 39.95
2023-06-10 05:30 | 45087.2292 | 0 | 8.7107 | 39.95
2023-06-10 06:00 | 45087.25 | 0 | 9.1905 | 39.95
2023-06-10 06:30 | 45087.2708 | 0 | 9.5274 | 39.95
2023-06-10 07:00 | 45087.2917 | 0 | 9.7093 | 39.95
2023-06-10 07:30 | 45087.3125 | 0 | 9.4244 | 39.95
2023-06-10 08:00 | 45087.3333 | 0 | 9.2231 | 39.95
2023-06-10 08:30 | 45087.3542 | 0 | 8.4679 | 39.95
2023-06-10 09:00 | 45087.375 | 0 | 7.7399 | 39.95
2023-06-10 09:30 | 45087.3958 | 0 | 6.9862 | 39.95
2023-06-10 10:00 | 45087.4167 | 0 | 6.2741 | 39.95
2023-06-10 10:30 | 45087.4375 | 0 | 6.3529 | 39.95
2023-06-10 11:00 | 45087.4583 | 0 | 6.3052 | 39.95
2023-06-10 11:30 | 45087.4792 | 0 | 6.2963 | 39.95
2023-06-10 12:00 | 45087.5 | 0 | 6.0713 | 39.95
2023-06-10 12:30 | 45087.5208 | 0 | 5.8915 | 39.95
2023-06-10 13:00 | 45087.5417 | 0 | 6.0737 | 39.95
2023-06-10 13:30 | 45087.5625 | 0 | 6.3039 | 39.95
2023-06-10 14:00 | 45087.5833 | 0 | 7.1029 | 39.95
2023-06-10 14:30 | 45087.6042 | 0 | 8.4718 | 39.95
2023-06-10 15:00 | 45087.625 | 0 | 8.4122 | 39.95
2023-06-10 15:30 | 45087.6458 | 0 | 9.2642 | 39.95
2023-06-10 16:00 | 45087.6667 | 0 | 9.9473 | 39.95
2023-06-10 16:30 | 45087.6875 | 0 | 10.6797 | 39.95
2023-06-10 17:00 | 45087.7083 | 0 | 11.3878 | 39.95
2023-06-10 17:30 | 45087.7292 | 0 | 11.8488 | 39.95
2023-06-10 18:00 | 45087.75 | 0 | 11.8911 | 39.95
2023-06-10 18:30 | 45087.7708 | 0 | 11.5165 | 39.95
2023-06-10 19:00 | 45087.7917 | 0 | 11.3851 | 39.95
2023-06-10 19:30 | 45087.8125 | 0 | 11.2488 | 39.95
2023-06-10 20:00 | 45087.8333 | 0 | 10.9935 | 39.95
2023-06-10 20:30 | 45087.8542 | 0 | 10.7602 | 39.95
2023-06-10 21:00 | 45087.875 | 0 | 10.5973 | 39.95
2023-06-10 21:30 | 45087.8958 | 0 | 9.9311 | 39.95
2023-06-10 22:00 | 45087.9167 | 0 | 9.2583 | 39.95
2023-06-10 22:30 | 45087.9375 | 0 | 8.9039 | 39.95
2023-06-10 23:00 | 45087.9583 | 0 | 8.6746 | 39.95
2023-06-10 23:30 | 45087.9792 | 0 | 8.3092 | 39.95
2023-06-11 | 45088 | 0 | 8.0018 | 39.95
2023-06-11 00:30 | 45088.0208 | 0 | 7.6986 | 39.95
2023-06-11 01:00 | 45088.0417 | 0 | 7.427 | 39.95
2023-06-11 01:30 | 45088.0625 | 0 | 7.3348 | 39.95
2023-06-11 02:00 | 45088.0833 | 0 | 7.2752 | 39.95
2023-06-11 02:30 | 45088.1042 | 0 | 7.2425 | 39.95
2023-06-11 03:00 | 45088.125 | 0 | 7.2707 | 39.95
2023-06-11 03:30 | 45088.1458 | 0 | 7.2648 | 39.95
2023-06-11 04:00 | 45088.1667 | 0 | 7.2753 | 39.95
2023-06-11 04:30 | 45088.1875 | 0 | 7.2768 | 39.95
2023-06-11 05:00 | 45088.2083 | 0 | 7.4585 | 39.95
2023-06-11 05:30 | 45088.2292 | 0 | 7.6728 | 39.95
2023-06-11 06:00 | 45088.25 | 0 | 8.0059 | 39.95
2023-06-11 06:30 | 45088.2708 | 0 | 8.2988 | 39.95
2023-06-11 07:00 | 45088.2917 | 0 | 8.4757 | 39.95
2023-06-11 07:30 | 45088.3125 | 0 | 8.0681 | 39.95
2023-06-11 08:00 | 45088.3333 | 0 | 7.8579 | 39.95
2023-06-11 08:30 | 45088.3542 | 0 | 7.3699 | 39.95
2023-06-11 09:00 | 45088.375 | 0 | 6.88 | 39.95
2023-06-11 09:30 | 45088.3958 | 0 | 6.1444 | 39.95
2023-06-11 10:00 | 45088.4167 | 0 | 5.5897 | 39.95
2023-06-11 10:30 | 45088.4375 | 0 | 5.6237 | 39.95
2023-06-11 11:00 | 45088.4583 | 0 | 6.1062 | 39.95
2023-06-11 11:30 | 45088.4792 | 0 | 8.39 | 39.95
2023-06-11 12:00 | 45088.5 | 0 | 5.9607 | 39.95
2023-06-11 12:30 | 45088.5208 | 0 | 5.2788 | 39.95
2023-06-11 13:00 | 45088.5417 | 0 | 5.4729 | 39.95
2023-06-11 13:30 | 45088.5625 | 0 | 5.5393 | 39.95
2023-06-11 14:00 | 45088.5833 | 0 | 5.9977 | 39.95
2023-06-11 14:30 | 45088.6042 | 0 | 6.9593 | 39.95
2023-06-11 15:00 | 45088.625 | 0 | 7.8443 | 39.95
2023-06-11 15:30 | 45088.6458 | 0 | 8.962 | 39.95
2023-06-11 16:00 | 45088.6667 | 0 | 10.1408 | 39.95
2023-06-11 16:30 | 45088.6875 | 0 | 10.7786 | 39.95
2023-06-11 17:00 | 45088.7083 | 0 | 11.4014 | 39.95
2023-06-11 17:30 | 45088.7292 | 0 | 12.2709 | 39.95
2023-06-11 18:00 | 45088.75 | 0 | 12.3624 | 39.95
2023-06-11 18:30 | 45088.7708 | 0 | 12.2389 | 39.95
2023-06-11 19:00 | 45088.7917 | 0 | 11.8876 | 39.95
2023-06-11 19:30 | 45088.8125 | 0 | 11.4126 | 39.95
2023-06-11 20:00 | 45088.8333 | 0 | 10.9683 | 39.95
2023-06-11 20:30 | 45088.8542 | 0 | 10.4596 | 39.95
2023-06-11 21:00 | 45088.875 | 0 | 10.1831 | 39.95
2023-06-11 21:30 | 45088.8958 | 0 | 9.6123 | 39.95
2023-06-11 22:00 | 45088.9167 | 0 | 8.9917 | 39.95
2023-06-11 22:30 | 45088.9375 | 0 | 8.5547 | 39.95
2023-06-11 23:00 | 45088.9583 | 0 | 8.2014 | 39.95
2023-06-11 23:30 | 45088.9792 | 0 | 8.0056 | 39.95
2023-06-12 | 45089 | 0 | 7.8446 | 39.95
2023-06-12 00:30 | 45089.0208 | 0 | 7.5089 | 39.95
2023-06-12 01:00 | 45089.0417 | 0 | 7.4286 | 39.95
2023-06-12 01:30 | 45089.0625 | 0 | 7.3564 | 39.95
2023-06-12 02:00 | 45089.0833 | 0 | 7.3355 | 39.95
2023-06-12 02:30 | 45089.1042 | 0 | 7.3816 | 39.95
2023-06-12 03:00 | 45089.125 | 0 | 7.3439 | 39.95
2023-06-12 03:30 | 45089.1458 | 0 | 7.7116 | 39.95
2023-06-12 04:00 | 45089.1667 | 0 | 7.8864 | 39.95
2023-06-12 04:30 | 45089.1875 | 0 | 8.2164 | 39.95
2023-06-12 05:00 | 45089.2083 | 0 | 8.887 | 39.95
2023-06-12 05:30 | 45089.2292 | 0 | 9.6636 | 39.95
2023-06-12 06:00 | 45089.25 | 0 | 10.8309 | 39.95
2023-06-12 06:30 | 45089.2708 | 0 | 11.9347 | 39.95
2023-06-12 07:00 | 45089.2917 | 0 | 12.5718 | 39.95
2023-06-12 07:30 | 45089.3125 | 0 | 12.5397 | 39.95
2023-06-12 08:00 | 45089.3333 | 0 | 12.3554 | 39.95
2023-06-12 08:30 | 45089.3542 | 0 | 13.0522 | 39.95
2023-06-12 09:00 | 45089.375 | 0 | 13.0912 | 39.95
2023-06-12 09:30 | 45089.3958 | 0 | 12.7391 | 39.95
2023-06-12 10:00 | 45089.4167 | 0 | 12.2613 | 39.95
2023-06-12 10:30 | 45089.4375 | 0 | 12.37 | 39.95
2023-06-12 11:00 | 45089.4583 | 0 | 11.2242 | 39.95
2023-06-12 11:30 | 45089.4792 | 0 | 10.9421 | 39.95
2023-06-12 12:00 | 45089.5 | 0 | 11.1012 | 39.95
2023-06-12 12:30 | 45089.5208 | 0 | 12.0223 | 39.95
2023-06-12 13:00 | 45089.5417 | 0 | 11.0682 | 39.95
2023-06-12 13:30 | 45089.5625 | 0 | 10.5097 | 39.95
2023-06-12 14:00 | 45089.5833 | 0 | 11.3793 | 39.95
2023-06-12 14:30 | 45089.6042 | 0 | 11.7701 | 39.95
2023-06-12 15:00 | 45089.625 | 0 | 11.9619 | 39.95
2023-06-12 15:30 | 45089.6458 | 0 | 12.3055 | 39.95
2023-06-12 16:00 | 45089.6667 | 0 | 12.7667 | 39.95
2023-06-12 16:30 | 45089.6875 | 0 | 13.0992 | 39.95
2023-06-12 17:00 | 45089.7083 | 0 | 13.8528 | 39.95
2023-06-12 17:30 | 45089.7292 | 0 | 14.5596 | 39.95
2023-06-12 18:00 | 45089.75 | 0 | 14.7469 | 39.95
2023-06-12 18:30 | 45089.7708 | 0 | 14.3282 | 39.95
2023-06-12 19:00 | 45089.7917 | 0 | 13.8555 | 39.95
2023-06-12 19:30 | 45089.8125 | 0 | 13.7419 | 39.95
2023-06-12 20:00 | 45089.8333 | 0 | 13.2445 | 39.95
2023-06-12 20:30 | 45089.8542 | 0 | 12.6862 | 39.95
2023-06-12 21:00 | 45089.875 | 0 | 12.2018 | 39.95
2023-06-12 21:30 | 45089.8958 | 0 | 11.5058 | 39.95
2023-06-12 22:00 | 45089.9167 | 0 | 10.6912 | 39.95
2023-06-12 22:30 | 45089.9375 | 0 | 10.0057 | 39.95
2023-06-12 23:00 | 45089.9583 | 0 | 9.6562 | 39.95
2023-06-12 23:30 | 45089.9792 | 0 | 9.2904 | 39.95
2023-06-13 | 45090 | 0 | 8.886 | 39.95
2023-06-13 00:30 | 45090.0208 | 0 | 8.4187 | 39.95
2023-06-13 01:00 | 45090.0417 | 0 | 8.2802 | 39.95
2023-06-13 01:30 | 45090.0625 | 0 | 8.1224 | 39.95
2023-06-13 02:00 | 45090.0833 | 0 | 8.1075 | 39.95
2023-06-13 02:30 | 45090.1042 | 0 | 8.0516 | 39.95
2023-06-13 03:00 | 45090.125 | 0 | 8.0674 | 39.95
2023-06-13 03:30 | 45090.1458 | 0 | 8.2633 | 39.95
2023-06-13 04:00 | 45090.1667 | 0 | 8.6333 | 39.95
2023-06-13 04:30 | 45090.1875 | 0 | 8.8789 | 39.95
2023-06-13 05:00 | 45090.2083 | 0 | 9.4857 | 39.95
2023-06-13 05:30 | 45090.2292 | 0 | 10.0879 | 39.95
2023-06-13 06:00 | 45090.25 | 0 | 11.1051 | 39.95
2023-06-13 06:30 | 45090.2708 | 0 | 12.3187 | 39.95
2023-06-13 07:00 | 45090.2917 | 0 | 12.6215 | 39.95
2023-06-13 07:30 | 45090.3125 | 0 | 11.876 | 39.95
2023-06-13 08:00 | 45090.3333 | 0 | 11.1003 | 39.95
2023-06-13 08:30 | 45090.3542 | 0 | 10.3571 | 39.95
2023-06-13 09:00 | 45090.375 | 0 | 9.765 | 39.95
2023-06-13 09:30 | 45090.3958 | 0 | 9.102 | 39.95
2023-06-13 10:00 | 45090.4167 | 0 | 8.8689 | 39.95
2023-06-13 10:30 | 45090.4375 | 0 | 8.3837 | 39.95
2023-06-13 11:00 | 45090.4583 | 0 | 8.4901 | 39.95
2023-06-13 11:30 | 45090.4792 | 0 | 8.5198 | 39.95
2023-06-13 12:00 | 45090.5 | 0 | 7.9732 | 39.95
2023-06-13 12:30 | 45090.5208 | 0 | 8.0661 | 39.95
2023-06-13 13:00 | 45090.5417 | 0 | 8.5825 | 39.95
2023-06-13 13:30 | 45090.5625 | 0 | 8.7859 | 39.95
2023-06-13 14:00 | 45090.5833 | 0 | 9.3914 | 39.95
2023-06-13 14:30 | 45090.6042 | 0 | 9.8228 | 39.95
2023-06-13 15:00 | 45090.625 | 0 | 10.5436 | 39.95
2023-06-13 15:30 | 45090.6458 | 0 | 11.4849 | 39.95
2023-06-13 16:00 | 45090.6667 | 0 | 12.0433 | 39.95
2023-06-13 16:30 | 45090.6875 | 0 | 12.514 | 39.95
2023-06-13 17:00 | 45090.7083 | 0 | 13.0851 | 39.95
2023-06-13 17:30 | 45090.7292 | 0 | 14.0014 | 39.95
2023-06-13 18:00 | 45090.75 | 0 | 14.1216 | 39.95
2023-06-13 18:30 | 45090.7708 | 0 | 13.7477 | 39.95
2023-06-13 19:00 | 45090.7917 | 0 | 13.4234 | 39.95
2023-06-13 19:30 | 45090.8125 | 0 | 13.1658 | 39.95
2023-06-13 20:00 | 45090.8333 | 0 | 12.7421 | 39.95
2023-06-13 20:30 | 45090.8542 | 0 | 12.3828 | 39.95
2023-06-13 21:00 | 45090.875 | 0 | 12.1266 | 39.95
2023-06-13 21:30 | 45090.8958 | 0 | 11.3035 | 39.95
2023-06-13 22:00 | 45090.9167 | 0 | 10.4306 | 39.95
2023-06-13 22:30 | 45090.9375 | 0 | 10.0088 | 39.95
2023-06-13 23:00 | 45090.9583 | 0 | 9.4873 | 39.95
2023-06-13 23:30 | 45090.9792 | 0 | 9.0909 | 39.95
2023-06-14 | 45091 | 0 | 8.8257 | 39.95
2023-06-14 00:30 | 45091.0208 | 0 | 8.5041 | 39.95
2023-06-14 01:00 | 45091.0417 | 0 | 8.2454 | 39.95
2023-06-14 01:30 | 45091.0625 | 0 | 8.1209 | 39.95
2023-06-14 02:00 | 45091.0833 | 0 | 8.095 | 39.95
2023-06-14 02:30 | 45091.1042 | 0 | 8.3537 | 39.95
2023-06-14 03:00 | 45091.125 | 0 | 8.1686 | 39.95
2023-06-14 03:30 | 45091.1458 | 0 | 8.3318 | 39.95
2023-06-14 04:00 | 45091.1667 | 0 | 8.5282 | 39.95
2023-06-14 04:30 | 45091.1875 | 0 | 8.795 | 39.95
2023-06-14 05:00 | 45091.2083 | 0 | 9.276 | 39.95
2023-06-14 05:30 | 45091.2292 | 0 | 10.1019 | 39.95
2023-06-14 06:00 | 45091.25 | 0 | 11.2773 | 39.95
2023-06-14 06:30 | 45091.2708 | 0 | 12.5664 | 39.95
2023-06-14 07:00 | 45091.2917 | 0 | 12.6121 | 39.95
2023-06-14 07:30 | 45091.3125 | 0 | 11.8101 | 39.95
2023-06-14 08:00 | 45091.3333 | 0 | 11.2304 | 39.95
2023-06-14 08:30 | 45091.3542 | 0 | 10.3482 | 39.95
2023-06-14 09:00 | 45091.375 | 0 | 9.4149 | 39.95
2023-06-14 09:30 | 45091.3958 | 0 | 8.8343 | 39.95
2023-06-14 10:00 | 45091.4167 | 0 | 8.3301 | 39.95
2023-06-14 10:30 | 45091.4375 | 0 | 8.38 | 39.95
2023-06-14 11:00 | 45091.4583 | 0 | 8.245 | 39.95
2023-06-14 11:30 | 45091.4792 | 0 | 8.2043 | 39.95
2023-06-14 12:00 | 45091.5 | 0 | 7.7687 | 39.95
2023-06-14 12:30 | 45091.5208 | 0 | 7.9496 | 39.95
2023-06-14 13:00 | 45091.5417 | 0 | 8.0712 | 39.95
2023-06-14 13:30 | 45091.5625 | 0 | 8.5535 | 39.95
2023-06-14 14:00 | 45091.5833 | 0 | 8.9774 | 39.95
2023-06-14 14:30 | 45091.6042 | 0 | 9.4777 | 39.95
2023-06-14 15:00 | 45091.625 | 0 | 10.2017 | 39.95
2023-06-14 15:30 | 45091.6458 | 0 | 11.052 | 39.95
2023-06-14 16:00 | 45091.6667 | 0 | 11.701 | 39.95
2023-06-14 16:30 | 45091.6875 | 0 | 12.324 | 39.95
2023-06-14 17:00 | 45091.7083 | 0 | 12.8007 | 39.95
2023-06-14 17:30 | 45091.7292 | 0 | 13.6657 | 39.95
2023-06-14 18:00 | 45091.75 | 0 | 13.9005 | 39.95
2023-06-14 18:30 | 45091.7708 | 0 | 13.8105 | 39.95
2023-06-14 19:00 | 45091.7917 | 0 | 13.4546 | 39.95
2023-06-14 19:30 | 45091.8125 | 0 | 13.1318 | 39.95
2023-06-14 20:00 | 45091.8333 | 0 | 12.9779 | 39.95
2023-06-14 20:30 | 45091.8542 | 0 | 12.498 | 39.95
2023-06-14 21:00 | 45091.875 | 0 | 12.1734 | 39.95
2023-06-14 21:30 | 45091.8958 | 0 | 11.4308 | 39.95
2023-06-14 22:00 | 45091.9167 | 0 | 10.7441 | 39.95
2023-06-14 22:30 | 45091.9375 | 0 | 10.1968 | 39.95
2023-06-14 23:00 | 45091.9583 | 0 | 9.6666 | 39.95
2023-06-14 23:30 | 45091.9792 | 0 | 9.2874 | 39.95
2023-06-15 | 45092 | 0 | 8.9877 | 39.95
2023-06-15 00:30 | 45092.0208 | 0 | 8.5101 | 39.95
2023-06-15 01:00 | 45092.0417 | 0 | 8.3082 | 39.95
2023-06-15 01:30 | 45092.0625 | 0 | 8.2807 | 39.95
2023-06-15 02:00 | 45092.0833 | 0 | 8.0443 | 39.95
2023-06-15 02:30 | 45092.1042 | 0 | 8.1001 | 39.95
2023-06-15 03:00 | 45092.125 | 0 | 8.1462 | 39.95
2023-06-15 03:30 | 45092.1458 | 0 | 8.2773 | 39.95
2023-06-15 04:00 | 45092.1667 | 0 | 8.5588 | 39.95
2023-06-15 04:30 | 45092.1875 | 0 | 8.9018 | 39.95
2023-06-15 05:00 | 45092.2083 | 0 | 9.5345 | 39.95
2023-06-15 05:30 | 45092.2292 | 0 | 10.3983 | 39.95
2023-06-15 06:00 | 45092.25 | 0 | 11.7407 | 39.95
2023-06-15 06:30 | 45092.2708 | 0 | 13.0749 | 39.95
2023-06-15 07:00 | 45092.2917 | 0 | 13.4669 | 39.95
2023-06-15 07:30 | 45092.3125 | 0 | 12.569 | 39.95
2023-06-15 08:00 | 45092.3333 | 0 | 11.4641 | 39.95
2023-06-15 08:30 | 45092.3542 | 0 | 10.5661 | 39.95
2023-06-15 09:00 | 45092.375 | 0 | 9.7856 | 39.95
2023-06-15 09:30 | 45092.3958 | 0 | 9.0683 | 39.95
2023-06-15 10:00 | 45092.4167 | 0 | 8.5113 | 39.95
2023-06-15 10:30 | 45092.4375 | 0 | 8.2218 | 39.95
2023-06-15 11:00 | 45092.4583 | 0 | 8.1134 | 39.95
2023-06-15 11:30 | 45092.4792 | 0 | 8.1408 | 39.95
2023-06-15 12:00 | 45092.5 | 0 | 7.5644 | 39.95
2023-06-15 12:30 | 45092.5208 | 0 | 7.6215 | 39.95
2023-06-15 13:00 | 45092.5417 | 0 | 8.0047 | 39.95
2023-06-15 13:30 | 45092.5625 | 0 | 8.2283 | 39.95
2023-06-15 14:00 | 45092.5833 | 0 | 8.6476 | 39.95
2023-06-15 14:30 | 45092.6042 | 0 | 9.3703 | 39.95
2023-06-15 15:00 | 45092.625 | 0 | 10.0343 | 39.95
2023-06-15 15:30 | 45092.6458 | 0 | 10.9997 | 39.95
2023-06-15 16:00 | 45092.6667 | 0 | 11.8543 | 39.95
2023-06-15 16:30 | 45092.6875 | 0 | 12.5354 | 39.95
2023-06-15 17:00 | 45092.7083 | 0 | 13.4521 | 39.95
2023-06-15 17:30 | 45092.7292 | 0 | 14.4819 | 39.95
2023-06-15 18:00 | 45092.75 | 0 | 14.6361 | 39.95
2023-06-15 18:30 | 45092.7708 | 0 | 14.4073 | 39.95
2023-06-15 19:00 | 45092.7917 | 0 | 14.1557 | 39.95
2023-06-15 19:30 | 45092.8125 | 0 | 13.9652 | 39.95
2023-06-15 20:00 | 45092.8333 | 0 | 13.6012 | 39.95
2023-06-15 20:30 | 45092.8542 | 0 | 13.2106 | 39.95
2023-06-15 21:00 | 45092.875 | 0 | 12.8483 | 39.95
2023-06-15 21:30 | 45092.8958 | 0 | 12.1267 | 39.95
2023-06-15 22:00 | 45092.9167 | 0 | 11.294 | 39.95
2023-06-15 22:30 | 45092.9375 | 0 | 10.6063 | 39.95
2023-06-15 23:00 | 45092.9583 | 0 | 9.9404 | 39.95
2023-06-15 23:30 | 45092.9792 | 0 | 9.5716 | 39.95
2023-06-16 | 45093 | 0 | 9.1985 | 39.95
2023-06-16 00:30 | 45093.0208 | 0 | 8.8146 | 39.95
2023-06-16 01:00 | 45093.0417 | 0 | 8.5956 | 39.95
2023-06-16 01:30 | 45093.0625 | 0 | 8.5229 | 39.95
2023-06-16 02:00 | 45093.0833 | 0 | 8.4111 | 39.95
2023-06-16 02:30 | 45093.1042 | 0 | 8.3257 | 39.95
2023-06-16 03:00 | 45093.125 | 0 | 8.3159 | 39.95
2023-06-16 03:30 | 45093.1458 | 0 | 8.465 | 39.95
2023-06-16 04:00 | 45093.1667 | 0 | 8.8442 | 39.95
2023-06-16 04:30 | 45093.1875 | 0 | 9.2638 | 39.95
2023-06-16 05:00 | 45093.2083 | 0 | 9.9552 | 39.95
2023-06-16 05:30 | 45093.2292 | 0 | 10.8985 | 39.95
2023-06-16 06:00 | 45093.25 | 0 | 12.1436 | 39.95
2023-06-16 06:30 | 45093.2708 | 0 | 13.7282 | 39.95
2023-06-16 07:00 | 45093.2917 | 0 | 14.2269 | 39.95
2023-06-16 07:30 | 45093.3125 | 0 | 13.6996 | 39.95
2023-06-16 08:00 | 45093.3333 | 0 | 13.0497 | 39.95
2023-06-16 08:30 | 45093.3542 | 0 | 11.8875 | 39.95
2023-06-16 09:00 | 45093.375 | 0 | 10.7878 | 39.95
2023-06-16 09:30 | 45093.3958 | 0 | 9.9833 | 39.95
2023-06-16 10:00 | 45093.4167 | 0 | 9.0616 | 39.95
2023-06-16 10:30 | 45093.4375 | 0 | 8.808 | 39.95
2023-06-16 11:00 | 45093.4583 | 0 | 8.7258 | 39.95
2023-06-16 11:30 | 45093.4792 | 0 | 8.5927 | 39.95
2023-06-16 12:00 | 45093.5 | 0 | 7.9868 | 39.95
2023-06-16 12:30 | 45093.5208 | 0 | 7.9364 | 39.95
2023-06-16 13:00 | 45093.5417 | 0 | 8.2918 | 39.95
2023-06-16 13:30 | 45093.5625 | 0 | 8.2841 | 39.95
2023-06-16 14:00 | 45093.5833 | 0 | 8.6311 | 39.95
2023-06-16 14:30 | 45093.6042 | 0 | 9.3177 | 39.95
2023-06-16 15:00 | 45093.625 | 0 | 10.1582 | 39.95
2023-06-16 15:30 | 45093.6458 | 0 | 10.8092 | 39.95
2023-06-16 16:00 | 45093.6667 | 0 | 11.7004 | 39.95
2023-06-16 16:30 | 45093.6875 | 0 | 12.5913 | 39.95
2023-06-16 17:00 | 45093.7083 | 0 | 13.3978 | 39.95
2023-06-16 17:30 | 45093.7292 | 0 | 14.0287 | 39.95
2023-06-16 18:00 | 45093.75 | 0 | 14.0552 | 39.95
2023-06-16 18:30 | 45093.7708 | 0 | 13.8491 | 39.95
2023-06-16 19:00 | 45093.7917 | 0 | 13.5551 | 39.95
2023-06-16 19:30 | 45093.8125 | 0 | 13.348 | 39.95
2023-06-16 20:00 | 45093.8333 | 0 | 13.0028 | 39.95
2023-06-16 20:30 | 45093.8542 | 0 | 12.7331 | 39.95
2023-06-16 21:00 | 45093.875 | 0 | 12.3973 | 39.95
2023-06-16 21:30 | 45093.8958 | 0 | 11.7159 | 39.95
2023-06-16 22:00 | 45093.9167 | 0 | 10.9682 | 39.95
2023-06-16 22:30 | 45093.9375 | 0 | 10.4827 | 39.95
2023-06-16 23:00 | 45093.9583 | 0 | 10.0792 | 39.95
2023-06-16 23:30 | 45093.9792 | 0 | 9.7266 | 39.95
2023-06-17 | 45094 | 0 | 9.3477 | 39.95
2023-06-17 00:30 | 45094.0208 | 0 | 8.8205 | 39.95
2023-06-17 01:00 | 45094.0417 | 0 | 8.5737 | 39.95
2023-06-17 01:30 | 45094.0625 | 0 | 8.3397 | 39.95
2023-06-17 02:00 | 45094.0833 | 0 | 8.2772 | 39.95
2023-06-17 02:30 | 45094.1042 | 0 | 8.1528 | 39.95
2023-06-17 03:00 | 45094.125 | 0 | 8.0703 | 39.95
2023-06-17 03:30 | 45094.1458 | 0 | 8.1046 | 39.95
2023-06-17 04:00 | 45094.1667 | 0 | 8.3436 | 39.95
2023-06-17 04:30 | 45094.1875 | 0 | 8.3697 | 39.95
2023-06-17 05:00 | 45094.2083 | 0 | 8.7433 | 39.95
2023-06-17 05:30 | 45094.2292 | 0 | 8.922 | 39.95
2023-06-17 06:00 | 45094.25 | 0 | 9.4386 | 39.95
2023-06-17 06:30 | 45094.2708 | 0 | 9.7773 | 39.95
2023-06-17 07:00 | 45094.2917 | 0 | 10.1219 | 39.95
2023-06-17 07:30 | 45094.3125 | 0 | 10.0257 | 39.95
2023-06-17 08:00 | 45094.3333 | 0 | 9.7376 | 39.95
2023-06-17 08:30 | 45094.3542 | 0 | 9.0831 | 39.95
2023-06-17 09:00 | 45094.375 | 0 | 8.2664 | 39.95
2023-06-17 09:30 | 45094.3958 | 0 | 7.614 | 39.95
2023-06-17 10:00 | 45094.4167 | 0 | 6.8036 | 39.95
2023-06-17 10:30 | 45094.4375 | 0 | 6.5428 | 39.95
2023-06-17 11:00 | 45094.4583 | 0 | 6.5485 | 39.95
2023-06-17 11:30 | 45094.4792 | 0 | 6.4392 | 39.95
2023-06-17 12:00 | 45094.5 | 0 | 6.0423 | 39.95
2023-06-17 12:30 | 45094.5208 | 0 | 5.9941 | 39.95
2023-06-17 13:00 | 45094.5417 | 0 | 6.1319 | 39.95
2023-06-17 13:30 | 45094.5625 | 0 | 6.2676 | 39.95
2023-06-17 14:00 | 45094.5833 | 0 | 6.7984 | 39.95
2023-06-17 14:30 | 45094.6042 | 0 | 8.6745 | 39.95
2023-06-17 15:00 | 45094.625 | 0 | 8.5678 | 39.95
2023-06-17 15:30 | 45094.6458 | 0 | 9.5478 | 39.95
2023-06-17 16:00 | 45094.6667 | 0 | 10.7008 | 39.95
2023-06-17 16:30 | 45094.6875 | 0 | 11.0561 | 39.95
2023-06-17 17:00 | 45094.7083 | 0 | 11.6232 | 39.95
2023-06-17 17:30 | 45094.7292 | 0 | 12.1208 | 39.95
2023-06-17 18:00 | 45094.75 | 0 | 12.221 | 39.95
2023-06-17 18:30 | 45094.7708 | 0 | 12.0074 | 39.95
2023-06-17 19:00 | 45094.7917 | 0 | 11.764 | 39.95
2023-06-17 19:30 | 45094.8125 | 0 | 11.4198 | 39.95
2023-06-17 20:00 | 45094.8333 | 0 | 11.269 | 39.95
2023-06-17 20:30 | 45094.8542 | 0 | 11.1097 | 39.95
2023-06-17 21:00 | 45094.875 | 0 | 10.9751 | 39.95
2023-06-17 21:30 | 45094.8958 | 0 | 10.3986 | 39.95
2023-06-17 22:00 | 45094.9167 | 0 | 9.7105 | 39.95
2023-06-17 22:30 | 45094.9375 | 0 | 9.236 | 39.95
2023-06-17 23:00 | 45094.9583 | 0 | 8.9236 | 39.95
2023-06-17 23:30 | 45094.9792 | 0 | 8.5399 | 39.95
2023-06-18 | 45095 | 0 | 8.1794 | 39.95
2023-06-18 00:30 | 45095.0208 | 0 | 7.8554 | 39.95
2023-06-18 01:00 | 45095.0417 | 0 | 7.6481 | 39.95
2023-06-18 01:30 | 45095.0625 | 0 | 7.5722 | 39.95
2023-06-18 02:00 | 45095.0833 | 0 | 7.3541 | 39.95
2023-06-18 02:30 | 45095.1042 | 0 | 7.4718 | 39.95
2023-06-18 03:00 | 45095.125 | 0 | 7.479 | 39.95
2023-06-18 03:30 | 45095.1458 | 0 | 7.343 | 39.95
2023-06-18 04:00 | 45095.1667 | 0 | 7.445 | 39.95
2023-06-18 04:30 | 45095.1875 | 0 | 7.3602 | 39.95
2023-06-18 05:00 | 45095.2083 | 0 | 7.6163 | 39.95
2023-06-18 05:30 | 45095.2292 | 0 | 7.8582 | 39.95
2023-06-18 06:00 | 45095.25 | 0 | 8.025 | 39.95
2023-06-18 06:30 | 45095.2708 | 0 | 8.2741 | 39.95
2023-06-18 07:00 | 45095.2917 | 0 | 8.3715 | 39.95
2023-06-18 07:30 | 45095.3125 | 0 | 8.2269 | 39.95
2023-06-18 08:00 | 45095.3333 | 0 | 9.4732 | 39.95
2023-06-18 08:30 | 45095.3542 | 0 | 9.1404 | 39.95
2023-06-18 09:00 | 45095.375 | 0 | 7.2452 | 39.95
2023-06-18 09:30 | 45095.3958 | 0 | 6.6184 | 39.95
2023-06-18 10:00 | 45095.4167 | 0 | 6.0832 | 39.95
2023-06-18 10:30 | 45095.4375 | 0 | 5.9726 | 39.95
2023-06-18 11:00 | 45095.4583 | 0 | 5.9029 | 39.95
2023-06-18 11:30 | 45095.4792 | 0 | 5.4969 | 39.95
2023-06-18 12:00 | 45095.5 | 0 | 5.2728 | 39.95
2023-06-18 12:30 | 45095.5208 | 0 | 5.7908 | 39.95
2023-06-18 13:00 | 45095.5417 | 0 | 5.6307 | 39.95
2023-06-18 13:30 | 45095.5625 | 0 | 5.6838 | 39.95
2023-06-18 14:00 | 45095.5833 | 0 | 6.1178 | 39.95
2023-06-18 14:30 | 45095.6042 | 0 | 6.9221 | 39.95
2023-06-18 15:00 | 45095.625 | 0 | 7.9052 | 39.95
2023-06-18 15:30 | 45095.6458 | 0 | 8.8378 | 39.95
2023-06-18 16:00 | 45095.6667 | 0 | 9.9328 | 39.95
2023-06-18 16:30 | 45095.6875 | 0 | 11.0162 | 39.95
2023-06-18 17:00 | 45095.7083 | 0 | 11.575 | 39.95
2023-06-18 17:30 | 45095.7292 | 0 | 12.4695 | 39.95
2023-06-18 18:00 | 45095.75 | 0 | 12.5934 | 39.95
2023-06-18 18:30 | 45095.7708 | 0 | 12.3968 | 39.95
2023-06-18 19:00 | 45095.7917 | 0 | 11.9447 | 39.95
2023-06-18 19:30 | 45095.8125 | 0 | 11.6337 | 39.95
2023-06-18 20:00 | 45095.8333 | 0 | 11.1868 | 39.95
2023-06-18 20:30 | 45095.8542 | 0 | 10.6846 | 39.95
2023-06-18 21:00 | 45095.875 | 0 | 10.313 | 39.95
2023-06-18 21:30 | 45095.8958 | 0 | 9.7249 | 39.95
2023-06-18 22:00 | 45095.9167 | 0 | 9.1563 | 39.95
2023-06-18 22:30 | 45095.9375 | 0 | 8.6432 | 39.95
2023-06-18 23:00 | 45095.9583 | 0 | 8.3753 | 39.95
2023-06-18 23:30 | 45095.9792 | 0 | 8.1045 | 39.95
2023-06-19 | 45096 | 0 | 7.7749 | 39.95
2023-06-19 00:30 | 45096.0208 | 0 | 7.5901 | 39.95
2023-06-19 01:00 | 45096.0417 | 0 | 7.4792 | 39.95
2023-06-19 01:30 | 45096.0625 | 0 | 7.3898 | 39.95
2023-06-19 02:00 | 45096.0833 | 0 | 7.4018 | 39.95
2023-06-19 02:30 | 45096.1042 | 0 | 7.5723 | 39.95
2023-06-19 03:00 | 45096.125 | 0 | 7.5328 | 39.95
2023-06-19 03:30 | 45096.1458 | 0 | 7.5836 | 39.95
2023-06-19 04:00 | 45096.1667 | 0 | 8.0563 | 39.95
2023-06-19 04:30 | 45096.1875 | 0 | 8.4012 | 39.95
2023-06-19 05:00 | 45096.2083 | 0 | 9.1264 | 39.95
2023-06-19 05:30 | 45096.2292 | 0 | 9.9897 | 39.95
2023-06-19 06:00 | 45096.25 | 0 | 11.0973 | 39.95
2023-06-19 06:30 | 45096.2708 | 0 | 12.5011 | 39.95
2023-06-19 07:00 | 45096.2917 | 0 | 12.7808 | 39.95
2023-06-19 07:30 | 45096.3125 | 0 | 12.4208 | 39.95
2023-06-19 08:00 | 45096.3333 | 0 | 11.6965 | 39.95
2023-06-19 08:30 | 45096.3542 | 0 | 10.4943 | 39.95
2023-06-19 09:00 | 45096.375 | 0 | 9.573 | 39.95
2023-06-19 09:30 | 45096.3958 | 0 | 8.89 | 39.95
2023-06-19 10:00 | 45096.4167 | 0 | 8.2264 | 39.95
2023-06-19 10:30 | 45096.4375 | 0 | 8.1648 | 39.95
2023-06-19 11:00 | 45096.4583 | 0 | 8.0609 | 39.95
2023-06-19 11:30 | 45096.4792 | 0 | 8.2071 | 39.95
2023-06-19 12:00 | 45096.5 | 0 | 7.6346 | 39.95
2023-06-19 12:30 | 45096.5208 | 0 | 7.6282 | 39.95
2023-06-19 13:00 | 45096.5417 | 0 | 8.0101 | 39.95
2023-06-19 13:30 | 45096.5625 | 0 | 8.0391 | 39.95
2023-06-19 14:00 | 45096.5833 | 0 | 8.6546 | 39.95
2023-06-19 14:30 | 45096.6042 | 0 | 8.9574 | 39.95
2023-06-19 15:00 | 45096.625 | 0 | 9.8388 | 39.95
2023-06-19 15:30 | 45096.6458 | 0 | 10.9493 | 39.95
2023-06-19 16:00 | 45096.6667 | 0 | 11.6262 | 39.95
2023-06-19 16:30 | 45096.6875 | 0 | 12.5034 | 39.95
2023-06-19 17:00 | 45096.7083 | 0 | 13.1338 | 39.95
2023-06-19 17:30 | 45096.7292 | 0 | 14.0701 | 39.95
2023-06-19 18:00 | 45096.75 | 0 | 14.3667 | 39.95
2023-06-19 18:30 | 45096.7708 | 0 | 14.2592 | 39.95
2023-06-19 19:00 | 45096.7917 | 0 | 14.1378 | 39.95
2023-06-19 19:30 | 45096.8125 | 0 | 13.5485 | 39.95
2023-06-19 20:00 | 45096.8333 | 0 | 13.0673 | 39.95
2023-06-19 20:30 | 45096.8542 | 0 | 12.6997 | 39.95
2023-06-19 21:00 | 45096.875 | 0 | 12.3891 | 39.95
2023-06-19 21:30 | 45096.8958 | 0 | 11.6453 | 39.95
2023-06-19 22:00 | 45096.9167 | 0 | 10.7522 | 39.95
2023-06-19 22:30 | 45096.9375 | 0 | 10.1243 | 39.95
2023-06-19 23:00 | 45096.9583 | 0 | 9.6474 | 39.95
2023-06-19 23:30 | 45096.9792 | 0 | 9.3445 | 39.95
2023-06-20 | 45097 | 0 | 8.8553 | 39.95
2023-06-20 00:30 | 45097.0208 | 0 | 8.685 | 39.95
2023-06-20 01:00 | 45097.0417 | 0 | 8.3814 | 39.95
2023-06-20 01:30 | 45097.0625 | 0 | 8.2087 | 39.95
2023-06-20 02:00 | 45097.0833 | 0 | 8.2161 | 39.95
2023-06-20 02:30 | 45097.1042 | 0 | 8.1307 | 39.95
2023-06-20 03:00 | 45097.125 | 0 | 8.3718 | 39.95
2023-06-20 03:30 | 45097.1458 | 0 | 8.4745 | 39.95
2023-06-20 04:00 | 45097.1667 | 0 | 8.809 | 39.95
2023-06-20 04:30 | 45097.1875 | 0 | 9.2427 | 39.95
2023-06-20 05:00 | 45097.2083 | 0 | 9.7424 | 39.95
2023-06-20 05:30 | 45097.2292 | 0 | 10.5922 | 39.95
2023-06-20 06:00 | 45097.25 | 0 | 11.9913 | 39.95
2023-06-20 06:30 | 45097.2708 | 0 | 13.3223 | 39.95
2023-06-20 07:00 | 45097.2917 | 0 | 13.6964 | 39.95
2023-06-20 07:30 | 45097.3125 | 0 | 13.13 | 39.95
2023-06-20 08:00 | 45097.3333 | 0 | 12.115 | 39.95
2023-06-20 08:30 | 45097.3542 | 0 | 11.0478 | 39.95
2023-06-20 09:00 | 45097.375 | 0 | 9.7846 | 39.95
2023-06-20 09:30 | 45097.3958 | 0 | 8.9009 | 39.95
2023-06-20 10:00 | 45097.4167 | 0 | 8.2619 | 39.95
2023-06-20 10:30 | 45097.4375 | 0 | 7.9765 | 39.95
2023-06-20 11:00 | 45097.4583 | 0 | 7.9669 | 39.95
2023-06-20 11:30 | 45097.4792 | 0 | 8.0805 | 39.95
2023-06-20 12:00 | 45097.5 | 0 | 7.5754 | 39.95
2023-06-20 12:30 | 45097.5208 | 0 | 7.5819 | 39.95
2023-06-20 13:00 | 45097.5417 | 0 | 8.062 | 39.95
2023-06-20 13:30 | 45097.5625 | 0 | 8.1598 | 39.95
2023-06-20 14:00 | 45097.5833 | 0 | 8.8783 | 39.95
2023-06-20 14:30 | 45097.6042 | 0 | 10.3802 | 39.95
2023-06-20 15:00 | 45097.625 | 0 | 11.4326 | 39.95
2023-06-20 15:30 | 45097.6458 | 0 | 12.1303 | 39.95
2023-06-20 16:00 | 45097.6667 | 0 | 12.3711 | 39.95
2023-06-20 16:30 | 45097.6875 | 0 | 12.9454 | 39.95
2023-06-20 17:00 | 45097.7083 | 0 | 13.9893 | 39.95
2023-06-20 17:30 | 45097.7292 | 0 | 14.9873 | 39.95
2023-06-20 18:00 | 45097.75 | 0 | 15.2315 | 39.95
2023-06-20 18:30 | 45097.7708 | 0 | 15.1429 | 39.95
2023-06-20 19:00 | 45097.7917 | 0 | 14.8231 | 39.95
2023-06-20 19:30 | 45097.8125 | 0 | 14.4645 | 39.95
2023-06-20 20:00 | 45097.8333 | 0 | 13.9531 | 39.95
2023-06-20 20:30 | 45097.8542 | 0 | 13.4272 | 39.95
2023-06-20 21:00 | 45097.875 | 0 | 12.9345 | 39.95
2023-06-20 21:30 | 45097.8958 | 0 | 12.064 | 39.95
2023-06-20 22:00 | 45097.9167 | 0 | 11.1598 | 39.95
2023-06-20 22:30 | 45097.9375 | 0 | 10.4999 | 39.95
2023-06-20 23:00 | 45097.9583 | 0 | 9.9864 | 39.95
2023-06-20 23:30 | 45097.9792 | 0 | 9.5813 | 39.95
2023-06-21 | 45098 | 0 | 9.2195 | 39.95
2023-06-21 00:30 | 45098.0208 | 0 | 8.8094 | 39.95
2023-06-21 01:00 | 45098.0417 | 0 | 8.6046 | 39.95
2023-06-21 01:30 | 45098.0625 | 0 | 8.3853 | 39.95
2023-06-21 02:00 | 45098.0833 | 0 | 8.3784 | 39.95
2023-06-21 02:30 | 45098.1042 | 0 | 8.3241 | 39.95
2023-06-21 03:00 | 45098.125 | 0 | 8.3614 | 39.95
2023-06-21 03:30 | 45098.1458 | 0 | 8.4657 | 39.95
2023-06-21 04:00 | 45098.1667 | 0 | 8.8259 | 39.95
2023-06-21 04:30 | 45098.1875 | 0 | 9.1715 | 39.95
2023-06-21 05:00 | 45098.2083 | 0 | 9.9618 | 39.95
2023-06-21 05:30 | 45098.2292 | 0 | 10.7772 | 39.95
2023-06-21 06:00 | 45098.25 | 0 | 12.1291 | 39.95
2023-06-21 06:30 | 45098.2708 | 0 | 13.7605 | 39.95
2023-06-21 07:00 | 45098.2917 | 0 | 14.2547 | 39.95
2023-06-21 07:30 | 45098.3125 | 0 | 13.5843 | 39.95
2023-06-21 08:00 | 45098.3333 | 0 | 12.7058 | 39.95
2023-06-21 08:30 | 45098.3542 | 0 | 11.5789 | 39.95
2023-06-21 09:00 | 45098.375 | 0 | 10.5629 | 39.95
2023-06-21 09:30 | 45098.3958 | 0 | 9.526 | 39.95
2023-06-21 10:00 | 45098.4167 | 0 | 8.8676 | 39.95
2023-06-21 10:30 | 45098.4375 | 0 | 8.6196 | 39.95
2023-06-21 11:00 | 45098.4583 | 0 | 8.4378 | 39.95
2023-06-21 11:30 | 45098.4792 | 0 | 8.3255 | 39.95
2023-06-21 12:00 | 45098.5 | 0 | 8.0017 | 39.95
2023-06-21 12:30 | 45098.5208 | 0 | 7.9767 | 39.95
2023-06-21 13:00 | 45098.5417 | 0 | 8.2727 | 39.95
2023-06-21 13:30 | 45098.5625 | 0 | 8.3437 | 39.95
2023-06-21 14:00 | 45098.5833 | 0 | 8.7655 | 39.95
2023-06-21 14:30 | 45098.6042 | 0 | 9.4749 | 39.95
2023-06-21 15:00 | 45098.625 | 0 | 10.1006 | 39.95
2023-06-21 15:30 | 45098.6458 | 0 | 11.104 | 39.95
2023-06-21 16:00 | 45098.6667 | 0 | 11.8609 | 39.95
2023-06-21 16:30 | 45098.6875 | 0 | 12.7671 | 39.95
2023-06-21 17:00 | 45098.7083 | 0 | 13.6812 | 39.95
2023-06-21 17:30 | 45098.7292 | 0 | 14.8902 | 39.95
2023-06-21 18:00 | 45098.75 | 0 | 15.2802 | 39.95
2023-06-21 18:30 | 45098.7708 | 0 | 15.2851 | 39.95
2023-06-21 19:00 | 45098.7917 | 0 | 15.1489 | 39.95
2023-06-21 19:30 | 45098.8125 | 0 | 14.9352 | 39.95
2023-06-21 20:00 | 45098.8333 | 0 | 14.4033 | 39.95
2023-06-21 20:30 | 45098.8542 | 0 | 13.8221 | 39.95
2023-06-21 21:00 | 45098.875 | 0 | 13.5452 | 39.95
2023-06-21 21:30 | 45098.8958 | 0 | 12.6158 | 39.95
2023-06-21 22:00 | 45098.9167 | 0 | 11.8133 | 39.95
2023-06-21 22:30 | 45098.9375 | 0 | 11.044 | 39.95
2023-06-21 23:00 | 45098.9583 | 0 | 10.4452 | 39.95
2023-06-21 23:30 | 45098.9792 | 0 | 10.054 | 39.95
2023-06-22 | 45099 | 0 | 9.6347 | 39.95
2023-06-22 00:30 | 45099.0208 | 0 | 9.0206 | 39.95
2023-06-22 01:00 | 45099.0417 | 0 | 8.8726 | 39.95
2023-06-22 01:30 | 45099.0625 | 0 | 8.6538 | 39.95
2023-06-22 02:00 | 45099.0833 | 0 | 8.5179 | 39.95
2023-06-22 02:30 | 45099.1042 | 0 | 8.5094 | 39.95
2023-06-22 03:00 | 45099.125 | 0 | 8.418 | 39.95
2023-06-22 03:30 | 45099.1458 | 0 | 8.5207 | 39.95
2023-06-22 04:00 | 45099.1667 | 0 | 8.8296 | 39.95
2023-06-22 04:30 | 45099.1875 | 0 | 9.3064 | 39.95
2023-06-22 05:00 | 45099.2083 | 0 | 10.1286 | 39.95
2023-06-22 05:30 | 45099.2292 | 0 | 10.9479 | 39.95
2023-06-22 06:00 | 45099.25 | 0 | 12.3282 | 39.95
2023-06-22 06:30 | 45099.2708 | 0 | 13.5809 | 39.95
2023-06-22 07:00 | 45099.2917 | 0 | 14.4512 | 39.95
2023-06-22 07:30 | 45099.3125 | 0 | 14.1651 | 39.95
2023-06-22 08:00 | 45099.3333 | 0 | 13.058 | 39.95
2023-06-22 08:30 | 45099.3542 | 0 | 12.4124 | 39.95
2023-06-22 09:00 | 45099.375 | 0 | 10.7326 | 39.95
2023-06-22 09:30 | 45099.3958 | 0 | 9.9646 | 39.95
2023-06-22 10:00 | 45099.4167 | 0 | 9.1989 | 39.95
2023-06-22 10:30 | 45099.4375 | 0 | 8.998 | 39.95
2023-06-22 11:00 | 45099.4583 | 0 | 8.8734 | 39.95
2023-06-22 11:30 | 45099.4792 | 0 | 9.4915 | 39.95
2023-06-22 12:00 | 45099.5 | 0 | 8.3986 | 39.95
2023-06-22 12:30 | 45099.5208 | 0 | 9.4219 | 39.95
2023-06-22 13:00 | 45099.5417 | 0 | 10.2484 | 39.95
2023-06-22 13:30 | 45099.5625 | 0 | 11.3857 | 39.95
2023-06-22 14:00 | 45099.5833 | 0 | 11.6455 | 39.95
2023-06-22 14:30 | 45099.6042 | 0 | 12.0975 | 39.95
2023-06-22 15:00 | 45099.625 | 0 | 11.8122 | 39.95
2023-06-22 15:30 | 45099.6458 | 0 | 11.9914 | 39.95
2023-06-22 16:00 | 45099.6667 | 0 | 13.0346 | 39.95
2023-06-22 16:30 | 45099.6875 | 0 | 13.5016 | 39.95
2023-06-22 17:00 | 45099.7083 | 0 | 14.1969 | 39.95
2023-06-22 17:30 | 45099.7292 | 0 | 14.7702 | 39.95
2023-06-22 18:00 | 45099.75 | 0 | 14.9964 | 39.95
2023-06-22 18:30 | 45099.7708 | 0 | 14.9339 | 39.95
2023-06-22 19:00 | 45099.7917 | 0 | 14.7735 | 39.95
2023-06-22 19:30 | 45099.8125 | 0 | 14.3389 | 39.95
2023-06-22 20:00 | 45099.8333 | 0 | 13.9306 | 39.95
2023-06-22 20:30 | 45099.8542 | 0 | 13.3098 | 39.95
2023-06-22 21:00 | 45099.875 | 0 | 12.8084 | 39.95
2023-06-22 21:30 | 45099.8958 | 0 | 12.0065 | 39.95
2023-06-22 22:00 | 45099.9167 | 0 | 10.9971 | 39.95
2023-06-22 22:30 | 45099.9375 | 0 | 10.3592 | 39.95
2023-06-22 23:00 | 45099.9583 | 0 | 9.9348 | 39.95
2023-06-22 23:30 | 45099.9792 | 0 | 9.5464 | 39.95
2023-06-23 | 45100 | 0 | 9.1858 | 39.95
2023-06-23 00:30 | 45100.0208 | 0 | 8.7795 | 39.95
2023-06-23 01:00 | 45100.0417 | 0 | 8.5436 | 39.95
2023-06-23 01:30 | 45100.0625 | 0 | 8.3658 | 39.95
2023-06-23 02:00 | 45100.0833 | 0 | 8.3405 | 39.95
2023-06-23 02:30 | 45100.1042 | 0 | 8.3426 | 39.95
2023-06-23 03:00 | 45100.125 | 0 | 8.217 | 39.95
2023-06-23 03:30 | 45100.1458 | 0 | 8.4016 | 39.95
2023-06-23 04:00 | 45100.1667 | 0 | 8.6653 | 39.95
2023-06-23 04:30 | 45100.1875 | 0 | 9.0538 | 39.95
2023-06-23 05:00 | 45100.2083 | 0 | 9.6905 | 39.95
2023-06-23 05:30 | 45100.2292 | 0 | 10.3419 | 39.95
2023-06-23 06:00 | 45100.25 | 0 | 11.4735 | 39.95
2023-06-23 06:30 | 45100.2708 | 0 | 12.6938 | 39.95
2023-06-23 07:00 | 45100.2917 | 0 | 12.9735 | 39.95
2023-06-23 07:30 | 45100.3125 | 0 | 12.3154 | 39.95
2023-06-23 08:00 | 45100.3333 | 0 | 12.1966 | 39.95
2023-06-23 08:30 | 45100.3542 | 0 | 11.1154 | 39.95
2023-06-23 09:00 | 45100.375 | 0 | 11.4323 | 39.95
2023-06-23 09:30 | 45100.3958 | 0 | 12.3379 | 39.95
2023-06-23 10:00 | 45100.4167 | 0 | 12.5683 | 39.95
2023-06-23 10:30 | 45100.4375 | 0 | 11.4289 | 39.95
2023-06-23 11:00 | 45100.4583 | 0 | 9.2558 | 39.95
2023-06-23 11:30 | 45100.4792 | 0 | 10.2476 | 39.95
2023-06-23 12:00 | 45100.5 | 0 | 8.5408 | 39.95
2023-06-23 12:30 | 45100.5208 | 0 | 10.7057 | 39.95
2023-06-23 13:00 | 45100.5417 | 0 | 8.5374 | 39.95
2023-06-23 13:30 | 45100.5625 | 0 | 8.9173 | 39.95
2023-06-23 14:00 | 45100.5833 | 0 | 10.3203 | 39.95
2023-06-23 14:30 | 45100.6042 | 0 | 9.6831 | 39.95
2023-06-23 15:00 | 45100.625 | 0 | 10.2529 | 39.95
2023-06-23 15:30 | 45100.6458 | 0 | 11.186 | 39.95
2023-06-23 16:00 | 45100.6667 | 0 | 11.6997 | 39.95
2023-06-23 16:30 | 45100.6875 | 0 | 12.3553 | 39.95
2023-06-23 17:00 | 45100.7083 | 0 | 12.7188 | 39.95
2023-06-23 17:30 | 45100.7292 | 0 | 13.3263 | 39.95
2023-06-23 18:00 | 45100.75 | 0 | 13.2886 | 39.95
2023-06-23 18:30 | 45100.7708 | 0 | 13.2171 | 39.95
2023-06-23 19:00 | 45100.7917 | 0 | 13.0145 | 39.95
2023-06-23 19:30 | 45100.8125 | 0 | 12.7141 | 39.95
2023-06-23 20:00 | 45100.8333 | 0 | 12.4077 | 39.95
2023-06-23 20:30 | 45100.8542 | 0 | 11.9664 | 39.95
2023-06-23 21:00 | 45100.875 | 0 | 11.8427 | 39.95
2023-06-23 21:30 | 45100.8958 | 0 | 11.2891 | 39.95
2023-06-23 22:00 | 45100.9167 | 0 | 10.5212 | 39.95
2023-06-23 22:30 | 45100.9375 | 0 | 9.9747 | 39.95
2023-06-23 23:00 | 45100.9583 | 0 | 9.58 | 39.95
2023-06-23 23:30 | 45100.9792 | 0 | 9.1913 | 39.95
2023-06-24 | 45101 | 0 | 8.9961 | 39.95
2023-06-24 00:30 | 45101.0208 | 0 | 8.5867 | 39.95
2023-06-24 01:00 | 45101.0417 | 0 | 8.3723 | 39.95
2023-06-24 01:30 | 45101.0625 | 0 | 8.132 | 39.95
2023-06-24 02:00 | 45101.0833 | 0 | 8.121 | 39.95
2023-06-24 02:30 | 45101.1042 | 0 | 8.1773 | 39.95
2023-06-24 03:00 | 45101.125 | 0 | 7.9334 | 39.95
2023-06-24 03:30 | 45101.1458 | 0 | 8.0457 | 39.95
2023-06-24 04:00 | 45101.1667 | 0 | 8.1054 | 39.95
2023-06-24 04:30 | 45101.1875 | 0 | 8.1947 | 39.95
2023-06-24 05:00 | 45101.2083 | 0 | 8.4113 | 39.95
2023-06-24 05:30 | 45101.2292 | 0 | 8.6578 | 39.95
2023-06-24 06:00 | 45101.25 | 0 | 8.8922 | 39.95
2023-06-24 06:30 | 45101.2708 | 0 | 9.2898 | 39.95
2023-06-24 07:00 | 45101.2917 | 0 | 9.6331 | 39.95
2023-06-24 07:30 | 45101.3125 | 0 | 9.4125 | 39.95
2023-06-24 08:00 | 45101.3333 | 0 | 9.2477 | 39.95
2023-06-24 08:30 | 45101.3542 | 0 | 8.5738 | 39.95
2023-06-24 09:00 | 45101.375 | 0 | 7.7486 | 39.95
2023-06-24 09:30 | 45101.3958 | 0 | 7.082 | 39.95
2023-06-24 10:00 | 45101.4167 | 0 | 6.3611 | 39.95
2023-06-24 10:30 | 45101.4375 | 0 | 6.2891 | 39.95
2023-06-24 11:00 | 45101.4583 | 0 | 6.3164 | 39.95
2023-06-24 11:30 | 45101.4792 | 0 | 6.2538 | 39.95
2023-06-24 12:00 | 45101.5 | 0 | 5.7883 | 39.95
2023-06-24 12:30 | 45101.5208 | 0 | 5.6526 | 39.95
2023-06-24 13:00 | 45101.5417 | 0 | 5.8543 | 39.95
2023-06-24 13:30 | 45101.5625 | 0 | 6.1925 | 39.95
2023-06-24 14:00 | 45101.5833 | 0 | 6.7133 | 39.95
2023-06-24 14:30 | 45101.6042 | 0 | 7.3402 | 39.95
2023-06-24 15:00 | 45101.625 | 0 | 8.049 | 39.95
2023-06-24 15:30 | 45101.6458 | 0 | 9.0465 | 39.95
2023-06-24 16:00 | 45101.6667 | 0 | 9.8037 | 39.95
2023-06-24 16:30 | 45101.6875 | 0 | 10.5026 | 39.95
2023-06-24 17:00 | 45101.7083 | 0 | 11.1146 | 39.95
2023-06-24 17:30 | 45101.7292 | 0 | 11.7928 | 39.95
2023-06-24 18:00 | 45101.75 | 0 | 11.6963 | 39.95
2023-06-24 18:30 | 45101.7708 | 0 | 11.5774 | 39.95
2023-06-24 19:00 | 45101.7917 | 0 | 11.4372 | 39.95
2023-06-24 19:30 | 45101.8125 | 0 | 11.1914 | 39.95
2023-06-24 20:00 | 45101.8333 | 0 | 10.8261 | 39.95
2023-06-24 20:30 | 45101.8542 | 0 | 10.6281 | 39.95
2023-06-24 21:00 | 45101.875 | 0 | 10.5473 | 39.95
2023-06-24 21:30 | 45101.8958 | 0 | 9.86 | 39.95
2023-06-24 22:00 | 45101.9167 | 0 | 9.3037 | 39.95
2023-06-24 22:30 | 45101.9375 | 0 | 8.9665 | 39.95
2023-06-24 23:00 | 45101.9583 | 0 | 8.6381 | 39.95
2023-06-24 23:30 | 45101.9792 | 0 | 8.4298 | 39.95
2023-06-25 | 45102 | 0 | 8.0099 | 39.95
2023-06-25 00:30 | 45102.0208 | 0 | 7.654 | 39.95
2023-06-25 01:00 | 45102.0417 | 0 | 7.4664 | 39.95
2023-06-25 01:30 | 45102.0625 | 0 | 7.1959 | 39.95
2023-06-25 02:00 | 45102.0833 | 0 | 7.1777 | 39.95
2023-06-25 02:30 | 45102.1042 | 0 | 7.197 | 39.95
2023-06-25 03:00 | 45102.125 | 0 | 7.2253 | 39.95
2023-06-25 03:30 | 45102.1458 | 0 | 7.1204 | 39.95
2023-06-25 04:00 | 45102.1667 | 0 | 7.2321 | 39.95
2023-06-25 04:30 | 45102.1875 | 0 | 7.2268 | 39.95
2023-06-25 05:00 | 45102.2083 | 0 | 7.3252 | 39.95
2023-06-25 05:30 | 45102.2292 | 0 | 7.7051 | 39.95
2023-06-25 06:00 | 45102.25 | 0 | 7.9194 | 39.95
2023-06-25 06:30 | 45102.2708 | 0 | 8.4303 | 39.95
2023-06-25 07:00 | 45102.2917 | 0 | 8.8279 | 39.95
2023-06-25 07:30 | 45102.3125 | 0 | 8.4624 | 39.95
2023-06-25 08:00 | 45102.3333 | 0 | 8.2973 | 39.95
2023-06-25 08:30 | 45102.3542 | 0 | 7.6792 | 39.95
2023-06-25 09:00 | 45102.375 | 0 | 7.0692 | 39.95
2023-06-25 09:30 | 45102.3958 | 0 | 6.3895 | 39.95
2023-06-25 10:00 | 45102.4167 | 0 | 5.9067 | 39.95
2023-06-25 10:30 | 45102.4375 | 0 | 5.7082 | 39.95
2023-06-25 11:00 | 45102.4583 | 0 | 5.6798 | 39.95
2023-06-25 11:30 | 45102.4792 | 0 | 5.6033 | 39.95
2023-06-25 12:00 | 45102.5 | 0 | 5.2503 | 39.95
2023-06-25 12:30 | 45102.5208 | 0 | 5.3109 | 39.95
2023-06-25 13:00 | 45102.5417 | 0 | 5.9384 | 39.95
2023-06-25 13:30 | 45102.5625 | 0 | 5.8482 | 39.95
2023-06-25 14:00 | 45102.5833 | 0 | 6.3935 | 39.95
2023-06-25 14:30 | 45102.6042 | 0 | 7.0979 | 39.95
2023-06-25 15:00 | 45102.625 | 0 | 7.8893 | 39.95
2023-06-25 15:30 | 45102.6458 | 0 | 8.7502 | 39.95
2023-06-25 16:00 | 45102.6667 | 0 | 9.7163 | 39.95
2023-06-25 16:30 | 45102.6875 | 0 | 10.4569 | 39.95
2023-06-25 17:00 | 45102.7083 | 0 | 11.0746 | 39.95
2023-06-25 17:30 | 45102.7292 | 0 | 11.8516 | 39.95
2023-06-25 18:00 | 45102.75 | 0 | 11.988 | 39.95
2023-06-25 18:30 | 45102.7708 | 0 | 11.7357 | 39.95
2023-06-25 19:00 | 45102.7917 | 0 | 11.4943 | 39.95
2023-06-25 19:30 | 45102.8125 | 0 | 11.1617 | 39.95
2023-06-25 20:00 | 45102.8333 | 0 | 10.7858 | 39.95
2023-06-25 20:30 | 45102.8542 | 0 | 10.4356 | 39.95
2023-06-25 21:00 | 45102.875 | 0 | 10.1202 | 39.95
2023-06-25 21:30 | 45102.8958 | 0 | 9.7485 | 39.95
2023-06-25 22:00 | 45102.9167 | 0 | 9.0318 | 39.95
2023-06-25 22:30 | 45102.9375 | 0 | 8.6538 | 39.95
2023-06-25 23:00 | 45102.9583 | 0 | 8.2289 | 39.95
2023-06-25 23:30 | 45102.9792 | 0 | 8.2029 | 39.95
2023-06-26 | 45103 | 0 | 7.9107 | 39.95
2023-06-26 00:30 | 45103.0208 | 0 | 7.7508 | 39.95
2023-06-26 01:00 | 45103.0417 | 0 | 7.4836 | 39.95
2023-06-26 01:30 | 45103.0625 | 0 | 7.5447 | 39.95
2023-06-26 02:00 | 45103.0833 | 0 | 7.4747 | 39.95
2023-06-26 02:30 | 45103.1042 | 0 | 7.3816 | 39.95
2023-06-26 03:00 | 45103.125 | 0 | 7.4652 | 39.95
2023-06-26 03:30 | 45103.1458 | 0 | 7.6691 | 39.95
2023-06-26 04:00 | 45103.1667 | 0 | 7.9624 | 39.95
2023-06-26 04:30 | 45103.1875 | 0 | 8.3325 | 39.95
2023-06-26 05:00 | 45103.2083 | 0 | 8.9497 | 39.95
2023-06-26 05:30 | 45103.2292 | 0 | 9.7902 | 39.95
2023-06-26 06:00 | 45103.25 | 0 | 10.6291 | 39.95
2023-06-26 06:30 | 45103.2708 | 0 | 11.5498 | 39.95
2023-06-26 07:00 | 45103.2917 | 0 | 11.8502 | 39.95
2023-06-26 07:30 | 45103.3125 | 0 | 11.3844 | 39.95
2023-06-26 08:00 | 45103.3333 | 0 | 10.9383 | 39.95
2023-06-26 08:30 | 45103.3542 | 0 | 10.2646 | 39.95
2023-06-26 09:00 | 45103.375 | 0 | 9.5512 | 39.95
2023-06-26 09:30 | 45103.3958 | 0 | 8.884 | 39.95
2023-06-26 10:00 | 45103.4167 | 0 | 8.2826 | 39.95
2023-06-26 10:30 | 45103.4375 | 0 | 8.0317 | 39.95
2023-06-26 11:00 | 45103.4583 | 0 | 7.9488 | 39.95
2023-06-26 11:30 | 45103.4792 | 0 | 7.9244 | 39.95
2023-06-26 12:00 | 45103.5 | 0 | 7.528 | 39.95
2023-06-26 12:30 | 45103.5208 | 0 | 7.7056 | 39.95
2023-06-26 13:00 | 45103.5417 | 0 | 8.0615 | 39.95
2023-06-26 13:30 | 45103.5625 | 0 | 8.2313 | 39.95
2023-06-26 14:00 | 45103.5833 | 0 | 8.6737 | 39.95
2023-06-26 14:30 | 45103.6042 | 0 | 9.4257 | 39.95
2023-06-26 15:00 | 45103.625 | 0 | 10.0095 | 39.95
2023-06-26 15:30 | 45103.6458 | 0 | 10.6872 | 39.95
2023-06-26 16:00 | 45103.6667 | 0 | 11.4299 | 39.95
2023-06-26 16:30 | 45103.6875 | 0 | 12.0402 | 39.95
2023-06-26 17:00 | 45103.7083 | 0 | 12.7978 | 39.95
2023-06-26 17:30 | 45103.7292 | 0 | 13.5311 | 39.95
2023-06-26 18:00 | 45103.75 | 0 | 13.8358 | 39.95
2023-06-26 18:30 | 45103.7708 | 0 | 13.6719 | 39.95
2023-06-26 19:00 | 45103.7917 | 0 | 13.2002 | 39.95
2023-06-26 19:30 | 45103.8125 | 0 | 13.0175 | 39.95
2023-06-26 20:00 | 45103.8333 | 0 | 12.5269 | 39.95
2023-06-26 20:30 | 45103.8542 | 0 | 11.9454 | 39.95
2023-06-26 21:00 | 45103.875 | 0 | 11.664 | 39.95
2023-06-26 21:30 | 45103.8958 | 0 | 11.1074 | 39.95
2023-06-26 22:00 | 45103.9167 | 0 | 10.2246 | 39.95
2023-06-26 22:30 | 45103.9375 | 0 | 9.8377 | 39.95
2023-06-26 23:00 | 45103.9583 | 0 | 9.2894 | 39.95
2023-06-26 23:30 | 45103.9792 | 0 | 8.9972 | 39.95
2023-06-27 | 45104 | 0 | 8.908 | 39.95
2023-06-27 00:30 | 45104.0208 | 0 | 8.4256 | 39.95
2023-06-27 01:00 | 45104.0417 | 0 | 8.0651 | 39.95
2023-06-27 01:30 | 45104.0625 | 0 | 8.0211 | 39.95
2023-06-27 02:00 | 45104.0833 | 0 | 7.972 | 39.95
2023-06-27 02:30 | 45104.1042 | 0 | 7.8887 | 39.95
2023-06-27 03:00 | 45104.125 | 0 | 8.053 | 39.95
2023-06-27 03:30 | 45104.1458 | 0 | 8.0467 | 39.95
2023-06-27 04:00 | 45104.1667 | 0 | 8.403 | 39.95
2023-06-27 04:30 | 45104.1875 | 0 | 8.832 | 39.95
2023-06-27 05:00 | 45104.2083 | 0 | 9.3529 | 39.95
2023-06-27 05:30 | 45104.2292 | 0 | 10.0064 | 39.95
2023-06-27 06:00 | 45104.25 | 0 | 11.1203 | 39.95
2023-06-27 06:30 | 45104.2708 | 0 | 12.3235 | 39.95
2023-06-27 07:00 | 45104.2917 | 0 | 12.5869 | 39.95
2023-06-27 07:30 | 45104.3125 | 0 | 12.0392 | 39.95
2023-06-27 08:00 | 45104.3333 | 0 | 11.4349 | 39.95
2023-06-27 08:30 | 45104.3542 | 0 | 10.4581 | 39.95
2023-06-27 09:00 | 45104.375 | 0 | 9.4894 | 39.95
2023-06-27 09:30 | 45104.3958 | 0 | 8.8516 | 39.95
2023-06-27 10:00 | 45104.4167 | 0 | 8.5683 | 39.95
2023-06-27 10:30 | 45104.4375 | 0 | 8.171 | 39.95
2023-06-27 11:00 | 45104.4583 | 0 | 7.9926 | 39.95
2023-06-27 11:30 | 45104.4792 | 0 | 7.4383 | 39.95
2023-06-27 12:00 | 45104.5 | 0 | 7.4033 | 39.95
2023-06-27 12:30 | 45104.5208 | 0 | 7.6885 | 39.95
2023-06-27 13:00 | 45104.5417 | 0 | 7.9989 | 39.95
2023-06-27 13:30 | 45104.5625 | 0 | 8.218 | 39.95
2023-06-27 14:00 | 45104.5833 | 0 | 8.7795 | 39.95
2023-06-27 14:30 | 45104.6042 | 0 | 9.251 | 39.95
2023-06-27 15:00 | 45104.625 | 0 | 10.1525 | 39.95
2023-06-27 15:30 | 45104.6458 | 0 | 10.8987 | 39.95
2023-06-27 16:00 | 45104.6667 | 0 | 11.5166 | 39.95
2023-06-27 16:30 | 45104.6875 | 0 | 12.3303 | 39.95
2023-06-27 17:00 | 45104.7083 | 0 | 13.0572 | 39.95
2023-06-27 17:30 | 45104.7292 | 0 | 13.8747 | 39.95
2023-06-27 18:00 | 45104.75 | 0 | 14.0427 | 39.95
2023-06-27 18:30 | 45104.7708 | 0 | 13.8767 | 39.95
2023-06-27 19:00 | 45104.7917 | 0 | 13.6852 | 39.95
2023-06-27 19:30 | 45104.8125 | 0 | 13.3183 | 39.95
2023-06-27 20:00 | 45104.8333 | 0 | 12.9912 | 39.95
2023-06-27 20:30 | 45104.8542 | 0 | 12.4423 | 39.95
2023-06-27 21:00 | 45104.875 | 0 | 12.0848 | 39.95
2023-06-27 21:30 | 45104.8958 | 0 | 11.4265 | 39.95
2023-06-27 22:00 | 45104.9167 | 0 | 10.5351 | 39.95
2023-06-27 22:30 | 45104.9375 | 0 | 10.0874 | 39.95
2023-06-27 23:00 | 45104.9583 | 0 | 9.657 | 39.95
2023-06-27 23:30 | 45104.9792 | 0 | 9.3454 | 39.95
2023-06-28 | 45105 | 0 | 8.9877 | 39.95
2023-06-28 00:30 | 45105.0208 | 0 | 8.4673 | 39.95
2023-06-28 01:00 | 45105.0417 | 0 | 8.3643 | 39.95
2023-06-28 01:30 | 45105.0625 | 0 | 8.1915 | 39.95
2023-06-28 02:00 | 45105.0833 | 0 | 8.1195 | 39.95
2023-06-28 02:30 | 45105.1042 | 0 | 8.1261 | 39.95
2023-06-28 03:00 | 45105.125 | 0 | 8.1596 | 39.95
2023-06-28 03:30 | 45105.1458 | 0 | 8.3258 | 39.95
2023-06-28 04:00 | 45105.1667 | 0 | 8.5245 | 39.95
2023-06-28 04:30 | 45105.1875 | 0 | 8.9753 | 39.95
2023-06-28 05:00 | 45105.2083 | 0 | 9.518 | 39.95
2023-06-28 05:30 | 45105.2292 | 0 | 10.1452 | 39.95
2023-06-28 06:00 | 45105.25 | 0 | 11.1684 | 39.95
2023-06-28 06:30 | 45105.2708 | 0 | 12.2524 | 39.95
2023-06-28 07:00 | 45105.2917 | 0 | 12.7933 | 39.95
2023-06-28 07:30 | 45105.3125 | 0 | 12.57 | 39.95
2023-06-28 08:00 | 45105.3333 | 0 | 12.5539 | 39.95
2023-06-28 08:30 | 45105.3542 | 0 | 11.4741 | 39.95
2023-06-28 09:00 | 45105.375 | 0 | 10.1071 | 39.95
2023-06-28 09:30 | 45105.3958 | 0 | 9.7416 | 39.95
2023-06-28 10:00 | 45105.4167 | 0 | 8.7187 | 39.95
2023-06-28 10:30 | 45105.4375 | 0 | 8.7967 | 39.95
2023-06-28 11:00 | 45105.4583 | 0 | 8.6817 | 39.95
2023-06-28 11:30 | 45105.4792 | 0 | 8.6018 | 39.95
2023-06-28 12:00 | 45105.5 | 0 | 7.9718 | 39.95
2023-06-28 12:30 | 45105.5208 | 0 | 7.9806 | 39.95
2023-06-28 13:00 | 45105.5417 | 0 | 8.7544 | 39.95
2023-06-28 13:30 | 45105.5625 | 0 | 8.8921 | 39.95
2023-06-28 14:00 | 45105.5833 | 0 | 9.6802 | 39.95
2023-06-28 14:30 | 45105.6042 | 0 | 10.7161 | 39.95
2023-06-28 15:00 | 45105.625 | 0 | 10.8418 | 39.95
2023-06-28 15:30 | 45105.6458 | 0 | 11.7977 | 39.95
2023-06-28 16:00 | 45105.6667 | 0 | 11.9197 | 39.95
2023-06-28 16:30 | 45105.6875 | 0 | 12.3144 | 39.95
2023-06-28 17:00 | 45105.7083 | 0 | 12.9649 | 39.95
2023-06-28 17:30 | 45105.7292 | 0 | 13.944 | 39.95
2023-06-28 18:00 | 45105.75 | 0 | 13.8527 | 39.95
2023-06-28 18:30 | 45105.7708 | 0 | 13.657 | 39.95
2023-06-28 19:00 | 45105.7917 | 0 | 13.2672 | 39.95
2023-06-28 19:30 | 45105.8125 | 0 | 13.2207 | 39.95
2023-06-28 20:00 | 45105.8333 | 0 | 12.7435 | 39.95
2023-06-28 20:30 | 45105.8542 | 0 | 12.3069 | 39.95
2023-06-28 21:00 | 45105.875 | 0 | 11.9864 | 39.95
2023-06-28 21:30 | 45105.8958 | 0 | 11.1896 | 39.95
2023-06-28 22:00 | 45105.9167 | 0 | 10.4932 | 39.95
2023-06-28 22:30 | 45105.9375 | 0 | 10.0652 | 39.95
2023-06-28 23:00 | 45105.9583 | 0 | 9.685 | 39.95
2023-06-28 23:30 | 45105.9792 | 0 | 9.3067 | 39.95
2023-06-29 | 45106 | 0 | 8.9839 | 39.95
2023-06-29 00:30 | 45106.0208 | 0 | 8.6537 | 39.95
2023-06-29 01:00 | 45106.0417 | 0 | 8.403 | 39.95
2023-06-29 01:30 | 45106.0625 | 0 | 8.3016 | 39.95
2023-06-29 02:00 | 45106.0833 | 0 | 8.3062 | 39.95
2023-06-29 02:30 | 45106.1042 | 0 | 8.2243 | 39.95
2023-06-29 03:00 | 45106.125 | 0 | 8.24 | 39.95
2023-06-29 03:30 | 45106.1458 | 0 | 8.2997 | 39.95
2023-06-29 04:00 | 45106.1667 | 0 | 8.596 | 39.95
2023-06-29 04:30 | 45106.1875 | 0 | 8.8825 | 39.95
2023-06-29 05:00 | 45106.2083 | 0 | 9.4327 | 39.95
2023-06-29 05:30 | 45106.2292 | 0 | 9.8912 | 39.95
2023-06-29 06:00 | 45106.25 | 0 | 10.7332 | 39.95
2023-06-29 06:30 | 45106.2708 | 0 | 11.6395 | 39.95
2023-06-29 07:00 | 45106.2917 | 0 | 12.0689 | 39.95
2023-06-29 07:30 | 45106.3125 | 0 | 12.141 | 39.95
2023-06-29 08:00 | 45106.3333 | 0 | 12.546 | 39.95
2023-06-29 08:30 | 45106.3542 | 0 | 12.1945 | 39.95
2023-06-29 09:00 | 45106.375 | 0 | 11.5688 | 39.95
2023-06-29 09:30 | 45106.3958 | 0 | 11.4839 | 39.95
2023-06-29 10:00 | 45106.4167 | 0 | 9.5874 | 39.95
2023-06-29 10:30 | 45106.4375 | 0 | 9.3043 | 39.95
2023-06-29 11:00 | 45106.4583 | 0 | 9.2325 | 39.95
2023-06-29 11:30 | 45106.4792 | 0 | 8.334 | 39.95
2023-06-29 12:00 | 45106.5 | 0 | 9.1796 | 39.95
2023-06-29 12:30 | 45106.5208 | 0 | 9.0094 | 39.95
2023-06-29 13:00 | 45106.5417 | 0 | 8.9146 | 39.95
2023-06-29 13:30 | 45106.5625 | 0 | 7.7134 | 39.95
2023-06-29 14:00 | 45106.5833 | 0 | 9.8432 | 39.95
2023-06-29 14:30 | 45106.6042 | 0 | 9.2853 | 39.95
2023-06-29 15:00 | 45106.625 | 0 | 10.4674 | 39.95
2023-06-29 15:30 | 45106.6458 | 0 | 11.5262 | 39.95
2023-06-29 16:00 | 45106.6667 | 0 | 12.1709 | 39.95
2023-06-29 16:30 | 45106.6875 | 0 | 12.4552 | 39.95
2023-06-29 17:00 | 45106.7083 | 0 | 13.1279 | 39.95
2023-06-29 17:30 | 45106.7292 | 0 | 13.8977 | 39.95
2023-06-29 18:00 | 45106.75 | 0 | 13.9079 | 39.95
2023-06-29 18:30 | 45106.7708 | 0 | 13.8081 | 39.95
2023-06-29 19:00 | 45106.7917 | 0 | 13.5767 | 39.95
2023-06-29 19:30 | 45106.8125 | 0 | 13.5225 | 39.95
2023-06-29 20:00 | 45106.8333 | 0 | 12.9796 | 39.95
2023-06-29 20:30 | 45106.8542 | 0 | 12.6471 | 39.95
2023-06-29 21:00 | 45106.875 | 0 | 12.476 | 39.95
2023-06-29 21:30 | 45106.8958 | 0 | 11.584 | 39.95
2023-06-29 22:00 | 45106.9167 | 0 | 10.8961 | 39.95
2023-06-29 22:30 | 45106.9375 | 0 | 10.3676 | 39.95
2023-06-29 23:00 | 45106.9583 | 0 | 10.0383 | 39.95
2023-06-29 23:30 | 45106.9792 | 0 | 9.6359 | 39.95
2023-06-30 | 45107 | 0 | 9.3081 | 39.95
2023-06-30 00:30 | 45107.0208 | 0 | 8.8801 | 39.95
2023-06-30 01:00 | 45107.0417 | 0 | 8.6155 | 39.95
2023-06-30 01:30 | 45107.0625 | 0 | 8.29 | 39.95
2023-06-30 02:00 | 45107.0833 | 0 | 8.3539 | 39.95
2023-06-30 02:30 | 45107.1042 | 0 | 8.3009 | 39.95
2023-06-30 03:00 | 45107.125 | 0 | 8.217 | 39.95
2023-06-30 03:30 | 45107.1458 | 0 | 8.494 | 39.95
2023-06-30 04:00 | 45107.1667 | 0 | 8.7387 | 39.95
2023-06-30 04:30 | 45107.1875 | 0 | 9.0636 | 39.95
2023-06-30 05:00 | 45107.2083 | 0 | 9.8118 | 39.95
2023-06-30 05:30 | 45107.2292 | 0 | 10.5523 | 39.95
2023-06-30 06:00 | 45107.25 | 0 | 11.5769 | 39.95
2023-06-30 06:30 | 45107.2708 | 0 | 12.9958 | 39.95
2023-06-30 07:00 | 45107.2917 | 0 | 13.2617 | 39.95
2023-06-30 07:30 | 45107.3125 | 0 | 12.7287 | 39.95
2023-06-30 08:00 | 45107.3333 | 0 | 12.2908 | 39.95
2023-06-30 08:30 | 45107.3542 | 0 | 11.4318 | 39.95
2023-06-30 09:00 | 45107.375 | 0 | 10.3857 | 39.95
2023-06-30 09:30 | 45107.3958 | 0 | 9.3499 | 39.95
2023-06-30 10:00 | 45107.4167 | 0 | 8.6634 | 39.95
2023-06-30 10:30 | 45107.4375 | 0 | 8.4815 | 39.95
2023-06-30 11:00 | 45107.4583 | 0 | 8.0232 | 39.95
2023-06-30 11:30 | 45107.4792 | 0 | 7.8595 | 39.95
2023-06-30 12:00 | 45107.5 | 0 | 7.4818 | 39.95
2023-06-30 12:30 | 45107.5208 | 0 | 7.34 | 39.95
2023-06-30 13:00 | 45107.5417 | 0 | 7.5896 | 39.95
2023-06-30 13:30 | 45107.5625 | 0 | 7.6363 | 39.95
2023-06-30 14:00 | 45107.5833 | 0 | 8.0826 | 39.95
2023-06-30 14:30 | 45107.6042 | 0 | 8.946 | 39.95
2023-06-30 15:00 | 45107.625 | 0 | 9.6875 | 39.95
2023-06-30 15:30 | 45107.6458 | 0 | 10.5915 | 39.95
2023-06-30 16:00 | 45107.6667 | 0 | 11.3978 | 39.95
2023-06-30 16:30 | 45107.6875 | 0 | 12.2254 | 39.95
2023-06-30 17:00 | 45107.7083 | 0 | 12.9274 | 39.95
2023-06-30 17:30 | 45107.7292 | 0 | 13.8519 | 39.95
2023-06-30 18:00 | 45107.75 | 0 | 14.1097 | 39.95
2023-06-30 18:30 | 45107.7708 | 0 | 13.9288 | 39.95
2023-06-30 19:00 | 45107.7917 | 0 | 13.7046 | 39.95
2023-06-30 19:30 | 45107.8125 | 0 | 13.3221 | 39.95
2023-06-30 20:00 | 45107.8333 | 0 | 13.1285 | 39.95
2023-06-30 20:30 | 45107.8542 | 0 | 12.8576 | 39.95
2023-06-30 21:00 | 45107.875 | 0 | 12.8357 | 39.95
2023-06-30 21:30 | 45107.8958 | 0 | 12.2552 | 39.95
2023-06-30 22:00 | 45107.9167 | 0 | 11.5688 | 39.95
2023-06-30 22:30 | 45107.9375 | 0 | 10.9765 | 39.95
2023-06-30 23:00 | 45107.9583 | 0 | 10.4777 | 39.95
2023-06-30 23:30 | 45107.9792 | 0 | 9.984 | 39.95

## Historic Data 677
33 kV feeder 677
Date | Time | Historic use of existing emergency response (MW) | Historic load trace (MVA) | Historic asset rating (MVA)
2020-07-01 | 44013 | 0 | 8.6487 | 39.95
2020-07-01 00:30 | 44013.0208 | 0 | 8.2735 | 39.95
2020-07-01 01:00 | 44013.0417 | 0 | 7.9868 | 39.95
2020-07-01 01:30 | 44013.0625 | 0 | 7.84 | 39.95
2020-07-01 02:00 | 44013.0833 | 0 | 7.7876 | 39.95
2020-07-01 02:30 | 44013.1042 | 0 | 7.7792 | 39.95
2020-07-01 03:00 | 44013.125 | 0 | 7.7857 | 39.95
2020-07-01 03:30 | 44013.1458 | 0 | 7.8477 | 39.95
2020-07-01 04:00 | 44013.1667 | 0 | 8.1431 | 39.95
2020-07-01 04:30 | 44013.1875 | 0 | 8.4183 | 39.95
2020-07-01 05:00 | 44013.2083 | 0 | 9.245 | 39.95
2020-07-01 05:30 | 44013.2292 | 0 | 10.0724 | 39.95
2020-07-01 06:00 | 44013.25 | 0 | 11.3166 | 39.95
2020-07-01 06:30 | 44013.2708 | 0 | 12.2954 | 39.95
2020-07-01 07:00 | 44013.2917 | 0 | 13.2302 | 39.95
2020-07-01 07:30 | 44013.3125 | 0 | 13.6187 | 39.95
2020-07-01 08:00 | 44013.3333 | 0 | 13.2772 | 39.95
2020-07-01 08:30 | 44013.3542 | 0 | 12.2892 | 39.95
2020-07-01 09:00 | 44013.375 | 0 | 11.4489 | 39.95
2020-07-01 09:30 | 44013.3958 | 0 | 10.825 | 39.95
2020-07-01 10:00 | 44013.4167 | 0 | 10.4057 | 39.95
2020-07-01 10:30 | 44013.4375 | 0 | 10.0316 | 39.95
2020-07-01 11:00 | 44013.4583 | 0 | 9.6736 | 39.95
2020-07-01 11:30 | 44013.4792 | 0 | 9.6254 | 39.95
2020-07-01 12:00 | 44013.5 | 0 | 9.5166 | 39.95
2020-07-01 12:30 | 44013.5208 | 0 | 9.6463 | 39.95
2020-07-01 13:00 | 44013.5417 | 0 | 10.0423 | 39.95
2020-07-01 13:30 | 44013.5625 | 0 | 10.4142 | 39.95
2020-07-01 14:00 | 44013.5833 | 0 | 10.957 | 39.95
2020-07-01 14:30 | 44013.6042 | 0 | 11.1414 | 39.95
2020-07-01 15:00 | 44013.625 | 0 | 11.2431 | 39.95
2020-07-01 15:30 | 44013.6458 | 0 | 11.2915 | 39.95
2020-07-01 16:00 | 44013.6667 | 0 | 11.7039 | 39.95
2020-07-01 16:30 | 44013.6875 | 0 | 12.5076 | 39.95
2020-07-01 17:00 | 44013.7083 | 0 | 13.454 | 39.95
2020-07-01 17:30 | 44013.7292 | 0 | 14.3192 | 39.95
2020-07-01 18:00 | 44013.75 | 0 | 14.3859 | 39.95
2020-07-01 18:30 | 44013.7708 | 0 | 14.6465 | 39.95
2020-07-01 19:00 | 44013.7917 | 0 | 14.4435 | 39.95
2020-07-01 19:30 | 44013.8125 | 0 | 14.1581 | 39.95
2020-07-01 20:00 | 44013.8333 | 0 | 14.0019 | 39.95
2020-07-01 20:30 | 44013.8542 | 0 | 13.6201 | 39.95
2020-07-01 21:00 | 44013.875 | 0 | 12.7396 | 39.95
2020-07-01 21:30 | 44013.8958 | 0 | 12.2226 | 39.95
2020-07-01 22:00 | 44013.9167 | 0 | 11.4772 | 39.95
2020-07-01 22:30 | 44013.9375 | 0 | 10.6929 | 39.95
2020-07-01 23:00 | 44013.9583 | 0 | 9.8544 | 39.95
2020-07-01 23:30 | 44013.9792 | 0 | 9.3011 | 39.95
2020-07-02 | 44014 | 0 | 8.6437 | 39.95
2020-07-02 00:30 | 44014.0208 | 0 | 8.1956 | 39.95
2020-07-02 01:00 | 44014.0417 | 0 | 7.9253 | 39.95
2020-07-02 01:30 | 44014.0625 | 0 | 7.8039 | 39.95
2020-07-02 02:00 | 44014.0833 | 0 | 7.7955 | 39.95
2020-07-02 02:30 | 44014.1042 | 0 | 7.7294 | 39.95
2020-07-02 03:00 | 44014.125 | 0 | 7.8139 | 39.95
2020-07-02 03:30 | 44014.1458 | 0 | 7.7048 | 39.95
2020-07-02 04:00 | 44014.1667 | 0 | 8.0402 | 39.95
2020-07-02 04:30 | 44014.1875 | 0 | 8.4532 | 39.95
2020-07-02 05:00 | 44014.2083 | 0 | 9.2264 | 39.95
2020-07-02 05:30 | 44014.2292 | 0 | 10.0156 | 39.95
2020-07-02 06:00 | 44014.25 | 0 | 11.1219 | 39.95
2020-07-02 06:30 | 44014.2708 | 0 | 12.1462 | 39.95
2020-07-02 07:00 | 44014.2917 | 0 | 13.1294 | 39.95
2020-07-02 07:30 | 44014.3125 | 0 | 13.214 | 39.95
2020-07-02 08:00 | 44014.3333 | 0 | 12.8095 | 39.95
2020-07-02 08:30 | 44014.3542 | 0 | 12.4657 | 39.95
2020-07-02 09:00 | 44014.375 | 0 | 12.303 | 39.95
2020-07-02 09:30 | 44014.3958 | 0 | 11.4004 | 39.95
2020-07-02 10:00 | 44014.4167 | 0 | 11.2 | 39.95
2020-07-02 10:30 | 44014.4375 | 0 | 10.8877 | 39.95
2020-07-02 11:00 | 44014.4583 | 0 | 10.3323 | 39.95
2020-07-02 11:30 | 44014.4792 | 0 | 9.6967 | 39.95
2020-07-02 12:00 | 44014.5 | 0 | 10.3337 | 39.95
2020-07-02 12:30 | 44014.5208 | 0 | 9.8209 | 39.95
2020-07-02 13:00 | 44014.5417 | 0 | 10.2285 | 39.95
2020-07-02 13:30 | 44014.5625 | 0 | 10.3127 | 39.95
2020-07-02 14:00 | 44014.5833 | 0 | 10.0268 | 39.95
2020-07-02 14:30 | 44014.6042 | 0 | 10.5214 | 39.95
2020-07-02 15:00 | 44014.625 | 0 | 10.8156 | 39.95
2020-07-02 15:30 | 44014.6458 | 0 | 11.1944 | 39.95
2020-07-02 16:00 | 44014.6667 | 0 | 11.7483 | 39.95
2020-07-02 16:30 | 44014.6875 | 0 | 12.449 | 39.95
2020-07-02 17:00 | 44014.7083 | 0 | 13.158 | 39.95
2020-07-02 17:30 | 44014.7292 | 0 | 14.1022 | 39.95
2020-07-02 18:00 | 44014.75 | 0 | 14.337 | 39.95
2020-07-02 18:30 | 44014.7708 | 0 | 14.4718 | 39.95
2020-07-02 19:00 | 44014.7917 | 0 | 14.226 | 39.95
2020-07-02 19:30 | 44014.8125 | 0 | 13.9683 | 39.95
2020-07-02 20:00 | 44014.8333 | 0 | 13.9222 | 39.95
2020-07-02 20:30 | 44014.8542 | 0 | 13.3173 | 39.95
2020-07-02 21:00 | 44014.875 | 0 | 12.5738 | 39.95
2020-07-02 21:30 | 44014.8958 | 0 | 12.0425 | 39.95
2020-07-02 22:00 | 44014.9167 | 0 | 11.5561 | 39.95
2020-07-02 22:30 | 44014.9375 | 0 | 10.5841 | 39.95
2020-07-02 23:00 | 44014.9583 | 0 | 9.9421 | 39.95
2020-07-02 23:30 | 44014.9792 | 0 | 9.3795 | 39.95
2020-07-03 | 44015 | 0 | 8.6235 | 39.95
2020-07-03 00:30 | 44015.0208 | 0 | 8.4179 | 39.95
2020-07-03 01:00 | 44015.0417 | 0 | 7.9255 | 39.95
2020-07-03 01:30 | 44015.0625 | 0 | 7.8458 | 39.95
2020-07-03 02:00 | 44015.0833 | 0 | 7.8736 | 39.95
2020-07-03 02:30 | 44015.1042 | 0 | 7.7508 | 39.95
2020-07-03 03:00 | 44015.125 | 0 | 7.8447 | 39.95
2020-07-03 03:30 | 44015.1458 | 0 | 7.9784 | 39.95
2020-07-03 04:00 | 44015.1667 | 0 | 8.1386 | 39.95
2020-07-03 04:30 | 44015.1875 | 0 | 8.5269 | 39.95
2020-07-03 05:00 | 44015.2083 | 0 | 9.1709 | 39.95
2020-07-03 05:30 | 44015.2292 | 0 | 9.9203 | 39.95
2020-07-03 06:00 | 44015.25 | 0 | 11.0532 | 39.95
2020-07-03 06:30 | 44015.2708 | 0 | 12.0868 | 39.95
2020-07-03 07:00 | 44015.2917 | 0 | 12.7654 | 39.95
2020-07-03 07:30 | 44015.3125 | 0 | 12.6821 | 39.95
2020-07-03 08:00 | 44015.3333 | 0 | 12.5005 | 39.95
2020-07-03 08:30 | 44015.3542 | 0 | 12.0038 | 39.95
2020-07-03 09:00 | 44015.375 | 0 | 11.3967 | 39.95
2020-07-03 09:30 | 44015.3958 | 0 | 10.6792 | 39.95
2020-07-03 10:00 | 44015.4167 | 0 | 10.175 | 39.95
2020-07-03 10:30 | 44015.4375 | 0 | 9.9589 | 39.95
2020-07-03 11:00 | 44015.4583 | 0 | 9.7022 | 39.95
2020-07-03 11:30 | 44015.4792 | 0 | 9.383 | 39.95
2020-07-03 12:00 | 44015.5 | 0 | 9.3365 | 39.95
2020-07-03 12:30 | 44015.5208 | 0 | 9.4179 | 39.95
2020-07-03 13:00 | 44015.5417 | 0 | 9.3029 | 39.95
2020-07-03 13:30 | 44015.5625 | 0 | 9.4747 | 39.95
2020-07-03 14:00 | 44015.5833 | 0 | 9.8558 | 39.95
2020-07-03 14:30 | 44015.6042 | 0 | 10.8317 | 39.95
2020-07-03 15:00 | 44015.625 | 0 | 11.0775 | 39.95
2020-07-03 15:30 | 44015.6458 | 0 | 11.1019 | 39.95
2020-07-03 16:00 | 44015.6667 | 0 | 11.6604 | 39.95
2020-07-03 16:30 | 44015.6875 | 0 | 12.1885 | 39.95
2020-07-03 17:00 | 44015.7083 | 0 | 12.599 | 39.95
2020-07-03 17:30 | 44015.7292 | 0 | 13.204 | 39.95
2020-07-03 18:00 | 44015.75 | 0 | 13.1871 | 39.95
2020-07-03 18:30 | 44015.7708 | 0 | 13.3055 | 39.95
2020-07-03 19:00 | 44015.7917 | 0 | 13.2305 | 39.95
2020-07-03 19:30 | 44015.8125 | 0 | 12.8674 | 39.95
2020-07-03 20:00 | 44015.8333 | 0 | 12.7636 | 39.95
2020-07-03 20:30 | 44015.8542 | 0 | 12.0556 | 39.95
2020-07-03 21:00 | 44015.875 | 0 | 11.5941 | 39.95
2020-07-03 21:30 | 44015.8958 | 0 | 11.1763 | 39.95
2020-07-03 22:00 | 44015.9167 | 0 | 10.9347 | 39.95
2020-07-03 22:30 | 44015.9375 | 0 | 10.2895 | 39.95
2020-07-03 23:00 | 44015.9583 | 0 | 9.6779 | 39.95
2020-07-03 23:30 | 44015.9792 | 0 | 9.2384 | 39.95
2020-07-04 | 44016 | 0 | 8.6685 | 39.95
2020-07-04 00:30 | 44016.0208 | 0 | 8.1522 | 39.95
2020-07-04 01:00 | 44016.0417 | 0 | 7.8513 | 39.95
2020-07-04 01:30 | 44016.0625 | 0 | 7.748 | 39.95
2020-07-04 02:00 | 44016.0833 | 0 | 7.6601 | 39.95
2020-07-04 02:30 | 44016.1042 | 0 | 7.6365 | 39.95
2020-07-04 03:00 | 44016.125 | 0 | 7.6065 | 39.95
2020-07-04 03:30 | 44016.1458 | 0 | 7.4563 | 39.95
2020-07-04 04:00 | 44016.1667 | 0 | 7.5666 | 39.95
2020-07-04 04:30 | 44016.1875 | 0 | 7.728 | 39.95
2020-07-04 05:00 | 44016.2083 | 0 | 7.889 | 39.95
2020-07-04 05:30 | 44016.2292 | 0 | 8.1082 | 39.95
2020-07-04 06:00 | 44016.25 | 0 | 8.6257 | 39.95
2020-07-04 06:30 | 44016.2708 | 0 | 9.1151 | 39.95
2020-07-04 07:00 | 44016.2917 | 0 | 9.469 | 39.95
2020-07-04 07:30 | 44016.3125 | 0 | 9.5194 | 39.95
2020-07-04 08:00 | 44016.3333 | 0 | 9.5555 | 39.95
2020-07-04 08:30 | 44016.3542 | 0 | 9.3992 | 39.95
2020-07-04 09:00 | 44016.375 | 0 | 9.1323 | 39.95
2020-07-04 09:30 | 44016.3958 | 0 | 8.6762 | 39.95
2020-07-04 10:00 | 44016.4167 | 0 | 8.232 | 39.95
2020-07-04 10:30 | 44016.4375 | 0 | 7.8345 | 39.95
2020-07-04 11:00 | 44016.4583 | 0 | 7.5523 | 39.95
2020-07-04 11:30 | 44016.4792 | 0 | 7.3704 | 39.95
2020-07-04 12:00 | 44016.5 | 0 | 7.2223 | 39.95
2020-07-04 12:30 | 44016.5208 | 0 | 6.9971 | 39.95
2020-07-04 13:00 | 44016.5417 | 0 | 7.1671 | 39.95
2020-07-04 13:30 | 44016.5625 | 0 | 7.2841 | 39.95
2020-07-04 14:00 | 44016.5833 | 0 | 7.6251 | 39.95
2020-07-04 14:30 | 44016.6042 | 0 | 8.2616 | 39.95
2020-07-04 15:00 | 44016.625 | 0 | 8.5771 | 39.95
2020-07-04 15:30 | 44016.6458 | 0 | 9.0137 | 39.95
2020-07-04 16:00 | 44016.6667 | 0 | 9.6916 | 39.95
2020-07-04 16:30 | 44016.6875 | 0 | 10.6772 | 39.95
2020-07-04 17:00 | 44016.7083 | 0 | 11.4935 | 39.95
2020-07-04 17:30 | 44016.7292 | 0 | 12.4413 | 39.95
2020-07-04 18:00 | 44016.75 | 0 | 12.7179 | 39.95
2020-07-04 18:30 | 44016.7708 | 0 | 12.7157 | 39.95
2020-07-04 19:00 | 44016.7917 | 0 | 12.2459 | 39.95
2020-07-04 19:30 | 44016.8125 | 0 | 12.1043 | 39.95
2020-07-04 20:00 | 44016.8333 | 0 | 12.1156 | 39.95
2020-07-04 20:30 | 44016.8542 | 0 | 11.6324 | 39.95
2020-07-04 21:00 | 44016.875 | 0 | 11.1355 | 39.95
2020-07-04 21:30 | 44016.8958 | 0 | 10.8507 | 39.95
2020-07-04 22:00 | 44016.9167 | 0 | 10.5242 | 39.95
2020-07-04 22:30 | 44016.9375 | 0 | 9.636 | 39.95
2020-07-04 23:00 | 44016.9583 | 0 | 9.138 | 39.95
2020-07-04 23:30 | 44016.9792 | 0 | 8.6866 | 39.95
2020-07-05 | 44017 | 0 | 8.0362 | 39.95
2020-07-05 00:30 | 44017.0208 | 0 | 7.7509 | 39.95
2020-07-05 01:00 | 44017.0417 | 0 | 7.6155 | 39.95
2020-07-05 01:30 | 44017.0625 | 0 | 7.5554 | 39.95
2020-07-05 02:00 | 44017.0833 | 0 | 7.4241 | 39.95
2020-07-05 02:30 | 44017.1042 | 0 | 7.3446 | 39.95
2020-07-05 03:00 | 44017.125 | 0 | 7.2489 | 39.95
2020-07-05 03:30 | 44017.1458 | 0 | 7.1837 | 39.95
2020-07-05 04:00 | 44017.1667 | 0 | 7.2892 | 39.95
2020-07-05 04:30 | 44017.1875 | 0 | 7.3348 | 39.95
2020-07-05 05:00 | 44017.2083 | 0 | 7.3824 | 39.95
2020-07-05 05:30 | 44017.2292 | 0 | 7.7308 | 39.95
2020-07-05 06:00 | 44017.25 | 0 | 8.1588 | 39.95
2020-07-05 06:30 | 44017.2708 | 0 | 8.652 | 39.95
2020-07-05 07:00 | 44017.2917 | 0 | 9.3416 | 39.95
2020-07-05 07:30 | 44017.3125 | 0 | 9.4915 | 39.95
2020-07-05 08:00 | 44017.3333 | 0 | 9.5068 | 39.95
2020-07-05 08:30 | 44017.3542 | 0 | 9.3943 | 39.95
2020-07-05 09:00 | 44017.375 | 0 | 9.0972 | 39.95
2020-07-05 09:30 | 44017.3958 | 0 | 8.6276 | 39.95
2020-07-05 10:00 | 44017.4167 | 0 | 8.0417 | 39.95
2020-07-05 10:30 | 44017.4375 | 0 | 7.6638 | 39.95
2020-07-05 11:00 | 44017.4583 | 0 | 7.2025 | 39.95
2020-07-05 11:30 | 44017.4792 | 0 | 6.863 | 39.95
2020-07-05 12:00 | 44017.5 | 0 | 6.6256 | 39.95
2020-07-05 12:30 | 44017.5208 | 0 | 7.6535 | 39.95
2020-07-05 13:00 | 44017.5417 | 0 | 6.8689 | 39.95
2020-07-05 13:30 | 44017.5625 | 0 | 6.8231 | 39.95
2020-07-05 14:00 | 44017.5833 | 0 | 7.8531 | 39.95
2020-07-05 14:30 | 44017.6042 | 0 | 8.1691 | 39.95
2020-07-05 15:00 | 44017.625 | 0 | 8.4186 | 39.95
2020-07-05 15:30 | 44017.6458 | 0 | 8.9529 | 39.95
2020-07-05 16:00 | 44017.6667 | 0 | 9.5902 | 39.95
2020-07-05 16:30 | 44017.6875 | 0 | 10.6846 | 39.95
2020-07-05 17:00 | 44017.7083 | 0 | 11.89 | 39.95
2020-07-05 17:30 | 44017.7292 | 0 | 13.0249 | 39.95
2020-07-05 18:00 | 44017.75 | 0 | 13.416 | 39.95
2020-07-05 18:30 | 44017.7708 | 0 | 13.5286 | 39.95
2020-07-05 19:00 | 44017.7917 | 0 | 13.3097 | 39.95
2020-07-05 19:30 | 44017.8125 | 0 | 13.0898 | 39.95
2020-07-05 20:00 | 44017.8333 | 0 | 13.1959 | 39.95
2020-07-05 20:30 | 44017.8542 | 0 | 12.5341 | 39.95
2020-07-05 21:00 | 44017.875 | 0 | 11.9133 | 39.95
2020-07-05 21:30 | 44017.8958 | 0 | 11.3375 | 39.95
2020-07-05 22:00 | 44017.9167 | 0 | 10.6807 | 39.95
2020-07-05 22:30 | 44017.9375 | 0 | 9.8226 | 39.95
2020-07-05 23:00 | 44017.9583 | 0 | 9.2032 | 39.95
2020-07-05 23:30 | 44017.9792 | 0 | 8.5662 | 39.95
2020-07-06 | 44018 | 0 | 8.1844 | 39.95
2020-07-06 00:30 | 44018.0208 | 0 | 7.8781 | 39.95
2020-07-06 01:00 | 44018.0417 | 0 | 7.5874 | 39.95
2020-07-06 01:30 | 44018.0625 | 0 | 7.5011 | 39.95
2020-07-06 02:00 | 44018.0833 | 0 | 7.5739 | 39.95
2020-07-06 02:30 | 44018.1042 | 0 | 7.4144 | 39.95
2020-07-06 03:00 | 44018.125 | 0 | 7.4689 | 39.95
2020-07-06 03:30 | 44018.1458 | 0 | 7.5513 | 39.95
2020-07-06 04:00 | 44018.1667 | 0 | 7.7713 | 39.95
2020-07-06 04:30 | 44018.1875 | 0 | 8.366 | 39.95
2020-07-06 05:00 | 44018.2083 | 0 | 9.1085 | 39.95
2020-07-06 05:30 | 44018.2292 | 0 | 10.157 | 39.95
2020-07-06 06:00 | 44018.25 | 0 | 11.4761 | 39.95
2020-07-06 06:30 | 44018.2708 | 0 | 12.744 | 39.95
2020-07-06 07:00 | 44018.2917 | 0 | 14.0572 | 39.95
2020-07-06 07:30 | 44018.3125 | 0 | 14.3286 | 39.95
2020-07-06 08:00 | 44018.3333 | 0 | 14.0426 | 39.95
2020-07-06 08:30 | 44018.3542 | 0 | 13.5195 | 39.95
2020-07-06 09:00 | 44018.375 | 0 | 12.5444 | 39.95
2020-07-06 09:30 | 44018.3958 | 0 | 11.4565 | 39.95
2020-07-06 10:00 | 44018.4167 | 0 | 10.8042 | 39.95
2020-07-06 10:30 | 44018.4375 | 0 | 10.4807 | 39.95
2020-07-06 11:00 | 44018.4583 | 0 | 10.048 | 39.95
2020-07-06 11:30 | 44018.4792 | 0 | 9.8105 | 39.95
2020-07-06 12:00 | 44018.5 | 0 | 9.5556 | 39.95
2020-07-06 12:30 | 44018.5208 | 0 | 9.4683 | 39.95
2020-07-06 13:00 | 44018.5417 | 0 | 9.5332 | 39.95
2020-07-06 13:30 | 44018.5625 | 0 | 9.8037 | 39.95
2020-07-06 14:00 | 44018.5833 | 0 | 9.9987 | 39.95
2020-07-06 14:30 | 44018.6042 | 0 | 10.4823 | 39.95
2020-07-06 15:00 | 44018.625 | 0 | 11.1983 | 39.95
2020-07-06 15:30 | 44018.6458 | 0 | 11.3575 | 39.95
2020-07-06 16:00 | 44018.6667 | 0 | 11.6894 | 39.95
2020-07-06 16:30 | 44018.6875 | 0 | 12.604 | 39.95
2020-07-06 17:00 | 44018.7083 | 0 | 13.582 | 39.95
2020-07-06 17:30 | 44018.7292 | 0 | 14.8162 | 39.95
2020-07-06 18:00 | 44018.75 | 0 | 15.2881 | 39.95
2020-07-06 18:30 | 44018.7708 | 0 | 15.4648 | 39.95
2020-07-06 19:00 | 44018.7917 | 0 | 15.0822 | 39.95
2020-07-06 19:30 | 44018.8125 | 0 | 14.7969 | 39.95
2020-07-06 20:00 | 44018.8333 | 0 | 14.672 | 39.95
2020-07-06 20:30 | 44018.8542 | 0 | 14.0626 | 39.95
2020-07-06 21:00 | 44018.875 | 0 | 13.2998 | 39.95
2020-07-06 21:30 | 44018.8958 | 0 | 12.6351 | 39.95
2020-07-06 22:00 | 44018.9167 | 0 | 12.0856 | 39.95
2020-07-06 22:30 | 44018.9375 | 0 | 11.3139 | 39.95
2020-07-06 23:00 | 44018.9583 | 0 | 10.355 | 39.95
2020-07-06 23:30 | 44018.9792 | 0 | 9.6802 | 39.95
2020-07-07 | 44019 | 0 | 9.1032 | 39.95
2020-07-07 00:30 | 44019.0208 | 0 | 8.5565 | 39.95
2020-07-07 01:00 | 44019.0417 | 0 | 8.284 | 39.95
2020-07-07 01:30 | 44019.0625 | 0 | 8.0207 | 39.95
2020-07-07 02:00 | 44019.0833 | 0 | 8.0048 | 39.95
2020-07-07 02:30 | 44019.1042 | 0 | 7.8373 | 39.95
2020-07-07 03:00 | 44019.125 | 0 | 7.8575 | 39.95
2020-07-07 03:30 | 44019.1458 | 0 | 8.0299 | 39.95
2020-07-07 04:00 | 44019.1667 | 0 | 8.2345 | 39.95
2020-07-07 04:30 | 44019.1875 | 0 | 8.8021 | 39.95
2020-07-07 05:00 | 44019.2083 | 0 | 9.6731 | 39.95
2020-07-07 05:30 | 44019.2292 | 0 | 10.4146 | 39.95
2020-07-07 06:00 | 44019.25 | 0 | 11.9269 | 39.95
2020-07-07 06:30 | 44019.2708 | 0 | 13.3747 | 39.95
2020-07-07 07:00 | 44019.2917 | 0 | 14.4817 | 39.95
2020-07-07 07:30 | 44019.3125 | 0 | 14.5575 | 39.95
2020-07-07 08:00 | 44019.3333 | 0 | 13.98 | 39.95
2020-07-07 08:30 | 44019.3542 | 0 | 13.2323 | 39.95
2020-07-07 09:00 | 44019.375 | 0 | 12.3221 | 39.95
2020-07-07 09:30 | 44019.3958 | 0 | 11.4354 | 39.95
2020-07-07 10:00 | 44019.4167 | 0 | 10.789 | 39.95
2020-07-07 10:30 | 44019.4375 | 0 | 10.3841 | 39.95
2020-07-07 11:00 | 44019.4583 | 0 | 9.9255 | 39.95
2020-07-07 11:30 | 44019.4792 | 0 | 9.6262 | 39.95
2020-07-07 12:00 | 44019.5 | 0 | 9.4038 | 39.95
2020-07-07 12:30 | 44019.5208 | 0 | 9.4049 | 39.95
2020-07-07 13:00 | 44019.5417 | 0 | 9.5863 | 39.95
2020-07-07 13:30 | 44019.5625 | 0 | 9.6593 | 39.95
2020-07-07 14:00 | 44019.5833 | 0 | 9.9594 | 39.95
2020-07-07 14:30 | 44019.6042 | 0 | 10.3917 | 39.95
2020-07-07 15:00 | 44019.625 | 0 | 10.761 | 39.95
2020-07-07 15:30 | 44019.6458 | 0 | 11.1302 | 39.95
2020-07-07 16:00 | 44019.6667 | 0 | 11.8281 | 39.95
2020-07-07 16:30 | 44019.6875 | 0 | 12.6755 | 39.95
2020-07-07 17:00 | 44019.7083 | 0 | 13.4549 | 39.95
2020-07-07 17:30 | 44019.7292 | 0 | 14.4762 | 39.95
2020-07-07 18:00 | 44019.75 | 0 | 14.7424 | 39.95
2020-07-07 18:30 | 44019.7708 | 0 | 15.0696 | 39.95
2020-07-07 19:00 | 44019.7917 | 0 | 14.9765 | 39.95
2020-07-07 19:30 | 44019.8125 | 0 | 14.3963 | 39.95
2020-07-07 20:00 | 44019.8333 | 0 | 14.2759 | 39.95
2020-07-07 20:30 | 44019.8542 | 0 | 13.6147 | 39.95
2020-07-07 21:00 | 44019.875 | 0 | 12.9695 | 39.95
2020-07-07 21:30 | 44019.8958 | 0 | 12.377 | 39.95
2020-07-07 22:00 | 44019.9167 | 0 | 11.624 | 39.95
2020-07-07 22:30 | 44019.9375 | 0 | 10.6935 | 39.95
2020-07-07 23:00 | 44019.9583 | 0 | 9.9078 | 39.95
2020-07-07 23:30 | 44019.9792 | 0 | 9.3364 | 39.95
2020-07-08 | 44020 | 0 | 8.7314 | 39.95
2020-07-08 00:30 | 44020.0208 | 0 | 8.3593 | 39.95
2020-07-08 01:00 | 44020.0417 | 0 | 8.1202 | 39.95
2020-07-08 01:30 | 44020.0625 | 0 | 7.8629 | 39.95
2020-07-08 02:00 | 44020.0833 | 0 | 7.8765 | 39.95
2020-07-08 02:30 | 44020.1042 | 0 | 7.7638 | 39.95
2020-07-08 03:00 | 44020.125 | 0 | 7.7285 | 39.95
2020-07-08 03:30 | 44020.1458 | 0 | 7.8225 | 39.95
2020-07-08 04:00 | 44020.1667 | 0 | 8.1296 | 39.95
2020-07-08 04:30 | 44020.1875 | 0 | 8.6022 | 39.95
2020-07-08 05:00 | 44020.2083 | 0 | 9.2628 | 39.95
2020-07-08 05:30 | 44020.2292 | 0 | 10.063 | 39.95
2020-07-08 06:00 | 44020.25 | 0 | 11.4163 | 39.95
2020-07-08 06:30 | 44020.2708 | 0 | 12.3807 | 39.95
2020-07-08 07:00 | 44020.2917 | 0 | 13.4545 | 39.95
2020-07-08 07:30 | 44020.3125 | 0 | 13.2164 | 39.95
2020-07-08 08:00 | 44020.3333 | 0 | 12.8943 | 39.95
2020-07-08 08:30 | 44020.3542 | 0 | 12.1271 | 39.95
2020-07-08 09:00 | 44020.375 | 0 | 11.4954 | 39.95
2020-07-08 09:30 | 44020.3958 | 0 | 10.9554 | 39.95
2020-07-08 10:00 | 44020.4167 | 0 | 10.2791 | 39.95
2020-07-08 10:30 | 44020.4375 | 0 | 9.8416 | 39.95
2020-07-08 11:00 | 44020.4583 | 0 | 9.4768 | 39.95
2020-07-08 11:30 | 44020.4792 | 0 | 9.4277 | 39.95
2020-07-08 12:00 | 44020.5 | 0 | 9.0321 | 39.95
2020-07-08 12:30 | 44020.5208 | 0 | 9.0349 | 39.95
2020-07-08 13:00 | 44020.5417 | 0 | 9.8881 | 39.95
2020-07-08 13:30 | 44020.5625 | 0 | 10.4871 | 39.95
2020-07-08 14:00 | 44020.5833 | 0 | 10.2004 | 39.95
2020-07-08 14:30 | 44020.6042 | 0 | 10.4329 | 39.95
2020-07-08 15:00 | 44020.625 | 0 | 10.5057 | 39.95
2020-07-08 15:30 | 44020.6458 | 0 | 11.4204 | 39.95
2020-07-08 16:00 | 44020.6667 | 0 | 11.9002 | 39.95
2020-07-08 16:30 | 44020.6875 | 0 | 12.549 | 39.95
2020-07-08 17:00 | 44020.7083 | 0 | 13.3122 | 39.95
2020-07-08 17:30 | 44020.7292 | 0 | 14.3441 | 39.95
2020-07-08 18:00 | 44020.75 | 0 | 14.5311 | 39.95
2020-07-08 18:30 | 44020.7708 | 0 | 14.8862 | 39.95
2020-07-08 19:00 | 44020.7917 | 0 | 14.4997 | 39.95
2020-07-08 19:30 | 44020.8125 | 0 | 14.1464 | 39.95
2020-07-08 20:00 | 44020.8333 | 0 | 13.9698 | 39.95
2020-07-08 20:30 | 44020.8542 | 0 | 13.3399 | 39.95
2020-07-08 21:00 | 44020.875 | 0 | 12.6026 | 39.95
2020-07-08 21:30 | 44020.8958 | 0 | 12.0583 | 39.95
2020-07-08 22:00 | 44020.9167 | 0 | 11.4681 | 39.95
2020-07-08 22:30 | 44020.9375 | 0 | 10.8515 | 39.95
2020-07-08 23:00 | 44020.9583 | 0 | 10.1698 | 39.95
2020-07-08 23:30 | 44020.9792 | 0 | 9.5071 | 39.95
2020-07-09 | 44021 | 0 | 8.7691 | 39.95
2020-07-09 00:30 | 44021.0208 | 0 | 8.2077 | 39.95
2020-07-09 01:00 | 44021.0417 | 0 | 7.9448 | 39.95
2020-07-09 01:30 | 44021.0625 | 0 | 7.8388 | 39.95
2020-07-09 02:00 | 44021.0833 | 0 | 7.7508 | 39.95
2020-07-09 02:30 | 44021.1042 | 0 | 7.6601 | 39.95
2020-07-09 03:00 | 44021.125 | 0 | 7.6625 | 39.95
2020-07-09 03:30 | 44021.1458 | 0 | 7.6556 | 39.95
2020-07-09 04:00 | 44021.1667 | 0 | 7.9272 | 39.95
2020-07-09 04:30 | 44021.1875 | 0 | 8.3229 | 39.95
2020-07-09 05:00 | 44021.2083 | 0 | 9.0569 | 39.95
2020-07-09 05:30 | 44021.2292 | 0 | 9.8553 | 39.95
2020-07-09 06:00 | 44021.25 | 0 | 10.9213 | 39.95
2020-07-09 06:30 | 44021.2708 | 0 | 11.9127 | 39.95
2020-07-09 07:00 | 44021.2917 | 0 | 12.6358 | 39.95
2020-07-09 07:30 | 44021.3125 | 0 | 12.9798 | 39.95
2020-07-09 08:00 | 44021.3333 | 0 | 13.1539 | 39.95
2020-07-09 08:30 | 44021.3542 | 0 | 13.0618 | 39.95
2020-07-09 09:00 | 44021.375 | 0 | 12.9031 | 39.95
2020-07-09 09:30 | 44021.3958 | 0 | 12.7386 | 39.95
2020-07-09 10:00 | 44021.4167 | 0 | 12.6821 | 39.95
2020-07-09 10:30 | 44021.4375 | 0 | 12.9023 | 39.95
2020-07-09 11:00 | 44021.4583 | 0 | 11.9127 | 39.95
2020-07-09 11:30 | 44021.4792 | 0 | 11.916 | 39.95
2020-07-09 12:00 | 44021.5 | 0 | 11.4005 | 39.95
2020-07-09 12:30 | 44021.5208 | 0 | 12.2067 | 39.95
2020-07-09 13:00 | 44021.5417 | 0 | 12.5356 | 39.95
2020-07-09 13:30 | 44021.5625 | 0 | 11.6958 | 39.95
2020-07-09 14:00 | 44021.5833 | 0 | 11.9149 | 39.95
2020-07-09 14:30 | 44021.6042 | 0 | 12.1956 | 39.95
2020-07-09 15:00 | 44021.625 | 0 | 12.8312 | 39.95
2020-07-09 15:30 | 44021.6458 | 0 | 12.2398 | 39.95
2020-07-09 16:00 | 44021.6667 | 0 | 12.7678 | 39.95
2020-07-09 16:30 | 44021.6875 | 0 | 13.4687 | 39.95
2020-07-09 17:00 | 44021.7083 | 0 | 14.3264 | 39.95
2020-07-09 17:30 | 44021.7292 | 0 | 15.1668 | 39.95
2020-07-09 18:00 | 44021.75 | 0 | 15.1135 | 39.95
2020-07-09 18:30 | 44021.7708 | 0 | 15.2182 | 39.95
2020-07-09 19:00 | 44021.7917 | 0 | 14.8962 | 39.95
2020-07-09 19:30 | 44021.8125 | 0 | 14.5048 | 39.95
2020-07-09 20:00 | 44021.8333 | 0 | 14.6558 | 39.95
2020-07-09 20:30 | 44021.8542 | 0 | 13.6768 | 39.95
2020-07-09 21:00 | 44021.875 | 0 | 13.2061 | 39.95
2020-07-09 21:30 | 44021.8958 | 0 | 12.4337 | 39.95
2020-07-09 22:00 | 44021.9167 | 0 | 11.8212 | 39.95
2020-07-09 22:30 | 44021.9375 | 0 | 10.947 | 39.95
2020-07-09 23:00 | 44021.9583 | 0 | 10.2816 | 39.95
2020-07-09 23:30 | 44021.9792 | 0 | 9.4673 | 39.95
2020-07-10 | 44022 | 0 | 8.8453 | 39.95
2020-07-10 00:30 | 44022.0208 | 0 | 8.1601 | 39.95
2020-07-10 01:00 | 44022.0417 | 0 | 8.0144 | 39.95
2020-07-10 01:30 | 44022.0625 | 0 | 7.7233 | 39.95
2020-07-10 02:00 | 44022.0833 | 0 | 7.6973 | 39.95
2020-07-10 02:30 | 44022.1042 | 0 | 7.7471 | 39.95
2020-07-10 03:00 | 44022.125 | 0 | 7.7182 | 39.95
2020-07-10 03:30 | 44022.1458 | 0 | 7.8165 | 39.95
2020-07-10 04:00 | 44022.1667 | 0 | 7.9463 | 39.95
2020-07-10 04:30 | 44022.1875 | 0 | 8.4963 | 39.95
2020-07-10 05:00 | 44022.2083 | 0 | 9.1496 | 39.95
2020-07-10 05:30 | 44022.2292 | 0 | 9.9595 | 39.95
2020-07-10 06:00 | 44022.25 | 0 | 10.9922 | 39.95
2020-07-10 06:30 | 44022.2708 | 0 | 11.8784 | 39.95
2020-07-10 07:00 | 44022.2917 | 0 | 12.7532 | 39.95
2020-07-10 07:30 | 44022.3125 | 0 | 13.0001 | 39.95
2020-07-10 08:00 | 44022.3333 | 0 | 12.4583 | 39.95
2020-07-10 08:30 | 44022.3542 | 0 | 12.0792 | 39.95
2020-07-10 09:00 | 44022.375 | 0 | 11.2494 | 39.95
2020-07-10 09:30 | 44022.3958 | 0 | 11.1461 | 39.95
2020-07-10 10:00 | 44022.4167 | 0 | 11.2256 | 39.95
2020-07-10 10:30 | 44022.4375 | 0 | 10.7153 | 39.95
2020-07-10 11:00 | 44022.4583 | 0 | 11.1952 | 39.95
2020-07-10 11:30 | 44022.4792 | 0 | 10.6746 | 39.95
2020-07-10 12:00 | 44022.5 | 0 | 10.2331 | 39.95
2020-07-10 12:30 | 44022.5208 | 0 | 10.542 | 39.95
2020-07-10 13:00 | 44022.5417 | 0 | 9.6081 | 39.95
2020-07-10 13:30 | 44022.5625 | 0 | 9.9474 | 39.95
2020-07-10 14:00 | 44022.5833 | 0 | 9.9944 | 39.95
2020-07-10 14:30 | 44022.6042 | 0 | 9.8963 | 39.95
2020-07-10 15:00 | 44022.625 | 0 | 10.8463 | 39.95
2020-07-10 15:30 | 44022.6458 | 0 | 11.3292 | 39.95
2020-07-10 16:00 | 44022.6667 | 0 | 11.7876 | 39.95
2020-07-10 16:30 | 44022.6875 | 0 | 12.2091 | 39.95
2020-07-10 17:00 | 44022.7083 | 0 | 12.8777 | 39.95
2020-07-10 17:30 | 44022.7292 | 0 | 13.5632 | 39.95
2020-07-10 18:00 | 44022.75 | 0 | 13.7833 | 39.95
2020-07-10 18:30 | 44022.7708 | 0 | 13.7667 | 39.95
2020-07-10 19:00 | 44022.7917 | 0 | 13.6676 | 39.95
2020-07-10 19:30 | 44022.8125 | 0 | 13.521 | 39.95
2020-07-10 20:00 | 44022.8333 | 0 | 13.4502 | 39.95
2020-07-10 20:30 | 44022.8542 | 0 | 12.8803 | 39.95
2020-07-10 21:00 | 44022.875 | 0 | 12.2263 | 39.95
2020-07-10 21:30 | 44022.8958 | 0 | 11.8104 | 39.95
2020-07-10 22:00 | 44022.9167 | 0 | 11.4406 | 39.95
2020-07-10 22:30 | 44022.9375 | 0 | 10.71 | 39.95
2020-07-10 23:00 | 44022.9583 | 0 | 10.0178 | 39.95
2020-07-10 23:30 | 44022.9792 | 0 | 9.4066 | 39.95
2020-07-11 | 44023 | 0 | 8.9455 | 39.95
2020-07-11 00:30 | 44023.0208 | 0 | 8.3579 | 39.95
2020-07-11 01:00 | 44023.0417 | 0 | 8.0218 | 39.95
2020-07-11 01:30 | 44023.0625 | 0 | 7.9155 | 39.95
2020-07-11 02:00 | 44023.0833 | 0 | 7.847 | 39.95
2020-07-11 02:30 | 44023.1042 | 0 | 7.7695 | 39.95
2020-07-11 03:00 | 44023.125 | 0 | 7.6601 | 39.95
2020-07-11 03:30 | 44023.1458 | 0 | 7.5902 | 39.95
2020-07-11 04:00 | 44023.1667 | 0 | 7.6169 | 39.95
2020-07-11 04:30 | 44023.1875 | 0 | 7.762 | 39.95
2020-07-11 05:00 | 44023.2083 | 0 | 7.9309 | 39.95
2020-07-11 05:30 | 44023.2292 | 0 | 8.0924 | 39.95
2020-07-11 06:00 | 44023.25 | 0 | 8.4843 | 39.95
2020-07-11 06:30 | 44023.2708 | 0 | 9.031 | 39.95
2020-07-11 07:00 | 44023.2917 | 0 | 9.5878 | 39.95
2020-07-11 07:30 | 44023.3125 | 0 | 9.804 | 39.95
2020-07-11 08:00 | 44023.3333 | 0 | 10.3863 | 39.95
2020-07-11 08:30 | 44023.3542 | 0 | 10.0295 | 39.95
2020-07-11 09:00 | 44023.375 | 0 | 9.3584 | 39.95
2020-07-11 09:30 | 44023.3958 | 0 | 8.8283 | 39.95
2020-07-11 10:00 | 44023.4167 | 0 | 8.4151 | 39.95
2020-07-11 10:30 | 44023.4375 | 0 | 8.1039 | 39.95
2020-07-11 11:00 | 44023.4583 | 0 | 8.6539 | 39.95
2020-07-11 11:30 | 44023.4792 | 0 | 8.8259 | 39.95
2020-07-11 12:00 | 44023.5 | 0 | 8.7761 | 39.95
2020-07-11 12:30 | 44023.5208 | 0 | 9.0523 | 39.95
2020-07-11 13:00 | 44023.5417 | 0 | 8.0717 | 39.95
2020-07-11 13:30 | 44023.5625 | 0 | 7.648 | 39.95
2020-07-11 14:00 | 44023.5833 | 0 | 8.0192 | 39.95
2020-07-11 14:30 | 44023.6042 | 0 | 8.5161 | 39.95
2020-07-11 15:00 | 44023.625 | 0 | 8.5981 | 39.95
2020-07-11 15:30 | 44023.6458 | 0 | 9.2069 | 39.95
2020-07-11 16:00 | 44023.6667 | 0 | 9.5883 | 39.95
2020-07-11 16:30 | 44023.6875 | 0 | 10.4911 | 39.95
2020-07-11 17:00 | 44023.7083 | 0 | 11.0319 | 39.95
2020-07-11 17:30 | 44023.7292 | 0 | 11.8073 | 39.95
2020-07-11 18:00 | 44023.75 | 0 | 11.9451 | 39.95
2020-07-11 18:30 | 44023.7708 | 0 | 12.0135 | 39.95
2020-07-11 19:00 | 44023.7917 | 0 | 11.6597 | 39.95
2020-07-11 19:30 | 44023.8125 | 0 | 11.3512 | 39.95
2020-07-11 20:00 | 44023.8333 | 0 | 11.3124 | 39.95
2020-07-11 20:30 | 44023.8542 | 0 | 10.7876 | 39.95
2020-07-11 21:00 | 44023.875 | 0 | 10.3025 | 39.95
2020-07-11 21:30 | 44023.8958 | 0 | 10.072 | 39.95
2020-07-11 22:00 | 44023.9167 | 0 | 9.6274 | 39.95
2020-07-11 22:30 | 44023.9375 | 0 | 9.039 | 39.95
2020-07-11 23:00 | 44023.9583 | 0 | 8.6321 | 39.95
2020-07-11 23:30 | 44023.9792 | 0 | 8.2904 | 39.95
2020-07-12 | 44024 | 0 | 7.768 | 39.95
2020-07-12 00:30 | 44024.0208 | 0 | 7.4981 | 39.95
2020-07-12 01:00 | 44024.0417 | 0 | 7.2502 | 39.95
2020-07-12 01:30 | 44024.0625 | 0 | 7.1138 | 39.95
2020-07-12 02:00 | 44024.0833 | 0 | 7.0571 | 39.95
2020-07-12 02:30 | 44024.1042 | 0 | 6.9524 | 39.95
2020-07-12 03:00 | 44024.125 | 0 | 6.9008 | 39.95
2020-07-12 03:30 | 44024.1458 | 0 | 6.8449 | 39.95
2020-07-12 04:00 | 44024.1667 | 0 | 6.7855 | 39.95
2020-07-12 04:30 | 44024.1875 | 0 | 6.9105 | 39.95
2020-07-12 05:00 | 44024.2083 | 0 | 6.9637 | 39.95
2020-07-12 05:30 | 44024.2292 | 0 | 7.2172 | 39.95
2020-07-12 06:00 | 44024.25 | 0 | 7.5765 | 39.95
2020-07-12 06:30 | 44024.2708 | 0 | 7.7439 | 39.95
2020-07-12 07:00 | 44024.2917 | 0 | 8.1208 | 39.95
2020-07-12 07:30 | 44024.3125 | 0 | 8.0756 | 39.95
2020-07-12 08:00 | 44024.3333 | 0 | 8.5582 | 39.95
2020-07-12 08:30 | 44024.3542 | 0 | 8.3467 | 39.95
2020-07-12 09:00 | 44024.375 | 0 | 8.0636 | 39.95
2020-07-12 09:30 | 44024.3958 | 0 | 8.3451 | 39.95
2020-07-12 10:00 | 44024.4167 | 0 | 8.0564 | 39.95
2020-07-12 10:30 | 44024.4375 | 0 | 7.4774 | 39.95
2020-07-12 11:00 | 44024.4583 | 0 | 7.2868 | 39.95
2020-07-12 11:30 | 44024.4792 | 0 | 9.1537 | 39.95
2020-07-12 12:00 | 44024.5 | 0 | 9.3571 | 39.95
2020-07-12 12:30 | 44024.5208 | 0 | 9.6589 | 39.95
2020-07-12 13:00 | 44024.5417 | 0 | 9.4419 | 39.95
2020-07-12 13:30 | 44024.5625 | 0 | 9.6513 | 39.95
2020-07-12 14:00 | 44024.5833 | 0 | 10.0497 | 39.95
2020-07-12 14:30 | 44024.6042 | 0 | 10.1866 | 39.95
2020-07-12 15:00 | 44024.625 | 0 | 10.2656 | 39.95
2020-07-12 15:30 | 44024.6458 | 0 | 10.505 | 39.95
2020-07-12 16:00 | 44024.6667 | 0 | 11.1103 | 39.95
2020-07-12 16:30 | 44024.6875 | 0 | 12.0228 | 39.95
2020-07-12 17:00 | 44024.7083 | 0 | 12.6132 | 39.95
2020-07-12 17:30 | 44024.7292 | 0 | 12.9395 | 39.95
2020-07-12 18:00 | 44024.75 | 0 | 12.9366 | 39.95
2020-07-12 18:30 | 44024.7708 | 0 | 12.9232 | 39.95
2020-07-12 19:00 | 44024.7917 | 0 | 12.4822 | 39.95
2020-07-12 19:30 | 44024.8125 | 0 | 12.074 | 39.95
2020-07-12 20:00 | 44024.8333 | 0 | 11.8054 | 39.95
2020-07-12 20:30 | 44024.8542 | 0 | 11.1637 | 39.95
2020-07-12 21:00 | 44024.875 | 0 | 10.5325 | 39.95
2020-07-12 21:30 | 44024.8958 | 0 | 10.139 | 39.95
2020-07-12 22:00 | 44024.9167 | 0 | 9.6746 | 39.95
2020-07-12 22:30 | 44024.9375 | 0 | 9.0388 | 39.95
2020-07-12 23:00 | 44024.9583 | 0 | 8.4333 | 39.95
2020-07-12 23:30 | 44024.9792 | 0 | 8.0309 | 39.95
2020-07-13 | 44025 | 0 | 7.6735 | 39.95
2020-07-13 00:30 | 44025.0208 | 0 | 7.4786 | 39.95
2020-07-13 01:00 | 44025.0417 | 0 | 7.3248 | 39.95
2020-07-13 01:30 | 44025.0625 | 0 | 7.0705 | 39.95
2020-07-13 02:00 | 44025.0833 | 0 | 7.0349 | 39.95
2020-07-13 02:30 | 44025.1042 | 0 | 7.0821 | 39.95
2020-07-13 03:00 | 44025.125 | 0 | 7.1005 | 39.95
2020-07-13 03:30 | 44025.1458 | 0 | 7.1055 | 39.95
2020-07-13 04:00 | 44025.1667 | 0 | 7.4193 | 39.95
2020-07-13 04:30 | 44025.1875 | 0 | 7.8667 | 39.95
2020-07-13 05:00 | 44025.2083 | 0 | 8.5738 | 39.95
2020-07-13 05:30 | 44025.2292 | 0 | 9.4179 | 39.95
2020-07-13 06:00 | 44025.25 | 0 | 10.5828 | 39.95
2020-07-13 06:30 | 44025.2708 | 0 | 11.7886 | 39.95
2020-07-13 07:00 | 44025.2917 | 0 | 12.9412 | 39.95
2020-07-13 07:30 | 44025.3125 | 0 | 13.4041 | 39.95
2020-07-13 08:00 | 44025.3333 | 0 | 13.1464 | 39.95
2020-07-13 08:30 | 44025.3542 | 0 | 13.353 | 39.95
2020-07-13 09:00 | 44025.375 | 0 | 12.8513 | 39.95
2020-07-13 09:30 | 44025.3958 | 0 | 12.4258 | 39.95
2020-07-13 10:00 | 44025.4167 | 0 | 11.2219 | 39.95
2020-07-13 10:30 | 44025.4375 | 0 | 10.7207 | 39.95
2020-07-13 11:00 | 44025.4583 | 0 | 10.1275 | 39.95
2020-07-13 11:30 | 44025.4792 | 0 | 9.3493 | 39.95
2020-07-13 12:00 | 44025.5 | 0 | 9.6417 | 39.95
2020-07-13 12:30 | 44025.5208 | 0 | 9.708 | 39.95
2020-07-13 13:00 | 44025.5417 | 0 | 10.5853 | 39.95
2020-07-13 13:30 | 44025.5625 | 0 | 9.8132 | 39.95
2020-07-13 14:00 | 44025.5833 | 0 | 9.7651 | 39.95
2020-07-13 14:30 | 44025.6042 | 0 | 10.0134 | 39.95
2020-07-13 15:00 | 44025.625 | 0 | 10.6445 | 39.95
2020-07-13 15:30 | 44025.6458 | 0 | 11.0264 | 39.95
2020-07-13 16:00 | 44025.6667 | 0 | 11.7386 | 39.95
2020-07-13 16:30 | 44025.6875 | 0 | 12.5849 | 39.95
2020-07-13 17:00 | 44025.7083 | 0 | 13.6565 | 39.95
2020-07-13 17:30 | 44025.7292 | 0 | 14.8569 | 39.95
2020-07-13 18:00 | 44025.75 | 0 | 15.4505 | 39.95
2020-07-13 18:30 | 44025.7708 | 0 | 15.5536 | 39.95
2020-07-13 19:00 | 44025.7917 | 0 | 15.3713 | 39.95
2020-07-13 19:30 | 44025.8125 | 0 | 15.1327 | 39.95
2020-07-13 20:00 | 44025.8333 | 0 | 14.9498 | 39.95
2020-07-13 20:30 | 44025.8542 | 0 | 14.2983 | 39.95
2020-07-13 21:00 | 44025.875 | 0 | 13.4938 | 39.95
2020-07-13 21:30 | 44025.8958 | 0 | 12.8864 | 39.95
2020-07-13 22:00 | 44025.9167 | 0 | 12.1543 | 39.95
2020-07-13 22:30 | 44025.9375 | 0 | 11.0018 | 39.95
2020-07-13 23:00 | 44025.9583 | 0 | 10.2952 | 39.95
2020-07-13 23:30 | 44025.9792 | 0 | 9.4964 | 39.95
2020-07-14 | 44026 | 0 | 8.9706 | 39.95
2020-07-14 00:30 | 44026.0208 | 0 | 8.4249 | 39.95
2020-07-14 01:00 | 44026.0417 | 0 | 8.1583 | 39.95
2020-07-14 01:30 | 44026.0625 | 0 | 8.0495 | 39.95
2020-07-14 02:00 | 44026.0833 | 0 | 7.8113 | 39.95
2020-07-14 02:30 | 44026.1042 | 0 | 7.7131 | 39.95
2020-07-14 03:00 | 44026.125 | 0 | 7.7998 | 39.95
2020-07-14 03:30 | 44026.1458 | 0 | 7.9951 | 39.95
2020-07-14 04:00 | 44026.1667 | 0 | 8.0457 | 39.95
2020-07-14 04:30 | 44026.1875 | 0 | 8.5612 | 39.95
2020-07-14 05:00 | 44026.2083 | 0 | 9.7132 | 39.95
2020-07-14 05:30 | 44026.2292 | 0 | 10.6217 | 39.95
2020-07-14 06:00 | 44026.25 | 0 | 12.4541 | 39.95
2020-07-14 06:30 | 44026.2708 | 0 | 14.3604 | 39.95
2020-07-14 07:00 | 44026.2917 | 0 | 15.5574 | 39.95
2020-07-14 07:30 | 44026.3125 | 0 | 15.3986 | 39.95
2020-07-14 08:00 | 44026.3333 | 0 | 14.6003 | 39.95
2020-07-14 08:30 | 44026.3542 | 0 | 13.4738 | 39.95
2020-07-14 09:00 | 44026.375 | 0 | 12.6239 | 39.95
2020-07-14 09:30 | 44026.3958 | 0 | 11.638 | 39.95
2020-07-14 10:00 | 44026.4167 | 0 | 11.0661 | 39.95
2020-07-14 10:30 | 44026.4375 | 0 | 10.8632 | 39.95
2020-07-14 11:00 | 44026.4583 | 0 | 10.3529 | 39.95
2020-07-14 11:30 | 44026.4792 | 0 | 10.0997 | 39.95
2020-07-14 12:00 | 44026.5 | 0 | 9.9031 | 39.95
2020-07-14 12:30 | 44026.5208 | 0 | 9.7808 | 39.95
2020-07-14 13:00 | 44026.5417 | 0 | 9.845 | 39.95
2020-07-14 13:30 | 44026.5625 | 0 | 9.9311 | 39.95
2020-07-14 14:00 | 44026.5833 | 0 | 10.3425 | 39.95
2020-07-14 14:30 | 44026.6042 | 0 | 10.6722 | 39.95
2020-07-14 15:00 | 44026.625 | 0 | 11.1469 | 39.95
2020-07-14 15:30 | 44026.6458 | 0 | 11.7195 | 39.95
2020-07-14 16:00 | 44026.6667 | 0 | 12.6492 | 39.95
2020-07-14 16:30 | 44026.6875 | 0 | 13.9404 | 39.95
2020-07-14 17:00 | 44026.7083 | 0 | 15.7752 | 39.95
2020-07-14 17:30 | 44026.7292 | 0 | 17.4839 | 39.95
2020-07-14 18:00 | 44026.75 | 0 | 18.1568 | 39.95
2020-07-14 18:30 | 44026.7708 | 0 | 18.5588 | 39.95
2020-07-14 19:00 | 44026.7917 | 0 | 18.4561 | 39.95
2020-07-14 19:30 | 44026.8125 | 0 | 17.9532 | 39.95
2020-07-14 20:00 | 44026.8333 | 0 | 17.5583 | 39.95
2020-07-14 20:30 | 44026.8542 | 0 | 16.5947 | 39.95
2020-07-14 21:00 | 44026.875 | 0 | 15.6395 | 39.95
2020-07-14 21:30 | 44026.8958 | 0 | 14.6534 | 39.95
2020-07-14 22:00 | 44026.9167 | 0 | 13.578 | 39.95
2020-07-14 22:30 | 44026.9375 | 0 | 11.9788 | 39.95
2020-07-14 23:00 | 44026.9583 | 0 | 10.8561 | 39.95
2020-07-14 23:30 | 44026.9792 | 0 | 10.1149 | 39.95
2020-07-15 | 44027 | 0 | 9.514 | 39.95
2020-07-15 00:30 | 44027.0208 | 0 | 8.9022 | 39.95
2020-07-15 01:00 | 44027.0417 | 0 | 8.6296 | 39.95
2020-07-15 01:30 | 44027.0625 | 0 | 8.5477 | 39.95
2020-07-15 02:00 | 44027.0833 | 0 | 8.3496 | 39.95
2020-07-15 02:30 | 44027.1042 | 0 | 8.2607 | 39.95
2020-07-15 03:00 | 44027.125 | 0 | 8.2868 | 39.95
2020-07-15 03:30 | 44027.1458 | 0 | 8.3138 | 39.95
2020-07-15 04:00 | 44027.1667 | 0 | 8.6165 | 39.95
2020-07-15 04:30 | 44027.1875 | 0 | 9.0507 | 39.95
2020-07-15 05:00 | 44027.2083 | 0 | 10.1401 | 39.95
2020-07-15 05:30 | 44027.2292 | 0 | 11.2784 | 39.95
2020-07-15 06:00 | 44027.25 | 0 | 12.9953 | 39.95
2020-07-15 06:30 | 44027.2708 | 0 | 14.6099 | 39.95
2020-07-15 07:00 | 44027.2917 | 0 | 15.7472 | 39.95
2020-07-15 07:30 | 44027.3125 | 0 | 15.4395 | 39.95
2020-07-15 08:00 | 44027.3333 | 0 | 14.569 | 39.95
2020-07-15 08:30 | 44027.3542 | 0 | 13.4041 | 39.95
2020-07-15 09:00 | 44027.375 | 0 | 12.2785 | 39.95
2020-07-15 09:30 | 44027.3958 | 0 | 11.3192 | 39.95
2020-07-15 10:00 | 44027.4167 | 0 | 10.7543 | 39.95
2020-07-15 10:30 | 44027.4375 | 0 | 10.2873 | 39.95
2020-07-15 11:00 | 44027.4583 | 0 | 9.7757 | 39.95
2020-07-15 11:30 | 44027.4792 | 0 | 9.6197 | 39.95
2020-07-15 12:00 | 44027.5 | 0 | 9.4662 | 39.95
2020-07-15 12:30 | 44027.5208 | 0 | 9.3083 | 39.95
2020-07-15 13:00 | 44027.5417 | 0 | 9.3388 | 39.95
2020-07-15 13:30 | 44027.5625 | 0 | 9.6889 | 39.95
2020-07-15 14:00 | 44027.5833 | 0 | 9.8962 | 39.95
2020-07-15 14:30 | 44027.6042 | 0 | 10.1696 | 39.95
2020-07-15 15:00 | 44027.625 | 0 | 10.5646 | 39.95
2020-07-15 15:30 | 44027.6458 | 0 | 11.1274 | 39.95
2020-07-15 16:00 | 44027.6667 | 0 | 11.8495 | 39.95
2020-07-15 16:30 | 44027.6875 | 0 | 12.7177 | 39.95
2020-07-15 17:00 | 44027.7083 | 0 | 13.4746 | 39.95
2020-07-15 17:30 | 44027.7292 | 0 | 14.9451 | 39.95
2020-07-15 18:00 | 44027.75 | 0 | 15.3307 | 39.95
2020-07-15 18:30 | 44027.7708 | 0 | 15.9728 | 39.95
2020-07-15 19:00 | 44027.7917 | 0 | 15.8682 | 39.95
2020-07-15 19:30 | 44027.8125 | 0 | 15.5708 | 39.95
2020-07-15 20:00 | 44027.8333 | 0 | 15.2747 | 39.95
2020-07-15 20:30 | 44027.8542 | 0 | 14.6507 | 39.95
2020-07-15 21:00 | 44027.875 | 0 | 13.7796 | 39.95
2020-07-15 21:30 | 44027.8958 | 0 | 12.9759 | 39.95
2020-07-15 22:00 | 44027.9167 | 0 | 12.2796 | 39.95
2020-07-15 22:30 | 44027.9375 | 0 | 11.3632 | 39.95
2020-07-15 23:00 | 44027.9583 | 0 | 10.6263 | 39.95
2020-07-15 23:30 | 44027.9792 | 0 | 9.9237 | 39.95
2020-07-16 | 44028 | 0 | 9.1561 | 39.95
2020-07-16 00:30 | 44028.0208 | 0 | 8.6126 | 39.95
2020-07-16 01:00 | 44028.0417 | 0 | 8.4263 | 39.95
2020-07-16 01:30 | 44028.0625 | 0 | 8.2119 | 39.95
2020-07-16 02:00 | 44028.0833 | 0 | 8.0593 | 39.95
2020-07-16 02:30 | 44028.1042 | 0 | 8.0648 | 39.95
2020-07-16 03:00 | 44028.125 | 0 | 8.0048 | 39.95
2020-07-16 03:30 | 44028.1458 | 0 | 8.0426 | 39.95
2020-07-16 04:00 | 44028.1667 | 0 | 8.3171 | 39.95
2020-07-16 04:30 | 44028.1875 | 0 | 8.8622 | 39.95
2020-07-16 05:00 | 44028.2083 | 0 | 9.7634 | 39.95
2020-07-16 05:30 | 44028.2292 | 0 | 10.8918 | 39.95
2020-07-16 06:00 | 44028.25 | 0 | 12.3881 | 39.95
2020-07-16 06:30 | 44028.2708 | 0 | 14.0219 | 39.95
2020-07-16 07:00 | 44028.2917 | 0 | 15.3935 | 39.95
2020-07-16 07:30 | 44028.3125 | 0 | 14.9474 | 39.95
2020-07-16 08:00 | 44028.3333 | 0 | 13.8085 | 39.95
2020-07-16 08:30 | 44028.3542 | 0 | 12.7457 | 39.95
2020-07-16 09:00 | 44028.375 | 0 | 11.911 | 39.95
2020-07-16 09:30 | 44028.3958 | 0 | 11.1198 | 39.95
2020-07-16 10:00 | 44028.4167 | 0 | 10.5926 | 39.95
2020-07-16 10:30 | 44028.4375 | 0 | 10.1885 | 39.95
2020-07-16 11:00 | 44028.4583 | 0 | 9.7107 | 39.95
2020-07-16 11:30 | 44028.4792 | 0 | 9.4131 | 39.95
2020-07-16 12:00 | 44028.5 | 0 | 9.3091 | 39.95
2020-07-16 12:30 | 44028.5208 | 0 | 9.1642 | 39.95
2020-07-16 13:00 | 44028.5417 | 0 | 9.293 | 39.95
2020-07-16 13:30 | 44028.5625 | 0 | 9.5885 | 39.95
2020-07-16 14:00 | 44028.5833 | 0 | 9.9358 | 39.95
2020-07-16 14:30 | 44028.6042 | 0 | 10.0318 | 39.95
2020-07-16 15:00 | 44028.625 | 0 | 10.3534 | 39.95
2020-07-16 15:30 | 44028.6458 | 0 | 10.804 | 39.95
2020-07-16 16:00 | 44028.6667 | 0 | 11.5431 | 39.95
2020-07-16 16:30 | 44028.6875 | 0 | 12.4461 | 39.95
2020-07-16 17:00 | 44028.7083 | 0 | 13.5849 | 39.95
2020-07-16 17:30 | 44028.7292 | 0 | 14.7712 | 39.95
2020-07-16 18:00 | 44028.75 | 0 | 15.354 | 39.95
2020-07-16 18:30 | 44028.7708 | 0 | 15.666 | 39.95
2020-07-16 19:00 | 44028.7917 | 0 | 15.6077 | 39.95
2020-07-16 19:30 | 44028.8125 | 0 | 15.3158 | 39.95
2020-07-16 20:00 | 44028.8333 | 0 | 15.0395 | 39.95
2020-07-16 20:30 | 44028.8542 | 0 | 14.5012 | 39.95
2020-07-16 21:00 | 44028.875 | 0 | 13.7616 | 39.95
2020-07-16 21:30 | 44028.8958 | 0 | 13.4513 | 39.95
2020-07-16 22:00 | 44028.9167 | 0 | 12.3961 | 39.95
2020-07-16 22:30 | 44028.9375 | 0 | 11.3165 | 39.95
2020-07-16 23:00 | 44028.9583 | 0 | 10.3996 | 39.95
2020-07-16 23:30 | 44028.9792 | 0 | 9.6686 | 39.95
2020-07-17 | 44029 | 0 | 9.0505 | 39.95
2020-07-17 00:30 | 44029.0208 | 0 | 8.5892 | 39.95
2020-07-17 01:00 | 44029.0417 | 0 | 8.3725 | 39.95
2020-07-17 01:30 | 44029.0625 | 0 | 8.2253 | 39.95
2020-07-17 02:00 | 44029.0833 | 0 | 8.1068 | 39.95
2020-07-17 02:30 | 44029.1042 | 0 | 8.0173 | 39.95
2020-07-17 03:00 | 44029.125 | 0 | 7.978 | 39.95
2020-07-17 03:30 | 44029.1458 | 0 | 8.024 | 39.95
2020-07-17 04:00 | 44029.1667 | 0 | 8.3993 | 39.95
2020-07-17 04:30 | 44029.1875 | 0 | 8.846 | 39.95
2020-07-17 05:00 | 44029.2083 | 0 | 9.6117 | 39.95
2020-07-17 05:30 | 44029.2292 | 0 | 10.5743 | 39.95
2020-07-17 06:00 | 44029.25 | 0 | 12.0904 | 39.95
2020-07-17 06:30 | 44029.2708 | 0 | 13.6974 | 39.95
2020-07-17 07:00 | 44029.2917 | 0 | 14.9718 | 39.95
2020-07-17 07:30 | 44029.3125 | 0 | 14.5957 | 39.95
2020-07-17 08:00 | 44029.3333 | 0 | 13.7637 | 39.95
2020-07-17 08:30 | 44029.3542 | 0 | 13.102 | 39.95
2020-07-17 09:00 | 44029.375 | 0 | 11.9791 | 39.95
2020-07-17 09:30 | 44029.3958 | 0 | 11.2174 | 39.95
2020-07-17 10:00 | 44029.4167 | 0 | 10.6037 | 39.95
2020-07-17 10:30 | 44029.4375 | 0 | 10.0456 | 39.95
2020-07-17 11:00 | 44029.4583 | 0 | 9.697 | 39.95
2020-07-17 11:30 | 44029.4792 | 0 | 9.476 | 39.95
2020-07-17 12:00 | 44029.5 | 0 | 9.208 | 39.95
2020-07-17 12:30 | 44029.5208 | 0 | 9.1362 | 39.95
2020-07-17 13:00 | 44029.5417 | 0 | 9.1565 | 39.95
2020-07-17 13:30 | 44029.5625 | 0 | 9.3345 | 39.95
2020-07-17 14:00 | 44029.5833 | 0 | 9.7131 | 39.95
2020-07-17 14:30 | 44029.6042 | 0 | 9.8942 | 39.95
2020-07-17 15:00 | 44029.625 | 0 | 10.3445 | 39.95
2020-07-17 15:30 | 44029.6458 | 0 | 11.1712 | 39.95
2020-07-17 16:00 | 44029.6667 | 0 | 11.766 | 39.95
2020-07-17 16:30 | 44029.6875 | 0 | 12.4689 | 39.95
2020-07-17 17:00 | 44029.7083 | 0 | 12.9202 | 39.95
2020-07-17 17:30 | 44029.7292 | 0 | 13.9265 | 39.95
2020-07-17 18:00 | 44029.75 | 0 | 14.2757 | 39.95
2020-07-17 18:30 | 44029.7708 | 0 | 14.6264 | 39.95
2020-07-17 19:00 | 44029.7917 | 0 | 14.4047 | 39.95
2020-07-17 19:30 | 44029.8125 | 0 | 14.3117 | 39.95
2020-07-17 20:00 | 44029.8333 | 0 | 14.2381 | 39.95
2020-07-17 20:30 | 44029.8542 | 0 | 13.5268 | 39.95
2020-07-17 21:00 | 44029.875 | 0 | 13.1556 | 39.95
2020-07-17 21:30 | 44029.8958 | 0 | 12.7666 | 39.95
2020-07-17 22:00 | 44029.9167 | 0 | 12.2295 | 39.95
2020-07-17 22:30 | 44029.9375 | 0 | 11.2402 | 39.95
2020-07-17 23:00 | 44029.9583 | 0 | 10.6443 | 39.95
2020-07-17 23:30 | 44029.9792 | 0 | 9.88 | 39.95
2020-07-18 | 44030 | 0 | 9.2102 | 39.95
2020-07-18 00:30 | 44030.0208 | 0 | 8.7514 | 39.95
2020-07-18 01:00 | 44030.0417 | 0 | 8.4629 | 39.95
2020-07-18 01:30 | 44030.0625 | 0 | 8.1514 | 39.95
2020-07-18 02:00 | 44030.0833 | 0 | 8.1291 | 39.95
2020-07-18 02:30 | 44030.1042 | 0 | 8.0794 | 39.95
2020-07-18 03:00 | 44030.125 | 0 | 7.9619 | 39.95
2020-07-18 03:30 | 44030.1458 | 0 | 7.9504 | 39.95
2020-07-18 04:00 | 44030.1667 | 0 | 7.9504 | 39.95
2020-07-18 04:30 | 44030.1875 | 0 | 8.1037 | 39.95
2020-07-18 05:00 | 44030.2083 | 0 | 8.5146 | 39.95
2020-07-18 05:30 | 44030.2292 | 0 | 8.7576 | 39.95
2020-07-18 06:00 | 44030.25 | 0 | 9.0897 | 39.95
2020-07-18 06:30 | 44030.2708 | 0 | 9.695 | 39.95
2020-07-18 07:00 | 44030.2917 | 0 | 10.3072 | 39.95
2020-07-18 07:30 | 44030.3125 | 0 | 10.3654 | 39.95
2020-07-18 08:00 | 44030.3333 | 0 | 10.2942 | 39.95
2020-07-18 08:30 | 44030.3542 | 0 | 10.1437 | 39.95
2020-07-18 09:00 | 44030.375 | 0 | 9.5331 | 39.95
2020-07-18 09:30 | 44030.3958 | 0 | 8.9712 | 39.95
2020-07-18 10:00 | 44030.4167 | 0 | 8.2741 | 39.95
2020-07-18 10:30 | 44030.4375 | 0 | 8.0841 | 39.95
2020-07-18 11:00 | 44030.4583 | 0 | 7.4894 | 39.95
2020-07-18 11:30 | 44030.4792 | 0 | 7.1717 | 39.95
2020-07-18 12:00 | 44030.5 | 0 | 7.0794 | 39.95
2020-07-18 12:30 | 44030.5208 | 0 | 6.8186 | 39.95
2020-07-18 13:00 | 44030.5417 | 0 | 6.9953 | 39.95
2020-07-18 13:30 | 44030.5625 | 0 | 7.1906 | 39.95
2020-07-18 14:00 | 44030.5833 | 0 | 7.5324 | 39.95
2020-07-18 14:30 | 44030.6042 | 0 | 7.8799 | 39.95
2020-07-18 15:00 | 44030.625 | 0 | 8.1672 | 39.95
2020-07-18 15:30 | 44030.6458 | 0 | 8.7715 | 39.95
2020-07-18 16:00 | 44030.6667 | 0 | 9.5197 | 39.95
2020-07-18 16:30 | 44030.6875 | 0 | 10.2809 | 39.95
2020-07-18 17:00 | 44030.7083 | 0 | 10.8155 | 39.95
2020-07-18 17:30 | 44030.7292 | 0 | 11.695 | 39.95
2020-07-18 18:00 | 44030.75 | 0 | 11.9425 | 39.95
2020-07-18 18:30 | 44030.7708 | 0 | 12.1632 | 39.95
2020-07-18 19:00 | 44030.7917 | 0 | 12.0529 | 39.95
2020-07-18 19:30 | 44030.8125 | 0 | 11.7395 | 39.95
2020-07-18 20:00 | 44030.8333 | 0 | 11.5075 | 39.95
2020-07-18 20:30 | 44030.8542 | 0 | 11.0669 | 39.95
2020-07-18 21:00 | 44030.875 | 0 | 10.6787 | 39.95
2020-07-18 21:30 | 44030.8958 | 0 | 10.438 | 39.95
2020-07-18 22:00 | 44030.9167 | 0 | 10.0809 | 39.95
2020-07-18 22:30 | 44030.9375 | 0 | 9.511 | 39.95
2020-07-18 23:00 | 44030.9583 | 0 | 9.0382 | 39.95
2020-07-18 23:30 | 44030.9792 | 0 | 8.5468 | 39.95
2020-07-19 | 44031 | 0 | 8.077 | 39.95
2020-07-19 00:30 | 44031.0208 | 0 | 7.693 | 39.95
2020-07-19 01:00 | 44031.0417 | 0 | 7.5037 | 39.95
2020-07-19 01:30 | 44031.0625 | 0 | 7.2567 | 39.95
2020-07-19 02:00 | 44031.0833 | 0 | 7.2934 | 39.95
2020-07-19 02:30 | 44031.1042 | 0 | 7.3109 | 39.95
2020-07-19 03:00 | 44031.125 | 0 | 7.1837 | 39.95
2020-07-19 03:30 | 44031.1458 | 0 | 7.0333 | 39.95
2020-07-19 04:00 | 44031.1667 | 0 | 7.0088 | 39.95
2020-07-19 04:30 | 44031.1875 | 0 | 7.0845 | 39.95
2020-07-19 05:00 | 44031.2083 | 0 | 7.2512 | 39.95
2020-07-19 05:30 | 44031.2292 | 0 | 7.5246 | 39.95
2020-07-19 06:00 | 44031.25 | 0 | 7.9468 | 39.95
2020-07-19 06:30 | 44031.2708 | 0 | 8.3246 | 39.95
2020-07-19 07:00 | 44031.2917 | 0 | 8.8196 | 39.95
2020-07-19 07:30 | 44031.3125 | 0 | 8.9742 | 39.95
2020-07-19 08:00 | 44031.3333 | 0 | 9.1138 | 39.95
2020-07-19 08:30 | 44031.3542 | 0 | 8.9144 | 39.95
2020-07-19 09:00 | 44031.375 | 0 | 8.4919 | 39.95
2020-07-19 09:30 | 44031.3958 | 0 | 8.0114 | 39.95
2020-07-19 10:00 | 44031.4167 | 0 | 7.606 | 39.95
2020-07-19 10:30 | 44031.4375 | 0 | 7.2852 | 39.95
2020-07-19 11:00 | 44031.4583 | 0 | 6.8323 | 39.95
2020-07-19 11:30 | 44031.4792 | 0 | 6.5374 | 39.95
2020-07-19 12:00 | 44031.5 | 0 | 6.4714 | 39.95
2020-07-19 12:30 | 44031.5208 | 0 | 6.3597 | 39.95
2020-07-19 13:00 | 44031.5417 | 0 | 6.4541 | 39.95
2020-07-19 13:30 | 44031.5625 | 0 | 6.5672 | 39.95
2020-07-19 14:00 | 44031.5833 | 0 | 7.1359 | 39.95
2020-07-19 14:30 | 44031.6042 | 0 | 7.6452 | 39.95
2020-07-19 15:00 | 44031.625 | 0 | 8.0415 | 39.95
2020-07-19 15:30 | 44031.6458 | 0 | 8.6706 | 39.95
2020-07-19 16:00 | 44031.6667 | 0 | 9.4847 | 39.95
2020-07-19 16:30 | 44031.6875 | 0 | 10.2591 | 39.95
2020-07-19 17:00 | 44031.7083 | 0 | 10.9817 | 39.95
2020-07-19 17:30 | 44031.7292 | 0 | 12.2112 | 39.95
2020-07-19 18:00 | 44031.75 | 0 | 12.6728 | 39.95
2020-07-19 18:30 | 44031.7708 | 0 | 12.7385 | 39.95
2020-07-19 19:00 | 44031.7917 | 0 | 12.3374 | 39.95
2020-07-19 19:30 | 44031.8125 | 0 | 12.0532 | 39.95
2020-07-19 20:00 | 44031.8333 | 0 | 11.7772 | 39.95
2020-07-19 20:30 | 44031.8542 | 0 | 11.2471 | 39.95
2020-07-19 21:00 | 44031.875 | 0 | 10.6562 | 39.95
2020-07-19 21:30 | 44031.8958 | 0 | 10.3146 | 39.95
2020-07-19 22:00 | 44031.9167 | 0 | 9.8903 | 39.95
2020-07-19 22:30 | 44031.9375 | 0 | 9.1222 | 39.95
2020-07-19 23:00 | 44031.9583 | 0 | 8.6044 | 39.95
2020-07-19 23:30 | 44031.9792 | 0 | 8.0803 | 39.95
2020-07-20 | 44032 | 0 | 7.8606 | 39.95
2020-07-20 00:30 | 44032.0208 | 0 | 7.5693 | 39.95
2020-07-20 01:00 | 44032.0417 | 0 | 7.3325 | 39.95
2020-07-20 01:30 | 44032.0625 | 0 | 7.1924 | 39.95
2020-07-20 02:00 | 44032.0833 | 0 | 7.266 | 39.95
2020-07-20 02:30 | 44032.1042 | 0 | 7.2291 | 39.95
2020-07-20 03:00 | 44032.125 | 0 | 7.1527 | 39.95
2020-07-20 03:30 | 44032.1458 | 0 | 7.2872 | 39.95
2020-07-20 04:00 | 44032.1667 | 0 | 7.4157 | 39.95
2020-07-20 04:30 | 44032.1875 | 0 | 8.0831 | 39.95
2020-07-20 05:00 | 44032.2083 | 0 | 8.9521 | 39.95
2020-07-20 05:30 | 44032.2292 | 0 | 9.9826 | 39.95
2020-07-20 06:00 | 44032.25 | 0 | 11.3987 | 39.95
2020-07-20 06:30 | 44032.2708 | 0 | 12.8733 | 39.95
2020-07-20 07:00 | 44032.2917 | 0 | 13.9044 | 39.95
2020-07-20 07:30 | 44032.3125 | 0 | 13.8333 | 39.95
2020-07-20 08:00 | 44032.3333 | 0 | 13.1328 | 39.95
2020-07-20 08:30 | 44032.3542 | 0 | 12.3455 | 39.95
2020-07-20 09:00 | 44032.375 | 0 | 11.3816 | 39.95
2020-07-20 09:30 | 44032.3958 | 0 | 10.66 | 39.95
2020-07-20 10:00 | 44032.4167 | 0 | 10.2053 | 39.95
2020-07-20 10:30 | 44032.4375 | 0 | 9.8879 | 39.95
2020-07-20 11:00 | 44032.4583 | 0 | 9.398 | 39.95
2020-07-20 11:30 | 44032.4792 | 0 | 9.366 | 39.95
2020-07-20 12:00 | 44032.5 | 0 | 9.3202 | 39.95
2020-07-20 12:30 | 44032.5208 | 0 | 9.1434 | 39.95
2020-07-20 13:00 | 44032.5417 | 0 | 9.3257 | 39.95
2020-07-20 13:30 | 44032.5625 | 0 | 9.484 | 39.95
2020-07-20 14:00 | 44032.5833 | 0 | 9.8752 | 39.95
2020-07-20 14:30 | 44032.6042 | 0 | 10.2128 | 39.95
2020-07-20 15:00 | 44032.625 | 0 | 10.7115 | 39.95
2020-07-20 15:30 | 44032.6458 | 0 | 11.155 | 39.95
2020-07-20 16:00 | 44032.6667 | 0 | 11.6664 | 39.95
2020-07-20 16:30 | 44032.6875 | 0 | 12.2836 | 39.95
2020-07-20 17:00 | 44032.7083 | 0 | 13.1128 | 39.95
2020-07-20 17:30 | 44032.7292 | 0 | 14.2901 | 39.95
2020-07-20 18:00 | 44032.75 | 0 | 14.9503 | 39.95
2020-07-20 18:30 | 44032.7708 | 0 | 14.9684 | 39.95
2020-07-20 19:00 | 44032.7917 | 0 | 14.6151 | 39.95
2020-07-20 19:30 | 44032.8125 | 0 | 14.1984 | 39.95
2020-07-20 20:00 | 44032.8333 | 0 | 13.8782 | 39.95
2020-07-20 20:30 | 44032.8542 | 0 | 13.3135 | 39.95
2020-07-20 21:00 | 44032.875 | 0 | 12.6698 | 39.95
2020-07-20 21:30 | 44032.8958 | 0 | 12.2713 | 39.95
2020-07-20 22:00 | 44032.9167 | 0 | 11.6635 | 39.95
2020-07-20 22:30 | 44032.9375 | 0 | 10.5217 | 39.95
2020-07-20 23:00 | 44032.9583 | 0 | 9.8095 | 39.95
2020-07-20 23:30 | 44032.9792 | 0 | 9.2379 | 39.95
2020-07-21 | 44033 | 0 | 8.5039 | 39.95
2020-07-21 00:30 | 44033.0208 | 0 | 8.035 | 39.95
2020-07-21 01:00 | 44033.0417 | 0 | 7.7786 | 39.95
2020-07-21 01:30 | 44033.0625 | 0 | 7.6378 | 39.95
2020-07-21 02:00 | 44033.0833 | 0 | 7.6155 | 39.95
2020-07-21 02:30 | 44033.1042 | 0 | 7.5931 | 39.95
2020-07-21 03:00 | 44033.125 | 0 | 7.6155 | 39.95
2020-07-21 03:30 | 44033.1458 | 0 | 7.6464 | 39.95
2020-07-21 04:00 | 44033.1667 | 0 | 7.7612 | 39.95
2020-07-21 04:30 | 44033.1875 | 0 | 8.3004 | 39.95
2020-07-21 05:00 | 44033.2083 | 0 | 9.1443 | 39.95
2020-07-21 05:30 | 44033.2292 | 0 | 9.9307 | 39.95
2020-07-21 06:00 | 44033.25 | 0 | 11.4644 | 39.95
2020-07-21 06:30 | 44033.2708 | 0 | 12.8515 | 39.95
2020-07-21 07:00 | 44033.2917 | 0 | 14.0619 | 39.95
2020-07-21 07:30 | 44033.3125 | 0 | 14.1986 | 39.95
2020-07-21 08:00 | 44033.3333 | 0 | 13.6834 | 39.95
2020-07-21 08:30 | 44033.3542 | 0 | 13.316 | 39.95
2020-07-21 09:00 | 44033.375 | 0 | 12.4324 | 39.95
2020-07-21 09:30 | 44033.3958 | 0 | 11.6311 | 39.95
2020-07-21 10:00 | 44033.4167 | 0 | 11.4247 | 39.95
2020-07-21 10:30 | 44033.4375 | 0 | 10.4823 | 39.95
2020-07-21 11:00 | 44033.4583 | 0 | 9.7467 | 39.95
2020-07-21 11:30 | 44033.4792 | 0 | 9.2562 | 39.95
2020-07-21 12:00 | 44033.5 | 0 | 9.6847 | 39.95
2020-07-21 12:30 | 44033.5208 | 0 | 10.3828 | 39.95
2020-07-21 13:00 | 44033.5417 | 0 | 10.2782 | 39.95
2020-07-21 13:30 | 44033.5625 | 0 | 10.4359 | 39.95
2020-07-21 14:00 | 44033.5833 | 0 | 10.2494 | 39.95
2020-07-21 14:30 | 44033.6042 | 0 | 11.325 | 39.95
2020-07-21 15:00 | 44033.625 | 0 | 11.3233 | 39.95
2020-07-21 15:30 | 44033.6458 | 0 | 11.6496 | 39.95
2020-07-21 16:00 | 44033.6667 | 0 | 12.2549 | 39.95
2020-07-21 16:30 | 44033.6875 | 0 | 12.9949 | 39.95
2020-07-21 17:00 | 44033.7083 | 0 | 13.9015 | 39.95
2020-07-21 17:30 | 44033.7292 | 0 | 15.0032 | 39.95
2020-07-21 18:00 | 44033.75 | 0 | 15.2842 | 39.95
2020-07-21 18:30 | 44033.7708 | 0 | 15.5435 | 39.95
2020-07-21 19:00 | 44033.7917 | 0 | 15.2654 | 39.95
2020-07-21 19:30 | 44033.8125 | 0 | 14.7604 | 39.95
2020-07-21 20:00 | 44033.8333 | 0 | 14.5972 | 39.95
2020-07-21 20:30 | 44033.8542 | 0 | 13.9955 | 39.95
2020-07-21 21:00 | 44033.875 | 0 | 13.1869 | 39.95
2020-07-21 21:30 | 44033.8958 | 0 | 12.5916 | 39.95
2020-07-21 22:00 | 44033.9167 | 0 | 11.7414 | 39.95
2020-07-21 22:30 | 44033.9375 | 0 | 10.8451 | 39.95
2020-07-21 23:00 | 44033.9583 | 0 | 10.0025 | 39.95
2020-07-21 23:30 | 44033.9792 | 0 | 9.3751 | 39.95
2020-07-22 | 44034 | 0 | 8.765 | 39.95
2020-07-22 00:30 | 44034.0208 | 0 | 8.4002 | 39.95
2020-07-22 01:00 | 44034.0417 | 0 | 8.1101 | 39.95
2020-07-22 01:30 | 44034.0625 | 0 | 7.99 | 39.95
2020-07-22 02:00 | 44034.0833 | 0 | 7.887 | 39.95
2020-07-22 02:30 | 44034.1042 | 0 | 7.902 | 39.95
2020-07-22 03:00 | 44034.125 | 0 | 7.8474 | 39.95
2020-07-22 03:30 | 44034.1458 | 0 | 7.8748 | 39.95
2020-07-22 04:00 | 44034.1667 | 0 | 8.2215 | 39.95
2020-07-22 04:30 | 44034.1875 | 0 | 8.6389 | 39.95
2020-07-22 05:00 | 44034.2083 | 0 | 9.2867 | 39.95
2020-07-22 05:30 | 44034.2292 | 0 | 10.3702 | 39.95
2020-07-22 06:00 | 44034.25 | 0 | 11.5864 | 39.95
2020-07-22 06:30 | 44034.2708 | 0 | 13.0615 | 39.95
2020-07-22 07:00 | 44034.2917 | 0 | 14.3188 | 39.95
2020-07-22 07:30 | 44034.3125 | 0 | 14.379 | 39.95
2020-07-22 08:00 | 44034.3333 | 0 | 14.2799 | 39.95
2020-07-22 08:30 | 44034.3542 | 0 | 14.2655 | 39.95
2020-07-22 09:00 | 44034.375 | 0 | 13.7436 | 39.95
2020-07-22 09:30 | 44034.3958 | 0 | 13.4739 | 39.95
2020-07-22 10:00 | 44034.4167 | 0 | 13.8264 | 39.95
2020-07-22 10:30 | 44034.4375 | 0 | 13.7295 | 39.95
2020-07-22 11:00 | 44034.4583 | 0 | 13.2773 | 39.95
2020-07-22 11:30 | 44034.4792 | 0 | 12.847 | 39.95
2020-07-22 12:00 | 44034.5 | 0 | 12.2161 | 39.95
2020-07-22 12:30 | 44034.5208 | 0 | 12.3927 | 39.95
2020-07-22 13:00 | 44034.5417 | 0 | 12.5509 | 39.95
2020-07-22 13:30 | 44034.5625 | 0 | 12.7388 | 39.95
2020-07-22 14:00 | 44034.5833 | 0 | 12.8547 | 39.95
2020-07-22 14:30 | 44034.6042 | 0 | 12.4668 | 39.95
2020-07-22 15:00 | 44034.625 | 0 | 12.4981 | 39.95
2020-07-22 15:30 | 44034.6458 | 0 | 12.9517 | 39.95
2020-07-22 16:00 | 44034.6667 | 0 | 13.3031 | 39.95
2020-07-22 16:30 | 44034.6875 | 0 | 14.0533 | 39.95
2020-07-22 17:00 | 44034.7083 | 0 | 14.7623 | 39.95
2020-07-22 17:30 | 44034.7292 | 0 | 15.6461 | 39.95
2020-07-22 18:00 | 44034.75 | 0 | 16.0732 | 39.95
2020-07-22 18:30 | 44034.7708 | 0 | 16.2788 | 39.95
2020-07-22 19:00 | 44034.7917 | 0 | 15.9418 | 39.95
2020-07-22 19:30 | 44034.8125 | 0 | 15.5799 | 39.95
2020-07-22 20:00 | 44034.8333 | 0 | 15.1129 | 39.95
2020-07-22 20:30 | 44034.8542 | 0 | 14.4372 | 39.95
2020-07-22 21:00 | 44034.875 | 0 | 13.7998 | 39.95
2020-07-22 21:30 | 44034.8958 | 0 | 13.1766 | 39.95
2020-07-22 22:00 | 44034.9167 | 0 | 12.1976 | 39.95
2020-07-22 22:30 | 44034.9375 | 0 | 11.3232 | 39.95
2020-07-22 23:00 | 44034.9583 | 0 | 10.2812 | 39.95
2020-07-22 23:30 | 44034.9792 | 0 | 9.588 | 39.95
2020-07-23 | 44035 | 0 | 9.0343 | 39.95
2020-07-23 00:30 | 44035.0208 | 0 | 8.6742 | 39.95
2020-07-23 01:00 | 44035.0417 | 0 | 8.3536 | 39.95
2020-07-23 01:30 | 44035.0625 | 0 | 8.101 | 39.95
2020-07-23 02:00 | 44035.0833 | 0 | 7.9696 | 39.95
2020-07-23 02:30 | 44035.1042 | 0 | 7.9266 | 39.95
2020-07-23 03:00 | 44035.125 | 0 | 7.9265 | 39.95
2020-07-23 03:30 | 44035.1458 | 0 | 7.9312 | 39.95
2020-07-23 04:00 | 44035.1667 | 0 | 8.1558 | 39.95
2020-07-23 04:30 | 44035.1875 | 0 | 8.6919 | 39.95
2020-07-23 05:00 | 44035.2083 | 0 | 9.5322 | 39.95
2020-07-23 05:30 | 44035.2292 | 0 | 10.4492 | 39.95
2020-07-23 06:00 | 44035.25 | 0 | 11.8821 | 39.95
2020-07-23 06:30 | 44035.2708 | 0 | 13.2021 | 39.95
2020-07-23 07:00 | 44035.2917 | 0 | 14.4038 | 39.95
2020-07-23 07:30 | 44035.3125 | 0 | 14.8265 | 39.95
2020-07-23 08:00 | 44035.3333 | 0 | 14.594 | 39.95
2020-07-23 08:30 | 44035.3542 | 0 | 14.3971 | 39.95
2020-07-23 09:00 | 44035.375 | 0 | 14.3898 | 39.95
2020-07-23 09:30 | 44035.3958 | 0 | 14.1128 | 39.95
2020-07-23 10:00 | 44035.4167 | 0 | 13.867 | 39.95
2020-07-23 10:30 | 44035.4375 | 0 | 13.7315 | 39.95
2020-07-23 11:00 | 44035.4583 | 0 | 13.4001 | 39.95
2020-07-23 11:30 | 44035.4792 | 0 | 13.0902 | 39.95
2020-07-23 12:00 | 44035.5 | 0 | 13.2209 | 39.95
2020-07-23 12:30 | 44035.5208 | 0 | 13.0822 | 39.95
2020-07-23 13:00 | 44035.5417 | 0 | 13.0245 | 39.95
2020-07-23 13:30 | 44035.5625 | 0 | 13.398 | 39.95
2020-07-23 14:00 | 44035.5833 | 0 | 13.7154 | 39.95
2020-07-23 14:30 | 44035.6042 | 0 | 13.6613 | 39.95
2020-07-23 15:00 | 44035.625 | 0 | 13.5621 | 39.95
2020-07-23 15:30 | 44035.6458 | 0 | 14.0767 | 39.95
2020-07-23 16:00 | 44035.6667 | 0 | 14.4297 | 39.95
2020-07-23 16:30 | 44035.6875 | 0 | 14.9836 | 39.95
2020-07-23 17:00 | 44035.7083 | 0 | 15.8783 | 39.95
2020-07-23 17:30 | 44035.7292 | 0 | 16.6094 | 39.95
2020-07-23 18:00 | 44035.75 | 0 | 16.8342 | 39.95
2020-07-23 18:30 | 44035.7708 | 0 | 17.126 | 39.95
2020-07-23 19:00 | 44035.7917 | 0 | 16.8175 | 39.95
2020-07-23 19:30 | 44035.8125 | 0 | 16.3239 | 39.95
2020-07-23 20:00 | 44035.8333 | 0 | 15.7192 | 39.95
2020-07-23 20:30 | 44035.8542 | 0 | 14.9763 | 39.95
2020-07-23 21:00 | 44035.875 | 0 | 14.235 | 39.95
2020-07-23 21:30 | 44035.8958 | 0 | 13.4575 | 39.95
2020-07-23 22:00 | 44035.9167 | 0 | 12.6141 | 39.95
2020-07-23 22:30 | 44035.9375 | 0 | 11.344 | 39.95
2020-07-23 23:00 | 44035.9583 | 0 | 10.515 | 39.95
2020-07-23 23:30 | 44035.9792 | 0 | 9.8487 | 39.95
2020-07-24 | 44036 | 0 | 9.2072 | 39.95
2020-07-24 00:30 | 44036.0208 | 0 | 8.8095 | 39.95
2020-07-24 01:00 | 44036.0417 | 0 | 8.3939 | 39.95
2020-07-24 01:30 | 44036.0625 | 0 | 8.1283 | 39.95
2020-07-24 02:00 | 44036.0833 | 0 | 8.1275 | 39.95
2020-07-24 02:30 | 44036.1042 | 0 | 8.0173 | 39.95
2020-07-24 03:00 | 44036.125 | 0 | 8.059 | 39.95
2020-07-24 03:30 | 44036.1458 | 0 | 8.0636 | 39.95
2020-07-24 04:00 | 44036.1667 | 0 | 8.0917 | 39.95
2020-07-24 04:30 | 44036.1875 | 0 | 8.7365 | 39.95
2020-07-24 05:00 | 44036.2083 | 0 | 9.547 | 39.95
2020-07-24 05:30 | 44036.2292 | 0 | 10.4858 | 39.95
2020-07-24 06:00 | 44036.25 | 0 | 11.624 | 39.95
2020-07-24 06:30 | 44036.2708 | 0 | 13.2378 | 39.95
2020-07-24 07:00 | 44036.2917 | 0 | 14.243 | 39.95
2020-07-24 07:30 | 44036.3125 | 0 | 14.7142 | 39.95
2020-07-24 08:00 | 44036.3333 | 0 | 14.6872 | 39.95
2020-07-24 08:30 | 44036.3542 | 0 | 13.9571 | 39.95
2020-07-24 09:00 | 44036.375 | 0 | 13.5951 | 39.95
2020-07-24 09:30 | 44036.3958 | 0 | 13.8608 | 39.95
2020-07-24 10:00 | 44036.4167 | 0 | 13.0171 | 39.95
2020-07-24 10:30 | 44036.4375 | 0 | 12.7112 | 39.95
2020-07-24 11:00 | 44036.4583 | 0 | 12.5232 | 39.95
2020-07-24 11:30 | 44036.4792 | 0 | 11.7039 | 39.95
2020-07-24 12:00 | 44036.5 | 0 | 10.1515 | 39.95
2020-07-24 12:30 | 44036.5208 | 0 | 10.5468 | 39.95
2020-07-24 13:00 | 44036.5417 | 0 | 9.9353 | 39.95
2020-07-24 13:30 | 44036.5625 | 0 | 10.0949 | 39.95
2020-07-24 14:00 | 44036.5833 | 0 | 10.2971 | 39.95
2020-07-24 14:30 | 44036.6042 | 0 | 10.486 | 39.95
2020-07-24 15:00 | 44036.625 | 0 | 11.4551 | 39.95
2020-07-24 15:30 | 44036.6458 | 0 | 12.1125 | 39.95
2020-07-24 16:00 | 44036.6667 | 0 | 12.4125 | 39.95
2020-07-24 16:30 | 44036.6875 | 0 | 13.069 | 39.95
2020-07-24 17:00 | 44036.7083 | 0 | 13.6328 | 39.95
2020-07-24 17:30 | 44036.7292 | 0 | 14.4344 | 39.95
2020-07-24 18:00 | 44036.75 | 0 | 14.5451 | 39.95
2020-07-24 18:30 | 44036.7708 | 0 | 14.8978 | 39.95
2020-07-24 19:00 | 44036.7917 | 0 | 14.6522 | 39.95
2020-07-24 19:30 | 44036.8125 | 0 | 14.4508 | 39.95
2020-07-24 20:00 | 44036.8333 | 0 | 14.2295 | 39.95
2020-07-24 20:30 | 44036.8542 | 0 | 13.7062 | 39.95
2020-07-24 21:00 | 44036.875 | 0 | 13.1935 | 39.95
2020-07-24 21:30 | 44036.8958 | 0 | 12.5843 | 39.95
2020-07-24 22:00 | 44036.9167 | 0 | 11.967 | 39.95
2020-07-24 22:30 | 44036.9375 | 0 | 11.2199 | 39.95
2020-07-24 23:00 | 44036.9583 | 0 | 10.4162 | 39.95
2020-07-24 23:30 | 44036.9792 | 0 | 9.7758 | 39.95
2020-07-25 | 44037 | 0 | 9.2296 | 39.95
2020-07-25 00:30 | 44037.0208 | 0 | 8.6658 | 39.95
2020-07-25 01:00 | 44037.0417 | 0 | 8.2165 | 39.95
2020-07-25 01:30 | 44037.0625 | 0 | 8.1056 | 39.95
2020-07-25 02:00 | 44037.0833 | 0 | 7.9727 | 39.95
2020-07-25 02:30 | 44037.1042 | 0 | 8.0281 | 39.95
2020-07-25 03:00 | 44037.125 | 0 | 7.8522 | 39.95
2020-07-25 03:30 | 44037.1458 | 0 | 7.7863 | 39.95
2020-07-25 04:00 | 44037.1667 | 0 | 7.8823 | 39.95
2020-07-25 04:30 | 44037.1875 | 0 | 8.1391 | 39.95
2020-07-25 05:00 | 44037.2083 | 0 | 8.3821 | 39.95
2020-07-25 05:30 | 44037.2292 | 0 | 8.8018 | 39.95
2020-07-25 06:00 | 44037.25 | 0 | 9.1808 | 39.95
2020-07-25 06:30 | 44037.2708 | 0 | 9.7617 | 39.95
2020-07-25 07:00 | 44037.2917 | 0 | 10.5591 | 39.95
2020-07-25 07:30 | 44037.3125 | 0 | 10.9415 | 39.95
2020-07-25 08:00 | 44037.3333 | 0 | 11.7302 | 39.95
2020-07-25 08:30 | 44037.3542 | 0 | 12.0967 | 39.95
2020-07-25 09:00 | 44037.375 | 0 | 12.4349 | 39.95
2020-07-25 09:30 | 44037.3958 | 0 | 12.1838 | 39.95
2020-07-25 10:00 | 44037.4167 | 0 | 11.958 | 39.95
2020-07-25 10:30 | 44037.4375 | 0 | 11.4548 | 39.95
2020-07-25 11:00 | 44037.4583 | 0 | 11.53 | 39.95
2020-07-25 11:30 | 44037.4792 | 0 | 10.9772 | 39.95
2020-07-25 12:00 | 44037.5 | 0 | 10.7596 | 39.95
2020-07-25 12:30 | 44037.5208 | 0 | 10.2048 | 39.95
2020-07-25 13:00 | 44037.5417 | 0 | 9.6754 | 39.95
2020-07-25 13:30 | 44037.5625 | 0 | 10.0109 | 39.95
2020-07-25 14:00 | 44037.5833 | 0 | 10.3309 | 39.95
2020-07-25 14:30 | 44037.6042 | 0 | 11.206 | 39.95
2020-07-25 15:00 | 44037.625 | 0 | 11.4673 | 39.95
2020-07-25 15:30 | 44037.6458 | 0 | 11.3717 | 39.95
2020-07-25 16:00 | 44037.6667 | 0 | 11.4548 | 39.95
2020-07-25 16:30 | 44037.6875 | 0 | 12.0379 | 39.95
2020-07-25 17:00 | 44037.7083 | 0 | 12.519 | 39.95
2020-07-25 17:30 | 44037.7292 | 0 | 13.0413 | 39.95
2020-07-25 18:00 | 44037.75 | 0 | 13.1997 | 39.95
2020-07-25 18:30 | 44037.7708 | 0 | 13.3553 | 39.95
2020-07-25 19:00 | 44037.7917 | 0 | 12.8832 | 39.95
2020-07-25 19:30 | 44037.8125 | 0 | 12.4363 | 39.95
2020-07-25 20:00 | 44037.8333 | 0 | 12.2642 | 39.95
2020-07-25 20:30 | 44037.8542 | 0 | 11.7624 | 39.95
2020-07-25 21:00 | 44037.875 | 0 | 11.2751 | 39.95
2020-07-25 21:30 | 44037.8958 | 0 | 10.7628 | 39.95
2020-07-25 22:00 | 44037.9167 | 0 | 10.2128 | 39.95
2020-07-25 22:30 | 44037.9375 | 0 | 9.67 | 39.95
2020-07-25 23:00 | 44037.9583 | 0 | 9.2513 | 39.95
2020-07-25 23:30 | 44037.9792 | 0 | 8.6694 | 39.95
2020-07-26 | 44038 | 0 | 8.1774 | 39.95
2020-07-26 00:30 | 44038.0208 | 0 | 7.7001 | 39.95
2020-07-26 01:00 | 44038.0417 | 0 | 7.4775 | 39.95
2020-07-26 01:30 | 44038.0625 | 0 | 7.3251 | 39.95
2020-07-26 02:00 | 44038.0833 | 0 | 7.3725 | 39.95
2020-07-26 02:30 | 44038.1042 | 0 | 7.3523 | 39.95
2020-07-26 03:00 | 44038.125 | 0 | 7.2013 | 39.95
2020-07-26 03:30 | 44038.1458 | 0 | 7.1144 | 39.95
2020-07-26 04:00 | 44038.1667 | 0 | 6.9689 | 39.95
2020-07-26 04:30 | 44038.1875 | 0 | 7.0794 | 39.95
2020-07-26 05:00 | 44038.2083 | 0 | 7.2596 | 39.95
2020-07-26 05:30 | 44038.2292 | 0 | 7.4603 | 39.95
2020-07-26 06:00 | 44038.25 | 0 | 7.7072 | 39.95
2020-07-26 06:30 | 44038.2708 | 0 | 7.8845 | 39.95
2020-07-26 07:00 | 44038.2917 | 0 | 8.2808 | 39.95
2020-07-26 07:30 | 44038.3125 | 0 | 8.6986 | 39.95
2020-07-26 08:00 | 44038.3333 | 0 | 9.1659 | 39.95
2020-07-26 08:30 | 44038.3542 | 0 | 9.3558 | 39.95
2020-07-26 09:00 | 44038.375 | 0 | 9.3424 | 39.95
2020-07-26 09:30 | 44038.3958 | 0 | 8.9399 | 39.95
2020-07-26 10:00 | 44038.4167 | 0 | 8.6043 | 39.95
2020-07-26 10:30 | 44038.4375 | 0 | 9.0647 | 39.95
2020-07-26 11:00 | 44038.4583 | 0 | 10.1257 | 39.95
2020-07-26 11:30 | 44038.4792 | 0 | 9.8262 | 39.95
2020-07-26 12:00 | 44038.5 | 0 | 9.2814 | 39.95
2020-07-26 12:30 | 44038.5208 | 0 | 7.4561 | 39.95
2020-07-26 13:00 | 44038.5417 | 0 | 7.3087 | 39.95
2020-07-26 13:30 | 44038.5625 | 0 | 7.588 | 39.95
2020-07-26 14:00 | 44038.5833 | 0 | 7.4229 | 39.95
2020-07-26 14:30 | 44038.6042 | 0 | 7.6996 | 39.95
2020-07-26 15:00 | 44038.625 | 0 | 8.2871 | 39.95
2020-07-26 15:30 | 44038.6458 | 0 | 9.1891 | 39.95
2020-07-26 16:00 | 44038.6667 | 0 | 10.7114 | 39.95
2020-07-26 16:30 | 44038.6875 | 0 | 11.4514 | 39.95
2020-07-26 17:00 | 44038.7083 | 0 | 11.7878 | 39.95
2020-07-26 17:30 | 44038.7292 | 0 | 12.5613 | 39.95
2020-07-26 18:00 | 44038.75 | 0 | 13.0157 | 39.95
2020-07-26 18:30 | 44038.7708 | 0 | 13.0987 | 39.95
2020-07-26 19:00 | 44038.7917 | 0 | 12.8373 | 39.95
2020-07-26 19:30 | 44038.8125 | 0 | 12.4499 | 39.95
2020-07-26 20:00 | 44038.8333 | 0 | 12.3967 | 39.95
2020-07-26 20:30 | 44038.8542 | 0 | 11.771 | 39.95
2020-07-26 21:00 | 44038.875 | 0 | 11.1766 | 39.95
2020-07-26 21:30 | 44038.8958 | 0 | 10.7181 | 39.95
2020-07-26 22:00 | 44038.9167 | 0 | 10.1955 | 39.95
2020-07-26 22:30 | 44038.9375 | 0 | 9.4393 | 39.95
2020-07-26 23:00 | 44038.9583 | 0 | 8.8587 | 39.95
2020-07-26 23:30 | 44038.9792 | 0 | 8.4043 | 39.95
2020-07-27 | 44039 | 0 | 7.8928 | 39.95
2020-07-27 00:30 | 44039.0208 | 0 | 7.5966 | 39.95
2020-07-27 01:00 | 44039.0417 | 0 | 7.3764 | 39.95
2020-07-27 01:30 | 44039.0625 | 0 | 7.4015 | 39.95
2020-07-27 02:00 | 44039.0833 | 0 | 7.392 | 39.95
2020-07-27 02:30 | 44039.1042 | 0 | 7.438 | 39.95
2020-07-27 03:00 | 44039.125 | 0 | 7.3698 | 39.95
2020-07-27 03:30 | 44039.1458 | 0 | 7.3146 | 39.95
2020-07-27 04:00 | 44039.1667 | 0 | 7.6832 | 39.95
2020-07-27 04:30 | 44039.1875 | 0 | 8.1062 | 39.95
2020-07-27 05:00 | 44039.2083 | 0 | 8.9173 | 39.95
2020-07-27 05:30 | 44039.2292 | 0 | 9.942 | 39.95
2020-07-27 06:00 | 44039.25 | 0 | 11.5031 | 39.95
2020-07-27 06:30 | 44039.2708 | 0 | 12.7755 | 39.95
2020-07-27 07:00 | 44039.2917 | 0 | 13.8282 | 39.95
2020-07-27 07:30 | 44039.3125 | 0 | 13.4334 | 39.95
2020-07-27 08:00 | 44039.3333 | 0 | 12.676 | 39.95
2020-07-27 08:30 | 44039.3542 | 0 | 11.9636 | 39.95
2020-07-27 09:00 | 44039.375 | 0 | 11.2395 | 39.95
2020-07-27 09:30 | 44039.3958 | 0 | 11.6727 | 39.95
2020-07-27 10:00 | 44039.4167 | 0 | 11.3303 | 39.95
2020-07-27 10:30 | 44039.4375 | 0 | 11.6965 | 39.95
2020-07-27 11:00 | 44039.4583 | 0 | 11.7617 | 39.95
2020-07-27 11:30 | 44039.4792 | 0 | 12.2832 | 39.95
2020-07-27 12:00 | 44039.5 | 0 | 10.8369 | 39.95
2020-07-27 12:30 | 44039.5208 | 0 | 10.0617 | 39.95
2020-07-27 13:00 | 44039.5417 | 0 | 11.1267 | 39.95
2020-07-27 13:30 | 44039.5625 | 0 | 9.9972 | 39.95
2020-07-27 14:00 | 44039.5833 | 0 | 10.8465 | 39.95
2020-07-27 14:30 | 44039.6042 | 0 | 11.3911 | 39.95
2020-07-27 15:00 | 44039.625 | 0 | 11.5636 | 39.95
2020-07-27 15:30 | 44039.6458 | 0 | 12.024 | 39.95
2020-07-27 16:00 | 44039.6667 | 0 | 12.428 | 39.95
2020-07-27 16:30 | 44039.6875 | 0 | 13.3043 | 39.95
2020-07-27 17:00 | 44039.7083 | 0 | 13.9304 | 39.95
2020-07-27 17:30 | 44039.7292 | 0 | 15.2523 | 39.95
2020-07-27 18:00 | 44039.75 | 0 | 15.6446 | 39.95
2020-07-27 18:30 | 44039.7708 | 0 | 15.9424 | 39.95
2020-07-27 19:00 | 44039.7917 | 0 | 15.9145 | 39.95
2020-07-27 19:30 | 44039.8125 | 0 | 15.4705 | 39.95
2020-07-27 20:00 | 44039.8333 | 0 | 14.9328 | 39.95
2020-07-27 20:30 | 44039.8542 | 0 | 14.1568 | 39.95
2020-07-27 21:00 | 44039.875 | 0 | 13.3804 | 39.95
2020-07-27 21:30 | 44039.8958 | 0 | 12.7405 | 39.95
2020-07-27 22:00 | 44039.9167 | 0 | 11.9918 | 39.95
2020-07-27 22:30 | 44039.9375 | 0 | 10.9403 | 39.95
2020-07-27 23:00 | 44039.9583 | 0 | 10.2835 | 39.95
2020-07-27 23:30 | 44039.9792 | 0 | 9.5543 | 39.95
2020-07-28 | 44040 | 0 | 8.8456 | 39.95
2020-07-28 00:30 | 44040.0208 | 0 | 8.4066 | 39.95
2020-07-28 01:00 | 44040.0417 | 0 | 8.1638 | 39.95
2020-07-28 01:30 | 44040.0625 | 0 | 7.9821 | 39.95
2020-07-28 02:00 | 44040.0833 | 0 | 7.9738 | 39.95
2020-07-28 02:30 | 44040.1042 | 0 | 7.9587 | 39.95
2020-07-28 03:00 | 44040.125 | 0 | 7.8164 | 39.95
2020-07-28 03:30 | 44040.1458 | 0 | 7.8846 | 39.95
2020-07-28 04:00 | 44040.1667 | 0 | 7.9751 | 39.95
2020-07-28 04:30 | 44040.1875 | 0 | 8.5953 | 39.95
2020-07-28 05:00 | 44040.2083 | 0 | 9.3789 | 39.95
2020-07-28 05:30 | 44040.2292 | 0 | 10.4306 | 39.95
2020-07-28 06:00 | 44040.25 | 0 | 11.7889 | 39.95
2020-07-28 06:30 | 44040.2708 | 0 | 13.1256 | 39.95
2020-07-28 07:00 | 44040.2917 | 0 | 13.7708 | 39.95
2020-07-28 07:30 | 44040.3125 | 0 | 13.5338 | 39.95
2020-07-28 08:00 | 44040.3333 | 0 | 12.6171 | 39.95
2020-07-28 08:30 | 44040.3542 | 0 | 11.9459 | 39.95
2020-07-28 09:00 | 44040.375 | 0 | 11.1217 | 39.95
2020-07-28 09:30 | 44040.3958 | 0 | 10.3146 | 39.95
2020-07-28 10:00 | 44040.4167 | 0 | 9.7161 | 39.95
2020-07-28 10:30 | 44040.4375 | 0 | 9.456 | 39.95
2020-07-28 11:00 | 44040.4583 | 0 | 9.2299 | 39.95
2020-07-28 11:30 | 44040.4792 | 0 | 8.9224 | 39.95
2020-07-28 12:00 | 44040.5 | 0 | 8.7528 | 39.95
2020-07-28 12:30 | 44040.5208 | 0 | 8.7559 | 39.95
2020-07-28 13:00 | 44040.5417 | 0 | 8.8078 | 39.95
2020-07-28 13:30 | 44040.5625 | 0 | 9.1724 | 39.95
2020-07-28 14:00 | 44040.5833 | 0 | 9.4033 | 39.95
2020-07-28 14:30 | 44040.6042 | 0 | 9.741 | 39.95
2020-07-28 15:00 | 44040.625 | 0 | 10.0581 | 39.95
2020-07-28 15:30 | 44040.6458 | 0 | 10.6353 | 39.95
2020-07-28 16:00 | 44040.6667 | 0 | 11.338 | 39.95
2020-07-28 16:30 | 44040.6875 | 0 | 12.0854 | 39.95
2020-07-28 17:00 | 44040.7083 | 0 | 13.0571 | 39.95
2020-07-28 17:30 | 44040.7292 | 0 | 14.1846 | 39.95
2020-07-28 18:00 | 44040.75 | 0 | 14.876 | 39.95
2020-07-28 18:30 | 44040.7708 | 0 | 15.379 | 39.95
2020-07-28 19:00 | 44040.7917 | 0 | 15.2184 | 39.95
2020-07-28 19:30 | 44040.8125 | 0 | 14.863 | 39.95
2020-07-28 20:00 | 44040.8333 | 0 | 14.7542 | 39.95
2020-07-28 20:30 | 44040.8542 | 0 | 14.2233 | 39.95
2020-07-28 21:00 | 44040.875 | 0 | 13.3813 | 39.95
2020-07-28 21:30 | 44040.8958 | 0 | 12.6795 | 39.95
2020-07-28 22:00 | 44040.9167 | 0 | 11.975 | 39.95
2020-07-28 22:30 | 44040.9375 | 0 | 11.0414 | 39.95
2020-07-28 23:00 | 44040.9583 | 0 | 10.0292 | 39.95
2020-07-28 23:30 | 44040.9792 | 0 | 9.3665 | 39.95
2020-07-29 | 44041 | 0 | 8.6133 | 39.95
2020-07-29 00:30 | 44041.0208 | 0 | 8.2669 | 39.95
2020-07-29 01:00 | 44041.0417 | 0 | 7.8694 | 39.95
2020-07-29 01:30 | 44041.0625 | 0 | 7.7122 | 39.95
2020-07-29 02:00 | 44041.0833 | 0 | 7.7345 | 39.95
2020-07-29 02:30 | 44041.1042 | 0 | 7.7043 | 39.95
2020-07-29 03:00 | 44041.125 | 0 | 7.7126 | 39.95
2020-07-29 03:30 | 44041.1458 | 0 | 7.749 | 39.95
2020-07-29 04:00 | 44041.1667 | 0 | 8.0346 | 39.95
2020-07-29 04:30 | 44041.1875 | 0 | 8.6902 | 39.95
2020-07-29 05:00 | 44041.2083 | 0 | 9.4125 | 39.95
2020-07-29 05:30 | 44041.2292 | 0 | 10.6201 | 39.95
2020-07-29 06:00 | 44041.25 | 0 | 12.116 | 39.95
2020-07-29 06:30 | 44041.2708 | 0 | 13.7179 | 39.95
2020-07-29 07:00 | 44041.2917 | 0 | 14.791 | 39.95
2020-07-29 07:30 | 44041.3125 | 0 | 14.3222 | 39.95
2020-07-29 08:00 | 44041.3333 | 0 | 13.3117 | 39.95
2020-07-29 08:30 | 44041.3542 | 0 | 12.3624 | 39.95
2020-07-29 09:00 | 44041.375 | 0 | 11.3042 | 39.95
2020-07-29 09:30 | 44041.3958 | 0 | 10.6551 | 39.95
2020-07-29 10:00 | 44041.4167 | 0 | 10.2726 | 39.95
2020-07-29 10:30 | 44041.4375 | 0 | 9.891 | 39.95
2020-07-29 11:00 | 44041.4583 | 0 | 9.4809 | 39.95
2020-07-29 11:30 | 44041.4792 | 0 | 9.4482 | 39.95
2020-07-29 12:00 | 44041.5 | 0 | 9.1211 | 39.95
2020-07-29 12:30 | 44041.5208 | 0 | 9.1011 | 39.95
2020-07-29 13:00 | 44041.5417 | 0 | 9.1548 | 39.95
2020-07-29 13:30 | 44041.5625 | 0 | 9.3766 | 39.95
2020-07-29 14:00 | 44041.5833 | 0 | 9.8245 | 39.95
2020-07-29 14:30 | 44041.6042 | 0 | 10.0388 | 39.95
2020-07-29 15:00 | 44041.625 | 0 | 10.5668 | 39.95
2020-07-29 15:30 | 44041.6458 | 0 | 10.8914 | 39.95
2020-07-29 16:00 | 44041.6667 | 0 | 11.5589 | 39.95
2020-07-29 16:30 | 44041.6875 | 0 | 12.3348 | 39.95
2020-07-29 17:00 | 44041.7083 | 0 | 12.9321 | 39.95
2020-07-29 17:30 | 44041.7292 | 0 | 14.1245 | 39.95
2020-07-29 18:00 | 44041.75 | 0 | 14.3984 | 39.95
2020-07-29 18:30 | 44041.7708 | 0 | 14.9015 | 39.95
2020-07-29 19:00 | 44041.7917 | 0 | 14.5288 | 39.95
2020-07-29 19:30 | 44041.8125 | 0 | 14.3481 | 39.95
2020-07-29 20:00 | 44041.8333 | 0 | 14.2693 | 39.95
2020-07-29 20:30 | 44041.8542 | 0 | 13.7559 | 39.95
2020-07-29 21:00 | 44041.875 | 0 | 13.0822 | 39.95
2020-07-29 21:30 | 44041.8958 | 0 | 12.5396 | 39.95
2020-07-29 22:00 | 44041.9167 | 0 | 11.8218 | 39.95
2020-07-29 22:30 | 44041.9375 | 0 | 10.9737 | 39.95
2020-07-29 23:00 | 44041.9583 | 0 | 10.2259 | 39.95
2020-07-29 23:30 | 44041.9792 | 0 | 9.4823 | 39.95
2020-07-30 | 44042 | 0 | 8.807 | 39.95
2020-07-30 00:30 | 44042.0208 | 0 | 8.3083 | 39.95
2020-07-30 01:00 | 44042.0417 | 0 | 8.1028 | 39.95
2020-07-30 01:30 | 44042.0625 | 0 | 7.9483 | 39.95
2020-07-30 02:00 | 44042.0833 | 0 | 7.8504 | 39.95
2020-07-30 02:30 | 44042.1042 | 0 | 7.8376 | 39.95
2020-07-30 03:00 | 44042.125 | 0 | 7.8176 | 39.95
2020-07-30 03:30 | 44042.1458 | 0 | 7.9069 | 39.95
2020-07-30 04:00 | 44042.1667 | 0 | 8.1999 | 39.95
2020-07-30 04:30 | 44042.1875 | 0 | 8.8488 | 39.95
2020-07-30 05:00 | 44042.2083 | 0 | 9.5133 | 39.95
2020-07-30 05:30 | 44042.2292 | 0 | 10.4782 | 39.95
2020-07-30 06:00 | 44042.25 | 0 | 11.92 | 39.95
2020-07-30 06:30 | 44042.2708 | 0 | 13.3747 | 39.95
2020-07-30 07:00 | 44042.2917 | 0 | 14.2434 | 39.95
2020-07-30 07:30 | 44042.3125 | 0 | 13.7666 | 39.95
2020-07-30 08:00 | 44042.3333 | 0 | 13.1496 | 39.95
2020-07-30 08:30 | 44042.3542 | 0 | 12.278 | 39.95
2020-07-30 09:00 | 44042.375 | 0 | 11.3564 | 39.95
2020-07-30 09:30 | 44042.3958 | 0 | 10.5546 | 39.95
2020-07-30 10:00 | 44042.4167 | 0 | 10.172 | 39.95
2020-07-30 10:30 | 44042.4375 | 0 | 9.8326 | 39.95
2020-07-30 11:00 | 44042.4583 | 0 | 9.6205 | 39.95
2020-07-30 11:30 | 44042.4792 | 0 | 9.4773 | 39.95
2020-07-30 12:00 | 44042.5 | 0 | 9.2528 | 39.95
2020-07-30 12:30 | 44042.5208 | 0 | 9.3695 | 39.95
2020-07-30 13:00 | 44042.5417 | 0 | 9.3479 | 39.95
2020-07-30 13:30 | 44042.5625 | 0 | 9.9113 | 39.95
2020-07-30 14:00 | 44042.5833 | 0 | 10.9083 | 39.95
2020-07-30 14:30 | 44042.6042 | 0 | 11.2234 | 39.95
2020-07-30 15:00 | 44042.625 | 0 | 11.9281 | 39.95
2020-07-30 15:30 | 44042.6458 | 0 | 11.8007 | 39.95
2020-07-30 16:00 | 44042.6667 | 0 | 11.9451 | 39.95
2020-07-30 16:30 | 44042.6875 | 0 | 12.3283 | 39.95
2020-07-30 17:00 | 44042.7083 | 0 | 12.8949 | 39.95
2020-07-30 17:30 | 44042.7292 | 0 | 13.9665 | 39.95
2020-07-30 18:00 | 44042.75 | 0 | 14.5212 | 39.95
2020-07-30 18:30 | 44042.7708 | 0 | 14.8312 | 39.95
2020-07-30 19:00 | 44042.7917 | 0 | 14.4725 | 39.95
2020-07-30 19:30 | 44042.8125 | 0 | 14.26 | 39.95
2020-07-30 20:00 | 44042.8333 | 0 | 14.2145 | 39.95
2020-07-30 20:30 | 44042.8542 | 0 | 13.629 | 39.95
2020-07-30 21:00 | 44042.875 | 0 | 12.9676 | 39.95
2020-07-30 21:30 | 44042.8958 | 0 | 12.3345 | 39.95
2020-07-30 22:00 | 44042.9167 | 0 | 11.8284 | 39.95
2020-07-30 22:30 | 44042.9375 | 0 | 10.9558 | 39.95
2020-07-30 23:00 | 44042.9583 | 0 | 9.9794 | 39.95
2020-07-30 23:30 | 44042.9792 | 0 | 9.2851 | 39.95
2020-07-31 | 44043 | 0 | 8.7107 | 39.95
2020-07-31 00:30 | 44043.0208 | 0 | 8.3929 | 39.95
2020-07-31 01:00 | 44043.0417 | 0 | 8.171 | 39.95
2020-07-31 01:30 | 44043.0625 | 0 | 7.9058 | 39.95
2020-07-31 02:00 | 44043.0833 | 0 | 7.9727 | 39.95
2020-07-31 02:30 | 44043.1042 | 0 | 7.9672 | 39.95
2020-07-31 03:00 | 44043.125 | 0 | 7.8295 | 39.95
2020-07-31 03:30 | 44043.1458 | 0 | 7.9552 | 39.95
2020-07-31 04:00 | 44043.1667 | 0 | 8.306 | 39.95
2020-07-31 04:30 | 44043.1875 | 0 | 8.651 | 39.95
2020-07-31 05:00 | 44043.2083 | 0 | 9.315 | 39.95
2020-07-31 05:30 | 44043.2292 | 0 | 10.3953 | 39.95
2020-07-31 06:00 | 44043.25 | 0 | 11.7488 | 39.95
2020-07-31 06:30 | 44043.2708 | 0 | 13.0858 | 39.95
2020-07-31 07:00 | 44043.2917 | 0 | 13.9384 | 39.95
2020-07-31 07:30 | 44043.3125 | 0 | 13.4424 | 39.95
2020-07-31 08:00 | 44043.3333 | 0 | 12.6166 | 39.95
2020-07-31 08:30 | 44043.3542 | 0 | 11.8752 | 39.95
2020-07-31 09:00 | 44043.375 | 0 | 11.2079 | 39.95
2020-07-31 09:30 | 44043.3958 | 0 | 10.3896 | 39.95
2020-07-31 10:00 | 44043.4167 | 0 | 9.9351 | 39.95
2020-07-31 10:30 | 44043.4375 | 0 | 9.6655 | 39.95
2020-07-31 11:00 | 44043.4583 | 0 | 9.3238 | 39.95
2020-07-31 11:30 | 44043.4792 | 0 | 9.2872 | 39.95
2020-07-31 12:00 | 44043.5 | 0 | 9.7144 | 39.95
2020-07-31 12:30 | 44043.5208 | 0 | 9.4081 | 39.95
2020-07-31 13:00 | 44043.5417 | 0 | 9.3959 | 39.95
2020-07-31 13:30 | 44043.5625 | 0 | 9.8521 | 39.95
2020-07-31 14:00 | 44043.5833 | 0 | 9.5741 | 39.95
2020-07-31 14:30 | 44043.6042 | 0 | 9.8534 | 39.95
2020-07-31 15:00 | 44043.625 | 0 | 10.2211 | 39.95
2020-07-31 15:30 | 44043.6458 | 0 | 10.8478 | 39.95
2020-07-31 16:00 | 44043.6667 | 0 | 11.4491 | 39.95
2020-07-31 16:30 | 44043.6875 | 0 | 12.1318 | 39.95
2020-07-31 17:00 | 44043.7083 | 0 | 12.7509 | 39.95
2020-07-31 17:30 | 44043.7292 | 0 | 13.5411 | 39.95
2020-07-31 18:00 | 44043.75 | 0 | 13.8766 | 39.95
2020-07-31 18:30 | 44043.7708 | 0 | 14.2572 | 39.95
2020-07-31 19:00 | 44043.7917 | 0 | 14.0159 | 39.95
2020-07-31 19:30 | 44043.8125 | 0 | 13.7562 | 39.95
2020-07-31 20:00 | 44043.8333 | 0 | 13.7156 | 39.95
2020-07-31 20:30 | 44043.8542 | 0 | 13.1884 | 39.95
2020-07-31 21:00 | 44043.875 | 0 | 12.5885 | 39.95
2020-07-31 21:30 | 44043.8958 | 0 | 12.2247 | 39.95
2020-07-31 22:00 | 44043.9167 | 0 | 11.5628 | 39.95
2020-07-31 22:30 | 44043.9375 | 0 | 10.8593 | 39.95
2020-07-31 23:00 | 44043.9583 | 0 | 9.9088 | 39.95
2020-07-31 23:30 | 44043.9792 | 0 | 9.4101 | 39.95
2020-08-01 | 44044 | 0 | 8.7558 | 39.95
2020-08-01 00:30 | 44044.0208 | 0 | 8.2432 | 39.95
2020-08-01 01:00 | 44044.0417 | 0 | 8.2293 | 39.95
2020-08-01 01:30 | 44044.0625 | 0 | 8.0913 | 39.95
2020-08-01 02:00 | 44044.0833 | 0 | 7.9247 | 39.95
2020-08-01 02:30 | 44044.1042 | 0 | 7.8836 | 39.95
2020-08-01 03:00 | 44044.125 | 0 | 7.7873 | 39.95
2020-08-01 03:30 | 44044.1458 | 0 | 7.8198 | 39.95
2020-08-01 04:00 | 44044.1667 | 0 | 7.8936 | 39.95
2020-08-01 04:30 | 44044.1875 | 0 | 8.1765 | 39.95
2020-08-01 05:00 | 44044.2083 | 0 | 8.3276 | 39.95
2020-08-01 05:30 | 44044.2292 | 0 | 8.6038 | 39.95
2020-08-01 06:00 | 44044.25 | 0 | 9.0829 | 39.95
2020-08-01 06:30 | 44044.2708 | 0 | 9.7776 | 39.95
2020-08-01 07:00 | 44044.2917 | 0 | 10.2077 | 39.95
2020-08-01 07:30 | 44044.3125 | 0 | 10.2337 | 39.95
2020-08-01 08:00 | 44044.3333 | 0 | 10.2545 | 39.95
2020-08-01 08:30 | 44044.3542 | 0 | 10.1065 | 39.95
2020-08-01 09:00 | 44044.375 | 0 | 9.1815 | 39.95
2020-08-01 09:30 | 44044.3958 | 0 | 8.8671 | 39.95
2020-08-01 10:00 | 44044.4167 | 0 | 8.6338 | 39.95
2020-08-01 10:30 | 44044.4375 | 0 | 8.0175 | 39.95
2020-08-01 11:00 | 44044.4583 | 0 | 8.7013 | 39.95
2020-08-01 11:30 | 44044.4792 | 0 | 8.6618 | 39.95
2020-08-01 12:00 | 44044.5 | 0 | 8.2581 | 39.95
2020-08-01 12:30 | 44044.5208 | 0 | 8.0663 | 39.95
2020-08-01 13:00 | 44044.5417 | 0 | 9.6678 | 39.95
2020-08-01 13:30 | 44044.5625 | 0 | 8.696 | 39.95
2020-08-01 14:00 | 44044.5833 | 0 | 7.8583 | 39.95
2020-08-01 14:30 | 44044.6042 | 0 | 8.359 | 39.95
2020-08-01 15:00 | 44044.625 | 0 | 8.3248 | 39.95
2020-08-01 15:30 | 44044.6458 | 0 | 8.7537 | 39.95
2020-08-01 16:00 | 44044.6667 | 0 | 9.4154 | 39.95
2020-08-01 16:30 | 44044.6875 | 0 | 10.3125 | 39.95
2020-08-01 17:00 | 44044.7083 | 0 | 10.9701 | 39.95
2020-08-01 17:30 | 44044.7292 | 0 | 11.8841 | 39.95
2020-08-01 18:00 | 44044.75 | 0 | 12.2863 | 39.95
2020-08-01 18:30 | 44044.7708 | 0 | 12.285 | 39.95
2020-08-01 19:00 | 44044.7917 | 0 | 12.2658 | 39.95
2020-08-01 19:30 | 44044.8125 | 0 | 11.9007 | 39.95
2020-08-01 20:00 | 44044.8333 | 0 | 11.6797 | 39.95
2020-08-01 20:30 | 44044.8542 | 0 | 11.315 | 39.95
2020-08-01 21:00 | 44044.875 | 0 | 10.8118 | 39.95
2020-08-01 21:30 | 44044.8958 | 0 | 10.5441 | 39.95
2020-08-01 22:00 | 44044.9167 | 0 | 10.0845 | 39.95
2020-08-01 22:30 | 44044.9375 | 0 | 9.5204 | 39.95
2020-08-01 23:00 | 44044.9583 | 0 | 9.0915 | 39.95
2020-08-01 23:30 | 44044.9792 | 0 | 8.5208 | 39.95
2020-08-02 | 44045 | 0 | 8.0891 | 39.95
2020-08-02 00:30 | 44045.0208 | 0 | 7.7601 | 39.95
2020-08-02 01:00 | 44045.0417 | 0 | 7.465 | 39.95
2020-08-02 01:30 | 44045.0625 | 0 | 7.3027 | 39.95
2020-08-02 02:00 | 44045.0833 | 0 | 7.3251 | 39.95
2020-08-02 02:30 | 44045.1042 | 0 | 7.2267 | 39.95
2020-08-02 03:00 | 44045.125 | 0 | 7.076 | 39.95
2020-08-02 03:30 | 44045.1458 | 0 | 7.1052 | 39.95
2020-08-02 04:00 | 44045.1667 | 0 | 6.9935 | 39.95
2020-08-02 04:30 | 44045.1875 | 0 | 7.1275 | 39.95
2020-08-02 05:00 | 44045.2083 | 0 | 7.2778 | 39.95
2020-08-02 05:30 | 44045.2292 | 0 | 7.5362 | 39.95
2020-08-02 06:00 | 44045.25 | 0 | 7.994 | 39.95
2020-08-02 06:30 | 44045.2708 | 0 | 8.3275 | 39.95
2020-08-02 07:00 | 44045.2917 | 0 | 8.5894 | 39.95
2020-08-02 07:30 | 44045.3125 | 0 | 8.4762 | 39.95
2020-08-02 08:00 | 44045.3333 | 0 | 8.5411 | 39.95
2020-08-02 08:30 | 44045.3542 | 0 | 8.4449 | 39.95
2020-08-02 09:00 | 44045.375 | 0 | 7.8953 | 39.95
2020-08-02 09:30 | 44045.3958 | 0 | 7.6544 | 39.95
2020-08-02 10:00 | 44045.4167 | 0 | 7.2492 | 39.95
2020-08-02 10:30 | 44045.4375 | 0 | 6.9091 | 39.95
2020-08-02 11:00 | 44045.4583 | 0 | 6.5143 | 39.95
2020-08-02 11:30 | 44045.4792 | 0 | 6.473 | 39.95
2020-08-02 12:00 | 44045.5 | 0 | 6.5969 | 39.95
2020-08-02 12:30 | 44045.5208 | 0 | 6.5821 | 39.95
2020-08-02 13:00 | 44045.5417 | 0 | 6.84 | 39.95
2020-08-02 13:30 | 44045.5625 | 0 | 7.0385 | 39.95
2020-08-02 14:00 | 44045.5833 | 0 | 7.9278 | 39.95
2020-08-02 14:30 | 44045.6042 | 0 | 7.3161 | 39.95
2020-08-02 15:00 | 44045.625 | 0 | 7.7832 | 39.95
2020-08-02 15:30 | 44045.6458 | 0 | 8.6755 | 39.95
2020-08-02 16:00 | 44045.6667 | 0 | 9.2359 | 39.95
2020-08-02 16:30 | 44045.6875 | 0 | 10.192 | 39.95
2020-08-02 17:00 | 44045.7083 | 0 | 11.0503 | 39.95
2020-08-02 17:30 | 44045.7292 | 0 | 12.0931 | 39.95
2020-08-02 18:00 | 44045.75 | 0 | 12.7107 | 39.95
2020-08-02 18:30 | 44045.7708 | 0 | 12.736 | 39.95
2020-08-02 19:00 | 44045.7917 | 0 | 12.329 | 39.95
2020-08-02 19:30 | 44045.8125 | 0 | 12.0028 | 39.95
2020-08-02 20:00 | 44045.8333 | 0 | 11.7432 | 39.95
2020-08-02 20:30 | 44045.8542 | 0 | 11.3092 | 39.95
2020-08-02 21:00 | 44045.875 | 0 | 10.7946 | 39.95
2020-08-02 21:30 | 44045.8958 | 0 | 10.3213 | 39.95
2020-08-02 22:00 | 44045.9167 | 0 | 9.8996 | 39.95
2020-08-02 22:30 | 44045.9375 | 0 | 9.1725 | 39.95
2020-08-02 23:00 | 44045.9583 | 0 | 8.552 | 39.95
2020-08-02 23:30 | 44045.9792 | 0 | 8.0885 | 39.95
2020-08-03 | 44046 | 0 | 7.7229 | 39.95
2020-08-03 00:30 | 44046.0208 | 0 | 7.4673 | 39.95
2020-08-03 01:00 | 44046.0417 | 0 | 7.2587 | 39.95
2020-08-03 01:30 | 44046.0625 | 0 | 7.26 | 39.95
2020-08-03 02:00 | 44046.0833 | 0 | 7.2879 | 39.95
2020-08-03 02:30 | 44046.1042 | 0 | 7.2285 | 39.95
2020-08-03 03:00 | 44046.125 | 0 | 7.2455 | 39.95
2020-08-03 03:30 | 44046.1458 | 0 | 7.3541 | 39.95
2020-08-03 04:00 | 44046.1667 | 0 | 7.541 | 39.95
2020-08-03 04:30 | 44046.1875 | 0 | 8.0161 | 39.95
2020-08-03 05:00 | 44046.2083 | 0 | 9.004 | 39.95
2020-08-03 05:30 | 44046.2292 | 0 | 9.8475 | 39.95
2020-08-03 06:00 | 44046.25 | 0 | 11.2437 | 39.95
2020-08-03 06:30 | 44046.2708 | 0 | 12.5305 | 39.95
2020-08-03 07:00 | 44046.2917 | 0 | 13.4041 | 39.95
2020-08-03 07:30 | 44046.3125 | 0 | 13.1541 | 39.95
2020-08-03 08:00 | 44046.3333 | 0 | 12.5986 | 39.95
2020-08-03 08:30 | 44046.3542 | 0 | 12.3118 | 39.95
2020-08-03 09:00 | 44046.375 | 0 | 12.1841 | 39.95
2020-08-03 09:30 | 44046.3958 | 0 | 11.8322 | 39.95
2020-08-03 10:00 | 44046.4167 | 0 | 11.0407 | 39.95
2020-08-03 10:30 | 44046.4375 | 0 | 10.7102 | 39.95
2020-08-03 11:00 | 44046.4583 | 0 | 10.2241 | 39.95
2020-08-03 11:30 | 44046.4792 | 0 | 10.0084 | 39.95
2020-08-03 12:00 | 44046.5 | 0 | 9.753 | 39.95
2020-08-03 12:30 | 44046.5208 | 0 | 9.1922 | 39.95
2020-08-03 13:00 | 44046.5417 | 0 | 9.3989 | 39.95
2020-08-03 13:30 | 44046.5625 | 0 | 10.2681 | 39.95
2020-08-03 14:00 | 44046.5833 | 0 | 10.3033 | 39.95
2020-08-03 14:30 | 44046.6042 | 0 | 11.3505 | 39.95
2020-08-03 15:00 | 44046.625 | 0 | 10.7635 | 39.95
2020-08-03 15:30 | 44046.6458 | 0 | 10.5532 | 39.95
2020-08-03 16:00 | 44046.6667 | 0 | 11.7981 | 39.95
2020-08-03 16:30 | 44046.6875 | 0 | 12.3406 | 39.95
2020-08-03 17:00 | 44046.7083 | 0 | 12.9671 | 39.95
2020-08-03 17:30 | 44046.7292 | 0 | 14.1039 | 39.95
2020-08-03 18:00 | 44046.75 | 0 | 14.6138 | 39.95
2020-08-03 18:30 | 44046.7708 | 0 | 15.0276 | 39.95
2020-08-03 19:00 | 44046.7917 | 0 | 14.6057 | 39.95
2020-08-03 19:30 | 44046.8125 | 0 | 14.4341 | 39.95
2020-08-03 20:00 | 44046.8333 | 0 | 14.2019 | 39.95
2020-08-03 20:30 | 44046.8542 | 0 | 13.4015 | 39.95
2020-08-03 21:00 | 44046.875 | 0 | 12.6548 | 39.95
2020-08-03 21:30 | 44046.8958 | 0 | 12.2234 | 39.95
2020-08-03 22:00 | 44046.9167 | 0 | 11.8027 | 39.95
2020-08-03 22:30 | 44046.9375 | 0 | 10.9552 | 39.95
2020-08-03 23:00 | 44046.9583 | 0 | 10.1536 | 39.95
2020-08-03 23:30 | 44046.9792 | 0 | 9.5143 | 39.95
2020-08-04 | 44047 | 0 | 8.8639 | 39.95
2020-08-04 00:30 | 44047.0208 | 0 | 8.3095 | 39.95
2020-08-04 01:00 | 44047.0417 | 0 | 8.1961 | 39.95
2020-08-04 01:30 | 44047.0625 | 0 | 8.144 | 39.95
2020-08-04 02:00 | 44047.0833 | 0 | 8.0447 | 39.95
2020-08-04 02:30 | 44047.1042 | 0 | 8.0099 | 39.95
2020-08-04 03:00 | 44047.125 | 0 | 7.9976 | 39.95
2020-08-04 03:30 | 44047.1458 | 0 | 8.0621 | 39.95
2020-08-04 04:00 | 44047.1667 | 0 | 8.1215 | 39.95
2020-08-04 04:30 | 44047.1875 | 0 | 8.6005 | 39.95
2020-08-04 05:00 | 44047.2083 | 0 | 9.2641 | 39.95
2020-08-04 05:30 | 44047.2292 | 0 | 10.0486 | 39.95
2020-08-04 06:00 | 44047.25 | 0 | 11.4604 | 39.95
2020-08-04 06:30 | 44047.2708 | 0 | 12.5422 | 39.95
2020-08-04 07:00 | 44047.2917 | 0 | 13.1313 | 39.95
2020-08-04 07:30 | 44047.3125 | 0 | 13.0721 | 39.95
2020-08-04 08:00 | 44047.3333 | 0 | 12.9826 | 39.95
2020-08-04 08:30 | 44047.3542 | 0 | 12.7774 | 39.95
2020-08-04 09:00 | 44047.375 | 0 | 12.3177 | 39.95
2020-08-04 09:30 | 44047.3958 | 0 | 11.7152 | 39.95
2020-08-04 10:00 | 44047.4167 | 0 | 11.2436 | 39.95
2020-08-04 10:30 | 44047.4375 | 0 | 10.9452 | 39.95
2020-08-04 11:00 | 44047.4583 | 0 | 10.1319 | 39.95
2020-08-04 11:30 | 44047.4792 | 0 | 9.1506 | 39.95
2020-08-04 12:00 | 44047.5 | 0 | 9.7453 | 39.95
2020-08-04 12:30 | 44047.5208 | 0 | 9.1796 | 39.95
2020-08-04 13:00 | 44047.5417 | 0 | 9.489 | 39.95
2020-08-04 13:30 | 44047.5625 | 0 | 10.4061 | 39.95
2020-08-04 14:00 | 44047.5833 | 0 | 9.8939 | 39.95
2020-08-04 14:30 | 44047.6042 | 0 | 10.3928 | 39.95
2020-08-04 15:00 | 44047.625 | 0 | 10.4088 | 39.95
2020-08-04 15:30 | 44047.6458 | 0 | 10.7319 | 39.95
2020-08-04 16:00 | 44047.6667 | 0 | 11.3372 | 39.95
2020-08-04 16:30 | 44047.6875 | 0 | 12.2183 | 39.95
2020-08-04 17:00 | 44047.7083 | 0 | 12.9432 | 39.95
2020-08-04 17:30 | 44047.7292 | 0 | 13.8792 | 39.95
2020-08-04 18:00 | 44047.75 | 0 | 14.3682 | 39.95
2020-08-04 18:30 | 44047.7708 | 0 | 14.7541 | 39.95
2020-08-04 19:00 | 44047.7917 | 0 | 14.3592 | 39.95
2020-08-04 19:30 | 44047.8125 | 0 | 14.1314 | 39.95
2020-08-04 20:00 | 44047.8333 | 0 | 13.8314 | 39.95
2020-08-04 20:30 | 44047.8542 | 0 | 13.6006 | 39.95
2020-08-04 21:00 | 44047.875 | 0 | 12.9361 | 39.95
2020-08-04 21:30 | 44047.8958 | 0 | 12.4296 | 39.95
2020-08-04 22:00 | 44047.9167 | 0 | 11.739 | 39.95
2020-08-04 22:30 | 44047.9375 | 0 | 10.7683 | 39.95
2020-08-04 23:00 | 44047.9583 | 0 | 9.8776 | 39.95
2020-08-04 23:30 | 44047.9792 | 0 | 9.4014 | 39.95
2020-08-05 | 44048 | 0 | 8.895 | 39.95
2020-08-05 00:30 | 44048.0208 | 0 | 8.4833 | 39.95
2020-08-05 01:00 | 44048.0417 | 0 | 8.2648 | 39.95
2020-08-05 01:30 | 44048.0625 | 0 | 8.1316 | 39.95
2020-08-05 02:00 | 44048.0833 | 0 | 8.1068 | 39.95
2020-08-05 02:30 | 44048.1042 | 0 | 8.1068 | 39.95
2020-08-05 03:00 | 44048.125 | 0 | 8.0844 | 39.95
2020-08-05 03:30 | 44048.1458 | 0 | 7.9498 | 39.95
2020-08-05 04:00 | 44048.1667 | 0 | 8.1024 | 39.95
2020-08-05 04:30 | 44048.1875 | 0 | 8.6004 | 39.95
2020-08-05 05:00 | 44048.2083 | 0 | 9.3245 | 39.95
2020-08-05 05:30 | 44048.2292 | 0 | 10.326 | 39.95
2020-08-05 06:00 | 44048.25 | 0 | 11.6551 | 39.95
2020-08-05 06:30 | 44048.2708 | 0 | 13.0519 | 39.95
2020-08-05 07:00 | 44048.2917 | 0 | 13.7435 | 39.95
2020-08-05 07:30 | 44048.3125 | 0 | 13.5187 | 39.95
2020-08-05 08:00 | 44048.3333 | 0 | 12.6723 | 39.95
2020-08-05 08:30 | 44048.3542 | 0 | 11.7133 | 39.95
2020-08-05 09:00 | 44048.375 | 0 | 10.8805 | 39.95
2020-08-05 09:30 | 44048.3958 | 0 | 10.2855 | 39.95
2020-08-05 10:00 | 44048.4167 | 0 | 9.9168 | 39.95
2020-08-05 10:30 | 44048.4375 | 0 | 9.6122 | 39.95
2020-08-05 11:00 | 44048.4583 | 0 | 9.3897 | 39.95
2020-08-05 11:30 | 44048.4792 | 0 | 9.2474 | 39.95
2020-08-05 12:00 | 44048.5 | 0 | 9.3403 | 39.95
2020-08-05 12:30 | 44048.5208 | 0 | 9.4385 | 39.95
2020-08-05 13:00 | 44048.5417 | 0 | 9.5244 | 39.95
2020-08-05 13:30 | 44048.5625 | 0 | 10.0784 | 39.95
2020-08-05 14:00 | 44048.5833 | 0 | 10.0862 | 39.95
2020-08-05 14:30 | 44048.6042 | 0 | 10.2358 | 39.95
2020-08-05 15:00 | 44048.625 | 0 | 10.8038 | 39.95
2020-08-05 15:30 | 44048.6458 | 0 | 11.3523 | 39.95
2020-08-05 16:00 | 44048.6667 | 0 | 11.6507 | 39.95
2020-08-05 16:30 | 44048.6875 | 0 | 12.1526 | 39.95
2020-08-05 17:00 | 44048.7083 | 0 | 12.8264 | 39.95
2020-08-05 17:30 | 44048.7292 | 0 | 13.7844 | 39.95
2020-08-05 18:00 | 44048.75 | 0 | 14.2462 | 39.95
2020-08-05 18:30 | 44048.7708 | 0 | 14.2847 | 39.95
2020-08-05 19:00 | 44048.7917 | 0 | 13.9026 | 39.95
2020-08-05 19:30 | 44048.8125 | 0 | 13.8025 | 39.95
2020-08-05 20:00 | 44048.8333 | 0 | 13.5641 | 39.95
2020-08-05 20:30 | 44048.8542 | 0 | 13.1234 | 39.95
2020-08-05 21:00 | 44048.875 | 0 | 12.5243 | 39.95
2020-08-05 21:30 | 44048.8958 | 0 | 11.9579 | 39.95
2020-08-05 22:00 | 44048.9167 | 0 | 11.6291 | 39.95
2020-08-05 22:30 | 44048.9375 | 0 | 10.8358 | 39.95
2020-08-05 23:00 | 44048.9583 | 0 | 10.0398 | 39.95
2020-08-05 23:30 | 44048.9792 | 0 | 9.4033 | 39.95
2020-08-06 | 44049 | 0 | 8.8903 | 39.95
2020-08-06 00:30 | 44049.0208 | 0 | 8.4412 | 39.95
2020-08-06 01:00 | 44049.0417 | 0 | 8.2995 | 39.95
2020-08-06 01:30 | 44049.0625 | 0 | 8.129 | 39.95
2020-08-06 02:00 | 44049.0833 | 0 | 8.0274 | 39.95
2020-08-06 02:30 | 44049.1042 | 0 | 7.8642 | 39.95
2020-08-06 03:00 | 44049.125 | 0 | 7.9189 | 39.95
2020-08-06 03:30 | 44049.1458 | 0 | 7.9082 | 39.95
2020-08-06 04:00 | 44049.1667 | 0 | 8.0933 | 39.95
2020-08-06 04:30 | 44049.1875 | 0 | 8.6832 | 39.95
2020-08-06 05:00 | 44049.2083 | 0 | 9.2417 | 39.95
2020-08-06 05:30 | 44049.2292 | 0 | 10.2796 | 39.95
2020-08-06 06:00 | 44049.25 | 0 | 11.6563 | 39.95
2020-08-06 06:30 | 44049.2708 | 0 | 12.912 | 39.95
2020-08-06 07:00 | 44049.2917 | 0 | 13.5863 | 39.95
2020-08-06 07:30 | 44049.3125 | 0 | 13.5014 | 39.95
2020-08-06 08:00 | 44049.3333 | 0 | 12.4677 | 39.95
2020-08-06 08:30 | 44049.3542 | 0 | 11.7173 | 39.95
2020-08-06 09:00 | 44049.375 | 0 | 10.9159 | 39.95
2020-08-06 09:30 | 44049.3958 | 0 | 10.3036 | 39.95
2020-08-06 10:00 | 44049.4167 | 0 | 9.8176 | 39.95
2020-08-06 10:30 | 44049.4375 | 0 | 9.4748 | 39.95
2020-08-06 11:00 | 44049.4583 | 0 | 9.2634 | 39.95
2020-08-06 11:30 | 44049.4792 | 0 | 9.1788 | 39.95
2020-08-06 12:00 | 44049.5 | 0 | 8.9232 | 39.95
2020-08-06 12:30 | 44049.5208 | 0 | 8.9925 | 39.95
2020-08-06 13:00 | 44049.5417 | 0 | 9.1819 | 39.95
2020-08-06 13:30 | 44049.5625 | 0 | 9.4293 | 39.95
2020-08-06 14:00 | 44049.5833 | 0 | 9.6948 | 39.95
2020-08-06 14:30 | 44049.6042 | 0 | 9.9114 | 39.95
2020-08-06 15:00 | 44049.625 | 0 | 10.2392 | 39.95
2020-08-06 15:30 | 44049.6458 | 0 | 10.7899 | 39.95
2020-08-06 16:00 | 44049.6667 | 0 | 11.5095 | 39.95
2020-08-06 16:30 | 44049.6875 | 0 | 12.0971 | 39.95
2020-08-06 17:00 | 44049.7083 | 0 | 12.5682 | 39.95
2020-08-06 17:30 | 44049.7292 | 0 | 13.6349 | 39.95
2020-08-06 18:00 | 44049.75 | 0 | 13.8902 | 39.95
2020-08-06 18:30 | 44049.7708 | 0 | 14.2888 | 39.95
2020-08-06 19:00 | 44049.7917 | 0 | 13.9622 | 39.95
2020-08-06 19:30 | 44049.8125 | 0 | 13.712 | 39.95
2020-08-06 20:00 | 44049.8333 | 0 | 13.4897 | 39.95
2020-08-06 20:30 | 44049.8542 | 0 | 13.0547 | 39.95
2020-08-06 21:00 | 44049.875 | 0 | 12.3415 | 39.95
2020-08-06 21:30 | 44049.8958 | 0 | 11.9886 | 39.95
2020-08-06 22:00 | 44049.9167 | 0 | 11.5288 | 39.95
2020-08-06 22:30 | 44049.9375 | 0 | 10.7187 | 39.95
2020-08-06 23:00 | 44049.9583 | 0 | 9.9728 | 39.95
2020-08-06 23:30 | 44049.9792 | 0 | 9.42 | 39.95
2020-08-07 | 44050 | 0 | 8.6852 | 39.95
2020-08-07 00:30 | 44050.0208 | 0 | 8.2772 | 39.95
2020-08-07 01:00 | 44050.0417 | 0 | 8.1539 | 39.95
2020-08-07 01:30 | 44050.0625 | 0 | 7.9604 | 39.95
2020-08-07 02:00 | 44050.0833 | 0 | 7.8586 | 39.95
2020-08-07 02:30 | 44050.1042 | 0 | 7.7962 | 39.95
2020-08-07 03:00 | 44050.125 | 0 | 7.7081 | 39.95
2020-08-07 03:30 | 44050.1458 | 0 | 7.5749 | 39.95
2020-08-07 04:00 | 44050.1667 | 0 | 7.9115 | 39.95
2020-08-07 04:30 | 44050.1875 | 0 | 8.1902 | 39.95
2020-08-07 05:00 | 44050.2083 | 0 | 8.6593 | 39.95
2020-08-07 05:30 | 44050.2292 | 0 | 9.4994 | 39.95
2020-08-07 06:00 | 44050.25 | 0 | 10.6954 | 39.95
2020-08-07 06:30 | 44050.2708 | 0 | 11.6707 | 39.95
2020-08-07 07:00 | 44050.2917 | 0 | 12.4017 | 39.95
2020-08-07 07:30 | 44050.3125 | 0 | 12.0041 | 39.95
2020-08-07 08:00 | 44050.3333 | 0 | 11.8367 | 39.95
2020-08-07 08:30 | 44050.3542 | 0 | 11.1041 | 39.95
2020-08-07 09:00 | 44050.375 | 0 | 10.3667 | 39.95
2020-08-07 09:30 | 44050.3958 | 0 | 10.6586 | 39.95
2020-08-07 10:00 | 44050.4167 | 0 | 10.1269 | 39.95
2020-08-07 10:30 | 44050.4375 | 0 | 10.7321 | 39.95
2020-08-07 11:00 | 44050.4583 | 0 | 10.0072 | 39.95
2020-08-07 11:30 | 44050.4792 | 0 | 10.2439 | 39.95
2020-08-07 12:00 | 44050.5 | 0 | 11.2876 | 39.95
2020-08-07 12:30 | 44050.5208 | 0 | 12.1224 | 39.95
2020-08-07 13:00 | 44050.5417 | 0 | 12.3797 | 39.95
2020-08-07 13:30 | 44050.5625 | 0 | 12.2644 | 39.95
2020-08-07 14:00 | 44050.5833 | 0 | 12.2478 | 39.95
2020-08-07 14:30 | 44050.6042 | 0 | 11.9722 | 39.95
2020-08-07 15:00 | 44050.625 | 0 | 12.4252 | 39.95
2020-08-07 15:30 | 44050.6458 | 0 | 12.7354 | 39.95
2020-08-07 16:00 | 44050.6667 | 0 | 12.752 | 39.95
2020-08-07 16:30 | 44050.6875 | 0 | 12.9143 | 39.95
2020-08-07 17:00 | 44050.7083 | 0 | 13.1147 | 39.95
2020-08-07 17:30 | 44050.7292 | 0 | 13.7121 | 39.95
2020-08-07 18:00 | 44050.75 | 0 | 13.9596 | 39.95
2020-08-07 18:30 | 44050.7708 | 0 | 14.0432 | 39.95
2020-08-07 19:00 | 44050.7917 | 0 | 13.7343 | 39.95
2020-08-07 19:30 | 44050.8125 | 0 | 13.5109 | 39.95
2020-08-07 20:00 | 44050.8333 | 0 | 13.1999 | 39.95
2020-08-07 20:30 | 44050.8542 | 0 | 12.6483 | 39.95
2020-08-07 21:00 | 44050.875 | 0 | 12.1151 | 39.95
2020-08-07 21:30 | 44050.8958 | 0 | 11.7471 | 39.95
2020-08-07 22:00 | 44050.9167 | 0 | 11.1625 | 39.95
2020-08-07 22:30 | 44050.9375 | 0 | 10.3732 | 39.95
2020-08-07 23:00 | 44050.9583 | 0 | 9.6938 | 39.95
2020-08-07 23:30 | 44050.9792 | 0 | 9.2944 | 39.95
2020-08-08 | 44051 | 0 | 8.7174 | 39.95
2020-08-08 00:30 | 44051.0208 | 0 | 8.1976 | 39.95
2020-08-08 01:00 | 44051.0417 | 0 | 7.9616 | 39.95
2020-08-08 01:30 | 44051.0625 | 0 | 7.7345 | 39.95
2020-08-08 02:00 | 44051.0833 | 0 | 7.6693 | 39.95
2020-08-08 02:30 | 44051.1042 | 0 | 7.5708 | 39.95
2020-08-08 03:00 | 44051.125 | 0 | 7.4478 | 39.95
2020-08-08 03:30 | 44051.1458 | 0 | 7.4258 | 39.95
2020-08-08 04:00 | 44051.1667 | 0 | 7.5206 | 39.95
2020-08-08 04:30 | 44051.1875 | 0 | 7.8019 | 39.95
2020-08-08 05:00 | 44051.2083 | 0 | 7.9728 | 39.95
2020-08-08 05:30 | 44051.2292 | 0 | 8.1582 | 39.95
2020-08-08 06:00 | 44051.25 | 0 | 8.6152 | 39.95
2020-08-08 06:30 | 44051.2708 | 0 | 8.9003 | 39.95
2020-08-08 07:00 | 44051.2917 | 0 | 9.3539 | 39.95
2020-08-08 07:30 | 44051.3125 | 0 | 8.9682 | 39.95
2020-08-08 08:00 | 44051.3333 | 0 | 9.261 | 39.95
2020-08-08 08:30 | 44051.3542 | 0 | 9.253 | 39.95
2020-08-08 09:00 | 44051.375 | 0 | 9.4765 | 39.95
2020-08-08 09:30 | 44051.3958 | 0 | 8.4912 | 39.95
2020-08-08 10:00 | 44051.4167 | 0 | 7.9197 | 39.95
2020-08-08 10:30 | 44051.4375 | 0 | 8.5574 | 39.95
2020-08-08 11:00 | 44051.4583 | 0 | 9.666 | 39.95
2020-08-08 11:30 | 44051.4792 | 0 | 9.653 | 39.95
2020-08-08 12:00 | 44051.5 | 0 | 10.3423 | 39.95
2020-08-08 12:30 | 44051.5208 | 0 | 9.6716 | 39.95
2020-08-08 13:00 | 44051.5417 | 0 | 7.3275 | 39.95
2020-08-08 13:30 | 44051.5625 | 0 | 7.2498 | 39.95
2020-08-08 14:00 | 44051.5833 | 0 | 7.5367 | 39.95
2020-08-08 14:30 | 44051.6042 | 0 | 8.1184 | 39.95
2020-08-08 15:00 | 44051.625 | 0 | 8.8767 | 39.95
2020-08-08 15:30 | 44051.6458 | 0 | 8.8704 | 39.95
2020-08-08 16:00 | 44051.6667 | 0 | 9.3708 | 39.95
2020-08-08 16:30 | 44051.6875 | 0 | 10.0215 | 39.95
2020-08-08 17:00 | 44051.7083 | 0 | 10.541 | 39.95
2020-08-08 17:30 | 44051.7292 | 0 | 11.2435 | 39.95
2020-08-08 18:00 | 44051.75 | 0 | 11.8381 | 39.95
2020-08-08 18:30 | 44051.7708 | 0 | 11.823 | 39.95
2020-08-08 19:00 | 44051.7917 | 0 | 11.5435 | 39.95
2020-08-08 19:30 | 44051.8125 | 0 | 11.332 | 39.95
2020-08-08 20:00 | 44051.8333 | 0 | 11.2385 | 39.95
2020-08-08 20:30 | 44051.8542 | 0 | 10.6627 | 39.95
2020-08-08 21:00 | 44051.875 | 0 | 10.2838 | 39.95
2020-08-08 21:30 | 44051.8958 | 0 | 10.0364 | 39.95
2020-08-08 22:00 | 44051.9167 | 0 | 9.8111 | 39.95
2020-08-08 22:30 | 44051.9375 | 0 | 9.253 | 39.95
2020-08-08 23:00 | 44051.9583 | 0 | 8.8155 | 39.95
2020-08-08 23:30 | 44051.9792 | 0 | 8.3212 | 39.95
2020-08-09 | 44052 | 0 | 7.9504 | 39.95
2020-08-09 00:30 | 44052.0208 | 0 | 7.5685 | 39.95
2020-08-09 01:00 | 44052.0417 | 0 | 7.3361 | 39.95
2020-08-09 01:30 | 44052.0625 | 0 | 7.1523 | 39.95
2020-08-09 02:00 | 44052.0833 | 0 | 7.2267 | 39.95
2020-08-09 02:30 | 44052.1042 | 0 | 7.1351 | 39.95
2020-08-09 03:00 | 44052.125 | 0 | 7.0012 | 39.95
2020-08-09 03:30 | 44052.1458 | 0 | 6.9064 | 39.95
2020-08-09 04:00 | 44052.1667 | 0 | 6.8451 | 39.95
2020-08-09 04:30 | 44052.1875 | 0 | 6.8448 | 39.95
2020-08-09 05:00 | 44052.2083 | 0 | 7.1078 | 39.95
2020-08-09 05:30 | 44052.2292 | 0 | 7.305 | 39.95
2020-08-09 06:00 | 44052.25 | 0 | 7.6107 | 39.95
2020-08-09 06:30 | 44052.2708 | 0 | 7.878 | 39.95
2020-08-09 07:00 | 44052.2917 | 0 | 8.107 | 39.95
2020-08-09 07:30 | 44052.3125 | 0 | 8.0787 | 39.95
2020-08-09 08:00 | 44052.3333 | 0 | 7.9337 | 39.95
2020-08-09 08:30 | 44052.3542 | 0 | 7.7847 | 39.95
2020-08-09 09:00 | 44052.375 | 0 | 7.673 | 39.95
2020-08-09 09:30 | 44052.3958 | 0 | 7.1259 | 39.95
2020-08-09 10:00 | 44052.4167 | 0 | 6.8688 | 39.95
2020-08-09 10:30 | 44052.4375 | 0 | 6.6833 | 39.95
2020-08-09 11:00 | 44052.4583 | 0 | 6.819 | 39.95
2020-08-09 11:30 | 44052.4792 | 0 | 6.8219 | 39.95
2020-08-09 12:00 | 44052.5 | 0 | 5.9515 | 39.95
2020-08-09 12:30 | 44052.5208 | 0 | 5.9574 | 39.95
2020-08-09 13:00 | 44052.5417 | 0 | 6.0784 | 39.95
2020-08-09 13:30 | 44052.5625 | 0 | 6.1675 | 39.95
2020-08-09 14:00 | 44052.5833 | 0 | 6.6779 | 39.95
2020-08-09 14:30 | 44052.6042 | 0 | 7.3004 | 39.95
2020-08-09 15:00 | 44052.625 | 0 | 7.7313 | 39.95
2020-08-09 15:30 | 44052.6458 | 0 | 8.3241 | 39.95
2020-08-09 16:00 | 44052.6667 | 0 | 9.1785 | 39.95
2020-08-09 16:30 | 44052.6875 | 0 | 10.217 | 39.95
2020-08-09 17:00 | 44052.7083 | 0 | 11.5683 | 39.95
2020-08-09 17:30 | 44052.7292 | 0 | 12.7843 | 39.95
2020-08-09 18:00 | 44052.75 | 0 | 13.4257 | 39.95
2020-08-09 18:30 | 44052.7708 | 0 | 13.6469 | 39.95
2020-08-09 19:00 | 44052.7917 | 0 | 13.3412 | 39.95
2020-08-09 19:30 | 44052.8125 | 0 | 12.8059 | 39.95
2020-08-09 20:00 | 44052.8333 | 0 | 12.6567 | 39.95
2020-08-09 20:30 | 44052.8542 | 0 | 12.0109 | 39.95
2020-08-09 21:00 | 44052.875 | 0 | 11.4067 | 39.95
2020-08-09 21:30 | 44052.8958 | 0 | 11.1547 | 39.95
2020-08-09 22:00 | 44052.9167 | 0 | 10.4861 | 39.95
2020-08-09 22:30 | 44052.9375 | 0 | 9.6315 | 39.95
2020-08-09 23:00 | 44052.9583 | 0 | 8.8607 | 39.95
2020-08-09 23:30 | 44052.9792 | 0 | 8.3295 | 39.95
2020-08-10 | 44053 | 0 | 7.9556 | 39.95
2020-08-10 00:30 | 44053.0208 | 0 | 7.7123 | 39.95
2020-08-10 01:00 | 44053.0417 | 0 | 7.4343 | 39.95
2020-08-10 01:30 | 44053.0625 | 0 | 7.3585 | 39.95
2020-08-10 02:00 | 44053.0833 | 0 | 7.3159 | 39.95
2020-08-10 02:30 | 44053.1042 | 0 | 7.3419 | 39.95
2020-08-10 03:00 | 44053.125 | 0 | 7.353 | 39.95
2020-08-10 03:30 | 44053.1458 | 0 | 7.4146 | 39.95
2020-08-10 04:00 | 44053.1667 | 0 | 7.6888 | 39.95
2020-08-10 04:30 | 44053.1875 | 0 | 8.0733 | 39.95
2020-08-10 05:00 | 44053.2083 | 0 | 8.7265 | 39.95
2020-08-10 05:30 | 44053.2292 | 0 | 9.6699 | 39.95
2020-08-10 06:00 | 44053.25 | 0 | 10.888 | 39.95
2020-08-10 06:30 | 44053.2708 | 0 | 12.4977 | 39.95
2020-08-10 07:00 | 44053.2917 | 0 | 13.2718 | 39.95
2020-08-10 07:30 | 44053.3125 | 0 | 13.1932 | 39.95
2020-08-10 08:00 | 44053.3333 | 0 | 12.3964 | 39.95
2020-08-10 08:30 | 44053.3542 | 0 | 11.1559 | 39.95
2020-08-10 09:00 | 44053.375 | 0 | 10.6737 | 39.95
2020-08-10 09:30 | 44053.3958 | 0 | 11.227 | 39.95
2020-08-10 10:00 | 44053.4167 | 0 | 10.0792 | 39.95
2020-08-10 10:30 | 44053.4375 | 0 | 9.6394 | 39.95
2020-08-10 11:00 | 44053.4583 | 0 | 9.275 | 39.95
2020-08-10 11:30 | 44053.4792 | 0 | 10.5546 | 39.95
2020-08-10 12:00 | 44053.5 | 0 | 8.5604 | 39.95
2020-08-10 12:30 | 44053.5208 | 0 | 8.5814 | 39.95
2020-08-10 13:00 | 44053.5417 | 0 | 8.6614 | 39.95
2020-08-10 13:30 | 44053.5625 | 0 | 8.6826 | 39.95
2020-08-10 14:00 | 44053.5833 | 0 | 8.9861 | 39.95
2020-08-10 14:30 | 44053.6042 | 0 | 9.0167 | 39.95
2020-08-10 15:00 | 44053.625 | 0 | 9.5111 | 39.95
2020-08-10 15:30 | 44053.6458 | 0 | 9.9942 | 39.95
2020-08-10 16:00 | 44053.6667 | 0 | 10.7033 | 39.95
2020-08-10 16:30 | 44053.6875 | 0 | 11.7485 | 39.95
2020-08-10 17:00 | 44053.7083 | 0 | 12.9859 | 39.95
2020-08-10 17:30 | 44053.7292 | 0 | 14.8215 | 39.95
2020-08-10 18:00 | 44053.75 | 0 | 15.8427 | 39.95
2020-08-10 18:30 | 44053.7708 | 0 | 16.3197 | 39.95
2020-08-10 19:00 | 44053.7917 | 0 | 15.8456 | 39.95
2020-08-10 19:30 | 44053.8125 | 0 | 15.2339 | 39.95
2020-08-10 20:00 | 44053.8333 | 0 | 14.8054 | 39.95
2020-08-10 20:30 | 44053.8542 | 0 | 14.0536 | 39.95
2020-08-10 21:00 | 44053.875 | 0 | 13.1371 | 39.95
2020-08-10 21:30 | 44053.8958 | 0 | 12.4161 | 39.95
2020-08-10 22:00 | 44053.9167 | 0 | 11.5488 | 39.95
2020-08-10 22:30 | 44053.9375 | 0 | 10.3883 | 39.95
2020-08-10 23:00 | 44053.9583 | 0 | 9.6068 | 39.95
2020-08-10 23:30 | 44053.9792 | 0 | 8.8743 | 39.95
2020-08-11 | 44054 | 0 | 8.3464 | 39.95
2020-08-11 00:30 | 44054.0208 | 0 | 7.8764 | 39.95
2020-08-11 01:00 | 44054.0417 | 0 | 7.6489 | 39.95
2020-08-11 01:30 | 44054.0625 | 0 | 7.5316 | 39.95
2020-08-11 02:00 | 44054.0833 | 0 | 7.5485 | 39.95
2020-08-11 02:30 | 44054.1042 | 0 | 7.4423 | 39.95
2020-08-11 03:00 | 44054.125 | 0 | 7.4983 | 39.95
2020-08-11 03:30 | 44054.1458 | 0 | 7.5261 | 39.95
2020-08-11 04:00 | 44054.1667 | 0 | 7.5878 | 39.95
2020-08-11 04:30 | 44054.1875 | 0 | 8.1328 | 39.95
2020-08-11 05:00 | 44054.2083 | 0 | 8.9104 | 39.95
2020-08-11 05:30 | 44054.2292 | 0 | 9.6874 | 39.95
2020-08-11 06:00 | 44054.25 | 0 | 11.2817 | 39.95
2020-08-11 06:30 | 44054.2708 | 0 | 12.7429 | 39.95
2020-08-11 07:00 | 44054.2917 | 0 | 13.3883 | 39.95
2020-08-11 07:30 | 44054.3125 | 0 | 12.6801 | 39.95
2020-08-11 08:00 | 44054.3333 | 0 | 11.7684 | 39.95
2020-08-11 08:30 | 44054.3542 | 0 | 10.7876 | 39.95
2020-08-11 09:00 | 44054.375 | 0 | 9.9601 | 39.95
2020-08-11 09:30 | 44054.3958 | 0 | 9.3617 | 39.95
2020-08-11 10:00 | 44054.4167 | 0 | 8.766 | 39.95
2020-08-11 10:30 | 44054.4375 | 0 | 8.313 | 39.95
2020-08-11 11:00 | 44054.4583 | 0 | 8.0319 | 39.95
2020-08-11 11:30 | 44054.4792 | 0 | 7.9962 | 39.95
2020-08-11 12:00 | 44054.5 | 0 | 8.7421 | 39.95
2020-08-11 12:30 | 44054.5208 | 0 | 7.9674 | 39.95
2020-08-11 13:00 | 44054.5417 | 0 | 7.9479 | 39.95
2020-08-11 13:30 | 44054.5625 | 0 | 8.6856 | 39.95
2020-08-11 14:00 | 44054.5833 | 0 | 10.5111 | 39.95
2020-08-11 14:30 | 44054.6042 | 0 | 10.0996 | 39.95
2020-08-11 15:00 | 44054.625 | 0 | 9.8062 | 39.95
2020-08-11 15:30 | 44054.6458 | 0 | 10.1746 | 39.95
2020-08-11 16:00 | 44054.6667 | 0 | 10.4076 | 39.95
2020-08-11 16:30 | 44054.6875 | 0 | 10.9987 | 39.95
2020-08-11 17:00 | 44054.7083 | 0 | 11.5998 | 39.95
2020-08-11 17:30 | 44054.7292 | 0 | 12.8526 | 39.95
2020-08-11 18:00 | 44054.75 | 0 | 13.4817 | 39.95
2020-08-11 18:30 | 44054.7708 | 0 | 13.7566 | 39.95
2020-08-11 19:00 | 44054.7917 | 0 | 13.4143 | 39.95
2020-08-11 19:30 | 44054.8125 | 0 | 13.1483 | 39.95
2020-08-11 20:00 | 44054.8333 | 0 | 13.0156 | 39.95
2020-08-11 20:30 | 44054.8542 | 0 | 12.5482 | 39.95
2020-08-11 21:00 | 44054.875 | 0 | 11.7962 | 39.95
2020-08-11 21:30 | 44054.8958 | 0 | 11.2313 | 39.95
2020-08-11 22:00 | 44054.9167 | 0 | 10.667 | 39.95
2020-08-11 22:30 | 44054.9375 | 0 | 9.6721 | 39.95
2020-08-11 23:00 | 44054.9583 | 0 | 9.0274 | 39.95
2020-08-11 23:30 | 44054.9792 | 0 | 8.4808 | 39.95
2020-08-12 | 44055 | 0 | 7.8593 | 39.95
2020-08-12 00:30 | 44055.0208 | 0 | 7.552 | 39.95
2020-08-12 01:00 | 44055.0417 | 0 | 7.3585 | 39.95
2020-08-12 01:30 | 44055.0625 | 0 | 7.1736 | 39.95
2020-08-12 02:00 | 44055.0833 | 0 | 7.193 | 39.95
2020-08-12 02:30 | 44055.1042 | 0 | 7.1241 | 39.95
2020-08-12 03:00 | 44055.125 | 0 | 7.1968 | 39.95
2020-08-12 03:30 | 44055.1458 | 0 | 7.1725 | 39.95
2020-08-12 04:00 | 44055.1667 | 0 | 7.3568 | 39.95
2020-08-12 04:30 | 44055.1875 | 0 | 7.7518 | 39.95
2020-08-12 05:00 | 44055.2083 | 0 | 8.4439 | 39.95
2020-08-12 05:30 | 44055.2292 | 0 | 9.3745 | 39.95
2020-08-12 06:00 | 44055.25 | 0 | 10.745 | 39.95
2020-08-12 06:30 | 44055.2708 | 0 | 11.8782 | 39.95
2020-08-12 07:00 | 44055.2917 | 0 | 12.4561 | 39.95
2020-08-12 07:30 | 44055.3125 | 0 | 12.2106 | 39.95
2020-08-12 08:00 | 44055.3333 | 0 | 11.4184 | 39.95
2020-08-12 08:30 | 44055.3542 | 0 | 11.0787 | 39.95
2020-08-12 09:00 | 44055.375 | 0 | 10.0124 | 39.95
2020-08-12 09:30 | 44055.3958 | 0 | 9.265 | 39.95
2020-08-12 10:00 | 44055.4167 | 0 | 8.5501 | 39.95
2020-08-12 10:30 | 44055.4375 | 0 | 8.2596 | 39.95
2020-08-12 11:00 | 44055.4583 | 0 | 8.0712 | 39.95
2020-08-12 11:30 | 44055.4792 | 0 | 8.9023 | 39.95
2020-08-12 12:00 | 44055.5 | 0 | 8.1736 | 39.95
2020-08-12 12:30 | 44055.5208 | 0 | 8.2428 | 39.95
2020-08-12 13:00 | 44055.5417 | 0 | 8.6156 | 39.95
2020-08-12 13:30 | 44055.5625 | 0 | 8.6159 | 39.95
2020-08-12 14:00 | 44055.5833 | 0 | 8.749 | 39.95
2020-08-12 14:30 | 44055.6042 | 0 | 9.0422 | 39.95
2020-08-12 15:00 | 44055.625 | 0 | 9.5722 | 39.95
2020-08-12 15:30 | 44055.6458 | 0 | 9.6326 | 39.95
2020-08-12 16:00 | 44055.6667 | 0 | 10.4196 | 39.95
2020-08-12 16:30 | 44055.6875 | 0 | 10.856 | 39.95
2020-08-12 17:00 | 44055.7083 | 0 | 11.4642 | 39.95
2020-08-12 17:30 | 44055.7292 | 0 | 12.6276 | 39.95
2020-08-12 18:00 | 44055.75 | 0 | 13.4639 | 39.95
2020-08-12 18:30 | 44055.7708 | 0 | 13.6674 | 39.95
2020-08-12 19:00 | 44055.7917 | 0 | 13.2406 | 39.95
2020-08-12 19:30 | 44055.8125 | 0 | 12.8415 | 39.95
2020-08-12 20:00 | 44055.8333 | 0 | 12.6713 | 39.95
2020-08-12 20:30 | 44055.8542 | 0 | 12.0071 | 39.95
2020-08-12 21:00 | 44055.875 | 0 | 11.537 | 39.95
2020-08-12 21:30 | 44055.8958 | 0 | 11.0486 | 39.95
2020-08-12 22:00 | 44055.9167 | 0 | 10.5801 | 39.95
2020-08-12 22:30 | 44055.9375 | 0 | 9.6394 | 39.95
2020-08-12 23:00 | 44055.9583 | 0 | 8.9445 | 39.95
2020-08-12 23:30 | 44055.9792 | 0 | 8.4248 | 39.95
2020-08-13 | 44056 | 0 | 7.9707 | 39.95
2020-08-13 00:30 | 44056.0208 | 0 | 7.4699 | 39.95
2020-08-13 01:00 | 44056.0417 | 0 | 7.286 | 39.95
2020-08-13 01:30 | 44056.0625 | 0 | 7.2122 | 39.95
2020-08-13 02:00 | 44056.0833 | 0 | 7.2283 | 39.95
2020-08-13 02:30 | 44056.1042 | 0 | 7.1724 | 39.95
2020-08-13 03:00 | 44056.125 | 0 | 7.2006 | 39.95
2020-08-13 03:30 | 44056.1458 | 0 | 7.1668 | 39.95
2020-08-13 04:00 | 44056.1667 | 0 | 7.2457 | 39.95
2020-08-13 04:30 | 44056.1875 | 0 | 7.6864 | 39.95
2020-08-13 05:00 | 44056.2083 | 0 | 8.3111 | 39.95
2020-08-13 05:30 | 44056.2292 | 0 | 9.0267 | 39.95
2020-08-13 06:00 | 44056.25 | 0 | 10.3914 | 39.95
2020-08-13 06:30 | 44056.2708 | 0 | 11.3346 | 39.95
2020-08-13 07:00 | 44056.2917 | 0 | 11.7696 | 39.95
2020-08-13 07:30 | 44056.3125 | 0 | 11.5284 | 39.95
2020-08-13 08:00 | 44056.3333 | 0 | 11.0052 | 39.95
2020-08-13 08:30 | 44056.3542 | 0 | 9.9516 | 39.95
2020-08-13 09:00 | 44056.375 | 0 | 9.3666 | 39.95
2020-08-13 09:30 | 44056.3958 | 0 | 8.8791 | 39.95
2020-08-13 10:00 | 44056.4167 | 0 | 8.4803 | 39.95
2020-08-13 10:30 | 44056.4375 | 0 | 8.0819 | 39.95
2020-08-13 11:00 | 44056.4583 | 0 | 8.1123 | 39.95
2020-08-13 11:30 | 44056.4792 | 0 | 7.9446 | 39.95
2020-08-13 12:00 | 44056.5 | 0 | 7.8331 | 39.95
2020-08-13 12:30 | 44056.5208 | 0 | 8.0284 | 39.95
2020-08-13 13:00 | 44056.5417 | 0 | 8.1072 | 39.95
2020-08-13 13:30 | 44056.5625 | 0 | 8.5279 | 39.95
2020-08-13 14:00 | 44056.5833 | 0 | 8.7361 | 39.95
2020-08-13 14:30 | 44056.6042 | 0 | 8.9444 | 39.95
2020-08-13 15:00 | 44056.625 | 0 | 9.2635 | 39.95
2020-08-13 15:30 | 44056.6458 | 0 | 9.8259 | 39.95
2020-08-13 16:00 | 44056.6667 | 0 | 10.4151 | 39.95
2020-08-13 16:30 | 44056.6875 | 0 | 10.9983 | 39.95
2020-08-13 17:00 | 44056.7083 | 0 | 11.4567 | 39.95
2020-08-13 17:30 | 44056.7292 | 0 | 12.0397 | 39.95
2020-08-13 18:00 | 44056.75 | 0 | 12.6517 | 39.95
2020-08-13 18:30 | 44056.7708 | 0 | 12.724 | 39.95
2020-08-13 19:00 | 44056.7917 | 0 | 12.3395 | 39.95
2020-08-13 19:30 | 44056.8125 | 0 | 12.0373 | 39.95
2020-08-13 20:00 | 44056.8333 | 0 | 12.0371 | 39.95
2020-08-13 20:30 | 44056.8542 | 0 | 11.4509 | 39.95
2020-08-13 21:00 | 44056.875 | 0 | 10.9008 | 39.95
2020-08-13 21:30 | 44056.8958 | 0 | 10.496 | 39.95
2020-08-13 22:00 | 44056.9167 | 0 | 10.1149 | 39.95
2020-08-13 22:30 | 44056.9375 | 0 | 9.3533 | 39.95
2020-08-13 23:00 | 44056.9583 | 0 | 8.8113 | 39.95
2020-08-13 23:30 | 44056.9792 | 0 | 8.3911 | 39.95
2020-08-14 | 44057 | 0 | 7.789 | 39.95
2020-08-14 00:30 | 44057.0208 | 0 | 7.3524 | 39.95
2020-08-14 01:00 | 44057.0417 | 0 | 7.152 | 39.95
2020-08-14 01:30 | 44057.0625 | 0 | 7.0125 | 39.95
2020-08-14 02:00 | 44057.0833 | 0 | 7.0012 | 39.95
2020-08-14 02:30 | 44057.1042 | 0 | 6.8671 | 39.95
2020-08-14 03:00 | 44057.125 | 0 | 6.8282 | 39.95
2020-08-14 03:30 | 44057.1458 | 0 | 6.7779 | 39.95
2020-08-14 04:00 | 44057.1667 | 0 | 6.8247 | 39.95
2020-08-14 04:30 | 44057.1875 | 0 | 7.0575 | 39.95
2020-08-14 05:00 | 44057.2083 | 0 | 7.4278 | 39.95
2020-08-14 05:30 | 44057.2292 | 0 | 7.7874 | 39.95
2020-08-14 06:00 | 44057.25 | 0 | 8.2874 | 39.95
2020-08-14 06:30 | 44057.2708 | 0 | 8.5479 | 39.95
2020-08-14 07:00 | 44057.2917 | 0 | 9.0897 | 39.95
2020-08-14 07:30 | 44057.3125 | 0 | 9.1782 | 39.95
2020-08-14 08:00 | 44057.3333 | 0 | 9.3146 | 39.95
2020-08-14 08:30 | 44057.3542 | 0 | 9.292 | 39.95
2020-08-14 09:00 | 44057.375 | 0 | 8.4081 | 39.95
2020-08-14 09:30 | 44057.3958 | 0 | 7.712 | 39.95
2020-08-14 10:00 | 44057.4167 | 0 | 7.5928 | 39.95
2020-08-14 10:30 | 44057.4375 | 0 | 7.2273 | 39.95
2020-08-14 11:00 | 44057.4583 | 0 | 6.8892 | 39.95
2020-08-14 11:30 | 44057.4792 | 0 | 6.707 | 39.95
2020-08-14 12:00 | 44057.5 | 0 | 6.3621 | 39.95
2020-08-14 12:30 | 44057.5208 | 0 | 6.4318 | 39.95
2020-08-14 13:00 | 44057.5417 | 0 | 6.5046 | 39.95
2020-08-14 13:30 | 44057.5625 | 0 | 6.8527 | 39.95
2020-08-14 14:00 | 44057.5833 | 0 | 7.14 | 39.95
2020-08-14 14:30 | 44057.6042 | 0 | 7.5609 | 39.95
2020-08-14 15:00 | 44057.625 | 0 | 7.9248 | 39.95
2020-08-14 15:30 | 44057.6458 | 0 | 8.4355 | 39.95
2020-08-14 16:00 | 44057.6667 | 0 | 9.0869 | 39.95
2020-08-14 16:30 | 44057.6875 | 0 | 9.9118 | 39.95
2020-08-14 17:00 | 44057.7083 | 0 | 10.2509 | 39.95
2020-08-14 17:30 | 44057.7292 | 0 | 10.9877 | 39.95
2020-08-14 18:00 | 44057.75 | 0 | 11.3152 | 39.95
2020-08-14 18:30 | 44057.7708 | 0 | 11.3317 | 39.95
2020-08-14 19:00 | 44057.7917 | 0 | 11.0767 | 39.95
2020-08-14 19:30 | 44057.8125 | 0 | 10.879 | 39.95
2020-08-14 20:00 | 44057.8333 | 0 | 10.7101 | 39.95
2020-08-14 20:30 | 44057.8542 | 0 | 10.2357 | 39.95
2020-08-14 21:00 | 44057.875 | 0 | 9.8501 | 39.95
2020-08-14 21:30 | 44057.8958 | 0 | 9.6904 | 39.95
2020-08-14 22:00 | 44057.9167 | 0 | 9.2745 | 39.95
2020-08-14 22:30 | 44057.9375 | 0 | 8.7952 | 39.95
2020-08-14 23:00 | 44057.9583 | 0 | 8.3687 | 39.95
2020-08-14 23:30 | 44057.9792 | 0 | 7.9397 | 39.95
2020-08-15 | 44058 | 0 | 7.5128 | 39.95
2020-08-15 00:30 | 44058.0208 | 0 | 7.0692 | 39.95
2020-08-15 01:00 | 44058.0417 | 0 | 6.8895 | 39.95
2020-08-15 01:30 | 44058.0625 | 0 | 6.7892 | 39.95
2020-08-15 02:00 | 44058.0833 | 0 | 6.7742 | 39.95
2020-08-15 02:30 | 44058.1042 | 0 | 6.7443 | 39.95
2020-08-15 03:00 | 44058.125 | 0 | 6.6923 | 39.95
2020-08-15 03:30 | 44058.1458 | 0 | 6.7576 | 39.95
2020-08-15 04:00 | 44058.1667 | 0 | 6.8729 | 39.95
2020-08-15 04:30 | 44058.1875 | 0 | 6.9176 | 39.95
2020-08-15 05:00 | 44058.2083 | 0 | 7.091 | 39.95
2020-08-15 05:30 | 44058.2292 | 0 | 7.3495 | 39.95
2020-08-15 06:00 | 44058.25 | 0 | 7.7569 | 39.95
2020-08-15 06:30 | 44058.2708 | 0 | 8.0178 | 39.95
2020-08-15 07:00 | 44058.2917 | 0 | 8.5789 | 39.95
2020-08-15 07:30 | 44058.3125 | 0 | 8.4045 | 39.95
2020-08-15 08:00 | 44058.3333 | 0 | 9.3067 | 39.95
2020-08-15 08:30 | 44058.3542 | 0 | 9.4655 | 39.95
2020-08-15 09:00 | 44058.375 | 0 | 8.6781 | 39.95
2020-08-15 09:30 | 44058.3958 | 0 | 8.4456 | 39.95
2020-08-15 10:00 | 44058.4167 | 0 | 8.813 | 39.95
2020-08-15 10:30 | 44058.4375 | 0 | 7.8442 | 39.95
2020-08-15 11:00 | 44058.4583 | 0 | 6.3651 | 39.95
2020-08-15 11:30 | 44058.4792 | 0 | 8.5561 | 39.95
2020-08-15 12:00 | 44058.5 | 0 | 7.9396 | 39.95
2020-08-15 12:30 | 44058.5208 | 0 | 8.3862 | 39.95
2020-08-15 13:00 | 44058.5417 | 0 | 6.882 | 39.95
2020-08-15 13:30 | 44058.5625 | 0 | 6.8293 | 39.95
2020-08-15 14:00 | 44058.5833 | 0 | 9.4995 | 39.95
2020-08-15 14:30 | 44058.6042 | 0 | 9.789 | 39.95
2020-08-15 15:00 | 44058.625 | 0 | 9.3357 | 39.95
2020-08-15 15:30 | 44058.6458 | 0 | 9.5189 | 39.95
2020-08-15 16:00 | 44058.6667 | 0 | 9.6986 | 39.95
2020-08-15 16:30 | 44058.6875 | 0 | 10.3177 | 39.95
2020-08-15 17:00 | 44058.7083 | 0 | 10.2805 | 39.95
2020-08-15 17:30 | 44058.7292 | 0 | 10.8021 | 39.95
2020-08-15 18:00 | 44058.75 | 0 | 11.1217 | 39.95
2020-08-15 18:30 | 44058.7708 | 0 | 11.2201 | 39.95
2020-08-15 19:00 | 44058.7917 | 0 | 10.9199 | 39.95
2020-08-15 19:30 | 44058.8125 | 0 | 10.7069 | 39.95
2020-08-15 20:00 | 44058.8333 | 0 | 10.6306 | 39.95
2020-08-15 20:30 | 44058.8542 | 0 | 10.1926 | 39.95
2020-08-15 21:00 | 44058.875 | 0 | 9.7634 | 39.95
2020-08-15 21:30 | 44058.8958 | 0 | 9.6254 | 39.95
2020-08-15 22:00 | 44058.9167 | 0 | 9.3009 | 39.95
2020-08-15 22:30 | 44058.9375 | 0 | 8.818 | 39.95
2020-08-15 23:00 | 44058.9583 | 0 | 8.4257 | 39.95
2020-08-15 23:30 | 44058.9792 | 0 | 7.9389 | 39.95
2020-08-16 | 44059 | 0 | 7.491 | 39.95
2020-08-16 00:30 | 44059.0208 | 0 | 7.1928 | 39.95
2020-08-16 01:00 | 44059.0417 | 0 | 6.92 | 39.95
2020-08-16 01:30 | 44059.0625 | 0 | 6.8619 | 39.95
2020-08-16 02:00 | 44059.0833 | 0 | 6.8503 | 39.95
2020-08-16 02:30 | 44059.1042 | 0 | 6.7519 | 39.95
2020-08-16 03:00 | 44059.125 | 0 | 6.7445 | 39.95
2020-08-16 03:30 | 44059.1458 | 0 | 6.642 | 39.95
2020-08-16 04:00 | 44059.1667 | 0 | 6.5991 | 39.95
2020-08-16 04:30 | 44059.1875 | 0 | 6.6162 | 39.95
2020-08-16 05:00 | 44059.2083 | 0 | 6.7204 | 39.95
2020-08-16 05:30 | 44059.2292 | 0 | 6.9794 | 39.95
2020-08-16 06:00 | 44059.25 | 0 | 7.2615 | 39.95
2020-08-16 06:30 | 44059.2708 | 0 | 7.3306 | 39.95
2020-08-16 07:00 | 44059.2917 | 0 | 7.3473 | 39.95
2020-08-16 07:30 | 44059.3125 | 0 | 7.325 | 39.95
2020-08-16 08:00 | 44059.3333 | 0 | 7.1537 | 39.95
2020-08-16 08:30 | 44059.3542 | 0 | 6.9673 | 39.95
2020-08-16 09:00 | 44059.375 | 0 | 6.5952 | 39.95
2020-08-16 09:30 | 44059.3958 | 0 | 6.2345 | 39.95
2020-08-16 10:00 | 44059.4167 | 0 | 6.0354 | 39.95
2020-08-16 10:30 | 44059.4375 | 0 | 5.795 | 39.95
2020-08-16 11:00 | 44059.4583 | 0 | 5.7195 | 39.95
2020-08-16 11:30 | 44059.4792 | 0 | 5.9406 | 39.95
2020-08-16 12:00 | 44059.5 | 0 | 5.2703 | 39.95
2020-08-16 12:30 | 44059.5208 | 0 | 5.2578 | 39.95
2020-08-16 13:00 | 44059.5417 | 0 | 5.8078 | 39.95
2020-08-16 13:30 | 44059.5625 | 0 | 5.8553 | 39.95
2020-08-16 14:00 | 44059.5833 | 0 | 6.311 | 39.95
2020-08-16 14:30 | 44059.6042 | 0 | 6.6018 | 39.95
2020-08-16 15:00 | 44059.625 | 0 | 7.2115 | 39.95
2020-08-16 15:30 | 44059.6458 | 0 | 7.7348 | 39.95
2020-08-16 16:00 | 44059.6667 | 0 | 8.4601 | 39.95
2020-08-16 16:30 | 44059.6875 | 0 | 9.6258 | 39.95
2020-08-16 17:00 | 44059.7083 | 0 | 10.3888 | 39.95
2020-08-16 17:30 | 44059.7292 | 0 | 11.3276 | 39.95
2020-08-16 18:00 | 44059.75 | 0 | 12.0786 | 39.95
2020-08-16 18:30 | 44059.7708 | 0 | 12.1869 | 39.95
2020-08-16 19:00 | 44059.7917 | 0 | 11.9527 | 39.95
2020-08-16 19:30 | 44059.8125 | 0 | 11.5124 | 39.95
2020-08-16 20:00 | 44059.8333 | 0 | 11.4642 | 39.95
2020-08-16 20:30 | 44059.8542 | 0 | 10.8328 | 39.95
2020-08-16 21:00 | 44059.875 | 0 | 10.363 | 39.95
2020-08-16 21:30 | 44059.8958 | 0 | 9.9992 | 39.95
2020-08-16 22:00 | 44059.9167 | 0 | 9.5594 | 39.95
2020-08-16 22:30 | 44059.9375 | 0 | 8.7738 | 39.95
2020-08-16 23:00 | 44059.9583 | 0 | 8.3012 | 39.95
2020-08-16 23:30 | 44059.9792 | 0 | 7.9032 | 39.95
2020-08-17 | 44060 | 0 | 7.4704 | 39.95
2020-08-17 00:30 | 44060.0208 | 0 | 7.2 | 39.95
2020-08-17 01:00 | 44060.0417 | 0 | 6.9954 | 39.95
2020-08-17 01:30 | 44060.0625 | 0 | 7.0499 | 39.95
2020-08-17 02:00 | 44060.0833 | 0 | 6.9623 | 39.95
2020-08-17 02:30 | 44060.1042 | 0 | 6.9736 | 39.95
2020-08-17 03:00 | 44060.125 | 0 | 7.0998 | 39.95
2020-08-17 03:30 | 44060.1458 | 0 | 7.139 | 39.95
2020-08-17 04:00 | 44060.1667 | 0 | 7.2379 | 39.95
2020-08-17 04:30 | 44060.1875 | 0 | 7.5599 | 39.95
2020-08-17 05:00 | 44060.2083 | 0 | 8.2847 | 39.95
2020-08-17 05:30 | 44060.2292 | 0 | 9.0966 | 39.95
2020-08-17 06:00 | 44060.25 | 0 | 10.367 | 39.95
2020-08-17 06:30 | 44060.2708 | 0 | 11.6744 | 39.95
2020-08-17 07:00 | 44060.2917 | 0 | 12.2002 | 39.95
2020-08-17 07:30 | 44060.3125 | 0 | 11.7541 | 39.95
2020-08-17 08:00 | 44060.3333 | 0 | 10.9775 | 39.95
2020-08-17 08:30 | 44060.3542 | 0 | 10.1327 | 39.95
2020-08-17 09:00 | 44060.375 | 0 | 9.35 | 39.95
2020-08-17 09:30 | 44060.3958 | 0 | 8.6883 | 39.95
2020-08-17 10:00 | 44060.4167 | 0 | 8.2854 | 39.95
2020-08-17 10:30 | 44060.4375 | 0 | 7.8493 | 39.95
2020-08-17 11:00 | 44060.4583 | 0 | 7.6601 | 39.95
2020-08-17 11:30 | 44060.4792 | 0 | 7.5178 | 39.95
2020-08-17 12:00 | 44060.5 | 0 | 7.4199 | 39.95
2020-08-17 12:30 | 44060.5208 | 0 | 7.5912 | 39.95
2020-08-17 13:00 | 44060.5417 | 0 | 7.691 | 39.95
2020-08-17 13:30 | 44060.5625 | 0 | 7.9132 | 39.95
2020-08-17 14:00 | 44060.5833 | 0 | 8.2839 | 39.95
2020-08-17 14:30 | 44060.6042 | 0 | 8.4755 | 39.95
2020-08-17 15:00 | 44060.625 | 0 | 8.8906 | 39.95
2020-08-17 15:30 | 44060.6458 | 0 | 9.5554 | 39.95
2020-08-17 16:00 | 44060.6667 | 0 | 10.2371 | 39.95
2020-08-17 16:30 | 44060.6875 | 0 | 11.1012 | 39.95
2020-08-17 17:00 | 44060.7083 | 0 | 11.8739 | 39.95
2020-08-17 17:30 | 44060.7292 | 0 | 13.095 | 39.95
2020-08-17 18:00 | 44060.75 | 0 | 13.9248 | 39.95
2020-08-17 18:30 | 44060.7708 | 0 | 14.2234 | 39.95
2020-08-17 19:00 | 44060.7917 | 0 | 13.8553 | 39.95
2020-08-17 19:30 | 44060.8125 | 0 | 13.8187 | 39.95
2020-08-17 20:00 | 44060.8333 | 0 | 13.4804 | 39.95
2020-08-17 20:30 | 44060.8542 | 0 | 12.7604 | 39.95
2020-08-17 21:00 | 44060.875 | 0 | 12.2527 | 39.95
2020-08-17 21:30 | 44060.8958 | 0 | 11.6193 | 39.95
2020-08-17 22:00 | 44060.9167 | 0 | 10.9242 | 39.95
2020-08-17 22:30 | 44060.9375 | 0 | 10.2311 | 39.95
2020-08-17 23:00 | 44060.9583 | 0 | 9.6145 | 39.95
2020-08-17 23:30 | 44060.9792 | 0 | 9.0639 | 39.95
2020-08-18 | 44061 | 0 | 8.4775 | 39.95
2020-08-18 00:30 | 44061.0208 | 0 | 7.9333 | 39.95
2020-08-18 01:00 | 44061.0417 | 0 | 7.7084 | 39.95
2020-08-18 01:30 | 44061.0625 | 0 | 7.565 | 39.95
2020-08-18 02:00 | 44061.0833 | 0 | 7.5653 | 39.95
2020-08-18 02:30 | 44061.1042 | 0 | 7.4931 | 39.95
2020-08-18 03:00 | 44061.125 | 0 | 7.5707 | 39.95
2020-08-18 03:30 | 44061.1458 | 0 | 7.5597 | 39.95
2020-08-18 04:00 | 44061.1667 | 0 | 7.7548 | 39.95
2020-08-18 04:30 | 44061.1875 | 0 | 8.1908 | 39.95
2020-08-18 05:00 | 44061.2083 | 0 | 9.0199 | 39.95
2020-08-18 05:30 | 44061.2292 | 0 | 10.0337 | 39.95
2020-08-18 06:00 | 44061.25 | 0 | 11.4 | 39.95
2020-08-18 06:30 | 44061.2708 | 0 | 12.6143 | 39.95
2020-08-18 07:00 | 44061.2917 | 0 | 13.4601 | 39.95
2020-08-18 07:30 | 44061.3125 | 0 | 12.8196 | 39.95
2020-08-18 08:00 | 44061.3333 | 0 | 11.6542 | 39.95
2020-08-18 08:30 | 44061.3542 | 0 | 10.6735 | 39.95
2020-08-18 09:00 | 44061.375 | 0 | 9.9284 | 39.95
2020-08-18 09:30 | 44061.3958 | 0 | 9.4655 | 39.95
2020-08-18 10:00 | 44061.4167 | 0 | 9.0242 | 39.95
2020-08-18 10:30 | 44061.4375 | 0 | 8.6855 | 39.95
2020-08-18 11:00 | 44061.4583 | 0 | 8.4898 | 39.95
2020-08-18 11:30 | 44061.4792 | 0 | 8.531 | 39.95
2020-08-18 12:00 | 44061.5 | 0 | 8.2224 | 39.95
2020-08-18 12:30 | 44061.5208 | 0 | 8.4665 | 39.95
2020-08-18 13:00 | 44061.5417 | 0 | 8.8666 | 39.95
2020-08-18 13:30 | 44061.5625 | 0 | 10.4103 | 39.95
2020-08-18 14:00 | 44061.5833 | 0 | 11.2547 | 39.95
2020-08-18 14:30 | 44061.6042 | 0 | 11.3517 | 39.95
2020-08-18 15:00 | 44061.625 | 0 | 10.9528 | 39.95
2020-08-18 15:30 | 44061.6458 | 0 | 11.1242 | 39.95
2020-08-18 16:00 | 44061.6667 | 0 | 11.037 | 39.95
2020-08-18 16:30 | 44061.6875 | 0 | 11.8802 | 39.95
2020-08-18 17:00 | 44061.7083 | 0 | 12.5421 | 39.95
2020-08-18 17:30 | 44061.7292 | 0 | 13.5698 | 39.95
2020-08-18 18:00 | 44061.75 | 0 | 14.3107 | 39.95
2020-08-18 18:30 | 44061.7708 | 0 | 14.4789 | 39.95
2020-08-18 19:00 | 44061.7917 | 0 | 14.1867 | 39.95
2020-08-18 19:30 | 44061.8125 | 0 | 13.8557 | 39.95
2020-08-18 20:00 | 44061.8333 | 0 | 13.6279 | 39.95
2020-08-18 20:30 | 44061.8542 | 0 | 12.9913 | 39.95
2020-08-18 21:00 | 44061.875 | 0 | 12.3154 | 39.95
2020-08-18 21:30 | 44061.8958 | 0 | 11.862 | 39.95
2020-08-18 22:00 | 44061.9167 | 0 | 11.3265 | 39.95
2020-08-18 22:30 | 44061.9375 | 0 | 10.4263 | 39.95
2020-08-18 23:00 | 44061.9583 | 0 | 9.7392 | 39.95
2020-08-18 23:30 | 44061.9792 | 0 | 9.1147 | 39.95
2020-08-19 | 44062 | 0 | 8.5383 | 39.95
2020-08-19 00:30 | 44062.0208 | 0 | 8.0004 | 39.95
2020-08-19 01:00 | 44062.0417 | 0 | 7.7906 | 39.95
2020-08-19 01:30 | 44062.0625 | 0 | 7.7994 | 39.95
2020-08-19 02:00 | 44062.0833 | 0 | 7.5867 | 39.95
2020-08-19 02:30 | 44062.1042 | 0 | 7.6267 | 39.95
2020-08-19 03:00 | 44062.125 | 0 | 7.6433 | 39.95
2020-08-19 03:30 | 44062.1458 | 0 | 7.7364 | 39.95
2020-08-19 04:00 | 44062.1667 | 0 | 8.0612 | 39.95
2020-08-19 04:30 | 44062.1875 | 0 | 8.5377 | 39.95
2020-08-19 05:00 | 44062.2083 | 0 | 9.1788 | 39.95
2020-08-19 05:30 | 44062.2292 | 0 | 10.0853 | 39.95
2020-08-19 06:00 | 44062.25 | 0 | 11.1433 | 39.95
2020-08-19 06:30 | 44062.2708 | 0 | 12.1455 | 39.95
2020-08-19 07:00 | 44062.2917 | 0 | 12.4746 | 39.95
2020-08-19 07:30 | 44062.3125 | 0 | 12.0348 | 39.95
2020-08-19 08:00 | 44062.3333 | 0 | 11.4684 | 39.95
2020-08-19 08:30 | 44062.3542 | 0 | 10.575 | 39.95
2020-08-19 09:00 | 44062.375 | 0 | 9.7523 | 39.95
2020-08-19 09:30 | 44062.3958 | 0 | 9.2472 | 39.95
2020-08-19 10:00 | 44062.4167 | 0 | 8.9463 | 39.95
2020-08-19 10:30 | 44062.4375 | 0 | 8.7282 | 39.95
2020-08-19 11:00 | 44062.4583 | 0 | 8.4547 | 39.95
2020-08-19 11:30 | 44062.4792 | 0 | 8.522 | 39.95
2020-08-19 12:00 | 44062.5 | 0 | 8.3913 | 39.95
2020-08-19 12:30 | 44062.5208 | 0 | 8.4139 | 39.95
2020-08-19 13:00 | 44062.5417 | 0 | 8.6881 | 39.95
2020-08-19 13:30 | 44062.5625 | 0 | 8.8659 | 39.95
2020-08-19 14:00 | 44062.5833 | 0 | 9.4778 | 39.95
2020-08-19 14:30 | 44062.6042 | 0 | 10.2693 | 39.95
2020-08-19 15:00 | 44062.625 | 0 | 11.1033 | 39.95
2020-08-19 15:30 | 44062.6458 | 0 | 10.7799 | 39.95
2020-08-19 16:00 | 44062.6667 | 0 | 11.1595 | 39.95
2020-08-19 16:30 | 44062.6875 | 0 | 11.8996 | 39.95
2020-08-19 17:00 | 44062.7083 | 0 | 12.9252 | 39.95
2020-08-19 17:30 | 44062.7292 | 0 | 13.9799 | 39.95
2020-08-19 18:00 | 44062.75 | 0 | 14.3877 | 39.95
2020-08-19 18:30 | 44062.7708 | 0 | 14.6637 | 39.95
2020-08-19 19:00 | 44062.7917 | 0 | 14.5044 | 39.95
2020-08-19 19:30 | 44062.8125 | 0 | 14.1787 | 39.95
2020-08-19 20:00 | 44062.8333 | 0 | 13.8071 | 39.95
2020-08-19 20:30 | 44062.8542 | 0 | 13.2188 | 39.95
2020-08-19 21:00 | 44062.875 | 0 | 12.655 | 39.95
2020-08-19 21:30 | 44062.8958 | 0 | 12.3257 | 39.95
2020-08-19 22:00 | 44062.9167 | 0 | 11.6609 | 39.95
2020-08-19 22:30 | 44062.9375 | 0 | 10.7911 | 39.95
2020-08-19 23:00 | 44062.9583 | 0 | 10.1675 | 39.95
2020-08-19 23:30 | 44062.9792 | 0 | 9.6103 | 39.95
2020-08-20 | 44063 | 0 | 9.0644 | 39.95
2020-08-20 00:30 | 44063.0208 | 0 | 8.5791 | 39.95
2020-08-20 01:00 | 44063.0417 | 0 | 8.3654 | 39.95
2020-08-20 01:30 | 44063.0625 | 0 | 8.26 | 39.95
2020-08-20 02:00 | 44063.0833 | 0 | 8.0936 | 39.95
2020-08-20 02:30 | 44063.1042 | 0 | 7.6042 | 39.95
2020-08-20 03:00 | 44063.125 | 0 | 7.6916 | 39.95
2020-08-20 03:30 | 44063.1458 | 0 | 7.5434 | 39.95
2020-08-20 04:00 | 44063.1667 | 0 | 7.7982 | 39.95
2020-08-20 04:30 | 44063.1875 | 0 | 8.1515 | 39.95
2020-08-20 05:00 | 44063.2083 | 0 | 8.9398 | 39.95
2020-08-20 05:30 | 44063.2292 | 0 | 9.6197 | 39.95
2020-08-20 06:00 | 44063.25 | 0 | 10.5971 | 39.95
2020-08-20 06:30 | 44063.2708 | 0 | 11.5349 | 39.95
2020-08-20 07:00 | 44063.2917 | 0 | 11.7727 | 39.95
2020-08-20 07:30 | 44063.3125 | 0 | 11.2124 | 39.95
2020-08-20 08:00 | 44063.3333 | 0 | 10.999 | 39.95
2020-08-20 08:30 | 44063.3542 | 0 | 10.3114 | 39.95
2020-08-20 09:00 | 44063.375 | 0 | 9.8196 | 39.95
2020-08-20 09:30 | 44063.3958 | 0 | 9.2138 | 39.95
2020-08-20 10:00 | 44063.4167 | 0 | 8.7698 | 39.95
2020-08-20 10:30 | 44063.4375 | 0 | 8.6421 | 39.95
2020-08-20 11:00 | 44063.4583 | 0 | 8.6094 | 39.95
2020-08-20 11:30 | 44063.4792 | 0 | 8.4693 | 39.95
2020-08-20 12:00 | 44063.5 | 0 | 8.302 | 39.95
2020-08-20 12:30 | 44063.5208 | 0 | 8.2931 | 39.95
2020-08-20 13:00 | 44063.5417 | 0 | 8.5776 | 39.95
2020-08-20 13:30 | 44063.5625 | 0 | 9.1253 | 39.95
2020-08-20 14:00 | 44063.5833 | 0 | 9.4302 | 39.95
2020-08-20 14:30 | 44063.6042 | 0 | 9.5697 | 39.95
2020-08-20 15:00 | 44063.625 | 0 | 9.905 | 39.95
2020-08-20 15:30 | 44063.6458 | 0 | 10.4487 | 39.95
2020-08-20 16:00 | 44063.6667 | 0 | 11.196 | 39.95
2020-08-20 16:30 | 44063.6875 | 0 | 11.8104 | 39.95
2020-08-20 17:00 | 44063.7083 | 0 | 12.3619 | 39.95
2020-08-20 17:30 | 44063.7292 | 0 | 13.4016 | 39.95
2020-08-20 18:00 | 44063.75 | 0 | 13.7906 | 39.95
2020-08-20 18:30 | 44063.7708 | 0 | 14.0103 | 39.95
2020-08-20 19:00 | 44063.7917 | 0 | 13.8143 | 39.95
2020-08-20 19:30 | 44063.8125 | 0 | 13.4854 | 39.95
2020-08-20 20:00 | 44063.8333 | 0 | 13.2825 | 39.95
2020-08-20 20:30 | 44063.8542 | 0 | 12.7775 | 39.95
2020-08-20 21:00 | 44063.875 | 0 | 12.2855 | 39.95
2020-08-20 21:30 | 44063.8958 | 0 | 11.9552 | 39.95
2020-08-20 22:00 | 44063.9167 | 0 | 11.4358 | 39.95
2020-08-20 22:30 | 44063.9375 | 0 | 10.6291 | 39.95
2020-08-20 23:00 | 44063.9583 | 0 | 9.943 | 39.95
2020-08-20 23:30 | 44063.9792 | 0 | 9.2538 | 39.95
2020-08-21 | 44064 | 0 | 8.6033 | 39.95
2020-08-21 00:30 | 44064.0208 | 0 | 8.0843 | 39.95
2020-08-21 01:00 | 44064.0417 | 0 | 7.9672 | 39.95
2020-08-21 01:30 | 44064.0625 | 0 | 7.8162 | 39.95
2020-08-21 02:00 | 44064.0833 | 0 | 7.7494 | 39.95
2020-08-21 02:30 | 44064.1042 | 0 | 7.6692 | 39.95
2020-08-21 03:00 | 44064.125 | 0 | 7.7849 | 39.95
2020-08-21 03:30 | 44064.1458 | 0 | 7.7514 | 39.95
2020-08-21 04:00 | 44064.1667 | 0 | 8.057 | 39.95
2020-08-21 04:30 | 44064.1875 | 0 | 8.3922 | 39.95
2020-08-21 05:00 | 44064.2083 | 0 | 9.1003 | 39.95
2020-08-21 05:30 | 44064.2292 | 0 | 10.0645 | 39.95
2020-08-21 06:00 | 44064.25 | 0 | 11.1836 | 39.95
2020-08-21 06:30 | 44064.2708 | 0 | 12.0901 | 39.95
2020-08-21 07:00 | 44064.2917 | 0 | 12.833 | 39.95
2020-08-21 07:30 | 44064.3125 | 0 | 13.1022 | 39.95
2020-08-21 08:00 | 44064.3333 | 0 | 11.3383 | 39.95
2020-08-21 08:30 | 44064.3542 | 0 | 10.9431 | 39.95
2020-08-21 09:00 | 44064.375 | 0 | 10.0495 | 39.95
2020-08-21 09:30 | 44064.3958 | 0 | 9.6113 | 39.95
2020-08-21 10:00 | 44064.4167 | 0 | 8.8851 | 39.95
2020-08-21 10:30 | 44064.4375 | 0 | 8.8115 | 39.95
2020-08-21 11:00 | 44064.4583 | 0 | 8.967 | 39.95
2020-08-21 11:30 | 44064.4792 | 0 | 8.4491 | 39.95
2020-08-21 12:00 | 44064.5 | 0 | 8.1978 | 39.95
2020-08-21 12:30 | 44064.5208 | 0 | 8.0465 | 39.95
2020-08-21 13:00 | 44064.5417 | 0 | 8.3353 | 39.95
2020-08-21 13:30 | 44064.5625 | 0 | 8.5147 | 39.95
2020-08-21 14:00 | 44064.5833 | 0 | 8.7695 | 39.95
2020-08-21 14:30 | 44064.6042 | 0 | 9.6163 | 39.95
2020-08-21 15:00 | 44064.625 | 0 | 9.9016 | 39.95
2020-08-21 15:30 | 44064.6458 | 0 | 10.3013 | 39.95
2020-08-21 16:00 | 44064.6667 | 0 | 10.632 | 39.95
2020-08-21 16:30 | 44064.6875 | 0 | 11.5916 | 39.95
2020-08-21 17:00 | 44064.7083 | 0 | 12.0168 | 39.95
2020-08-21 17:30 | 44064.7292 | 0 | 12.7975 | 39.95
2020-08-21 18:00 | 44064.75 | 0 | 13.042 | 39.95
2020-08-21 18:30 | 44064.7708 | 0 | 13.3819 | 39.95
2020-08-21 19:00 | 44064.7917 | 0 | 13.0867 | 39.95
2020-08-21 19:30 | 44064.8125 | 0 | 12.9007 | 39.95
2020-08-21 20:00 | 44064.8333 | 0 | 12.7526 | 39.95
2020-08-21 20:30 | 44064.8542 | 0 | 12.1263 | 39.95
2020-08-21 21:00 | 44064.875 | 0 | 11.9542 | 39.95
2020-08-21 21:30 | 44064.8958 | 0 | 11.6968 | 39.95
2020-08-21 22:00 | 44064.9167 | 0 | 11.1414 | 39.95
2020-08-21 22:30 | 44064.9375 | 0 | 10.3869 | 39.95
2020-08-21 23:00 | 44064.9583 | 0 | 9.8629 | 39.95
2020-08-21 23:30 | 44064.9792 | 0 | 9.3404 | 39.95
2020-08-22 | 44065 | 0 | 8.7521 | 39.95
2020-08-22 00:30 | 44065.0208 | 0 | 8.1309 | 39.95
2020-08-22 01:00 | 44065.0417 | 0 | 7.8388 | 39.95
2020-08-22 01:30 | 44065.0625 | 0 | 7.7231 | 39.95
2020-08-22 02:00 | 44065.0833 | 0 | 7.5986 | 39.95
2020-08-22 02:30 | 44065.1042 | 0 | 7.5986 | 39.95
2020-08-22 03:00 | 44065.125 | 0 | 7.4265 | 39.95
2020-08-22 03:30 | 44065.1458 | 0 | 7.4423 | 39.95
2020-08-22 04:00 | 44065.1667 | 0 | 7.5988 | 39.95
2020-08-22 04:30 | 44065.1875 | 0 | 7.7758 | 39.95
2020-08-22 05:00 | 44065.2083 | 0 | 7.9562 | 39.95
2020-08-22 05:30 | 44065.2292 | 0 | 8.3286 | 39.95
2020-08-22 06:00 | 44065.25 | 0 | 8.7099 | 39.95
2020-08-22 06:30 | 44065.2708 | 0 | 8.978 | 39.95
2020-08-22 07:00 | 44065.2917 | 0 | 9.1172 | 39.95
2020-08-22 07:30 | 44065.3125 | 0 | 8.8041 | 39.95
2020-08-22 08:00 | 44065.3333 | 0 | 8.5166 | 39.95
2020-08-22 08:30 | 44065.3542 | 0 | 8.153 | 39.95
2020-08-22 09:00 | 44065.375 | 0 | 9.07 | 39.95
2020-08-22 09:30 | 44065.3958 | 0 | 8.8966 | 39.95
2020-08-22 10:00 | 44065.4167 | 0 | 8.9834 | 39.95
2020-08-22 10:30 | 44065.4375 | 0 | 9.0612 | 39.95
2020-08-22 11:00 | 44065.4583 | 0 | 8.191 | 39.95
2020-08-22 11:30 | 44065.4792 | 0 | 6.6294 | 39.95
2020-08-22 12:00 | 44065.5 | 0 | 6.4877 | 39.95
2020-08-22 12:30 | 44065.5208 | 0 | 6.3758 | 39.95
2020-08-22 13:00 | 44065.5417 | 0 | 6.4933 | 39.95
2020-08-22 13:30 | 44065.5625 | 0 | 6.9001 | 39.95
2020-08-22 14:00 | 44065.5833 | 0 | 7.1634 | 39.95
2020-08-22 14:30 | 44065.6042 | 0 | 7.3422 | 39.95
2020-08-22 15:00 | 44065.625 | 0 | 8.1174 | 39.95
2020-08-22 15:30 | 44065.6458 | 0 | 8.4096 | 39.95
2020-08-22 16:00 | 44065.6667 | 0 | 9.0444 | 39.95
2020-08-22 16:30 | 44065.6875 | 0 | 9.8674 | 39.95
2020-08-22 17:00 | 44065.7083 | 0 | 10.5363 | 39.95
2020-08-22 17:30 | 44065.7292 | 0 | 11.2473 | 39.95
2020-08-22 18:00 | 44065.75 | 0 | 11.6803 | 39.95
2020-08-22 18:30 | 44065.7708 | 0 | 11.8289 | 39.95
2020-08-22 19:00 | 44065.7917 | 0 | 11.7001 | 39.95
2020-08-22 19:30 | 44065.8125 | 0 | 11.3522 | 39.95
2020-08-22 20:00 | 44065.8333 | 0 | 11.1208 | 39.95
2020-08-22 20:30 | 44065.8542 | 0 | 10.7807 | 39.95
2020-08-22 21:00 | 44065.875 | 0 | 10.3844 | 39.95
2020-08-22 21:30 | 44065.8958 | 0 | 9.9992 | 39.95
2020-08-22 22:00 | 44065.9167 | 0 | 9.7533 | 39.95
2020-08-22 22:30 | 44065.9375 | 0 | 9.1763 | 39.95
2020-08-22 23:00 | 44065.9583 | 0 | 8.615 | 39.95
2020-08-22 23:30 | 44065.9792 | 0 | 8.1093 | 39.95
2020-08-23 | 44066 | 0 | 7.6764 | 39.95
2020-08-23 00:30 | 44066.0208 | 0 | 7.299 | 39.95
2020-08-23 01:00 | 44066.0417 | 0 | 7.1705 | 39.95
2020-08-23 01:30 | 44066.0625 | 0 | 7.0458 | 39.95
2020-08-23 02:00 | 44066.0833 | 0 | 7.0348 | 39.95
2020-08-23 02:30 | 44066.1042 | 0 | 7.0069 | 39.95
2020-08-23 03:00 | 44066.125 | 0 | 6.8782 | 39.95
2020-08-23 03:30 | 44066.1458 | 0 | 6.8059 | 39.95
2020-08-23 04:00 | 44066.1667 | 0 | 6.7891 | 39.95
2020-08-23 04:30 | 44066.1875 | 0 | 6.8201 | 39.95
2020-08-23 05:00 | 44066.2083 | 0 | 6.987 | 39.95
2020-08-23 05:30 | 44066.2292 | 0 | 7.2781 | 39.95
2020-08-23 06:00 | 44066.25 | 0 | 7.6773 | 39.95
2020-08-23 06:30 | 44066.2708 | 0 | 7.9164 | 39.95
2020-08-23 07:00 | 44066.2917 | 0 | 7.9838 | 39.95
2020-08-23 07:30 | 44066.3125 | 0 | 7.8219 | 39.95
2020-08-23 08:00 | 44066.3333 | 0 | 7.9672 | 39.95
2020-08-23 08:30 | 44066.3542 | 0 | 7.6949 | 39.95
2020-08-23 09:00 | 44066.375 | 0 | 7.2636 | 39.95
2020-08-23 09:30 | 44066.3958 | 0 | 6.9651 | 39.95
2020-08-23 10:00 | 44066.4167 | 0 | 6.605 | 39.95
2020-08-23 10:30 | 44066.4375 | 0 | 6.0845 | 39.95
2020-08-23 11:00 | 44066.4583 | 0 | 5.7896 | 39.95
2020-08-23 11:30 | 44066.4792 | 0 | 5.6873 | 39.95
2020-08-23 12:00 | 44066.5 | 0 | 5.6351 | 39.95
2020-08-23 12:30 | 44066.5208 | 0 | 5.5777 | 39.95
2020-08-23 13:00 | 44066.5417 | 0 | 5.7549 | 39.95
2020-08-23 13:30 | 44066.5625 | 0 | 6.0355 | 39.95
2020-08-23 14:00 | 44066.5833 | 0 | 6.4523 | 39.95
2020-08-23 14:30 | 44066.6042 | 0 | 6.7658 | 39.95
2020-08-23 15:00 | 44066.625 | 0 | 7.26 | 39.95
2020-08-23 15:30 | 44066.6458 | 0 | 7.8755 | 39.95
2020-08-23 16:00 | 44066.6667 | 0 | 8.7125 | 39.95
2020-08-23 16:30 | 44066.6875 | 0 | 9.7682 | 39.95
2020-08-23 17:00 | 44066.7083 | 0 | 10.669 | 39.95
2020-08-23 17:30 | 44066.7292 | 0 | 11.6754 | 39.95
2020-08-23 18:00 | 44066.75 | 0 | 12.6204 | 39.95
2020-08-23 18:30 | 44066.7708 | 0 | 12.8617 | 39.95
2020-08-23 19:00 | 44066.7917 | 0 | 12.5731 | 39.95
2020-08-23 19:30 | 44066.8125 | 0 | 12.4097 | 39.95
2020-08-23 20:00 | 44066.8333 | 0 | 12.3069 | 39.95
2020-08-23 20:30 | 44066.8542 | 0 | 11.5934 | 39.95
2020-08-23 21:00 | 44066.875 | 0 | 11.06 | 39.95
2020-08-23 21:30 | 44066.8958 | 0 | 10.5778 | 39.95
2020-08-23 22:00 | 44066.9167 | 0 | 10.0123 | 39.95
2020-08-23 22:30 | 44066.9375 | 0 | 8.9093 | 39.95
2020-08-23 23:00 | 44066.9583 | 0 | 8.4841 | 39.95
2020-08-23 23:30 | 44066.9792 | 0 | 7.8884 | 39.95
2020-08-24 | 44067 | 0 | 7.4798 | 39.95
2020-08-24 00:30 | 44067.0208 | 0 | 7.375 | 39.95
2020-08-24 01:00 | 44067.0417 | 0 | 7.2209 | 39.95
2020-08-24 01:30 | 44067.0625 | 0 | 7.1577 | 39.95
2020-08-24 02:00 | 44067.0833 | 0 | 7.2097 | 39.95
2020-08-24 02:30 | 44067.1042 | 0 | 7.1129 | 39.95
2020-08-24 03:00 | 44067.125 | 0 | 7.2173 | 39.95
2020-08-24 03:30 | 44067.1458 | 0 | 7.2117 | 39.95
2020-08-24 04:00 | 44067.1667 | 0 | 7.5826 | 39.95
2020-08-24 04:30 | 44067.1875 | 0 | 7.9673 | 39.95
2020-08-24 05:00 | 44067.2083 | 0 | 8.7593 | 39.95
2020-08-24 05:30 | 44067.2292 | 0 | 9.7876 | 39.95
2020-08-24 06:00 | 44067.25 | 0 | 11.311 | 39.95
2020-08-24 06:30 | 44067.2708 | 0 | 12.6157 | 39.95
2020-08-24 07:00 | 44067.2917 | 0 | 13.3365 | 39.95
2020-08-24 07:30 | 44067.3125 | 0 | 12.5084 | 39.95
2020-08-24 08:00 | 44067.3333 | 0 | 11.6946 | 39.95
2020-08-24 08:30 | 44067.3542 | 0 | 10.7266 | 39.95
2020-08-24 09:00 | 44067.375 | 0 | 10.045 | 39.95
2020-08-24 09:30 | 44067.3958 | 0 | 9.4354 | 39.95
2020-08-24 10:00 | 44067.4167 | 0 | 9.1393 | 39.95
2020-08-24 10:30 | 44067.4375 | 0 | 8.8381 | 39.95
2020-08-24 11:00 | 44067.4583 | 0 | 8.4524 | 39.95
2020-08-24 11:30 | 44067.4792 | 0 | 8.2898 | 39.95
2020-08-24 12:00 | 44067.5 | 0 | 8.1605 | 39.95
2020-08-24 12:30 | 44067.5208 | 0 | 8.0006 | 39.95
2020-08-24 13:00 | 44067.5417 | 0 | 8.2616 | 39.95
2020-08-24 13:30 | 44067.5625 | 0 | 8.4977 | 39.95
2020-08-24 14:00 | 44067.5833 | 0 | 8.7155 | 39.95
2020-08-24 14:30 | 44067.6042 | 0 | 9.0172 | 39.95
2020-08-24 15:00 | 44067.625 | 0 | 9.335 | 39.95
2020-08-24 15:30 | 44067.6458 | 0 | 9.89 | 39.95
2020-08-24 16:00 | 44067.6667 | 0 | 10.5609 | 39.95
2020-08-24 16:30 | 44067.6875 | 0 | 11.4987 | 39.95
2020-08-24 17:00 | 44067.7083 | 0 | 12.1401 | 39.95
2020-08-24 17:30 | 44067.7292 | 0 | 13.4584 | 39.95
2020-08-24 18:00 | 44067.75 | 0 | 14.3251 | 39.95
2020-08-24 18:30 | 44067.7708 | 0 | 14.5775 | 39.95
2020-08-24 19:00 | 44067.7917 | 0 | 14.484 | 39.95
2020-08-24 19:30 | 44067.8125 | 0 | 14.0311 | 39.95
2020-08-24 20:00 | 44067.8333 | 0 | 13.7433 | 39.95
2020-08-24 20:30 | 44067.8542 | 0 | 13.1657 | 39.95
2020-08-24 21:00 | 44067.875 | 0 | 12.6706 | 39.95
2020-08-24 21:30 | 44067.8958 | 0 | 12.2333 | 39.95
2020-08-24 22:00 | 44067.9167 | 0 | 11.2146 | 39.95
2020-08-24 22:30 | 44067.9375 | 0 | 10.5235 | 39.95
2020-08-24 23:00 | 44067.9583 | 0 | 9.742 | 39.95
2020-08-24 23:30 | 44067.9792 | 0 | 9.2728 | 39.95
2020-08-25 | 44068 | 0 | 8.6665 | 39.95
2020-08-25 00:30 | 44068.0208 | 0 | 8.3741 | 39.95
2020-08-25 01:00 | 44068.0417 | 0 | 8.0227 | 39.95
2020-08-25 01:30 | 44068.0625 | 0 | 7.822 | 39.95
2020-08-25 02:00 | 44068.0833 | 0 | 7.8555 | 39.95
2020-08-25 02:30 | 44068.1042 | 0 | 7.8611 | 39.95
2020-08-25 03:00 | 44068.125 | 0 | 7.8498 | 39.95
2020-08-25 03:30 | 44068.1458 | 0 | 7.8501 | 39.95
2020-08-25 04:00 | 44068.1667 | 0 | 8.0569 | 39.95
2020-08-25 04:30 | 44068.1875 | 0 | 8.7026 | 39.95
2020-08-25 05:00 | 44068.2083 | 0 | 9.395 | 39.95
2020-08-25 05:30 | 44068.2292 | 0 | 10.4949 | 39.95
2020-08-25 06:00 | 44068.25 | 0 | 12.0991 | 39.95
2020-08-25 06:30 | 44068.2708 | 0 | 13.4997 | 39.95
2020-08-25 07:00 | 44068.2917 | 0 | 13.9113 | 39.95
2020-08-25 07:30 | 44068.3125 | 0 | 13.3241 | 39.95
2020-08-25 08:00 | 44068.3333 | 0 | 12.3094 | 39.95
2020-08-25 08:30 | 44068.3542 | 0 | 11.2219 | 39.95
2020-08-25 09:00 | 44068.375 | 0 | 10.3406 | 39.95
2020-08-25 09:30 | 44068.3958 | 0 | 9.6264 | 39.95
2020-08-25 10:00 | 44068.4167 | 0 | 9.074 | 39.95
2020-08-25 10:30 | 44068.4375 | 0 | 8.8066 | 39.95
2020-08-25 11:00 | 44068.4583 | 0 | 8.5906 | 39.95
2020-08-25 11:30 | 44068.4792 | 0 | 8.4641 | 39.95
2020-08-25 12:00 | 44068.5 | 0 | 8.3188 | 39.95
2020-08-25 12:30 | 44068.5208 | 0 | 8.2648 | 39.95
2020-08-25 13:00 | 44068.5417 | 0 | 8.6303 | 39.95
2020-08-25 13:30 | 44068.5625 | 0 | 8.6183 | 39.95
2020-08-25 14:00 | 44068.5833 | 0 | 8.818 | 39.95
2020-08-25 14:30 | 44068.6042 | 0 | 9.092 | 39.95
2020-08-25 15:00 | 44068.625 | 0 | 9.4859 | 39.95
2020-08-25 15:30 | 44068.6458 | 0 | 10.1227 | 39.95
2020-08-25 16:00 | 44068.6667 | 0 | 10.7364 | 39.95
2020-08-25 16:30 | 44068.6875 | 0 | 11.7676 | 39.95
2020-08-25 17:00 | 44068.7083 | 0 | 12.4863 | 39.95
2020-08-25 17:30 | 44068.7292 | 0 | 13.6856 | 39.95
2020-08-25 18:00 | 44068.75 | 0 | 14.4101 | 39.95
2020-08-25 18:30 | 44068.7708 | 0 | 14.7527 | 39.95
2020-08-25 19:00 | 44068.7917 | 0 | 14.462 | 39.95
2020-08-25 19:30 | 44068.8125 | 0 | 14.1418 | 39.95
2020-08-25 20:00 | 44068.8333 | 0 | 14.0241 | 39.95
2020-08-25 20:30 | 44068.8542 | 0 | 13.4514 | 39.95
2020-08-25 21:00 | 44068.875 | 0 | 12.9079 | 39.95
2020-08-25 21:30 | 44068.8958 | 0 | 12.2212 | 39.95
2020-08-25 22:00 | 44068.9167 | 0 | 11.5882 | 39.95
2020-08-25 22:30 | 44068.9375 | 0 | 10.6772 | 39.95
2020-08-25 23:00 | 44068.9583 | 0 | 9.9287 | 39.95
2020-08-25 23:30 | 44068.9792 | 0 | 9.3251 | 39.95
2020-08-26 | 44069 | 0 | 8.6443 | 39.95
2020-08-26 00:30 | 44069.0208 | 0 | 8.1637 | 39.95
2020-08-26 01:00 | 44069.0417 | 0 | 8.0566 | 39.95
2020-08-26 01:30 | 44069.0625 | 0 | 7.8946 | 39.95
2020-08-26 02:00 | 44069.0833 | 0 | 7.8944 | 39.95
2020-08-26 02:30 | 44069.1042 | 0 | 7.7661 | 39.95
2020-08-26 03:00 | 44069.125 | 0 | 7.9078 | 39.95
2020-08-26 03:30 | 44069.1458 | 0 | 8.0287 | 39.95
2020-08-26 04:00 | 44069.1667 | 0 | 8.2561 | 39.95
2020-08-26 04:30 | 44069.1875 | 0 | 8.7897 | 39.95
2020-08-26 05:00 | 44069.2083 | 0 | 9.6376 | 39.95
2020-08-26 05:30 | 44069.2292 | 0 | 10.5739 | 39.95
2020-08-26 06:00 | 44069.25 | 0 | 12.0142 | 39.95
2020-08-26 06:30 | 44069.2708 | 0 | 13.21 | 39.95
2020-08-26 07:00 | 44069.2917 | 0 | 14.2219 | 39.95
2020-08-26 07:30 | 44069.3125 | 0 | 13.9025 | 39.95
2020-08-26 08:00 | 44069.3333 | 0 | 12.4121 | 39.95
2020-08-26 08:30 | 44069.3542 | 0 | 11.3382 | 39.95
2020-08-26 09:00 | 44069.375 | 0 | 10.599 | 39.95
2020-08-26 09:30 | 44069.3958 | 0 | 10.2233 | 39.95
2020-08-26 10:00 | 44069.4167 | 0 | 10.6856 | 39.95
2020-08-26 10:30 | 44069.4375 | 0 | 11.1106 | 39.95
2020-08-26 11:00 | 44069.4583 | 0 | 10.349 | 39.95
2020-08-26 11:30 | 44069.4792 | 0 | 10.7065 | 39.95
2020-08-26 12:00 | 44069.5 | 0 | 11.6406 | 39.95
2020-08-26 12:30 | 44069.5208 | 0 | 9.6915 | 39.95
2020-08-26 13:00 | 44069.5417 | 0 | 9.4765 | 39.95
2020-08-26 13:30 | 44069.5625 | 0 | 9.7999 | 39.95
2020-08-26 14:00 | 44069.5833 | 0 | 10.7886 | 39.95
2020-08-26 14:30 | 44069.6042 | 0 | 10.5439 | 39.95
2020-08-26 15:00 | 44069.625 | 0 | 10.2288 | 39.95
2020-08-26 15:30 | 44069.6458 | 0 | 10.5952 | 39.95
2020-08-26 16:00 | 44069.6667 | 0 | 11.2626 | 39.95
2020-08-26 16:30 | 44069.6875 | 0 | 12.1308 | 39.95
2020-08-26 17:00 | 44069.7083 | 0 | 12.7972 | 39.95
2020-08-26 17:30 | 44069.7292 | 0 | 13.7857 | 39.95
2020-08-26 18:00 | 44069.75 | 0 | 14.5237 | 39.95
2020-08-26 18:30 | 44069.7708 | 0 | 14.9668 | 39.95
2020-08-26 19:00 | 44069.7917 | 0 | 14.8564 | 39.95
2020-08-26 19:30 | 44069.8125 | 0 | 14.4565 | 39.95
2020-08-26 20:00 | 44069.8333 | 0 | 14.3532 | 39.95
2020-08-26 20:30 | 44069.8542 | 0 | 13.6842 | 39.95
2020-08-26 21:00 | 44069.875 | 0 | 12.996 | 39.95
2020-08-26 21:30 | 44069.8958 | 0 | 12.5017 | 39.95
2020-08-26 22:00 | 44069.9167 | 0 | 11.6806 | 39.95
2020-08-26 22:30 | 44069.9375 | 0 | 10.7883 | 39.95
2020-08-26 23:00 | 44069.9583 | 0 | 10.0996 | 39.95
2020-08-26 23:30 | 44069.9792 | 0 | 9.6 | 39.95
2020-08-27 | 44070 | 0 | 8.9367 | 39.95
2020-08-27 00:30 | 44070.0208 | 0 | 8.3897 | 39.95
2020-08-27 01:00 | 44070.0417 | 0 | 8.2593 | 39.95
2020-08-27 01:30 | 44070.0625 | 0 | 7.9611 | 39.95
2020-08-27 02:00 | 44070.0833 | 0 | 7.8577 | 39.95
2020-08-27 02:30 | 44070.1042 | 0 | 7.8553 | 39.95
2020-08-27 03:00 | 44070.125 | 0 | 7.8555 | 39.95
2020-08-27 03:30 | 44070.1458 | 0 | 7.8107 | 39.95
2020-08-27 04:00 | 44070.1667 | 0 | 7.947 | 39.95
2020-08-27 04:30 | 44070.1875 | 0 | 8.5029 | 39.95
2020-08-27 05:00 | 44070.2083 | 0 | 9.5198 | 39.95
2020-08-27 05:30 | 44070.2292 | 0 | 10.4399 | 39.95
2020-08-27 06:00 | 44070.25 | 0 | 11.5593 | 39.95
2020-08-27 06:30 | 44070.2708 | 0 | 12.7205 | 39.95
2020-08-27 07:00 | 44070.2917 | 0 | 13.0531 | 39.95
2020-08-27 07:30 | 44070.3125 | 0 | 12.5528 | 39.95
2020-08-27 08:00 | 44070.3333 | 0 | 11.8197 | 39.95
2020-08-27 08:30 | 44070.3542 | 0 | 10.7029 | 39.95
2020-08-27 09:00 | 44070.375 | 0 | 9.8362 | 39.95
2020-08-27 09:30 | 44070.3958 | 0 | 9.3199 | 39.95
2020-08-27 10:00 | 44070.4167 | 0 | 9.3205 | 39.95
2020-08-27 10:30 | 44070.4375 | 0 | 9.3739 | 39.95
2020-08-27 11:00 | 44070.4583 | 0 | 9.8129 | 39.95
2020-08-27 11:30 | 44070.4792 | 0 | 9.654 | 39.95
2020-08-27 12:00 | 44070.5 | 0 | 9.8288 | 39.95
2020-08-27 12:30 | 44070.5208 | 0 | 9.5036 | 39.95
2020-08-27 13:00 | 44070.5417 | 0 | 8.3599 | 39.95
2020-08-27 13:30 | 44070.5625 | 0 | 8.4534 | 39.95
2020-08-27 14:00 | 44070.5833 | 0 | 8.9609 | 39.95
2020-08-27 14:30 | 44070.6042 | 0 | 9.3281 | 39.95
2020-08-27 15:00 | 44070.625 | 0 | 10.2238 | 39.95
2020-08-27 15:30 | 44070.6458 | 0 | 10.2798 | 39.95
2020-08-27 16:00 | 44070.6667 | 0 | 11.3544 | 39.95
2020-08-27 16:30 | 44070.6875 | 0 | 11.4438 | 39.95
2020-08-27 17:00 | 44070.7083 | 0 | 12.2772 | 39.95
2020-08-27 17:30 | 44070.7292 | 0 | 13.416 | 39.95
2020-08-27 18:00 | 44070.75 | 0 | 14.027 | 39.95
2020-08-27 18:30 | 44070.7708 | 0 | 14.5282 | 39.95
2020-08-27 19:00 | 44070.7917 | 0 | 14.3094 | 39.95
2020-08-27 19:30 | 44070.8125 | 0 | 14.0235 | 39.95
2020-08-27 20:00 | 44070.8333 | 0 | 13.9705 | 39.95
2020-08-27 20:30 | 44070.8542 | 0 | 13.3941 | 39.95
2020-08-27 21:00 | 44070.875 | 0 | 12.8984 | 39.95
2020-08-27 21:30 | 44070.8958 | 0 | 12.3989 | 39.95
2020-08-27 22:00 | 44070.9167 | 0 | 11.8075 | 39.95
2020-08-27 22:30 | 44070.9375 | 0 | 10.8965 | 39.95
2020-08-27 23:00 | 44070.9583 | 0 | 10.0008 | 39.95
2020-08-27 23:30 | 44070.9792 | 0 | 9.396 | 39.95
2020-08-28 | 44071 | 0 | 8.6586 | 39.95
2020-08-28 00:30 | 44071.0208 | 0 | 8.1905 | 39.95
2020-08-28 01:00 | 44071.0417 | 0 | 8.0563 | 39.95
2020-08-28 01:30 | 44071.0625 | 0 | 7.8833 | 39.95
2020-08-28 02:00 | 44071.0833 | 0 | 7.8222 | 39.95
2020-08-28 02:30 | 44071.1042 | 0 | 7.8106 | 39.95
2020-08-28 03:00 | 44071.125 | 0 | 7.8388 | 39.95
2020-08-28 03:30 | 44071.1458 | 0 | 7.8556 | 39.95
2020-08-28 04:00 | 44071.1667 | 0 | 8.0736 | 39.95
2020-08-28 04:30 | 44071.1875 | 0 | 8.6406 | 39.95
2020-08-28 05:00 | 44071.2083 | 0 | 9.4429 | 39.95
2020-08-28 05:30 | 44071.2292 | 0 | 10.1449 | 39.95
2020-08-28 06:00 | 44071.25 | 0 | 11.5162 | 39.95
2020-08-28 06:30 | 44071.2708 | 0 | 12.517 | 39.95
2020-08-28 07:00 | 44071.2917 | 0 | 12.7908 | 39.95
2020-08-28 07:30 | 44071.3125 | 0 | 12.1996 | 39.95
2020-08-28 08:00 | 44071.3333 | 0 | 14.0949 | 39.95
2020-08-28 08:30 | 44071.3542 | 0 | 20.2379 | 39.95
2020-08-28 09:00 | 44071.375 | 0 | 19.0186 | 39.95
2020-08-28 09:30 | 44071.3958 | 0 | 17.9286 | 39.95
2020-08-28 10:00 | 44071.4167 | 0 | 17.0653 | 39.95
2020-08-28 10:30 | 44071.4375 | 0 | 16.2637 | 39.95
2020-08-28 11:00 | 44071.4583 | 0 | 15.8129 | 39.95
2020-08-28 11:30 | 44071.4792 | 0 | 15.2419 | 39.95
2020-08-28 12:00 | 44071.5 | 0 | 15.1079 | 39.95
2020-08-28 12:30 | 44071.5208 | 0 | 15.1016 | 39.95
2020-08-28 13:00 | 44071.5417 | 0 | 14.5798 | 39.95
2020-08-28 13:30 | 44071.5625 | 0 | 8.1012 | 39.95
2020-08-28 14:00 | 44071.5833 | 0 | 8.5024 | 39.95
2020-08-28 14:30 | 44071.6042 | 0 | 8.9481 | 39.95
2020-08-28 15:00 | 44071.625 | 0 | 9.5587 | 39.95
2020-08-28 15:30 | 44071.6458 | 0 | 9.9642 | 39.95
2020-08-28 16:00 | 44071.6667 | 0 | 10.7233 | 39.95
2020-08-28 16:30 | 44071.6875 | 0 | 11.3693 | 39.95
2020-08-28 17:00 | 44071.7083 | 0 | 11.7919 | 39.95
2020-08-28 17:30 | 44071.7292 | 0 | 12.5478 | 39.95
2020-08-28 18:00 | 44071.75 | 0 | 12.9436 | 39.95
2020-08-28 18:30 | 44071.7708 | 0 | 13.3248 | 39.95
2020-08-28 19:00 | 44071.7917 | 0 | 13.1764 | 39.95
2020-08-28 19:30 | 44071.8125 | 0 | 12.91 | 39.95
2020-08-28 20:00 | 44071.8333 | 0 | 12.7125 | 39.95
2020-08-28 20:30 | 44071.8542 | 0 | 12.0702 | 39.95
2020-08-28 21:00 | 44071.875 | 0 | 11.6879 | 39.95
2020-08-28 21:30 | 44071.8958 | 0 | 11.4526 | 39.95
2020-08-28 22:00 | 44071.9167 | 0 | 10.8379 | 39.95
2020-08-28 22:30 | 44071.9375 | 0 | 10.1695 | 39.95
2020-08-28 23:00 | 44071.9583 | 0 | 9.6257 | 39.95
2020-08-28 23:30 | 44071.9792 | 0 | 9.1968 | 39.95
2020-08-29 | 44072 | 0 | 8.5864 | 39.95
2020-08-29 00:30 | 44072.0208 | 0 | 8.0188 | 39.95
2020-08-29 01:00 | 44072.0417 | 0 | 7.9058 | 39.95
2020-08-29 01:30 | 44072.0625 | 0 | 7.8219 | 39.95
2020-08-29 02:00 | 44072.0833 | 0 | 7.6729 | 39.95
2020-08-29 02:30 | 44072.1042 | 0 | 7.5148 | 39.95
2020-08-29 03:00 | 44072.125 | 0 | 7.653 | 39.95
2020-08-29 03:30 | 44072.1458 | 0 | 7.6915 | 39.95
2020-08-29 04:00 | 44072.1667 | 0 | 7.6661 | 39.95
2020-08-29 04:30 | 44072.1875 | 0 | 7.9171 | 39.95
2020-08-29 05:00 | 44072.2083 | 0 | 8.2223 | 39.95
2020-08-29 05:30 | 44072.2292 | 0 | 8.5541 | 39.95
2020-08-29 06:00 | 44072.25 | 0 | 8.796 | 39.95
2020-08-29 06:30 | 44072.2708 | 0 | 9.1007 | 39.95
2020-08-29 07:00 | 44072.2917 | 0 | 9.1758 | 39.95
2020-08-29 07:30 | 44072.3125 | 0 | 8.9691 | 39.95
2020-08-29 08:00 | 44072.3333 | 0 | 8.9444 | 39.95
2020-08-29 08:30 | 44072.3542 | 0 | 8.6497 | 39.95
2020-08-29 09:00 | 44072.375 | 0 | 8.1198 | 39.95
2020-08-29 09:30 | 44072.3958 | 0 | 8.0169 | 39.95
2020-08-29 10:00 | 44072.4167 | 0 | 7.6805 | 39.95
2020-08-29 10:30 | 44072.4375 | 0 | 8.0197 | 39.95
2020-08-29 11:00 | 44072.4583 | 0 | 8.7215 | 39.95
2020-08-29 11:30 | 44072.4792 | 0 | 7.3868 | 39.95
2020-08-29 12:00 | 44072.5 | 0 | 6.6642 | 39.95
2020-08-29 12:30 | 44072.5208 | 0 | 6.609 | 39.95
2020-08-29 13:00 | 44072.5417 | 0 | 7.3865 | 39.95
2020-08-29 13:30 | 44072.5625 | 0 | 7.0546 | 39.95
2020-08-29 14:00 | 44072.5833 | 0 | 6.9826 | 39.95
2020-08-29 14:30 | 44072.6042 | 0 | 7.515 | 39.95
2020-08-29 15:00 | 44072.625 | 0 | 7.8046 | 39.95
2020-08-29 15:30 | 44072.6458 | 0 | 8.2278 | 39.95
2020-08-29 16:00 | 44072.6667 | 0 | 8.8963 | 39.95
2020-08-29 16:30 | 44072.6875 | 0 | 9.6274 | 39.95
2020-08-29 17:00 | 44072.7083 | 0 | 10.223 | 39.95
2020-08-29 17:30 | 44072.7292 | 0 | 10.9848 | 39.95
2020-08-29 18:00 | 44072.75 | 0 | 11.5789 | 39.95
2020-08-29 18:30 | 44072.7708 | 0 | 11.7504 | 39.95
2020-08-29 19:00 | 44072.7917 | 0 | 11.665 | 39.95
2020-08-29 19:30 | 44072.8125 | 0 | 11.4639 | 39.95
2020-08-29 20:00 | 44072.8333 | 0 | 11.1706 | 39.95
2020-08-29 20:30 | 44072.8542 | 0 | 10.7881 | 39.95
2020-08-29 21:00 | 44072.875 | 0 | 10.2285 | 39.95
2020-08-29 21:30 | 44072.8958 | 0 | 10.1335 | 39.95
2020-08-29 22:00 | 44072.9167 | 0 | 9.8184 | 39.95
2020-08-29 22:30 | 44072.9375 | 0 | 9.2137 | 39.95
2020-08-29 23:00 | 44072.9583 | 0 | 8.6997 | 39.95
2020-08-29 23:30 | 44072.9792 | 0 | 8.1847 | 39.95
2020-08-30 | 44073 | 0 | 7.7532 | 39.95
2020-08-30 00:30 | 44073.0208 | 0 | 7.3752 | 39.95
2020-08-30 01:00 | 44073.0417 | 0 | 7.2152 | 39.95
2020-08-30 01:30 | 44073.0625 | 0 | 7.1018 | 39.95
2020-08-30 02:00 | 44073.0833 | 0 | 7.0458 | 39.95
2020-08-30 02:30 | 44073.1042 | 0 | 6.9396 | 39.95
2020-08-30 03:00 | 44073.125 | 0 | 6.8785 | 39.95
2020-08-30 03:30 | 44073.1458 | 0 | 6.8393 | 39.95
2020-08-30 04:00 | 44073.1667 | 0 | 6.7577 | 39.95
2020-08-30 04:30 | 44073.1875 | 0 | 6.8228 | 39.95
2020-08-30 05:00 | 44073.2083 | 0 | 7.0293 | 39.95
2020-08-30 05:30 | 44073.2292 | 0 | 7.1049 | 39.95
2020-08-30 06:00 | 44073.25 | 0 | 7.3609 | 39.95
2020-08-30 06:30 | 44073.2708 | 0 | 7.6306 | 39.95
2020-08-30 07:00 | 44073.2917 | 0 | 7.4866 | 39.95
2020-08-30 07:30 | 44073.3125 | 0 | 8.1851 | 39.95
2020-08-30 08:00 | 44073.3333 | 0 | 8.7675 | 39.95
2020-08-30 08:30 | 44073.3542 | 0 | 8.7893 | 39.95
2020-08-30 09:00 | 44073.375 | 0 | 7.8608 | 39.95
2020-08-30 09:30 | 44073.3958 | 0 | 7.7223 | 39.95
2020-08-30 10:00 | 44073.4167 | 0 | 7.9682 | 39.95
2020-08-30 10:30 | 44073.4375 | 0 | 8.0427 | 39.95
2020-08-30 11:00 | 44073.4583 | 0 | 7.312 | 39.95
2020-08-30 11:30 | 44073.4792 | 0 | 7.4292 | 39.95
2020-08-30 12:00 | 44073.5 | 0 | 5.9463 | 39.95
2020-08-30 12:30 | 44073.5208 | 0 | 6.0141 | 39.95
2020-08-30 13:00 | 44073.5417 | 0 | 5.8274 | 39.95
2020-08-30 13:30 | 44073.5625 | 0 | 5.8625 | 39.95
2020-08-30 14:00 | 44073.5833 | 0 | 6.4315 | 39.95
2020-08-30 14:30 | 44073.6042 | 0 | 7.9796 | 39.95
2020-08-30 15:00 | 44073.625 | 0 | 7.5937 | 39.95
2020-08-30 15:30 | 44073.6458 | 0 | 7.6099 | 39.95
2020-08-30 16:00 | 44073.6667 | 0 | 8.4828 | 39.95
2020-08-30 16:30 | 44073.6875 | 0 | 9.5992 | 39.95
2020-08-30 17:00 | 44073.7083 | 0 | 10.1727 | 39.95
2020-08-30 17:30 | 44073.7292 | 0 | 11.1031 | 39.95
2020-08-30 18:00 | 44073.75 | 0 | 11.8236 | 39.95
2020-08-30 18:30 | 44073.7708 | 0 | 12.1382 | 39.95
2020-08-30 19:00 | 44073.7917 | 0 | 11.745 | 39.95
2020-08-30 19:30 | 44073.8125 | 0 | 11.4194 | 39.95
2020-08-30 20:00 | 44073.8333 | 0 | 11.3116 | 39.95
2020-08-30 20:30 | 44073.8542 | 0 | 10.7434 | 39.95
2020-08-30 21:00 | 44073.875 | 0 | 10.1836 | 39.95
2020-08-30 21:30 | 44073.8958 | 0 | 9.9028 | 39.95
2020-08-30 22:00 | 44073.9167 | 0 | 9.4352 | 39.95
2020-08-30 22:30 | 44073.9375 | 0 | 8.7552 | 39.95
2020-08-30 23:00 | 44073.9583 | 0 | 8.1947 | 39.95
2020-08-30 23:30 | 44073.9792 | 0 | 7.7768 | 39.95
2020-08-31 | 44074 | 0 | 7.4394 | 39.95
2020-08-31 00:30 | 44074.0208 | 0 | 7.2525 | 39.95
2020-08-31 01:00 | 44074.0417 | 0 | 7.0403 | 39.95
2020-08-31 01:30 | 44074.0625 | 0 | 7.0012 | 39.95
2020-08-31 02:00 | 44074.0833 | 0 | 7.0125 | 39.95
2020-08-31 02:30 | 44074.1042 | 0 | 7.1301 | 39.95
2020-08-31 03:00 | 44074.125 | 0 | 7.1052 | 39.95
2020-08-31 03:30 | 44074.1458 | 0 | 7.2714 | 39.95
2020-08-31 04:00 | 44074.1667 | 0 | 7.5227 | 39.95
2020-08-31 04:30 | 44074.1875 | 0 | 7.8295 | 39.95
2020-08-31 05:00 | 44074.2083 | 0 | 8.5552 | 39.95
2020-08-31 05:30 | 44074.2292 | 0 | 9.6115 | 39.95
2020-08-31 06:00 | 44074.25 | 0 | 10.5837 | 39.95
2020-08-31 06:30 | 44074.2708 | 0 | 11.6331 | 39.95
2020-08-31 07:00 | 44074.2917 | 0 | 12.0075 | 39.95
2020-08-31 07:30 | 44074.3125 | 0 | 11.4619 | 39.95
2020-08-31 08:00 | 44074.3333 | 0 | 10.933 | 39.95
2020-08-31 08:30 | 44074.3542 | 0 | 10.1925 | 39.95
2020-08-31 09:00 | 44074.375 | 0 | 9.7031 | 39.95
2020-08-31 09:30 | 44074.3958 | 0 | 9.2976 | 39.95
2020-08-31 10:00 | 44074.4167 | 0 | 8.9495 | 39.95
2020-08-31 10:30 | 44074.4375 | 0 | 8.7152 | 39.95
2020-08-31 11:00 | 44074.4583 | 0 | 8.5981 | 39.95
2020-08-31 11:30 | 44074.4792 | 0 | 8.5589 | 39.95
2020-08-31 12:00 | 44074.5 | 0 | 8.5924 | 39.95
2020-08-31 12:30 | 44074.5208 | 0 | 8.442 | 39.95
2020-08-31 13:00 | 44074.5417 | 0 | 8.7212 | 39.95
2020-08-31 13:30 | 44074.5625 | 0 | 9.1688 | 39.95
2020-08-31 14:00 | 44074.5833 | 0 | 9.3896 | 39.95
2020-08-31 14:30 | 44074.6042 | 0 | 9.7395 | 39.95
2020-08-31 15:00 | 44074.625 | 0 | 10.3197 | 39.95
2020-08-31 15:30 | 44074.6458 | 0 | 10.7383 | 39.95
2020-08-31 16:00 | 44074.6667 | 0 | 11.117 | 39.95
2020-08-31 16:30 | 44074.6875 | 0 | 11.7469 | 39.95
2020-08-31 17:00 | 44074.7083 | 0 | 12.2273 | 39.95
2020-08-31 17:30 | 44074.7292 | 0 | 13.2077 | 39.95
2020-08-31 18:00 | 44074.75 | 0 | 13.8073 | 39.95
2020-08-31 18:30 | 44074.7708 | 0 | 14.1689 | 39.95
2020-08-31 19:00 | 44074.7917 | 0 | 13.8835 | 39.95
2020-08-31 19:30 | 44074.8125 | 0 | 13.3787 | 39.95
2020-08-31 20:00 | 44074.8333 | 0 | 13.0715 | 39.95
2020-08-31 20:30 | 44074.8542 | 0 | 12.4282 | 39.95
2020-08-31 21:00 | 44074.875 | 0 | 11.9029 | 39.95
2020-08-31 21:30 | 44074.8958 | 0 | 11.499 | 39.95
2020-08-31 22:00 | 44074.9167 | 0 | 10.7053 | 39.95
2020-08-31 22:30 | 44074.9375 | 0 | 10.0765 | 39.95
2020-08-31 23:00 | 44074.9583 | 0 | 9.5613 | 39.95
2020-08-31 23:30 | 44074.9792 | 0 | 9.0017 | 39.95
2020-09-01 | 44075 | 0 | 8.3547 | 39.95
2020-09-01 00:30 | 44075.0208 | 0 | 8.0226 | 39.95
2020-09-01 01:00 | 44075.0417 | 0 | 7.8947 | 39.95
2020-09-01 01:30 | 44075.0625 | 0 | 7.6805 | 39.95
2020-09-01 02:00 | 44075.0833 | 0 | 7.5812 | 39.95
2020-09-01 02:30 | 44075.1042 | 0 | 7.6099 | 39.95
2020-09-01 03:00 | 44075.125 | 0 | 7.5873 | 39.95
2020-09-01 03:30 | 44075.1458 | 0 | 7.4815 | 39.95
2020-09-01 04:00 | 44075.1667 | 0 | 7.7236 | 39.95
2020-09-01 04:30 | 44075.1875 | 0 | 8.1183 | 39.95
2020-09-01 05:00 | 44075.2083 | 0 | 8.9097 | 39.95
2020-09-01 05:30 | 44075.2292 | 0 | 9.6954 | 39.95
2020-09-01 06:00 | 44075.25 | 0 | 10.6558 | 39.95
2020-09-01 06:30 | 44075.2708 | 0 | 11.4431 | 39.95
2020-09-01 07:00 | 44075.2917 | 0 | 11.7955 | 39.95
2020-09-01 07:30 | 44075.3125 | 0 | 11.2751 | 39.95
2020-09-01 08:00 | 44075.3333 | 0 | 10.5651 | 39.95
2020-09-01 08:30 | 44075.3542 | 0 | 9.9824 | 39.95
2020-09-01 09:00 | 44075.375 | 0 | 9.5141 | 39.95
2020-09-01 09:30 | 44075.3958 | 0 | 9.2416 | 39.95
2020-09-01 10:00 | 44075.4167 | 0 | 8.7338 | 39.95
2020-09-01 10:30 | 44075.4375 | 0 | 8.6317 | 39.95
2020-09-01 11:00 | 44075.4583 | 0 | 8.6146 | 39.95
2020-09-01 11:30 | 44075.4792 | 0 | 8.6689 | 39.95
2020-09-01 12:00 | 44075.5 | 0 | 8.8142 | 39.95
2020-09-01 12:30 | 44075.5208 | 0 | 9.3824 | 39.95
2020-09-01 13:00 | 44075.5417 | 0 | 9.8085 | 39.95
2020-09-01 13:30 | 44075.5625 | 0 | 10.5308 | 39.95
2020-09-01 14:00 | 44075.5833 | 0 | 10.6365 | 39.95
2020-09-01 14:30 | 44075.6042 | 0 | 10.5351 | 39.95
2020-09-01 15:00 | 44075.625 | 0 | 10.2919 | 39.95
2020-09-01 15:30 | 44075.6458 | 0 | 10.8443 | 39.95
2020-09-01 16:00 | 44075.6667 | 0 | 11.3239 | 39.95
2020-09-01 16:30 | 44075.6875 | 0 | 11.996 | 39.95
2020-09-01 17:00 | 44075.7083 | 0 | 12.3872 | 39.95
2020-09-01 17:30 | 44075.7292 | 0 | 13.3316 | 39.95
2020-09-01 18:00 | 44075.75 | 0 | 13.8643 | 39.95
2020-09-01 18:30 | 44075.7708 | 0 | 14.0067 | 39.95
2020-09-01 19:00 | 44075.7917 | 0 | 13.6506 | 39.95
2020-09-01 19:30 | 44075.8125 | 0 | 13.5691 | 39.95
2020-09-01 20:00 | 44075.8333 | 0 | 13.2998 | 39.95
2020-09-01 20:30 | 44075.8542 | 0 | 12.7975 | 39.95
2020-09-01 21:00 | 44075.875 | 0 | 11.9737 | 39.95
2020-09-01 21:30 | 44075.8958 | 0 | 11.6353 | 39.95
2020-09-01 22:00 | 44075.9167 | 0 | 11.0224 | 39.95
2020-09-01 22:30 | 44075.9375 | 0 | 10.1794 | 39.95
2020-09-01 23:00 | 44075.9583 | 0 | 9.5079 | 39.95
2020-09-01 23:30 | 44075.9792 | 0 | 8.9435 | 39.95
2020-09-02 | 44076 | 0 | 8.3052 | 39.95
2020-09-02 00:30 | 44076.0208 | 0 | 8.0319 | 39.95
2020-09-02 01:00 | 44076.0417 | 0 | 7.8443 | 39.95
2020-09-02 01:30 | 44076.0625 | 0 | 7.7773 | 39.95
2020-09-02 02:00 | 44076.0833 | 0 | 7.7457 | 39.95
2020-09-02 02:30 | 44076.1042 | 0 | 7.5818 | 39.95
2020-09-02 03:00 | 44076.125 | 0 | 7.6433 | 39.95
2020-09-02 03:30 | 44076.1458 | 0 | 7.6212 | 39.95
2020-09-02 04:00 | 44076.1667 | 0 | 7.9045 | 39.95
2020-09-02 04:30 | 44076.1875 | 0 | 8.3862 | 39.95
2020-09-02 05:00 | 44076.2083 | 0 | 9.0475 | 39.95
2020-09-02 05:30 | 44076.2292 | 0 | 9.8455 | 39.95
2020-09-02 06:00 | 44076.25 | 0 | 10.7986 | 39.95
2020-09-02 06:30 | 44076.2708 | 0 | 11.3377 | 39.95
2020-09-02 07:00 | 44076.2917 | 0 | 11.6913 | 39.95
2020-09-02 07:30 | 44076.3125 | 0 | 11.1314 | 39.95
2020-09-02 08:00 | 44076.3333 | 0 | 10.8893 | 39.95
2020-09-02 08:30 | 44076.3542 | 0 | 10.1558 | 39.95
2020-09-02 09:00 | 44076.375 | 0 | 10.8173 | 39.95
2020-09-02 09:30 | 44076.3958 | 0 | 11.7408 | 39.95
2020-09-02 10:00 | 44076.4167 | 0 | 10.809 | 39.95
2020-09-02 10:30 | 44076.4375 | 0 | 9.6718 | 39.95
2020-09-02 11:00 | 44076.4583 | 0 | 10.7327 | 39.95
2020-09-02 11:30 | 44076.4792 | 0 | 10.3063 | 39.95
2020-09-02 12:00 | 44076.5 | 0 | 10.6778 | 39.95
2020-09-02 12:30 | 44076.5208 | 0 | 9.8958 | 39.95
2020-09-02 13:00 | 44076.5417 | 0 | 9.6281 | 39.95
2020-09-02 13:30 | 44076.5625 | 0 | 9.9047 | 39.95
2020-09-02 14:00 | 44076.5833 | 0 | 9.6825 | 39.95
2020-09-02 14:30 | 44076.6042 | 0 | 9.853 | 39.95
2020-09-02 15:00 | 44076.625 | 0 | 10.3526 | 39.95
2020-09-02 15:30 | 44076.6458 | 0 | 11.1911 | 39.95
2020-09-02 16:00 | 44076.6667 | 0 | 11.6512 | 39.95
2020-09-02 16:30 | 44076.6875 | 0 | 12.319 | 39.95
2020-09-02 17:00 | 44076.7083 | 0 | 12.7743 | 39.95
2020-09-02 17:30 | 44076.7292 | 0 | 13.3981 | 39.95
2020-09-02 18:00 | 44076.75 | 0 | 13.8911 | 39.95
2020-09-02 18:30 | 44076.7708 | 0 | 14.2237 | 39.95
2020-09-02 19:00 | 44076.7917 | 0 | 14.0407 | 39.95
2020-09-02 19:30 | 44076.8125 | 0 | 13.4739 | 39.95
2020-09-02 20:00 | 44076.8333 | 0 | 13.2977 | 39.95
2020-09-02 20:30 | 44076.8542 | 0 | 12.7608 | 39.95
2020-09-02 21:00 | 44076.875 | 0 | 12.1861 | 39.95
2020-09-02 21:30 | 44076.8958 | 0 | 11.6716 | 39.95
2020-09-02 22:00 | 44076.9167 | 0 | 11.0815 | 39.95
2020-09-02 22:30 | 44076.9375 | 0 | 10.2087 | 39.95
2020-09-02 23:00 | 44076.9583 | 0 | 9.6758 | 39.95
2020-09-02 23:30 | 44076.9792 | 0 | 9.1206 | 39.95
2020-09-03 | 44077 | 0 | 8.4961 | 39.95
2020-09-03 00:30 | 44077.0208 | 0 | 8.0443 | 39.95
2020-09-03 01:00 | 44077.0417 | 0 | 7.9614 | 39.95
2020-09-03 01:30 | 44077.0625 | 0 | 7.8051 | 39.95
2020-09-03 02:00 | 44077.0833 | 0 | 7.7233 | 39.95
2020-09-03 02:30 | 44077.1042 | 0 | 7.6637 | 39.95
2020-09-03 03:00 | 44077.125 | 0 | 7.6378 | 39.95
2020-09-03 03:30 | 44077.1458 | 0 | 7.6323 | 39.95
2020-09-03 04:00 | 44077.1667 | 0 | 7.8597 | 39.95
2020-09-03 04:30 | 44077.1875 | 0 | 8.3675 | 39.95
2020-09-03 05:00 | 44077.2083 | 0 | 9.1685 | 39.95
2020-09-03 05:30 | 44077.2292 | 0 | 9.796 | 39.95
2020-09-03 06:00 | 44077.25 | 0 | 10.6427 | 39.95
2020-09-03 06:30 | 44077.2708 | 0 | 11.5895 | 39.95
2020-09-03 07:00 | 44077.2917 | 0 | 12.082 | 39.95
2020-09-03 07:30 | 44077.3125 | 0 | 12.1432 | 39.95
2020-09-03 08:00 | 44077.3333 | 0 | 11.5707 | 39.95
2020-09-03 08:30 | 44077.3542 | 0 | 11.7419 | 39.95
2020-09-03 09:00 | 44077.375 | 0 | 11.1976 | 39.95
2020-09-03 09:30 | 44077.3958 | 0 | 10.5407 | 39.95
2020-09-03 10:00 | 44077.4167 | 0 | 10.5414 | 39.95
2020-09-03 10:30 | 44077.4375 | 0 | 11.4614 | 39.95
2020-09-03 11:00 | 44077.4583 | 0 | 10.4587 | 39.95
2020-09-03 11:30 | 44077.4792 | 0 | 9.3806 | 39.95
2020-09-03 12:00 | 44077.5 | 0 | 9.1922 | 39.95
2020-09-03 12:30 | 44077.5208 | 0 | 9.3753 | 39.95
2020-09-03 13:00 | 44077.5417 | 0 | 9.1789 | 39.95
2020-09-03 13:30 | 44077.5625 | 0 | 9.7224 | 39.95
2020-09-03 14:00 | 44077.5833 | 0 | 10.0521 | 39.95
2020-09-03 14:30 | 44077.6042 | 0 | 10.5836 | 39.95
2020-09-03 15:00 | 44077.625 | 0 | 11.1307 | 39.95
2020-09-03 15:30 | 44077.6458 | 0 | 11.2311 | 39.95
2020-09-03 16:00 | 44077.6667 | 0 | 11.8462 | 39.95
2020-09-03 16:30 | 44077.6875 | 0 | 12.3356 | 39.95
2020-09-03 17:00 | 44077.7083 | 0 | 12.6403 | 39.95
2020-09-03 17:30 | 44077.7292 | 0 | 13.0687 | 39.95
2020-09-03 18:00 | 44077.75 | 0 | 13.4877 | 39.95
2020-09-03 18:30 | 44077.7708 | 0 | 13.6593 | 39.95
2020-09-03 19:00 | 44077.7917 | 0 | 13.2568 | 39.95
2020-09-03 19:30 | 44077.8125 | 0 | 13.1671 | 39.95
2020-09-03 20:00 | 44077.8333 | 0 | 13.1261 | 39.95
2020-09-03 20:30 | 44077.8542 | 0 | 12.392 | 39.95
2020-09-03 21:00 | 44077.875 | 0 | 12.1518 | 39.95
2020-09-03 21:30 | 44077.8958 | 0 | 11.7577 | 39.95
2020-09-03 22:00 | 44077.9167 | 0 | 11.1636 | 39.95
2020-09-03 22:30 | 44077.9375 | 0 | 10.3356 | 39.95
2020-09-03 23:00 | 44077.9583 | 0 | 9.6651 | 39.95
2020-09-03 23:30 | 44077.9792 | 0 | 9.1609 | 39.95
2020-09-04 | 44078 | 0 | 8.5263 | 39.95
2020-09-04 00:30 | 44078.0208 | 0 | 8.0035 | 39.95
2020-09-04 01:00 | 44078.0417 | 0 | 7.9559 | 39.95
2020-09-04 01:30 | 44078.0625 | 0 | 7.8331 | 39.95
2020-09-04 02:00 | 44078.0833 | 0 | 7.7083 | 39.95
2020-09-04 02:30 | 44078.1042 | 0 | 7.6826 | 39.95
2020-09-04 03:00 | 44078.125 | 0 | 7.6842 | 39.95
2020-09-04 03:30 | 44078.1458 | 0 | 7.6603 | 39.95
2020-09-04 04:00 | 44078.1667 | 0 | 7.8556 | 39.95
2020-09-04 04:30 | 44078.1875 | 0 | 8.4073 | 39.95
2020-09-04 05:00 | 44078.2083 | 0 | 9.051 | 39.95
2020-09-04 05:30 | 44078.2292 | 0 | 9.7912 | 39.95
2020-09-04 06:00 | 44078.25 | 0 | 10.4847 | 39.95
2020-09-04 06:30 | 44078.2708 | 0 | 11.2182 | 39.95
2020-09-04 07:00 | 44078.2917 | 0 | 11.7225 | 39.95
2020-09-04 07:30 | 44078.3125 | 0 | 12.0518 | 39.95
2020-09-04 08:00 | 44078.3333 | 0 | 11.3556 | 39.95
2020-09-04 08:30 | 44078.3542 | 0 | 11.0624 | 39.95
2020-09-04 09:00 | 44078.375 | 0 | 11.3599 | 39.95
2020-09-04 09:30 | 44078.3958 | 0 | 11.4332 | 39.95
2020-09-04 10:00 | 44078.4167 | 0 | 10.2144 | 39.95
2020-09-04 10:30 | 44078.4375 | 0 | 9.3957 | 39.95
2020-09-04 11:00 | 44078.4583 | 0 | 9.2564 | 39.95
2020-09-04 11:30 | 44078.4792 | 0 | 9.2784 | 39.95
2020-09-04 12:00 | 44078.5 | 0 | 9.1117 | 39.95
2020-09-04 12:30 | 44078.5208 | 0 | 9.1545 | 39.95
2020-09-04 13:00 | 44078.5417 | 0 | 9.0517 | 39.95
2020-09-04 13:30 | 44078.5625 | 0 | 9.2175 | 39.95
2020-09-04 14:00 | 44078.5833 | 0 | 10.2858 | 39.95
2020-09-04 14:30 | 44078.6042 | 0 | 10.6515 | 39.95
2020-09-04 15:00 | 44078.625 | 0 | 10.7455 | 39.95
2020-09-04 15:30 | 44078.6458 | 0 | 10.7687 | 39.95
2020-09-04 16:00 | 44078.6667 | 0 | 11.2837 | 39.95
2020-09-04 16:30 | 44078.6875 | 0 | 12.0179 | 39.95
2020-09-04 17:00 | 44078.7083 | 0 | 12.2515 | 39.95
2020-09-04 17:30 | 44078.7292 | 0 | 12.7293 | 39.95
2020-09-04 18:00 | 44078.75 | 0 | 13.103 | 39.95
2020-09-04 18:30 | 44078.7708 | 0 | 13.1888 | 39.95
2020-09-04 19:00 | 44078.7917 | 0 | 13.0316 | 39.95
2020-09-04 19:30 | 44078.8125 | 0 | 12.8241 | 39.95
2020-09-04 20:00 | 44078.8333 | 0 | 12.5735 | 39.95
2020-09-04 20:30 | 44078.8542 | 0 | 11.9813 | 39.95
2020-09-04 21:00 | 44078.875 | 0 | 11.6371 | 39.95
2020-09-04 21:30 | 44078.8958 | 0 | 11.3159 | 39.95
2020-09-04 22:00 | 44078.9167 | 0 | 10.7771 | 39.95
2020-09-04 22:30 | 44078.9375 | 0 | 10.0326 | 39.95
2020-09-04 23:00 | 44078.9583 | 0 | 9.5019 | 39.95
2020-09-04 23:30 | 44078.9792 | 0 | 9.1846 | 39.95
2020-09-05 | 44079 | 0 | 8.6086 | 39.95
2020-09-05 00:30 | 44079.0208 | 0 | 8.1533 | 39.95
2020-09-05 01:00 | 44079.0417 | 0 | 7.8897 | 39.95
2020-09-05 01:30 | 44079.0625 | 0 | 7.8246 | 39.95
2020-09-05 02:00 | 44079.0833 | 0 | 7.6962 | 39.95
2020-09-05 02:30 | 44079.1042 | 0 | 7.6091 | 39.95
2020-09-05 03:00 | 44079.125 | 0 | 7.5458 | 39.95
2020-09-05 03:30 | 44079.1458 | 0 | 7.4723 | 39.95
2020-09-05 04:00 | 44079.1667 | 0 | 7.6091 | 39.95
2020-09-05 04:30 | 44079.1875 | 0 | 7.6645 | 39.95
2020-09-05 05:00 | 44079.2083 | 0 | 7.9522 | 39.95
2020-09-05 05:30 | 44079.2292 | 0 | 8.1358 | 39.95
2020-09-05 06:00 | 44079.25 | 0 | 8.4392 | 39.95
2020-09-05 06:30 | 44079.2708 | 0 | 8.5248 | 39.95
2020-09-05 07:00 | 44079.2917 | 0 | 8.6107 | 39.95
2020-09-05 07:30 | 44079.3125 | 0 | 8.6604 | 39.95
2020-09-05 08:00 | 44079.3333 | 0 | 8.5444 | 39.95
2020-09-05 08:30 | 44079.3542 | 0 | 8.2958 | 39.95
2020-09-05 09:00 | 44079.375 | 0 | 8.021 | 39.95
2020-09-05 09:30 | 44079.3958 | 0 | 7.4802 | 39.95
2020-09-05 10:00 | 44079.4167 | 0 | 7.2083 | 39.95
2020-09-05 10:30 | 44079.4375 | 0 | 7.1186 | 39.95
2020-09-05 11:00 | 44079.4583 | 0 | 6.9162 | 39.95
2020-09-05 11:30 | 44079.4792 | 0 | 6.7171 | 39.95
2020-09-05 12:00 | 44079.5 | 0 | 6.7072 | 39.95
2020-09-05 12:30 | 44079.5208 | 0 | 6.7384 | 39.95
2020-09-05 13:00 | 44079.5417 | 0 | 6.7493 | 39.95
2020-09-05 13:30 | 44079.5625 | 0 | 7.4048 | 39.95
2020-09-05 14:00 | 44079.5833 | 0 | 7.4965 | 39.95
2020-09-05 14:30 | 44079.6042 | 0 | 8.205 | 39.95
2020-09-05 15:00 | 44079.625 | 0 | 8.3159 | 39.95
2020-09-05 15:30 | 44079.6458 | 0 | 8.9259 | 39.95
2020-09-05 16:00 | 44079.6667 | 0 | 9.4498 | 39.95
2020-09-05 16:30 | 44079.6875 | 0 | 10.0755 | 39.95
2020-09-05 17:00 | 44079.7083 | 0 | 10.4767 | 39.95
2020-09-05 17:30 | 44079.7292 | 0 | 11.1062 | 39.95
2020-09-05 18:00 | 44079.75 | 0 | 11.5139 | 39.95
2020-09-05 18:30 | 44079.7708 | 0 | 11.6146 | 39.95
2020-09-05 19:00 | 44079.7917 | 0 | 11.2671 | 39.95
2020-09-05 19:30 | 44079.8125 | 0 | 10.9887 | 39.95
2020-09-05 20:00 | 44079.8333 | 0 | 10.7737 | 39.95
2020-09-05 20:30 | 44079.8542 | 0 | 10.4025 | 39.95
2020-09-05 21:00 | 44079.875 | 0 | 9.9416 | 39.95
2020-09-05 21:30 | 44079.8958 | 0 | 9.7847 | 39.95
2020-09-05 22:00 | 44079.9167 | 0 | 9.4418 | 39.95
2020-09-05 22:30 | 44079.9375 | 0 | 8.9175 | 39.95
2020-09-05 23:00 | 44079.9583 | 0 | 8.4625 | 39.95
2020-09-05 23:30 | 44079.9792 | 0 | 7.9696 | 39.95
2020-09-06 | 44080 | 0 | 7.6597 | 39.95
2020-09-06 00:30 | 44080.0208 | 0 | 7.331 | 39.95
2020-09-06 01:00 | 44080.0417 | 0 | 7.1541 | 39.95
2020-09-06 01:30 | 44080.0625 | 0 | 7.1402 | 39.95
2020-09-06 02:00 | 44080.0833 | 0 | 7.0697 | 39.95
2020-09-06 02:30 | 44080.1042 | 0 | 6.9643 | 39.95
2020-09-06 03:00 | 44080.125 | 0 | 6.8212 | 39.95
2020-09-06 03:30 | 44080.1458 | 0 | 6.8024 | 39.95
2020-09-06 04:00 | 44080.1667 | 0 | 6.6532 | 39.95
2020-09-06 04:30 | 44080.1875 | 0 | 6.8052 | 39.95
2020-09-06 05:00 | 44080.2083 | 0 | 6.8338 | 39.95
2020-09-06 05:30 | 44080.2292 | 0 | 7.0526 | 39.95
2020-09-06 06:00 | 44080.25 | 0 | 7.2286 | 39.95
2020-09-06 06:30 | 44080.2708 | 0 | 7.3188 | 39.95
2020-09-06 07:00 | 44080.2917 | 0 | 7.6651 | 39.95
2020-09-06 07:30 | 44080.3125 | 0 | 7.5192 | 39.95
2020-09-06 08:00 | 44080.3333 | 0 | 7.8407 | 39.95
2020-09-06 08:30 | 44080.3542 | 0 | 7.4884 | 39.95
2020-09-06 09:00 | 44080.375 | 0 | 7.2873 | 39.95
2020-09-06 09:30 | 44080.3958 | 0 | 7.7073 | 39.95
2020-09-06 10:00 | 44080.4167 | 0 | 8.8986 | 39.95
2020-09-06 10:30 | 44080.4375 | 0 | 7.9766 | 39.95
2020-09-06 11:00 | 44080.4583 | 0 | 7.5424 | 39.95
2020-09-06 11:30 | 44080.4792 | 0 | 9.9365 | 39.95
2020-09-06 12:00 | 44080.5 | 0 | 9.8178 | 39.95
2020-09-06 12:30 | 44080.5208 | 0 | 9.3658 | 39.95
2020-09-06 13:00 | 44080.5417 | 0 | 9.0001 | 39.95
2020-09-06 13:30 | 44080.5625 | 0 | 8.8336 | 39.95
2020-09-06 14:00 | 44080.5833 | 0 | 9.1841 | 39.95
2020-09-06 14:30 | 44080.6042 | 0 | 9.3225 | 39.95
2020-09-06 15:00 | 44080.625 | 0 | 9.0867 | 39.95
2020-09-06 15:30 | 44080.6458 | 0 | 9.1524 | 39.95
2020-09-06 16:00 | 44080.6667 | 0 | 9.2971 | 39.95
2020-09-06 16:30 | 44080.6875 | 0 | 9.9532 | 39.95
2020-09-06 17:00 | 44080.7083 | 0 | 10.2551 | 39.95
2020-09-06 17:30 | 44080.7292 | 0 | 11.0368 | 39.95
2020-09-06 18:00 | 44080.75 | 0 | 11.4441 | 39.95
2020-09-06 18:30 | 44080.7708 | 0 | 11.7968 | 39.95
2020-09-06 19:00 | 44080.7917 | 0 | 11.4488 | 39.95
2020-09-06 19:30 | 44080.8125 | 0 | 10.9867 | 39.95
2020-09-06 20:00 | 44080.8333 | 0 | 10.847 | 39.95
2020-09-06 20:30 | 44080.8542 | 0 | 10.3825 | 39.95
2020-09-06 21:00 | 44080.875 | 0 | 9.9385 | 39.95
2020-09-06 21:30 | 44080.8958 | 0 | 9.6663 | 39.95
2020-09-06 22:00 | 44080.9167 | 0 | 9.1878 | 39.95
2020-09-06 22:30 | 44080.9375 | 0 | 8.5751 | 39.95
2020-09-06 23:00 | 44080.9583 | 0 | 8.1357 | 39.95
2020-09-06 23:30 | 44080.9792 | 0 | 7.6946 | 39.95
2020-09-07 | 44081 | 0 | 7.4099 | 39.95
2020-09-07 00:30 | 44081.0208 | 0 | 7.1506 | 39.95
2020-09-07 01:00 | 44081.0417 | 0 | 7.009 | 39.95
2020-09-07 01:30 | 44081.0625 | 0 | 7.0348 | 39.95
2020-09-07 02:00 | 44081.0833 | 0 | 6.9615 | 39.95
2020-09-07 02:30 | 44081.1042 | 0 | 7.0634 | 39.95
2020-09-07 03:00 | 44081.125 | 0 | 6.9964 | 39.95
2020-09-07 03:30 | 44081.1458 | 0 | 7.0273 | 39.95
2020-09-07 04:00 | 44081.1667 | 0 | 7.3983 | 39.95
2020-09-07 04:30 | 44081.1875 | 0 | 7.8405 | 39.95
2020-09-07 05:00 | 44081.2083 | 0 | 8.5733 | 39.95
2020-09-07 05:30 | 44081.2292 | 0 | 9.2048 | 39.95
2020-09-07 06:00 | 44081.25 | 0 | 9.877 | 39.95
2020-09-07 06:30 | 44081.2708 | 0 | 10.5982 | 39.95
2020-09-07 07:00 | 44081.2917 | 0 | 10.9065 | 39.95
2020-09-07 07:30 | 44081.3125 | 0 | 10.5196 | 39.95
2020-09-07 08:00 | 44081.3333 | 0 | 10.2673 | 39.95
2020-09-07 08:30 | 44081.3542 | 0 | 9.7993 | 39.95
2020-09-07 09:00 | 44081.375 | 0 | 9.2464 | 39.95
2020-09-07 09:30 | 44081.3958 | 0 | 8.9022 | 39.95
2020-09-07 10:00 | 44081.4167 | 0 | 8.8724 | 39.95
2020-09-07 10:30 | 44081.4375 | 0 | 8.9952 | 39.95
2020-09-07 11:00 | 44081.4583 | 0 | 9.4555 | 39.95
2020-09-07 11:30 | 44081.4792 | 0 | 9.822 | 39.95
2020-09-07 12:00 | 44081.5 | 0 | 9.7461 | 39.95
2020-09-07 12:30 | 44081.5208 | 0 | 9.0344 | 39.95
2020-09-07 13:00 | 44081.5417 | 0 | 9.4788 | 39.95
2020-09-07 13:30 | 44081.5625 | 0 | 9.8858 | 39.95
2020-09-07 14:00 | 44081.5833 | 0 | 10.9618 | 39.95
2020-09-07 14:30 | 44081.6042 | 0 | 11.3948 | 39.95
2020-09-07 15:00 | 44081.625 | 0 | 11.5418 | 39.95
2020-09-07 15:30 | 44081.6458 | 0 | 11.522 | 39.95
2020-09-07 16:00 | 44081.6667 | 0 | 11.68 | 39.95
2020-09-07 16:30 | 44081.6875 | 0 | 12.0846 | 39.95
2020-09-07 17:00 | 44081.7083 | 0 | 12.5634 | 39.95
2020-09-07 17:30 | 44081.7292 | 0 | 13.2869 | 39.95
2020-09-07 18:00 | 44081.75 | 0 | 13.8365 | 39.95
2020-09-07 18:30 | 44081.7708 | 0 | 13.8737 | 39.95
2020-09-07 19:00 | 44081.7917 | 0 | 13.5864 | 39.95
2020-09-07 19:30 | 44081.8125 | 0 | 13.2041 | 39.95
2020-09-07 20:00 | 44081.8333 | 0 | 12.9081 | 39.95
2020-09-07 20:30 | 44081.8542 | 0 | 12.1804 | 39.95
2020-09-07 21:00 | 44081.875 | 0 | 11.7219 | 39.95
2020-09-07 21:30 | 44081.8958 | 0 | 11.2984 | 39.95
2020-09-07 22:00 | 44081.9167 | 0 | 10.7509 | 39.95
2020-09-07 22:30 | 44081.9375 | 0 | 9.9697 | 39.95
2020-09-07 23:00 | 44081.9583 | 0 | 9.2516 | 39.95
2020-09-07 23:30 | 44081.9792 | 0 | 8.8027 | 39.95
2020-09-08 | 44082 | 0 | 8.2423 | 39.95
2020-09-08 00:30 | 44082.0208 | 0 | 7.9086 | 39.95
2020-09-08 01:00 | 44082.0417 | 0 | 7.7301 | 39.95
2020-09-08 01:30 | 44082.0625 | 0 | 7.6887 | 39.95
2020-09-08 02:00 | 44082.0833 | 0 | 7.6154 | 39.95
2020-09-08 02:30 | 44082.1042 | 0 | 7.4967 | 39.95
2020-09-08 03:00 | 44082.125 | 0 | 7.4431 | 39.95
2020-09-08 03:30 | 44082.1458 | 0 | 7.5135 | 39.95
2020-09-08 04:00 | 44082.1667 | 0 | 7.6778 | 39.95
2020-09-08 04:30 | 44082.1875 | 0 | 8.2463 | 39.95
2020-09-08 05:00 | 44082.2083 | 0 | 8.929 | 39.95
2020-09-08 05:30 | 44082.2292 | 0 | 9.565 | 39.95
2020-09-08 06:00 | 44082.25 | 0 | 10.5177 | 39.95
2020-09-08 06:30 | 44082.2708 | 0 | 11.2768 | 39.95
2020-09-08 07:00 | 44082.2917 | 0 | 11.9972 | 39.95
2020-09-08 07:30 | 44082.3125 | 0 | 11.6041 | 39.95
2020-09-08 08:00 | 44082.3333 | 0 | 10.2428 | 39.95
2020-09-08 08:30 | 44082.3542 | 0 | 9.9622 | 39.95
2020-09-08 09:00 | 44082.375 | 0 | 10.4719 | 39.95
2020-09-08 09:30 | 44082.3958 | 0 | 10.3127 | 39.95
2020-09-08 10:00 | 44082.4167 | 0 | 9.6806 | 39.95
2020-09-08 10:30 | 44082.4375 | 0 | 9.676 | 39.95
2020-09-08 11:00 | 44082.4583 | 0 | 10.0075 | 39.95
2020-09-08 11:30 | 44082.4792 | 0 | 9.7247 | 39.95
2020-09-08 12:00 | 44082.5 | 0 | 10.4251 | 39.95
2020-09-08 12:30 | 44082.5208 | 0 | 10.0743 | 39.95
2020-09-08 13:00 | 44082.5417 | 0 | 10.1052 | 39.95
2020-09-08 13:30 | 44082.5625 | 0 | 9.9912 | 39.95
2020-09-08 14:00 | 44082.5833 | 0 | 9.939 | 39.95
2020-09-08 14:30 | 44082.6042 | 0 | 10.4347 | 39.95
2020-09-08 15:00 | 44082.625 | 0 | 9.8465 | 39.95
2020-09-08 15:30 | 44082.6458 | 0 | 10.434 | 39.95
2020-09-08 16:00 | 44082.6667 | 0 | 11.134 | 39.95
2020-09-08 16:30 | 44082.6875 | 0 | 11.6164 | 39.95
2020-09-08 17:00 | 44082.7083 | 0 | 12.0529 | 39.95
2020-09-08 17:30 | 44082.7292 | 0 | 12.7898 | 39.95
2020-09-08 18:00 | 44082.75 | 0 | 13.5251 | 39.95
2020-09-08 18:30 | 44082.7708 | 0 | 13.7122 | 39.95
2020-09-08 19:00 | 44082.7917 | 0 | 13.6015 | 39.95
2020-09-08 19:30 | 44082.8125 | 0 | 13.3601 | 39.95
2020-09-08 20:00 | 44082.8333 | 0 | 13.0504 | 39.95
2020-09-08 20:30 | 44082.8542 | 0 | 12.5092 | 39.95
2020-09-08 21:00 | 44082.875 | 0 | 11.9024 | 39.95
2020-09-08 21:30 | 44082.8958 | 0 | 11.6828 | 39.95
2020-09-08 22:00 | 44082.9167 | 0 | 10.9688 | 39.95
2020-09-08 22:30 | 44082.9375 | 0 | 10.0808 | 39.95
2020-09-08 23:00 | 44082.9583 | 0 | 9.464 | 39.95
2020-09-08 23:30 | 44082.9792 | 0 | 9.0447 | 39.95
2020-09-09 | 44083 | 0 | 9.0447 | 39.95
2020-09-09 00:30 | 44083.0208 | 0 | 8.4668 | 39.95
2020-09-09 01:00 | 44083.0417 | 0 | 7.7324 | 39.95
2020-09-09 01:30 | 44083.0625 | 0 | 7.6218 | 39.95
2020-09-09 02:00 | 44083.0833 | 0 | 7.6252 | 39.95
2020-09-09 02:30 | 44083.1042 | 0 | 7.4459 | 39.95
2020-09-09 03:00 | 44083.125 | 0 | 7.3761 | 39.95
2020-09-09 03:30 | 44083.1458 | 0 | 7.4947 | 39.95
2020-09-09 04:00 | 44083.1667 | 0 | 7.7647 | 39.95
2020-09-09 04:30 | 44083.1875 | 0 | 8.1364 | 39.95
2020-09-09 05:00 | 44083.2083 | 0 | 8.8393 | 39.95
2020-09-09 05:30 | 44083.2292 | 0 | 9.377 | 39.95
2020-09-09 06:00 | 44083.25 | 0 | 10.3562 | 39.95
2020-09-09 06:30 | 44083.2708 | 0 | 11.1188 | 39.95
2020-09-09 07:00 | 44083.2917 | 0 | 11.3306 | 39.95
2020-09-09 07:30 | 44083.3125 | 0 | 10.6549 | 39.95
2020-09-09 08:00 | 44083.3333 | 0 | 10.5401 | 39.95
2020-09-09 08:30 | 44083.3542 | 0 | 9.7064 | 39.95
2020-09-09 09:00 | 44083.375 | 0 | 9.8896 | 39.95
2020-09-09 09:30 | 44083.3958 | 0 | 9.4599 | 39.95
2020-09-09 10:00 | 44083.4167 | 0 | 9.5932 | 39.95
2020-09-09 10:30 | 44083.4375 | 0 | 9.203 | 39.95
2020-09-09 11:00 | 44083.4583 | 0 | 9.3198 | 39.95
2020-09-09 11:30 | 44083.4792 | 0 | 9.2801 | 39.95
2020-09-09 12:00 | 44083.5 | 0 | 9.4816 | 39.95
2020-09-09 12:30 | 44083.5208 | 0 | 9.2744 | 39.95
2020-09-09 13:00 | 44083.5417 | 0 | 9.2148 | 39.95
2020-09-09 13:30 | 44083.5625 | 0 | 9.2975 | 39.95
2020-09-09 14:00 | 44083.5833 | 0 | 9.2788 | 39.95
2020-09-09 14:30 | 44083.6042 | 0 | 9.7914 | 39.95
2020-09-09 15:00 | 44083.625 | 0 | 9.8384 | 39.95
2020-09-09 15:30 | 44083.6458 | 0 | 10.4154 | 39.95
2020-09-09 16:00 | 44083.6667 | 0 | 10.9313 | 39.95
2020-09-09 16:30 | 44083.6875 | 0 | 11.5703 | 39.95
2020-09-09 17:00 | 44083.7083 | 0 | 12.1515 | 39.95
2020-09-09 17:30 | 44083.7292 | 0 | 12.875 | 39.95
2020-09-09 18:00 | 44083.75 | 0 | 13.59 | 39.95
2020-09-09 18:30 | 44083.7708 | 0 | 13.864 | 39.95
2020-09-09 19:00 | 44083.7917 | 0 | 13.3777 | 39.95
2020-09-09 19:30 | 44083.8125 | 0 | 13.0611 | 39.95
2020-09-09 20:00 | 44083.8333 | 0 | 12.9611 | 39.95
2020-09-09 20:30 | 44083.8542 | 0 | 12.2766 | 39.95
2020-09-09 21:00 | 44083.875 | 0 | 11.6891 | 39.95
2020-09-09 21:30 | 44083.8958 | 0 | 11.4264 | 39.95
2020-09-09 22:00 | 44083.9167 | 0 | 10.8272 | 39.95
2020-09-09 22:30 | 44083.9375 | 0 | 10.0244 | 39.95
2020-09-09 23:00 | 44083.9583 | 0 | 9.3684 | 39.95
2020-09-09 23:30 | 44083.9792 | 0 | 8.8316 | 39.95
2020-09-10 | 44084 | 0 | 8.3196 | 39.95
2020-09-10 00:30 | 44084.0208 | 0 | 8.0026 | 39.95
2020-09-10 01:00 | 44084.0417 | 0 | 7.8137 | 39.95
2020-09-10 01:30 | 44084.0625 | 0 | 7.6219 | 39.95
2020-09-10 02:00 | 44084.0833 | 0 | 7.6252 | 39.95
2020-09-10 02:30 | 44084.1042 | 0 | 7.494 | 39.95
2020-09-10 03:00 | 44084.125 | 0 | 7.5164 | 39.95
2020-09-10 03:30 | 44084.1458 | 0 | 7.5038 | 39.95
2020-09-10 04:00 | 44084.1667 | 0 | 7.9287 | 39.95
2020-09-10 04:30 | 44084.1875 | 0 | 8.2661 | 39.95
2020-09-10 05:00 | 44084.2083 | 0 | 8.9651 | 39.95
2020-09-10 05:30 | 44084.2292 | 0 | 9.5604 | 39.95
2020-09-10 06:00 | 44084.25 | 0 | 10.6421 | 39.95
2020-09-10 06:30 | 44084.2708 | 0 | 11.4554 | 39.95
2020-09-10 07:00 | 44084.2917 | 0 | 12.091 | 39.95
2020-09-10 07:30 | 44084.3125 | 0 | 11.3767 | 39.95
2020-09-10 08:00 | 44084.3333 | 0 | 11.6638 | 39.95
2020-09-10 08:30 | 44084.3542 | 0 | 11.4395 | 39.95
2020-09-10 09:00 | 44084.375 | 0 | 10.9188 | 39.95
2020-09-10 09:30 | 44084.3958 | 0 | 11.0626 | 39.95
2020-09-10 10:00 | 44084.4167 | 0 | 11.9696 | 39.95
2020-09-10 10:30 | 44084.4375 | 0 | 11.6274 | 39.95
2020-09-10 11:00 | 44084.4583 | 0 | 11.1415 | 39.95
2020-09-10 11:30 | 44084.4792 | 0 | 11.4509 | 39.95
2020-09-10 12:00 | 44084.5 | 0 | 11.9666 | 39.95
2020-09-10 12:30 | 44084.5208 | 0 | 12.0362 | 39.95
2020-09-10 13:00 | 44084.5417 | 0 | 11.9456 | 39.95
2020-09-10 13:30 | 44084.5625 | 0 | 12.188 | 39.95
2020-09-10 14:00 | 44084.5833 | 0 | 11.6381 | 39.95
2020-09-10 14:30 | 44084.6042 | 0 | 11.5941 | 39.95
2020-09-10 15:00 | 44084.625 | 0 | 11.9633 | 39.95
2020-09-10 15:30 | 44084.6458 | 0 | 12.2668 | 39.95
2020-09-10 16:00 | 44084.6667 | 0 | 12.4799 | 39.95
2020-09-10 16:30 | 44084.6875 | 0 | 13.1945 | 39.95
2020-09-10 17:00 | 44084.7083 | 0 | 13.5034 | 39.95
2020-09-10 17:30 | 44084.7292 | 0 | 14.0969 | 39.95
2020-09-10 18:00 | 44084.75 | 0 | 14.5088 | 39.95
2020-09-10 18:30 | 44084.7708 | 0 | 14.6834 | 39.95
2020-09-10 19:00 | 44084.7917 | 0 | 14.1246 | 39.95
2020-09-10 19:30 | 44084.8125 | 0 | 13.8498 | 39.95
2020-09-10 20:00 | 44084.8333 | 0 | 13.6282 | 39.95
2020-09-10 20:30 | 44084.8542 | 0 | 13.0862 | 39.95
2020-09-10 21:00 | 44084.875 | 0 | 12.6272 | 39.95
2020-09-10 21:30 | 44084.8958 | 0 | 12.0902 | 39.95
2020-09-10 22:00 | 44084.9167 | 0 | 11.4095 | 39.95
2020-09-10 22:30 | 44084.9375 | 0 | 10.299 | 39.95
2020-09-10 23:00 | 44084.9583 | 0 | 9.6088 | 39.95
2020-09-10 23:30 | 44084.9792 | 0 | 9.0776 | 39.95
2020-09-11 | 44085 | 0 | 8.6449 | 39.95
2020-09-11 00:30 | 44085.0208 | 0 | 8.1539 | 39.95
2020-09-11 01:00 | 44085.0417 | 0 | 7.9614 | 39.95
2020-09-11 01:30 | 44085.0625 | 0 | 7.9391 | 39.95
2020-09-11 02:00 | 44085.0833 | 0 | 7.7143 | 39.95
2020-09-11 02:30 | 44085.1042 | 0 | 7.7197 | 39.95
2020-09-11 03:00 | 44085.125 | 0 | 7.7569 | 39.95
2020-09-11 03:30 | 44085.1458 | 0 | 7.7122 | 39.95
2020-09-11 04:00 | 44085.1667 | 0 | 7.9158 | 39.95
2020-09-11 04:30 | 44085.1875 | 0 | 8.4589 | 39.95
2020-09-11 05:00 | 44085.2083 | 0 | 8.9685 | 39.95
2020-09-11 05:30 | 44085.2292 | 0 | 9.7145 | 39.95
2020-09-11 06:00 | 44085.25 | 0 | 10.5258 | 39.95
2020-09-11 06:30 | 44085.2708 | 0 | 10.9574 | 39.95
2020-09-11 07:00 | 44085.2917 | 0 | 11.6455 | 39.95
2020-09-11 07:30 | 44085.3125 | 0 | 11.2058 | 39.95
2020-09-11 08:00 | 44085.3333 | 0 | 10.6708 | 39.95
2020-09-11 08:30 | 44085.3542 | 0 | 10.3086 | 39.95
2020-09-11 09:00 | 44085.375 | 0 | 10.1235 | 39.95
2020-09-11 09:30 | 44085.3958 | 0 | 10.7754 | 39.95
2020-09-11 10:00 | 44085.4167 | 0 | 9.7129 | 39.95
2020-09-11 10:30 | 44085.4375 | 0 | 9.7164 | 39.95
2020-09-11 11:00 | 44085.4583 | 0 | 9.2664 | 39.95
2020-09-11 11:30 | 44085.4792 | 0 | 8.9738 | 39.95
2020-09-11 12:00 | 44085.5 | 0 | 9.3088 | 39.95
2020-09-11 12:30 | 44085.5208 | 0 | 9.2459 | 39.95
2020-09-11 13:00 | 44085.5417 | 0 | 9.938 | 39.95
2020-09-11 13:30 | 44085.5625 | 0 | 9.612 | 39.95
2020-09-11 14:00 | 44085.5833 | 0 | 8.6949 | 39.95
2020-09-11 14:30 | 44085.6042 | 0 | 9.4268 | 39.95
2020-09-11 15:00 | 44085.625 | 0 | 10.1821 | 39.95
2020-09-11 15:30 | 44085.6458 | 0 | 10.2779 | 39.95
2020-09-11 16:00 | 44085.6667 | 0 | 11.2338 | 39.95
2020-09-11 16:30 | 44085.6875 | 0 | 11.5886 | 39.95
2020-09-11 17:00 | 44085.7083 | 0 | 11.9407 | 39.95
2020-09-11 17:30 | 44085.7292 | 0 | 12.6358 | 39.95
2020-09-11 18:00 | 44085.75 | 0 | 13.1148 | 39.95
2020-09-11 18:30 | 44085.7708 | 0 | 13.3902 | 39.95
2020-09-11 19:00 | 44085.7917 | 0 | 13.0644 | 39.95
2020-09-11 19:30 | 44085.8125 | 0 | 12.8497 | 39.95
2020-09-11 20:00 | 44085.8333 | 0 | 12.6681 | 39.95
2020-09-11 20:30 | 44085.8542 | 0 | 12.0239 | 39.95
2020-09-11 21:00 | 44085.875 | 0 | 11.8044 | 39.95
2020-09-11 21:30 | 44085.8958 | 0 | 11.5121 | 39.95
2020-09-11 22:00 | 44085.9167 | 0 | 10.9757 | 39.95
2020-09-11 22:30 | 44085.9375 | 0 | 10.2243 | 39.95
2020-09-11 23:00 | 44085.9583 | 0 | 9.7668 | 39.95
2020-09-11 23:30 | 44085.9792 | 0 | 9.189 | 39.95
2020-09-12 | 44086 | 0 | 8.5752 | 39.95
2020-09-12 00:30 | 44086.0208 | 0 | 8.0171 | 39.95
2020-09-12 01:00 | 44086.0417 | 0 | 7.9391 | 39.95
2020-09-12 01:30 | 44086.0625 | 0 | 7.7381 | 39.95
2020-09-12 02:00 | 44086.0833 | 0 | 7.7292 | 39.95
2020-09-12 02:30 | 44086.1042 | 0 | 7.6693 | 39.95
2020-09-12 03:00 | 44086.125 | 0 | 7.6041 | 39.95
2020-09-12 03:30 | 44086.1458 | 0 | 7.5206 | 39.95
2020-09-12 04:00 | 44086.1667 | 0 | 7.6303 | 39.95
2020-09-12 04:30 | 44086.1875 | 0 | 7.802 | 39.95
2020-09-12 05:00 | 44086.2083 | 0 | 8.1271 | 39.95
2020-09-12 05:30 | 44086.2292 | 0 | 8.2074 | 39.95
2020-09-12 06:00 | 44086.25 | 0 | 8.4439 | 39.95
2020-09-12 06:30 | 44086.2708 | 0 | 8.5479 | 39.95
2020-09-12 07:00 | 44086.2917 | 0 | 8.4696 | 39.95
2020-09-12 07:30 | 44086.3125 | 0 | 8.2626 | 39.95
2020-09-12 08:00 | 44086.3333 | 0 | 8.2035 | 39.95
2020-09-12 08:30 | 44086.3542 | 0 | 7.9741 | 39.95
2020-09-12 09:00 | 44086.375 | 0 | 8.2211 | 39.95
2020-09-12 09:30 | 44086.3958 | 0 | 8.6872 | 39.95
2020-09-12 10:00 | 44086.4167 | 0 | 7.9265 | 39.95
2020-09-12 10:30 | 44086.4375 | 0 | 8.5036 | 39.95
2020-09-12 11:00 | 44086.4583 | 0 | 7.1914 | 39.95
2020-09-12 11:30 | 44086.4792 | 0 | 6.8852 | 39.95
2020-09-12 12:00 | 44086.5 | 0 | 6.7621 | 39.95
2020-09-12 12:30 | 44086.5208 | 0 | 7.1871 | 39.95
2020-09-12 13:00 | 44086.5417 | 0 | 7.4409 | 39.95
2020-09-12 13:30 | 44086.5625 | 0 | 7.3001 | 39.95
2020-09-12 14:00 | 44086.5833 | 0 | 7.084 | 39.95
2020-09-12 14:30 | 44086.6042 | 0 | 7.5432 | 39.95
2020-09-12 15:00 | 44086.625 | 0 | 7.8428 | 39.95
2020-09-12 15:30 | 44086.6458 | 0 | 8.3434 | 39.95
2020-09-12 16:00 | 44086.6667 | 0 | 8.8021 | 39.95
2020-09-12 16:30 | 44086.6875 | 0 | 9.6279 | 39.95
2020-09-12 17:00 | 44086.7083 | 0 | 10.0821 | 39.95
2020-09-12 17:30 | 44086.7292 | 0 | 10.7594 | 39.95
2020-09-12 18:00 | 44086.75 | 0 | 11.2278 | 39.95
2020-09-12 18:30 | 44086.7708 | 0 | 11.4909 | 39.95
2020-09-12 19:00 | 44086.7917 | 0 | 11.1214 | 39.95
2020-09-12 19:30 | 44086.8125 | 0 | 10.9375 | 39.95
2020-09-12 20:00 | 44086.8333 | 0 | 10.844 | 39.95
2020-09-12 20:30 | 44086.8542 | 0 | 10.3297 | 39.95
2020-09-12 21:00 | 44086.875 | 0 | 9.9903 | 39.95
2020-09-12 21:30 | 44086.8958 | 0 | 9.7911 | 39.95
2020-09-12 22:00 | 44086.9167 | 0 | 9.3484 | 39.95
2020-09-12 22:30 | 44086.9375 | 0 | 8.9496 | 39.95
2020-09-12 23:00 | 44086.9583 | 0 | 8.468 | 39.95
2020-09-12 23:30 | 44086.9792 | 0 | 8.1156 | 39.95
2020-09-13 | 44087 | 0 | 7.5468 | 39.95
2020-09-13 00:30 | 44087.0208 | 0 | 7.2319 | 39.95
2020-09-13 01:00 | 44087.0417 | 0 | 7.1312 | 39.95
2020-09-13 01:30 | 44087.0625 | 0 | 7.0013 | 39.95
2020-09-13 02:00 | 44087.0833 | 0 | 6.9565 | 39.95
2020-09-13 02:30 | 44087.1042 | 0 | 6.8729 | 39.95
2020-09-13 03:00 | 44087.125 | 0 | 6.7553 | 39.95
2020-09-13 03:30 | 44087.1458 | 0 | 6.7317 | 39.95
2020-09-13 04:00 | 44087.1667 | 0 | 6.8134 | 39.95
2020-09-13 04:30 | 44087.1875 | 0 | 6.7238 | 39.95
2020-09-13 05:00 | 44087.2083 | 0 | 6.7967 | 39.95
2020-09-13 05:30 | 44087.2292 | 0 | 6.9678 | 39.95
2020-09-13 06:00 | 44087.25 | 0 | 7.0293 | 39.95
2020-09-13 06:30 | 44087.2708 | 0 | 7.0458 | 39.95
2020-09-13 07:00 | 44087.2917 | 0 | 6.9455 | 39.95
2020-09-13 07:30 | 44087.3125 | 0 | 6.8448 | 39.95
2020-09-13 08:00 | 44087.3333 | 0 | 6.7219 | 39.95
2020-09-13 08:30 | 44087.3542 | 0 | 6.6868 | 39.95
2020-09-13 09:00 | 44087.375 | 0 | 6.644 | 39.95
2020-09-13 09:30 | 44087.3958 | 0 | 6.8896 | 39.95
2020-09-13 10:00 | 44087.4167 | 0 | 7.5735 | 39.95
2020-09-13 10:30 | 44087.4375 | 0 | 8.4092 | 39.95
2020-09-13 11:00 | 44087.4583 | 0 | 9.4739 | 39.95
2020-09-13 11:30 | 44087.4792 | 0 | 9.0663 | 39.95
2020-09-13 12:00 | 44087.5 | 0 | 8.1284 | 39.95
2020-09-13 12:30 | 44087.5208 | 0 | 7.4118 | 39.95
2020-09-13 13:00 | 44087.5417 | 0 | 7.0742 | 39.95
2020-09-13 13:30 | 44087.5625 | 0 | 6.4002 | 39.95
2020-09-13 14:00 | 44087.5833 | 0 | 6.1175 | 39.95
2020-09-13 14:30 | 44087.6042 | 0 | 6.892 | 39.95
2020-09-13 15:00 | 44087.625 | 0 | 7.2989 | 39.95
2020-09-13 15:30 | 44087.6458 | 0 | 7.9318 | 39.95
2020-09-13 16:00 | 44087.6667 | 0 | 8.6341 | 39.95
2020-09-13 16:30 | 44087.6875 | 0 | 9.442 | 39.95
2020-09-13 17:00 | 44087.7083 | 0 | 10.1805 | 39.95
2020-09-13 17:30 | 44087.7292 | 0 | 11.0354 | 39.95
2020-09-13 18:00 | 44087.75 | 0 | 11.6747 | 39.95
2020-09-13 18:30 | 44087.7708 | 0 | 11.9331 | 39.95
2020-09-13 19:00 | 44087.7917 | 0 | 11.574 | 39.95
2020-09-13 19:30 | 44087.8125 | 0 | 10.7202 | 39.95
2020-09-13 20:00 | 44087.8333 | 0 | 10.2943 | 39.95
2020-09-13 20:30 | 44087.8542 | 0 | 10.1002 | 39.95
2020-09-13 21:00 | 44087.875 | 0 | 9.9824 | 39.95
2020-09-13 21:30 | 44087.8958 | 0 | 9.61 | 39.95
2020-09-13 22:00 | 44087.9167 | 0 | 9.1453 | 39.95
2020-09-13 22:30 | 44087.9375 | 0 | 8.3861 | 39.95
2020-09-13 23:00 | 44087.9583 | 0 | 7.9193 | 39.95
2020-09-13 23:30 | 44087.9792 | 0 | 7.6169 | 39.95
2020-09-14 | 44088 | 0 | 7.2841 | 39.95
2020-09-14 00:30 | 44088.0208 | 0 | 7.0739 | 39.95
2020-09-14 01:00 | 44088.0417 | 0 | 6.8837 | 39.95
2020-09-14 01:30 | 44088.0625 | 0 | 6.8451 | 39.95
2020-09-14 02:00 | 44088.0833 | 0 | 6.9286 | 39.95
2020-09-14 02:30 | 44088.1042 | 0 | 6.9344 | 39.95
2020-09-14 03:00 | 44088.125 | 0 | 6.9341 | 39.95
2020-09-14 03:30 | 44088.1458 | 0 | 6.9959 | 39.95
2020-09-14 04:00 | 44088.1667 | 0 | 7.3463 | 39.95
2020-09-14 04:30 | 44088.1875 | 0 | 7.7171 | 39.95
2020-09-14 05:00 | 44088.2083 | 0 | 8.4488 | 39.95
2020-09-14 05:30 | 44088.2292 | 0 | 9.0983 | 39.95
2020-09-14 06:00 | 44088.25 | 0 | 9.8697 | 39.95
2020-09-14 06:30 | 44088.2708 | 0 | 10.5545 | 39.95
2020-09-14 07:00 | 44088.2917 | 0 | 10.8836 | 39.95
2020-09-14 07:30 | 44088.3125 | 0 | 10.5832 | 39.95
2020-09-14 08:00 | 44088.3333 | 0 | 10.1178 | 39.95
2020-09-14 08:30 | 44088.3542 | 0 | 9.7272 | 39.95
2020-09-14 09:00 | 44088.375 | 0 | 9.3425 | 39.95
2020-09-14 09:30 | 44088.3958 | 0 | 9.186 | 39.95
2020-09-14 10:00 | 44088.4167 | 0 | 8.7664 | 39.95
2020-09-14 10:30 | 44088.4375 | 0 | 8.775 | 39.95
2020-09-14 11:00 | 44088.4583 | 0 | 8.7545 | 39.95
2020-09-14 11:30 | 44088.4792 | 0 | 8.8394 | 39.95
2020-09-14 12:00 | 44088.5 | 0 | 8.8994 | 39.95
2020-09-14 12:30 | 44088.5208 | 0 | 8.978 | 39.95
2020-09-14 13:00 | 44088.5417 | 0 | 9.4644 | 39.95
2020-09-14 13:30 | 44088.5625 | 0 | 9.6398 | 39.95
2020-09-14 14:00 | 44088.5833 | 0 | 9.5363 | 39.95
2020-09-14 14:30 | 44088.6042 | 0 | 10.0466 | 39.95
2020-09-14 15:00 | 44088.625 | 0 | 10.2346 | 39.95
2020-09-14 15:30 | 44088.6458 | 0 | 10.4899 | 39.95
2020-09-14 16:00 | 44088.6667 | 0 | 10.8959 | 39.95
2020-09-14 16:30 | 44088.6875 | 0 | 11.5975 | 39.95
2020-09-14 17:00 | 44088.7083 | 0 | 11.7674 | 39.95
2020-09-14 17:30 | 44088.7292 | 0 | 12.8462 | 39.95
2020-09-14 18:00 | 44088.75 | 0 | 13.6418 | 39.95
2020-09-14 18:30 | 44088.7708 | 0 | 13.828 | 39.95
2020-09-14 19:00 | 44088.7917 | 0 | 13.4588 | 39.95
2020-09-14 19:30 | 44088.8125 | 0 | 13.0365 | 39.95
2020-09-14 20:00 | 44088.8333 | 0 | 12.8549 | 39.95
2020-09-14 20:30 | 44088.8542 | 0 | 12.218 | 39.95
2020-09-14 21:00 | 44088.875 | 0 | 11.7551 | 39.95
2020-09-14 21:30 | 44088.8958 | 0 | 11.1919 | 39.95
2020-09-14 22:00 | 44088.9167 | 0 | 10.616 | 39.95
2020-09-14 22:30 | 44088.9375 | 0 | 9.7139 | 39.95
2020-09-14 23:00 | 44088.9583 | 0 | 9.1451 | 39.95
2020-09-14 23:30 | 44088.9792 | 0 | 8.7537 | 39.95
2020-09-15 | 44089 | 0 | 8.3124 | 39.95
2020-09-15 00:30 | 44089.0208 | 0 | 7.8563 | 39.95
2020-09-15 01:00 | 44089.0417 | 0 | 7.6023 | 39.95
2020-09-15 01:30 | 44089.0625 | 0 | 7.6209 | 39.95
2020-09-15 02:00 | 44089.0833 | 0 | 7.5148 | 39.95
2020-09-15 02:30 | 44089.1042 | 0 | 7.5428 | 39.95
2020-09-15 03:00 | 44089.125 | 0 | 7.4031 | 39.95
2020-09-15 03:30 | 44089.1458 | 0 | 7.4814 | 39.95
2020-09-15 04:00 | 44089.1667 | 0 | 7.5768 | 39.95
2020-09-15 04:30 | 44089.1875 | 0 | 8.1995 | 39.95
2020-09-15 05:00 | 44089.2083 | 0 | 8.7922 | 39.95
2020-09-15 05:30 | 44089.2292 | 0 | 9.2945 | 39.95
2020-09-15 06:00 | 44089.25 | 0 | 10.2497 | 39.95
2020-09-15 06:30 | 44089.2708 | 0 | 10.5912 | 39.95
2020-09-15 07:00 | 44089.2917 | 0 | 10.8299 | 39.95
2020-09-15 07:30 | 44089.3125 | 0 | 10.693 | 39.95
2020-09-15 08:00 | 44089.3333 | 0 | 10.1755 | 39.95
2020-09-15 08:30 | 44089.3542 | 0 | 10.4176 | 39.95
2020-09-15 09:00 | 44089.375 | 0 | 9.7417 | 39.95
2020-09-15 09:30 | 44089.3958 | 0 | 9.731 | 39.95
2020-09-15 10:00 | 44089.4167 | 0 | 9.0144 | 39.95
2020-09-15 10:30 | 44089.4375 | 0 | 8.9499 | 39.95
2020-09-15 11:00 | 44089.4583 | 0 | 8.7418 | 39.95
2020-09-15 11:30 | 44089.4792 | 0 | 8.7616 | 39.95
2020-09-15 12:00 | 44089.5 | 0 | 9.064 | 39.95
2020-09-15 12:30 | 44089.5208 | 0 | 9.1387 | 39.95
2020-09-15 13:00 | 44089.5417 | 0 | 9.3625 | 39.95
2020-09-15 13:30 | 44089.5625 | 0 | 10.1171 | 39.95
2020-09-15 14:00 | 44089.5833 | 0 | 10.232 | 39.95
2020-09-15 14:30 | 44089.6042 | 0 | 10.6592 | 39.95
2020-09-15 15:00 | 44089.625 | 0 | 10.9849 | 39.95
2020-09-15 15:30 | 44089.6458 | 0 | 11.4304 | 39.95
2020-09-15 16:00 | 44089.6667 | 0 | 11.3813 | 39.95
2020-09-15 16:30 | 44089.6875 | 0 | 12.11 | 39.95
2020-09-15 17:00 | 44089.7083 | 0 | 12.5362 | 39.95
2020-09-15 17:30 | 44089.7292 | 0 | 13.28 | 39.95
2020-09-15 18:00 | 44089.75 | 0 | 13.8239 | 39.95
2020-09-15 18:30 | 44089.7708 | 0 | 13.9472 | 39.95
2020-09-15 19:00 | 44089.7917 | 0 | 13.5859 | 39.95
2020-09-15 19:30 | 44089.8125 | 0 | 13.3026 | 39.95
2020-09-15 20:00 | 44089.8333 | 0 | 13.0684 | 39.95
2020-09-15 20:30 | 44089.8542 | 0 | 12.3967 | 39.95
2020-09-15 21:00 | 44089.875 | 0 | 11.7078 | 39.95
2020-09-15 21:30 | 44089.8958 | 0 | 11.436 | 39.95
2020-09-15 22:00 | 44089.9167 | 0 | 10.7595 | 39.95
2020-09-15 22:30 | 44089.9375 | 0 | 9.982 | 39.95
2020-09-15 23:00 | 44089.9583 | 0 | 9.3283 | 39.95
2020-09-15 23:30 | 44089.9792 | 0 | 8.7913 | 39.95
2020-09-16 | 44090 | 0 | 8.2327 | 39.95
2020-09-16 00:30 | 44090.0208 | 0 | 7.8425 | 39.95
2020-09-16 01:00 | 44090.0417 | 0 | 7.7233 | 39.95
2020-09-16 01:30 | 44090.0625 | 0 | 7.742 | 39.95
2020-09-16 02:00 | 44090.0833 | 0 | 7.5986 | 39.95
2020-09-16 02:30 | 44090.1042 | 0 | 7.6209 | 39.95
2020-09-16 03:00 | 44090.125 | 0 | 7.5708 | 39.95
2020-09-16 03:30 | 44090.1458 | 0 | 7.6099 | 39.95
2020-09-16 04:00 | 44090.1667 | 0 | 7.8522 | 39.95
2020-09-16 04:30 | 44090.1875 | 0 | 8.2068 | 39.95
2020-09-16 05:00 | 44090.2083 | 0 | 8.7274 | 39.95
2020-09-16 05:30 | 44090.2292 | 0 | 9.3281 | 39.95
2020-09-16 06:00 | 44090.25 | 0 | 10.2362 | 39.95
2020-09-16 06:30 | 44090.2708 | 0 | 11.0555 | 39.95
2020-09-16 07:00 | 44090.2917 | 0 | 11.634 | 39.95
2020-09-16 07:30 | 44090.3125 | 0 | 12.0373 | 39.95
2020-09-16 08:00 | 44090.3333 | 0 | 11.4433 | 39.95
2020-09-16 08:30 | 44090.3542 | 0 | 10.6472 | 39.95
2020-09-16 09:00 | 44090.375 | 0 | 10.2203 | 39.95
2020-09-16 09:30 | 44090.3958 | 0 | 9.7104 | 39.95
2020-09-16 10:00 | 44090.4167 | 0 | 10.8242 | 39.95
2020-09-16 10:30 | 44090.4375 | 0 | 9.3165 | 39.95
2020-09-16 11:00 | 44090.4583 | 0 | 9.0282 | 39.95
2020-09-16 11:30 | 44090.4792 | 0 | 8.5975 | 39.95
2020-09-16 12:00 | 44090.5 | 0 | 8.8529 | 39.95
2020-09-16 12:30 | 44090.5208 | 0 | 8.8584 | 39.95
2020-09-16 13:00 | 44090.5417 | 0 | 9.0828 | 39.95
2020-09-16 13:30 | 44090.5625 | 0 | 9.458 | 39.95
2020-09-16 14:00 | 44090.5833 | 0 | 9.9152 | 39.95
2020-09-16 14:30 | 44090.6042 | 0 | 10.192 | 39.95
2020-09-16 15:00 | 44090.625 | 0 | 10.5355 | 39.95
2020-09-16 15:30 | 44090.6458 | 0 | 11.0811 | 39.95
2020-09-16 16:00 | 44090.6667 | 0 | 11.5457 | 39.95
2020-09-16 16:30 | 44090.6875 | 0 | 12.1214 | 39.95
2020-09-16 17:00 | 44090.7083 | 0 | 12.5114 | 39.95
2020-09-16 17:30 | 44090.7292 | 0 | 13.0949 | 39.95
2020-09-16 18:00 | 44090.75 | 0 | 13.8284 | 39.95
2020-09-16 18:30 | 44090.7708 | 0 | 14.2853 | 39.95
2020-09-16 19:00 | 44090.7917 | 0 | 13.7496 | 39.95
2020-09-16 19:30 | 44090.8125 | 0 | 13.4349 | 39.95
2020-09-16 20:00 | 44090.8333 | 0 | 13.268 | 39.95
2020-09-16 20:30 | 44090.8542 | 0 | 12.5675 | 39.95
2020-09-16 21:00 | 44090.875 | 0 | 12.0959 | 39.95
2020-09-16 21:30 | 44090.8958 | 0 | 11.7279 | 39.95
2020-09-16 22:00 | 44090.9167 | 0 | 11.0047 | 39.95
2020-09-16 22:30 | 44090.9375 | 0 | 10.2901 | 39.95
2020-09-16 23:00 | 44090.9583 | 0 | 9.6646 | 39.95
2020-09-16 23:30 | 44090.9792 | 0 | 9.0891 | 39.95
2020-09-17 | 44091 | 0 | 8.5066 | 39.95
2020-09-17 00:30 | 44091.0208 | 0 | 8.0632 | 39.95
2020-09-17 01:00 | 44091.0417 | 0 | 7.999 | 39.95
2020-09-17 01:30 | 44091.0625 | 0 | 7.9783 | 39.95
2020-09-17 02:00 | 44091.0833 | 0 | 7.7175 | 39.95
2020-09-17 02:30 | 44091.1042 | 0 | 7.7737 | 39.95
2020-09-17 03:00 | 44091.125 | 0 | 7.7849 | 39.95
2020-09-17 03:30 | 44091.1458 | 0 | 7.7735 | 39.95
2020-09-17 04:00 | 44091.1667 | 0 | 7.9584 | 39.95
2020-09-17 04:30 | 44091.1875 | 0 | 8.4092 | 39.95
2020-09-17 05:00 | 44091.2083 | 0 | 9.0084 | 39.95
2020-09-17 05:30 | 44091.2292 | 0 | 9.6432 | 39.95
2020-09-17 06:00 | 44091.25 | 0 | 10.3803 | 39.95
2020-09-17 06:30 | 44091.2708 | 0 | 10.7142 | 39.95
2020-09-17 07:00 | 44091.2917 | 0 | 10.9564 | 39.95
2020-09-17 07:30 | 44091.3125 | 0 | 10.7972 | 39.95
2020-09-17 08:00 | 44091.3333 | 0 | 10.4233 | 39.95
2020-09-17 08:30 | 44091.3542 | 0 | 9.8187 | 39.95
2020-09-17 09:00 | 44091.375 | 0 | 9.4592 | 39.95
2020-09-17 09:30 | 44091.3958 | 0 | 9.4349 | 39.95
2020-09-17 10:00 | 44091.4167 | 0 | 9.1674 | 39.95
2020-09-17 10:30 | 44091.4375 | 0 | 9.1564 | 39.95
2020-09-17 11:00 | 44091.4583 | 0 | 8.9331 | 39.95
2020-09-17 11:30 | 44091.4792 | 0 | 9.1117 | 39.95
2020-09-17 12:00 | 44091.5 | 0 | 9.0502 | 39.95
2020-09-17 12:30 | 44091.5208 | 0 | 9.1624 | 39.95
2020-09-17 13:00 | 44091.5417 | 0 | 9.4134 | 39.95
2020-09-17 13:30 | 44091.5625 | 0 | 9.7931 | 39.95
2020-09-17 14:00 | 44091.5833 | 0 | 10.0723 | 39.95
2020-09-17 14:30 | 44091.6042 | 0 | 10.4553 | 39.95
2020-09-17 15:00 | 44091.625 | 0 | 10.6472 | 39.95
2020-09-17 15:30 | 44091.6458 | 0 | 11.2226 | 39.95
2020-09-17 16:00 | 44091.6667 | 0 | 11.8417 | 39.95
2020-09-17 16:30 | 44091.6875 | 0 | 12.2895 | 39.95
2020-09-17 17:00 | 44091.7083 | 0 | 12.9066 | 39.95
2020-09-17 17:30 | 44091.7292 | 0 | 13.2423 | 39.95
2020-09-17 18:00 | 44091.75 | 0 | 13.7817 | 39.95
2020-09-17 18:30 | 44091.7708 | 0 | 14.1276 | 39.95
2020-09-17 19:00 | 44091.7917 | 0 | 13.7226 | 39.95
2020-09-17 19:30 | 44091.8125 | 0 | 13.2728 | 39.95
2020-09-17 20:00 | 44091.8333 | 0 | 13.0274 | 39.95
2020-09-17 20:30 | 44091.8542 | 0 | 12.6455 | 39.95
2020-09-17 21:00 | 44091.875 | 0 | 12.095 | 39.95
2020-09-17 21:30 | 44091.8958 | 0 | 11.6508 | 39.95
2020-09-17 22:00 | 44091.9167 | 0 | 11.0969 | 39.95
2020-09-17 22:30 | 44091.9375 | 0 | 10.3116 | 39.95
2020-09-17 23:00 | 44091.9583 | 0 | 9.6377 | 39.95
2020-09-17 23:30 | 44091.9792 | 0 | 9.0617 | 39.95
2020-09-18 | 44092 | 0 | 8.4154 | 39.95
2020-09-18 00:30 | 44092.0208 | 0 | 8.0748 | 39.95
2020-09-18 01:00 | 44092.0417 | 0 | 8.0508 | 39.95
2020-09-18 01:30 | 44092.0625 | 0 | 7.8721 | 39.95
2020-09-18 02:00 | 44092.0833 | 0 | 7.8109 | 39.95
2020-09-18 02:30 | 44092.1042 | 0 | 7.8666 | 39.95
2020-09-18 03:00 | 44092.125 | 0 | 7.7661 | 39.95
2020-09-18 03:30 | 44092.1458 | 0 | 7.7904 | 39.95
2020-09-18 04:00 | 44092.1667 | 0 | 7.9954 | 39.95
2020-09-18 04:30 | 44092.1875 | 0 | 8.3723 | 39.95
2020-09-18 05:00 | 44092.2083 | 0 | 9.0195 | 39.95
2020-09-18 05:30 | 44092.2292 | 0 | 9.5755 | 39.95
2020-09-18 06:00 | 44092.25 | 0 | 10.0659 | 39.95
2020-09-18 06:30 | 44092.2708 | 0 | 10.4419 | 39.95
2020-09-18 07:00 | 44092.2917 | 0 | 10.7999 | 39.95
2020-09-18 07:30 | 44092.3125 | 0 | 10.926 | 39.95
2020-09-18 08:00 | 44092.3333 | 0 | 11.2895 | 39.95
2020-09-18 08:30 | 44092.3542 | 0 | 11.1132 | 39.95
2020-09-18 09:00 | 44092.375 | 0 | 11.3948 | 39.95
2020-09-18 09:30 | 44092.3958 | 0 | 10.3851 | 39.95
2020-09-18 10:00 | 44092.4167 | 0 | 10.7348 | 39.95
2020-09-18 10:30 | 44092.4375 | 0 | 10.5633 | 39.95
2020-09-18 11:00 | 44092.4583 | 0 | 9.8081 | 39.95
2020-09-18 11:30 | 44092.4792 | 0 | 10.2493 | 39.95
2020-09-18 12:00 | 44092.5 | 0 | 9.5787 | 39.95
2020-09-18 12:30 | 44092.5208 | 0 | 10.0193 | 39.95
2020-09-18 13:00 | 44092.5417 | 0 | 10.3846 | 39.95
2020-09-18 13:30 | 44092.5625 | 0 | 10.4203 | 39.95
2020-09-18 14:00 | 44092.5833 | 0 | 10.6058 | 39.95
2020-09-18 14:30 | 44092.6042 | 0 | 10.6338 | 39.95
2020-09-18 15:00 | 44092.625 | 0 | 11.346 | 39.95
2020-09-18 15:30 | 44092.6458 | 0 | 11.7526 | 39.95
2020-09-18 16:00 | 44092.6667 | 0 | 11.8972 | 39.95
2020-09-18 16:30 | 44092.6875 | 0 | 12.5307 | 39.95
2020-09-18 17:00 | 44092.7083 | 0 | 12.5286 | 39.95
2020-09-18 17:30 | 44092.7292 | 0 | 12.8853 | 39.95
2020-09-18 18:00 | 44092.75 | 0 | 13.1597 | 39.95
2020-09-18 18:30 | 44092.7708 | 0 | 13.296 | 39.95
2020-09-18 19:00 | 44092.7917 | 0 | 12.9769 | 39.95
2020-09-18 19:30 | 44092.8125 | 0 | 12.6681 | 39.95
2020-09-18 20:00 | 44092.8333 | 0 | 12.4762 | 39.95
2020-09-18 20:30 | 44092.8542 | 0 | 11.9978 | 39.95
2020-09-18 21:00 | 44092.875 | 0 | 11.5755 | 39.95
2020-09-18 21:30 | 44092.8958 | 0 | 11.2424 | 39.95
2020-09-18 22:00 | 44092.9167 | 0 | 10.7925 | 39.95
2020-09-18 22:30 | 44092.9375 | 0 | 10.2263 | 39.95
2020-09-18 23:00 | 44092.9583 | 0 | 9.7875 | 39.95
2020-09-18 23:30 | 44092.9792 | 0 | 9.2679 | 39.95
2020-09-19 | 44093 | 0 | 8.6906 | 39.95
2020-09-19 00:30 | 44093.0208 | 0 | 8.2246 | 39.95
2020-09-19 01:00 | 44093.0417 | 0 | 7.9896 | 39.95
2020-09-19 01:30 | 44093.0625 | 0 | 7.8719 | 39.95
2020-09-19 02:00 | 44093.0833 | 0 | 7.7345 | 39.95
2020-09-19 02:30 | 44093.1042 | 0 | 7.5818 | 39.95
2020-09-19 03:00 | 44093.125 | 0 | 7.6918 | 39.95
2020-09-19 03:30 | 44093.1458 | 0 | 7.5313 | 39.95
2020-09-19 04:00 | 44093.1667 | 0 | 7.6474 | 39.95
2020-09-19 04:30 | 44093.1875 | 0 | 7.7254 | 39.95
2020-09-19 05:00 | 44093.2083 | 0 | 7.8633 | 39.95
2020-09-19 05:30 | 44093.2292 | 0 | 8.0566 | 39.95
2020-09-19 06:00 | 44093.25 | 0 | 8.211 | 39.95
2020-09-19 06:30 | 44093.2708 | 0 | 8.1291 | 39.95
2020-09-19 07:00 | 44093.2917 | 0 | 8.1123 | 39.95
2020-09-19 07:30 | 44093.3125 | 0 | 8.1711 | 39.95
2020-09-19 08:00 | 44093.3333 | 0 | 8.0943 | 39.95
2020-09-19 08:30 | 44093.3542 | 0 | 7.7388 | 39.95
2020-09-19 09:00 | 44093.375 | 0 | 8.0544 | 39.95
2020-09-19 09:30 | 44093.3958 | 0 | 7.0436 | 39.95
2020-09-19 10:00 | 44093.4167 | 0 | 7.7107 | 39.95
2020-09-19 10:30 | 44093.4375 | 0 | 7.645 | 39.95
2020-09-19 11:00 | 44093.4583 | 0 | 7.0342 | 39.95
2020-09-19 11:30 | 44093.4792 | 0 | 7.0138 | 39.95
2020-09-19 12:00 | 44093.5 | 0 | 6.6005 | 39.95
2020-09-19 12:30 | 44093.5208 | 0 | 6.1218 | 39.95
2020-09-19 13:00 | 44093.5417 | 0 | 6.3802 | 39.95
2020-09-19 13:30 | 44093.5625 | 0 | 6.396 | 39.95
2020-09-19 14:00 | 44093.5833 | 0 | 7.1549 | 39.95
2020-09-19 14:30 | 44093.6042 | 0 | 7.6178 | 39.95
2020-09-19 15:00 | 44093.625 | 0 | 8.4897 | 39.95
2020-09-19 15:30 | 44093.6458 | 0 | 8.6349 | 39.95
2020-09-19 16:00 | 44093.6667 | 0 | 9.0087 | 39.95
2020-09-19 16:30 | 44093.6875 | 0 | 9.945 | 39.95
2020-09-19 17:00 | 44093.7083 | 0 | 10.3065 | 39.95
2020-09-19 17:30 | 44093.7292 | 0 | 10.6718 | 39.95
2020-09-19 18:00 | 44093.75 | 0 | 11.0436 | 39.95
2020-09-19 18:30 | 44093.7708 | 0 | 11.3058 | 39.95
2020-09-19 19:00 | 44093.7917 | 0 | 11.0114 | 39.95
2020-09-19 19:30 | 44093.8125 | 0 | 10.7756 | 39.95
2020-09-19 20:00 | 44093.8333 | 0 | 10.5365 | 39.95
2020-09-19 20:30 | 44093.8542 | 0 | 10.1816 | 39.95
2020-09-19 21:00 | 44093.875 | 0 | 9.7123 | 39.95
2020-09-19 21:30 | 44093.8958 | 0 | 9.5949 | 39.95
2020-09-19 22:00 | 44093.9167 | 0 | 9.2805 | 39.95
2020-09-19 22:30 | 44093.9375 | 0 | 8.7102 | 39.95
2020-09-19 23:00 | 44093.9583 | 0 | 8.3394 | 39.95
2020-09-19 23:30 | 44093.9792 | 0 | 8.0171 | 39.95
2020-09-20 | 44094 | 0 | 7.5205 | 39.95
2020-09-20 00:30 | 44094.0208 | 0 | 7.2973 | 39.95
2020-09-20 01:00 | 44094.0417 | 0 | 7.0773 | 39.95
2020-09-20 01:30 | 44094.0625 | 0 | 7.085 | 39.95
2020-09-20 02:00 | 44094.0833 | 0 | 6.951 | 39.95
2020-09-20 02:30 | 44094.1042 | 0 | 7.0626 | 39.95
2020-09-20 03:00 | 44094.125 | 0 | 6.8225 | 39.95
2020-09-20 03:30 | 44094.1458 | 0 | 6.7445 | 39.95
2020-09-20 04:00 | 44094.1667 | 0 | 6.725 | 39.95
2020-09-20 04:30 | 44094.1875 | 0 | 6.7799 | 39.95
2020-09-20 05:00 | 44094.2083 | 0 | 6.9402 | 39.95
2020-09-20 05:30 | 44094.2292 | 0 | 7.0461 | 39.95
2020-09-20 06:00 | 44094.25 | 0 | 7.0681 | 39.95
2020-09-20 06:30 | 44094.2708 | 0 | 7.2586 | 39.95
2020-09-20 07:00 | 44094.2917 | 0 | 6.8749 | 39.95
2020-09-20 07:30 | 44094.3125 | 0 | 6.7317 | 39.95
2020-09-20 08:00 | 44094.3333 | 0 | 7.8527 | 39.95
2020-09-20 08:30 | 44094.3542 | 0 | 8.5052 | 39.95
2020-09-20 09:00 | 44094.375 | 0 | 8.0604 | 39.95
2020-09-20 09:30 | 44094.3958 | 0 | 7.1103 | 39.95
2020-09-20 10:00 | 44094.4167 | 0 | 7.8069 | 39.95
2020-09-20 10:30 | 44094.4375 | 0 | 7.9519 | 39.95
2020-09-20 11:00 | 44094.4583 | 0 | 6.7411 | 39.95
2020-09-20 11:30 | 44094.4792 | 0 | 7.6629 | 39.95
2020-09-20 12:00 | 44094.5 | 0 | 6.4056 | 39.95
2020-09-20 12:30 | 44094.5208 | 0 | 6.4823 | 39.95
2020-09-20 13:00 | 44094.5417 | 0 | 6.1988 | 39.95
2020-09-20 13:30 | 44094.5625 | 0 | 7.1178 | 39.95
2020-09-20 14:00 | 44094.5833 | 0 | 7.3583 | 39.95
2020-09-20 14:30 | 44094.6042 | 0 | 7.4676 | 39.95
2020-09-20 15:00 | 44094.625 | 0 | 8.1461 | 39.95
2020-09-20 15:30 | 44094.6458 | 0 | 8.5661 | 39.95
2020-09-20 16:00 | 44094.6667 | 0 | 9.2729 | 39.95
2020-09-20 16:30 | 44094.6875 | 0 | 10.1493 | 39.95
2020-09-20 17:00 | 44094.7083 | 0 | 10.6295 | 39.95
2020-09-20 17:30 | 44094.7292 | 0 | 11.0591 | 39.95
2020-09-20 18:00 | 44094.75 | 0 | 11.669 | 39.95
2020-09-20 18:30 | 44094.7708 | 0 | 12.0004 | 39.95
2020-09-20 19:00 | 44094.7917 | 0 | 11.7078 | 39.95
2020-09-20 19:30 | 44094.8125 | 0 | 11.2316 | 39.95
2020-09-20 20:00 | 44094.8333 | 0 | 10.8474 | 39.95
2020-09-20 20:30 | 44094.8542 | 0 | 10.4339 | 39.95
2020-09-20 21:00 | 44094.875 | 0 | 9.9879 | 39.95
2020-09-20 21:30 | 44094.8958 | 0 | 9.7611 | 39.95
2020-09-20 22:00 | 44094.9167 | 0 | 9.5166 | 39.95
2020-09-20 22:30 | 44094.9375 | 0 | 8.7159 | 39.95
2020-09-20 23:00 | 44094.9583 | 0 | 8.3013 | 39.95
2020-09-20 23:30 | 44094.9792 | 0 | 7.9501 | 39.95
2020-09-21 | 44095 | 0 | 7.6078 | 39.95
2020-09-21 00:30 | 44095.0208 | 0 | 7.3897 | 39.95
2020-09-21 01:00 | 44095.0417 | 0 | 7.2879 | 39.95
2020-09-21 01:30 | 44095.0625 | 0 | 7.286 | 39.95
2020-09-21 02:00 | 44095.0833 | 0 | 7.2581 | 39.95
2020-09-21 02:30 | 44095.1042 | 0 | 7.3251 | 39.95
2020-09-21 03:00 | 44095.125 | 0 | 7.3083 | 39.95
2020-09-21 03:30 | 44095.1458 | 0 | 7.2469 | 39.95
2020-09-21 04:00 | 44095.1667 | 0 | 7.6066 | 39.95
2020-09-21 04:30 | 44095.1875 | 0 | 8.2682 | 39.95
2020-09-21 05:00 | 44095.2083 | 0 | 8.7996 | 39.95
2020-09-21 05:30 | 44095.2292 | 0 | 9.3256 | 39.95
2020-09-21 06:00 | 44095.25 | 0 | 9.7265 | 39.95
2020-09-21 06:30 | 44095.2708 | 0 | 10.1727 | 39.95
2020-09-21 07:00 | 44095.2917 | 0 | 10.3813 | 39.95
2020-09-21 07:30 | 44095.3125 | 0 | 10.7514 | 39.95
2020-09-21 08:00 | 44095.3333 | 0 | 10.8578 | 39.95
2020-09-21 08:30 | 44095.3542 | 0 | 10.5384 | 39.95
2020-09-21 09:00 | 44095.375 | 0 | 10.2434 | 39.95
2020-09-21 09:30 | 44095.3958 | 0 | 10.1796 | 39.95
2020-09-21 10:00 | 44095.4167 | 0 | 10.117 | 39.95
2020-09-21 10:30 | 44095.4375 | 0 | 10.0326 | 39.95
2020-09-21 11:00 | 44095.4583 | 0 | 10.1677 | 39.95
2020-09-21 11:30 | 44095.4792 | 0 | 10.0806 | 39.95
2020-09-21 12:00 | 44095.5 | 0 | 9.9904 | 39.95
2020-09-21 12:30 | 44095.5208 | 0 | 10.3109 | 39.95
2020-09-21 13:00 | 44095.5417 | 0 | 10.7842 | 39.95
2020-09-21 13:30 | 44095.5625 | 0 | 10.8333 | 39.95
2020-09-21 14:00 | 44095.5833 | 0 | 11.2912 | 39.95
2020-09-21 14:30 | 44095.6042 | 0 | 11.7574 | 39.95
2020-09-21 15:00 | 44095.625 | 0 | 12.3166 | 39.95
2020-09-21 15:30 | 44095.6458 | 0 | 12.7485 | 39.95
2020-09-21 16:00 | 44095.6667 | 0 | 13.1796 | 39.95
2020-09-21 16:30 | 44095.6875 | 0 | 13.7212 | 39.95
2020-09-21 17:00 | 44095.7083 | 0 | 13.6896 | 39.95
2020-09-21 17:30 | 44095.7292 | 0 | 13.9472 | 39.95
2020-09-21 18:00 | 44095.75 | 0 | 14.5517 | 39.95
2020-09-21 18:30 | 44095.7708 | 0 | 14.7426 | 39.95
2020-09-21 19:00 | 44095.7917 | 0 | 14.3577 | 39.95
2020-09-21 19:30 | 44095.8125 | 0 | 13.9971 | 39.95
2020-09-21 20:00 | 44095.8333 | 0 | 13.7826 | 39.95
2020-09-21 20:30 | 44095.8542 | 0 | 13.2497 | 39.95
2020-09-21 21:00 | 44095.875 | 0 | 12.6048 | 39.95
2020-09-21 21:30 | 44095.8958 | 0 | 12.2865 | 39.95
2020-09-21 22:00 | 44095.9167 | 0 | 11.6266 | 39.95
2020-09-21 22:30 | 44095.9375 | 0 | 11.0534 | 39.95
2020-09-21 23:00 | 44095.9583 | 0 | 10.385 | 39.95
2020-09-21 23:30 | 44095.9792 | 0 | 9.8343 | 39.95
2020-09-22 | 44096 | 0 | 9.1105 | 39.95
2020-09-22 00:30 | 44096.0208 | 0 | 8.7301 | 39.95
2020-09-22 01:00 | 44096.0417 | 0 | 8.4693 | 39.95
2020-09-22 01:30 | 44096.0625 | 0 | 8.3803 | 39.95
2020-09-22 02:00 | 44096.0833 | 0 | 8.2482 | 39.95
2020-09-22 02:30 | 44096.1042 | 0 | 8.2514 | 39.95
2020-09-22 03:00 | 44096.125 | 0 | 8.2202 | 39.95
2020-09-22 03:30 | 44096.1458 | 0 | 8.265 | 39.95
2020-09-22 04:00 | 44096.1667 | 0 | 8.4329 | 39.95
2020-09-22 04:30 | 44096.1875 | 0 | 8.9187 | 39.95
2020-09-22 05:00 | 44096.2083 | 0 | 9.6246 | 39.95
2020-09-22 05:30 | 44096.2292 | 0 | 10.2023 | 39.95
2020-09-22 06:00 | 44096.25 | 0 | 10.9157 | 39.95
2020-09-22 06:30 | 44096.2708 | 0 | 11.2612 | 39.95
2020-09-22 07:00 | 44096.2917 | 0 | 11.2442 | 39.95
2020-09-22 07:30 | 44096.3125 | 0 | 11.7991 | 39.95
2020-09-22 08:00 | 44096.3333 | 0 | 11.8117 | 39.95
2020-09-22 08:30 | 44096.3542 | 0 | 12.2964 | 39.95
2020-09-22 09:00 | 44096.375 | 0 | 11.8283 | 39.95
2020-09-22 09:30 | 44096.3958 | 0 | 11.6802 | 39.95
2020-09-22 10:00 | 44096.4167 | 0 | 11.7898 | 39.95
2020-09-22 10:30 | 44096.4375 | 0 | 11.6337 | 39.95
2020-09-22 11:00 | 44096.4583 | 0 | 11.1732 | 39.95
2020-09-22 11:30 | 44096.4792 | 0 | 11.6478 | 39.95
2020-09-22 12:00 | 44096.5 | 0 | 12.8863 | 39.95
2020-09-22 12:30 | 44096.5208 | 0 | 13.5952 | 39.95
2020-09-22 13:00 | 44096.5417 | 0 | 12.6409 | 39.95
2020-09-22 13:30 | 44096.5625 | 0 | 12.843 | 39.95
2020-09-22 14:00 | 44096.5833 | 0 | 13.1502 | 39.95
2020-09-22 14:30 | 44096.6042 | 0 | 13.1398 | 39.95
2020-09-22 15:00 | 44096.625 | 0 | 12.4541 | 39.95
2020-09-22 15:30 | 44096.6458 | 0 | 11.9584 | 39.95
2020-09-22 16:00 | 44096.6667 | 0 | 12.5231 | 39.95
2020-09-22 16:30 | 44096.6875 | 0 | 13.4614 | 39.95
2020-09-22 17:00 | 44096.7083 | 0 | 13.8071 | 39.95
2020-09-22 17:30 | 44096.7292 | 0 | 14.1637 | 39.95
2020-09-22 18:00 | 44096.75 | 0 | 14.6282 | 39.95
2020-09-22 18:30 | 44096.7708 | 0 | 15.1287 | 39.95
2020-09-22 19:00 | 44096.7917 | 0 | 14.6421 | 39.95
2020-09-22 19:30 | 44096.8125 | 0 | 14.3073 | 39.95
2020-09-22 20:00 | 44096.8333 | 0 | 13.9707 | 39.95
2020-09-22 20:30 | 44096.8542 | 0 | 13.5052 | 39.95
2020-09-22 21:00 | 44096.875 | 0 | 13.0285 | 39.95
2020-09-22 21:30 | 44096.8958 | 0 | 12.5079 | 39.95
2020-09-22 22:00 | 44096.9167 | 0 | 11.9082 | 39.95
2020-09-22 22:30 | 44096.9375 | 0 | 11.0978 | 39.95
2020-09-22 23:00 | 44096.9583 | 0 | 10.6839 | 39.95
2020-09-22 23:30 | 44096.9792 | 0 | 10.0306 | 39.95
2020-09-23 | 44097 | 0 | 9.2815 | 39.95
2020-09-23 00:30 | 44097.0208 | 0 | 8.8623 | 39.95
2020-09-23 01:00 | 44097.0417 | 0 | 8.6798 | 39.95
2020-09-23 01:30 | 44097.0625 | 0 | 8.6372 | 39.95
2020-09-23 02:00 | 44097.0833 | 0 | 8.6036 | 39.95
2020-09-23 02:30 | 44097.1042 | 0 | 8.4864 | 39.95
2020-09-23 03:00 | 44097.125 | 0 | 8.4528 | 39.95
2020-09-23 03:30 | 44097.1458 | 0 | 8.4696 | 39.95
2020-09-23 04:00 | 44097.1667 | 0 | 8.7306 | 39.95
2020-09-23 04:30 | 44097.1875 | 0 | 9.1861 | 39.95
2020-09-23 05:00 | 44097.2083 | 0 | 9.7792 | 39.95
2020-09-23 05:30 | 44097.2292 | 0 | 10.3162 | 39.95
2020-09-23 06:00 | 44097.25 | 0 | 10.9984 | 39.95
2020-09-23 06:30 | 44097.2708 | 0 | 11.5314 | 39.95
2020-09-23 07:00 | 44097.2917 | 0 | 12.554 | 39.95
2020-09-23 07:30 | 44097.3125 | 0 | 12.9753 | 39.95
2020-09-23 08:00 | 44097.3333 | 0 | 12.9015 | 39.95
2020-09-23 08:30 | 44097.3542 | 0 | 12.7333 | 39.95
2020-09-23 09:00 | 44097.375 | 0 | 13.0072 | 39.95
2020-09-23 09:30 | 44097.3958 | 0 | 12.5079 | 39.95
2020-09-23 10:00 | 44097.4167 | 0 | 12.77 | 39.95
2020-09-23 10:30 | 44097.4375 | 0 | 11.8327 | 39.95
2020-09-23 11:00 | 44097.4583 | 0 | 10.9622 | 39.95
2020-09-23 11:30 | 44097.4792 | 0 | 10.3618 | 39.95
2020-09-23 12:00 | 44097.5 | 0 | 10.3393 | 39.95
2020-09-23 12:30 | 44097.5208 | 0 | 12.6032 | 39.95
2020-09-23 13:00 | 44097.5417 | 0 | 11.6017 | 39.95
2020-09-23 13:30 | 44097.5625 | 0 | 12.8198 | 39.95
2020-09-23 14:00 | 44097.5833 | 0 | 13.2508 | 39.95
2020-09-23 14:30 | 44097.6042 | 0 | 12.6494 | 39.95
2020-09-23 15:00 | 44097.625 | 0 | 12.3763 | 39.95
2020-09-23 15:30 | 44097.6458 | 0 | 12.4488 | 39.95
2020-09-23 16:00 | 44097.6667 | 0 | 13.1563 | 39.95
2020-09-23 16:30 | 44097.6875 | 0 | 13.5276 | 39.95
2020-09-23 17:00 | 44097.7083 | 0 | 13.707 | 39.95
2020-09-23 17:30 | 44097.7292 | 0 | 14.1762 | 39.95
2020-09-23 18:00 | 44097.75 | 0 | 14.6025 | 39.95
2020-09-23 18:30 | 44097.7708 | 0 | 14.9803 | 39.95
2020-09-23 19:00 | 44097.7917 | 0 | 14.5885 | 39.95
2020-09-23 19:30 | 44097.8125 | 0 | 14.3466 | 39.95
2020-09-23 20:00 | 44097.8333 | 0 | 13.94 | 39.95
2020-09-23 20:30 | 44097.8542 | 0 | 13.2985 | 39.95
2020-09-23 21:00 | 44097.875 | 0 | 12.8121 | 39.95
2020-09-23 21:30 | 44097.8958 | 0 | 12.4634 | 39.95
2020-09-23 22:00 | 44097.9167 | 0 | 11.7847 | 39.95
2020-09-23 22:30 | 44097.9375 | 0 | 10.9706 | 39.95
2020-09-23 23:00 | 44097.9583 | 0 | 10.2536 | 39.95
2020-09-23 23:30 | 44097.9792 | 0 | 9.703 | 39.95
2020-09-24 | 44098 | 0 | 9.0385 | 39.95
2020-09-24 00:30 | 44098.0208 | 0 | 8.4776 | 39.95
2020-09-24 01:00 | 44098.0417 | 0 | 8.1463 | 39.95
2020-09-24 01:30 | 44098.0625 | 0 | 8.0006 | 39.95
2020-09-24 02:00 | 44098.0833 | 0 | 8.0342 | 39.95
2020-09-24 02:30 | 44098.1042 | 0 | 7.9281 | 39.95
2020-09-24 03:00 | 44098.125 | 0 | 7.8831 | 39.95
2020-09-24 03:30 | 44098.1458 | 0 | 7.8892 | 39.95
2020-09-24 04:00 | 44098.1667 | 0 | 8.1966 | 39.95
2020-09-24 04:30 | 44098.1875 | 0 | 8.4713 | 39.95
2020-09-24 05:00 | 44098.2083 | 0 | 9.0954 | 39.95
2020-09-24 05:30 | 44098.2292 | 0 | 9.5957 | 39.95
2020-09-24 06:00 | 44098.25 | 0 | 10.1523 | 39.95
2020-09-24 06:30 | 44098.2708 | 0 | 10.3331 | 39.95
2020-09-24 07:00 | 44098.2917 | 0 | 10.6444 | 39.95
2020-09-24 07:30 | 44098.3125 | 0 | 10.2965 | 39.95
2020-09-24 08:00 | 44098.3333 | 0 | 10.8593 | 39.95
2020-09-24 08:30 | 44098.3542 | 0 | 10.3769 | 39.95
2020-09-24 09:00 | 44098.375 | 0 | 9.542 | 39.95
2020-09-24 09:30 | 44098.3958 | 0 | 9.6359 | 39.95
2020-09-24 10:00 | 44098.4167 | 0 | 9.5382 | 39.95
2020-09-24 10:30 | 44098.4375 | 0 | 9.3033 | 39.95
2020-09-24 11:00 | 44098.4583 | 0 | 9.4079 | 39.95
2020-09-24 11:30 | 44098.4792 | 0 | 9.603 | 39.95
2020-09-24 12:00 | 44098.5 | 0 | 9.7079 | 39.95
2020-09-24 12:30 | 44098.5208 | 0 | 9.8317 | 39.95
2020-09-24 13:00 | 44098.5417 | 0 | 9.89 | 39.95
2020-09-24 13:30 | 44098.5625 | 0 | 10.2438 | 39.95
2020-09-24 14:00 | 44098.5833 | 0 | 10.7794 | 39.95
2020-09-24 14:30 | 44098.6042 | 0 | 11.1185 | 39.95
2020-09-24 15:00 | 44098.625 | 0 | 11.3898 | 39.95
2020-09-24 15:30 | 44098.6458 | 0 | 11.8299 | 39.95
2020-09-24 16:00 | 44098.6667 | 0 | 12.2998 | 39.95
2020-09-24 16:30 | 44098.6875 | 0 | 12.9515 | 39.95
2020-09-24 17:00 | 44098.7083 | 0 | 12.9769 | 39.95
2020-09-24 17:30 | 44098.7292 | 0 | 13.2288 | 39.95
2020-09-24 18:00 | 44098.75 | 0 | 13.6714 | 39.95
2020-09-24 18:30 | 44098.7708 | 0 | 13.9131 | 39.95
2020-09-24 19:00 | 44098.7917 | 0 | 13.5502 | 39.95
2020-09-24 19:30 | 44098.8125 | 0 | 13.2488 | 39.95
2020-09-24 20:00 | 44098.8333 | 0 | 12.9729 | 39.95
2020-09-24 20:30 | 44098.8542 | 0 | 12.3732 | 39.95
2020-09-24 21:00 | 44098.875 | 0 | 11.8937 | 39.95
2020-09-24 21:30 | 44098.8958 | 0 | 11.6004 | 39.95
2020-09-24 22:00 | 44098.9167 | 0 | 11.2184 | 39.95
2020-09-24 22:30 | 44098.9375 | 0 | 10.3516 | 39.95
2020-09-24 23:00 | 44098.9583 | 0 | 9.8446 | 39.95
2020-09-24 23:30 | 44098.9792 | 0 | 9.3282 | 39.95
2020-09-25 | 44099 | 0 | 8.6622 | 39.95
2020-09-25 00:30 | 44099.0208 | 0 | 8.2734 | 39.95
2020-09-25 01:00 | 44099.0417 | 0 | 8.1514 | 39.95
2020-09-25 01:30 | 44099.0625 | 0 | 8.0268 | 39.95
2020-09-25 02:00 | 44099.0833 | 0 | 7.9449 | 39.95
2020-09-25 02:30 | 44099.1042 | 0 | 7.8443 | 39.95
2020-09-25 03:00 | 44099.125 | 0 | 7.7905 | 39.95
2020-09-25 03:30 | 44099.1458 | 0 | 7.8944 | 39.95
2020-09-25 04:00 | 44099.1667 | 0 | 8.0514 | 39.95
2020-09-25 04:30 | 44099.1875 | 0 | 8.5042 | 39.95
2020-09-25 05:00 | 44099.2083 | 0 | 8.941 | 39.95
2020-09-25 05:30 | 44099.2292 | 0 | 9.2598 | 39.95
2020-09-25 06:00 | 44099.25 | 0 | 9.7063 | 39.95
2020-09-25 06:30 | 44099.2708 | 0 | 9.927 | 39.95
2020-09-25 07:00 | 44099.2917 | 0 | 10.1895 | 39.95
2020-09-25 07:30 | 44099.3125 | 0 | 10.1332 | 39.95
2020-09-25 08:00 | 44099.3333 | 0 | 10.1448 | 39.95
2020-09-25 08:30 | 44099.3542 | 0 | 10.1387 | 39.95
2020-09-25 09:00 | 44099.375 | 0 | 9.6287 | 39.95
2020-09-25 09:30 | 44099.3958 | 0 | 9.7966 | 39.95
2020-09-25 10:00 | 44099.4167 | 0 | 9.7409 | 39.95
2020-09-25 10:30 | 44099.4375 | 0 | 9.6364 | 39.95
2020-09-25 11:00 | 44099.4583 | 0 | 9.7017 | 39.95
2020-09-25 11:30 | 44099.4792 | 0 | 9.6254 | 39.95
2020-09-25 12:00 | 44099.5 | 0 | 9.6532 | 39.95
2020-09-25 12:30 | 44099.5208 | 0 | 9.7764 | 39.95
2020-09-25 13:00 | 44099.5417 | 0 | 10.1266 | 39.95
2020-09-25 13:30 | 44099.5625 | 0 | 10.2991 | 39.95
2020-09-25 14:00 | 44099.5833 | 0 | 10.5818 | 39.95
2020-09-25 14:30 | 44099.6042 | 0 | 11.0781 | 39.95
2020-09-25 15:00 | 44099.625 | 0 | 11.4833 | 39.95
2020-09-25 15:30 | 44099.6458 | 0 | 12.2253 | 39.95
2020-09-25 16:00 | 44099.6667 | 0 | 12.6975 | 39.95
2020-09-25 16:30 | 44099.6875 | 0 | 13.0945 | 39.95
2020-09-25 17:00 | 44099.7083 | 0 | 13.3732 | 39.95
2020-09-25 17:30 | 44099.7292 | 0 | 13.549 | 39.95
2020-09-25 18:00 | 44099.75 | 0 | 13.7142 | 39.95
2020-09-25 18:30 | 44099.7708 | 0 | 13.8509 | 39.95
2020-09-25 19:00 | 44099.7917 | 0 | 13.7122 | 39.95
2020-09-25 19:30 | 44099.8125 | 0 | 13.3138 | 39.95
2020-09-25 20:00 | 44099.8333 | 0 | 13.0915 | 39.95
2020-09-25 20:30 | 44099.8542 | 0 | 12.5835 | 39.95
2020-09-25 21:00 | 44099.875 | 0 | 12.0594 | 39.95
2020-09-25 21:30 | 44099.8958 | 0 | 11.769 | 39.95
2020-09-25 22:00 | 44099.9167 | 0 | 11.2989 | 39.95
2020-09-25 22:30 | 44099.9375 | 0 | 10.6792 | 39.95
2020-09-25 23:00 | 44099.9583 | 0 | 10.1834 | 39.95
2020-09-25 23:30 | 44099.9792 | 0 | 9.8675 | 39.95
2020-09-26 | 44100 | 0 | 9.272 | 39.95
2020-09-26 00:30 | 44100.0208 | 0 | 8.7934 | 39.95
2020-09-26 01:00 | 44100.0417 | 0 | 8.5754 | 39.95
2020-09-26 01:30 | 44100.0625 | 0 | 8.1588 | 39.95
2020-09-26 02:00 | 44100.0833 | 0 | 8.0844 | 39.95
2020-09-26 02:30 | 44100.1042 | 0 | 7.7844 | 39.95
2020-09-26 03:00 | 44100.125 | 0 | 7.6284 | 39.95
2020-09-26 03:30 | 44100.1458 | 0 | 7.7065 | 39.95
2020-09-26 04:00 | 44100.1667 | 0 | 7.6209 | 39.95
2020-09-26 04:30 | 44100.1875 | 0 | 7.6695 | 39.95
2020-09-26 05:00 | 44100.2083 | 0 | 7.9176 | 39.95
2020-09-26 05:30 | 44100.2292 | 0 | 7.9951 | 39.95
2020-09-26 06:00 | 44100.25 | 0 | 7.9504 | 39.95
2020-09-26 06:30 | 44100.2708 | 0 | 7.7509 | 39.95
2020-09-26 07:00 | 44100.2917 | 0 | 7.5709 | 39.95
2020-09-26 07:30 | 44100.3125 | 0 | 7.3585 | 39.95
2020-09-26 08:00 | 44100.3333 | 0 | 7.3251 | 39.95
2020-09-26 08:30 | 44100.3542 | 0 | 7.0159 | 39.95
2020-09-26 09:00 | 44100.375 | 0 | 6.519 | 39.95
2020-09-26 09:30 | 44100.3958 | 0 | 6.1435 | 39.95
2020-09-26 10:00 | 44100.4167 | 0 | 5.9849 | 39.95
2020-09-26 10:30 | 44100.4375 | 0 | 5.7056 | 39.95
2020-09-26 11:00 | 44100.4583 | 0 | 5.5082 | 39.95
2020-09-26 11:30 | 44100.4792 | 0 | 5.4323 | 39.95
2020-09-26 12:00 | 44100.5 | 0 | 5.343 | 39.95
2020-09-26 12:30 | 44100.5208 | 0 | 5.3653 | 39.95
2020-09-26 13:00 | 44100.5417 | 0 | 5.4941 | 39.95
2020-09-26 13:30 | 44100.5625 | 0 | 5.7471 | 39.95
2020-09-26 14:00 | 44100.5833 | 0 | 5.9323 | 39.95
2020-09-26 14:30 | 44100.6042 | 0 | 6.5758 | 39.95
2020-09-26 15:00 | 44100.625 | 0 | 7.0113 | 39.95
2020-09-26 15:30 | 44100.6458 | 0 | 7.6648 | 39.95
2020-09-26 16:00 | 44100.6667 | 0 | 8.3787 | 39.95
2020-09-26 16:30 | 44100.6875 | 0 | 9.1203 | 39.95
2020-09-26 17:00 | 44100.7083 | 0 | 9.7094 | 39.95
2020-09-26 17:30 | 44100.7292 | 0 | 10.1434 | 39.95
2020-09-26 18:00 | 44100.75 | 0 | 10.6644 | 39.95
2020-09-26 18:30 | 44100.7708 | 0 | 10.9783 | 39.95
2020-09-26 19:00 | 44100.7917 | 0 | 10.6504 | 39.95
2020-09-26 19:30 | 44100.8125 | 0 | 10.3946 | 39.95
2020-09-26 20:00 | 44100.8333 | 0 | 10.2298 | 39.95
2020-09-26 20:30 | 44100.8542 | 0 | 9.8738 | 39.95
2020-09-26 21:00 | 44100.875 | 0 | 9.5022 | 39.95
2020-09-26 21:30 | 44100.8958 | 0 | 9.2661 | 39.95
2020-09-26 22:00 | 44100.9167 | 0 | 8.92 | 39.95
2020-09-26 22:30 | 44100.9375 | 0 | 8.3858 | 39.95
2020-09-26 23:00 | 44100.9583 | 0 | 8.1305 | 39.95
2020-09-26 23:30 | 44100.9792 | 0 | 7.6765 | 39.95
2020-09-27 | 44101 | 0 | 7.3752 | 39.95
2020-09-27 00:30 | 44101.0208 | 0 | 7.1015 | 39.95
2020-09-27 01:00 | 44101.0417 | 0 | 6.9231 | 39.95
2020-09-27 01:30 | 44101.0625 | 0 | 6.8377 | 39.95
2020-09-27 02:00 | 44101.0833 | 0 | 6.9063 | 39.95
2020-09-27 02:30 | 44101.1042 | 0 | 6.8561 | 39.95
2020-09-27 03:00 | 44101.125 | 0 | 6.7946 | 39.95
2020-09-27 03:30 | 44101.1458 | 0 | 6.7221 | 39.95
2020-09-27 04:00 | 44101.1667 | 0 | 6.5918 | 39.95
2020-09-27 04:30 | 44101.1875 | 0 | 6.6775 | 39.95
2020-09-27 05:00 | 44101.2083 | 0 | 6.7371 | 39.95
2020-09-27 05:30 | 44101.2292 | 0 | 6.8393 | 39.95
2020-09-27 06:00 | 44101.25 | 0 | 6.8228 | 39.95
2020-09-27 06:30 | 44101.2708 | 0 | 6.5019 | 39.95
2020-09-27 07:00 | 44101.2917 | 0 | 6.2653 | 39.95
2020-09-27 07:30 | 44101.3125 | 0 | 6.0466 | 39.95
2020-09-27 08:00 | 44101.3333 | 0 | 6.0632 | 39.95
2020-09-27 08:30 | 44101.3542 | 0 | 5.7615 | 39.95
2020-09-27 09:00 | 44101.375 | 0 | 5.449 | 39.95
2020-09-27 09:30 | 44101.3958 | 0 | 5.3764 | 39.95
2020-09-27 10:00 | 44101.4167 | 0 | 5.1939 | 39.95
2020-09-27 10:30 | 44101.4375 | 0 | 4.9634 | 39.95
2020-09-27 11:00 | 44101.4583 | 0 | 4.9912 | 39.95
2020-09-27 11:30 | 44101.4792 | 0 | 4.807 | 39.95
2020-09-27 12:00 | 44101.5 | 0 | 4.7198 | 39.95
2020-09-27 12:30 | 44101.5208 | 0 | 4.7792 | 39.95
2020-09-27 13:00 | 44101.5417 | 0 | 5.0799 | 39.95
2020-09-27 13:30 | 44101.5625 | 0 | 5.3097 | 39.95
2020-09-27 14:00 | 44101.5833 | 0 | 5.6675 | 39.95
2020-09-27 14:30 | 44101.6042 | 0 | 6.2423 | 39.95
2020-09-27 15:00 | 44101.625 | 0 | 6.8612 | 39.95
2020-09-27 15:30 | 44101.6458 | 0 | 7.5001 | 39.95
2020-09-27 16:00 | 44101.6667 | 0 | 8.1857 | 39.95
2020-09-27 16:30 | 44101.6875 | 0 | 9.0804 | 39.95
2020-09-27 17:00 | 44101.7083 | 0 | 9.6479 | 39.95
2020-09-27 17:30 | 44101.7292 | 0 | 10.241 | 39.95
2020-09-27 18:00 | 44101.75 | 0 | 10.9815 | 39.95
2020-09-27 18:30 | 44101.7708 | 0 | 11.0993 | 39.95
2020-09-27 19:00 | 44101.7917 | 0 | 11.0208 | 39.95
2020-09-27 19:30 | 44101.8125 | 0 | 10.5466 | 39.95
2020-09-27 20:00 | 44101.8333 | 0 | 10.2949 | 39.95
2020-09-27 20:30 | 44101.8542 | 0 | 9.7778 | 39.95
2020-09-27 21:00 | 44101.875 | 0 | 9.4666 | 39.95
2020-09-27 21:30 | 44101.8958 | 0 | 9.1635 | 39.95
2020-09-27 22:00 | 44101.9167 | 0 | 8.8319 | 39.95
2020-09-27 22:30 | 44101.9375 | 0 | 8.2101 | 39.95
2020-09-27 23:00 | 44101.9583 | 0 | 7.7633 | 39.95
2020-09-27 23:30 | 44101.9792 | 0 | 7.3916 | 39.95
2020-09-28 | 44102 | 0 | 7.2879 | 39.95
2020-09-28 00:30 | 44102.0208 | 0 | 7.085 | 39.95
2020-09-28 01:00 | 44102.0417 | 0 | 6.8586 | 39.95
2020-09-28 01:30 | 44102.0625 | 0 | 6.8393 | 39.95
2020-09-28 02:00 | 44102.0833 | 0 | 6.9568 | 39.95
2020-09-28 02:30 | 44102.1042 | 0 | 6.9455 | 39.95
2020-09-28 03:00 | 44102.125 | 0 | 6.9901 | 39.95
2020-09-28 03:30 | 44102.1458 | 0 | 7.1523 | 39.95
2020-09-28 04:00 | 44102.1667 | 0 | 7.2873 | 39.95
2020-09-28 04:30 | 44102.1875 | 0 | 7.5599 | 39.95
2020-09-28 05:00 | 44102.2083 | 0 | 8.1801 | 39.95
2020-09-28 05:30 | 44102.2292 | 0 | 8.7515 | 39.95
2020-09-28 06:00 | 44102.25 | 0 | 9.3658 | 39.95
2020-09-28 06:30 | 44102.2708 | 0 | 9.6697 | 39.95
2020-09-28 07:00 | 44102.2917 | 0 | 9.5642 | 39.95
2020-09-28 07:30 | 44102.3125 | 0 | 9.3737 | 39.95
2020-09-28 08:00 | 44102.3333 | 0 | 9.2001 | 39.95
2020-09-28 08:30 | 44102.3542 | 0 | 8.8212 | 39.95
2020-09-28 09:00 | 44102.375 | 0 | 8.5646 | 39.95
2020-09-28 09:30 | 44102.3958 | 0 | 8.9353 | 39.95
2020-09-28 10:00 | 44102.4167 | 0 | 9.2312 | 39.95
2020-09-28 10:30 | 44102.4375 | 0 | 9.9398 | 39.95
2020-09-28 11:00 | 44102.4583 | 0 | 11.1944 | 39.95
2020-09-28 11:30 | 44102.4792 | 0 | 9.5326 | 39.95
2020-09-28 12:00 | 44102.5 | 0 | 10.1168 | 39.95
2020-09-28 12:30 | 44102.5208 | 0 | 8.8931 | 39.95
2020-09-28 13:00 | 44102.5417 | 0 | 9.8762 | 39.95
2020-09-28 13:30 | 44102.5625 | 0 | 9.8184 | 39.95
2020-09-28 14:00 | 44102.5833 | 0 | 9.4209 | 39.95
2020-09-28 14:30 | 44102.6042 | 0 | 10.1423 | 39.95
2020-09-28 15:00 | 44102.625 | 0 | 10.4009 | 39.95
2020-09-28 15:30 | 44102.6458 | 0 | 10.9428 | 39.95
2020-09-28 16:00 | 44102.6667 | 0 | 11.1411 | 39.95
2020-09-28 16:30 | 44102.6875 | 0 | 11.1581 | 39.95
2020-09-28 17:00 | 44102.7083 | 0 | 11.6858 | 39.95
2020-09-28 17:30 | 44102.7292 | 0 | 12.2912 | 39.95
2020-09-28 18:00 | 44102.75 | 0 | 13.0478 | 39.95
2020-09-28 18:30 | 44102.7708 | 0 | 13.3251 | 39.95
2020-09-28 19:00 | 44102.7917 | 0 | 13.1148 | 39.95
2020-09-28 19:30 | 44102.8125 | 0 | 12.772 | 39.95
2020-09-28 20:00 | 44102.8333 | 0 | 12.5469 | 39.95
2020-09-28 20:30 | 44102.8542 | 0 | 12.1324 | 39.95
2020-09-28 21:00 | 44102.875 | 0 | 11.4797 | 39.95
2020-09-28 21:30 | 44102.8958 | 0 | 11.1162 | 39.95
2020-09-28 22:00 | 44102.9167 | 0 | 10.489 | 39.95
2020-09-28 22:30 | 44102.9375 | 0 | 9.8197 | 39.95
2020-09-28 23:00 | 44102.9583 | 0 | 9.2982 | 39.95
2020-09-28 23:30 | 44102.9792 | 0 | 8.8324 | 39.95
2020-09-29 | 44103 | 0 | 8.3846 | 39.95
2020-09-29 00:30 | 44103.0208 | 0 | 8.0618 | 39.95
2020-09-29 01:00 | 44103.0417 | 0 | 7.6897 | 39.95
2020-09-29 01:30 | 44103.0625 | 0 | 7.7681 | 39.95
2020-09-29 02:00 | 44103.0833 | 0 | 7.6182 | 39.95
2020-09-29 02:30 | 44103.1042 | 0 | 7.7218 | 39.95
2020-09-29 03:00 | 44103.125 | 0 | 7.591 | 39.95
2020-09-29 03:30 | 44103.1458 | 0 | 7.5038 | 39.95
2020-09-29 04:00 | 44103.1667 | 0 | 7.7386 | 39.95
2020-09-29 04:30 | 44103.1875 | 0 | 8.0552 | 39.95
2020-09-29 05:00 | 44103.2083 | 0 | 8.7324 | 39.95
2020-09-29 05:30 | 44103.2292 | 0 | 9.3183 | 39.95
2020-09-29 06:00 | 44103.25 | 0 | 9.6854 | 39.95
2020-09-29 06:30 | 44103.2708 | 0 | 10.4305 | 39.95
2020-09-29 07:00 | 44103.2917 | 0 | 10.7226 | 39.95
2020-09-29 07:30 | 44103.3125 | 0 | 10.2939 | 39.95
2020-09-29 08:00 | 44103.3333 | 0 | 10.6744 | 39.95
2020-09-29 08:30 | 44103.3542 | 0 | 9.6649 | 39.95
2020-09-29 09:00 | 44103.375 | 0 | 10.5361 | 39.95
2020-09-29 09:30 | 44103.3958 | 0 | 10.0242 | 39.95
2020-09-29 10:00 | 44103.4167 | 0 | 10.7141 | 39.95
2020-09-29 10:30 | 44103.4375 | 0 | 10.1032 | 39.95
2020-09-29 11:00 | 44103.4583 | 0 | 9.4065 | 39.95
2020-09-29 11:30 | 44103.4792 | 0 | 9.9849 | 39.95
2020-09-29 12:00 | 44103.5 | 0 | 9.4329 | 39.95
2020-09-29 12:30 | 44103.5208 | 0 | 9.4686 | 39.95
2020-09-29 13:00 | 44103.5417 | 0 | 10.4091 | 39.95
2020-09-29 13:30 | 44103.5625 | 0 | 10.8018 | 39.95
2020-09-29 14:00 | 44103.5833 | 0 | 10.3209 | 39.95
2020-09-29 14:30 | 44103.6042 | 0 | 10.4586 | 39.95
2020-09-29 15:00 | 44103.625 | 0 | 10.2302 | 39.95
2020-09-29 15:30 | 44103.6458 | 0 | 10.8544 | 39.95
2020-09-29 16:00 | 44103.6667 | 0 | 10.7758 | 39.95
2020-09-29 16:30 | 44103.6875 | 0 | 11.2487 | 39.95
2020-09-29 17:00 | 44103.7083 | 0 | 11.7322 | 39.95
2020-09-29 17:30 | 44103.7292 | 0 | 12.2408 | 39.95
2020-09-29 18:00 | 44103.75 | 0 | 13.0923 | 39.95
2020-09-29 18:30 | 44103.7708 | 0 | 13.5132 | 39.95
2020-09-29 19:00 | 44103.7917 | 0 | 13.1145 | 39.95
2020-09-29 19:30 | 44103.8125 | 0 | 12.8934 | 39.95
2020-09-29 20:00 | 44103.8333 | 0 | 12.7843 | 39.95
2020-09-29 20:30 | 44103.8542 | 0 | 12.3569 | 39.95
2020-09-29 21:00 | 44103.875 | 0 | 11.6805 | 39.95
2020-09-29 21:30 | 44103.8958 | 0 | 11.1663 | 39.95
2020-09-29 22:00 | 44103.9167 | 0 | 10.757 | 39.95
2020-09-29 22:30 | 44103.9375 | 0 | 10.0316 | 39.95
2020-09-29 23:00 | 44103.9583 | 0 | 9.3902 | 39.95
2020-09-29 23:30 | 44103.9792 | 0 | 8.9341 | 39.95
2020-09-30 | 44104 | 0 | 8.2801 | 39.95
2020-09-30 00:30 | 44104.0208 | 0 | 7.8553 | 39.95
2020-09-30 01:00 | 44104.0417 | 0 | 7.62 | 39.95
2020-09-30 01:30 | 44104.0625 | 0 | 7.6546 | 39.95
2020-09-30 02:00 | 44104.0833 | 0 | 7.6544 | 39.95
2020-09-30 02:30 | 44104.1042 | 0 | 7.5989 | 39.95
2020-09-30 03:00 | 44104.125 | 0 | 7.5481 | 39.95
2020-09-30 03:30 | 44104.1458 | 0 | 7.6046 | 39.95
2020-09-30 04:00 | 44104.1667 | 0 | 7.9061 | 39.95
2020-09-30 04:30 | 44104.1875 | 0 | 8.2395 | 39.95
2020-09-30 05:00 | 44104.2083 | 0 | 8.825 | 39.95
2020-09-30 05:30 | 44104.2292 | 0 | 9.4424 | 39.95
2020-09-30 06:00 | 44104.25 | 0 | 10.3486 | 39.95
2020-09-30 06:30 | 44104.2708 | 0 | 10.2968 | 39.95
2020-09-30 07:00 | 44104.2917 | 0 | 10.2656 | 39.95
2020-09-30 07:30 | 44104.3125 | 0 | 10.2608 | 39.95
2020-09-30 08:00 | 44104.3333 | 0 | 9.8984 | 39.95
2020-09-30 08:30 | 44104.3542 | 0 | 9.5098 | 39.95
2020-09-30 09:00 | 44104.375 | 0 | 8.9395 | 39.95
2020-09-30 09:30 | 44104.3958 | 0 | 9.171 | 39.95
2020-09-30 10:00 | 44104.4167 | 0 | 9.3945 | 39.95
2020-09-30 10:30 | 44104.4375 | 0 | 9.5558 | 39.95
2020-09-30 11:00 | 44104.4583 | 0 | 9.6004 | 39.95
2020-09-30 11:30 | 44104.4792 | 0 | 9.1848 | 39.95
2020-09-30 12:00 | 44104.5 | 0 | 10.197 | 39.95
2020-09-30 12:30 | 44104.5208 | 0 | 9.3202 | 39.95
2020-09-30 13:00 | 44104.5417 | 0 | 9.4975 | 39.95
2020-09-30 13:30 | 44104.5625 | 0 | 10.5234 | 39.95
2020-09-30 14:00 | 44104.5833 | 0 | 9.9025 | 39.95
2020-09-30 14:30 | 44104.6042 | 0 | 10.3033 | 39.95
2020-09-30 15:00 | 44104.625 | 0 | 11.2002 | 39.95
2020-09-30 15:30 | 44104.6458 | 0 | 10.7339 | 39.95
2020-09-30 16:00 | 44104.6667 | 0 | 11.0061 | 39.95
2020-09-30 16:30 | 44104.6875 | 0 | 11.7498 | 39.95
2020-09-30 17:00 | 44104.7083 | 0 | 12.2529 | 39.95
2020-09-30 17:30 | 44104.7292 | 0 | 12.483 | 39.95
2020-09-30 18:00 | 44104.75 | 0 | 13.1721 | 39.95
2020-09-30 18:30 | 44104.7708 | 0 | 13.3472 | 39.95
2020-09-30 19:00 | 44104.7917 | 0 | 13.0139 | 39.95
2020-09-30 19:30 | 44104.8125 | 0 | 12.7914 | 39.95
2020-09-30 20:00 | 44104.8333 | 0 | 12.761 | 39.95
2020-09-30 20:30 | 44104.8542 | 0 | 12.219 | 39.95
2020-09-30 21:00 | 44104.875 | 0 | 11.5768 | 39.95
2020-09-30 21:30 | 44104.8958 | 0 | 11.1534 | 39.95
2020-09-30 22:00 | 44104.9167 | 0 | 10.6129 | 39.95
2020-09-30 22:30 | 44104.9375 | 0 | 9.9716 | 39.95
2020-09-30 23:00 | 44104.9583 | 0 | 9.3939 | 39.95
2020-09-30 23:30 | 44104.9792 | 0 | 8.8838 | 39.95
2020-10-01 | 44105 | 0 | 8.3981 | 39.95
2020-10-01 00:30 | 44105.0208 | 0 | 7.9538 | 39.95
2020-10-01 01:00 | 44105.0417 | 0 | 7.8219 | 39.95
2020-10-01 01:30 | 44105.0625 | 0 | 7.7618 | 39.95
2020-10-01 02:00 | 44105.0833 | 0 | 7.6918 | 39.95
2020-10-01 02:30 | 44105.1042 | 0 | 7.6973 | 39.95
2020-10-01 03:00 | 44105.125 | 0 | 7.6603 | 39.95
2020-10-01 03:30 | 44105.1458 | 0 | 7.7773 | 39.95
2020-10-01 04:00 | 44105.1667 | 0 | 7.9174 | 39.95
2020-10-01 04:30 | 44105.1875 | 0 | 8.2691 | 39.95
2020-10-01 05:00 | 44105.2083 | 0 | 8.8046 | 39.95
2020-10-01 05:30 | 44105.2292 | 0 | 9.2352 | 39.95
2020-10-01 06:00 | 44105.25 | 0 | 9.8035 | 39.95
2020-10-01 06:30 | 44105.2708 | 0 | 9.8768 | 39.95
2020-10-01 07:00 | 44105.2917 | 0 | 9.9164 | 39.95
2020-10-01 07:30 | 44105.3125 | 0 | 10.1715 | 39.95
2020-10-01 08:00 | 44105.3333 | 0 | 9.8821 | 39.95
2020-10-01 08:30 | 44105.3542 | 0 | 9.688 | 39.95
2020-10-01 09:00 | 44105.375 | 0 | 9.2102 | 39.95
2020-10-01 09:30 | 44105.3958 | 0 | 9.2608 | 39.95
2020-10-01 10:00 | 44105.4167 | 0 | 9.0591 | 39.95
2020-10-01 10:30 | 44105.4375 | 0 | 9.0584 | 39.95
2020-10-01 11:00 | 44105.4583 | 0 | 9.1163 | 39.95
2020-10-01 11:30 | 44105.4792 | 0 | 9.0169 | 39.95
2020-10-01 12:00 | 44105.5 | 0 | 8.9441 | 39.95
2020-10-01 12:30 | 44105.5208 | 0 | 9.456 | 39.95
2020-10-01 13:00 | 44105.5417 | 0 | 9.3903 | 39.95
2020-10-01 13:30 | 44105.5625 | 0 | 9.7484 | 39.95
2020-10-01 14:00 | 44105.5833 | 0 | 10.1606 | 39.95
2020-10-01 14:30 | 44105.6042 | 0 | 11.7034 | 39.95
2020-10-01 15:00 | 44105.625 | 0 | 12.7116 | 39.95
2020-10-01 15:30 | 44105.6458 | 0 | 10.5866 | 39.95
2020-10-01 16:00 | 44105.6667 | 0 | 12.2402 | 39.95
2020-10-01 16:30 | 44105.6875 | 0 | 11.9425 | 39.95
2020-10-01 17:00 | 44105.7083 | 0 | 12.4129 | 39.95
2020-10-01 17:30 | 44105.7292 | 0 | 12.7695 | 39.95
2020-10-01 18:00 | 44105.75 | 0 | 13.206 | 39.95
2020-10-01 18:30 | 44105.7708 | 0 | 13.4964 | 39.95
2020-10-01 19:00 | 44105.7917 | 0 | 13.2577 | 39.95
2020-10-01 19:30 | 44105.8125 | 0 | 12.9829 | 39.95
2020-10-01 20:00 | 44105.8333 | 0 | 12.8981 | 39.95
2020-10-01 20:30 | 44105.8542 | 0 | 12.4239 | 39.95
2020-10-01 21:00 | 44105.875 | 0 | 11.7577 | 39.95
2020-10-01 21:30 | 44105.8958 | 0 | 11.3697 | 39.95
2020-10-01 22:00 | 44105.9167 | 0 | 10.9093 | 39.95
2020-10-01 22:30 | 44105.9375 | 0 | 9.9786 | 39.95
2020-10-01 23:00 | 44105.9583 | 0 | 9.3383 | 39.95
2020-10-01 23:30 | 44105.9792 | 0 | 8.9549 | 39.95
2020-10-02 | 44106 | 0 | 8.4289 | 39.95
2020-10-02 00:30 | 44106.0208 | 0 | 8.1939 | 39.95
2020-10-02 01:00 | 44106.0417 | 0 | 7.8776 | 39.95
2020-10-02 01:30 | 44106.0625 | 0 | 7.9113 | 39.95
2020-10-02 02:00 | 44106.0833 | 0 | 7.8219 | 39.95
2020-10-02 02:30 | 44106.1042 | 0 | 7.7221 | 39.95
2020-10-02 03:00 | 44106.125 | 0 | 7.7626 | 39.95
2020-10-02 03:30 | 44106.1458 | 0 | 7.7661 | 39.95
2020-10-02 04:00 | 44106.1667 | 0 | 7.8092 | 39.95
2020-10-02 04:30 | 44106.1875 | 0 | 8.3111 | 39.95
2020-10-02 05:00 | 44106.2083 | 0 | 8.92 | 39.95
2020-10-02 05:30 | 44106.2292 | 0 | 9.2443 | 39.95
2020-10-02 06:00 | 44106.25 | 0 | 9.6597 | 39.95
2020-10-02 06:30 | 44106.2708 | 0 | 9.871 | 39.95
2020-10-02 07:00 | 44106.2917 | 0 | 9.9549 | 39.95
2020-10-02 07:30 | 44106.3125 | 0 | 10.0947 | 39.95
2020-10-02 08:00 | 44106.3333 | 0 | 9.9992 | 39.95
2020-10-02 08:30 | 44106.3542 | 0 | 9.6844 | 39.95
2020-10-02 09:00 | 44106.375 | 0 | 9.4914 | 39.95
2020-10-02 09:30 | 44106.3958 | 0 | 9.4299 | 39.95
2020-10-02 10:00 | 44106.4167 | 0 | 9.5027 | 39.95
2020-10-02 10:30 | 44106.4375 | 0 | 9.6592 | 39.95
2020-10-02 11:00 | 44106.4583 | 0 | 9.5673 | 39.95
2020-10-02 11:30 | 44106.4792 | 0 | 9.581 | 39.95
2020-10-02 12:00 | 44106.5 | 0 | 9.5244 | 39.95
2020-10-02 12:30 | 44106.5208 | 0 | 9.2698 | 39.95
2020-10-02 13:00 | 44106.5417 | 0 | 9.5048 | 39.95
2020-10-02 13:30 | 44106.5625 | 0 | 9.7445 | 39.95
2020-10-02 14:00 | 44106.5833 | 0 | 9.9902 | 39.95
2020-10-02 14:30 | 44106.6042 | 0 | 10.5098 | 39.95
2020-10-02 15:00 | 44106.625 | 0 | 11.0968 | 39.95
2020-10-02 15:30 | 44106.6458 | 0 | 11.6354 | 39.95
2020-10-02 16:00 | 44106.6667 | 0 | 11.9578 | 39.95
2020-10-02 16:30 | 44106.6875 | 0 | 12.3929 | 39.95
2020-10-02 17:00 | 44106.7083 | 0 | 12.4019 | 39.95
2020-10-02 17:30 | 44106.7292 | 0 | 12.5307 | 39.95
2020-10-02 18:00 | 44106.75 | 0 | 12.6259 | 39.95
2020-10-02 18:30 | 44106.7708 | 0 | 13.2417 | 39.95
2020-10-02 19:00 | 44106.7917 | 0 | 12.9678 | 39.95
2020-10-02 19:30 | 44106.8125 | 0 | 12.8173 | 39.95
2020-10-02 20:00 | 44106.8333 | 0 | 12.7348 | 39.95
2020-10-02 20:30 | 44106.8542 | 0 | 12.1021 | 39.95
2020-10-02 21:00 | 44106.875 | 0 | 11.8099 | 39.95
2020-10-02 21:30 | 44106.8958 | 0 | 11.6576 | 39.95
2020-10-02 22:00 | 44106.9167 | 0 | 11.2466 | 39.95
2020-10-02 22:30 | 44106.9375 | 0 | 10.4511 | 39.95
2020-10-02 23:00 | 44106.9583 | 0 | 9.863 | 39.95
2020-10-02 23:30 | 44106.9792 | 0 | 9.3302 | 39.95
2020-10-03 | 44107 | 0 | 8.7296 | 39.95
2020-10-03 00:30 | 44107.0208 | 0 | 8.2796 | 39.95
2020-10-03 01:00 | 44107.0417 | 0 | 7.9617 | 39.95
2020-10-03 01:30 | 44107.0625 | 0 | 7.8587 | 39.95
2020-10-03 02:00 | 44107.0833 | 0 | 7.7197 | 39.95
2020-10-03 02:30 | 44107.1042 | 0 | 7.7569 | 39.95
2020-10-03 03:00 | 44107.125 | 0 | 7.6488 | 39.95
2020-10-03 03:30 | 44107.1458 | 0 | 7.5821 | 39.95
2020-10-03 04:00 | 44107.1667 | 0 | 7.6209 | 39.95
2020-10-03 04:30 | 44107.1875 | 0 | 7.7141 | 39.95
2020-10-03 05:00 | 44107.2083 | 0 | 7.8072 | 39.95
2020-10-03 05:30 | 44107.2292 | 0 | 7.8554 | 39.95
2020-10-03 06:00 | 44107.25 | 0 | 7.8911 | 39.95
2020-10-03 06:30 | 44107.2708 | 0 | 7.6392 | 39.95
2020-10-03 07:00 | 44107.2917 | 0 | 7.4869 | 39.95
2020-10-03 07:30 | 44107.3125 | 0 | 7.661 | 39.95
2020-10-03 08:00 | 44107.3333 | 0 | 7.97 | 39.95
2020-10-03 08:30 | 44107.3542 | 0 | 8.3212 | 39.95
2020-10-03 09:00 | 44107.375 | 0 | 8.6668 | 39.95
2020-10-03 09:30 | 44107.3958 | 0 | 8.2728 | 39.95
2020-10-03 10:00 | 44107.4167 | 0 | 7.5037 | 39.95
2020-10-03 10:30 | 44107.4375 | 0 | 6.902 | 39.95
2020-10-03 11:00 | 44107.4583 | 0 | 6.7407 | 39.95
2020-10-03 11:30 | 44107.4792 | 0 | 6.6587 | 39.95
2020-10-03 12:00 | 44107.5 | 0 | 6.8184 | 39.95
2020-10-03 12:30 | 44107.5208 | 0 | 7.0056 | 39.95
2020-10-03 13:00 | 44107.5417 | 0 | 7.4972 | 39.95
2020-10-03 13:30 | 44107.5625 | 0 | 7.9179 | 39.95
2020-10-03 14:00 | 44107.5833 | 0 | 7.861 | 39.95
2020-10-03 14:30 | 44107.6042 | 0 | 7.9149 | 39.95
2020-10-03 15:00 | 44107.625 | 0 | 8.2257 | 39.95
2020-10-03 15:30 | 44107.6458 | 0 | 8.7569 | 39.95
2020-10-03 16:00 | 44107.6667 | 0 | 9.1996 | 39.95
2020-10-03 16:30 | 44107.6875 | 0 | 9.8154 | 39.95
2020-10-03 17:00 | 44107.7083 | 0 | 10.1484 | 39.95
2020-10-03 17:30 | 44107.7292 | 0 | 10.4759 | 39.95
2020-10-03 18:00 | 44107.75 | 0 | 11.0265 | 39.95
2020-10-03 18:30 | 44107.7708 | 0 | 11.1492 | 39.95
2020-10-03 19:00 | 44107.7917 | 0 | 10.9988 | 39.95
2020-10-03 19:30 | 44107.8125 | 0 | 10.6009 | 39.95
2020-10-03 20:00 | 44107.8333 | 0 | 10.4903 | 39.95
2020-10-03 20:30 | 44107.8542 | 0 | 10.0855 | 39.95
2020-10-03 21:00 | 44107.875 | 0 | 9.7349 | 39.95
2020-10-03 21:30 | 44107.8958 | 0 | 9.4801 | 39.95
2020-10-03 22:00 | 44107.9167 | 0 | 9.2224 | 39.95
2020-10-03 22:30 | 44107.9375 | 0 | 8.6536 | 39.95
2020-10-03 23:00 | 44107.9583 | 0 | 8.1752 | 39.95
2020-10-03 23:30 | 44107.9792 | 0 | 7.8129 | 39.95
2020-10-04 | 44108 | 0 | 7.4735 | 39.95
2020-10-04 00:30 | 44108.0208 | 0 | 7.2188 | 39.95
2020-10-04 01:00 | 44108.0417 | 0 | 7.0167 | 39.95
2020-10-04 01:30 | 44108.0625 | 0 | 7.0348 | 39.95
2020-10-04 02:00 | 44108.0833 | 0 | 7.0125 | 39.95
2020-10-04 02:30 | 44108.1042 | 0 | 7.0011 | 39.95
2020-10-04 03:00 | 44108.125 | 0 | 6.817 | 39.95
2020-10-04 03:30 | 44108.1458 | 0 | 6.7723 | 39.95
2020-10-04 04:00 | 44108.1667 | 0 | 6.6941 | 39.95
2020-10-04 04:30 | 44108.1875 | 0 | 6.7018 | 39.95
2020-10-04 05:00 | 44108.2083 | 0 | 6.8638 | 39.95
2020-10-04 05:30 | 44108.2292 | 0 | 6.8561 | 39.95
2020-10-04 06:00 | 44108.25 | 0 | 6.8001 | 39.95
2020-10-04 06:30 | 44108.2708 | 0 | 6.477 | 39.95
2020-10-04 07:00 | 44108.2917 | 0 | 6.3391 | 39.95
2020-10-04 07:30 | 44108.3125 | 0 | 6.2267 | 39.95
2020-10-04 08:00 | 44108.3333 | 0 | 6.7901 | 39.95
2020-10-04 08:30 | 44108.3542 | 0 | 8.1119 | 39.95
2020-10-04 09:00 | 44108.375 | 0 | 7.6358 | 39.95
2020-10-04 09:30 | 44108.3958 | 0 | 6.5297 | 39.95
2020-10-04 10:00 | 44108.4167 | 0 | 5.9404 | 39.95
2020-10-04 10:30 | 44108.4375 | 0 | 5.4859 | 39.95
2020-10-04 11:00 | 44108.4583 | 0 | 5.3097 | 39.95
2020-10-04 11:30 | 44108.4792 | 0 | 5.3488 | 39.95
2020-10-04 12:00 | 44108.5 | 0 | 5.3207 | 39.95
2020-10-04 12:30 | 44108.5208 | 0 | 5.4828 | 39.95
2020-10-04 13:00 | 44108.5417 | 0 | 5.6317 | 39.95
2020-10-04 13:30 | 44108.5625 | 0 | 5.9388 | 39.95
2020-10-04 14:00 | 44108.5833 | 0 | 6.1713 | 39.95
2020-10-04 14:30 | 44108.6042 | 0 | 6.7024 | 39.95
2020-10-04 15:00 | 44108.625 | 0 | 7.2653 | 39.95
2020-10-04 15:30 | 44108.6458 | 0 | 7.869 | 39.95
2020-10-04 16:00 | 44108.6667 | 0 | 8.4647 | 39.95
2020-10-04 16:30 | 44108.6875 | 0 | 9.1853 | 39.95
2020-10-04 17:00 | 44108.7083 | 0 | 9.637 | 39.95
2020-10-04 17:30 | 44108.7292 | 0 | 9.9981 | 39.95
2020-10-04 18:00 | 44108.75 | 0 | 10.6203 | 39.95
2020-10-04 18:30 | 44108.7708 | 0 | 10.8974 | 39.95
2020-10-04 19:00 | 44108.7917 | 0 | 10.7104 | 39.95
2020-10-04 19:30 | 44108.8125 | 0 | 10.3081 | 39.95
2020-10-04 20:00 | 44108.8333 | 0 | 10.1364 | 39.95
2020-10-04 20:30 | 44108.8542 | 0 | 9.7294 | 39.95
2020-10-04 21:00 | 44108.875 | 0 | 9.4464 | 39.95
2020-10-04 21:30 | 44108.8958 | 0 | 9.2586 | 39.95
2020-10-04 22:00 | 44108.9167 | 0 | 9.0778 | 39.95
2020-10-04 22:30 | 44108.9375 | 0 | 8.4611 | 39.95
2020-10-04 23:00 | 44108.9583 | 0 | 7.9284 | 39.95
2020-10-04 23:30 | 44108.9792 | 0 | 7.7716 | 39.95
2020-10-05 | 44109 | 0 | 7.3863 | 39.95
2020-10-05 00:30 | 44109.0208 | 0 | 7.1334 | 39.95
2020-10-05 01:00 | 44109.0417 | 0 | 6.9901 | 39.95
2020-10-05 01:30 | 44109.0625 | 0 | 6.8225 | 39.95
2020-10-05 02:00 | 44109.0833 | 0 | 6.9063 | 39.95
2020-10-05 02:30 | 44109.1042 | 0 | 6.8283 | 39.95
2020-10-05 03:00 | 44109.125 | 0 | 6.8729 | 39.95
2020-10-05 03:30 | 44109.1458 | 0 | 6.7778 | 39.95
2020-10-05 04:00 | 44109.1667 | 0 | 6.8302 | 39.95
2020-10-05 04:30 | 44109.1875 | 0 | 6.9904 | 39.95
2020-10-05 05:00 | 44109.2083 | 0 | 7.1668 | 39.95
2020-10-05 05:30 | 44109.2292 | 0 | 7.3272 | 39.95
2020-10-05 06:00 | 44109.25 | 0 | 7.2656 | 39.95
2020-10-05 06:30 | 44109.2708 | 0 | 7.0883 | 39.95
2020-10-05 07:00 | 44109.2917 | 0 | 7.0345 | 39.95
2020-10-05 07:30 | 44109.3125 | 0 | 6.696 | 39.95
2020-10-05 08:00 | 44109.3333 | 0 | 6.8974 | 39.95
2020-10-05 08:30 | 44109.3542 | 0 | 6.8446 | 39.95
2020-10-05 09:00 | 44109.375 | 0 | 6.6979 | 39.95
2020-10-05 09:30 | 44109.3958 | 0 | 6.6924 | 39.95
2020-10-05 10:00 | 44109.4167 | 0 | 6.6981 | 39.95
2020-10-05 10:30 | 44109.4375 | 0 | 7.0074 | 39.95
2020-10-05 11:00 | 44109.4583 | 0 | 6.6176 | 39.95
2020-10-05 11:30 | 44109.4792 | 0 | 6.544 | 39.95
2020-10-05 12:00 | 44109.5 | 0 | 6.385 | 39.95
2020-10-05 12:30 | 44109.5208 | 0 | 6.5211 | 39.95
2020-10-05 13:00 | 44109.5417 | 0 | 6.7262 | 39.95
2020-10-05 13:30 | 44109.5625 | 0 | 6.9898 | 39.95
2020-10-05 14:00 | 44109.5833 | 0 | 7.4278 | 39.95
2020-10-05 14:30 | 44109.6042 | 0 | 7.9082 | 39.95
2020-10-05 15:00 | 44109.625 | 0 | 8.492 | 39.95
2020-10-05 15:30 | 44109.6458 | 0 | 9.1543 | 39.95
2020-10-05 16:00 | 44109.6667 | 0 | 9.8601 | 39.95
2020-10-05 16:30 | 44109.6875 | 0 | 10.6821 | 39.95
2020-10-05 17:00 | 44109.7083 | 0 | 11.1553 | 39.95
2020-10-05 17:30 | 44109.7292 | 0 | 11.643 | 39.95
2020-10-05 18:00 | 44109.75 | 0 | 12.3472 | 39.95
2020-10-05 18:30 | 44109.7708 | 0 | 12.6403 | 39.95
2020-10-05 19:00 | 44109.7917 | 0 | 12.2414 | 39.95
2020-10-05 19:30 | 44109.8125 | 0 | 11.8062 | 39.95
2020-10-05 20:00 | 44109.8333 | 0 | 11.6528 | 39.95
2020-10-05 20:30 | 44109.8542 | 0 | 11.1839 | 39.95
2020-10-05 21:00 | 44109.875 | 0 | 10.5295 | 39.95
2020-10-05 21:30 | 44109.8958 | 0 | 10.0529 | 39.95
2020-10-05 22:00 | 44109.9167 | 0 | 9.6712 | 39.95
2020-10-05 22:30 | 44109.9375 | 0 | 9.0288 | 39.95
2020-10-05 23:00 | 44109.9583 | 0 | 8.4966 | 39.95
2020-10-05 23:30 | 44109.9792 | 0 | 8.1325 | 39.95
2020-10-06 | 44110 | 0 | 7.6947 | 39.95
2020-10-06 00:30 | 44110.0208 | 0 | 7.3918 | 39.95
2020-10-06 01:00 | 44110.0417 | 0 | 7.2431 | 39.95
2020-10-06 01:30 | 44110.0625 | 0 | 7.1343 | 39.95
2020-10-06 02:00 | 44110.0833 | 0 | 7.2454 | 39.95
2020-10-06 02:30 | 44110.1042 | 0 | 7.2469 | 39.95
2020-10-06 03:00 | 44110.125 | 0 | 7.2395 | 39.95
2020-10-06 03:30 | 44110.1458 | 0 | 7.2824 | 39.95
2020-10-06 04:00 | 44110.1667 | 0 | 7.4283 | 39.95
2020-10-06 04:30 | 44110.1875 | 0 | 7.8428 | 39.95
2020-10-06 05:00 | 44110.2083 | 0 | 8.4712 | 39.95
2020-10-06 05:30 | 44110.2292 | 0 | 8.7955 | 39.95
2020-10-06 06:00 | 44110.25 | 0 | 9.4555 | 39.95
2020-10-06 06:30 | 44110.2708 | 0 | 10.0197 | 39.95
2020-10-06 07:00 | 44110.2917 | 0 | 10.8784 | 39.95
2020-10-06 07:30 | 44110.3125 | 0 | 10.4394 | 39.95
2020-10-06 08:00 | 44110.3333 | 0 | 10.8955 | 39.95
2020-10-06 08:30 | 44110.3542 | 0 | 11.7314 | 39.95
2020-10-06 09:00 | 44110.375 | 0 | 11.7787 | 39.95
2020-10-06 09:30 | 44110.3958 | 0 | 11.8934 | 39.95
2020-10-06 10:00 | 44110.4167 | 0 | 11.2348 | 39.95
2020-10-06 10:30 | 44110.4375 | 0 | 11.0049 | 39.95
2020-10-06 11:00 | 44110.4583 | 0 | 9.9968 | 39.95
2020-10-06 11:30 | 44110.4792 | 0 | 9.4894 | 39.95
2020-10-06 12:00 | 44110.5 | 0 | 9.6059 | 39.95
2020-10-06 12:30 | 44110.5208 | 0 | 9.6805 | 39.95
2020-10-06 13:00 | 44110.5417 | 0 | 9.592 | 39.95
2020-10-06 13:30 | 44110.5625 | 0 | 10.037 | 39.95
2020-10-06 14:00 | 44110.5833 | 0 | 10.5802 | 39.95
2020-10-06 14:30 | 44110.6042 | 0 | 10.8335 | 39.95
2020-10-06 15:00 | 44110.625 | 0 | 11.1144 | 39.95
2020-10-06 15:30 | 44110.6458 | 0 | 11.4811 | 39.95
2020-10-06 16:00 | 44110.6667 | 0 | 11.8357 | 39.95
2020-10-06 16:30 | 44110.6875 | 0 | 12.5566 | 39.95
2020-10-06 17:00 | 44110.7083 | 0 | 12.8672 | 39.95
2020-10-06 17:30 | 44110.7292 | 0 | 13.3491 | 39.95
2020-10-06 18:00 | 44110.75 | 0 | 13.822 | 39.95
2020-10-06 18:30 | 44110.7708 | 0 | 14.1812 | 39.95
2020-10-06 19:00 | 44110.7917 | 0 | 13.7281 | 39.95
2020-10-06 19:30 | 44110.8125 | 0 | 13.4202 | 39.95
2020-10-06 20:00 | 44110.8333 | 0 | 13.0547 | 39.95
2020-10-06 20:30 | 44110.8542 | 0 | 12.629 | 39.95
2020-10-06 21:00 | 44110.875 | 0 | 12.0301 | 39.95
2020-10-06 21:30 | 44110.8958 | 0 | 11.7114 | 39.95
2020-10-06 22:00 | 44110.9167 | 0 | 11.169 | 39.95
2020-10-06 22:30 | 44110.9375 | 0 | 10.3409 | 39.95
2020-10-06 23:00 | 44110.9583 | 0 | 9.5449 | 39.95
2020-10-06 23:30 | 44110.9792 | 0 | 9.1984 | 39.95
2020-10-07 | 44111 | 0 | 8.6244 | 39.95
2020-10-07 00:30 | 44111.0208 | 0 | 8.1264 | 39.95
2020-10-07 01:00 | 44111.0417 | 0 | 7.9614 | 39.95
2020-10-07 01:30 | 44111.0625 | 0 | 7.8255 | 39.95
2020-10-07 02:00 | 44111.0833 | 0 | 7.7883 | 39.95
2020-10-07 02:30 | 44111.1042 | 0 | 7.7569 | 39.95
2020-10-07 03:00 | 44111.125 | 0 | 7.6525 | 39.95
2020-10-07 03:30 | 44111.1458 | 0 | 7.6491 | 39.95
2020-10-07 04:00 | 44111.1667 | 0 | 7.8801 | 39.95
2020-10-07 04:30 | 44111.1875 | 0 | 8.2534 | 39.95
2020-10-07 05:00 | 44111.2083 | 0 | 8.8445 | 39.95
2020-10-07 05:30 | 44111.2292 | 0 | 9.1399 | 39.95
2020-10-07 06:00 | 44111.25 | 0 | 9.6437 | 39.95
2020-10-07 06:30 | 44111.2708 | 0 | 10.0332 | 39.95
2020-10-07 07:00 | 44111.2917 | 0 | 10.533 | 39.95
2020-10-07 07:30 | 44111.3125 | 0 | 10.4533 | 39.95
2020-10-07 08:00 | 44111.3333 | 0 | 10.5195 | 39.95
2020-10-07 08:30 | 44111.3542 | 0 | 11.021 | 39.95
2020-10-07 09:00 | 44111.375 | 0 | 11.06 | 39.95
2020-10-07 09:30 | 44111.3958 | 0 | 11.3152 | 39.95
2020-10-07 10:00 | 44111.4167 | 0 | 11.051 | 39.95
2020-10-07 10:30 | 44111.4375 | 0 | 10.9209 | 39.95
2020-10-07 11:00 | 44111.4583 | 0 | 10.0571 | 39.95
2020-10-07 11:30 | 44111.4792 | 0 | 10.4889 | 39.95
2020-10-07 12:00 | 44111.5 | 0 | 9.4805 | 39.95
2020-10-07 12:30 | 44111.5208 | 0 | 9.5694 | 39.95
2020-10-07 13:00 | 44111.5417 | 0 | 9.6482 | 39.95
2020-10-07 13:30 | 44111.5625 | 0 | 10.0102 | 39.95
2020-10-07 14:00 | 44111.5833 | 0 | 10.3083 | 39.95
2020-10-07 14:30 | 44111.6042 | 0 | 10.5413 | 39.95
2020-10-07 15:00 | 44111.625 | 0 | 10.9656 | 39.95
2020-10-07 15:30 | 44111.6458 | 0 | 11.3526 | 39.95
2020-10-07 16:00 | 44111.6667 | 0 | 12.1346 | 39.95
2020-10-07 16:30 | 44111.6875 | 0 | 12.4806 | 39.95
2020-10-07 17:00 | 44111.7083 | 0 | 12.6828 | 39.95
2020-10-07 17:30 | 44111.7292 | 0 | 13.1447 | 39.95
2020-10-07 18:00 | 44111.75 | 0 | 13.8402 | 39.95
2020-10-07 18:30 | 44111.7708 | 0 | 14.2819 | 39.95
2020-10-07 19:00 | 44111.7917 | 0 | 13.9961 | 39.95
2020-10-07 19:30 | 44111.8125 | 0 | 13.355 | 39.95
2020-10-07 20:00 | 44111.8333 | 0 | 13.2468 | 39.95
2020-10-07 20:30 | 44111.8542 | 0 | 12.6512 | 39.95
2020-10-07 21:00 | 44111.875 | 0 | 11.9747 | 39.95
2020-10-07 21:30 | 44111.8958 | 0 | 11.6463 | 39.95
2020-10-07 22:00 | 44111.9167 | 0 | 11.0761 | 39.95
2020-10-07 22:30 | 44111.9375 | 0 | 10.2206 | 39.95
2020-10-07 23:00 | 44111.9583 | 0 | 9.7579 | 39.95
2020-10-07 23:30 | 44111.9792 | 0 | 9.257 | 39.95
2020-10-08 | 44112 | 0 | 8.6722 | 39.95
2020-10-08 00:30 | 44112.0208 | 0 | 8.3249 | 39.95
2020-10-08 01:00 | 44112.0417 | 0 | 8.1048 | 39.95
2020-10-08 01:30 | 44112.0625 | 0 | 7.9728 | 39.95
2020-10-08 02:00 | 44112.0833 | 0 | 7.9336 | 39.95
2020-10-08 02:30 | 44112.1042 | 0 | 7.8106 | 39.95
2020-10-08 03:00 | 44112.125 | 0 | 7.7442 | 39.95
2020-10-08 03:30 | 44112.1458 | 0 | 7.8556 | 39.95
2020-10-08 04:00 | 44112.1667 | 0 | 7.9449 | 39.95
2020-10-08 04:30 | 44112.1875 | 0 | 8.3938 | 39.95
2020-10-08 05:00 | 44112.2083 | 0 | 8.8904 | 39.95
2020-10-08 05:30 | 44112.2292 | 0 | 9.1624 | 39.95
2020-10-08 06:00 | 44112.25 | 0 | 9.9462 | 39.95
2020-10-08 06:30 | 44112.2708 | 0 | 10.3866 | 39.95
2020-10-08 07:00 | 44112.2917 | 0 | 10.9965 | 39.95
2020-10-08 07:30 | 44112.3125 | 0 | 10.2841 | 39.95
2020-10-08 08:00 | 44112.3333 | 0 | 10.6106 | 39.95
2020-10-08 08:30 | 44112.3542 | 0 | 9.6632 | 39.95
2020-10-08 09:00 | 44112.375 | 0 | 9.5082 | 39.95
2020-10-08 09:30 | 44112.3958 | 0 | 9.8895 | 39.95
2020-10-08 10:00 | 44112.4167 | 0 | 10.1379 | 39.95
2020-10-08 10:30 | 44112.4375 | 0 | 9.9596 | 39.95
2020-10-08 11:00 | 44112.4583 | 0 | 10.2722 | 39.95
2020-10-08 11:30 | 44112.4792 | 0 | 10.377 | 39.95
2020-10-08 12:00 | 44112.5 | 0 | 9.8172 | 39.95
2020-10-08 12:30 | 44112.5208 | 0 | 9.7294 | 39.95
2020-10-08 13:00 | 44112.5417 | 0 | 10.4767 | 39.95
2020-10-08 13:30 | 44112.5625 | 0 | 11.2819 | 39.95
2020-10-08 14:00 | 44112.5833 | 0 | 11.9761 | 39.95
2020-10-08 14:30 | 44112.6042 | 0 | 12.3861 | 39.95
2020-10-08 15:00 | 44112.625 | 0 | 11.9907 | 39.95
2020-10-08 15:30 | 44112.6458 | 0 | 11.2626 | 39.95
2020-10-08 16:00 | 44112.6667 | 0 | 11.808 | 39.95
2020-10-08 16:30 | 44112.6875 | 0 | 12.5773 | 39.95
2020-10-08 17:00 | 44112.7083 | 0 | 12.989 | 39.95
2020-10-08 17:30 | 44112.7292 | 0 | 13.2795 | 39.95
2020-10-08 18:00 | 44112.75 | 0 | 13.8356 | 39.95
2020-10-08 18:30 | 44112.7708 | 0 | 14.1195 | 39.95
2020-10-08 19:00 | 44112.7917 | 0 | 13.6618 | 39.95
2020-10-08 19:30 | 44112.8125 | 0 | 13.6596 | 39.95
2020-10-08 20:00 | 44112.8333 | 0 | 13.2444 | 39.95
2020-10-08 20:30 | 44112.8542 | 0 | 12.8449 | 39.95
2020-10-08 21:00 | 44112.875 | 0 | 12.135 | 39.95
2020-10-08 21:30 | 44112.8958 | 0 | 11.8903 | 39.95
2020-10-08 22:00 | 44112.9167 | 0 | 11.3041 | 39.95
2020-10-08 22:30 | 44112.9375 | 0 | 10.4429 | 39.95
2020-10-08 23:00 | 44112.9583 | 0 | 9.7515 | 39.95
2020-10-08 23:30 | 44112.9792 | 0 | 9.2617 | 39.95
2020-10-09 | 44113 | 0 | 8.6193 | 39.95
2020-10-09 00:30 | 44113.0208 | 0 | 8.2557 | 39.95
2020-10-09 01:00 | 44113.0417 | 0 | 8.0786 | 39.95
2020-10-09 01:30 | 44113.0625 | 0 | 8.0064 | 39.95
2020-10-09 02:00 | 44113.0833 | 0 | 7.9278 | 39.95
2020-10-09 02:30 | 44113.1042 | 0 | 7.8443 | 39.95
2020-10-09 03:00 | 44113.125 | 0 | 7.8388 | 39.95
2020-10-09 03:30 | 44113.1458 | 0 | 7.7941 | 39.95
2020-10-09 04:00 | 44113.1667 | 0 | 7.9339 | 39.95
2020-10-09 04:30 | 44113.1875 | 0 | 8.394 | 39.95
2020-10-09 05:00 | 44113.2083 | 0 | 8.7275 | 39.95
2020-10-09 05:30 | 44113.2292 | 0 | 9.4797 | 39.95
2020-10-09 06:00 | 44113.25 | 0 | 9.7745 | 39.95
2020-10-09 06:30 | 44113.2708 | 0 | 10.245 | 39.95
2020-10-09 07:00 | 44113.2917 | 0 | 10.6808 | 39.95
2020-10-09 07:30 | 44113.3125 | 0 | 10.563 | 39.95
2020-10-09 08:00 | 44113.3333 | 0 | 10.4089 | 39.95
2020-10-09 08:30 | 44113.3542 | 0 | 10.4858 | 39.95
2020-10-09 09:00 | 44113.375 | 0 | 10.2209 | 39.95
2020-10-09 09:30 | 44113.3958 | 0 | 10.3587 | 39.95
2020-10-09 10:00 | 44113.4167 | 0 | 10.4015 | 39.95
2020-10-09 10:30 | 44113.4375 | 0 | 10.176 | 39.95
2020-10-09 11:00 | 44113.4583 | 0 | 10.2601 | 39.95
2020-10-09 11:30 | 44113.4792 | 0 | 10.2991 | 39.95
2020-10-09 12:00 | 44113.5 | 0 | 10.34 | 39.95
2020-10-09 12:30 | 44113.5208 | 0 | 10.3196 | 39.95
2020-10-09 13:00 | 44113.5417 | 0 | 10.6648 | 39.95
2020-10-09 13:30 | 44113.5625 | 0 | 11.1162 | 39.95
2020-10-09 14:00 | 44113.5833 | 0 | 11.6179 | 39.95
2020-10-09 14:30 | 44113.6042 | 0 | 12.1302 | 39.95
2020-10-09 15:00 | 44113.625 | 0 | 14.0783 | 39.95
2020-10-09 15:30 | 44113.6458 | 0 | 13.6519 | 39.95
2020-10-09 16:00 | 44113.6667 | 0 | 13.3299 | 39.95
2020-10-09 16:30 | 44113.6875 | 0 | 13.3984 | 39.95
2020-10-09 17:00 | 44113.7083 | 0 | 13.4774 | 39.95
2020-10-09 17:30 | 44113.7292 | 0 | 13.5266 | 39.95
2020-10-09 18:00 | 44113.75 | 0 | 13.9699 | 39.95
2020-10-09 18:30 | 44113.7708 | 0 | 14.3133 | 39.95
2020-10-09 19:00 | 44113.7917 | 0 | 13.8923 | 39.95
2020-10-09 19:30 | 44113.8125 | 0 | 13.7034 | 39.95
2020-10-09 20:00 | 44113.8333 | 0 | 13.4964 | 39.95
2020-10-09 20:30 | 44113.8542 | 0 | 13.0698 | 39.95
2020-10-09 21:00 | 44113.875 | 0 | 12.5331 | 39.95
2020-10-09 21:30 | 44113.8958 | 0 | 12.3202 | 39.95
2020-10-09 22:00 | 44113.9167 | 0 | 11.8047 | 39.95
2020-10-09 22:30 | 44113.9375 | 0 | 10.9025 | 39.95
2020-10-09 23:00 | 44113.9583 | 0 | 10.2745 | 39.95
2020-10-09 23:30 | 44113.9792 | 0 | 9.7712 | 39.95
2020-10-10 | 44114 | 0 | 9.0958 | 39.95
2020-10-10 00:30 | 44114.0208 | 0 | 8.6833 | 39.95
2020-10-10 01:00 | 44114.0417 | 0 | 8.4754 | 39.95
2020-10-10 01:30 | 44114.0625 | 0 | 8.3653 | 39.95
2020-10-10 02:00 | 44114.0833 | 0 | 8.1605 | 39.95
2020-10-10 02:30 | 44114.1042 | 0 | 7.9281 | 39.95
2020-10-10 03:00 | 44114.125 | 0 | 7.9171 | 39.95
2020-10-10 03:30 | 44114.1458 | 0 | 8.0602 | 39.95
2020-10-10 04:00 | 44114.1667 | 0 | 8.1183 | 39.95
2020-10-10 04:30 | 44114.1875 | 0 | 8.3301 | 39.95
2020-10-10 05:00 | 44114.2083 | 0 | 8.4922 | 39.95
2020-10-10 05:30 | 44114.2292 | 0 | 8.4362 | 39.95
2020-10-10 06:00 | 44114.25 | 0 | 8.5256 | 39.95
2020-10-10 06:30 | 44114.2708 | 0 | 8.4359 | 39.95
2020-10-10 07:00 | 44114.2917 | 0 | 8.276 | 39.95
2020-10-10 07:30 | 44114.3125 | 0 | 8.2033 | 39.95
2020-10-10 08:00 | 44114.3333 | 0 | 8.4549 | 39.95
2020-10-10 08:30 | 44114.3542 | 0 | 8.0096 | 39.95
2020-10-10 09:00 | 44114.375 | 0 | 7.6433 | 39.95
2020-10-10 09:30 | 44114.3958 | 0 | 7.6548 | 39.95
2020-10-10 10:00 | 44114.4167 | 0 | 7.8387 | 39.95
2020-10-10 10:30 | 44114.4375 | 0 | 7.7703 | 39.95
2020-10-10 11:00 | 44114.4583 | 0 | 7.3114 | 39.95
2020-10-10 11:30 | 44114.4792 | 0 | 7.3326 | 39.95
2020-10-10 12:00 | 44114.5 | 0 | 7.2041 | 39.95
2020-10-10 12:30 | 44114.5208 | 0 | 7.4481 | 39.95
2020-10-10 13:00 | 44114.5417 | 0 | 7.7273 | 39.95
2020-10-10 13:30 | 44114.5625 | 0 | 7.5991 | 39.95
2020-10-10 14:00 | 44114.5833 | 0 | 8.0401 | 39.95
2020-10-10 14:30 | 44114.6042 | 0 | 8.4416 | 39.95
2020-10-10 15:00 | 44114.625 | 0 | 9.0584 | 39.95
2020-10-10 15:30 | 44114.6458 | 0 | 9.3838 | 39.95
2020-10-10 16:00 | 44114.6667 | 0 | 9.9792 | 39.95
2020-10-10 16:30 | 44114.6875 | 0 | 10.5614 | 39.95
2020-10-10 17:00 | 44114.7083 | 0 | 10.8407 | 39.95
2020-10-10 17:30 | 44114.7292 | 0 | 10.9771 | 39.95
2020-10-10 18:00 | 44114.75 | 0 | 11.4442 | 39.95
2020-10-10 18:30 | 44114.7708 | 0 | 11.7682 | 39.95
2020-10-10 19:00 | 44114.7917 | 0 | 11.6059 | 39.95
2020-10-10 19:30 | 44114.8125 | 0 | 11.3656 | 39.95
2020-10-10 20:00 | 44114.8333 | 0 | 11.1247 | 39.95
2020-10-10 20:30 | 44114.8542 | 0 | 10.7159 | 39.95
2020-10-10 21:00 | 44114.875 | 0 | 10.3415 | 39.95
2020-10-10 21:30 | 44114.8958 | 0 | 10.0216 | 39.95
2020-10-10 22:00 | 44114.9167 | 0 | 9.6732 | 39.95
2020-10-10 22:30 | 44114.9375 | 0 | 9.0499 | 39.95
2020-10-10 23:00 | 44114.9583 | 0 | 8.5631 | 39.95
2020-10-10 23:30 | 44114.9792 | 0 | 8.2927 | 39.95
2020-10-11 | 44115 | 0 | 7.7321 | 39.95
2020-10-11 00:30 | 44115.0208 | 0 | 7.3639 | 39.95
2020-10-11 01:00 | 44115.0417 | 0 | 7.1894 | 39.95
2020-10-11 01:30 | 44115.0625 | 0 | 7.2469 | 39.95
2020-10-11 02:00 | 44115.0833 | 0 | 7.1628 | 39.95
2020-10-11 02:30 | 44115.1042 | 0 | 7.2005 | 39.95
2020-10-11 03:00 | 44115.125 | 0 | 7.1837 | 39.95
2020-10-11 03:30 | 44115.1458 | 0 | 7.0626 | 39.95
2020-10-11 04:00 | 44115.1667 | 0 | 6.9788 | 39.95
2020-10-11 04:30 | 44115.1875 | 0 | 6.9791 | 39.95
2020-10-11 05:00 | 44115.2083 | 0 | 6.9956 | 39.95
2020-10-11 05:30 | 44115.2292 | 0 | 7.0403 | 39.95
2020-10-11 06:00 | 44115.25 | 0 | 6.895 | 39.95
2020-10-11 06:30 | 44115.2708 | 0 | 6.7891 | 39.95
2020-10-11 07:00 | 44115.2917 | 0 | 6.6198 | 39.95
2020-10-11 07:30 | 44115.3125 | 0 | 6.8956 | 39.95
2020-10-11 08:00 | 44115.3333 | 0 | 7.0892 | 39.95
2020-10-11 08:30 | 44115.3542 | 0 | 7.3396 | 39.95
2020-10-11 09:00 | 44115.375 | 0 | 6.7368 | 39.95
2020-10-11 09:30 | 44115.3958 | 0 | 6.4821 | 39.95
2020-10-11 10:00 | 44115.4167 | 0 | 6.5326 | 39.95
2020-10-11 10:30 | 44115.4375 | 0 | 6.4914 | 39.95
2020-10-11 11:00 | 44115.4583 | 0 | 6.1369 | 39.95
2020-10-11 11:30 | 44115.4792 | 0 | 6.3893 | 39.95
2020-10-11 12:00 | 44115.5 | 0 | 6.4713 | 39.95
2020-10-11 12:30 | 44115.5208 | 0 | 6.5883 | 39.95
2020-10-11 13:00 | 44115.5417 | 0 | 6.5415 | 39.95
2020-10-11 13:30 | 44115.5625 | 0 | 6.9436 | 39.95
2020-10-11 14:00 | 44115.5833 | 0 | 7.4828 | 39.95
2020-10-11 14:30 | 44115.6042 | 0 | 7.8597 | 39.95
2020-10-11 15:00 | 44115.625 | 0 | 8.4644 | 39.95
2020-10-11 15:30 | 44115.6458 | 0 | 9.0594 | 39.95
2020-10-11 16:00 | 44115.6667 | 0 | 9.6911 | 39.95
2020-10-11 16:30 | 44115.6875 | 0 | 10.7447 | 39.95
2020-10-11 17:00 | 44115.7083 | 0 | 11.1888 | 39.95
2020-10-11 17:30 | 44115.7292 | 0 | 11.546 | 39.95
2020-10-11 18:00 | 44115.75 | 0 | 12.1606 | 39.95
2020-10-11 18:30 | 44115.7708 | 0 | 12.5534 | 39.95
2020-10-11 19:00 | 44115.7917 | 0 | 12.2054 | 39.95
2020-10-11 19:30 | 44115.8125 | 0 | 11.8714 | 39.95
2020-10-11 20:00 | 44115.8333 | 0 | 11.5117 | 39.95
2020-10-11 20:30 | 44115.8542 | 0 | 11.1269 | 39.95
2020-10-11 21:00 | 44115.875 | 0 | 10.5236 | 39.95
2020-10-11 21:30 | 44115.8958 | 0 | 10.2432 | 39.95
2020-10-11 22:00 | 44115.9167 | 0 | 9.7489 | 39.95
2020-10-11 22:30 | 44115.9375 | 0 | 9.0781 | 39.95
2020-10-11 23:00 | 44115.9583 | 0 | 8.5628 | 39.95
2020-10-11 23:30 | 44115.9792 | 0 | 8.1662 | 39.95
2020-10-12 | 44116 | 0 | 7.9134 | 39.95
2020-10-12 00:30 | 44116.0208 | 0 | 7.7547 | 39.95
2020-10-12 01:00 | 44116.0417 | 0 | 7.6323 | 39.95
2020-10-12 01:30 | 44116.0625 | 0 | 7.6488 | 39.95
2020-10-12 02:00 | 44116.0833 | 0 | 7.5653 | 39.95
2020-10-12 02:30 | 44116.1042 | 0 | 7.4925 | 39.95
2020-10-12 03:00 | 44116.125 | 0 | 7.5206 | 39.95
2020-10-12 03:30 | 44116.1458 | 0 | 7.7514 | 39.95
2020-10-12 04:00 | 44116.1667 | 0 | 7.8467 | 39.95
2020-10-12 04:30 | 44116.1875 | 0 | 8.0549 | 39.95
2020-10-12 05:00 | 44116.2083 | 0 | 8.5615 | 39.95
2020-10-12 05:30 | 44116.2292 | 0 | 9.2545 | 39.95
2020-10-12 06:00 | 44116.25 | 0 | 9.9004 | 39.95
2020-10-12 06:30 | 44116.2708 | 0 | 10.6739 | 39.95
2020-10-12 07:00 | 44116.2917 | 0 | 11.5539 | 39.95
2020-10-12 07:30 | 44116.3125 | 0 | 11.3546 | 39.95
2020-10-12 08:00 | 44116.3333 | 0 | 11.7682 | 39.95
2020-10-12 08:30 | 44116.3542 | 0 | 11.173 | 39.95
2020-10-12 09:00 | 44116.375 | 0 | 11.3913 | 39.95
2020-10-12 09:30 | 44116.3958 | 0 | 10.6306 | 39.95
2020-10-12 10:00 | 44116.4167 | 0 | 11.7037 | 39.95
2020-10-12 10:30 | 44116.4375 | 0 | 12.1993 | 39.95
2020-10-12 11:00 | 44116.4583 | 0 | 12.343 | 39.95
2020-10-12 11:30 | 44116.4792 | 0 | 11.4984 | 39.95
2020-10-12 12:00 | 44116.5 | 0 | 10.2922 | 39.95
2020-10-12 12:30 | 44116.5208 | 0 | 10.3823 | 39.95
2020-10-12 13:00 | 44116.5417 | 0 | 10.3384 | 39.95
2020-10-12 13:30 | 44116.5625 | 0 | 10.7505 | 39.95
2020-10-12 14:00 | 44116.5833 | 0 | 10.6299 | 39.95
2020-10-12 14:30 | 44116.6042 | 0 | 10.833 | 39.95
2020-10-12 15:00 | 44116.625 | 0 | 11.1164 | 39.95
2020-10-12 15:30 | 44116.6458 | 0 | 11.5866 | 39.95
2020-10-12 16:00 | 44116.6667 | 0 | 12.1495 | 39.95
2020-10-12 16:30 | 44116.6875 | 0 | 12.6908 | 39.95
2020-10-12 17:00 | 44116.7083 | 0 | 12.8898 | 39.95
2020-10-12 17:30 | 44116.7292 | 0 | 13.1342 | 39.95
2020-10-12 18:00 | 44116.75 | 0 | 13.7023 | 39.95
2020-10-12 18:30 | 44116.7708 | 0 | 14.0636 | 39.95
2020-10-12 19:00 | 44116.7917 | 0 | 13.7422 | 39.95
2020-10-12 19:30 | 44116.8125 | 0 | 13.5559 | 39.95
2020-10-12 20:00 | 44116.8333 | 0 | 13.3136 | 39.95
2020-10-12 20:30 | 44116.8542 | 0 | 12.7257 | 39.95
2020-10-12 21:00 | 44116.875 | 0 | 11.8433 | 39.95
2020-10-12 21:30 | 44116.8958 | 0 | 11.5058 | 39.95
2020-10-12 22:00 | 44116.9167 | 0 | 11.0084 | 39.95
2020-10-12 22:30 | 44116.9375 | 0 | 10.273 | 39.95
2020-10-12 23:00 | 44116.9583 | 0 | 9.6174 | 39.95
2020-10-12 23:30 | 44116.9792 | 0 | 9.1906 | 39.95
2020-10-13 | 44117 | 0 | 8.7333 | 39.95
2020-10-13 00:30 | 44117.0208 | 0 | 8.3041 | 39.95
2020-10-13 01:00 | 44117.0417 | 0 | 8.0119 | 39.95
2020-10-13 01:30 | 44117.0625 | 0 | 7.9391 | 39.95
2020-10-13 02:00 | 44117.0833 | 0 | 7.5987 | 39.95
2020-10-13 02:30 | 44117.1042 | 0 | 7.8803 | 39.95
2020-10-13 03:00 | 44117.125 | 0 | 7.9333 | 39.95
2020-10-13 03:30 | 44117.1458 | 0 | 7.9171 | 39.95
2020-10-13 04:00 | 44117.1667 | 0 | 8.0064 | 39.95
2020-10-13 04:30 | 44117.1875 | 0 | 8.3831 | 39.95
2020-10-13 05:00 | 44117.2083 | 0 | 8.908 | 39.95
2020-10-13 05:30 | 44117.2292 | 0 | 9.421 | 39.95
2020-10-13 06:00 | 44117.25 | 0 | 9.6213 | 39.95
2020-10-13 06:30 | 44117.2708 | 0 | 10.2845 | 39.95
2020-10-13 07:00 | 44117.2917 | 0 | 10.5892 | 39.95
2020-10-13 07:30 | 44117.3125 | 0 | 10.4313 | 39.95
2020-10-13 08:00 | 44117.3333 | 0 | 10.3677 | 39.95
2020-10-13 08:30 | 44117.3542 | 0 | 10.3894 | 39.95
2020-10-13 09:00 | 44117.375 | 0 | 10.3399 | 39.95
2020-10-13 09:30 | 44117.3958 | 0 | 10.52 | 39.95
2020-10-13 10:00 | 44117.4167 | 0 | 11.3891 | 39.95
2020-10-13 10:30 | 44117.4375 | 0 | 11.9695 | 39.95
2020-10-13 11:00 | 44117.4583 | 0 | 11.4153 | 39.95
2020-10-13 11:30 | 44117.4792 | 0 | 11.0114 | 39.95
2020-10-13 12:00 | 44117.5 | 0 | 10.0725 | 39.95
2020-10-13 12:30 | 44117.5208 | 0 | 10.2921 | 39.95
2020-10-13 13:00 | 44117.5417 | 0 | 10.9381 | 39.95
2020-10-13 13:30 | 44117.5625 | 0 | 11.258 | 39.95
2020-10-13 14:00 | 44117.5833 | 0 | 12.1829 | 39.95
2020-10-13 14:30 | 44117.6042 | 0 | 11.1049 | 39.95
2020-10-13 15:00 | 44117.625 | 0 | 11.7543 | 39.95
2020-10-13 15:30 | 44117.6458 | 0 | 11.444 | 39.95
2020-10-13 16:00 | 44117.6667 | 0 | 12.2033 | 39.95
2020-10-13 16:30 | 44117.6875 | 0 | 12.573 | 39.95
2020-10-13 17:00 | 44117.7083 | 0 | 12.551 | 39.95
2020-10-13 17:30 | 44117.7292 | 0 | 13.0899 | 39.95
2020-10-13 18:00 | 44117.75 | 0 | 13.76 | 39.95
2020-10-13 18:30 | 44117.7708 | 0 | 14.1531 | 39.95
2020-10-13 19:00 | 44117.7917 | 0 | 13.825 | 39.95
2020-10-13 19:30 | 44117.8125 | 0 | 13.4237 | 39.95
2020-10-13 20:00 | 44117.8333 | 0 | 13.2766 | 39.95
2020-10-13 20:30 | 44117.8542 | 0 | 12.8676 | 39.95
2020-10-13 21:00 | 44117.875 | 0 | 12.1566 | 39.95
2020-10-13 21:30 | 44117.8958 | 0 | 11.5719 | 39.95
2020-10-13 22:00 | 44117.9167 | 0 | 11.1731 | 39.95
2020-10-13 22:30 | 44117.9375 | 0 | 10.2538 | 39.95
2020-10-13 23:00 | 44117.9583 | 0 | 9.6907 | 39.95
2020-10-13 23:30 | 44117.9792 | 0 | 9.171 | 39.95
2020-10-14 | 44118 | 0 | 8.5889 | 39.95
2020-10-14 00:30 | 44118.0208 | 0 | 8.1911 | 39.95
2020-10-14 01:00 | 44118.0417 | 0 | 7.8779 | 39.95
2020-10-14 01:30 | 44118.0625 | 0 | 7.8666 | 39.95
2020-10-14 02:00 | 44118.0833 | 0 | 7.8556 | 39.95
2020-10-14 02:30 | 44118.1042 | 0 | 7.8462 | 39.95
2020-10-14 03:00 | 44118.125 | 0 | 7.7771 | 39.95
2020-10-14 03:30 | 44118.1458 | 0 | 7.8969 | 39.95
2020-10-14 04:00 | 44118.1667 | 0 | 8.2002 | 39.95
2020-10-14 04:30 | 44118.1875 | 0 | 8.4578 | 39.95
2020-10-14 05:00 | 44118.2083 | 0 | 8.9376 | 39.95
2020-10-14 05:30 | 44118.2292 | 0 | 9.2181 | 39.95
2020-10-14 06:00 | 44118.25 | 0 | 9.7204 | 39.95
2020-10-14 06:30 | 44118.2708 | 0 | 10.6259 | 39.95
2020-10-14 07:00 | 44118.2917 | 0 | 11.3291 | 39.95
2020-10-14 07:30 | 44118.3125 | 0 | 10.9491 | 39.95
2020-10-14 08:00 | 44118.3333 | 0 | 11.8089 | 39.95
2020-10-14 08:30 | 44118.3542 | 0 | 11.6547 | 39.95
2020-10-14 09:00 | 44118.375 | 0 | 12.1606 | 39.95
2020-10-14 09:30 | 44118.3958 | 0 | 11.5425 | 39.95
2020-10-14 10:00 | 44118.4167 | 0 | 11.303 | 39.95
2020-10-14 10:30 | 44118.4375 | 0 | 9.658 | 39.95
2020-10-14 11:00 | 44118.4583 | 0 | 8.9217 | 39.95
2020-10-14 11:30 | 44118.4792 | 0 | 11.1715 | 39.95
2020-10-14 12:00 | 44118.5 | 0 | 11.7789 | 39.95
2020-10-14 12:30 | 44118.5208 | 0 | 10.6035 | 39.95
2020-10-14 13:00 | 44118.5417 | 0 | 11.718 | 39.95
2020-10-14 13:30 | 44118.5625 | 0 | 10.4853 | 39.95
2020-10-14 14:00 | 44118.5833 | 0 | 10.5997 | 39.95
2020-10-14 14:30 | 44118.6042 | 0 | 11.5088 | 39.95
2020-10-14 15:00 | 44118.625 | 0 | 11.5074 | 39.95
2020-10-14 15:30 | 44118.6458 | 0 | 11.3642 | 39.95
2020-10-14 16:00 | 44118.6667 | 0 | 12.1324 | 39.95
2020-10-14 16:30 | 44118.6875 | 0 | 12.1658 | 39.95
2020-10-14 17:00 | 44118.7083 | 0 | 12.3874 | 39.95
2020-10-14 17:30 | 44118.7292 | 0 | 12.7763 | 39.95
2020-10-14 18:00 | 44118.75 | 0 | 13.4323 | 39.95
2020-10-14 18:30 | 44118.7708 | 0 | 14.0379 | 39.95
2020-10-14 19:00 | 44118.7917 | 0 | 13.5836 | 39.95
2020-10-14 19:30 | 44118.8125 | 0 | 13.0598 | 39.95
2020-10-14 20:00 | 44118.8333 | 0 | 12.9097 | 39.95
2020-10-14 20:30 | 44118.8542 | 0 | 12.4755 | 39.95
2020-10-14 21:00 | 44118.875 | 0 | 11.6415 | 39.95
2020-10-14 21:30 | 44118.8958 | 0 | 11.371 | 39.95
2020-10-14 22:00 | 44118.9167 | 0 | 10.822 | 39.95
2020-10-14 22:30 | 44118.9375 | 0 | 9.9488 | 39.95
2020-10-14 23:00 | 44118.9583 | 0 | 9.3955 | 39.95
2020-10-14 23:30 | 44118.9792 | 0 | 8.9546 | 39.95
2020-10-15 | 44119 | 0 | 8.4329 | 39.95
2020-10-15 00:30 | 44119.0208 | 0 | 7.9906 | 39.95
2020-10-15 01:00 | 44119.0417 | 0 | 7.8109 | 39.95
2020-10-15 01:30 | 44119.0625 | 0 | 7.7399 | 39.95
2020-10-15 02:00 | 44119.0833 | 0 | 7.7624 | 39.95
2020-10-15 02:30 | 44119.1042 | 0 | 7.6546 | 39.95
2020-10-15 03:00 | 44119.125 | 0 | 7.6862 | 39.95
2020-10-15 03:30 | 44119.1458 | 0 | 7.7792 | 39.95
2020-10-15 04:00 | 44119.1667 | 0 | 7.9061 | 39.95
2020-10-15 04:30 | 44119.1875 | 0 | 8.3549 | 39.95
2020-10-15 05:00 | 44119.2083 | 0 | 8.7585 | 39.95
2020-10-15 05:30 | 44119.2292 | 0 | 9.1828 | 39.95
2020-10-15 06:00 | 44119.25 | 0 | 9.8039 | 39.95
2020-10-15 06:30 | 44119.2708 | 0 | 10.1669 | 39.95
2020-10-15 07:00 | 44119.2917 | 0 | 10.29 | 39.95
2020-10-15 07:30 | 44119.3125 | 0 | 10.0641 | 39.95
2020-10-15 08:00 | 44119.3333 | 0 | 10.238 | 39.95
2020-10-15 08:30 | 44119.3542 | 0 | 10.8938 | 39.95
2020-10-15 09:00 | 44119.375 | 0 | 14.789 | 39.95
2020-10-15 09:30 | 44119.3958 | 0 | 19.4811 | 39.95
2020-10-15 10:00 | 44119.4167 | 0 | 18.7495 | 39.95
2020-10-15 10:30 | 44119.4375 | 0 | 19.4864 | 39.95
2020-10-15 11:00 | 44119.4583 | 0 | 19.6091 | 39.95
2020-10-15 11:30 | 44119.4792 | 0 | 19.3125 | 39.95
2020-10-15 12:00 | 44119.5 | 0 | 18.3511 | 39.95
2020-10-15 12:30 | 44119.5208 | 0 | 18.3638 | 39.95
2020-10-15 13:00 | 44119.5417 | 0 | 14.936 | 39.95
2020-10-15 13:30 | 44119.5625 | 0 | 9.893 | 39.95
2020-10-15 14:00 | 44119.5833 | 0 | 10.1514 | 39.95
2020-10-15 14:30 | 44119.6042 | 0 | 10.4111 | 39.95
2020-10-15 15:00 | 44119.625 | 0 | 10.8862 | 39.95
2020-10-15 15:30 | 44119.6458 | 0 | 11.4289 | 39.95
2020-10-15 16:00 | 44119.6667 | 0 | 12.0174 | 39.95
2020-10-15 16:30 | 44119.6875 | 0 | 12.4525 | 39.95
2020-10-15 17:00 | 44119.7083 | 0 | 12.7128 | 39.95
2020-10-15 17:30 | 44119.7292 | 0 | 12.9415 | 39.95
2020-10-15 18:00 | 44119.75 | 0 | 13.3496 | 39.95
2020-10-15 18:30 | 44119.7708 | 0 | 13.7698 | 39.95
2020-10-15 19:00 | 44119.7917 | 0 | 13.5308 | 39.95
2020-10-15 19:30 | 44119.8125 | 0 | 13.2154 | 39.95
2020-10-15 20:00 | 44119.8333 | 0 | 13.176 | 39.95
2020-10-15 20:30 | 44119.8542 | 0 | 12.5713 | 39.95
2020-10-15 21:00 | 44119.875 | 0 | 11.8928 | 39.95
2020-10-15 21:30 | 44119.8958 | 0 | 11.5123 | 39.95
2020-10-15 22:00 | 44119.9167 | 0 | 11.1178 | 39.95
2020-10-15 22:30 | 44119.9375 | 0 | 10.2929 | 39.95
2020-10-15 23:00 | 44119.9583 | 0 | 9.7833 | 39.95
2020-10-15 23:30 | 44119.9792 | 0 | 9.144 | 39.95
2020-10-16 | 44120 | 0 | 8.6254 | 39.95
2020-10-16 00:30 | 44120.0208 | 0 | 8.1956 | 39.95
2020-10-16 01:00 | 44120.0417 | 0 | 7.9281 | 39.95
2020-10-16 01:30 | 44120.0625 | 0 | 7.8721 | 39.95
2020-10-16 02:00 | 44120.0833 | 0 | 7.8275 | 39.95
2020-10-16 02:30 | 44120.1042 | 0 | 7.8072 | 39.95
2020-10-16 03:00 | 44120.125 | 0 | 7.7715 | 39.95
2020-10-16 03:30 | 44120.1458 | 0 | 7.7996 | 39.95
2020-10-16 04:00 | 44120.1667 | 0 | 8.029 | 39.95
2020-10-16 04:30 | 44120.1875 | 0 | 8.4261 | 39.95
2020-10-16 05:00 | 44120.2083 | 0 | 8.7868 | 39.95
2020-10-16 05:30 | 44120.2292 | 0 | 9.1287 | 39.95
2020-10-16 06:00 | 44120.25 | 0 | 9.7079 | 39.95
2020-10-16 06:30 | 44120.2708 | 0 | 9.8992 | 39.95
2020-10-16 07:00 | 44120.2917 | 0 | 10.2005 | 39.95
2020-10-16 07:30 | 44120.3125 | 0 | 10.0717 | 39.95
2020-10-16 08:00 | 44120.3333 | 0 | 9.8485 | 39.95
2020-10-16 08:30 | 44120.3542 | 0 | 9.6846 | 39.95
2020-10-16 09:00 | 44120.375 | 0 | 9.5975 | 39.95
2020-10-16 09:30 | 44120.3958 | 0 | 9.4575 | 39.95
2020-10-16 10:00 | 44120.4167 | 0 | 9.5773 | 39.95
2020-10-16 10:30 | 44120.4375 | 0 | 9.6234 | 39.95
2020-10-16 11:00 | 44120.4583 | 0 | 9.7037 | 39.95
2020-10-16 11:30 | 44120.4792 | 0 | 9.6962 | 39.95
2020-10-16 12:00 | 44120.5 | 0 | 9.7723 | 39.95
2020-10-16 12:30 | 44120.5208 | 0 | 9.8507 | 39.95
2020-10-16 13:00 | 44120.5417 | 0 | 9.7743 | 39.95
2020-10-16 13:30 | 44120.5625 | 0 | 10.0686 | 39.95
2020-10-16 14:00 | 44120.5833 | 0 | 10.5744 | 39.95
2020-10-16 14:30 | 44120.6042 | 0 | 11.0519 | 39.95
2020-10-16 15:00 | 44120.625 | 0 | 11.254 | 39.95
2020-10-16 15:30 | 44120.6458 | 0 | 11.8737 | 39.95
2020-10-16 16:00 | 44120.6667 | 0 | 12.4544 | 39.95
2020-10-16 16:30 | 44120.6875 | 0 | 12.9405 | 39.95
2020-10-16 17:00 | 44120.7083 | 0 | 13.0431 | 39.95
2020-10-16 17:30 | 44120.7292 | 0 | 12.9529 | 39.95
2020-10-16 18:00 | 44120.75 | 0 | 13.0426 | 39.95
2020-10-16 18:30 | 44120.7708 | 0 | 13.4575 | 39.95
2020-10-16 19:00 | 44120.7917 | 0 | 13.2093 | 39.95
2020-10-16 19:30 | 44120.8125 | 0 | 13.0759 | 39.95
2020-10-16 20:00 | 44120.8333 | 0 | 12.9584 | 39.95
2020-10-16 20:30 | 44120.8542 | 0 | 12.4724 | 39.95
2020-10-16 21:00 | 44120.875 | 0 | 12.037 | 39.95
2020-10-16 21:30 | 44120.8958 | 0 | 11.7525 | 39.95
2020-10-16 22:00 | 44120.9167 | 0 | 11.0186 | 39.95
2020-10-16 22:30 | 44120.9375 | 0 | 10.2959 | 39.95
2020-10-16 23:00 | 44120.9583 | 0 | 9.8285 | 39.95
2020-10-16 23:30 | 44120.9792 | 0 | 9.4837 | 39.95
2020-10-17 | 44121 | 0 | 8.7457 | 39.95
2020-10-17 00:30 | 44121.0208 | 0 | 8.3747 | 39.95
2020-10-17 01:00 | 44121.0417 | 0 | 8.071 | 39.95
2020-10-17 01:30 | 44121.0625 | 0 | 7.9281 | 39.95
2020-10-17 02:00 | 44121.0833 | 0 | 7.8889 | 39.95
2020-10-17 02:30 | 44121.1042 | 0 | 7.831 | 39.95
2020-10-17 03:00 | 44121.125 | 0 | 7.6656 | 39.95
2020-10-17 03:30 | 44121.1458 | 0 | 7.7645 | 39.95
2020-10-17 04:00 | 44121.1667 | 0 | 7.7177 | 39.95
2020-10-17 04:30 | 44121.1875 | 0 | 7.8054 | 39.95
2020-10-17 05:00 | 44121.2083 | 0 | 7.9058 | 39.95
2020-10-17 05:30 | 44121.2292 | 0 | 7.7939 | 39.95
2020-10-17 06:00 | 44121.25 | 0 | 7.8574 | 39.95
2020-10-17 06:30 | 44121.2708 | 0 | 7.6861 | 39.95
2020-10-17 07:00 | 44121.2917 | 0 | 7.8015 | 39.95
2020-10-17 07:30 | 44121.3125 | 0 | 7.6656 | 39.95
2020-10-17 08:00 | 44121.3333 | 0 | 8.3002 | 39.95
2020-10-17 08:30 | 44121.3542 | 0 | 8.0731 | 39.95
2020-10-17 09:00 | 44121.375 | 0 | 8.2985 | 39.95
2020-10-17 09:30 | 44121.3958 | 0 | 7.8294 | 39.95
2020-10-17 10:00 | 44121.4167 | 0 | 7.3638 | 39.95
2020-10-17 10:30 | 44121.4375 | 0 | 7.1904 | 39.95
2020-10-17 11:00 | 44121.4583 | 0 | 7.2579 | 39.95
2020-10-17 11:30 | 44121.4792 | 0 | 7.3784 | 39.95
2020-10-17 12:00 | 44121.5 | 0 | 7.3919 | 39.95
2020-10-17 12:30 | 44121.5208 | 0 | 7.2955 | 39.95
2020-10-17 13:00 | 44121.5417 | 0 | 8.4167 | 39.95
2020-10-17 13:30 | 44121.5625 | 0 | 8.7231 | 39.95
2020-10-17 14:00 | 44121.5833 | 0 | 8.2793 | 39.95
2020-10-17 14:30 | 44121.6042 | 0 | 9.2151 | 39.95
2020-10-17 15:00 | 44121.625 | 0 | 8.7788 | 39.95
2020-10-17 15:30 | 44121.6458 | 0 | 8.8338 | 39.95
2020-10-17 16:00 | 44121.6667 | 0 | 9.5577 | 39.95
2020-10-17 16:30 | 44121.6875 | 0 | 10.1686 | 39.95
2020-10-17 17:00 | 44121.7083 | 0 | 10.5041 | 39.95
2020-10-17 17:30 | 44121.7292 | 0 | 10.8196 | 39.95
2020-10-17 18:00 | 44121.75 | 0 | 11.2002 | 39.95
2020-10-17 18:30 | 44121.7708 | 0 | 11.5906 | 39.95
2020-10-17 19:00 | 44121.7917 | 0 | 11.3128 | 39.95
2020-10-17 19:30 | 44121.8125 | 0 | 10.9822 | 39.95
2020-10-17 20:00 | 44121.8333 | 0 | 10.7775 | 39.95
2020-10-17 20:30 | 44121.8542 | 0 | 10.3359 | 39.95
2020-10-17 21:00 | 44121.875 | 0 | 10.1219 | 39.95
2020-10-17 21:30 | 44121.8958 | 0 | 9.8597 | 39.95
2020-10-17 22:00 | 44121.9167 | 0 | 9.6341 | 39.95
2020-10-17 22:30 | 44121.9375 | 0 | 9.0574 | 39.95
2020-10-17 23:00 | 44121.9583 | 0 | 8.5334 | 39.95
2020-10-17 23:30 | 44121.9792 | 0 | 8.2124 | 39.95
2020-10-18 | 44122 | 0 | 7.8828 | 39.95
2020-10-18 00:30 | 44122.0208 | 0 | 7.565 | 39.95
2020-10-18 01:00 | 44122.0417 | 0 | 7.3193 | 39.95
2020-10-18 01:30 | 44122.0625 | 0 | 7.1537 | 39.95
2020-10-18 02:00 | 44122.0833 | 0 | 7.1409 | 39.95
2020-10-18 02:30 | 44122.1042 | 0 | 7.11 | 39.95
2020-10-18 03:00 | 44122.125 | 0 | 6.9846 | 39.95
2020-10-18 03:30 | 44122.1458 | 0 | 6.8726 | 39.95
2020-10-18 04:00 | 44122.1667 | 0 | 6.8283 | 39.95
2020-10-18 04:30 | 44122.1875 | 0 | 6.8506 | 39.95
2020-10-18 05:00 | 44122.2083 | 0 | 6.8785 | 39.95
2020-10-18 05:30 | 44122.2292 | 0 | 6.7778 | 39.95
2020-10-18 06:00 | 44122.25 | 0 | 6.6866 | 39.95
2020-10-18 06:30 | 44122.2708 | 0 | 6.56 | 39.95
2020-10-18 07:00 | 44122.2917 | 0 | 6.4025 | 39.95
2020-10-18 07:30 | 44122.3125 | 0 | 6.3758 | 39.95
2020-10-18 08:00 | 44122.3333 | 0 | 6.4431 | 39.95
2020-10-18 08:30 | 44122.3542 | 0 | 6.4373 | 39.95
2020-10-18 09:00 | 44122.375 | 0 | 6.3648 | 39.95
2020-10-18 09:30 | 44122.3958 | 0 | 6.3425 | 39.95
2020-10-18 10:00 | 44122.4167 | 0 | 6.3946 | 39.95
2020-10-18 10:30 | 44122.4375 | 0 | 6.3941 | 39.95
2020-10-18 11:00 | 44122.4583 | 0 | 6.5063 | 39.95
2020-10-18 11:30 | 44122.4792 | 0 | 6.4507 | 39.95
2020-10-18 12:00 | 44122.5 | 0 | 7.1122 | 39.95
2020-10-18 12:30 | 44122.5208 | 0 | 7.4046 | 39.95
2020-10-18 13:00 | 44122.5417 | 0 | 6.6533 | 39.95
2020-10-18 13:30 | 44122.5625 | 0 | 6.9867 | 39.95
2020-10-18 14:00 | 44122.5833 | 0 | 7.5852 | 39.95
2020-10-18 14:30 | 44122.6042 | 0 | 8.4689 | 39.95
2020-10-18 15:00 | 44122.625 | 0 | 8.5624 | 39.95
2020-10-18 15:30 | 44122.6458 | 0 | 9.191 | 39.95
2020-10-18 16:00 | 44122.6667 | 0 | 9.7822 | 39.95
2020-10-18 16:30 | 44122.6875 | 0 | 10.726 | 39.95
2020-10-18 17:00 | 44122.7083 | 0 | 11.0213 | 39.95
2020-10-18 17:30 | 44122.7292 | 0 | 11.5538 | 39.95
2020-10-18 18:00 | 44122.75 | 0 | 12.0635 | 39.95
2020-10-18 18:30 | 44122.7708 | 0 | 12.5956 | 39.95
2020-10-18 19:00 | 44122.7917 | 0 | 12.2227 | 39.95
2020-10-18 19:30 | 44122.8125 | 0 | 11.8049 | 39.95
2020-10-18 20:00 | 44122.8333 | 0 | 11.6405 | 39.95
2020-10-18 20:30 | 44122.8542 | 0 | 11.271 | 39.95
2020-10-18 21:00 | 44122.875 | 0 | 10.7695 | 39.95
2020-10-18 21:30 | 44122.8958 | 0 | 10.3343 | 39.95
2020-10-18 22:00 | 44122.9167 | 0 | 9.8727 | 39.95
2020-10-18 22:30 | 44122.9375 | 0 | 9.2186 | 39.95
2020-10-18 23:00 | 44122.9583 | 0 | 8.5788 | 39.95
2020-10-18 23:30 | 44122.9792 | 0 | 8.2811 | 39.95
2020-10-19 | 44123 | 0 | 7.9951 | 39.95
2020-10-19 00:30 | 44123.0208 | 0 | 7.7734 | 39.95
2020-10-19 01:00 | 44123.0417 | 0 | 7.4743 | 39.95
2020-10-19 01:30 | 44123.0625 | 0 | 7.4928 | 39.95
2020-10-19 02:00 | 44123.0833 | 0 | 7.5316 | 39.95
2020-10-19 02:30 | 44123.1042 | 0 | 7.4646 | 39.95
2020-10-19 03:00 | 44123.125 | 0 | 7.4872 | 39.95
2020-10-19 03:30 | 44123.1458 | 0 | 7.5708 | 39.95
2020-10-19 04:00 | 44123.1667 | 0 | 7.7703 | 39.95
2020-10-19 04:30 | 44123.1875 | 0 | 8.1252 | 39.95
2020-10-19 05:00 | 44123.2083 | 0 | 8.5669 | 39.95
2020-10-19 05:30 | 44123.2292 | 0 | 9.1031 | 39.95
2020-10-19 06:00 | 44123.25 | 0 | 9.4211 | 39.95
2020-10-19 06:30 | 44123.2708 | 0 | 9.6127 | 39.95
2020-10-19 07:00 | 44123.2917 | 0 | 10.4067 | 39.95
2020-10-19 07:30 | 44123.3125 | 0 | 10.1054 | 39.95
2020-10-19 08:00 | 44123.3333 | 0 | 9.9932 | 39.95
2020-10-19 08:30 | 44123.3542 | 0 | 9.6715 | 39.95
2020-10-19 09:00 | 44123.375 | 0 | 9.3907 | 39.95
2020-10-19 09:30 | 44123.3958 | 0 | 9.3985 | 39.95
2020-10-19 10:00 | 44123.4167 | 0 | 9.2535 | 39.95
2020-10-19 10:30 | 44123.4375 | 0 | 9.2328 | 39.95
2020-10-19 11:00 | 44123.4583 | 0 | 9.5775 | 39.95
2020-10-19 11:30 | 44123.4792 | 0 | 10.1633 | 39.95
2020-10-19 12:00 | 44123.5 | 0 | 10.0479 | 39.95
2020-10-19 12:30 | 44123.5208 | 0 | 10.2071 | 39.95
2020-10-19 13:00 | 44123.5417 | 0 | 11.1647 | 39.95
2020-10-19 13:30 | 44123.5625 | 0 | 11.4971 | 39.95
2020-10-19 14:00 | 44123.5833 | 0 | 12.5931 | 39.95
2020-10-19 14:30 | 44123.6042 | 0 | 13.5153 | 39.95
2020-10-19 15:00 | 44123.625 | 0 | 13.7951 | 39.95
2020-10-19 15:30 | 44123.6458 | 0 | 13.5242 | 39.95
2020-10-19 16:00 | 44123.6667 | 0 | 13.1907 | 39.95
2020-10-19 16:30 | 44123.6875 | 0 | 13.3014 | 39.95
2020-10-19 17:00 | 44123.7083 | 0 | 13.2319 | 39.95
2020-10-19 17:30 | 44123.7292 | 0 | 13.6198 | 39.95
2020-10-19 18:00 | 44123.75 | 0 | 13.9302 | 39.95
2020-10-19 18:30 | 44123.7708 | 0 | 14.2987 | 39.95
2020-10-19 19:00 | 44123.7917 | 0 | 14.0522 | 39.95
2020-10-19 19:30 | 44123.8125 | 0 | 13.57 | 39.95
2020-10-19 20:00 | 44123.8333 | 0 | 13.4795 | 39.95
2020-10-19 20:30 | 44123.8542 | 0 | 12.925 | 39.95
2020-10-19 21:00 | 44123.875 | 0 | 12.2746 | 39.95
2020-10-19 21:30 | 44123.8958 | 0 | 11.9368 | 39.95
2020-10-19 22:00 | 44123.9167 | 0 | 11.4684 | 39.95
2020-10-19 22:30 | 44123.9375 | 0 | 10.7257 | 39.95
2020-10-19 23:00 | 44123.9583 | 0 | 10.0892 | 39.95
2020-10-19 23:30 | 44123.9792 | 0 | 9.6398 | 39.95
2020-10-20 | 44124 | 0 | 9.0923 | 39.95
2020-10-20 00:30 | 44124.0208 | 0 | 8.5291 | 39.95
2020-10-20 01:00 | 44124.0417 | 0 | 8.3747 | 39.95
2020-10-20 01:30 | 44124.0625 | 0 | 8.222 | 39.95
2020-10-20 02:00 | 44124.0833 | 0 | 8.2351 | 39.95
2020-10-20 02:30 | 44124.1042 | 0 | 8.1718 | 39.95
2020-10-20 03:00 | 44124.125 | 0 | 7.9838 | 39.95
2020-10-20 03:30 | 44124.1458 | 0 | 8.0127 | 39.95
2020-10-20 04:00 | 44124.1667 | 0 | 8.0516 | 39.95
2020-10-20 04:30 | 44124.1875 | 0 | 8.4755 | 39.95
2020-10-20 05:00 | 44124.2083 | 0 | 8.8805 | 39.95
2020-10-20 05:30 | 44124.2292 | 0 | 9.466 | 39.95
2020-10-20 06:00 | 44124.25 | 0 | 9.8867 | 39.95
2020-10-20 06:30 | 44124.2708 | 0 | 10.3989 | 39.95
2020-10-20 07:00 | 44124.2917 | 0 | 10.7061 | 39.95
2020-10-20 07:30 | 44124.3125 | 0 | 10.7463 | 39.95
2020-10-20 08:00 | 44124.3333 | 0 | 11.0214 | 39.95
2020-10-20 08:30 | 44124.3542 | 0 | 9.977 | 39.95
2020-10-20 09:00 | 44124.375 | 0 | 10.4991 | 39.95
2020-10-20 09:30 | 44124.3958 | 0 | 10.634 | 39.95
2020-10-20 10:00 | 44124.4167 | 0 | 10.4704 | 39.95
2020-10-20 10:30 | 44124.4375 | 0 | 12.0529 | 39.95
2020-10-20 11:00 | 44124.4583 | 0 | 11.8497 | 39.95
2020-10-20 11:30 | 44124.4792 | 0 | 12.1019 | 39.95
2020-10-20 12:00 | 44124.5 | 0 | 11.2557 | 39.95
2020-10-20 12:30 | 44124.5208 | 0 | 9.9782 | 39.95
2020-10-20 13:00 | 44124.5417 | 0 | 11.0517 | 39.95
2020-10-20 13:30 | 44124.5625 | 0 | 10.8343 | 39.95
2020-10-20 14:00 | 44124.5833 | 0 | 11.0011 | 39.95
2020-10-20 14:30 | 44124.6042 | 0 | 11.5432 | 39.95
2020-10-20 15:00 | 44124.625 | 0 | 11.9213 | 39.95
2020-10-20 15:30 | 44124.6458 | 0 | 11.6169 | 39.95
2020-10-20 16:00 | 44124.6667 | 0 | 12.4415 | 39.95
2020-10-20 16:30 | 44124.6875 | 0 | 12.543 | 39.95
2020-10-20 17:00 | 44124.7083 | 0 | 12.7745 | 39.95
2020-10-20 17:30 | 44124.7292 | 0 | 13.3089 | 39.95
2020-10-20 18:00 | 44124.75 | 0 | 13.9085 | 39.95
2020-10-20 18:30 | 44124.7708 | 0 | 14.4272 | 39.95
2020-10-20 19:00 | 44124.7917 | 0 | 14.1134 | 39.95
2020-10-20 19:30 | 44124.8125 | 0 | 13.8353 | 39.95
2020-10-20 20:00 | 44124.8333 | 0 | 13.5689 | 39.95
2020-10-20 20:30 | 44124.8542 | 0 | 12.9824 | 39.95
2020-10-20 21:00 | 44124.875 | 0 | 12.3256 | 39.95
2020-10-20 21:30 | 44124.8958 | 0 | 11.8322 | 39.95
2020-10-20 22:00 | 44124.9167 | 0 | 11.1285 | 39.95
2020-10-20 22:30 | 44124.9375 | 0 | 10.603 | 39.95
2020-10-20 23:00 | 44124.9583 | 0 | 9.9196 | 39.95
2020-10-20 23:30 | 44124.9792 | 0 | 9.3091 | 39.95
2020-10-21 | 44125 | 0 | 8.5922 | 39.95
2020-10-21 00:30 | 44125.0208 | 0 | 8.4024 | 39.95
2020-10-21 01:00 | 44125.0417 | 0 | 8.0786 | 39.95
2020-10-21 01:30 | 44125.0625 | 0 | 8.0119 | 39.95
2020-10-21 02:00 | 44125.0833 | 0 | 8.1627 | 39.95
2020-10-21 02:30 | 44125.1042 | 0 | 8.0508 | 39.95
2020-10-21 03:00 | 44125.125 | 0 | 7.9614 | 39.95
2020-10-21 03:30 | 44125.1458 | 0 | 8.0566 | 39.95
2020-10-21 04:00 | 44125.1667 | 0 | 8.1517 | 39.95
2020-10-21 04:30 | 44125.1875 | 0 | 8.5054 | 39.95
2020-10-21 05:00 | 44125.2083 | 0 | 8.8106 | 39.95
2020-10-21 05:30 | 44125.2292 | 0 | 9.2385 | 39.95
2020-10-21 06:00 | 44125.25 | 0 | 9.636 | 39.95
2020-10-21 06:30 | 44125.2708 | 0 | 10.1017 | 39.95
2020-10-21 07:00 | 44125.2917 | 0 | 10.5744 | 39.95
2020-10-21 07:30 | 44125.3125 | 0 | 10.2121 | 39.95
2020-10-21 08:00 | 44125.3333 | 0 | 10.1168 | 39.95
2020-10-21 08:30 | 44125.3542 | 0 | 10.5114 | 39.95
2020-10-21 09:00 | 44125.375 | 0 | 10.4227 | 39.95
2020-10-21 09:30 | 44125.3958 | 0 | 10.4126 | 39.95
2020-10-21 10:00 | 44125.4167 | 0 | 9.6453 | 39.95
2020-10-21 10:30 | 44125.4375 | 0 | 10.0855 | 39.95
2020-10-21 11:00 | 44125.4583 | 0 | 10.0518 | 39.95
2020-10-21 11:30 | 44125.4792 | 0 | 9.743 | 39.95
2020-10-21 12:00 | 44125.5 | 0 | 10.8288 | 39.95
2020-10-21 12:30 | 44125.5208 | 0 | 9.9127 | 39.95
2020-10-21 13:00 | 44125.5417 | 0 | 12.3416 | 39.95
2020-10-21 13:30 | 44125.5625 | 0 | 12.2715 | 39.95
2020-10-21 14:00 | 44125.5833 | 0 | 12.6956 | 39.95
2020-10-21 14:30 | 44125.6042 | 0 | 13.2041 | 39.95
2020-10-21 15:00 | 44125.625 | 0 | 12.964 | 39.95
2020-10-21 15:30 | 44125.6458 | 0 | 13.2157 | 39.95
2020-10-21 16:00 | 44125.6667 | 0 | 12.9599 | 39.95
2020-10-21 16:30 | 44125.6875 | 0 | 13.0353 | 39.95
2020-10-21 17:00 | 44125.7083 | 0 | 12.9878 | 39.95
2020-10-21 17:30 | 44125.7292 | 0 | 13.3763 | 39.95
2020-10-21 18:00 | 44125.75 | 0 | 13.5823 | 39.95
2020-10-21 18:30 | 44125.7708 | 0 | 14.0918 | 39.95
2020-10-21 19:00 | 44125.7917 | 0 | 13.8309 | 39.95
2020-10-21 19:30 | 44125.8125 | 0 | 13.5353 | 39.95
2020-10-21 20:00 | 44125.8333 | 0 | 13.1599 | 39.95
2020-10-21 20:30 | 44125.8542 | 0 | 12.6975 | 39.95
2020-10-21 21:00 | 44125.875 | 0 | 12.1463 | 39.95
2020-10-21 21:30 | 44125.8958 | 0 | 11.6667 | 39.95
2020-10-21 22:00 | 44125.9167 | 0 | 11.0617 | 39.95
2020-10-21 22:30 | 44125.9375 | 0 | 10.2395 | 39.95
2020-10-21 23:00 | 44125.9583 | 0 | 9.6751 | 39.95
2020-10-21 23:30 | 44125.9792 | 0 | 9.3031 | 39.95
2020-10-22 | 44126 | 0 | 8.768 | 39.95
2020-10-22 00:30 | 44126.0208 | 0 | 8.4693 | 39.95
2020-10-22 01:00 | 44126.0417 | 0 | 8.078 | 39.95
2020-10-22 01:30 | 44126.0625 | 0 | 8.1327 | 39.95
2020-10-22 02:00 | 44126.0833 | 0 | 8.1461 | 39.95
2020-10-22 02:30 | 44126.1042 | 0 | 7.9761 | 39.95
2020-10-22 03:00 | 44126.125 | 0 | 7.9896 | 39.95
2020-10-22 03:30 | 44126.1458 | 0 | 7.9614 | 39.95
2020-10-22 04:00 | 44126.1667 | 0 | 8.1462 | 39.95
2020-10-22 04:30 | 44126.1875 | 0 | 8.6704 | 39.95
2020-10-22 05:00 | 44126.2083 | 0 | 9.1024 | 39.95
2020-10-22 05:30 | 44126.2292 | 0 | 9.5418 | 39.95
2020-10-22 06:00 | 44126.25 | 0 | 10.1741 | 39.95
2020-10-22 06:30 | 44126.2708 | 0 | 10.5856 | 39.95
2020-10-22 07:00 | 44126.2917 | 0 | 11.5149 | 39.95
2020-10-22 07:30 | 44126.3125 | 0 | 12.3819 | 39.95
2020-10-22 08:00 | 44126.3333 | 0 | 12.7844 | 39.95
2020-10-22 08:30 | 44126.3542 | 0 | 11.9841 | 39.95
2020-10-22 09:00 | 44126.375 | 0 | 11.6858 | 39.95
2020-10-22 09:30 | 44126.3958 | 0 | 11.5098 | 39.95
2020-10-22 10:00 | 44126.4167 | 0 | 11.1891 | 39.95
2020-10-22 10:30 | 44126.4375 | 0 | 12.2221 | 39.95
2020-10-22 11:00 | 44126.4583 | 0 | 12.6094 | 39.95
2020-10-22 11:30 | 44126.4792 | 0 | 12.8293 | 39.95
2020-10-22 12:00 | 44126.5 | 0 | 12.6249 | 39.95
2020-10-22 12:30 | 44126.5208 | 0 | 13.4184 | 39.95
2020-10-22 13:00 | 44126.5417 | 0 | 11.9706 | 39.95
2020-10-22 13:30 | 44126.5625 | 0 | 11.1345 | 39.95
2020-10-22 14:00 | 44126.5833 | 0 | 12.101 | 39.95
2020-10-22 14:30 | 44126.6042 | 0 | 12.9588 | 39.95
2020-10-22 15:00 | 44126.625 | 0 | 12.7161 | 39.95
2020-10-22 15:30 | 44126.6458 | 0 | 12.9408 | 39.95
2020-10-22 16:00 | 44126.6667 | 0 | 12.5955 | 39.95
2020-10-22 16:30 | 44126.6875 | 0 | 12.7022 | 39.95
2020-10-22 17:00 | 44126.7083 | 0 | 12.9289 | 39.95
2020-10-22 17:30 | 44126.7292 | 0 | 13.4623 | 39.95
2020-10-22 18:00 | 44126.75 | 0 | 13.8687 | 39.95
2020-10-22 18:30 | 44126.7708 | 0 | 14.2761 | 39.95
2020-10-22 19:00 | 44126.7917 | 0 | 14.0694 | 39.95
2020-10-22 19:30 | 44126.8125 | 0 | 13.6531 | 39.95
2020-10-22 20:00 | 44126.8333 | 0 | 13.5336 | 39.95
2020-10-22 20:30 | 44126.8542 | 0 | 13.0237 | 39.95
2020-10-22 21:00 | 44126.875 | 0 | 12.4603 | 39.95
2020-10-22 21:30 | 44126.8958 | 0 | 12.1153 | 39.95
2020-10-22 22:00 | 44126.9167 | 0 | 11.6479 | 39.95
2020-10-22 22:30 | 44126.9375 | 0 | 10.835 | 39.95
2020-10-22 23:00 | 44126.9583 | 0 | 10.0201 | 39.95
2020-10-22 23:30 | 44126.9792 | 0 | 9.3806 | 39.95
2020-10-23 | 44127 | 0 | 8.9716 | 39.95
2020-10-23 00:30 | 44127.0208 | 0 | 8.6005 | 39.95
2020-10-23 01:00 | 44127.0417 | 0 | 8.3689 | 39.95
2020-10-23 01:30 | 44127.0625 | 0 | 8.3524 | 39.95
2020-10-23 02:00 | 44127.0833 | 0 | 8.3042 | 39.95
2020-10-23 02:30 | 44127.1042 | 0 | 8.2852 | 39.95
2020-10-23 03:00 | 44127.125 | 0 | 8.2314 | 39.95
2020-10-23 03:30 | 44127.1458 | 0 | 8.2986 | 39.95
2020-10-23 04:00 | 44127.1667 | 0 | 8.442 | 39.95
2020-10-23 04:30 | 44127.1875 | 0 | 8.7902 | 39.95
2020-10-23 05:00 | 44127.2083 | 0 | 9.2549 | 39.95
2020-10-23 05:30 | 44127.2292 | 0 | 9.5287 | 39.95
2020-10-23 06:00 | 44127.25 | 0 | 10.4051 | 39.95
2020-10-23 06:30 | 44127.2708 | 0 | 11.2933 | 39.95
2020-10-23 07:00 | 44127.2917 | 0 | 12.1486 | 39.95
2020-10-23 07:30 | 44127.3125 | 0 | 12.2548 | 39.95
2020-10-23 08:00 | 44127.3333 | 0 | 12.4805 | 39.95
2020-10-23 08:30 | 44127.3542 | 0 | 12.161 | 39.95
2020-10-23 09:00 | 44127.375 | 0 | 12.7444 | 39.95
2020-10-23 09:30 | 44127.3958 | 0 | 12.4312 | 39.95
2020-10-23 10:00 | 44127.4167 | 0 | 12.6481 | 39.95
2020-10-23 10:30 | 44127.4375 | 0 | 11.4623 | 39.95
2020-10-23 11:00 | 44127.4583 | 0 | 12.7449 | 39.95
2020-10-23 11:30 | 44127.4792 | 0 | 12.8129 | 39.95
2020-10-23 12:00 | 44127.5 | 0 | 12.4139 | 39.95
2020-10-23 12:30 | 44127.5208 | 0 | 10.3284 | 39.95
2020-10-23 13:00 | 44127.5417 | 0 | 10.9556 | 39.95
2020-10-23 13:30 | 44127.5625 | 0 | 11.4013 | 39.95
2020-10-23 14:00 | 44127.5833 | 0 | 11.3655 | 39.95
2020-10-23 14:30 | 44127.6042 | 0 | 11.2872 | 39.95
2020-10-23 15:00 | 44127.625 | 0 | 12.0559 | 39.95
2020-10-23 15:30 | 44127.6458 | 0 | 12.178 | 39.95
2020-10-23 16:00 | 44127.6667 | 0 | 13.0012 | 39.95
2020-10-23 16:30 | 44127.6875 | 0 | 13.5349 | 39.95
2020-10-23 17:00 | 44127.7083 | 0 | 13.4459 | 39.95
2020-10-23 17:30 | 44127.7292 | 0 | 13.5918 | 39.95
2020-10-23 18:00 | 44127.75 | 0 | 13.8686 | 39.95
2020-10-23 18:30 | 44127.7708 | 0 | 14.0684 | 39.95
2020-10-23 19:00 | 44127.7917 | 0 | 13.655 | 39.95
2020-10-23 19:30 | 44127.8125 | 0 | 13.5077 | 39.95
2020-10-23 20:00 | 44127.8333 | 0 | 13.3842 | 39.95
2020-10-23 20:30 | 44127.8542 | 0 | 12.8352 | 39.95
2020-10-23 21:00 | 44127.875 | 0 | 12.3355 | 39.95
2020-10-23 21:30 | 44127.8958 | 0 | 12.2215 | 39.95
2020-10-23 22:00 | 44127.9167 | 0 | 11.7918 | 39.95
2020-10-23 22:30 | 44127.9375 | 0 | 10.8093 | 39.95
2020-10-23 23:00 | 44127.9583 | 0 | 10.3141 | 39.95
2020-10-23 23:30 | 44127.9792 | 0 | 9.9265 | 39.95
2020-10-24 | 44128 | 0 | 9.2204 | 39.95
2020-10-24 00:30 | 44128.0208 | 0 | 8.8342 | 39.95
2020-10-24 01:00 | 44128.0417 | 0 | 8.6241 | 39.95
2020-10-24 01:30 | 44128.0625 | 0 | 8.5589 | 39.95
2020-10-24 02:00 | 44128.0833 | 0 | 8.5482 | 39.95
2020-10-24 02:30 | 44128.1042 | 0 | 8.5029 | 39.95
2020-10-24 03:00 | 44128.125 | 0 | 8.4641 | 39.95
2020-10-24 03:30 | 44128.1458 | 0 | 8.4919 | 39.95
2020-10-24 04:00 | 44128.1667 | 0 | 8.5479 | 39.95
2020-10-24 04:30 | 44128.1875 | 0 | 8.4919 | 39.95
2020-10-24 05:00 | 44128.2083 | 0 | 8.5906 | 39.95
2020-10-24 05:30 | 44128.2292 | 0 | 8.7698 | 39.95
2020-10-24 06:00 | 44128.25 | 0 | 9.0451 | 39.95
2020-10-24 06:30 | 44128.2708 | 0 | 9.5029 | 39.95
2020-10-24 07:00 | 44128.2917 | 0 | 8.5447 | 39.95
2020-10-24 07:30 | 44128.3125 | 0 | 9.2896 | 39.95
2020-10-24 08:00 | 44128.3333 | 0 | 10.3398 | 39.95
2020-10-24 08:30 | 44128.3542 | 0 | 10.1342 | 39.95
2020-10-24 09:00 | 44128.375 | 0 | 10.7728 | 39.95
2020-10-24 09:30 | 44128.3958 | 0 | 10.9374 | 39.95
2020-10-24 10:00 | 44128.4167 | 0 | 11.1783 | 39.95
2020-10-24 10:30 | 44128.4375 | 0 | 11.2084 | 39.95
2020-10-24 11:00 | 44128.4583 | 0 | 10.8331 | 39.95
2020-10-24 11:30 | 44128.4792 | 0 | 11.2635 | 39.95
2020-10-24 12:00 | 44128.5 | 0 | 10.7558 | 39.95
2020-10-24 12:30 | 44128.5208 | 0 | 10.5608 | 39.95
2020-10-24 13:00 | 44128.5417 | 0 | 11.5559 | 39.95
2020-10-24 13:30 | 44128.5625 | 0 | 11.8857 | 39.95
2020-10-24 14:00 | 44128.5833 | 0 | 11.9109 | 39.95
2020-10-24 14:30 | 44128.6042 | 0 | 12.2606 | 39.95
2020-10-24 15:00 | 44128.625 | 0 | 11.8824 | 39.95
2020-10-24 15:30 | 44128.6458 | 0 | 11.6344 | 39.95
2020-10-24 16:00 | 44128.6667 | 0 | 11.669 | 39.95
2020-10-24 16:30 | 44128.6875 | 0 | 11.7304 | 39.95
2020-10-24 17:00 | 44128.7083 | 0 | 11.6797 | 39.95
2020-10-24 17:30 | 44128.7292 | 0 | 11.7903 | 39.95
2020-10-24 18:00 | 44128.75 | 0 | 11.9273 | 39.95
2020-10-24 18:30 | 44128.7708 | 0 | 12.0202 | 39.95
2020-10-24 19:00 | 44128.7917 | 0 | 11.5571 | 39.95
2020-10-24 19:30 | 44128.8125 | 0 | 11.166 | 39.95
2020-10-24 20:00 | 44128.8333 | 0 | 11.0935 | 39.95
2020-10-24 20:30 | 44128.8542 | 0 | 10.6985 | 39.95
2020-10-24 21:00 | 44128.875 | 0 | 10.217 | 39.95
2020-10-24 21:30 | 44128.8958 | 0 | 9.9995 | 39.95
2020-10-24 22:00 | 44128.9167 | 0 | 9.8856 | 39.95
2020-10-24 22:30 | 44128.9375 | 0 | 9.1746 | 39.95
2020-10-24 23:00 | 44128.9583 | 0 | 8.8994 | 39.95
2020-10-24 23:30 | 44128.9792 | 0 | 8.569 | 39.95
2020-10-25 | 44129 | 0 | 8.1871 | 39.95
2020-10-25 00:30 | 44129.0208 | 0 | 7.8721 | 39.95
2020-10-25 01:00 | 44129.0417 | 0 | 7.6188 | 39.95
2020-10-25 01:30 | 44129.0625 | 0 | 7.3336 | 39.95
2020-10-25 02:00 | 44129.0833 | 0 | 7.4034 | 39.95
2020-10-25 02:30 | 44129.1042 | 0 | 7.2579 | 39.95
2020-10-25 03:00 | 44129.125 | 0 | 7.206 | 39.95
2020-10-25 03:30 | 44129.1458 | 0 | 7.1668 | 39.95
2020-10-25 04:00 | 44129.1667 | 0 | 7.0905 | 39.95
2020-10-25 04:30 | 44129.1875 | 0 | 7.0908 | 39.95
2020-10-25 05:00 | 44129.2083 | 0 | 7.0458 | 39.95
2020-10-25 05:30 | 44129.2292 | 0 | 6.9568 | 39.95
2020-10-25 06:00 | 44129.25 | 0 | 6.758 | 39.95
2020-10-25 06:30 | 44129.2708 | 0 | 6.7658 | 39.95
2020-10-25 07:00 | 44129.2917 | 0 | 7.1557 | 39.95
2020-10-25 07:30 | 44129.3125 | 0 | 8.6558 | 39.95
2020-10-25 08:00 | 44129.3333 | 0 | 8.1523 | 39.95
2020-10-25 08:30 | 44129.3542 | 0 | 7.111 | 39.95
2020-10-25 09:00 | 44129.375 | 0 | 7.8464 | 39.95
2020-10-25 09:30 | 44129.3958 | 0 | 9.0206 | 39.95
2020-10-25 10:00 | 44129.4167 | 0 | 8.7974 | 39.95
2020-10-25 10:30 | 44129.4375 | 0 | 9.6501 | 39.95
2020-10-25 11:00 | 44129.4583 | 0 | 8.4209 | 39.95
2020-10-25 11:30 | 44129.4792 | 0 | 9.9895 | 39.95
2020-10-25 12:00 | 44129.5 | 0 | 8.5787 | 39.95
2020-10-25 12:30 | 44129.5208 | 0 | 9.9709 | 39.95
2020-10-25 13:00 | 44129.5417 | 0 | 10.1841 | 39.95
2020-10-25 13:30 | 44129.5625 | 0 | 12.0504 | 39.95
2020-10-25 14:00 | 44129.5833 | 0 | 12.3425 | 39.95
2020-10-25 14:30 | 44129.6042 | 0 | 11.4613 | 39.95
2020-10-25 15:00 | 44129.625 | 0 | 8.9346 | 39.95
2020-10-25 15:30 | 44129.6458 | 0 | 9.5258 | 39.95
2020-10-25 16:00 | 44129.6667 | 0 | 10.6064 | 39.95
2020-10-25 16:30 | 44129.6875 | 0 | 10.6697 | 39.95
2020-10-25 17:00 | 44129.7083 | 0 | 11.2094 | 39.95
2020-10-25 17:30 | 44129.7292 | 0 | 11.6517 | 39.95
2020-10-25 18:00 | 44129.75 | 0 | 12.3318 | 39.95
2020-10-25 18:30 | 44129.7708 | 0 | 12.9326 | 39.95
2020-10-25 19:00 | 44129.7917 | 0 | 12.7089 | 39.95
2020-10-25 19:30 | 44129.8125 | 0 | 12.4095 | 39.95
2020-10-25 20:00 | 44129.8333 | 0 | 12.0427 | 39.95
2020-10-25 20:30 | 44129.8542 | 0 | 11.5959 | 39.95
2020-10-25 21:00 | 44129.875 | 0 | 11.045 | 39.95
2020-10-25 21:30 | 44129.8958 | 0 | 10.7027 | 39.95
2020-10-25 22:00 | 44129.9167 | 0 | 10.2466 | 39.95
2020-10-25 22:30 | 44129.9375 | 0 | 9.6844 | 39.95
2020-10-25 23:00 | 44129.9583 | 0 | 8.9831 | 39.95
2020-10-25 23:30 | 44129.9792 | 0 | 8.8269 | 39.95
2020-10-26 | 44130 | 0 | 8.5151 | 39.95
2020-10-26 00:30 | 44130.0208 | 0 | 8.2312 | 39.95
2020-10-26 01:00 | 44130.0417 | 0 | 7.9391 | 39.95
2020-10-26 01:30 | 44130.0625 | 0 | 7.8498 | 39.95
2020-10-26 02:00 | 44130.0833 | 0 | 7.8501 | 39.95
2020-10-26 02:30 | 44130.1042 | 0 | 7.8944 | 39.95
2020-10-26 03:00 | 44130.125 | 0 | 7.7285 | 39.95
2020-10-26 03:30 | 44130.1458 | 0 | 7.9584 | 39.95
2020-10-26 04:00 | 44130.1667 | 0 | 8.2904 | 39.95
2020-10-26 04:30 | 44130.1875 | 0 | 8.7372 | 39.95
2020-10-26 05:00 | 44130.2083 | 0 | 9.1233 | 39.95
2020-10-26 05:30 | 44130.2292 | 0 | 9.5975 | 39.95
2020-10-26 06:00 | 44130.25 | 0 | 10.3511 | 39.95
2020-10-26 06:30 | 44130.2708 | 0 | 11.2741 | 39.95
2020-10-26 07:00 | 44130.2917 | 0 | 11.3795 | 39.95
2020-10-26 07:30 | 44130.3125 | 0 | 11.7863 | 39.95
2020-10-26 08:00 | 44130.3333 | 0 | 12.9126 | 39.95
2020-10-26 08:30 | 44130.3542 | 0 | 13.0505 | 39.95
2020-10-26 09:00 | 44130.375 | 0 | 13.5971 | 39.95
2020-10-26 09:30 | 44130.3958 | 0 | 12.2713 | 39.95
2020-10-26 10:00 | 44130.4167 | 0 | 10.744 | 39.95
2020-10-26 10:30 | 44130.4375 | 0 | 10.8572 | 39.95
2020-10-26 11:00 | 44130.4583 | 0 | 11.0492 | 39.95
2020-10-26 11:30 | 44130.4792 | 0 | 11.5828 | 39.95
2020-10-26 12:00 | 44130.5 | 0 | 11.8123 | 39.95
2020-10-26 12:30 | 44130.5208 | 0 | 12.0094 | 39.95
2020-10-26 13:00 | 44130.5417 | 0 | 12.7679 | 39.95
2020-10-26 13:30 | 44130.5625 | 0 | 12.7457 | 39.95
2020-10-26 14:00 | 44130.5833 | 0 | 15.3128 | 39.95
2020-10-26 14:30 | 44130.6042 | 0 | 14.1521 | 39.95
2020-10-26 15:00 | 44130.625 | 0 | 13.5074 | 39.95
2020-10-26 15:30 | 44130.6458 | 0 | 13.6915 | 39.95
2020-10-26 16:00 | 44130.6667 | 0 | 14.3984 | 39.95
2020-10-26 16:30 | 44130.6875 | 0 | 14.6337 | 39.95
2020-10-26 17:00 | 44130.7083 | 0 | 14.6389 | 39.95
2020-10-26 17:30 | 44130.7292 | 0 | 15.0741 | 39.95
2020-10-26 18:00 | 44130.75 | 0 | 15.6329 | 39.95
2020-10-26 18:30 | 44130.7708 | 0 | 16.1463 | 39.95
2020-10-26 19:00 | 44130.7917 | 0 | 15.7212 | 39.95
2020-10-26 19:30 | 44130.8125 | 0 | 15.2306 | 39.95
2020-10-26 20:00 | 44130.8333 | 0 | 14.8296 | 39.95
2020-10-26 20:30 | 44130.8542 | 0 | 14.1197 | 39.95
2020-10-26 21:00 | 44130.875 | 0 | 13.4745 | 39.95
2020-10-26 21:30 | 44130.8958 | 0 | 13.0607 | 39.95
2020-10-26 22:00 | 44130.9167 | 0 | 12.5211 | 39.95
2020-10-26 22:30 | 44130.9375 | 0 | 11.7051 | 39.95
2020-10-26 23:00 | 44130.9583 | 0 | 11.004 | 39.95
2020-10-26 23:30 | 44130.9792 | 0 | 10.4131 | 39.95
2020-10-27 | 44131 | 0 | 9.8405 | 39.95
2020-10-27 00:30 | 44131.0208 | 0 | 9.31 | 39.95
2020-10-27 01:00 | 44131.0417 | 0 | 9.0169 | 39.95
2020-10-27 01:30 | 44131.0625 | 0 | 8.9719 | 39.95
2020-10-27 02:00 | 44131.0833 | 0 | 8.795 | 39.95
2020-10-27 02:30 | 44131.1042 | 0 | 8.6204 | 39.95
2020-10-27 03:00 | 44131.125 | 0 | 8.6372 | 39.95
2020-10-27 03:30 | 44131.1458 | 0 | 8.8086 | 39.95
2020-10-27 04:00 | 44131.1667 | 0 | 8.989 | 39.95
2020-10-27 04:30 | 44131.1875 | 0 | 9.3281 | 39.95
2020-10-27 05:00 | 44131.2083 | 0 | 9.7439 | 39.95
2020-10-27 05:30 | 44131.2292 | 0 | 10.1902 | 39.95
2020-10-27 06:00 | 44131.25 | 0 | 10.5773 | 39.95
2020-10-27 06:30 | 44131.2708 | 0 | 12.0354 | 39.95
2020-10-27 07:00 | 44131.2917 | 0 | 12.4786 | 39.95
2020-10-27 07:30 | 44131.3125 | 0 | 13.1143 | 39.95
2020-10-27 08:00 | 44131.3333 | 0 | 12.2498 | 39.95
2020-10-27 08:30 | 44131.3542 | 0 | 12.227 | 39.95
2020-10-27 09:00 | 44131.375 | 0 | 12.9848 | 39.95
2020-10-27 09:30 | 44131.3958 | 0 | 13.0417 | 39.95
2020-10-27 10:00 | 44131.4167 | 0 | 12.8319 | 39.95
2020-10-27 10:30 | 44131.4375 | 0 | 12.9571 | 39.95
2020-10-27 11:00 | 44131.4583 | 0 | 14.4153 | 39.95
2020-10-27 11:30 | 44131.4792 | 0 | 14.3825 | 39.95
2020-10-27 12:00 | 44131.5 | 0 | 13.1679 | 39.95
2020-10-27 12:30 | 44131.5208 | 0 | 12.9594 | 39.95
2020-10-27 13:00 | 44131.5417 | 0 | 13.4856 | 39.95
2020-10-27 13:30 | 44131.5625 | 0 | 13.7882 | 39.95
2020-10-27 14:00 | 44131.5833 | 0 | 14.0816 | 39.95
2020-10-27 14:30 | 44131.6042 | 0 | 14.2963 | 39.95
2020-10-27 15:00 | 44131.625 | 0 | 14.1757 | 39.95
2020-10-27 15:30 | 44131.6458 | 0 | 14.2482 | 39.95
2020-10-27 16:00 | 44131.6667 | 0 | 14.4329 | 39.95
2020-10-27 16:30 | 44131.6875 | 0 | 14.7544 | 39.95
2020-10-27 17:00 | 44131.7083 | 0 | 14.5048 | 39.95
2020-10-27 17:30 | 44131.7292 | 0 | 14.675 | 39.95
2020-10-27 18:00 | 44131.75 | 0 | 14.7955 | 39.95
2020-10-27 18:30 | 44131.7708 | 0 | 14.8771 | 39.95
2020-10-27 19:00 | 44131.7917 | 0 | 14.4825 | 39.95
2020-10-27 19:30 | 44131.8125 | 0 | 13.9985 | 39.95
2020-10-27 20:00 | 44131.8333 | 0 | 13.8081 | 39.95
2020-10-27 20:30 | 44131.8542 | 0 | 13.1956 | 39.95
2020-10-27 21:00 | 44131.875 | 0 | 12.5447 | 39.95
2020-10-27 21:30 | 44131.8958 | 0 | 12.0001 | 39.95
2020-10-27 22:00 | 44131.9167 | 0 | 11.6285 | 39.95
2020-10-27 22:30 | 44131.9375 | 0 | 10.6834 | 39.95
2020-10-27 23:00 | 44131.9583 | 0 | 10.1432 | 39.95
2020-10-27 23:30 | 44131.9792 | 0 | 9.7412 | 39.95
2020-10-28 | 44132 | 0 | 9.1132 | 39.95
2020-10-28 00:30 | 44132.0208 | 0 | 8.702 | 39.95
2020-10-28 01:00 | 44132.0417 | 0 | 8.5029 | 39.95
2020-10-28 01:30 | 44132.0625 | 0 | 8.4809 | 39.95
2020-10-28 02:00 | 44132.0833 | 0 | 8.4864 | 39.95
2020-10-28 02:30 | 44132.1042 | 0 | 8.3207 | 39.95
2020-10-28 03:00 | 44132.125 | 0 | 8.3075 | 39.95
2020-10-28 03:30 | 44132.1458 | 0 | 8.6452 | 39.95
2020-10-28 04:00 | 44132.1667 | 0 | 9.0135 | 39.95
2020-10-28 04:30 | 44132.1875 | 0 | 9.3078 | 39.95
2020-10-28 05:00 | 44132.2083 | 0 | 9.734 | 39.95
2020-10-28 05:30 | 44132.2292 | 0 | 10.194 | 39.95
2020-10-28 06:00 | 44132.25 | 0 | 10.8354 | 39.95
2020-10-28 06:30 | 44132.2708 | 0 | 11.0153 | 39.95
2020-10-28 07:00 | 44132.2917 | 0 | 11.5482 | 39.95
2020-10-28 07:30 | 44132.3125 | 0 | 11.4733 | 39.95
2020-10-28 08:00 | 44132.3333 | 0 | 11.3822 | 39.95
2020-10-28 08:30 | 44132.3542 | 0 | 12.0514 | 39.95
2020-10-28 09:00 | 44132.375 | 0 | 13.6816 | 39.95
2020-10-28 09:30 | 44132.3958 | 0 | 12.7036 | 39.95
2020-10-28 10:00 | 44132.4167 | 0 | 12.141 | 39.95
2020-10-28 10:30 | 44132.4375 | 0 | 12.365 | 39.95
2020-10-28 11:00 | 44132.4583 | 0 | 12.6632 | 39.95
2020-10-28 11:30 | 44132.4792 | 0 | 11.7018 | 39.95
2020-10-28 12:00 | 44132.5 | 0 | 12.4564 | 39.95
2020-10-28 12:30 | 44132.5208 | 0 | 12.6741 | 39.95
2020-10-28 13:00 | 44132.5417 | 0 | 11.692 | 39.95
2020-10-28 13:30 | 44132.5625 | 0 | 13.7932 | 39.95
2020-10-28 14:00 | 44132.5833 | 0 | 15.7282 | 39.95
2020-10-28 14:30 | 44132.6042 | 0 | 15.6623 | 39.95
2020-10-28 15:00 | 44132.625 | 0 | 15.2493 | 39.95
2020-10-28 15:30 | 44132.6458 | 0 | 13.2978 | 39.95
2020-10-28 16:00 | 44132.6667 | 0 | 13.4403 | 39.95
2020-10-28 16:30 | 44132.6875 | 0 | 14.1704 | 39.95
2020-10-28 17:00 | 44132.7083 | 0 | 14.0013 | 39.95
2020-10-28 17:30 | 44132.7292 | 0 | 14.4253 | 39.95
2020-10-28 18:00 | 44132.75 | 0 | 14.7919 | 39.95
2020-10-28 18:30 | 44132.7708 | 0 | 15.3579 | 39.95
2020-10-28 19:00 | 44132.7917 | 0 | 15.0575 | 39.95
2020-10-28 19:30 | 44132.8125 | 0 | 14.6513 | 39.95
2020-10-28 20:00 | 44132.8333 | 0 | 14.3745 | 39.95
2020-10-28 20:30 | 44132.8542 | 0 | 13.7753 | 39.95
2020-10-28 21:00 | 44132.875 | 0 | 13.1523 | 39.95
2020-10-28 21:30 | 44132.8958 | 0 | 12.6565 | 39.95
2020-10-28 22:00 | 44132.9167 | 0 | 11.98 | 39.95
2020-10-28 22:30 | 44132.9375 | 0 | 11.0966 | 39.95
2020-10-28 23:00 | 44132.9583 | 0 | 10.4348 | 39.95
2020-10-28 23:30 | 44132.9792 | 0 | 9.9188 | 39.95
2020-10-29 | 44133 | 0 | 9.3404 | 39.95
2020-10-29 00:30 | 44133.0208 | 0 | 8.8961 | 39.95
2020-10-29 01:00 | 44133.0417 | 0 | 8.6204 | 39.95
2020-10-29 01:30 | 44133.0625 | 0 | 8.5699 | 39.95
2020-10-29 02:00 | 44133.0833 | 0 | 8.5366 | 39.95
2020-10-29 02:30 | 44133.1042 | 0 | 8.4919 | 39.95
2020-10-29 03:00 | 44133.125 | 0 | 8.5032 | 39.95
2020-10-29 03:30 | 44133.1458 | 0 | 8.5479 | 39.95
2020-10-29 04:00 | 44133.1667 | 0 | 8.783 | 39.95
2020-10-29 04:30 | 44133.1875 | 0 | 9.2692 | 39.95
2020-10-29 05:00 | 44133.2083 | 0 | 9.6259 | 39.95
2020-10-29 05:30 | 44133.2292 | 0 | 10.1539 | 39.95
2020-10-29 06:00 | 44133.25 | 0 | 10.6288 | 39.95
2020-10-29 06:30 | 44133.2708 | 0 | 10.9935 | 39.95
2020-10-29 07:00 | 44133.2917 | 0 | 11.3647 | 39.95
2020-10-29 07:30 | 44133.3125 | 0 | 11.4156 | 39.95
2020-10-29 08:00 | 44133.3333 | 0 | 11.3637 | 39.95
2020-10-29 08:30 | 44133.3542 | 0 | 11.0106 | 39.95
2020-10-29 09:00 | 44133.375 | 0 | 10.9877 | 39.95
2020-10-29 09:30 | 44133.3958 | 0 | 11.0433 | 39.95
2020-10-29 10:00 | 44133.4167 | 0 | 11.4702 | 39.95
2020-10-29 10:30 | 44133.4375 | 0 | 11.6047 | 39.95
2020-10-29 11:00 | 44133.4583 | 0 | 11.8753 | 39.95
2020-10-29 11:30 | 44133.4792 | 0 | 12.3625 | 39.95
2020-10-29 12:00 | 44133.5 | 0 | 11.6743 | 39.95
2020-10-29 12:30 | 44133.5208 | 0 | 12.3626 | 39.95
2020-10-29 13:00 | 44133.5417 | 0 | 12.378 | 39.95
2020-10-29 13:30 | 44133.5625 | 0 | 12.9839 | 39.95
2020-10-29 14:00 | 44133.5833 | 0 | 13.139 | 39.95
2020-10-29 14:30 | 44133.6042 | 0 | 12.7247 | 39.95
2020-10-29 15:00 | 44133.625 | 0 | 13.1057 | 39.95
2020-10-29 15:30 | 44133.6458 | 0 | 13.8021 | 39.95
2020-10-29 16:00 | 44133.6667 | 0 | 14.5114 | 39.95
2020-10-29 16:30 | 44133.6875 | 0 | 15.2415 | 39.95
2020-10-29 17:00 | 44133.7083 | 0 | 15.1636 | 39.95
2020-10-29 17:30 | 44133.7292 | 0 | 15.2868 | 39.95
2020-10-29 18:00 | 44133.75 | 0 | 15.5193 | 39.95
2020-10-29 18:30 | 44133.7708 | 0 | 16.2603 | 39.95
2020-10-29 19:00 | 44133.7917 | 0 | 16.1965 | 39.95
2020-10-29 19:30 | 44133.8125 | 0 | 15.7497 | 39.95
2020-10-29 20:00 | 44133.8333 | 0 | 15.3367 | 39.95
2020-10-29 20:30 | 44133.8542 | 0 | 14.7739 | 39.95
2020-10-29 21:00 | 44133.875 | 0 | 14.0121 | 39.95
2020-10-29 21:30 | 44133.8958 | 0 | 13.301 | 39.95
2020-10-29 22:00 | 44133.9167 | 0 | 12.6927 | 39.95
2020-10-29 22:30 | 44133.9375 | 0 | 11.8948 | 39.95
2020-10-29 23:00 | 44133.9583 | 0 | 11.0302 | 39.95
2020-10-29 23:30 | 44133.9792 | 0 | 10.4437 | 39.95
2020-10-30 | 44134 | 0 | 9.7493 | 39.95
2020-10-30 00:30 | 44134.0208 | 0 | 9.3012 | 39.95
2020-10-30 01:00 | 44134.0417 | 0 | 9.3035 | 39.95
2020-10-30 01:30 | 44134.0625 | 0 | 9.1523 | 39.95
2020-10-30 02:00 | 44134.0833 | 0 | 9.1007 | 39.95
2020-10-30 02:30 | 44134.1042 | 0 | 9.1007 | 39.95
2020-10-30 03:00 | 44134.125 | 0 | 9.1655 | 39.95
2020-10-30 03:30 | 44134.1458 | 0 | 8.9832 | 39.95
2020-10-30 04:00 | 44134.1667 | 0 | 9.0784 | 39.95
2020-10-30 04:30 | 44134.1875 | 0 | 9.4287 | 39.95
2020-10-30 05:00 | 44134.2083 | 0 | 9.8732 | 39.95
2020-10-30 05:30 | 44134.2292 | 0 | 10.0376 | 39.95
2020-10-30 06:00 | 44134.25 | 0 | 10.6392 | 39.95
2020-10-30 06:30 | 44134.2708 | 0 | 10.9207 | 39.95
2020-10-30 07:00 | 44134.2917 | 0 | 11.2485 | 39.95
2020-10-30 07:30 | 44134.3125 | 0 | 11.298 | 39.95
2020-10-30 08:00 | 44134.3333 | 0 | 11.3913 | 39.95
2020-10-30 08:30 | 44134.3542 | 0 | 11.3565 | 39.95
2020-10-30 09:00 | 44134.375 | 0 | 11.479 | 39.95
2020-10-30 09:30 | 44134.3958 | 0 | 11.5181 | 39.95
2020-10-30 10:00 | 44134.4167 | 0 | 11.7026 | 39.95
2020-10-30 10:30 | 44134.4375 | 0 | 11.6632 | 39.95
2020-10-30 11:00 | 44134.4583 | 0 | 11.691 | 39.95
2020-10-30 11:30 | 44134.4792 | 0 | 11.5738 | 39.95
2020-10-30 12:00 | 44134.5 | 0 | 11.6075 | 39.95
2020-10-30 12:30 | 44134.5208 | 0 | 11.5347 | 39.95
2020-10-30 13:00 | 44134.5417 | 0 | 11.7622 | 39.95
2020-10-30 13:30 | 44134.5625 | 0 | 11.9276 | 39.95
2020-10-30 14:00 | 44134.5833 | 0 | 12.3196 | 39.95
2020-10-30 14:30 | 44134.6042 | 0 | 12.7572 | 39.95
2020-10-30 15:00 | 44134.625 | 0 | 13.0557 | 39.95
2020-10-30 15:30 | 44134.6458 | 0 | 13.7831 | 39.95
2020-10-30 16:00 | 44134.6667 | 0 | 14.2693 | 39.95
2020-10-30 16:30 | 44134.6875 | 0 | 14.8641 | 39.95
2020-10-30 17:00 | 44134.7083 | 0 | 15.0148 | 39.95
2020-10-30 17:30 | 44134.7292 | 0 | 14.9237 | 39.95
2020-10-30 18:00 | 44134.75 | 0 | 15.0155 | 39.95
2020-10-30 18:30 | 44134.7708 | 0 | 15.7827 | 39.95
2020-10-30 19:00 | 44134.7917 | 0 | 15.7064 | 39.95
2020-10-30 19:30 | 44134.8125 | 0 | 15.4751 | 39.95
2020-10-30 20:00 | 44134.8333 | 0 | 15.2954 | 39.95
2020-10-30 20:30 | 44134.8542 | 0 | 14.94 | 39.95
2020-10-30 21:00 | 44134.875 | 0 | 14.3409 | 39.95
2020-10-30 21:30 | 44134.8958 | 0 | 14.013 | 39.95
2020-10-30 22:00 | 44134.9167 | 0 | 13.5757 | 39.95
2020-10-30 22:30 | 44134.9375 | 0 | 12.7995 | 39.95
2020-10-30 23:00 | 44134.9583 | 0 | 12.1316 | 39.95
2020-10-30 23:30 | 44134.9792 | 0 | 11.4603 | 39.95
2020-10-31 | 44135 | 0 | 10.6554 | 39.95
2020-10-31 00:30 | 44135.0208 | 0 | 10.1054 | 39.95
2020-10-31 01:00 | 44135.0417 | 0 | 10.016 | 39.95
2020-10-31 01:30 | 44135.0625 | 0 | 9.7945 | 39.95
2020-10-31 02:00 | 44135.0833 | 0 | 9.7074 | 39.95
2020-10-31 02:30 | 44135.1042 | 0 | 9.5862 | 39.95
2020-10-31 03:00 | 44135.125 | 0 | 9.5082 | 39.95
2020-10-31 03:30 | 44135.1458 | 0 | 9.5471 | 39.95
2020-10-31 04:00 | 44135.1667 | 0 | 9.4412 | 39.95
2020-10-31 04:30 | 44135.1875 | 0 | 9.6312 | 39.95
2020-10-31 05:00 | 44135.2083 | 0 | 9.5804 | 39.95
2020-10-31 05:30 | 44135.2292 | 0 | 9.3684 | 39.95
2020-10-31 06:00 | 44135.25 | 0 | 9.4862 | 39.95
2020-10-31 06:30 | 44135.2708 | 0 | 9.8821 | 39.95
2020-10-31 07:00 | 44135.2917 | 0 | 9.7034 | 39.95
2020-10-31 07:30 | 44135.3125 | 0 | 10.2528 | 39.95
2020-10-31 08:00 | 44135.3333 | 0 | 10.6907 | 39.95
2020-10-31 08:30 | 44135.3542 | 0 | 10.8505 | 39.95
2020-10-31 09:00 | 44135.375 | 0 | 10.3797 | 39.95
2020-10-31 09:30 | 44135.3958 | 0 | 11.3087 | 39.95
2020-10-31 10:00 | 44135.4167 | 0 | 10.6293 | 39.95
2020-10-31 10:30 | 44135.4375 | 0 | 11.065 | 39.95
2020-10-31 11:00 | 44135.4583 | 0 | 10.41 | 39.95
2020-10-31 11:30 | 44135.4792 | 0 | 10.31 | 39.95
2020-10-31 12:00 | 44135.5 | 0 | 10.2659 | 39.95
2020-10-31 12:30 | 44135.5208 | 0 | 12.8816 | 39.95
2020-10-31 13:00 | 44135.5417 | 0 | 11.6786 | 39.95
2020-10-31 13:30 | 44135.5625 | 0 | 12.9982 | 39.95
2020-10-31 14:00 | 44135.5833 | 0 | 14.0411 | 39.95
2020-10-31 14:30 | 44135.6042 | 0 | 14.7016 | 39.95
2020-10-31 15:00 | 44135.625 | 0 | 14.4729 | 39.95
2020-10-31 15:30 | 44135.6458 | 0 | 13.6855 | 39.95
2020-10-31 16:00 | 44135.6667 | 0 | 13.1014 | 39.95
2020-10-31 16:30 | 44135.6875 | 0 | 12.5544 | 39.95
2020-10-31 17:00 | 44135.7083 | 0 | 12.0899 | 39.95
2020-10-31 17:30 | 44135.7292 | 0 | 12.3149 | 39.95
2020-10-31 18:00 | 44135.75 | 0 | 12.5135 | 39.95
2020-10-31 18:30 | 44135.7708 | 0 | 12.994 | 39.95
2020-10-31 19:00 | 44135.7917 | 0 | 12.8222 | 39.95
2020-10-31 19:30 | 44135.8125 | 0 | 12.4244 | 39.95
2020-10-31 20:00 | 44135.8333 | 0 | 12.4215 | 39.95
2020-10-31 20:30 | 44135.8542 | 0 | 11.9599 | 39.95
2020-10-31 21:00 | 44135.875 | 0 | 11.479 | 39.95
2020-10-31 21:30 | 44135.8958 | 0 | 11.3373 | 39.95
2020-10-31 22:00 | 44135.9167 | 0 | 10.8491 | 39.95
2020-10-31 22:30 | 44135.9375 | 0 | 10.1606 | 39.95
2020-10-31 23:00 | 44135.9583 | 0 | 9.733 | 39.95
2020-10-31 23:30 | 44135.9792 | 0 | 9.2269 | 39.95
2020-11-01 | 44136 | 0 | 8.7805 | 37.78
2020-11-01 00:30 | 44136.0208 | 0 | 8.447 | 37.78
2020-11-01 01:00 | 44136.0417 | 0 | 8.2482 | 37.78
2020-11-01 01:30 | 44136.0625 | 0 | 8.1325 | 37.78
2020-11-01 02:00 | 44136.0833 | 0 | 8.1889 | 37.78
2020-11-01 02:30 | 44136.1042 | 0 | 8.0016 | 37.78
2020-11-01 03:00 | 44136.125 | 0 | 7.7993 | 37.78
2020-11-01 03:30 | 44136.1458 | 0 | 7.7382 | 37.78
2020-11-01 04:00 | 44136.1667 | 0 | 7.7028 | 37.78
2020-11-01 04:30 | 44136.1875 | 0 | 7.6695 | 37.78
2020-11-01 05:00 | 44136.2083 | 0 | 7.5986 | 37.78
2020-11-01 05:30 | 44136.2292 | 0 | 7.3847 | 37.78
2020-11-01 06:00 | 44136.25 | 0 | 7.2117 | 37.78
2020-11-01 06:30 | 44136.2708 | 0 | 7.0382 | 37.78
2020-11-01 07:00 | 44136.2917 | 0 | 7.0461 | 37.78
2020-11-01 07:30 | 44136.3125 | 0 | 6.9843 | 37.78
2020-11-01 08:00 | 44136.3333 | 0 | 6.9901 | 37.78
2020-11-01 08:30 | 44136.3542 | 0 | 6.8442 | 37.78
2020-11-01 09:00 | 44136.375 | 0 | 6.793 | 37.78
2020-11-01 09:30 | 44136.3958 | 0 | 6.7911 | 37.78
2020-11-01 10:00 | 44136.4167 | 0 | 6.7855 | 37.78
2020-11-01 10:30 | 44136.4375 | 0 | 6.8384 | 37.78
2020-11-01 11:00 | 44136.4583 | 0 | 7.1241 | 37.78
2020-11-01 11:30 | 44136.4792 | 0 | 7.2936 | 37.78
2020-11-01 12:00 | 44136.5 | 0 | 7.26 | 37.78
2020-11-01 12:30 | 44136.5208 | 0 | 7.5697 | 37.78
2020-11-01 13:00 | 44136.5417 | 0 | 7.9116 | 37.78
2020-11-01 13:30 | 44136.5625 | 0 | 8.4431 | 37.78
2020-11-01 14:00 | 44136.5833 | 0 | 9.1682 | 37.78
2020-11-01 14:30 | 44136.6042 | 0 | 9.9077 | 37.78
2020-11-01 15:00 | 44136.625 | 0 | 10.6292 | 37.78
2020-11-01 15:30 | 44136.6458 | 0 | 11.6637 | 37.78
2020-11-01 16:00 | 44136.6667 | 0 | 12.3464 | 37.78
2020-11-01 16:30 | 44136.6875 | 0 | 13.0829 | 37.78
2020-11-01 17:00 | 44136.7083 | 0 | 13.5559 | 37.78
2020-11-01 17:30 | 44136.7292 | 0 | 13.9146 | 37.78
2020-11-01 18:00 | 44136.75 | 0 | 14.2597 | 37.78
2020-11-01 18:30 | 44136.7708 | 0 | 15.0825 | 37.78
2020-11-01 19:00 | 44136.7917 | 0 | 14.8336 | 37.78
2020-11-01 19:30 | 44136.8125 | 0 | 14.2984 | 37.78
2020-11-01 20:00 | 44136.8333 | 0 | 13.8321 | 37.78
2020-11-01 20:30 | 44136.8542 | 0 | 13.0557 | 37.78
2020-11-01 21:00 | 44136.875 | 0 | 12.3942 | 37.78
2020-11-01 21:30 | 44136.8958 | 0 | 11.8882 | 37.78
2020-11-01 22:00 | 44136.9167 | 0 | 11.3385 | 37.78
2020-11-01 22:30 | 44136.9375 | 0 | 10.4622 | 37.78
2020-11-01 23:00 | 44136.9583 | 0 | 9.8475 | 37.78
2020-11-01 23:30 | 44136.9792 | 0 | 9.3777 | 37.78
2020-11-02 | 44137 | 0 | 8.9047 | 37.78
2020-11-02 00:30 | 44137.0208 | 0 | 8.7229 | 37.78
2020-11-02 01:00 | 44137.0417 | 0 | 8.4583 | 37.78
2020-11-02 01:30 | 44137.0625 | 0 | 8.3801 | 37.78
2020-11-02 02:00 | 44137.0833 | 0 | 8.4047 | 37.78
2020-11-02 02:30 | 44137.1042 | 0 | 8.3075 | 37.78
2020-11-02 03:00 | 44137.125 | 0 | 8.3545 | 37.78
2020-11-02 03:30 | 44137.1458 | 0 | 8.5032 | 37.78
2020-11-02 04:00 | 44137.1667 | 0 | 8.6487 | 37.78
2020-11-02 04:30 | 44137.1875 | 0 | 9.0861 | 37.78
2020-11-02 05:00 | 44137.2083 | 0 | 9.4883 | 37.78
2020-11-02 05:30 | 44137.2292 | 0 | 9.9194 | 37.78
2020-11-02 06:00 | 44137.25 | 0 | 10.5189 | 37.78
2020-11-02 06:30 | 44137.2708 | 0 | 11.152 | 37.78
2020-11-02 07:00 | 44137.2917 | 0 | 11.5515 | 37.78
2020-11-02 07:30 | 44137.3125 | 0 | 11.602 | 37.78
2020-11-02 08:00 | 44137.3333 | 0 | 11.7083 | 37.78
2020-11-02 08:30 | 44137.3542 | 0 | 12.205 | 37.78
2020-11-02 09:00 | 44137.375 | 0 | 12.2794 | 37.78
2020-11-02 09:30 | 44137.3958 | 0 | 12.5323 | 37.78
2020-11-02 10:00 | 44137.4167 | 0 | 12.708 | 37.78
2020-11-02 10:30 | 44137.4375 | 0 | 13.1624 | 37.78
2020-11-02 11:00 | 44137.4583 | 0 | 13.1461 | 37.78
2020-11-02 11:30 | 44137.4792 | 0 | 13.7615 | 37.78
2020-11-02 12:00 | 44137.5 | 0 | 13.7379 | 37.78
2020-11-02 12:30 | 44137.5208 | 0 | 11.8264 | 37.78
2020-11-02 13:00 | 44137.5417 | 0 | 11.5934 | 37.78
2020-11-02 13:30 | 44137.5625 | 0 | 12.4794 | 37.78
2020-11-02 14:00 | 44137.5833 | 0 | 14.8186 | 37.78
2020-11-02 14:30 | 44137.6042 | 0 | 13.6093 | 37.78
2020-11-02 15:00 | 44137.625 | 0 | 13.6331 | 37.78
2020-11-02 15:30 | 44137.6458 | 0 | 13.5671 | 37.78
2020-11-02 16:00 | 44137.6667 | 0 | 14.1239 | 37.78
2020-11-02 16:30 | 44137.6875 | 0 | 14.7146 | 37.78
2020-11-02 17:00 | 44137.7083 | 0 | 14.953 | 37.78
2020-11-02 17:30 | 44137.7292 | 0 | 14.8793 | 37.78
2020-11-02 18:00 | 44137.75 | 0 | 14.9871 | 37.78
2020-11-02 18:30 | 44137.7708 | 0 | 15.5797 | 37.78
2020-11-02 19:00 | 44137.7917 | 0 | 15.2679 | 37.78
2020-11-02 19:30 | 44137.8125 | 0 | 15.0001 | 37.78
2020-11-02 20:00 | 44137.8333 | 0 | 14.5957 | 37.78
2020-11-02 20:30 | 44137.8542 | 0 | 13.7607 | 37.78
2020-11-02 21:00 | 44137.875 | 0 | 13.111 | 37.78
2020-11-02 21:30 | 44137.8958 | 0 | 12.657 | 37.78
2020-11-02 22:00 | 44137.9167 | 0 | 12.0307 | 37.78
2020-11-02 22:30 | 44137.9375 | 0 | 11.2156 | 37.78
2020-11-02 23:00 | 44137.9583 | 0 | 10.4509 | 37.78
2020-11-02 23:30 | 44137.9792 | 0 | 9.8612 | 37.78
2020-11-03 | 44138 | 0 | 9.3178 | 37.78
2020-11-03 00:30 | 44138.0208 | 0 | 8.9065 | 37.78
2020-11-03 01:00 | 44138.0417 | 0 | 8.7301 | 37.78
2020-11-03 01:30 | 44138.0625 | 0 | 8.5198 | 37.78
2020-11-03 02:00 | 44138.0833 | 0 | 8.5534 | 37.78
2020-11-03 02:30 | 44138.1042 | 0 | 8.5702 | 37.78
2020-11-03 03:00 | 44138.125 | 0 | 8.4528 | 37.78
2020-11-03 03:30 | 44138.1458 | 0 | 8.5479 | 37.78
2020-11-03 04:00 | 44138.1667 | 0 | 8.6151 | 37.78
2020-11-03 04:30 | 44138.1875 | 0 | 8.9585 | 37.78
2020-11-03 05:00 | 44138.2083 | 0 | 9.581 | 37.78
2020-11-03 05:30 | 44138.2292 | 0 | 9.8806 | 37.78
2020-11-03 06:00 | 44138.25 | 0 | 10.3051 | 37.78
2020-11-03 06:30 | 44138.2708 | 0 | 10.8501 | 37.78
2020-11-03 07:00 | 44138.2917 | 0 | 11.1553 | 37.78
2020-11-03 07:30 | 44138.3125 | 0 | 10.8477 | 37.78
2020-11-03 08:00 | 44138.3333 | 0 | 10.7232 | 37.78
2020-11-03 08:30 | 44138.3542 | 0 | 10.3281 | 37.78
2020-11-03 09:00 | 44138.375 | 0 | 10.3465 | 37.78
2020-11-03 09:30 | 44138.3958 | 0 | 10.4351 | 37.78
2020-11-03 10:00 | 44138.4167 | 0 | 10.555 | 37.78
2020-11-03 10:30 | 44138.4375 | 0 | 10.7201 | 37.78
2020-11-03 11:00 | 44138.4583 | 0 | 11.5326 | 37.78
2020-11-03 11:30 | 44138.4792 | 0 | 11.3015 | 37.78
2020-11-03 12:00 | 44138.5 | 0 | 11.5612 | 37.78
2020-11-03 12:30 | 44138.5208 | 0 | 11.174 | 37.78
2020-11-03 13:00 | 44138.5417 | 0 | 11.6019 | 37.78
2020-11-03 13:30 | 44138.5625 | 0 | 11.6332 | 37.78
2020-11-03 14:00 | 44138.5833 | 0 | 11.5204 | 37.78
2020-11-03 14:30 | 44138.6042 | 0 | 11.8142 | 37.78
2020-11-03 15:00 | 44138.625 | 0 | 12.306 | 37.78
2020-11-03 15:30 | 44138.6458 | 0 | 12.6412 | 37.78
2020-11-03 16:00 | 44138.6667 | 0 | 13.2575 | 37.78
2020-11-03 16:30 | 44138.6875 | 0 | 13.7459 | 37.78
2020-11-03 17:00 | 44138.7083 | 0 | 13.8275 | 37.78
2020-11-03 17:30 | 44138.7292 | 0 | 14.2209 | 37.78
2020-11-03 18:00 | 44138.75 | 0 | 14.2261 | 37.78
2020-11-03 18:30 | 44138.7708 | 0 | 15.2048 | 37.78
2020-11-03 19:00 | 44138.7917 | 0 | 14.9558 | 37.78
2020-11-03 19:30 | 44138.8125 | 0 | 14.451 | 37.78
2020-11-03 20:00 | 44138.8333 | 0 | 14.0698 | 37.78
2020-11-03 20:30 | 44138.8542 | 0 | 13.6016 | 37.78
2020-11-03 21:00 | 44138.875 | 0 | 12.8155 | 37.78
2020-11-03 21:30 | 44138.8958 | 0 | 12.4299 | 37.78
2020-11-03 22:00 | 44138.9167 | 0 | 11.9359 | 37.78
2020-11-03 22:30 | 44138.9375 | 0 | 10.8551 | 37.78
2020-11-03 23:00 | 44138.9583 | 0 | 10.1784 | 37.78
2020-11-03 23:30 | 44138.9792 | 0 | 9.805 | 37.78
2020-11-04 | 44139 | 0 | 9.5076 | 37.78
2020-11-04 00:30 | 44139.0208 | 0 | 8.8351 | 37.78
2020-11-04 01:00 | 44139.0417 | 0 | 8.7674 | 37.78
2020-11-04 01:30 | 44139.0625 | 0 | 8.6427 | 37.78
2020-11-04 02:00 | 44139.0833 | 0 | 8.5318 | 37.78
2020-11-04 02:30 | 44139.1042 | 0 | 8.1906 | 37.78
2020-11-04 03:00 | 44139.125 | 0 | 8.4103 | 37.78
2020-11-04 03:30 | 44139.1458 | 0 | 8.3805 | 37.78
2020-11-04 04:00 | 44139.1667 | 0 | 8.6404 | 37.78
2020-11-04 04:30 | 44139.1875 | 0 | 8.964 | 37.78
2020-11-04 05:00 | 44139.2083 | 0 | 9.5024 | 37.78
2020-11-04 05:30 | 44139.2292 | 0 | 9.676 | 37.78
2020-11-04 06:00 | 44139.25 | 0 | 10.2871 | 37.78
2020-11-04 06:30 | 44139.2708 | 0 | 10.7321 | 37.78
2020-11-04 07:00 | 44139.2917 | 0 | 10.906 | 37.78
2020-11-04 07:30 | 44139.3125 | 0 | 10.7603 | 37.78
2020-11-04 08:00 | 44139.3333 | 0 | 10.4265 | 37.78
2020-11-04 08:30 | 44139.3542 | 0 | 10.2598 | 37.78
2020-11-04 09:00 | 44139.375 | 0 | 10.2884 | 37.78
2020-11-04 09:30 | 44139.3958 | 0 | 10.6653 | 37.78
2020-11-04 10:00 | 44139.4167 | 0 | 10.2368 | 37.78
2020-11-04 10:30 | 44139.4375 | 0 | 10.8366 | 37.78
2020-11-04 11:00 | 44139.4583 | 0 | 10.7312 | 37.78
2020-11-04 11:30 | 44139.4792 | 0 | 10.9985 | 37.78
2020-11-04 12:00 | 44139.5 | 0 | 10.6746 | 37.78
2020-11-04 12:30 | 44139.5208 | 0 | 10.7046 | 37.78
2020-11-04 13:00 | 44139.5417 | 0 | 10.9344 | 37.78
2020-11-04 13:30 | 44139.5625 | 0 | 11.514 | 37.78
2020-11-04 14:00 | 44139.5833 | 0 | 11.7919 | 37.78
2020-11-04 14:30 | 44139.6042 | 0 | 12.1857 | 37.78
2020-11-04 15:00 | 44139.625 | 0 | 12.5668 | 37.78
2020-11-04 15:30 | 44139.6458 | 0 | 13.1599 | 37.78
2020-11-04 16:00 | 44139.6667 | 0 | 13.6511 | 37.78
2020-11-04 16:30 | 44139.6875 | 0 | 14.3435 | 37.78
2020-11-04 17:00 | 44139.7083 | 0 | 14.6056 | 37.78
2020-11-04 17:30 | 44139.7292 | 0 | 14.6337 | 37.78
2020-11-04 18:00 | 44139.75 | 0 | 14.858 | 37.78
2020-11-04 18:30 | 44139.7708 | 0 | 15.4895 | 37.78
2020-11-04 19:00 | 44139.7917 | 0 | 15.2435 | 37.78
2020-11-04 19:30 | 44139.8125 | 0 | 14.7732 | 37.78
2020-11-04 20:00 | 44139.8333 | 0 | 14.5607 | 37.78
2020-11-04 20:30 | 44139.8542 | 0 | 14.048 | 37.78
2020-11-04 21:00 | 44139.875 | 0 | 13.2506 | 37.78
2020-11-04 21:30 | 44139.8958 | 0 | 12.7942 | 37.78
2020-11-04 22:00 | 44139.9167 | 0 | 12.3848 | 37.78
2020-11-04 22:30 | 44139.9375 | 0 | 11.4139 | 37.78
2020-11-04 23:00 | 44139.9583 | 0 | 10.8253 | 37.78
2020-11-04 23:30 | 44139.9792 | 0 | 10.2174 | 37.78
2020-11-05 | 44140 | 0 | 9.5411 | 37.78
2020-11-05 00:30 | 44140.0208 | 0 | 9.1264 | 37.78
2020-11-05 01:00 | 44140.0417 | 0 | 9.1991 | 37.78
2020-11-05 01:30 | 44140.0625 | 0 | 9.0123 | 37.78
2020-11-05 02:00 | 44140.0833 | 0 | 8.8829 | 37.78
2020-11-05 02:30 | 44140.1042 | 0 | 8.758 | 37.78
2020-11-05 03:00 | 44140.125 | 0 | 8.7767 | 37.78
2020-11-05 03:30 | 44140.1458 | 0 | 8.7878 | 37.78
2020-11-05 04:00 | 44140.1667 | 0 | 8.9633 | 37.78
2020-11-05 04:30 | 44140.1875 | 0 | 9.4379 | 37.78
2020-11-05 05:00 | 44140.2083 | 0 | 10.0755 | 37.78
2020-11-05 05:30 | 44140.2292 | 0 | 10.435 | 37.78
2020-11-05 06:00 | 44140.25 | 0 | 11.0626 | 37.78
2020-11-05 06:30 | 44140.2708 | 0 | 11.6163 | 37.78
2020-11-05 07:00 | 44140.2917 | 0 | 11.8234 | 37.78
2020-11-05 07:30 | 44140.3125 | 0 | 12.0786 | 37.78
2020-11-05 08:00 | 44140.3333 | 0 | 12.1432 | 37.78
2020-11-05 08:30 | 44140.3542 | 0 | 12.1771 | 37.78
2020-11-05 09:00 | 44140.375 | 0 | 12.3092 | 37.78
2020-11-05 09:30 | 44140.3958 | 0 | 12.5531 | 37.78
2020-11-05 10:00 | 44140.4167 | 0 | 12.7467 | 37.78
2020-11-05 10:30 | 44140.4375 | 0 | 12.8675 | 37.78
2020-11-05 11:00 | 44140.4583 | 0 | 12.9266 | 37.78
2020-11-05 11:30 | 44140.4792 | 0 | 14.168 | 37.78
2020-11-05 12:00 | 44140.5 | 0 | 15.7736 | 37.78
2020-11-05 12:30 | 44140.5208 | 0 | 14.4908 | 37.78
2020-11-05 13:00 | 44140.5417 | 0 | 13.6245 | 37.78
2020-11-05 13:30 | 44140.5625 | 0 | 14.4601 | 37.78
2020-11-05 14:00 | 44140.5833 | 0 | 15.036 | 37.78
2020-11-05 14:30 | 44140.6042 | 0 | 15.5798 | 37.78
2020-11-05 15:00 | 44140.625 | 0 | 16.7481 | 37.78
2020-11-05 15:30 | 44140.6458 | 0 | 17.3588 | 37.78
2020-11-05 16:00 | 44140.6667 | 0 | 15.4272 | 37.78
2020-11-05 16:30 | 44140.6875 | 0 | 16.9558 | 37.78
2020-11-05 17:00 | 44140.7083 | 0 | 17.2329 | 37.78
2020-11-05 17:30 | 44140.7292 | 0 | 17.1236 | 37.78
2020-11-05 18:00 | 44140.75 | 0 | 17.0492 | 37.78
2020-11-05 18:30 | 44140.7708 | 0 | 17.8602 | 37.78
2020-11-05 19:00 | 44140.7917 | 0 | 17.7776 | 37.78
2020-11-05 19:30 | 44140.8125 | 0 | 17.3413 | 37.78
2020-11-05 20:00 | 44140.8333 | 0 | 16.9041 | 37.78
2020-11-05 20:30 | 44140.8542 | 0 | 16.3053 | 37.78
2020-11-05 21:00 | 44140.875 | 0 | 15.3704 | 37.78
2020-11-05 21:30 | 44140.8958 | 0 | 14.3294 | 37.78
2020-11-05 22:00 | 44140.9167 | 0 | 13.4871 | 37.78
2020-11-05 22:30 | 44140.9375 | 0 | 12.2619 | 37.78
2020-11-05 23:00 | 44140.9583 | 0 | 11.2918 | 37.78
2020-11-05 23:30 | 44140.9792 | 0 | 10.5341 | 37.78
2020-11-06 | 44141 | 0 | 9.914 | 37.78
2020-11-06 00:30 | 44141.0208 | 0 | 9.4602 | 37.78
2020-11-06 01:00 | 44141.0417 | 0 | 9.1523 | 37.78
2020-11-06 01:30 | 44141.0625 | 0 | 9.002 | 37.78
2020-11-06 02:00 | 44141.0833 | 0 | 8.9331 | 37.78
2020-11-06 02:30 | 44141.1042 | 0 | 8.8435 | 37.78
2020-11-06 03:00 | 44141.125 | 0 | 8.7097 | 37.78
2020-11-06 03:30 | 44141.1458 | 0 | 8.8365 | 37.78
2020-11-06 04:00 | 44141.1667 | 0 | 9.0337 | 37.78
2020-11-06 04:30 | 44141.1875 | 0 | 9.3143 | 37.78
2020-11-06 05:00 | 44141.2083 | 0 | 9.7131 | 37.78
2020-11-06 05:30 | 44141.2292 | 0 | 9.8806 | 37.78
2020-11-06 06:00 | 44141.25 | 0 | 10.1946 | 37.78
2020-11-06 06:30 | 44141.2708 | 0 | 10.4688 | 37.78
2020-11-06 07:00 | 44141.2917 | 0 | 10.5474 | 37.78
2020-11-06 07:30 | 44141.3125 | 0 | 10.4817 | 37.78
2020-11-06 08:00 | 44141.3333 | 0 | 10.463 | 37.78
2020-11-06 08:30 | 44141.3542 | 0 | 10.28 | 37.78
2020-11-06 09:00 | 44141.375 | 0 | 10.4059 | 37.78
2020-11-06 09:30 | 44141.3958 | 0 | 10.206 | 37.78
2020-11-06 10:00 | 44141.4167 | 0 | 10.2341 | 37.78
2020-11-06 10:30 | 44141.4375 | 0 | 10.2601 | 37.78
2020-11-06 11:00 | 44141.4583 | 0 | 10.3026 | 37.78
2020-11-06 11:30 | 44141.4792 | 0 | 10.4001 | 37.78
2020-11-06 12:00 | 44141.5 | 0 | 10.588 | 37.78
2020-11-06 12:30 | 44141.5208 | 0 | 10.3551 | 37.78
2020-11-06 13:00 | 44141.5417 | 0 | 10.4853 | 37.78
2020-11-06 13:30 | 44141.5625 | 0 | 10.8605 | 37.78
2020-11-06 14:00 | 44141.5833 | 0 | 11.1464 | 37.78
2020-11-06 14:30 | 44141.6042 | 0 | 11.5381 | 37.78
2020-11-06 15:00 | 44141.625 | 0 | 12.1878 | 37.78
2020-11-06 15:30 | 44141.6458 | 0 | 12.9126 | 37.78
2020-11-06 16:00 | 44141.6667 | 0 | 13.5035 | 37.78
2020-11-06 16:30 | 44141.6875 | 0 | 14.0458 | 37.78
2020-11-06 17:00 | 44141.7083 | 0 | 14.0097 | 37.78
2020-11-06 17:30 | 44141.7292 | 0 | 13.9653 | 37.78
2020-11-06 18:00 | 44141.75 | 0 | 14.0586 | 37.78
2020-11-06 18:30 | 44141.7708 | 0 | 14.6006 | 37.78
2020-11-06 19:00 | 44141.7917 | 0 | 14.0796 | 37.78
2020-11-06 19:30 | 44141.8125 | 0 | 13.956 | 37.78
2020-11-06 20:00 | 44141.8333 | 0 | 13.8107 | 37.78
2020-11-06 20:30 | 44141.8542 | 0 | 13.3435 | 37.78
2020-11-06 21:00 | 44141.875 | 0 | 12.7942 | 37.78
2020-11-06 21:30 | 44141.8958 | 0 | 12.5564 | 37.78
2020-11-06 22:00 | 44141.9167 | 0 | 12.0662 | 37.78
2020-11-06 22:30 | 44141.9375 | 0 | 11.2643 | 37.78
2020-11-06 23:00 | 44141.9583 | 0 | 10.6237 | 37.78
2020-11-06 23:30 | 44141.9792 | 0 | 10.0699 | 37.78
2020-11-07 | 44142 | 0 | 9.4966 | 37.78
2020-11-07 00:30 | 44142.0208 | 0 | 9.1504 | 37.78
2020-11-07 01:00 | 44142.0417 | 0 | 8.9829 | 37.78
2020-11-07 01:30 | 44142.0625 | 0 | 8.717 | 37.78
2020-11-07 02:00 | 44142.0833 | 0 | 8.5589 | 37.78
2020-11-07 02:30 | 44142.1042 | 0 | 8.3997 | 37.78
2020-11-07 03:00 | 44142.125 | 0 | 8.3861 | 37.78
2020-11-07 03:30 | 44142.1458 | 0 | 8.4809 | 37.78
2020-11-07 04:00 | 44142.1667 | 0 | 8.5087 | 37.78
2020-11-07 04:30 | 44142.1875 | 0 | 8.5534 | 37.78
2020-11-07 05:00 | 44142.2083 | 0 | 8.734 | 37.78
2020-11-07 05:30 | 44142.2292 | 0 | 8.721 | 37.78
2020-11-07 06:00 | 44142.25 | 0 | 8.5187 | 37.78
2020-11-07 06:30 | 44142.2708 | 0 | 8.259 | 37.78
2020-11-07 07:00 | 44142.2917 | 0 | 7.8553 | 37.78
2020-11-07 07:30 | 44142.3125 | 0 | 8.1197 | 37.78
2020-11-07 08:00 | 44142.3333 | 0 | 8.2257 | 37.78
2020-11-07 08:30 | 44142.3542 | 0 | 8.787 | 37.78
2020-11-07 09:00 | 44142.375 | 0 | 9.1833 | 37.78
2020-11-07 09:30 | 44142.3958 | 0 | 8.7971 | 37.78
2020-11-07 10:00 | 44142.4167 | 0 | 9.5403 | 37.78
2020-11-07 10:30 | 44142.4375 | 0 | 8.8173 | 37.78
2020-11-07 11:00 | 44142.4583 | 0 | 8.6094 | 37.78
2020-11-07 11:30 | 44142.4792 | 0 | 9.7917 | 37.78
2020-11-07 12:00 | 44142.5 | 0 | 10.7792 | 37.78
2020-11-07 12:30 | 44142.5208 | 0 | 10.096 | 37.78
2020-11-07 13:00 | 44142.5417 | 0 | 8.5106 | 37.78
2020-11-07 13:30 | 44142.5625 | 0 | 8.9727 | 37.78
2020-11-07 14:00 | 44142.5833 | 0 | 9.5867 | 37.78
2020-11-07 14:30 | 44142.6042 | 0 | 11.1333 | 37.78
2020-11-07 15:00 | 44142.625 | 0 | 10.2585 | 37.78
2020-11-07 15:30 | 44142.6458 | 0 | 11.0037 | 37.78
2020-11-07 16:00 | 44142.6667 | 0 | 11.8503 | 37.78
2020-11-07 16:30 | 44142.6875 | 0 | 11.9352 | 37.78
2020-11-07 17:00 | 44142.7083 | 0 | 11.7148 | 37.78
2020-11-07 17:30 | 44142.7292 | 0 | 11.7251 | 37.78
2020-11-07 18:00 | 44142.75 | 0 | 12.0321 | 37.78
2020-11-07 18:30 | 44142.7708 | 0 | 12.7005 | 37.78
2020-11-07 19:00 | 44142.7917 | 0 | 12.4109 | 37.78
2020-11-07 19:30 | 44142.8125 | 0 | 12.0326 | 37.78
2020-11-07 20:00 | 44142.8333 | 0 | 11.9292 | 37.78
2020-11-07 20:30 | 44142.8542 | 0 | 11.4053 | 37.78
2020-11-07 21:00 | 44142.875 | 0 | 11.211 | 37.78
2020-11-07 21:30 | 44142.8958 | 0 | 10.9391 | 37.78
2020-11-07 22:00 | 44142.9167 | 0 | 10.6197 | 37.78
2020-11-07 22:30 | 44142.9375 | 0 | 9.9293 | 37.78
2020-11-07 23:00 | 44142.9583 | 0 | 9.4967 | 37.78
2020-11-07 23:30 | 44142.9792 | 0 | 9.1121 | 37.78
2020-11-08 | 44143 | 0 | 8.6082 | 37.78
2020-11-08 00:30 | 44143.0208 | 0 | 8.3635 | 37.78
2020-11-08 01:00 | 44143.0417 | 0 | 8.222 | 37.78
2020-11-08 01:30 | 44143.0625 | 0 | 8.1236 | 37.78
2020-11-08 02:00 | 44143.0833 | 0 | 8.0061 | 37.78
2020-11-08 02:30 | 44143.1042 | 0 | 7.8889 | 37.78
2020-11-08 03:00 | 44143.125 | 0 | 7.8666 | 37.78
2020-11-08 03:30 | 44143.1458 | 0 | 7.8947 | 37.78
2020-11-08 04:00 | 44143.1667 | 0 | 7.8498 | 37.78
2020-11-08 04:30 | 44143.1875 | 0 | 7.8443 | 37.78
2020-11-08 05:00 | 44143.2083 | 0 | 7.8779 | 37.78
2020-11-08 05:30 | 44143.2292 | 0 | 7.8666 | 37.78
2020-11-08 06:00 | 44143.25 | 0 | 7.7884 | 37.78
2020-11-08 06:30 | 44143.2708 | 0 | 7.5039 | 37.78
2020-11-08 07:00 | 44143.2917 | 0 | 7.8005 | 37.78
2020-11-08 07:30 | 44143.3125 | 0 | 8.2248 | 37.78
2020-11-08 08:00 | 44143.3333 | 0 | 9.2829 | 37.78
2020-11-08 08:30 | 44143.3542 | 0 | 9.5057 | 37.78
2020-11-08 09:00 | 44143.375 | 0 | 9.4966 | 37.78
2020-11-08 09:30 | 44143.3958 | 0 | 9.918 | 37.78
2020-11-08 10:00 | 44143.4167 | 0 | 9.7402 | 37.78
2020-11-08 10:30 | 44143.4375 | 0 | 8.7718 | 37.78
2020-11-08 11:00 | 44143.4583 | 0 | 8.2118 | 37.78
2020-11-08 11:30 | 44143.4792 | 0 | 9.0813 | 37.78
2020-11-08 12:00 | 44143.5 | 0 | 10.0158 | 37.78
2020-11-08 12:30 | 44143.5208 | 0 | 9.4234 | 37.78
2020-11-08 13:00 | 44143.5417 | 0 | 9.5582 | 37.78
2020-11-08 13:30 | 44143.5625 | 0 | 9.8093 | 37.78
2020-11-08 14:00 | 44143.5833 | 0 | 9.6623 | 37.78
2020-11-08 14:30 | 44143.6042 | 0 | 9.2582 | 37.78
2020-11-08 15:00 | 44143.625 | 0 | 8.9606 | 37.78
2020-11-08 15:30 | 44143.6458 | 0 | 9.705 | 37.78
2020-11-08 16:00 | 44143.6667 | 0 | 9.9005 | 37.78
2020-11-08 16:30 | 44143.6875 | 0 | 10.4194 | 37.78
2020-11-08 17:00 | 44143.7083 | 0 | 10.828 | 37.78
2020-11-08 17:30 | 44143.7292 | 0 | 11.1475 | 37.78
2020-11-08 18:00 | 44143.75 | 0 | 11.5489 | 37.78
2020-11-08 18:30 | 44143.7708 | 0 | 12.2177 | 37.78
2020-11-08 19:00 | 44143.7917 | 0 | 12.0181 | 37.78
2020-11-08 19:30 | 44143.8125 | 0 | 11.7635 | 37.78
2020-11-08 20:00 | 44143.8333 | 0 | 11.624 | 37.78
2020-11-08 20:30 | 44143.8542 | 0 | 11.1298 | 37.78
2020-11-08 21:00 | 44143.875 | 0 | 10.6447 | 37.78
2020-11-08 21:30 | 44143.8958 | 0 | 10.2188 | 37.78
2020-11-08 22:00 | 44143.9167 | 0 | 9.7602 | 37.78
2020-11-08 22:30 | 44143.9375 | 0 | 9.0495 | 37.78
2020-11-08 23:00 | 44143.9583 | 0 | 8.571 | 37.78
2020-11-08 23:30 | 44143.9792 | 0 | 8.2962 | 37.78
2020-11-09 | 44144 | 0 | 7.989 | 37.78
2020-11-09 00:30 | 44144.0208 | 0 | 7.7231 | 37.78
2020-11-09 01:00 | 44144.0417 | 0 | 7.5931 | 37.78
2020-11-09 01:30 | 44144.0625 | 0 | 7.5708 | 37.78
2020-11-09 02:00 | 44144.0833 | 0 | 7.6769 | 37.78
2020-11-09 02:30 | 44144.1042 | 0 | 7.565 | 37.78
2020-11-09 03:00 | 44144.125 | 0 | 7.6157 | 37.78
2020-11-09 03:30 | 44144.1458 | 0 | 7.675 | 37.78
2020-11-09 04:00 | 44144.1667 | 0 | 7.9873 | 37.78
2020-11-09 04:30 | 44144.1875 | 0 | 8.321 | 37.78
2020-11-09 05:00 | 44144.2083 | 0 | 8.8681 | 37.78
2020-11-09 05:30 | 44144.2292 | 0 | 9.2049 | 37.78
2020-11-09 06:00 | 44144.25 | 0 | 9.6681 | 37.78
2020-11-09 06:30 | 44144.2708 | 0 | 9.901 | 37.78
2020-11-09 07:00 | 44144.2917 | 0 | 10.4958 | 37.78
2020-11-09 07:30 | 44144.3125 | 0 | 10.3398 | 37.78
2020-11-09 08:00 | 44144.3333 | 0 | 10.342 | 37.78
2020-11-09 08:30 | 44144.3542 | 0 | 9.9118 | 37.78
2020-11-09 09:00 | 44144.375 | 0 | 10.1133 | 37.78
2020-11-09 09:30 | 44144.3958 | 0 | 10.8996 | 37.78
2020-11-09 10:00 | 44144.4167 | 0 | 10.5468 | 37.78
2020-11-09 10:30 | 44144.4375 | 0 | 10.4792 | 37.78
2020-11-09 11:00 | 44144.4583 | 0 | 10.9923 | 37.78
2020-11-09 11:30 | 44144.4792 | 0 | 10.3068 | 37.78
2020-11-09 12:00 | 44144.5 | 0 | 10.6233 | 37.78
2020-11-09 12:30 | 44144.5208 | 0 | 10.1866 | 37.78
2020-11-09 13:00 | 44144.5417 | 0 | 9.8449 | 37.78
2020-11-09 13:30 | 44144.5625 | 0 | 11.0455 | 37.78
2020-11-09 14:00 | 44144.5833 | 0 | 12.1738 | 37.78
2020-11-09 14:30 | 44144.6042 | 0 | 11.5331 | 37.78
2020-11-09 15:00 | 44144.625 | 0 | 12.2777 | 37.78
2020-11-09 15:30 | 44144.6458 | 0 | 12.5024 | 37.78
2020-11-09 16:00 | 44144.6667 | 0 | 12.6184 | 37.78
2020-11-09 16:30 | 44144.6875 | 0 | 13.2265 | 37.78
2020-11-09 17:00 | 44144.7083 | 0 | 13.0696 | 37.78
2020-11-09 17:30 | 44144.7292 | 0 | 13.5623 | 37.78
2020-11-09 18:00 | 44144.75 | 0 | 13.8926 | 37.78
2020-11-09 18:30 | 44144.7708 | 0 | 14.638 | 37.78
2020-11-09 19:00 | 44144.7917 | 0 | 14.2035 | 37.78
2020-11-09 19:30 | 44144.8125 | 0 | 13.6903 | 37.78
2020-11-09 20:00 | 44144.8333 | 0 | 13.4062 | 37.78
2020-11-09 20:30 | 44144.8542 | 0 | 12.7884 | 37.78
2020-11-09 21:00 | 44144.875 | 0 | 12.2895 | 37.78
2020-11-09 21:30 | 44144.8958 | 0 | 11.9423 | 37.78
2020-11-09 22:00 | 44144.9167 | 0 | 11.2459 | 37.78
2020-11-09 22:30 | 44144.9375 | 0 | 10.4972 | 37.78
2020-11-09 23:00 | 44144.9583 | 0 | 9.9887 | 37.78
2020-11-09 23:30 | 44144.9792 | 0 | 9.4267 | 37.78
2020-11-10 | 44145 | 0 | 8.8781 | 37.78
2020-11-10 00:30 | 44145.0208 | 0 | 8.4249 | 37.78
2020-11-10 01:00 | 44145.0417 | 0 | 8.3075 | 37.78
2020-11-10 01:30 | 44145.0625 | 0 | 8.2165 | 37.78
2020-11-10 02:00 | 44145.0833 | 0 | 8.2055 | 37.78
2020-11-10 02:30 | 44145.1042 | 0 | 8.1123 | 37.78
2020-11-10 03:00 | 44145.125 | 0 | 7.9669 | 37.78
2020-11-10 03:30 | 44145.1458 | 0 | 8.0569 | 37.78
2020-11-10 04:00 | 44145.1667 | 0 | 8.2354 | 37.78
2020-11-10 04:30 | 44145.1875 | 0 | 8.6096 | 37.78
2020-11-10 05:00 | 44145.2083 | 0 | 9.1398 | 37.78
2020-11-10 05:30 | 44145.2292 | 0 | 9.6329 | 37.78
2020-11-10 06:00 | 44145.25 | 0 | 10.0019 | 37.78
2020-11-10 06:30 | 44145.2708 | 0 | 10.298 | 37.78
2020-11-10 07:00 | 44145.2917 | 0 | 10.5242 | 37.78
2020-11-10 07:30 | 44145.3125 | 0 | 10.6248 | 37.78
2020-11-10 08:00 | 44145.3333 | 0 | 10.5452 | 37.78
2020-11-10 08:30 | 44145.3542 | 0 | 10.8836 | 37.78
2020-11-10 09:00 | 44145.375 | 0 | 10.7042 | 37.78
2020-11-10 09:30 | 44145.3958 | 0 | 9.9003 | 37.78
2020-11-10 10:00 | 44145.4167 | 0 | 11.6598 | 37.78
2020-11-10 10:30 | 44145.4375 | 0 | 11.8238 | 37.78
2020-11-10 11:00 | 44145.4583 | 0 | 10.8214 | 37.78
2020-11-10 11:30 | 44145.4792 | 0 | 12.1175 | 37.78
2020-11-10 12:00 | 44145.5 | 0 | 12.1006 | 37.78
2020-11-10 12:30 | 44145.5208 | 0 | 11.6139 | 37.78
2020-11-10 13:00 | 44145.5417 | 0 | 11.4105 | 37.78
2020-11-10 13:30 | 44145.5625 | 0 | 11.4951 | 37.78
2020-11-10 14:00 | 44145.5833 | 0 | 11.9385 | 37.78
2020-11-10 14:30 | 44145.6042 | 0 | 12.8082 | 37.78
2020-11-10 15:00 | 44145.625 | 0 | 12.3884 | 37.78
2020-11-10 15:30 | 44145.6458 | 0 | 11.8651 | 37.78
2020-11-10 16:00 | 44145.6667 | 0 | 12.525 | 37.78
2020-11-10 16:30 | 44145.6875 | 0 | 13.3941 | 37.78
2020-11-10 17:00 | 44145.7083 | 0 | 13.2708 | 37.78
2020-11-10 17:30 | 44145.7292 | 0 | 13.581 | 37.78
2020-11-10 18:00 | 44145.75 | 0 | 14.0803 | 37.78
2020-11-10 18:30 | 44145.7708 | 0 | 14.8195 | 37.78
2020-11-10 19:00 | 44145.7917 | 0 | 14.492 | 37.78
2020-11-10 19:30 | 44145.8125 | 0 | 14.2201 | 37.78
2020-11-10 20:00 | 44145.8333 | 0 | 14.1922 | 37.78
2020-11-10 20:30 | 44145.8542 | 0 | 13.5155 | 37.78
2020-11-10 21:00 | 44145.875 | 0 | 12.4861 | 37.78
2020-11-10 21:30 | 44145.8958 | 0 | 12.1545 | 37.78
2020-11-10 22:00 | 44145.9167 | 0 | 11.7862 | 37.78
2020-11-10 22:30 | 44145.9375 | 0 | 10.8924 | 37.78
2020-11-10 23:00 | 44145.9583 | 0 | 10.2138 | 37.78
2020-11-10 23:30 | 44145.9792 | 0 | 9.7486 | 37.78
2020-11-11 | 44146 | 0 | 9.2101 | 37.78
2020-11-11 00:30 | 44146.0208 | 0 | 8.7123 | 37.78
2020-11-11 01:00 | 44146.0417 | 0 | 8.5644 | 37.78
2020-11-11 01:30 | 44146.0625 | 0 | 8.5142 | 37.78
2020-11-11 02:00 | 44146.0833 | 0 | 8.4696 | 37.78
2020-11-11 02:30 | 44146.1042 | 0 | 8.4252 | 37.78
2020-11-11 03:00 | 44146.125 | 0 | 8.4194 | 37.78
2020-11-11 03:30 | 44146.1458 | 0 | 8.4026 | 37.78
2020-11-11 04:00 | 44146.1667 | 0 | 8.6096 | 37.78
2020-11-11 04:30 | 44146.1875 | 0 | 8.9865 | 37.78
2020-11-11 05:00 | 44146.2083 | 0 | 9.5327 | 37.78
2020-11-11 05:30 | 44146.2292 | 0 | 9.7989 | 37.78
2020-11-11 06:00 | 44146.25 | 0 | 10.136 | 37.78
2020-11-11 06:30 | 44146.2708 | 0 | 10.6991 | 37.78
2020-11-11 07:00 | 44146.2917 | 0 | 10.9061 | 37.78
2020-11-11 07:30 | 44146.3125 | 0 | 10.7655 | 37.78
2020-11-11 08:00 | 44146.3333 | 0 | 11.0828 | 37.78
2020-11-11 08:30 | 44146.3542 | 0 | 11.0709 | 37.78
2020-11-11 09:00 | 44146.375 | 0 | 11.0943 | 37.78
2020-11-11 09:30 | 44146.3958 | 0 | 10.9799 | 37.78
2020-11-11 10:00 | 44146.4167 | 0 | 10.5575 | 37.78
2020-11-11 10:30 | 44146.4375 | 0 | 10.5019 | 37.78
2020-11-11 11:00 | 44146.4583 | 0 | 10.3172 | 37.78
2020-11-11 11:30 | 44146.4792 | 0 | 10.4905 | 37.78
2020-11-11 12:00 | 44146.5 | 0 | 10.3007 | 37.78
2020-11-11 12:30 | 44146.5208 | 0 | 10.2656 | 37.78
2020-11-11 13:00 | 44146.5417 | 0 | 10.5156 | 37.78
2020-11-11 13:30 | 44146.5625 | 0 | 10.9843 | 37.78
2020-11-11 14:00 | 44146.5833 | 0 | 11.4232 | 37.78
2020-11-11 14:30 | 44146.6042 | 0 | 11.6341 | 37.78
2020-11-11 15:00 | 44146.625 | 0 | 12.2202 | 37.78
2020-11-11 15:30 | 44146.6458 | 0 | 12.8844 | 37.78
2020-11-11 16:00 | 44146.6667 | 0 | 13.6626 | 37.78
2020-11-11 16:30 | 44146.6875 | 0 | 14.029 | 37.78
2020-11-11 17:00 | 44146.7083 | 0 | 14.4642 | 37.78
2020-11-11 17:30 | 44146.7292 | 0 | 14.6246 | 37.78
2020-11-11 18:00 | 44146.75 | 0 | 14.5664 | 37.78
2020-11-11 18:30 | 44146.7708 | 0 | 15.2345 | 37.78
2020-11-11 19:00 | 44146.7917 | 0 | 15.0056 | 37.78
2020-11-11 19:30 | 44146.8125 | 0 | 14.6168 | 37.78
2020-11-11 20:00 | 44146.8333 | 0 | 14.2314 | 37.78
2020-11-11 20:30 | 44146.8542 | 0 | 13.6337 | 37.78
2020-11-11 21:00 | 44146.875 | 0 | 13.0936 | 37.78
2020-11-11 21:30 | 44146.8958 | 0 | 12.64 | 37.78
2020-11-11 22:00 | 44146.9167 | 0 | 11.9411 | 37.78
2020-11-11 22:30 | 44146.9375 | 0 | 11.1657 | 37.78
2020-11-11 23:00 | 44146.9583 | 0 | 10.6408 | 37.78
2020-11-11 23:30 | 44146.9792 | 0 | 10.0121 | 37.78
2020-11-12 | 44147 | 0 | 9.3542 | 37.78
2020-11-12 00:30 | 44147.0208 | 0 | 8.9774 | 37.78
2020-11-12 01:00 | 44147.0417 | 0 | 8.745 | 37.78
2020-11-12 01:30 | 44147.0625 | 0 | 8.6638 | 37.78
2020-11-12 02:00 | 44147.0833 | 0 | 8.7378 | 37.78
2020-11-12 02:30 | 44147.1042 | 0 | 8.6406 | 37.78
2020-11-12 03:00 | 44147.125 | 0 | 8.68 | 37.78
2020-11-12 03:30 | 44147.1458 | 0 | 8.7248 | 37.78
2020-11-12 04:00 | 44147.1667 | 0 | 8.8123 | 37.78
2020-11-12 04:30 | 44147.1875 | 0 | 9.1719 | 37.78
2020-11-12 05:00 | 44147.2083 | 0 | 9.6386 | 37.78
2020-11-12 05:30 | 44147.2292 | 0 | 10.1115 | 37.78
2020-11-12 06:00 | 44147.25 | 0 | 11.0727 | 37.78
2020-11-12 06:30 | 44147.2708 | 0 | 11.3744 | 37.78
2020-11-12 07:00 | 44147.2917 | 0 | 12.1989 | 37.78
2020-11-12 07:30 | 44147.3125 | 0 | 12.659 | 37.78
2020-11-12 08:00 | 44147.3333 | 0 | 11.963 | 37.78
2020-11-12 08:30 | 44147.3542 | 0 | 11.9982 | 37.78
2020-11-12 09:00 | 44147.375 | 0 | 12.3424 | 37.78
2020-11-12 09:30 | 44147.3958 | 0 | 11.6516 | 37.78
2020-11-12 10:00 | 44147.4167 | 0 | 11.6055 | 37.78
2020-11-12 10:30 | 44147.4375 | 0 | 11.8464 | 37.78
2020-11-12 11:00 | 44147.4583 | 0 | 11.3788 | 37.78
2020-11-12 11:30 | 44147.4792 | 0 | 11.4457 | 37.78
2020-11-12 12:00 | 44147.5 | 0 | 12.0082 | 37.78
2020-11-12 12:30 | 44147.5208 | 0 | 11.322 | 37.78
2020-11-12 13:00 | 44147.5417 | 0 | 12.1631 | 37.78
2020-11-12 13:30 | 44147.5625 | 0 | 11.4135 | 37.78
2020-11-12 14:00 | 44147.5833 | 0 | 11.7322 | 37.78
2020-11-12 14:30 | 44147.6042 | 0 | 12.0059 | 37.78
2020-11-12 15:00 | 44147.625 | 0 | 12.3168 | 37.78
2020-11-12 15:30 | 44147.6458 | 0 | 12.2755 | 37.78
2020-11-12 16:00 | 44147.6667 | 0 | 12.7243 | 37.78
2020-11-12 16:30 | 44147.6875 | 0 | 13.21 | 37.78
2020-11-12 17:00 | 44147.7083 | 0 | 13.5504 | 37.78
2020-11-12 17:30 | 44147.7292 | 0 | 13.6696 | 37.78
2020-11-12 18:00 | 44147.75 | 0 | 13.9162 | 37.78
2020-11-12 18:30 | 44147.7708 | 0 | 14.3524 | 37.78
2020-11-12 19:00 | 44147.7917 | 0 | 14.1366 | 37.78
2020-11-12 19:30 | 44147.8125 | 0 | 14.0141 | 37.78
2020-11-12 20:00 | 44147.8333 | 0 | 13.7954 | 37.78
2020-11-12 20:30 | 44147.8542 | 0 | 13.3556 | 37.78
2020-11-12 21:00 | 44147.875 | 0 | 12.7933 | 37.78
2020-11-12 21:30 | 44147.8958 | 0 | 12.4386 | 37.78
2020-11-12 22:00 | 44147.9167 | 0 | 11.846 | 37.78
2020-11-12 22:30 | 44147.9375 | 0 | 10.8771 | 37.78
2020-11-12 23:00 | 44147.9583 | 0 | 10.2866 | 37.78
2020-11-12 23:30 | 44147.9792 | 0 | 9.6905 | 37.78
2020-11-13 | 44148 | 0 | 9.0731 | 37.78
2020-11-13 00:30 | 44148.0208 | 0 | 8.7205 | 37.78
2020-11-13 01:00 | 44148.0417 | 0 | 8.661 | 37.78
2020-11-13 01:30 | 44148.0625 | 0 | 8.4397 | 37.78
2020-11-13 02:00 | 44148.0833 | 0 | 8.3707 | 37.78
2020-11-13 02:30 | 44148.1042 | 0 | 8.2746 | 37.78
2020-11-13 03:00 | 44148.125 | 0 | 8.1582 | 37.78
2020-11-13 03:30 | 44148.1458 | 0 | 8.3152 | 37.78
2020-11-13 04:00 | 44148.1667 | 0 | 8.4072 | 37.78
2020-11-13 04:30 | 44148.1875 | 0 | 8.8248 | 37.78
2020-11-13 05:00 | 44148.2083 | 0 | 9.1517 | 37.78
2020-11-13 05:30 | 44148.2292 | 0 | 9.5272 | 37.78
2020-11-13 06:00 | 44148.25 | 0 | 10.0051 | 37.78
2020-11-13 06:30 | 44148.2708 | 0 | 10.5915 | 37.78
2020-11-13 07:00 | 44148.2917 | 0 | 10.9154 | 37.78
2020-11-13 07:30 | 44148.3125 | 0 | 11.6091 | 37.78
2020-11-13 08:00 | 44148.3333 | 0 | 11.1525 | 37.78
2020-11-13 08:30 | 44148.3542 | 0 | 12.2191 | 37.78
2020-11-13 09:00 | 44148.375 | 0 | 10.6784 | 37.78
2020-11-13 09:30 | 44148.3958 | 0 | 12.5564 | 37.78
2020-11-13 10:00 | 44148.4167 | 0 | 14.0255 | 37.78
2020-11-13 10:30 | 44148.4375 | 0 | 14.3978 | 37.78
2020-11-13 11:00 | 44148.4583 | 0 | 13.7768 | 37.78
2020-11-13 11:30 | 44148.4792 | 0 | 13.2869 | 37.78
2020-11-13 12:00 | 44148.5 | 0 | 13.0944 | 37.78
2020-11-13 12:30 | 44148.5208 | 0 | 12.5917 | 37.78
2020-11-13 13:00 | 44148.5417 | 0 | 10.951 | 37.78
2020-11-13 13:30 | 44148.5625 | 0 | 11.4085 | 37.78
2020-11-13 14:00 | 44148.5833 | 0 | 11.8706 | 37.78
2020-11-13 14:30 | 44148.6042 | 0 | 11.6306 | 37.78
2020-11-13 15:00 | 44148.625 | 0 | 11.9881 | 37.78
2020-11-13 15:30 | 44148.6458 | 0 | 12.4678 | 37.78
2020-11-13 16:00 | 44148.6667 | 0 | 13.8445 | 37.78
2020-11-13 16:30 | 44148.6875 | 0 | 14.1391 | 37.78
2020-11-13 17:00 | 44148.7083 | 0 | 14.2096 | 37.78
2020-11-13 17:30 | 44148.7292 | 0 | 14.1203 | 37.78
2020-11-13 18:00 | 44148.75 | 0 | 14.0032 | 37.78
2020-11-13 18:30 | 44148.7708 | 0 | 14.4256 | 37.78
2020-11-13 19:00 | 44148.7917 | 0 | 14.3497 | 37.78
2020-11-13 19:30 | 44148.8125 | 0 | 13.9999 | 37.78
2020-11-13 20:00 | 44148.8333 | 0 | 13.8676 | 37.78
2020-11-13 20:30 | 44148.8542 | 0 | 13.5457 | 37.78
2020-11-13 21:00 | 44148.875 | 0 | 12.9828 | 37.78
2020-11-13 21:30 | 44148.8958 | 0 | 12.5651 | 37.78
2020-11-13 22:00 | 44148.9167 | 0 | 11.9109 | 37.78
2020-11-13 22:30 | 44148.9375 | 0 | 11.2767 | 37.78
2020-11-13 23:00 | 44148.9583 | 0 | 10.5347 | 37.78
2020-11-13 23:30 | 44148.9792 | 0 | 9.9949 | 37.78
2020-11-14 | 44149 | 0 | 9.4234 | 37.78
2020-11-14 00:30 | 44149.0208 | 0 | 9.0179 | 37.78
2020-11-14 01:00 | 44149.0417 | 0 | 8.8478 | 37.78
2020-11-14 01:30 | 44149.0625 | 0 | 8.5135 | 37.78
2020-11-14 02:00 | 44149.0833 | 0 | 8.397 | 37.78
2020-11-14 02:30 | 44149.1042 | 0 | 8.3003 | 37.78
2020-11-14 03:00 | 44149.125 | 0 | 8.2349 | 37.78
2020-11-14 03:30 | 44149.1458 | 0 | 8.3186 | 37.78
2020-11-14 04:00 | 44149.1667 | 0 | 8.393 | 37.78
2020-11-14 04:30 | 44149.1875 | 0 | 8.4864 | 37.78
2020-11-14 05:00 | 44149.2083 | 0 | 8.6402 | 37.78
2020-11-14 05:30 | 44149.2292 | 0 | 8.5798 | 37.78
2020-11-14 06:00 | 44149.25 | 0 | 8.6123 | 37.78
2020-11-14 06:30 | 44149.2708 | 0 | 8.6549 | 37.78
2020-11-14 07:00 | 44149.2917 | 0 | 8.6163 | 37.78
2020-11-14 07:30 | 44149.3125 | 0 | 8.7429 | 37.78
2020-11-14 08:00 | 44149.3333 | 0 | 9.0623 | 37.78
2020-11-14 08:30 | 44149.3542 | 0 | 9.0894 | 37.78
2020-11-14 09:00 | 44149.375 | 0 | 9.2273 | 37.78
2020-11-14 09:30 | 44149.3958 | 0 | 9.5503 | 37.78
2020-11-14 10:00 | 44149.4167 | 0 | 9.532 | 37.78
2020-11-14 10:30 | 44149.4375 | 0 | 9.7347 | 37.78
2020-11-14 11:00 | 44149.4583 | 0 | 9.8873 | 37.78
2020-11-14 11:30 | 44149.4792 | 0 | 10.0599 | 37.78
2020-11-14 12:00 | 44149.5 | 0 | 10.0944 | 37.78
2020-11-14 12:30 | 44149.5208 | 0 | 10.514 | 37.78
2020-11-14 13:00 | 44149.5417 | 0 | 10.9302 | 37.78
2020-11-14 13:30 | 44149.5625 | 0 | 11.7732 | 37.78
2020-11-14 14:00 | 44149.5833 | 0 | 12.1182 | 37.78
2020-11-14 14:30 | 44149.6042 | 0 | 12.5651 | 37.78
2020-11-14 15:00 | 44149.625 | 0 | 13.2773 | 37.78
2020-11-14 15:30 | 44149.6458 | 0 | 13.6735 | 37.78
2020-11-14 16:00 | 44149.6667 | 0 | 14.0673 | 37.78
2020-11-14 16:30 | 44149.6875 | 0 | 14.4533 | 37.78
2020-11-14 17:00 | 44149.7083 | 0 | 14.6989 | 37.78
2020-11-14 17:30 | 44149.7292 | 0 | 14.4113 | 37.78
2020-11-14 18:00 | 44149.75 | 0 | 14.3904 | 37.78
2020-11-14 18:30 | 44149.7708 | 0 | 14.9035 | 37.78
2020-11-14 19:00 | 44149.7917 | 0 | 14.8977 | 37.78
2020-11-14 19:30 | 44149.8125 | 0 | 14.5988 | 37.78
2020-11-14 20:00 | 44149.8333 | 0 | 14.3572 | 37.78
2020-11-14 20:30 | 44149.8542 | 0 | 13.7473 | 37.78
2020-11-14 21:00 | 44149.875 | 0 | 13.1637 | 37.78
2020-11-14 21:30 | 44149.8958 | 0 | 12.7708 | 37.78
2020-11-14 22:00 | 44149.9167 | 0 | 12.0785 | 37.78
2020-11-14 22:30 | 44149.9375 | 0 | 11.2875 | 37.78
2020-11-14 23:00 | 44149.9583 | 0 | 10.6906 | 37.78
2020-11-14 23:30 | 44149.9792 | 0 | 10.1423 | 37.78
2020-11-15 | 44150 | 0 | 9.4946 | 37.78
2020-11-15 00:30 | 44150.0208 | 0 | 9.1713 | 37.78
2020-11-15 01:00 | 44150.0417 | 0 | 8.8715 | 37.78
2020-11-15 01:30 | 44150.0625 | 0 | 8.7686 | 37.78
2020-11-15 02:00 | 44150.0833 | 0 | 8.6102 | 37.78
2020-11-15 02:30 | 44150.1042 | 0 | 8.4499 | 37.78
2020-11-15 03:00 | 44150.125 | 0 | 8.3118 | 37.78
2020-11-15 03:30 | 44150.1458 | 0 | 8.1747 | 37.78
2020-11-15 04:00 | 44150.1667 | 0 | 8.0661 | 37.78
2020-11-15 04:30 | 44150.1875 | 0 | 8.0621 | 37.78
2020-11-15 05:00 | 44150.2083 | 0 | 7.9179 | 37.78
2020-11-15 05:30 | 44150.2292 | 0 | 7.8604 | 37.78
2020-11-15 06:00 | 44150.25 | 0 | 7.9829 | 37.78
2020-11-15 06:30 | 44150.2708 | 0 | 8.1927 | 37.78
2020-11-15 07:00 | 44150.2917 | 0 | 7.769 | 37.78
2020-11-15 07:30 | 44150.3125 | 0 | 8.169 | 37.78
2020-11-15 08:00 | 44150.3333 | 0 | 8.3118 | 37.78
2020-11-15 08:30 | 44150.3542 | 0 | 8.5404 | 37.78
2020-11-15 09:00 | 44150.375 | 0 | 8.628 | 37.78
2020-11-15 09:30 | 44150.3958 | 0 | 8.751 | 37.78
2020-11-15 10:00 | 44150.4167 | 0 | 8.9168 | 37.78
2020-11-15 10:30 | 44150.4375 | 0 | 9.4175 | 37.78
2020-11-15 11:00 | 44150.4583 | 0 | 9.6436 | 37.78
2020-11-15 11:30 | 44150.4792 | 0 | 9.9084 | 37.78
2020-11-15 12:00 | 44150.5 | 0 | 9.9725 | 37.78
2020-11-15 12:30 | 44150.5208 | 0 | 10.2981 | 37.78
2020-11-15 13:00 | 44150.5417 | 0 | 10.8968 | 37.78
2020-11-15 13:30 | 44150.5625 | 0 | 11.4875 | 37.78
2020-11-15 14:00 | 44150.5833 | 0 | 12.1462 | 37.78
2020-11-15 14:30 | 44150.6042 | 0 | 12.7888 | 37.78
2020-11-15 15:00 | 44150.625 | 0 | 13.5728 | 37.78
2020-11-15 15:30 | 44150.6458 | 0 | 14.2193 | 37.78
2020-11-15 16:00 | 44150.6667 | 0 | 14.8201 | 37.78
2020-11-15 16:30 | 44150.6875 | 0 | 15.1936 | 37.78
2020-11-15 17:00 | 44150.7083 | 0 | 15.2674 | 37.78
2020-11-15 17:30 | 44150.7292 | 0 | 15.3304 | 37.78
2020-11-15 18:00 | 44150.75 | 0 | 15.5198 | 37.78
2020-11-15 18:30 | 44150.7708 | 0 | 15.9191 | 37.78
2020-11-15 19:00 | 44150.7917 | 0 | 15.9908 | 37.78
2020-11-15 19:30 | 44150.8125 | 0 | 15.4888 | 37.78
2020-11-15 20:00 | 44150.8333 | 0 | 15.0747 | 37.78
2020-11-15 20:30 | 44150.8542 | 0 | 14.357 | 37.78
2020-11-15 21:00 | 44150.875 | 0 | 13.5677 | 37.78
2020-11-15 21:30 | 44150.8958 | 0 | 12.8751 | 37.78
2020-11-15 22:00 | 44150.9167 | 0 | 12.1057 | 37.78
2020-11-15 22:30 | 44150.9375 | 0 | 11.2069 | 37.78
2020-11-15 23:00 | 44150.9583 | 0 | 10.4452 | 37.78
2020-11-15 23:30 | 44150.9792 | 0 | 9.9904 | 37.78
2020-11-16 | 44151 | 0 | 9.6658 | 37.78
2020-11-16 00:30 | 44151.0208 | 0 | 9.3878 | 37.78
2020-11-16 01:00 | 44151.0417 | 0 | 9.1491 | 37.78
2020-11-16 01:30 | 44151.0625 | 0 | 9.0078 | 37.78
2020-11-16 02:00 | 44151.0833 | 0 | 9.01 | 37.78
2020-11-16 02:30 | 44151.1042 | 0 | 8.8701 | 37.78
2020-11-16 03:00 | 44151.125 | 0 | 8.8437 | 37.78
2020-11-16 03:30 | 44151.1458 | 0 | 8.8295 | 37.78
2020-11-16 04:00 | 44151.1667 | 0 | 9.0387 | 37.78
2020-11-16 04:30 | 44151.1875 | 0 | 9.6015 | 37.78
2020-11-16 05:00 | 44151.2083 | 0 | 10.1019 | 37.78
2020-11-16 05:30 | 44151.2292 | 0 | 10.8514 | 37.78
2020-11-16 06:00 | 44151.25 | 0 | 11.6647 | 37.78
2020-11-16 06:30 | 44151.2708 | 0 | 12.385 | 37.78
2020-11-16 07:00 | 44151.2917 | 0 | 13.8713 | 37.78
2020-11-16 07:30 | 44151.3125 | 0 | 14.3483 | 37.78
2020-11-16 08:00 | 44151.3333 | 0 | 14.8703 | 37.78
2020-11-16 08:30 | 44151.3542 | 0 | 15.1906 | 37.78
2020-11-16 09:00 | 44151.375 | 0 | 13.7352 | 37.78
2020-11-16 09:30 | 44151.3958 | 0 | 14.2847 | 37.78
2020-11-16 10:00 | 44151.4167 | 0 | 15.371 | 37.78
2020-11-16 10:30 | 44151.4375 | 0 | 14.6451 | 37.78
2020-11-16 11:00 | 44151.4583 | 0 | 15.2911 | 37.78
2020-11-16 11:30 | 44151.4792 | 0 | 15.308 | 37.78
2020-11-16 12:00 | 44151.5 | 0 | 14.9189 | 37.78
2020-11-16 12:30 | 44151.5208 | 0 | 15.0306 | 37.78
2020-11-16 13:00 | 44151.5417 | 0 | 15.5716 | 37.78
2020-11-16 13:30 | 44151.5625 | 0 | 16.1022 | 37.78
2020-11-16 14:00 | 44151.5833 | 0 | 16.5478 | 37.78
2020-11-16 14:30 | 44151.6042 | 0 | 16.8165 | 37.78
2020-11-16 15:00 | 44151.625 | 0 | 17.0143 | 37.78
2020-11-16 15:30 | 44151.6458 | 0 | 17.6214 | 37.78
2020-11-16 16:00 | 44151.6667 | 0 | 17.8438 | 37.78
2020-11-16 16:30 | 44151.6875 | 0 | 18.4476 | 37.78
2020-11-16 17:00 | 44151.7083 | 0 | 18.249 | 37.78
2020-11-16 17:30 | 44151.7292 | 0 | 18.1152 | 37.78
2020-11-16 18:00 | 44151.75 | 0 | 17.9189 | 37.78
2020-11-16 18:30 | 44151.7708 | 0 | 18.6897 | 37.78
2020-11-16 19:00 | 44151.7917 | 0 | 18.3247 | 37.78
2020-11-16 19:30 | 44151.8125 | 0 | 17.9886 | 37.78
2020-11-16 20:00 | 44151.8333 | 0 | 17.6431 | 37.78
2020-11-16 20:30 | 44151.8542 | 0 | 16.6727 | 37.78
2020-11-16 21:00 | 44151.875 | 0 | 15.799 | 37.78
2020-11-16 21:30 | 44151.8958 | 0 | 15.105 | 37.78
2020-11-16 22:00 | 44151.9167 | 0 | 14.2737 | 37.78
2020-11-16 22:30 | 44151.9375 | 0 | 13.1767 | 37.78
2020-11-16 23:00 | 44151.9583 | 0 | 12.4209 | 37.78
2020-11-16 23:30 | 44151.9792 | 0 | 11.6547 | 37.78
2020-11-17 | 44152 | 0 | 10.9587 | 37.78
2020-11-17 00:30 | 44152.0208 | 0 | 10.4777 | 37.78
2020-11-17 01:00 | 44152.0417 | 0 | 10.07 | 37.78
2020-11-17 01:30 | 44152.0625 | 0 | 9.7306 | 37.78
2020-11-17 02:00 | 44152.0833 | 0 | 9.7289 | 37.78
2020-11-17 02:30 | 44152.1042 | 0 | 9.6087 | 37.78
2020-11-17 03:00 | 44152.125 | 0 | 9.4812 | 37.78
2020-11-17 03:30 | 44152.1458 | 0 | 9.4873 | 37.78
2020-11-17 04:00 | 44152.1667 | 0 | 9.5868 | 37.78
2020-11-17 04:30 | 44152.1875 | 0 | 10.1563 | 37.78
2020-11-17 05:00 | 44152.2083 | 0 | 10.5627 | 37.78
2020-11-17 05:30 | 44152.2292 | 0 | 10.7662 | 37.78
2020-11-17 06:00 | 44152.25 | 0 | 11.9308 | 37.78
2020-11-17 06:30 | 44152.2708 | 0 | 12.3255 | 37.78
2020-11-17 07:00 | 44152.2917 | 0 | 12.8519 | 37.78
2020-11-17 07:30 | 44152.3125 | 0 | 13.5954 | 37.78
2020-11-17 08:00 | 44152.3333 | 0 | 13.627 | 37.78
2020-11-17 08:30 | 44152.3542 | 0 | 13.8754 | 37.78
2020-11-17 09:00 | 44152.375 | 0 | 14.0472 | 37.78
2020-11-17 09:30 | 44152.3958 | 0 | 14.5784 | 37.78
2020-11-17 10:00 | 44152.4167 | 0 | 15.003 | 37.78
2020-11-17 10:30 | 44152.4375 | 0 | 15.6503 | 37.78
2020-11-17 11:00 | 44152.4583 | 0 | 15.3941 | 37.78
2020-11-17 11:30 | 44152.4792 | 0 | 16.5759 | 37.78
2020-11-17 12:00 | 44152.5 | 0 | 17.4236 | 37.78
2020-11-17 12:30 | 44152.5208 | 0 | 17.3444 | 37.78
2020-11-17 13:00 | 44152.5417 | 0 | 17.5014 | 37.78
2020-11-17 13:30 | 44152.5625 | 0 | 19.0547 | 37.78
2020-11-17 14:00 | 44152.5833 | 0 | 19.4362 | 37.78
2020-11-17 14:30 | 44152.6042 | 0 | 18.5649 | 37.78
2020-11-17 15:00 | 44152.625 | 0 | 17.6069 | 37.78
2020-11-17 15:30 | 44152.6458 | 0 | 17.3565 | 37.78
2020-11-17 16:00 | 44152.6667 | 0 | 17.5189 | 37.78
2020-11-17 16:30 | 44152.6875 | 0 | 17.7312 | 37.78
2020-11-17 17:00 | 44152.7083 | 0 | 17.4837 | 37.78
2020-11-17 17:30 | 44152.7292 | 0 | 17.3565 | 37.78
2020-11-17 18:00 | 44152.75 | 0 | 17.2449 | 37.78
2020-11-17 18:30 | 44152.7708 | 0 | 17.2266 | 37.78
2020-11-17 19:00 | 44152.7917 | 0 | 16.8179 | 37.78
2020-11-17 19:30 | 44152.8125 | 0 | 16.2956 | 37.78
2020-11-17 20:00 | 44152.8333 | 0 | 15.8677 | 37.78
2020-11-17 20:30 | 44152.8542 | 0 | 14.8989 | 37.78
2020-11-17 21:00 | 44152.875 | 0 | 14.1985 | 37.78
2020-11-17 21:30 | 44152.8958 | 0 | 13.6656 | 37.78
2020-11-17 22:00 | 44152.9167 | 0 | 12.8848 | 37.78
2020-11-17 22:30 | 44152.9375 | 0 | 11.9153 | 37.78
2020-11-17 23:00 | 44152.9583 | 0 | 11.296 | 37.78
2020-11-17 23:30 | 44152.9792 | 0 | 10.4719 | 37.78
2020-11-18 | 44153 | 0 | 9.9165 | 37.78
2020-11-18 00:30 | 44153.0208 | 0 | 9.6193 | 37.78
2020-11-18 01:00 | 44153.0417 | 0 | 9.398 | 37.78
2020-11-18 01:30 | 44153.0625 | 0 | 9.1994 | 37.78
2020-11-18 02:00 | 44153.0833 | 0 | 9.0183 | 37.78
2020-11-18 02:30 | 44153.1042 | 0 | 8.9188 | 37.78
2020-11-18 03:00 | 44153.125 | 0 | 9.0326 | 37.78
2020-11-18 03:30 | 44153.1458 | 0 | 9.0407 | 37.78
2020-11-18 04:00 | 44153.1667 | 0 | 9.2525 | 37.78
2020-11-18 04:30 | 44153.1875 | 0 | 9.6373 | 37.78
2020-11-18 05:00 | 44153.2083 | 0 | 10.1127 | 37.78
2020-11-18 05:30 | 44153.2292 | 0 | 10.451 | 37.78
2020-11-18 06:00 | 44153.25 | 0 | 10.8175 | 37.78
2020-11-18 06:30 | 44153.2708 | 0 | 11.2922 | 37.78
2020-11-18 07:00 | 44153.2917 | 0 | 11.5389 | 37.78
2020-11-18 07:30 | 44153.3125 | 0 | 12.2594 | 37.78
2020-11-18 08:00 | 44153.3333 | 0 | 11.9767 | 37.78
2020-11-18 08:30 | 44153.3542 | 0 | 11.9737 | 37.78
2020-11-18 09:00 | 44153.375 | 0 | 11.885 | 37.78
2020-11-18 09:30 | 44153.3958 | 0 | 12.1866 | 37.78
2020-11-18 10:00 | 44153.4167 | 0 | 12.3411 | 37.78
2020-11-18 10:30 | 44153.4375 | 0 | 12.8131 | 37.78
2020-11-18 11:00 | 44153.4583 | 0 | 12.5774 | 37.78
2020-11-18 11:30 | 44153.4792 | 0 | 12.7018 | 37.78
2020-11-18 12:00 | 44153.5 | 0 | 12.1326 | 37.78
2020-11-18 12:30 | 44153.5208 | 0 | 12.2525 | 37.78
2020-11-18 13:00 | 44153.5417 | 0 | 12.7532 | 37.78
2020-11-18 13:30 | 44153.5625 | 0 | 13.3303 | 37.78
2020-11-18 14:00 | 44153.5833 | 0 | 13.5341 | 37.78
2020-11-18 14:30 | 44153.6042 | 0 | 13.8279 | 37.78
2020-11-18 15:00 | 44153.625 | 0 | 14.0802 | 37.78
2020-11-18 15:30 | 44153.6458 | 0 | 14.6206 | 37.78
2020-11-18 16:00 | 44153.6667 | 0 | 15.0236 | 37.78
2020-11-18 16:30 | 44153.6875 | 0 | 15.1354 | 37.78
2020-11-18 17:00 | 44153.7083 | 0 | 14.6726 | 37.78
2020-11-18 17:30 | 44153.7292 | 0 | 14.5487 | 37.78
2020-11-18 18:00 | 44153.75 | 0 | 14.5271 | 37.78
2020-11-18 18:30 | 44153.7708 | 0 | 15.1006 | 37.78
2020-11-18 19:00 | 44153.7917 | 0 | 14.9268 | 37.78
2020-11-18 19:30 | 44153.8125 | 0 | 14.3689 | 37.78
2020-11-18 20:00 | 44153.8333 | 0 | 14.1175 | 37.78
2020-11-18 20:30 | 44153.8542 | 0 | 13.6432 | 37.78
2020-11-18 21:00 | 44153.875 | 0 | 13.0018 | 37.78
2020-11-18 21:30 | 44153.8958 | 0 | 12.6415 | 37.78
2020-11-18 22:00 | 44153.9167 | 0 | 12.1703 | 37.78
2020-11-18 22:30 | 44153.9375 | 0 | 11.3136 | 37.78
2020-11-18 23:00 | 44153.9583 | 0 | 10.6855 | 37.78
2020-11-18 23:30 | 44153.9792 | 0 | 10.1153 | 37.78
2020-11-19 | 44154 | 0 | 9.6078 | 37.78
2020-11-19 00:30 | 44154.0208 | 0 | 8.9861 | 37.78
2020-11-19 01:00 | 44154.0417 | 0 | 8.8884 | 37.78
2020-11-19 01:30 | 44154.0625 | 0 | 8.7882 | 37.78
2020-11-19 02:00 | 44154.0833 | 0 | 8.7131 | 37.78
2020-11-19 02:30 | 44154.1042 | 0 | 8.6393 | 37.78
2020-11-19 03:00 | 44154.125 | 0 | 8.6163 | 37.78
2020-11-19 03:30 | 44154.1458 | 0 | 8.7023 | 37.78
2020-11-19 04:00 | 44154.1667 | 0 | 8.9392 | 37.78
2020-11-19 04:30 | 44154.1875 | 0 | 9.0671 | 37.78
2020-11-19 05:00 | 44154.2083 | 0 | 9.4948 | 37.78
2020-11-19 05:30 | 44154.2292 | 0 | 9.8149 | 37.78
2020-11-19 06:00 | 44154.25 | 0 | 10.3256 | 37.78
2020-11-19 06:30 | 44154.2708 | 0 | 10.6869 | 37.78
2020-11-19 07:00 | 44154.2917 | 0 | 11.0506 | 37.78
2020-11-19 07:30 | 44154.3125 | 0 | 11.2836 | 37.78
2020-11-19 08:00 | 44154.3333 | 0 | 11.9477 | 37.78
2020-11-19 08:30 | 44154.3542 | 0 | 12.2476 | 37.78
2020-11-19 09:00 | 44154.375 | 0 | 12.1473 | 37.78
2020-11-19 09:30 | 44154.3958 | 0 | 11.6556 | 37.78
2020-11-19 10:00 | 44154.4167 | 0 | 12.2825 | 37.78
2020-11-19 10:30 | 44154.4375 | 0 | 12.7434 | 37.78
2020-11-19 11:00 | 44154.4583 | 0 | 12.4152 | 37.78
2020-11-19 11:30 | 44154.4792 | 0 | 12.1058 | 37.78
2020-11-19 12:00 | 44154.5 | 0 | 11.6292 | 37.78
2020-11-19 12:30 | 44154.5208 | 0 | 11.7159 | 37.78
2020-11-19 13:00 | 44154.5417 | 0 | 12.0285 | 37.78
2020-11-19 13:30 | 44154.5625 | 0 | 12.1879 | 37.78
2020-11-19 14:00 | 44154.5833 | 0 | 12.3236 | 37.78
2020-11-19 14:30 | 44154.6042 | 0 | 12.9175 | 37.78
2020-11-19 15:00 | 44154.625 | 0 | 13.0274 | 37.78
2020-11-19 15:30 | 44154.6458 | 0 | 13.6298 | 37.78
2020-11-19 16:00 | 44154.6667 | 0 | 14.1771 | 37.78
2020-11-19 16:30 | 44154.6875 | 0 | 14.6638 | 37.78
2020-11-19 17:00 | 44154.7083 | 0 | 14.7781 | 37.78
2020-11-19 17:30 | 44154.7292 | 0 | 14.8349 | 37.78
2020-11-19 18:00 | 44154.75 | 0 | 14.6137 | 37.78
2020-11-19 18:30 | 44154.7708 | 0 | 15.2128 | 37.78
2020-11-19 19:00 | 44154.7917 | 0 | 14.9698 | 37.78
2020-11-19 19:30 | 44154.8125 | 0 | 14.7152 | 37.78
2020-11-19 20:00 | 44154.8333 | 0 | 14.4898 | 37.78
2020-11-19 20:30 | 44154.8542 | 0 | 13.8327 | 37.78
2020-11-19 21:00 | 44154.875 | 0 | 13.2169 | 37.78
2020-11-19 21:30 | 44154.8958 | 0 | 12.7162 | 37.78
2020-11-19 22:00 | 44154.9167 | 0 | 11.9849 | 37.78
2020-11-19 22:30 | 44154.9375 | 0 | 11.0087 | 37.78
2020-11-19 23:00 | 44154.9583 | 0 | 10.4001 | 37.78
2020-11-19 23:30 | 44154.9792 | 0 | 9.9556 | 37.78
2020-11-20 | 44155 | 0 | 9.4629 | 37.78
2020-11-20 00:30 | 44155.0208 | 0 | 9.1423 | 37.78
2020-11-20 01:00 | 44155.0417 | 0 | 8.864 | 37.78
2020-11-20 01:30 | 44155.0625 | 0 | 8.617 | 37.78
2020-11-20 02:00 | 44155.0833 | 0 | 8.6529 | 37.78
2020-11-20 02:30 | 44155.1042 | 0 | 8.5615 | 37.78
2020-11-20 03:00 | 44155.125 | 0 | 8.4275 | 37.78
2020-11-20 03:30 | 44155.1458 | 0 | 8.5047 | 37.78
2020-11-20 04:00 | 44155.1667 | 0 | 8.6793 | 37.78
2020-11-20 04:30 | 44155.1875 | 0 | 9.0062 | 37.78
2020-11-20 05:00 | 44155.2083 | 0 | 9.4975 | 37.78
2020-11-20 05:30 | 44155.2292 | 0 | 9.603 | 37.78
2020-11-20 06:00 | 44155.25 | 0 | 10.0265 | 37.78
2020-11-20 06:30 | 44155.2708 | 0 | 10.4835 | 37.78
2020-11-20 07:00 | 44155.2917 | 0 | 11.069 | 37.78
2020-11-20 07:30 | 44155.3125 | 0 | 11.1156 | 37.78
2020-11-20 08:00 | 44155.3333 | 0 | 11.2814 | 37.78
2020-11-20 08:30 | 44155.3542 | 0 | 11.3071 | 37.78
2020-11-20 09:00 | 44155.375 | 0 | 11.4012 | 37.78
2020-11-20 09:30 | 44155.3958 | 0 | 11.1135 | 37.78
2020-11-20 10:00 | 44155.4167 | 0 | 11.3112 | 37.78
2020-11-20 10:30 | 44155.4375 | 0 | 11.2597 | 37.78
2020-11-20 11:00 | 44155.4583 | 0 | 11.2035 | 37.78
2020-11-20 11:30 | 44155.4792 | 0 | 11.3491 | 37.78
2020-11-20 12:00 | 44155.5 | 0 | 11.5189 | 37.78
2020-11-20 12:30 | 44155.5208 | 0 | 11.7117 | 37.78
2020-11-20 13:00 | 44155.5417 | 0 | 12.1156 | 37.78
2020-11-20 13:30 | 44155.5625 | 0 | 12.4427 | 37.78
2020-11-20 14:00 | 44155.5833 | 0 | 12.9908 | 37.78
2020-11-20 14:30 | 44155.6042 | 0 | 13.5471 | 37.78
2020-11-20 15:00 | 44155.625 | 0 | 13.7675 | 37.78
2020-11-20 15:30 | 44155.6458 | 0 | 14.3989 | 37.78
2020-11-20 16:00 | 44155.6667 | 0 | 14.8715 | 37.78
2020-11-20 16:30 | 44155.6875 | 0 | 15.4093 | 37.78
2020-11-20 17:00 | 44155.7083 | 0 | 15.3094 | 37.78
2020-11-20 17:30 | 44155.7292 | 0 | 14.9703 | 37.78
2020-11-20 18:00 | 44155.75 | 0 | 14.4916 | 37.78
2020-11-20 18:30 | 44155.7708 | 0 | 14.858 | 37.78
2020-11-20 19:00 | 44155.7917 | 0 | 14.7544 | 37.78
2020-11-20 19:30 | 44155.8125 | 0 | 14.5866 | 37.78
2020-11-20 20:00 | 44155.8333 | 0 | 14.1655 | 37.78
2020-11-20 20:30 | 44155.8542 | 0 | 13.5691 | 37.78
2020-11-20 21:00 | 44155.875 | 0 | 13.1729 | 37.78
2020-11-20 21:30 | 44155.8958 | 0 | 12.5731 | 37.78
2020-11-20 22:00 | 44155.9167 | 0 | 12.1514 | 37.78
2020-11-20 22:30 | 44155.9375 | 0 | 11.2727 | 37.78
2020-11-20 23:00 | 44155.9583 | 0 | 10.8103 | 37.78
2020-11-20 23:30 | 44155.9792 | 0 | 10.242 | 37.78
2020-11-21 | 44156 | 0 | 9.6748 | 37.78
2020-11-21 00:30 | 44156.0208 | 0 | 9.2498 | 37.78
2020-11-21 01:00 | 44156.0417 | 0 | 8.9635 | 37.78
2020-11-21 01:30 | 44156.0625 | 0 | 8.7503 | 37.78
2020-11-21 02:00 | 44156.0833 | 0 | 8.6468 | 37.78
2020-11-21 02:30 | 44156.1042 | 0 | 8.4634 | 37.78
2020-11-21 03:00 | 44156.125 | 0 | 8.4742 | 37.78
2020-11-21 03:30 | 44156.1458 | 0 | 8.4641 | 37.78
2020-11-21 04:00 | 44156.1667 | 0 | 8.46 | 37.78
2020-11-21 04:30 | 44156.1875 | 0 | 8.4681 | 37.78
2020-11-21 05:00 | 44156.2083 | 0 | 8.5047 | 37.78
2020-11-21 05:30 | 44156.2292 | 0 | 8.4986 | 37.78
2020-11-21 06:00 | 44156.25 | 0 | 8.3071 | 37.78
2020-11-21 06:30 | 44156.2708 | 0 | 8.2299 | 37.78
2020-11-21 07:00 | 44156.2917 | 0 | 8.2482 | 37.78
2020-11-21 07:30 | 44156.3125 | 0 | 8.3673 | 37.78
2020-11-21 08:00 | 44156.3333 | 0 | 8.9386 | 37.78
2020-11-21 08:30 | 44156.3542 | 0 | 9.2407 | 37.78
2020-11-21 09:00 | 44156.375 | 0 | 9.6477 | 37.78
2020-11-21 09:30 | 44156.3958 | 0 | 9.5671 | 37.78
2020-11-21 10:00 | 44156.4167 | 0 | 9.4873 | 37.78
2020-11-21 10:30 | 44156.4375 | 0 | 9.5543 | 37.78
2020-11-21 11:00 | 44156.4583 | 0 | 9.5503 | 37.78
2020-11-21 11:30 | 44156.4792 | 0 | 9.7452 | 37.78
2020-11-21 12:00 | 44156.5 | 0 | 9.871 | 37.78
2020-11-21 12:30 | 44156.5208 | 0 | 9.867 | 37.78
2020-11-21 13:00 | 44156.5417 | 0 | 10.4064 | 37.78
2020-11-21 13:30 | 44156.5625 | 0 | 10.6446 | 37.78
2020-11-21 14:00 | 44156.5833 | 0 | 11.0777 | 37.78
2020-11-21 14:30 | 44156.6042 | 0 | 11.712 | 37.78
2020-11-21 15:00 | 44156.625 | 0 | 12.1628 | 37.78
2020-11-21 15:30 | 44156.6458 | 0 | 12.3202 | 37.78
2020-11-21 16:00 | 44156.6667 | 0 | 13.0854 | 37.78
2020-11-21 16:30 | 44156.6875 | 0 | 13.5038 | 37.78
2020-11-21 17:00 | 44156.7083 | 0 | 13.56 | 37.78
2020-11-21 17:30 | 44156.7292 | 0 | 13.474 | 37.78
2020-11-21 18:00 | 44156.75 | 0 | 13.5925 | 37.78
2020-11-21 18:30 | 44156.7708 | 0 | 13.9171 | 37.78
2020-11-21 19:00 | 44156.7917 | 0 | 13.6824 | 37.78
2020-11-21 19:30 | 44156.8125 | 0 | 13.3251 | 37.78
2020-11-21 20:00 | 44156.8333 | 0 | 13.1422 | 37.78
2020-11-21 20:30 | 44156.8542 | 0 | 12.4251 | 37.78
2020-11-21 21:00 | 44156.875 | 0 | 11.9348 | 37.78
2020-11-21 21:30 | 44156.8958 | 0 | 11.7246 | 37.78
2020-11-21 22:00 | 44156.9167 | 0 | 11.2893 | 37.78
2020-11-21 22:30 | 44156.9375 | 0 | 10.6693 | 37.78
2020-11-21 23:00 | 44156.9583 | 0 | 10.0353 | 37.78
2020-11-21 23:30 | 44156.9792 | 0 | 9.6342 | 37.78
2020-11-22 | 44157 | 0 | 8.9769 | 37.78
2020-11-22 00:30 | 44157.0208 | 0 | 8.7395 | 37.78
2020-11-22 01:00 | 44157.0417 | 0 | 8.4768 | 37.78
2020-11-22 01:30 | 44157.0625 | 0 | 8.2509 | 37.78
2020-11-22 02:00 | 44157.0833 | 0 | 8.1968 | 37.78
2020-11-22 02:30 | 44157.1042 | 0 | 8.0215 | 37.78
2020-11-22 03:00 | 44157.125 | 0 | 8.066 | 37.78
2020-11-22 03:30 | 44157.1458 | 0 | 7.8096 | 37.78
2020-11-22 04:00 | 44157.1667 | 0 | 7.694 | 37.78
2020-11-22 04:30 | 44157.1875 | 0 | 7.5674 | 37.78
2020-11-22 05:00 | 44157.2083 | 0 | 7.4326 | 37.78
2020-11-22 05:30 | 44157.2292 | 0 | 7.2398 | 37.78
2020-11-22 06:00 | 44157.25 | 0 | 7.2547 | 37.78
2020-11-22 06:30 | 44157.2708 | 0 | 7.4388 | 37.78
2020-11-22 07:00 | 44157.2917 | 0 | 8.1027 | 37.78
2020-11-22 07:30 | 44157.3125 | 0 | 8.1622 | 37.78
2020-11-22 08:00 | 44157.3333 | 0 | 8.1832 | 37.78
2020-11-22 08:30 | 44157.3542 | 0 | 7.5987 | 37.78
2020-11-22 09:00 | 44157.375 | 0 | 7.4591 | 37.78
2020-11-22 09:30 | 44157.3958 | 0 | 7.6967 | 37.78
2020-11-22 10:00 | 44157.4167 | 0 | 7.924 | 37.78
2020-11-22 10:30 | 44157.4375 | 0 | 8.0174 | 37.78
2020-11-22 11:00 | 44157.4583 | 0 | 8.1632 | 37.78
2020-11-22 11:30 | 44157.4792 | 0 | 8.2489 | 37.78
2020-11-22 12:00 | 44157.5 | 0 | 8.1663 | 37.78
2020-11-22 12:30 | 44157.5208 | 0 | 8.433 | 37.78
2020-11-22 13:00 | 44157.5417 | 0 | 8.7016 | 37.78
2020-11-22 13:30 | 44157.5625 | 0 | 9.0853 | 37.78
2020-11-22 14:00 | 44157.5833 | 0 | 9.718 | 37.78
2020-11-22 14:30 | 44157.6042 | 0 | 10.4974 | 37.78
2020-11-22 15:00 | 44157.625 | 0 | 11.194 | 37.78
2020-11-22 15:30 | 44157.6458 | 0 | 12.1041 | 37.78
2020-11-22 16:00 | 44157.6667 | 0 | 13.1142 | 37.78
2020-11-22 16:30 | 44157.6875 | 0 | 13.7144 | 37.78
2020-11-22 17:00 | 44157.7083 | 0 | 13.4328 | 37.78
2020-11-22 17:30 | 44157.7292 | 0 | 13.7984 | 37.78
2020-11-22 18:00 | 44157.75 | 0 | 13.9992 | 37.78
2020-11-22 18:30 | 44157.7708 | 0 | 14.5019 | 37.78
2020-11-22 19:00 | 44157.7917 | 0 | 14.5237 | 37.78
2020-11-22 19:30 | 44157.8125 | 0 | 13.9734 | 37.78
2020-11-22 20:00 | 44157.8333 | 0 | 13.5463 | 37.78
2020-11-22 20:30 | 44157.8542 | 0 | 12.8743 | 37.78
2020-11-22 21:00 | 44157.875 | 0 | 12.1193 | 37.78
2020-11-22 21:30 | 44157.8958 | 0 | 11.7415 | 37.78
2020-11-22 22:00 | 44157.9167 | 0 | 11.071 | 37.78
2020-11-22 22:30 | 44157.9375 | 0 | 10.2308 | 37.78
2020-11-22 23:00 | 44157.9583 | 0 | 9.5746 | 37.78
2020-11-22 23:30 | 44157.9792 | 0 | 9.1247 | 37.78
2020-11-23 | 44158 | 0 | 8.7992 | 37.78
2020-11-23 00:30 | 44158.0208 | 0 | 8.4762 | 37.78
2020-11-23 01:00 | 44158.0417 | 0 | 8.3429 | 37.78
2020-11-23 01:30 | 44158.0625 | 0 | 8.3301 | 37.78
2020-11-23 02:00 | 44158.0833 | 0 | 8.2069 | 37.78
2020-11-23 02:30 | 44158.1042 | 0 | 8.215 | 37.78
2020-11-23 03:00 | 44158.125 | 0 | 8.1968 | 37.78
2020-11-23 03:30 | 44158.1458 | 0 | 8.2516 | 37.78
2020-11-23 04:00 | 44158.1667 | 0 | 8.4032 | 37.78
2020-11-23 04:30 | 44158.1875 | 0 | 8.7159 | 37.78
2020-11-23 05:00 | 44158.2083 | 0 | 9.1178 | 37.78
2020-11-23 05:30 | 44158.2292 | 0 | 9.5596 | 37.78
2020-11-23 06:00 | 44158.25 | 0 | 10.3086 | 37.78
2020-11-23 06:30 | 44158.2708 | 0 | 11.0098 | 37.78
2020-11-23 07:00 | 44158.2917 | 0 | 11.5965 | 37.78
2020-11-23 07:30 | 44158.3125 | 0 | 11.5724 | 37.78
2020-11-23 08:00 | 44158.3333 | 0 | 11.8715 | 37.78
2020-11-23 08:30 | 44158.3542 | 0 | 11.8735 | 37.78
2020-11-23 09:00 | 44158.375 | 0 | 11.8444 | 37.78
2020-11-23 09:30 | 44158.3958 | 0 | 11.9737 | 37.78
2020-11-23 10:00 | 44158.4167 | 0 | 12.2444 | 37.78
2020-11-23 10:30 | 44158.4375 | 0 | 12.5232 | 37.78
2020-11-23 11:00 | 44158.4583 | 0 | 13.0661 | 37.78
2020-11-23 11:30 | 44158.4792 | 0 | 13.2534 | 37.78
2020-11-23 12:00 | 44158.5 | 0 | 13.6773 | 37.78
2020-11-23 12:30 | 44158.5208 | 0 | 13.7888 | 37.78
2020-11-23 13:00 | 44158.5417 | 0 | 14.2699 | 37.78
2020-11-23 13:30 | 44158.5625 | 0 | 14.7646 | 37.78
2020-11-23 14:00 | 44158.5833 | 0 | 15.3522 | 37.78
2020-11-23 14:30 | 44158.6042 | 0 | 15.6735 | 37.78
2020-11-23 15:00 | 44158.625 | 0 | 15.8105 | 37.78
2020-11-23 15:30 | 44158.6458 | 0 | 16.4912 | 37.78
2020-11-23 16:00 | 44158.6667 | 0 | 17.0626 | 37.78
2020-11-23 16:30 | 44158.6875 | 0 | 17.4865 | 37.78
2020-11-23 17:00 | 44158.7083 | 0 | 17.5419 | 37.78
2020-11-23 17:30 | 44158.7292 | 0 | 17.7538 | 37.78
2020-11-23 18:00 | 44158.75 | 0 | 17.5954 | 37.78
2020-11-23 18:30 | 44158.7708 | 0 | 17.9942 | 37.78
2020-11-23 19:00 | 44158.7917 | 0 | 17.9289 | 37.78
2020-11-23 19:30 | 44158.8125 | 0 | 17.3816 | 37.78
2020-11-23 20:00 | 44158.8333 | 0 | 16.5537 | 37.78
2020-11-23 20:30 | 44158.8542 | 0 | 15.859 | 37.78
2020-11-23 21:00 | 44158.875 | 0 | 15.1416 | 37.78
2020-11-23 21:30 | 44158.8958 | 0 | 14.5658 | 37.78
2020-11-23 22:00 | 44158.9167 | 0 | 13.7523 | 37.78
2020-11-23 22:30 | 44158.9375 | 0 | 12.8507 | 37.78
2020-11-23 23:00 | 44158.9583 | 0 | 11.9629 | 37.78
2020-11-23 23:30 | 44158.9792 | 0 | 11.2594 | 37.78
2020-11-24 | 44159 | 0 | 10.5954 | 37.78
2020-11-24 00:30 | 44159.0208 | 0 | 10.0991 | 37.78
2020-11-24 01:00 | 44159.0417 | 0 | 9.8517 | 37.78
2020-11-24 01:30 | 44159.0625 | 0 | 9.4751 | 37.78
2020-11-24 02:00 | 44159.0833 | 0 | 9.4975 | 37.78
2020-11-24 02:30 | 44159.1042 | 0 | 9.3993 | 37.78
2020-11-24 03:00 | 44159.125 | 0 | 9.168 | 37.78
2020-11-24 03:30 | 44159.1458 | 0 | 9.2275 | 37.78
2020-11-24 04:00 | 44159.1667 | 0 | 9.6133 | 37.78
2020-11-24 04:30 | 44159.1875 | 0 | 10.0831 | 37.78
2020-11-24 05:00 | 44159.2083 | 0 | 10.3434 | 37.78
2020-11-24 05:30 | 44159.2292 | 0 | 10.7372 | 37.78
2020-11-24 06:00 | 44159.25 | 0 | 11.3459 | 37.78
2020-11-24 06:30 | 44159.2708 | 0 | 11.8336 | 37.78
2020-11-24 07:00 | 44159.2917 | 0 | 12.7357 | 37.78
2020-11-24 07:30 | 44159.3125 | 0 | 12.3864 | 37.78
2020-11-24 08:00 | 44159.3333 | 0 | 12.4264 | 37.78
2020-11-24 08:30 | 44159.3542 | 0 | 12.9801 | 37.78
2020-11-24 09:00 | 44159.375 | 0 | 13.376 | 37.78
2020-11-24 09:30 | 44159.3958 | 0 | 13.5351 | 37.78
2020-11-24 10:00 | 44159.4167 | 0 | 14.0466 | 37.78
2020-11-24 10:30 | 44159.4375 | 0 | 14.5039 | 37.78
2020-11-24 11:00 | 44159.4583 | 0 | 14.5785 | 37.78
2020-11-24 11:30 | 44159.4792 | 0 | 14.77 | 37.78
2020-11-24 12:00 | 44159.5 | 0 | 15.397 | 37.78
2020-11-24 12:30 | 44159.5208 | 0 | 15.767 | 37.78
2020-11-24 13:00 | 44159.5417 | 0 | 15.7774 | 37.78
2020-11-24 13:30 | 44159.5625 | 0 | 16.3456 | 37.78
2020-11-24 14:00 | 44159.5833 | 0 | 17.2406 | 37.78
2020-11-24 14:30 | 44159.6042 | 0 | 17.7043 | 37.78
2020-11-24 15:00 | 44159.625 | 0 | 17.5366 | 37.78
2020-11-24 15:30 | 44159.6458 | 0 | 17.91 | 37.78
2020-11-24 16:00 | 44159.6667 | 0 | 17.5617 | 37.78
2020-11-24 16:30 | 44159.6875 | 0 | 17.4723 | 37.78
2020-11-24 17:00 | 44159.7083 | 0 | 16.9935 | 37.78
2020-11-24 17:30 | 44159.7292 | 0 | 16.5442 | 37.78
2020-11-24 18:00 | 44159.75 | 0 | 16.4341 | 37.78
2020-11-24 18:30 | 44159.7708 | 0 | 16.7616 | 37.78
2020-11-24 19:00 | 44159.7917 | 0 | 16.3656 | 37.78
2020-11-24 19:30 | 44159.8125 | 0 | 16.0132 | 37.78
2020-11-24 20:00 | 44159.8333 | 0 | 15.8658 | 37.78
2020-11-24 20:30 | 44159.8542 | 0 | 15.3669 | 37.78
2020-11-24 21:00 | 44159.875 | 0 | 14.4524 | 37.78
2020-11-24 21:30 | 44159.8958 | 0 | 13.806 | 37.78
2020-11-24 22:00 | 44159.9167 | 0 | 13.087 | 37.78
2020-11-24 22:30 | 44159.9375 | 0 | 12.1288 | 37.78
2020-11-24 23:00 | 44159.9583 | 0 | 11.6024 | 37.78
2020-11-24 23:30 | 44159.9792 | 0 | 10.9995 | 37.78
2020-11-25 | 44160 | 0 | 10.3887 | 37.78
2020-11-25 00:30 | 44160.0208 | 0 | 9.8911 | 37.78
2020-11-25 01:00 | 44160.0417 | 0 | 9.7411 | 37.78
2020-11-25 01:30 | 44160.0625 | 0 | 9.536 | 37.78
2020-11-25 02:00 | 44160.0833 | 0 | 9.5482 | 37.78
2020-11-25 02:30 | 44160.1042 | 0 | 9.3493 | 37.78
2020-11-25 03:00 | 44160.125 | 0 | 9.2244 | 37.78
2020-11-25 03:30 | 44160.1458 | 0 | 9.3012 | 37.78
2020-11-25 04:00 | 44160.1667 | 0 | 9.4591 | 37.78
2020-11-25 04:30 | 44160.1875 | 0 | 10.0883 | 37.78
2020-11-25 05:00 | 44160.2083 | 0 | 10.4756 | 37.78
2020-11-25 05:30 | 44160.2292 | 0 | 10.7826 | 37.78
2020-11-25 06:00 | 44160.25 | 0 | 11.784 | 37.78
2020-11-25 06:30 | 44160.2708 | 0 | 12.6336 | 37.78
2020-11-25 07:00 | 44160.2917 | 0 | 13.2189 | 37.78
2020-11-25 07:30 | 44160.3125 | 0 | 13.8237 | 37.78
2020-11-25 08:00 | 44160.3333 | 0 | 13.9457 | 37.78
2020-11-25 08:30 | 44160.3542 | 0 | 14.0486 | 37.78
2020-11-25 09:00 | 44160.375 | 0 | 14.5757 | 37.78
2020-11-25 09:30 | 44160.3958 | 0 | 14.4201 | 37.78
2020-11-25 10:00 | 44160.4167 | 0 | 14.1959 | 37.78
2020-11-25 10:30 | 44160.4375 | 0 | 14.0619 | 37.78
2020-11-25 11:00 | 44160.4583 | 0 | 13.0141 | 37.78
2020-11-25 11:30 | 44160.4792 | 0 | 13.4522 | 37.78
2020-11-25 12:00 | 44160.5 | 0 | 13.409 | 37.78
2020-11-25 12:30 | 44160.5208 | 0 | 13.3644 | 37.78
2020-11-25 13:00 | 44160.5417 | 0 | 12.942 | 37.78
2020-11-25 13:30 | 44160.5625 | 0 | 12.7611 | 37.78
2020-11-25 14:00 | 44160.5833 | 0 | 13.6611 | 37.78
2020-11-25 14:30 | 44160.6042 | 0 | 13.2553 | 37.78
2020-11-25 15:00 | 44160.625 | 0 | 14.3809 | 37.78
2020-11-25 15:30 | 44160.6458 | 0 | 13.8276 | 37.78
2020-11-25 16:00 | 44160.6667 | 0 | 13.7164 | 37.78
2020-11-25 16:30 | 44160.6875 | 0 | 13.9194 | 37.78
2020-11-25 17:00 | 44160.7083 | 0 | 14.2442 | 37.78
2020-11-25 17:30 | 44160.7292 | 0 | 14.2746 | 37.78
2020-11-25 18:00 | 44160.75 | 0 | 14.5122 | 37.78
2020-11-25 18:30 | 44160.7708 | 0 | 14.9445 | 37.78
2020-11-25 19:00 | 44160.7917 | 0 | 14.9588 | 37.78
2020-11-25 19:30 | 44160.8125 | 0 | 14.8066 | 37.78
2020-11-25 20:00 | 44160.8333 | 0 | 14.6996 | 37.78
2020-11-25 20:30 | 44160.8542 | 0 | 14.017 | 37.78
2020-11-25 21:00 | 44160.875 | 0 | 13.5265 | 37.78
2020-11-25 21:30 | 44160.8958 | 0 | 12.966 | 37.78
2020-11-25 22:00 | 44160.9167 | 0 | 12.4441 | 37.78
2020-11-25 22:30 | 44160.9375 | 0 | 11.2305 | 37.78
2020-11-25 23:00 | 44160.9583 | 0 | 10.6119 | 37.78
2020-11-25 23:30 | 44160.9792 | 0 | 10.0312 | 37.78
2020-11-26 | 44161 | 0 | 9.5767 | 37.78
2020-11-26 00:30 | 44161.0208 | 0 | 9.1604 | 37.78
2020-11-26 01:00 | 44161.0417 | 0 | 8.8417 | 37.78
2020-11-26 01:30 | 44161.0625 | 0 | 8.7355 | 37.78
2020-11-26 02:00 | 44161.0833 | 0 | 8.7129 | 37.78
2020-11-26 02:30 | 44161.1042 | 0 | 8.59 | 37.78
2020-11-26 03:00 | 44161.125 | 0 | 8.6833 | 37.78
2020-11-26 03:30 | 44161.1458 | 0 | 8.6732 | 37.78
2020-11-26 04:00 | 44161.1667 | 0 | 8.9862 | 37.78
2020-11-26 04:30 | 44161.1875 | 0 | 9.2275 | 37.78
2020-11-26 05:00 | 44161.2083 | 0 | 9.534 | 37.78
2020-11-26 05:30 | 44161.2292 | 0 | 9.8966 | 37.78
2020-11-26 06:00 | 44161.25 | 0 | 10.6 | 37.78
2020-11-26 06:30 | 44161.2708 | 0 | 11.1473 | 37.78
2020-11-26 07:00 | 44161.2917 | 0 | 11.6146 | 37.78
2020-11-26 07:30 | 44161.3125 | 0 | 12.8799 | 37.78
2020-11-26 08:00 | 44161.3333 | 0 | 12.7479 | 37.78
2020-11-26 08:30 | 44161.3542 | 0 | 12.0286 | 37.78
2020-11-26 09:00 | 44161.375 | 0 | 12.3012 | 37.78
2020-11-26 09:30 | 44161.3958 | 0 | 12.3668 | 37.78
2020-11-26 10:00 | 44161.4167 | 0 | 12.5367 | 37.78
2020-11-26 10:30 | 44161.4375 | 0 | 12.4359 | 37.78
2020-11-26 11:00 | 44161.4583 | 0 | 12.6179 | 37.78
2020-11-26 11:30 | 44161.4792 | 0 | 12.691 | 37.78
2020-11-26 12:00 | 44161.5 | 0 | 12.8677 | 37.78
2020-11-26 12:30 | 44161.5208 | 0 | 13.0623 | 37.78
2020-11-26 13:00 | 44161.5417 | 0 | 13.382 | 37.78
2020-11-26 13:30 | 44161.5625 | 0 | 13.9828 | 37.78
2020-11-26 14:00 | 44161.5833 | 0 | 14.2097 | 37.78
2020-11-26 14:30 | 44161.6042 | 0 | 14.4594 | 37.78
2020-11-26 15:00 | 44161.625 | 0 | 14.766 | 37.78
2020-11-26 15:30 | 44161.6458 | 0 | 15.4867 | 37.78
2020-11-26 16:00 | 44161.6667 | 0 | 16.0978 | 37.78
2020-11-26 16:30 | 44161.6875 | 0 | 16.4592 | 37.78
2020-11-26 17:00 | 44161.7083 | 0 | 16.2825 | 37.78
2020-11-26 17:30 | 44161.7292 | 0 | 16.2318 | 37.78
2020-11-26 18:00 | 44161.75 | 0 | 16.0504 | 37.78
2020-11-26 18:30 | 44161.7708 | 0 | 16.3353 | 37.78
2020-11-26 19:00 | 44161.7917 | 0 | 16.2439 | 37.78
2020-11-26 19:30 | 44161.8125 | 0 | 15.9868 | 37.78
2020-11-26 20:00 | 44161.8333 | 0 | 15.707 | 37.78
2020-11-26 20:30 | 44161.8542 | 0 | 15.172 | 37.78
2020-11-26 21:00 | 44161.875 | 0 | 14.5051 | 37.78
2020-11-26 21:30 | 44161.8958 | 0 | 14.0289 | 37.78
2020-11-26 22:00 | 44161.9167 | 0 | 13.2468 | 37.78
2020-11-26 22:30 | 44161.9375 | 0 | 12.2291 | 37.78
2020-11-26 23:00 | 44161.9583 | 0 | 11.5268 | 37.78
2020-11-26 23:30 | 44161.9792 | 0 | 10.8778 | 37.78
2020-11-27 | 44162 | 0 | 10.2614 | 37.78
2020-11-27 00:30 | 44162.0208 | 0 | 9.7118 | 37.78
2020-11-27 01:00 | 44162.0417 | 0 | 9.5075 | 37.78
2020-11-27 01:30 | 44162.0625 | 0 | 9.3554 | 37.78
2020-11-27 02:00 | 44162.0833 | 0 | 9.2938 | 37.78
2020-11-27 02:30 | 44162.1042 | 0 | 9.1503 | 37.78
2020-11-27 03:00 | 44162.125 | 0 | 9.0447 | 37.78
2020-11-27 03:30 | 44162.1458 | 0 | 9.2336 | 37.78
2020-11-27 04:00 | 44162.1667 | 0 | 9.3973 | 37.78
2020-11-27 04:30 | 44162.1875 | 0 | 9.8521 | 37.78
2020-11-27 05:00 | 44162.2083 | 0 | 10.1533 | 37.78
2020-11-27 05:30 | 44162.2292 | 0 | 10.5089 | 37.78
2020-11-27 06:00 | 44162.25 | 0 | 11.2926 | 37.78
2020-11-27 06:30 | 44162.2708 | 0 | 11.9799 | 37.78
2020-11-27 07:00 | 44162.2917 | 0 | 12.6464 | 37.78
2020-11-27 07:30 | 44162.3125 | 0 | 13.1517 | 37.78
2020-11-27 08:00 | 44162.3333 | 0 | 13.3422 | 37.78
2020-11-27 08:30 | 44162.3542 | 0 | 13.5687 | 37.78
2020-11-27 09:00 | 44162.375 | 0 | 14.3101 | 37.78
2020-11-27 09:30 | 44162.3958 | 0 | 13.8248 | 37.78
2020-11-27 10:00 | 44162.4167 | 0 | 14.0953 | 37.78
2020-11-27 10:30 | 44162.4375 | 0 | 14.172 | 37.78
2020-11-27 11:00 | 44162.4583 | 0 | 12.8257 | 37.78
2020-11-27 11:30 | 44162.4792 | 0 | 12.8156 | 37.78
2020-11-27 12:00 | 44162.5 | 0 | 12.9252 | 37.78
2020-11-27 12:30 | 44162.5208 | 0 | 13.3773 | 37.78
2020-11-27 13:00 | 44162.5417 | 0 | 13.2879 | 37.78
2020-11-27 13:30 | 44162.5625 | 0 | 13.5404 | 37.78
2020-11-27 14:00 | 44162.5833 | 0 | 13.8785 | 37.78
2020-11-27 14:30 | 44162.6042 | 0 | 14.3923 | 37.78
2020-11-27 15:00 | 44162.625 | 0 | 14.4971 | 37.78
2020-11-27 15:30 | 44162.6458 | 0 | 15.0328 | 37.78
2020-11-27 16:00 | 44162.6667 | 0 | 15.44 | 37.78
2020-11-27 16:30 | 44162.6875 | 0 | 15.7466 | 37.78
2020-11-27 17:00 | 44162.7083 | 0 | 15.6937 | 37.78
2020-11-27 17:30 | 44162.7292 | 0 | 15.5882 | 37.78
2020-11-27 18:00 | 44162.75 | 0 | 15.2065 | 37.78
2020-11-27 18:30 | 44162.7708 | 0 | 15.3304 | 37.78
2020-11-27 19:00 | 44162.7917 | 0 | 15.1984 | 37.78
2020-11-27 19:30 | 44162.8125 | 0 | 15.0151 | 37.78
2020-11-27 20:00 | 44162.8333 | 0 | 14.8146 | 37.78
2020-11-27 20:30 | 44162.8542 | 0 | 14.2076 | 37.78
2020-11-27 21:00 | 44162.875 | 0 | 13.4361 | 37.78
2020-11-27 21:30 | 44162.8958 | 0 | 13.1769 | 37.78
2020-11-27 22:00 | 44162.9167 | 0 | 12.5836 | 37.78
2020-11-27 22:30 | 44162.9375 | 0 | 11.5308 | 37.78
2020-11-27 23:00 | 44162.9583 | 0 | 10.9648 | 37.78
2020-11-27 23:30 | 44162.9792 | 0 | 10.5532 | 37.78
2020-11-28 | 44163 | 0 | 9.7597 | 37.78
2020-11-28 00:30 | 44163.0208 | 0 | 9.4213 | 37.78
2020-11-28 01:00 | 44163.0417 | 0 | 9.1679 | 37.78
2020-11-28 01:30 | 44163.0625 | 0 | 8.9412 | 37.78
2020-11-28 02:00 | 44163.0833 | 0 | 8.7354 | 37.78
2020-11-28 02:30 | 44163.1042 | 0 | 8.6245 | 37.78
2020-11-28 03:00 | 44163.125 | 0 | 8.5429 | 37.78
2020-11-28 03:30 | 44163.1458 | 0 | 8.4762 | 37.78
2020-11-28 04:00 | 44163.1667 | 0 | 8.4377 | 37.78
2020-11-28 04:30 | 44163.1875 | 0 | 8.5412 | 37.78
2020-11-28 05:00 | 44163.2083 | 0 | 8.6021 | 37.78
2020-11-28 05:30 | 44163.2292 | 0 | 8.5311 | 37.78
2020-11-28 06:00 | 44163.25 | 0 | 8.5128 | 37.78
2020-11-28 06:30 | 44163.2708 | 0 | 8.6163 | 37.78
2020-11-28 07:00 | 44163.2917 | 0 | 8.9843 | 37.78
2020-11-28 07:30 | 44163.3125 | 0 | 9.1022 | 37.78
2020-11-28 08:00 | 44163.3333 | 0 | 9.0244 | 37.78
2020-11-28 08:30 | 44163.3542 | 0 | 9.1077 | 37.78
2020-11-28 09:00 | 44163.375 | 0 | 9.1753 | 37.78
2020-11-28 09:30 | 44163.3958 | 0 | 9.0373 | 37.78
2020-11-28 10:00 | 44163.4167 | 0 | 9.1158 | 37.78
2020-11-28 10:30 | 44163.4375 | 0 | 9.13 | 37.78
2020-11-28 11:00 | 44163.4583 | 0 | 9.0264 | 37.78
2020-11-28 11:30 | 44163.4792 | 0 | 9.1158 | 37.78
2020-11-28 12:00 | 44163.5 | 0 | 9.2782 | 37.78
2020-11-28 12:30 | 44163.5208 | 0 | 9.7204 | 37.78
2020-11-28 13:00 | 44163.5417 | 0 | 10.1538 | 37.78
2020-11-28 13:30 | 44163.5625 | 0 | 10.6405 | 37.78
2020-11-28 14:00 | 44163.5833 | 0 | 10.9598 | 37.78
2020-11-28 14:30 | 44163.6042 | 0 | 11.5345 | 37.78
2020-11-28 15:00 | 44163.625 | 0 | 11.9753 | 37.78
2020-11-28 15:30 | 44163.6458 | 0 | 12.5245 | 37.78
2020-11-28 16:00 | 44163.6667 | 0 | 12.7966 | 37.78
2020-11-28 16:30 | 44163.6875 | 0 | 13.4265 | 37.78
2020-11-28 17:00 | 44163.7083 | 0 | 13.474 | 37.78
2020-11-28 17:30 | 44163.7292 | 0 | 13.5004 | 37.78
2020-11-28 18:00 | 44163.75 | 0 | 13.3353 | 37.78
2020-11-28 18:30 | 44163.7708 | 0 | 13.5492 | 37.78
2020-11-28 19:00 | 44163.7917 | 0 | 13.5376 | 37.78
2020-11-28 19:30 | 44163.8125 | 0 | 13.313 | 37.78
2020-11-28 20:00 | 44163.8333 | 0 | 12.9741 | 37.78
2020-11-28 20:30 | 44163.8542 | 0 | 12.4717 | 37.78
2020-11-28 21:00 | 44163.875 | 0 | 12.082 | 37.78
2020-11-28 21:30 | 44163.8958 | 0 | 11.8444 | 37.78
2020-11-28 22:00 | 44163.9167 | 0 | 11.4427 | 37.78
2020-11-28 22:30 | 44163.9375 | 0 | 10.6589 | 37.78
2020-11-28 23:00 | 44163.9583 | 0 | 10.0588 | 37.78
2020-11-28 23:30 | 44163.9792 | 0 | 9.5458 | 37.78
2020-11-29 | 44164 | 0 | 9.0467 | 37.78
2020-11-29 00:30 | 44164.0208 | 0 | 8.587 | 37.78
2020-11-29 01:00 | 44164.0417 | 0 | 8.4641 | 37.78
2020-11-29 01:30 | 44164.0625 | 0 | 8.3118 | 37.78
2020-11-29 02:00 | 44164.0833 | 0 | 8.2787 | 37.78
2020-11-29 02:30 | 44164.1042 | 0 | 8.0912 | 37.78
2020-11-29 03:00 | 44164.125 | 0 | 8.0613 | 37.78
2020-11-29 03:30 | 44164.1458 | 0 | 7.8753 | 37.78
2020-11-29 04:00 | 44164.1667 | 0 | 7.7467 | 37.78
2020-11-29 04:30 | 44164.1875 | 0 | 7.6445 | 37.78
2020-11-29 05:00 | 44164.2083 | 0 | 7.5972 | 37.78
2020-11-29 05:30 | 44164.2292 | 0 | 7.4896 | 37.78
2020-11-29 06:00 | 44164.25 | 0 | 7.4185 | 37.78
2020-11-29 06:30 | 44164.2708 | 0 | 7.4185 | 37.78
2020-11-29 07:00 | 44164.2917 | 0 | 7.3393 | 37.78
2020-11-29 07:30 | 44164.3125 | 0 | 7.4733 | 37.78
2020-11-29 08:00 | 44164.3333 | 0 | 7.5444 | 37.78
2020-11-29 08:30 | 44164.3542 | 0 | 7.7867 | 37.78
2020-11-29 09:00 | 44164.375 | 0 | 8.0946 | 37.78
2020-11-29 09:30 | 44164.3958 | 0 | 8.5028 | 37.78
2020-11-29 10:00 | 44164.4167 | 0 | 8.6874 | 37.78
2020-11-29 10:30 | 44164.4375 | 0 | 8.9958 | 37.78
2020-11-29 11:00 | 44164.4583 | 0 | 9.1787 | 37.78
2020-11-29 11:30 | 44164.4792 | 0 | 9.5781 | 37.78
2020-11-29 12:00 | 44164.5 | 0 | 10.0111 | 37.78
2020-11-29 12:30 | 44164.5208 | 0 | 10.1895 | 37.78
2020-11-29 13:00 | 44164.5417 | 0 | 11.003 | 37.78
2020-11-29 13:30 | 44164.5625 | 0 | 11.5934 | 37.78
2020-11-29 14:00 | 44164.5833 | 0 | 11.9296 | 37.78
2020-11-29 14:30 | 44164.6042 | 0 | 12.4317 | 37.78
2020-11-29 15:00 | 44164.625 | 0 | 12.9548 | 37.78
2020-11-29 15:30 | 44164.6458 | 0 | 13.5498 | 37.78
2020-11-29 16:00 | 44164.6667 | 0 | 14.1846 | 37.78
2020-11-29 16:30 | 44164.6875 | 0 | 15.0166 | 37.78
2020-11-29 17:00 | 44164.7083 | 0 | 15.0745 | 37.78
2020-11-29 17:30 | 44164.7292 | 0 | 15.182 | 37.78
2020-11-29 18:00 | 44164.75 | 0 | 15.2024 | 37.78
2020-11-29 18:30 | 44164.7708 | 0 | 15.8192 | 37.78
2020-11-29 19:00 | 44164.7917 | 0 | 16.024 | 37.78
2020-11-29 19:30 | 44164.8125 | 0 | 15.8115 | 37.78
2020-11-29 20:00 | 44164.8333 | 0 | 15.4132 | 37.78
2020-11-29 20:30 | 44164.8542 | 0 | 14.5768 | 37.78
2020-11-29 21:00 | 44164.875 | 0 | 13.8714 | 37.78
2020-11-29 21:30 | 44164.8958 | 0 | 13.1968 | 37.78
2020-11-29 22:00 | 44164.9167 | 0 | 12.5571 | 37.78
2020-11-29 22:30 | 44164.9375 | 0 | 11.4156 | 37.78
2020-11-29 23:00 | 44164.9583 | 0 | 10.884 | 37.78
2020-11-29 23:30 | 44164.9792 | 0 | 10.2748 | 37.78
2020-11-30 | 44165 | 0 | 9.7299 | 37.78
2020-11-30 00:30 | 44165.0208 | 0 | 9.4508 | 37.78
2020-11-30 01:00 | 44165.0417 | 0 | 9.1638 | 37.78
2020-11-30 01:30 | 44165.0625 | 0 | 9.1307 | 37.78
2020-11-30 02:00 | 44165.0833 | 0 | 9.0041 | 37.78
2020-11-30 02:30 | 44165.1042 | 0 | 8.9513 | 37.78
2020-11-30 03:00 | 44165.125 | 0 | 8.7778 | 37.78
2020-11-30 03:30 | 44165.1458 | 0 | 8.8106 | 37.78
2020-11-30 04:00 | 44165.1667 | 0 | 8.9977 | 37.78
2020-11-30 04:30 | 44165.1875 | 0 | 9.335 | 37.78
2020-11-30 05:00 | 44165.2083 | 0 | 9.8463 | 37.78
2020-11-30 05:30 | 44165.2292 | 0 | 10.4011 | 37.78
2020-11-30 06:00 | 44165.25 | 0 | 11.3028 | 37.78
2020-11-30 06:30 | 44165.2708 | 0 | 12.1602 | 37.78
2020-11-30 07:00 | 44165.2917 | 0 | 12.933 | 37.78
2020-11-30 07:30 | 44165.3125 | 0 | 13.3198 | 37.78
2020-11-30 08:00 | 44165.3333 | 0 | 13.2983 | 37.78
2020-11-30 08:30 | 44165.3542 | 0 | 13.7459 | 37.78
2020-11-30 09:00 | 44165.375 | 0 | 14.3655 | 37.78
2020-11-30 09:30 | 44165.3958 | 0 | 15.1269 | 37.78
2020-11-30 10:00 | 44165.4167 | 0 | 14.6986 | 37.78
2020-11-30 10:30 | 44165.4375 | 0 | 15.0373 | 37.78
2020-11-30 11:00 | 44165.4583 | 0 | 15.0069 | 37.78
2020-11-30 11:30 | 44165.4792 | 0 | 15.5098 | 37.78
2020-11-30 12:00 | 44165.5 | 0 | 15.7814 | 37.78
2020-11-30 12:30 | 44165.5208 | 0 | 16.1157 | 37.78
2020-11-30 13:00 | 44165.5417 | 0 | 16.9308 | 37.78
2020-11-30 13:30 | 44165.5625 | 0 | 16.8332 | 37.78
2020-11-30 14:00 | 44165.5833 | 0 | 16.9789 | 37.78
2020-11-30 14:30 | 44165.6042 | 0 | 17.0775 | 37.78
2020-11-30 15:00 | 44165.625 | 0 | 17.1569 | 37.78
2020-11-30 15:30 | 44165.6458 | 0 | 17.8077 | 37.78
2020-11-30 16:00 | 44165.6667 | 0 | 18.0637 | 37.78
2020-11-30 16:30 | 44165.6875 | 0 | 18.4236 | 37.78
2020-11-30 17:00 | 44165.7083 | 0 | 18.0695 | 37.78
2020-11-30 17:30 | 44165.7292 | 0 | 17.8357 | 37.78
2020-11-30 18:00 | 44165.75 | 0 | 17.4607 | 37.78
2020-11-30 18:30 | 44165.7708 | 0 | 17.837 | 37.78
2020-11-30 19:00 | 44165.7917 | 0 | 17.7017 | 37.78
2020-11-30 19:30 | 44165.8125 | 0 | 17.4835 | 37.78
2020-11-30 20:00 | 44165.8333 | 0 | 16.9525 | 37.78
2020-11-30 20:30 | 44165.8542 | 0 | 16.1689 | 37.78
2020-11-30 21:00 | 44165.875 | 0 | 15.3211 | 37.78
2020-11-30 21:30 | 44165.8958 | 0 | 14.8336 | 37.78
2020-11-30 22:00 | 44165.9167 | 0 | 14.0927 | 37.78
2020-11-30 22:30 | 44165.9375 | 0 | 13.0474 | 37.78
2020-11-30 23:00 | 44165.9583 | 0 | 12.5052 | 37.78
2020-11-30 23:30 | 44165.9792 | 0 | 11.9626 | 37.78
2020-12-01 | 44166 | 0 | 11.1573 | 37.78
2020-12-01 00:30 | 44166.0208 | 0 | 10.6351 | 37.78
2020-12-01 01:00 | 44166.0417 | 0 | 10.3211 | 37.78
2020-12-01 01:30 | 44166.0625 | 0 | 9.9175 | 37.78
2020-12-01 02:00 | 44166.0833 | 0 | 9.938 | 37.78
2020-12-01 02:30 | 44166.1042 | 0 | 9.8832 | 37.78
2020-12-01 03:00 | 44166.125 | 0 | 9.7743 | 37.78
2020-12-01 03:30 | 44166.1458 | 0 | 9.7546 | 37.78
2020-12-01 04:00 | 44166.1667 | 0 | 9.9489 | 37.78
2020-12-01 04:30 | 44166.1875 | 0 | 10.4471 | 37.78
2020-12-01 05:00 | 44166.2083 | 0 | 10.6811 | 37.78
2020-12-01 05:30 | 44166.2292 | 0 | 11.4366 | 37.78
2020-12-01 06:00 | 44166.25 | 0 | 12.1283 | 37.78
2020-12-01 06:30 | 44166.2708 | 0 | 12.8862 | 37.78
2020-12-01 07:00 | 44166.2917 | 0 | 13.925 | 37.78
2020-12-01 07:30 | 44166.3125 | 0 | 14.1893 | 37.78
2020-12-01 08:00 | 44166.3333 | 0 | 14.232 | 37.78
2020-12-01 08:30 | 44166.3542 | 0 | 13.9833 | 37.78
2020-12-01 09:00 | 44166.375 | 0 | 14.2198 | 37.78
2020-12-01 09:30 | 44166.3958 | 0 | 14.7648 | 37.78
2020-12-01 10:00 | 44166.4167 | 0 | 15.3472 | 37.78
2020-12-01 10:30 | 44166.4375 | 0 | 16.4111 | 37.78
2020-12-01 11:00 | 44166.4583 | 0 | 16.1292 | 37.78
2020-12-01 11:30 | 44166.4792 | 0 | 16.2318 | 37.78
2020-12-01 12:00 | 44166.5 | 0 | 16.6553 | 37.78
2020-12-01 12:30 | 44166.5208 | 0 | 16.2081 | 37.78
2020-12-01 13:00 | 44166.5417 | 0 | 16.8429 | 37.78
2020-12-01 13:30 | 44166.5625 | 0 | 17.5537 | 37.78
2020-12-01 14:00 | 44166.5833 | 0 | 17.9879 | 37.78
2020-12-01 14:30 | 44166.6042 | 0 | 18.1918 | 37.78
2020-12-01 15:00 | 44166.625 | 0 | 18.8192 | 37.78
2020-12-01 15:30 | 44166.6458 | 0 | 19.5856 | 37.78
2020-12-01 16:00 | 44166.6667 | 0 | 19.9045 | 37.78
2020-12-01 16:30 | 44166.6875 | 0 | 20.3155 | 37.78
2020-12-01 17:00 | 44166.7083 | 0 | 20.5095 | 37.78
2020-12-01 17:30 | 44166.7292 | 0 | 20.4709 | 37.78
2020-12-01 18:00 | 44166.75 | 0 | 20.3532 | 37.78
2020-12-01 18:30 | 44166.7708 | 0 | 20.3978 | 37.78
2020-12-01 19:00 | 44166.7917 | 0 | 20.475 | 37.78
2020-12-01 19:30 | 44166.8125 | 0 | 20.0716 | 37.78
2020-12-01 20:00 | 44166.8333 | 0 | 19.6832 | 37.78
2020-12-01 20:30 | 44166.8542 | 0 | 19.0078 | 37.78
2020-12-01 21:00 | 44166.875 | 0 | 17.8944 | 37.78
2020-12-01 21:30 | 44166.8958 | 0 | 16.8411 | 37.78
2020-12-01 22:00 | 44166.9167 | 0 | 15.9218 | 37.78
2020-12-01 22:30 | 44166.9375 | 0 | 14.7462 | 37.78
2020-12-01 23:00 | 44166.9583 | 0 | 13.9301 | 37.78
2020-12-01 23:30 | 44166.9792 | 0 | 13.1422 | 37.78
2020-12-02 | 44167 | 0 | 12.3277 | 37.78
2020-12-02 00:30 | 44167.0208 | 0 | 11.6682 | 37.78
2020-12-02 01:00 | 44167.0417 | 0 | 11.2908 | 37.78
2020-12-02 01:30 | 44167.0625 | 0 | 11.144 | 37.78
2020-12-02 02:00 | 44167.0833 | 0 | 11.0141 | 37.78
2020-12-02 02:30 | 44167.1042 | 0 | 10.7588 | 37.78
2020-12-02 03:00 | 44167.125 | 0 | 10.6242 | 37.78
2020-12-02 03:30 | 44167.1458 | 0 | 10.5918 | 37.78
2020-12-02 04:00 | 44167.1667 | 0 | 10.7278 | 37.78
2020-12-02 04:30 | 44167.1875 | 0 | 11.0689 | 37.78
2020-12-02 05:00 | 44167.2083 | 0 | 11.3631 | 37.78
2020-12-02 05:30 | 44167.2292 | 0 | 11.9566 | 37.78
2020-12-02 06:00 | 44167.25 | 0 | 12.8779 | 37.78
2020-12-02 06:30 | 44167.2708 | 0 | 13.7206 | 37.78
2020-12-02 07:00 | 44167.2917 | 0 | 14.7549 | 37.78
2020-12-02 07:30 | 44167.3125 | 0 | 15.5519 | 37.78
2020-12-02 08:00 | 44167.3333 | 0 | 16.1297 | 37.78
2020-12-02 08:30 | 44167.3542 | 0 | 16.625 | 37.78
2020-12-02 09:00 | 44167.375 | 0 | 17.0669 | 37.78
2020-12-02 09:30 | 44167.3958 | 0 | 17.3017 | 37.78
2020-12-02 10:00 | 44167.4167 | 0 | 17.2611 | 37.78
2020-12-02 10:30 | 44167.4375 | 0 | 17.4115 | 37.78
2020-12-02 11:00 | 44167.4583 | 0 | 17.6381 | 37.78
2020-12-02 11:30 | 44167.4792 | 0 | 17.9067 | 37.78
2020-12-02 12:00 | 44167.5 | 0 | 18.3874 | 37.78
2020-12-02 12:30 | 44167.5208 | 0 | 18.5388 | 37.78
2020-12-02 13:00 | 44167.5417 | 0 | 18.8638 | 37.78
2020-12-02 13:30 | 44167.5625 | 0 | 19.3069 | 37.78
2020-12-02 14:00 | 44167.5833 | 0 | 19.3543 | 37.78
2020-12-02 14:30 | 44167.6042 | 0 | 19.409 | 37.78
2020-12-02 15:00 | 44167.625 | 0 | 20.0283 | 37.78
2020-12-02 15:30 | 44167.6458 | 0 | 20.832 | 37.78
2020-12-02 16:00 | 44167.6667 | 0 | 21.2933 | 37.78
2020-12-02 16:30 | 44167.6875 | 0 | 21.2498 | 37.78
2020-12-02 17:00 | 44167.7083 | 0 | 20.7083 | 37.78
2020-12-02 17:30 | 44167.7292 | 0 | 20.5954 | 37.78
2020-12-02 18:00 | 44167.75 | 0 | 20.5487 | 37.78
2020-12-02 18:30 | 44167.7708 | 0 | 20.8885 | 37.78
2020-12-02 19:00 | 44167.7917 | 0 | 20.4804 | 37.78
2020-12-02 19:30 | 44167.8125 | 0 | 19.7815 | 37.78
2020-12-02 20:00 | 44167.8333 | 0 | 19.7662 | 37.78
2020-12-02 20:30 | 44167.8542 | 0 | 19.2699 | 37.78
2020-12-02 21:00 | 44167.875 | 0 | 18.2735 | 37.78
2020-12-02 21:30 | 44167.8958 | 0 | 17.5456 | 37.78
2020-12-02 22:00 | 44167.9167 | 0 | 16.1339 | 37.78
2020-12-02 22:30 | 44167.9375 | 0 | 15.1682 | 37.78
2020-12-02 23:00 | 44167.9583 | 0 | 14.2799 | 37.78
2020-12-02 23:30 | 44167.9792 | 0 | 13.9017 | 37.78
2020-12-03 | 44168 | 0 | 13.114 | 37.78
2020-12-03 00:30 | 44168.0208 | 0 | 12.6942 | 37.78
2020-12-03 01:00 | 44168.0417 | 0 | 12.2702 | 37.78
2020-12-03 01:30 | 44168.0625 | 0 | 11.9033 | 37.78
2020-12-03 02:00 | 44168.0833 | 0 | 11.6248 | 37.78
2020-12-03 02:30 | 44168.1042 | 0 | 11.4302 | 37.78
2020-12-03 03:00 | 44168.125 | 0 | 11.3788 | 37.78
2020-12-03 03:30 | 44168.1458 | 0 | 11.3782 | 37.78
2020-12-03 04:00 | 44168.1667 | 0 | 11.5825 | 37.78
2020-12-03 04:30 | 44168.1875 | 0 | 12.0086 | 37.78
2020-12-03 05:00 | 44168.2083 | 0 | 12.4562 | 37.78
2020-12-03 05:30 | 44168.2292 | 0 | 13.0453 | 37.78
2020-12-03 06:00 | 44168.25 | 0 | 13.9624 | 37.78
2020-12-03 06:30 | 44168.2708 | 0 | 14.6705 | 37.78
2020-12-03 07:00 | 44168.2917 | 0 | 15.36 | 37.78
2020-12-03 07:30 | 44168.3125 | 0 | 15.4905 | 37.78
2020-12-03 08:00 | 44168.3333 | 0 | 16.4037 | 37.78
2020-12-03 08:30 | 44168.3542 | 0 | 15.7434 | 37.78
2020-12-03 09:00 | 44168.375 | 0 | 16.3157 | 37.78
2020-12-03 09:30 | 44168.3958 | 0 | 16.6625 | 37.78
2020-12-03 10:00 | 44168.4167 | 0 | 16.2137 | 37.78
2020-12-03 10:30 | 44168.4375 | 0 | 17.0331 | 37.78
2020-12-03 11:00 | 44168.4583 | 0 | 16.4864 | 37.78
2020-12-03 11:30 | 44168.4792 | 0 | 16.4414 | 37.78
2020-12-03 12:00 | 44168.5 | 0 | 15.4675 | 37.78
2020-12-03 12:30 | 44168.5208 | 0 | 15.9873 | 37.78
2020-12-03 13:00 | 44168.5417 | 0 | 16.1905 | 37.78
2020-12-03 13:30 | 44168.5625 | 0 | 16.9179 | 37.78
2020-12-03 14:00 | 44168.5833 | 0 | 17.4539 | 37.78
2020-12-03 14:30 | 44168.6042 | 0 | 17.7727 | 37.78
2020-12-03 15:00 | 44168.625 | 0 | 18.1691 | 37.78
2020-12-03 15:30 | 44168.6458 | 0 | 18.6424 | 37.78
2020-12-03 16:00 | 44168.6667 | 0 | 19.1565 | 37.78
2020-12-03 16:30 | 44168.6875 | 0 | 19.568 | 37.78
2020-12-03 17:00 | 44168.7083 | 0 | 19.2623 | 37.78
2020-12-03 17:30 | 44168.7292 | 0 | 19.0281 | 37.78
2020-12-03 18:00 | 44168.75 | 0 | 18.7553 | 37.78
2020-12-03 18:30 | 44168.7708 | 0 | 19.0776 | 37.78
2020-12-03 19:00 | 44168.7917 | 0 | 19.4517 | 37.78
2020-12-03 19:30 | 44168.8125 | 0 | 19.3583 | 37.78
2020-12-03 20:00 | 44168.8333 | 0 | 18.9659 | 37.78
2020-12-03 20:30 | 44168.8542 | 0 | 18.2772 | 37.78
2020-12-03 21:00 | 44168.875 | 0 | 17.276 | 37.78
2020-12-03 21:30 | 44168.8958 | 0 | 16.6412 | 37.78
2020-12-03 22:00 | 44168.9167 | 0 | 15.4751 | 37.78
2020-12-03 22:30 | 44168.9375 | 0 | 14.1681 | 37.78
2020-12-03 23:00 | 44168.9583 | 0 | 13.6845 | 37.78
2020-12-03 23:30 | 44168.9792 | 0 | 13.0023 | 37.78
2020-12-04 | 44169 | 0 | 12.2777 | 37.78
2020-12-04 00:30 | 44169.0208 | 0 | 11.6456 | 37.78
2020-12-04 01:00 | 44169.0417 | 0 | 11.4188 | 37.78
2020-12-04 01:30 | 44169.0625 | 0 | 11.1934 | 37.78
2020-12-04 02:00 | 44169.0833 | 0 | 11.0404 | 37.78
2020-12-04 02:30 | 44169.1042 | 0 | 10.8943 | 37.78
2020-12-04 03:00 | 44169.125 | 0 | 10.7445 | 37.78
2020-12-04 03:30 | 44169.1458 | 0 | 10.7975 | 37.78
2020-12-04 04:00 | 44169.1667 | 0 | 10.9538 | 37.78
2020-12-04 04:30 | 44169.1875 | 0 | 11.3754 | 37.78
2020-12-04 05:00 | 44169.2083 | 0 | 11.8126 | 37.78
2020-12-04 05:30 | 44169.2292 | 0 | 12.3195 | 37.78
2020-12-04 06:00 | 44169.25 | 0 | 13.0457 | 37.78
2020-12-04 06:30 | 44169.2708 | 0 | 13.7677 | 37.78
2020-12-04 07:00 | 44169.2917 | 0 | 14.0483 | 37.78
2020-12-04 07:30 | 44169.3125 | 0 | 14.6902 | 37.78
2020-12-04 08:00 | 44169.3333 | 0 | 15.2632 | 37.78
2020-12-04 08:30 | 44169.3542 | 0 | 15.4874 | 37.78
2020-12-04 09:00 | 44169.375 | 0 | 15.6304 | 37.78
2020-12-04 09:30 | 44169.3958 | 0 | 16.7301 | 37.78
2020-12-04 10:00 | 44169.4167 | 0 | 16.7655 | 37.78
2020-12-04 10:30 | 44169.4375 | 0 | 19.1932 | 37.78
2020-12-04 11:00 | 44169.4583 | 0 | 19.5621 | 37.78
2020-12-04 11:30 | 44169.4792 | 0 | 18.8211 | 37.78
2020-12-04 12:00 | 44169.5 | 0 | 18.5627 | 37.78
2020-12-04 12:30 | 44169.5208 | 0 | 27.0418 | 37.78
2020-12-04 13:00 | 44169.5417 | 0 | 25.7897 | 37.78
2020-12-04 13:30 | 44169.5625 | 0 | 18.8406 | 37.78
2020-12-04 14:00 | 44169.5833 | 0 | 18.9521 | 37.78
2020-12-04 14:30 | 44169.6042 | 0 | 19.7982 | 37.78
2020-12-04 15:00 | 44169.625 | 0 | 19.9065 | 37.78
2020-12-04 15:30 | 44169.6458 | 0 | 20.4383 | 37.78
2020-12-04 16:00 | 44169.6667 | 0 | 20.7606 | 37.78
2020-12-04 16:30 | 44169.6875 | 0 | 21.101 | 37.78
2020-12-04 17:00 | 44169.7083 | 0 | 20.766 | 37.78
2020-12-04 17:30 | 44169.7292 | 0 | 20.4329 | 37.78
2020-12-04 18:00 | 44169.75 | 0 | 19.5401 | 37.78
2020-12-04 18:30 | 44169.7708 | 0 | 19.4866 | 37.78
2020-12-04 19:00 | 44169.7917 | 0 | 19.4754 | 37.78
2020-12-04 19:30 | 44169.8125 | 0 | 19.0944 | 37.78
2020-12-04 20:00 | 44169.8333 | 0 | 18.751 | 37.78
2020-12-04 20:30 | 44169.8542 | 0 | 18.0359 | 37.78
2020-12-04 21:00 | 44169.875 | 0 | 17.2783 | 37.78
2020-12-04 21:30 | 44169.8958 | 0 | 16.8478 | 37.78
2020-12-04 22:00 | 44169.9167 | 0 | 16.3087 | 37.78
2020-12-04 22:30 | 44169.9375 | 0 | 15.1392 | 37.78
2020-12-04 23:00 | 44169.9583 | 0 | 14.2993 | 37.78
2020-12-04 23:30 | 44169.9792 | 0 | 13.4436 | 37.78
2020-12-05 | 44170 | 0 | 12.5628 | 37.78
2020-12-05 00:30 | 44170.0208 | 0 | 11.882 | 37.78
2020-12-05 01:00 | 44170.0417 | 0 | 11.4235 | 37.78
2020-12-05 01:30 | 44170.0625 | 0 | 11.2157 | 37.78
2020-12-05 02:00 | 44170.0833 | 0 | 11.0785 | 37.78
2020-12-05 02:30 | 44170.1042 | 0 | 10.8164 | 37.78
2020-12-05 03:00 | 44170.125 | 0 | 10.6385 | 37.78
2020-12-05 03:30 | 44170.1458 | 0 | 10.5227 | 37.78
2020-12-05 04:00 | 44170.1667 | 0 | 10.333 | 37.78
2020-12-05 04:30 | 44170.1875 | 0 | 10.2656 | 37.78
2020-12-05 05:00 | 44170.2083 | 0 | 10.3962 | 37.78
2020-12-05 05:30 | 44170.2292 | 0 | 10.474 | 37.78
2020-12-05 06:00 | 44170.25 | 0 | 10.7012 | 37.78
2020-12-05 06:30 | 44170.2708 | 0 | 10.7928 | 37.78
2020-12-05 07:00 | 44170.2917 | 0 | 11.1651 | 37.78
2020-12-05 07:30 | 44170.3125 | 0 | 11.7497 | 37.78
2020-12-05 08:00 | 44170.3333 | 0 | 12.5112 | 37.78
2020-12-05 08:30 | 44170.3542 | 0 | 13.0449 | 37.78
2020-12-05 09:00 | 44170.375 | 0 | 13.4161 | 37.78
2020-12-05 09:30 | 44170.3958 | 0 | 13.8016 | 37.78
2020-12-05 10:00 | 44170.4167 | 0 | 14.1129 | 37.78
2020-12-05 10:30 | 44170.4375 | 0 | 14.3646 | 37.78
2020-12-05 11:00 | 44170.4583 | 0 | 14.5245 | 37.78
2020-12-05 11:30 | 44170.4792 | 0 | 14.6908 | 37.78
2020-12-05 12:00 | 44170.5 | 0 | 14.9649 | 37.78
2020-12-05 12:30 | 44170.5208 | 0 | 15.0739 | 37.78
2020-12-05 13:00 | 44170.5417 | 0 | 16.8752 | 37.78
2020-12-05 13:30 | 44170.5625 | 0 | 15.6565 | 37.78
2020-12-05 14:00 | 44170.5833 | 0 | 16.036 | 37.78
2020-12-05 14:30 | 44170.6042 | 0 | 16.4973 | 37.78
2020-12-05 15:00 | 44170.625 | 0 | 17.0686 | 37.78
2020-12-05 15:30 | 44170.6458 | 0 | 16.5287 | 37.78
2020-12-05 16:00 | 44170.6667 | 0 | 17.1471 | 37.78
2020-12-05 16:30 | 44170.6875 | 0 | 16.9919 | 37.78
2020-12-05 17:00 | 44170.7083 | 0 | 17.2821 | 37.78
2020-12-05 17:30 | 44170.7292 | 0 | 16.7408 | 37.78
2020-12-05 18:00 | 44170.75 | 0 | 16.47 | 37.78
2020-12-05 18:30 | 44170.7708 | 0 | 16.6757 | 37.78
2020-12-05 19:00 | 44170.7917 | 0 | 16.6338 | 37.78
2020-12-05 19:30 | 44170.8125 | 0 | 16.3475 | 37.78
2020-12-05 20:00 | 44170.8333 | 0 | 16.1236 | 37.78
2020-12-05 20:30 | 44170.8542 | 0 | 15.574 | 37.78
2020-12-05 21:00 | 44170.875 | 0 | 15.0303 | 37.78
2020-12-05 21:30 | 44170.8958 | 0 | 14.4854 | 37.78
2020-12-05 22:00 | 44170.9167 | 0 | 13.9457 | 37.78
2020-12-05 22:30 | 44170.9375 | 0 | 12.9644 | 37.78
2020-12-05 23:00 | 44170.9583 | 0 | 12.3315 | 37.78
2020-12-05 23:30 | 44170.9792 | 0 | 11.8265 | 37.78
2020-12-06 | 44171 | 0 | 11.5317 | 37.78
2020-12-06 00:30 | 44171.0208 | 0 | 10.9395 | 37.78
2020-12-06 01:00 | 44171.0417 | 0 | 10.4943 | 37.78
2020-12-06 01:30 | 44171.0625 | 0 | 10.145 | 37.78
2020-12-06 02:00 | 44171.0833 | 0 | 10.0619 | 37.78
2020-12-06 02:30 | 44171.1042 | 0 | 9.8791 | 37.78
2020-12-06 03:00 | 44171.125 | 0 | 9.8081 | 37.78
2020-12-06 03:30 | 44171.1458 | 0 | 9.6098 | 37.78
2020-12-06 04:00 | 44171.1667 | 0 | 9.474 | 37.78
2020-12-06 04:30 | 44171.1875 | 0 | 9.3838 | 37.78
2020-12-06 05:00 | 44171.2083 | 0 | 9.3019 | 37.78
2020-12-06 05:30 | 44171.2292 | 0 | 9.086 | 37.78
2020-12-06 06:00 | 44171.25 | 0 | 9.5408 | 37.78
2020-12-06 06:30 | 44171.2708 | 0 | 9.2545 | 37.78
2020-12-06 07:00 | 44171.2917 | 0 | 9.5577 | 37.78
2020-12-06 07:30 | 44171.3125 | 0 | 9.9018 | 37.78
2020-12-06 08:00 | 44171.3333 | 0 | 10.3317 | 37.78
2020-12-06 08:30 | 44171.3542 | 0 | 10.838 | 37.78
2020-12-06 09:00 | 44171.375 | 0 | 11.8529 | 37.78
2020-12-06 09:30 | 44171.3958 | 0 | 12.9258 | 37.78
2020-12-06 10:00 | 44171.4167 | 0 | 12.4434 | 37.78
2020-12-06 10:30 | 44171.4375 | 0 | 12.4058 | 37.78
2020-12-06 11:00 | 44171.4583 | 0 | 13.1911 | 37.78
2020-12-06 11:30 | 44171.4792 | 0 | 13.7784 | 37.78
2020-12-06 12:00 | 44171.5 | 0 | 14.2685 | 37.78
2020-12-06 12:30 | 44171.5208 | 0 | 15.4359 | 37.78
2020-12-06 13:00 | 44171.5417 | 0 | 15.9296 | 37.78
2020-12-06 13:30 | 44171.5625 | 0 | 16.4143 | 37.78
2020-12-06 14:00 | 44171.5833 | 0 | 16.7783 | 37.78
2020-12-06 14:30 | 44171.6042 | 0 | 16.2891 | 37.78
2020-12-06 15:00 | 44171.625 | 0 | 16.7117 | 37.78
2020-12-06 15:30 | 44171.6458 | 0 | 17.5939 | 37.78
2020-12-06 16:00 | 44171.6667 | 0 | 16.9734 | 37.78
2020-12-06 16:30 | 44171.6875 | 0 | 18.2142 | 37.78
2020-12-06 17:00 | 44171.7083 | 0 | 18.1233 | 37.78
2020-12-06 17:30 | 44171.7292 | 0 | 18.1622 | 37.78
2020-12-06 18:00 | 44171.75 | 0 | 18.9458 | 37.78
2020-12-06 18:30 | 44171.7708 | 0 | 20.0411 | 37.78
2020-12-06 19:00 | 44171.7917 | 0 | 20.5853 | 37.78
2020-12-06 19:30 | 44171.8125 | 0 | 20.3227 | 37.78
2020-12-06 20:00 | 44171.8333 | 0 | 19.8705 | 37.78
2020-12-06 20:30 | 44171.8542 | 0 | 19.0718 | 37.78
2020-12-06 21:00 | 44171.875 | 0 | 18.0433 | 37.78
2020-12-06 21:30 | 44171.8958 | 0 | 17.1994 | 37.78
2020-12-06 22:00 | 44171.9167 | 0 | 16.26 | 37.78
2020-12-06 22:30 | 44171.9375 | 0 | 15.0279 | 37.78
2020-12-06 23:00 | 44171.9583 | 0 | 14.2859 | 37.78
2020-12-06 23:30 | 44171.9792 | 0 | 13.6655 | 37.78
2020-12-07 | 44172 | 0 | 13.2785 | 37.78
2020-12-07 00:30 | 44172.0208 | 0 | 13.0178 | 37.78
2020-12-07 01:00 | 44172.0417 | 0 | 12.7485 | 37.78
2020-12-07 01:30 | 44172.0625 | 0 | 12.4547 | 37.78
2020-12-07 02:00 | 44172.0833 | 0 | 12.3757 | 37.78
2020-12-07 02:30 | 44172.1042 | 0 | 11.9144 | 37.78
2020-12-07 03:00 | 44172.125 | 0 | 11.9067 | 37.78
2020-12-07 03:30 | 44172.1458 | 0 | 11.5219 | 37.78
2020-12-07 04:00 | 44172.1667 | 0 | 11.5054 | 37.78
2020-12-07 04:30 | 44172.1875 | 0 | 11.8634 | 37.78
2020-12-07 05:00 | 44172.2083 | 0 | 12.2556 | 37.78
2020-12-07 05:30 | 44172.2292 | 0 | 12.9454 | 37.78
2020-12-07 06:00 | 44172.25 | 0 | 13.9852 | 37.78
2020-12-07 06:30 | 44172.2708 | 0 | 14.7348 | 37.78
2020-12-07 07:00 | 44172.2917 | 0 | 16.3701 | 37.78
2020-12-07 07:30 | 44172.3125 | 0 | 17.1929 | 37.78
2020-12-07 08:00 | 44172.3333 | 0 | 17.6638 | 37.78
2020-12-07 08:30 | 44172.3542 | 0 | 18.1398 | 37.78
2020-12-07 09:00 | 44172.375 | 0 | 18.2126 | 37.78
2020-12-07 09:30 | 44172.3958 | 0 | 17.9342 | 37.78
2020-12-07 10:00 | 44172.4167 | 0 | 18.8364 | 37.78
2020-12-07 10:30 | 44172.4375 | 0 | 19.2189 | 37.78
2020-12-07 11:00 | 44172.4583 | 0 | 18.1068 | 37.78
2020-12-07 11:30 | 44172.4792 | 0 | 18.9892 | 37.78
2020-12-07 12:00 | 44172.5 | 0 | 18.688 | 37.78
2020-12-07 12:30 | 44172.5208 | 0 | 19.4242 | 37.78
2020-12-07 13:00 | 44172.5417 | 0 | 21.7358 | 37.78
2020-12-07 13:30 | 44172.5625 | 0 | 22.1674 | 37.78
2020-12-07 14:00 | 44172.5833 | 0 | 22.425 | 37.78
2020-12-07 14:30 | 44172.6042 | 0 | 20.7796 | 37.78
2020-12-07 15:00 | 44172.625 | 0 | 19.921 | 37.78
2020-12-07 15:30 | 44172.6458 | 0 | 20.4107 | 37.78
2020-12-07 16:00 | 44172.6667 | 0 | 19.5982 | 37.78
2020-12-07 16:30 | 44172.6875 | 0 | 18.8472 | 37.78
2020-12-07 17:00 | 44172.7083 | 0 | 18.1923 | 37.78
2020-12-07 17:30 | 44172.7292 | 0 | 18.5469 | 37.78
2020-12-07 18:00 | 44172.75 | 0 | 18.1761 | 37.78
2020-12-07 18:30 | 44172.7708 | 0 | 18.6459 | 37.78
2020-12-07 19:00 | 44172.7917 | 0 | 18.2415 | 37.78
2020-12-07 19:30 | 44172.8125 | 0 | 17.7025 | 37.78
2020-12-07 20:00 | 44172.8333 | 0 | 17.2678 | 37.78
2020-12-07 20:30 | 44172.8542 | 0 | 16.8316 | 37.78
2020-12-07 21:00 | 44172.875 | 0 | 15.9576 | 37.78
2020-12-07 21:30 | 44172.8958 | 0 | 15.3193 | 37.78
2020-12-07 22:00 | 44172.9167 | 0 | 14.2933 | 37.78
2020-12-07 22:30 | 44172.9375 | 0 | 13.5652 | 37.78
2020-12-07 23:00 | 44172.9583 | 0 | 12.9627 | 37.78
2020-12-07 23:30 | 44172.9792 | 0 | 12.0318 | 37.78
2020-12-08 | 44173 | 0 | 11.4145 | 37.78
2020-12-08 00:30 | 44173.0208 | 0 | 10.9369 | 37.78
2020-12-08 01:00 | 44173.0417 | 0 | 10.6743 | 37.78
2020-12-08 01:30 | 44173.0625 | 0 | 10.4517 | 37.78
2020-12-08 02:00 | 44173.0833 | 0 | 10.2913 | 37.78
2020-12-08 02:30 | 44173.1042 | 0 | 9.9849 | 37.78
2020-12-08 03:00 | 44173.125 | 0 | 9.8893 | 37.78
2020-12-08 03:30 | 44173.1458 | 0 | 9.9482 | 37.78
2020-12-08 04:00 | 44173.1667 | 0 | 10.2575 | 37.78
2020-12-08 04:30 | 44173.1875 | 0 | 10.5694 | 37.78
2020-12-08 05:00 | 44173.2083 | 0 | 11.108 | 37.78
2020-12-08 05:30 | 44173.2292 | 0 | 11.7708 | 37.78
2020-12-08 06:00 | 44173.25 | 0 | 12.5489 | 37.78
2020-12-08 06:30 | 44173.2708 | 0 | 13.497 | 37.78
2020-12-08 07:00 | 44173.2917 | 0 | 14.1874 | 37.78
2020-12-08 07:30 | 44173.3125 | 0 | 14.7829 | 37.78
2020-12-08 08:00 | 44173.3333 | 0 | 15.2793 | 37.78
2020-12-08 08:30 | 44173.3542 | 0 | 14.9633 | 37.78
2020-12-08 09:00 | 44173.375 | 0 | 15.465 | 37.78
2020-12-08 09:30 | 44173.3958 | 0 | 15.6444 | 37.78
2020-12-08 10:00 | 44173.4167 | 0 | 15.8479 | 37.78
2020-12-08 10:30 | 44173.4375 | 0 | 14.8991 | 37.78
2020-12-08 11:00 | 44173.4583 | 0 | 15.0822 | 37.78
2020-12-08 11:30 | 44173.4792 | 0 | 15.2248 | 37.78
2020-12-08 12:00 | 44173.5 | 0 | 14.0097 | 37.78
2020-12-08 12:30 | 44173.5208 | 0 | 13.5532 | 37.78
2020-12-08 13:00 | 44173.5417 | 0 | 13.6968 | 37.78
2020-12-08 13:30 | 44173.5625 | 0 | 14.2322 | 37.78
2020-12-08 14:00 | 44173.5833 | 0 | 14.4485 | 37.78
2020-12-08 14:30 | 44173.6042 | 0 | 15.1075 | 37.78
2020-12-08 15:00 | 44173.625 | 0 | 16.2037 | 37.78
2020-12-08 15:30 | 44173.6458 | 0 | 15.8804 | 37.78
2020-12-08 16:00 | 44173.6667 | 0 | 15.5889 | 37.78
2020-12-08 16:30 | 44173.6875 | 0 | 16.7144 | 37.78
2020-12-08 17:00 | 44173.7083 | 0 | 16.7278 | 37.78
2020-12-08 17:30 | 44173.7292 | 0 | 16.3632 | 37.78
2020-12-08 18:00 | 44173.75 | 0 | 16.3358 | 37.78
2020-12-08 18:30 | 44173.7708 | 0 | 17.0913 | 37.78
2020-12-08 19:00 | 44173.7917 | 0 | 17.1291 | 37.78
2020-12-08 19:30 | 44173.8125 | 0 | 16.851 | 37.78
2020-12-08 20:00 | 44173.8333 | 0 | 16.4857 | 37.78
2020-12-08 20:30 | 44173.8542 | 0 | 15.955 | 37.78
2020-12-08 21:00 | 44173.875 | 0 | 15.1674 | 37.78
2020-12-08 21:30 | 44173.8958 | 0 | 14.6055 | 37.78
2020-12-08 22:00 | 44173.9167 | 0 | 13.8941 | 37.78
2020-12-08 22:30 | 44173.9375 | 0 | 12.8041 | 37.78
2020-12-08 23:00 | 44173.9583 | 0 | 12.0393 | 37.78
2020-12-08 23:30 | 44173.9792 | 0 | 11.3179 | 37.78
2020-12-09 | 44174 | 0 | 10.4813 | 37.78
2020-12-09 00:30 | 44174.0208 | 0 | 9.9768 | 37.78
2020-12-09 01:00 | 44174.0417 | 0 | 9.8866 | 37.78
2020-12-09 01:30 | 44174.0625 | 0 | 9.6484 | 37.78
2020-12-09 02:00 | 44174.0833 | 0 | 9.4325 | 37.78
2020-12-09 02:30 | 44174.1042 | 0 | 9.3432 | 37.78
2020-12-09 03:00 | 44174.125 | 0 | 9.1706 | 37.78
2020-12-09 03:30 | 44174.1458 | 0 | 9.2017 | 37.78
2020-12-09 04:00 | 44174.1667 | 0 | 9.4345 | 37.78
2020-12-09 04:30 | 44174.1875 | 0 | 9.7021 | 37.78
2020-12-09 05:00 | 44174.2083 | 0 | 10.0192 | 37.78
2020-12-09 05:30 | 44174.2292 | 0 | 10.3485 | 37.78
2020-12-09 06:00 | 44174.25 | 0 | 11.0396 | 37.78
2020-12-09 06:30 | 44174.2708 | 0 | 11.3856 | 37.78
2020-12-09 07:00 | 44174.2917 | 0 | 11.8188 | 37.78
2020-12-09 07:30 | 44174.3125 | 0 | 11.9222 | 37.78
2020-12-09 08:00 | 44174.3333 | 0 | 12.5068 | 37.78
2020-12-09 08:30 | 44174.3542 | 0 | 13.0423 | 37.78
2020-12-09 09:00 | 44174.375 | 0 | 13.6925 | 37.78
2020-12-09 09:30 | 44174.3958 | 0 | 13.1869 | 37.78
2020-12-09 10:00 | 44174.4167 | 0 | 12.6989 | 37.78
2020-12-09 10:30 | 44174.4375 | 0 | 14.1031 | 37.78
2020-12-09 11:00 | 44174.4583 | 0 | 13.0809 | 37.78
2020-12-09 11:30 | 44174.4792 | 0 | 12.8585 | 37.78
2020-12-09 12:00 | 44174.5 | 0 | 12.6301 | 37.78
2020-12-09 12:30 | 44174.5208 | 0 | 12.7293 | 37.78
2020-12-09 13:00 | 44174.5417 | 0 | 12.9424 | 37.78
2020-12-09 13:30 | 44174.5625 | 0 | 13.9686 | 37.78
2020-12-09 14:00 | 44174.5833 | 0 | 13.761 | 37.78
2020-12-09 14:30 | 44174.6042 | 0 | 14.3319 | 37.78
2020-12-09 15:00 | 44174.625 | 0 | 14.6726 | 37.78
2020-12-09 15:30 | 44174.6458 | 0 | 14.7308 | 37.78
2020-12-09 16:00 | 44174.6667 | 0 | 15.1364 | 37.78
2020-12-09 16:30 | 44174.6875 | 0 | 15.3608 | 37.78
2020-12-09 17:00 | 44174.7083 | 0 | 15.6099 | 37.78
2020-12-09 17:30 | 44174.7292 | 0 | 15.6735 | 37.78
2020-12-09 18:00 | 44174.75 | 0 | 15.4555 | 37.78
2020-12-09 18:30 | 44174.7708 | 0 | 15.6735 | 37.78
2020-12-09 19:00 | 44174.7917 | 0 | 15.7486 | 37.78
2020-12-09 19:30 | 44174.8125 | 0 | 15.6356 | 37.78
2020-12-09 20:00 | 44174.8333 | 0 | 15.2552 | 37.78
2020-12-09 20:30 | 44174.8542 | 0 | 14.7376 | 37.78
2020-12-09 21:00 | 44174.875 | 0 | 14.2672 | 37.78
2020-12-09 21:30 | 44174.8958 | 0 | 13.7673 | 37.78
2020-12-09 22:00 | 44174.9167 | 0 | 13.0657 | 37.78
2020-12-09 22:30 | 44174.9375 | 0 | 12.2928 | 37.78
2020-12-09 23:00 | 44174.9583 | 0 | 11.6294 | 37.78
2020-12-09 23:30 | 44174.9792 | 0 | 10.9998 | 37.78
2020-12-10 | 44175 | 0 | 10.3933 | 37.78
2020-12-10 00:30 | 44175.0208 | 0 | 9.9213 | 37.78
2020-12-10 01:00 | 44175.0417 | 0 | 9.8602 | 37.78
2020-12-10 01:30 | 44175.0625 | 0 | 9.7153 | 37.78
2020-12-10 02:00 | 44175.0833 | 0 | 9.6741 | 37.78
2020-12-10 02:30 | 44175.1042 | 0 | 9.5807 | 37.78
2020-12-10 03:00 | 44175.125 | 0 | 9.5584 | 37.78
2020-12-10 03:30 | 44175.1458 | 0 | 9.5097 | 37.78
2020-12-10 04:00 | 44175.1667 | 0 | 9.7844 | 37.78
2020-12-10 04:30 | 44175.1875 | 0 | 10.2514 | 37.78
2020-12-10 05:00 | 44175.2083 | 0 | 10.5694 | 37.78
2020-12-10 05:30 | 44175.2292 | 0 | 10.7863 | 37.78
2020-12-10 06:00 | 44175.25 | 0 | 11.4424 | 37.78
2020-12-10 06:30 | 44175.2708 | 0 | 12.1266 | 37.78
2020-12-10 07:00 | 44175.2917 | 0 | 12.6403 | 37.78
2020-12-10 07:30 | 44175.3125 | 0 | 13.0557 | 37.78
2020-12-10 08:00 | 44175.3333 | 0 | 13.7213 | 37.78
2020-12-10 08:30 | 44175.3542 | 0 | 13.7255 | 37.78
2020-12-10 09:00 | 44175.375 | 0 | 12.5838 | 37.78
2020-12-10 09:30 | 44175.3958 | 0 | 12.7679 | 37.78
2020-12-10 10:00 | 44175.4167 | 0 | 13.2315 | 37.78
2020-12-10 10:30 | 44175.4375 | 0 | 13.3626 | 37.78
2020-12-10 11:00 | 44175.4583 | 0 | 13.2209 | 37.78
2020-12-10 11:30 | 44175.4792 | 0 | 13.5455 | 37.78
2020-12-10 12:00 | 44175.5 | 0 | 13.2317 | 37.78
2020-12-10 12:30 | 44175.5208 | 0 | 13.3509 | 37.78
2020-12-10 13:00 | 44175.5417 | 0 | 13.8035 | 37.78
2020-12-10 13:30 | 44175.5625 | 0 | 14.3739 | 37.78
2020-12-10 14:00 | 44175.5833 | 0 | 14.7172 | 37.78
2020-12-10 14:30 | 44175.6042 | 0 | 14.8918 | 37.78
2020-12-10 15:00 | 44175.625 | 0 | 15.2569 | 37.78
2020-12-10 15:30 | 44175.6458 | 0 | 15.7909 | 37.78
2020-12-10 16:00 | 44175.6667 | 0 | 16.0964 | 37.78
2020-12-10 16:30 | 44175.6875 | 0 | 16.3394 | 37.78
2020-12-10 17:00 | 44175.7083 | 0 | 16.6248 | 37.78
2020-12-10 17:30 | 44175.7292 | 0 | 16.3908 | 37.78
2020-12-10 18:00 | 44175.75 | 0 | 16.0754 | 37.78
2020-12-10 18:30 | 44175.7708 | 0 | 16.4917 | 37.78
2020-12-10 19:00 | 44175.7917 | 0 | 16.4199 | 37.78
2020-12-10 19:30 | 44175.8125 | 0 | 16.0606 | 37.78
2020-12-10 20:00 | 44175.8333 | 0 | 15.7685 | 37.78
2020-12-10 20:30 | 44175.8542 | 0 | 15.4359 | 37.78
2020-12-10 21:00 | 44175.875 | 0 | 14.7995 | 37.78
2020-12-10 21:30 | 44175.8958 | 0 | 14.3458 | 37.78
2020-12-10 22:00 | 44175.9167 | 0 | 13.5389 | 37.78
2020-12-10 22:30 | 44175.9375 | 0 | 12.7941 | 37.78
2020-12-10 23:00 | 44175.9583 | 0 | 12.0607 | 37.78
2020-12-10 23:30 | 44175.9792 | 0 | 11.3885 | 37.78
2020-12-11 | 44176 | 0 | 10.7434 | 37.78
2020-12-11 00:30 | 44176.0208 | 0 | 10.2588 | 37.78
2020-12-11 01:00 | 44176.0417 | 0 | 10.0274 | 37.78
2020-12-11 01:30 | 44176.0625 | 0 | 10.0314 | 37.78
2020-12-11 02:00 | 44176.0833 | 0 | 9.9068 | 37.78
2020-12-11 02:30 | 44176.1042 | 0 | 9.7485 | 37.78
2020-12-11 03:00 | 44176.125 | 0 | 9.6112 | 37.78
2020-12-11 03:30 | 44176.1458 | 0 | 9.5503 | 37.78
2020-12-11 04:00 | 44176.1667 | 0 | 9.8372 | 37.78
2020-12-11 04:30 | 44176.1875 | 0 | 10.0557 | 37.78
2020-12-11 05:00 | 44176.2083 | 0 | 10.5165 | 37.78
2020-12-11 05:30 | 44176.2292 | 0 | 10.9718 | 37.78
2020-12-11 06:00 | 44176.25 | 0 | 11.1054 | 37.78
2020-12-11 06:30 | 44176.2708 | 0 | 11.7647 | 37.78
2020-12-11 07:00 | 44176.2917 | 0 | 11.951 | 37.78
2020-12-11 07:30 | 44176.3125 | 0 | 13.4427 | 37.78
2020-12-11 08:00 | 44176.3333 | 0 | 12.936 | 37.78
2020-12-11 08:30 | 44176.3542 | 0 | 12.6202 | 37.78
2020-12-11 09:00 | 44176.375 | 0 | 14.2626 | 37.78
2020-12-11 09:30 | 44176.3958 | 0 | 13.8368 | 37.78
2020-12-11 10:00 | 44176.4167 | 0 | 13.8247 | 37.78
2020-12-11 10:30 | 44176.4375 | 0 | 13.9378 | 37.78
2020-12-11 11:00 | 44176.4583 | 0 | 14.2123 | 37.78
2020-12-11 11:30 | 44176.4792 | 0 | 14.2812 | 37.78
2020-12-11 12:00 | 44176.5 | 0 | 13.9214 | 37.78
2020-12-11 12:30 | 44176.5208 | 0 | 13.7616 | 37.78
2020-12-11 13:00 | 44176.5417 | 0 | 13.5783 | 37.78
2020-12-11 13:30 | 44176.5625 | 0 | 13.1923 | 37.78
2020-12-11 14:00 | 44176.5833 | 0 | 13.1214 | 37.78
2020-12-11 14:30 | 44176.6042 | 0 | 13.1552 | 37.78
2020-12-11 15:00 | 44176.625 | 0 | 13.7143 | 37.78
2020-12-11 15:30 | 44176.6458 | 0 | 13.3823 | 37.78
2020-12-11 16:00 | 44176.6667 | 0 | 13.2737 | 37.78
2020-12-11 16:30 | 44176.6875 | 0 | 13.3028 | 37.78
2020-12-11 17:00 | 44176.7083 | 0 | 13.1255 | 37.78
2020-12-11 17:30 | 44176.7292 | 0 | 12.811 | 37.78
2020-12-11 18:00 | 44176.75 | 0 | 12.687 | 37.78
2020-12-11 18:30 | 44176.7708 | 0 | 13.177 | 37.78
2020-12-11 19:00 | 44176.7917 | 0 | 13.2169 | 37.78
2020-12-11 19:30 | 44176.8125 | 0 | 13.028 | 37.78
2020-12-11 20:00 | 44176.8333 | 0 | 12.8816 | 37.78
2020-12-11 20:30 | 44176.8542 | 0 | 12.3655 | 37.78
2020-12-11 21:00 | 44176.875 | 0 | 11.9478 | 37.78
2020-12-11 21:30 | 44176.8958 | 0 | 11.6617 | 37.78
2020-12-11 22:00 | 44176.9167 | 0 | 11.3655 | 37.78
2020-12-11 22:30 | 44176.9375 | 0 | 10.6138 | 37.78
2020-12-11 23:00 | 44176.9583 | 0 | 10.2216 | 37.78
2020-12-11 23:30 | 44176.9792 | 0 | 9.7246 | 37.78
2020-12-12 | 44177 | 0 | 9.3149 | 37.78
2020-12-12 00:30 | 44177.0208 | 0 | 8.9371 | 37.78
2020-12-12 01:00 | 44177.0417 | 0 | 8.7436 | 37.78
2020-12-12 01:30 | 44177.0625 | 0 | 8.6285 | 37.78
2020-12-12 02:00 | 44177.0833 | 0 | 8.5534 | 37.78
2020-12-12 02:30 | 44177.1042 | 0 | 8.5047 | 37.78
2020-12-12 03:00 | 44177.125 | 0 | 8.3772 | 37.78
2020-12-12 03:30 | 44177.1458 | 0 | 8.4377 | 37.78
2020-12-12 04:00 | 44177.1667 | 0 | 8.4783 | 37.78
2020-12-12 04:30 | 44177.1875 | 0 | 8.6021 | 37.78
2020-12-12 05:00 | 44177.2083 | 0 | 8.6751 | 37.78
2020-12-12 05:30 | 44177.2292 | 0 | 8.592 | 37.78
2020-12-12 06:00 | 44177.25 | 0 | 8.7404 | 37.78
2020-12-12 06:30 | 44177.2708 | 0 | 8.996 | 37.78
2020-12-12 07:00 | 44177.2917 | 0 | 9.4634 | 37.78
2020-12-12 07:30 | 44177.3125 | 0 | 9.3959 | 37.78
2020-12-12 08:00 | 44177.3333 | 0 | 9.9005 | 37.78
2020-12-12 08:30 | 44177.3542 | 0 | 10.6067 | 37.78
2020-12-12 09:00 | 44177.375 | 0 | 9.9017 | 37.78
2020-12-12 09:30 | 44177.3958 | 0 | 10.288 | 37.78
2020-12-12 10:00 | 44177.4167 | 0 | 10.3962 | 37.78
2020-12-12 10:30 | 44177.4375 | 0 | 10.0842 | 37.78
2020-12-12 11:00 | 44177.4583 | 0 | 9.7656 | 37.78
2020-12-12 11:30 | 44177.4792 | 0 | 9.1368 | 37.78
2020-12-12 12:00 | 44177.5 | 0 | 9.5382 | 37.78
2020-12-12 12:30 | 44177.5208 | 0 | 9.6321 | 37.78
2020-12-12 13:00 | 44177.5417 | 0 | 7.5248 | 37.78
2020-12-12 13:30 | 44177.5625 | 0 | 6.5723 | 37.78
2020-12-12 14:00 | 44177.5833 | 0 | 6.8642 | 37.78
2020-12-12 14:30 | 44177.6042 | 0 | 7.739 | 37.78
2020-12-12 15:00 | 44177.625 | 0 | 9.0043 | 37.78
2020-12-12 15:30 | 44177.6458 | 0 | 8.9005 | 37.78
2020-12-12 16:00 | 44177.6667 | 0 | 9.3319 | 37.78
2020-12-12 16:30 | 44177.6875 | 0 | 9.8071 | 37.78
2020-12-12 17:00 | 44177.7083 | 0 | 10.697 | 37.78
2020-12-12 17:30 | 44177.7292 | 0 | 11.1968 | 37.78
2020-12-12 18:00 | 44177.75 | 0 | 11.0729 | 37.78
2020-12-12 18:30 | 44177.7708 | 0 | 11.4492 | 37.78
2020-12-12 19:00 | 44177.7917 | 0 | 11.393 | 37.78
2020-12-12 19:30 | 44177.8125 | 0 | 11.1663 | 37.78
2020-12-12 20:00 | 44177.8333 | 0 | 11.016 | 37.78
2020-12-12 20:30 | 44177.8542 | 0 | 10.4638 | 37.78
2020-12-12 21:00 | 44177.875 | 0 | 10.2148 | 37.78
2020-12-12 21:30 | 44177.8958 | 0 | 9.9766 | 37.78
2020-12-12 22:00 | 44177.9167 | 0 | 9.626 | 37.78
2020-12-12 22:30 | 44177.9375 | 0 | 9.2001 | 37.78
2020-12-12 23:00 | 44177.9583 | 0 | 8.6908 | 37.78
2020-12-12 23:30 | 44177.9792 | 0 | 8.326 | 37.78
2020-12-13 | 44178 | 0 | 7.993 | 37.78
2020-12-13 00:30 | 44178.0208 | 0 | 7.7779 | 37.78
2020-12-13 01:00 | 44178.0417 | 0 | 7.7 | 37.78
2020-12-13 01:30 | 44178.0625 | 0 | 7.5383 | 37.78
2020-12-13 02:00 | 44178.0833 | 0 | 7.5159 | 37.78
2020-12-13 02:30 | 44178.1042 | 0 | 7.2026 | 37.78
2020-12-13 03:00 | 44178.125 | 0 | 7.2087 | 37.78
2020-12-13 03:30 | 44178.1458 | 0 | 7.1774 | 37.78
2020-12-13 04:00 | 44178.1667 | 0 | 7.2019 | 37.78
2020-12-13 04:30 | 44178.1875 | 0 | 7.2398 | 37.78
2020-12-13 05:00 | 44178.2083 | 0 | 7.2724 | 37.78
2020-12-13 05:30 | 44178.2292 | 0 | 7.2243 | 37.78
2020-12-13 06:00 | 44178.25 | 0 | 7.6193 | 37.78
2020-12-13 06:30 | 44178.2708 | 0 | 7.8564 | 37.78
2020-12-13 07:00 | 44178.2917 | 0 | 8.5951 | 37.78
2020-12-13 07:30 | 44178.3125 | 0 | 8.2713 | 37.78
2020-12-13 08:00 | 44178.3333 | 0 | 9.2743 | 37.78
2020-12-13 08:30 | 44178.3542 | 0 | 9.488 | 37.78
2020-12-13 09:00 | 44178.375 | 0 | 9.6795 | 37.78
2020-12-13 09:30 | 44178.3958 | 0 | 10.4127 | 37.78
2020-12-13 10:00 | 44178.4167 | 0 | 10.6544 | 37.78
2020-12-13 10:30 | 44178.4375 | 0 | 10.6628 | 37.78
2020-12-13 11:00 | 44178.4583 | 0 | 10.0336 | 37.78
2020-12-13 11:30 | 44178.4792 | 0 | 10.2658 | 37.78
2020-12-13 12:00 | 44178.5 | 0 | 10.4415 | 37.78
2020-12-13 12:30 | 44178.5208 | 0 | 10.2691 | 37.78
2020-12-13 13:00 | 44178.5417 | 0 | 10.2575 | 37.78
2020-12-13 13:30 | 44178.5625 | 0 | 9.6741 | 37.78
2020-12-13 14:00 | 44178.5833 | 0 | 9.3418 | 37.78
2020-12-13 14:30 | 44178.6042 | 0 | 9.4479 | 37.78
2020-12-13 15:00 | 44178.625 | 0 | 9.6991 | 37.78
2020-12-13 15:30 | 44178.6458 | 0 | 9.9232 | 37.78
2020-12-13 16:00 | 44178.6667 | 0 | 10.1495 | 37.78
2020-12-13 16:30 | 44178.6875 | 0 | 10.6404 | 37.78
2020-12-13 17:00 | 44178.7083 | 0 | 10.7609 | 37.78
2020-12-13 17:30 | 44178.7292 | 0 | 10.8835 | 37.78
2020-12-13 18:00 | 44178.75 | 0 | 10.9977 | 37.78
2020-12-13 18:30 | 44178.7708 | 0 | 11.5088 | 37.78
2020-12-13 19:00 | 44178.7917 | 0 | 11.5906 | 37.78
2020-12-13 19:30 | 44178.8125 | 0 | 11.0817 | 37.78
2020-12-13 20:00 | 44178.8333 | 0 | 11.0699 | 37.78
2020-12-13 20:30 | 44178.8542 | 0 | 10.6486 | 37.78
2020-12-13 21:00 | 44178.875 | 0 | 10.4706 | 37.78
2020-12-13 21:30 | 44178.8958 | 0 | 10.1877 | 37.78
2020-12-13 22:00 | 44178.9167 | 0 | 9.8266 | 37.78
2020-12-13 22:30 | 44178.9375 | 0 | 9.5996 | 37.78
2020-12-13 23:00 | 44178.9583 | 0 | 9.0975 | 37.78
2020-12-13 23:30 | 44178.9792 | 0 | 8.7547 | 37.78
2020-12-14 | 44179 | 0 | 8.4905 | 37.78
2020-12-14 00:30 | 44179.0208 | 0 | 8.326 | 37.78
2020-12-14 01:00 | 44179.0417 | 0 | 8.2191 | 37.78
2020-12-14 01:30 | 44179.0625 | 0 | 8.236 | 37.78
2020-12-14 02:00 | 44179.0833 | 0 | 8.3456 | 37.78
2020-12-14 02:30 | 44179.1042 | 0 | 8.1805 | 37.78
2020-12-14 03:00 | 44179.125 | 0 | 7.7902 | 37.78
2020-12-14 03:30 | 44179.1458 | 0 | 7.9782 | 37.78
2020-12-14 04:00 | 44179.1667 | 0 | 8.265 | 37.78
2020-12-14 04:30 | 44179.1875 | 0 | 8.7901 | 37.78
2020-12-14 05:00 | 44179.2083 | 0 | 9.2383 | 37.78
2020-12-14 05:30 | 44179.2292 | 0 | 9.912 | 37.78
2020-12-14 06:00 | 44179.25 | 0 | 10.477 | 37.78
2020-12-14 06:30 | 44179.2708 | 0 | 11.382 | 37.78
2020-12-14 07:00 | 44179.2917 | 0 | 12.4471 | 37.78
2020-12-14 07:30 | 44179.3125 | 0 | 12.9376 | 37.78
2020-12-14 08:00 | 44179.3333 | 0 | 13.3089 | 37.78
2020-12-14 08:30 | 44179.3542 | 0 | 13.296 | 37.78
2020-12-14 09:00 | 44179.375 | 0 | 13.4138 | 37.78
2020-12-14 09:30 | 44179.3958 | 0 | 12.3454 | 37.78
2020-12-14 10:00 | 44179.4167 | 0 | 12.4585 | 37.78
2020-12-14 10:30 | 44179.4375 | 0 | 13.4061 | 37.78
2020-12-14 11:00 | 44179.4583 | 0 | 13.9775 | 37.78
2020-12-14 11:30 | 44179.4792 | 0 | 13.7905 | 37.78
2020-12-14 12:00 | 44179.5 | 0 | 10.6462 | 37.78
2020-12-14 12:30 | 44179.5208 | 0 | 11.9975 | 37.78
2020-12-14 13:00 | 44179.5417 | 0 | 13.1418 | 37.78
2020-12-14 13:30 | 44179.5625 | 0 | 12.7855 | 37.78
2020-12-14 14:00 | 44179.5833 | 0 | 11.8921 | 37.78
2020-12-14 14:30 | 44179.6042 | 0 | 12.9228 | 37.78
2020-12-14 15:00 | 44179.625 | 0 | 12.9488 | 37.78
2020-12-14 15:30 | 44179.6458 | 0 | 12.8444 | 37.78
2020-12-14 16:00 | 44179.6667 | 0 | 12.8056 | 37.78
2020-12-14 16:30 | 44179.6875 | 0 | 13.5234 | 37.78
2020-12-14 17:00 | 44179.7083 | 0 | 13.8131 | 37.78
2020-12-14 17:30 | 44179.7292 | 0 | 14.0046 | 37.78
2020-12-14 18:00 | 44179.75 | 0 | 14.2866 | 37.78
2020-12-14 18:30 | 44179.7708 | 0 | 14.9093 | 37.78
2020-12-14 19:00 | 44179.7917 | 0 | 14.8617 | 37.78
2020-12-14 19:30 | 44179.8125 | 0 | 14.2827 | 37.78
2020-12-14 20:00 | 44179.8333 | 0 | 14.0832 | 37.78
2020-12-14 20:30 | 44179.8542 | 0 | 13.5904 | 37.78
2020-12-14 21:00 | 44179.875 | 0 | 13.2025 | 37.78
2020-12-14 21:30 | 44179.8958 | 0 | 12.7274 | 37.78
2020-12-14 22:00 | 44179.9167 | 0 | 12.1643 | 37.78
2020-12-14 22:30 | 44179.9375 | 0 | 11.4388 | 37.78
2020-12-14 23:00 | 44179.9583 | 0 | 10.6797 | 37.78
2020-12-14 23:30 | 44179.9792 | 0 | 10.3627 | 37.78
2020-12-15 | 44180 | 0 | 9.7614 | 37.78
2020-12-15 00:30 | 44180.0208 | 0 | 9.3208 | 37.78
2020-12-15 01:00 | 44180.0417 | 0 | 9.3012 | 37.78
2020-12-15 01:30 | 44180.0625 | 0 | 8.975 | 37.78
2020-12-15 02:00 | 44180.0833 | 0 | 9.0813 | 37.78
2020-12-15 02:30 | 44180.1042 | 0 | 8.8295 | 37.78
2020-12-15 03:00 | 44180.125 | 0 | 8.7172 | 37.78
2020-12-15 03:30 | 44180.1458 | 0 | 8.9317 | 37.78
2020-12-15 04:00 | 44180.1667 | 0 | 9.0752 | 37.78
2020-12-15 04:30 | 44180.1875 | 0 | 9.4177 | 37.78
2020-12-15 05:00 | 44180.2083 | 0 | 9.7398 | 37.78
2020-12-15 05:30 | 44180.2292 | 0 | 10.2407 | 37.78
2020-12-15 06:00 | 44180.25 | 0 | 10.7633 | 37.78
2020-12-15 06:30 | 44180.2708 | 0 | 11.465 | 37.78
2020-12-15 07:00 | 44180.2917 | 0 | 12.0718 | 37.78
2020-12-15 07:30 | 44180.3125 | 0 | 12.4938 | 37.78
2020-12-15 08:00 | 44180.3333 | 0 | 13.1323 | 37.78
2020-12-15 08:30 | 44180.3542 | 0 | 14.0826 | 37.78
2020-12-15 09:00 | 44180.375 | 0 | 13.6457 | 37.78
2020-12-15 09:30 | 44180.3958 | 0 | 14.1791 | 37.78
2020-12-15 10:00 | 44180.4167 | 0 | 15.3806 | 37.78
2020-12-15 10:30 | 44180.4375 | 0 | 14.7033 | 37.78
2020-12-15 11:00 | 44180.4583 | 0 | 13.5206 | 37.78
2020-12-15 11:30 | 44180.4792 | 0 | 14.0632 | 37.78
2020-12-15 12:00 | 44180.5 | 0 | 14.1578 | 37.78
2020-12-15 12:30 | 44180.5208 | 0 | 13.825 | 37.78
2020-12-15 13:00 | 44180.5417 | 0 | 14.5452 | 37.78
2020-12-15 13:30 | 44180.5625 | 0 | 14.388 | 37.78
2020-12-15 14:00 | 44180.5833 | 0 | 15.1955 | 37.78
2020-12-15 14:30 | 44180.6042 | 0 | 15.6807 | 37.78
2020-12-15 15:00 | 44180.625 | 0 | 16.4979 | 37.78
2020-12-15 15:30 | 44180.6458 | 0 | 16.5941 | 37.78
2020-12-15 16:00 | 44180.6667 | 0 | 16.8601 | 37.78
2020-12-15 16:30 | 44180.6875 | 0 | 17.2556 | 37.78
2020-12-15 17:00 | 44180.7083 | 0 | 17.3366 | 37.78
2020-12-15 17:30 | 44180.7292 | 0 | 17.3586 | 37.78
2020-12-15 18:00 | 44180.75 | 0 | 17.3159 | 37.78
2020-12-15 18:30 | 44180.7708 | 0 | 17.6978 | 37.78
2020-12-15 19:00 | 44180.7917 | 0 | 17.8539 | 37.78
2020-12-15 19:30 | 44180.8125 | 0 | 17.7402 | 37.78
2020-12-15 20:00 | 44180.8333 | 0 | 17.4837 | 37.78
2020-12-15 20:30 | 44180.8542 | 0 | 16.8271 | 37.78
2020-12-15 21:00 | 44180.875 | 0 | 15.8365 | 37.78
2020-12-15 21:30 | 44180.8958 | 0 | 15.3317 | 37.78
2020-12-15 22:00 | 44180.9167 | 0 | 14.481 | 37.78
2020-12-15 22:30 | 44180.9375 | 0 | 13.4757 | 37.78
2020-12-15 23:00 | 44180.9583 | 0 | 12.6214 | 37.78
2020-12-15 23:30 | 44180.9792 | 0 | 11.9689 | 37.78
2020-12-16 | 44181 | 0 | 11.1223 | 37.78
2020-12-16 00:30 | 44181.0208 | 0 | 10.5585 | 37.78
2020-12-16 01:00 | 44181.0417 | 0 | 10.4212 | 37.78
2020-12-16 01:30 | 44181.0625 | 0 | 10.2987 | 37.78
2020-12-16 02:00 | 44181.0833 | 0 | 10.2284 | 37.78
2020-12-16 02:30 | 44181.1042 | 0 | 10.0889 | 37.78
2020-12-16 03:00 | 44181.125 | 0 | 10.0497 | 37.78
2020-12-16 03:30 | 44181.1458 | 0 | 10.2349 | 37.78
2020-12-16 04:00 | 44181.1667 | 0 | 10.4517 | 37.78
2020-12-16 04:30 | 44181.1875 | 0 | 10.7379 | 37.78
2020-12-16 05:00 | 44181.2083 | 0 | 11.1336 | 37.78
2020-12-16 05:30 | 44181.2292 | 0 | 11.2861 | 37.78
2020-12-16 06:00 | 44181.25 | 0 | 12.4122 | 37.78
2020-12-16 06:30 | 44181.2708 | 0 | 13.2781 | 37.78
2020-12-16 07:00 | 44181.2917 | 0 | 14.516 | 37.78
2020-12-16 07:30 | 44181.3125 | 0 | 15.1756 | 37.78
2020-12-16 08:00 | 44181.3333 | 0 | 14.4942 | 37.78
2020-12-16 08:30 | 44181.3542 | 0 | 14.9509 | 37.78
2020-12-16 09:00 | 44181.375 | 0 | 15.457 | 37.78
2020-12-16 09:30 | 44181.3958 | 0 | 15.9721 | 37.78
2020-12-16 10:00 | 44181.4167 | 0 | 15.5267 | 37.78
2020-12-16 10:30 | 44181.4375 | 0 | 15.1993 | 37.78
2020-12-16 11:00 | 44181.4583 | 0 | 15.5141 | 37.78
2020-12-16 11:30 | 44181.4792 | 0 | 15.9165 | 37.78
2020-12-16 12:00 | 44181.5 | 0 | 17.3141 | 37.78
2020-12-16 12:30 | 44181.5208 | 0 | 15.455 | 37.78
2020-12-16 13:00 | 44181.5417 | 0 | 15.9149 | 37.78
2020-12-16 13:30 | 44181.5625 | 0 | 16.484 | 37.78
2020-12-16 14:00 | 44181.5833 | 0 | 17.2038 | 37.78
2020-12-16 14:30 | 44181.6042 | 0 | 18.4194 | 37.78
2020-12-16 15:00 | 44181.625 | 0 | 18.8536 | 37.78
2020-12-16 15:30 | 44181.6458 | 0 | 18.3082 | 37.78
2020-12-16 16:00 | 44181.6667 | 0 | 18.119 | 37.78
2020-12-16 16:30 | 44181.6875 | 0 | 18.2007 | 37.78
2020-12-16 17:00 | 44181.7083 | 0 | 17.5774 | 37.78
2020-12-16 17:30 | 44181.7292 | 0 | 17.5047 | 37.78
2020-12-16 18:00 | 44181.75 | 0 | 17.4119 | 37.78
2020-12-16 18:30 | 44181.7708 | 0 | 17.762 | 37.78
2020-12-16 19:00 | 44181.7917 | 0 | 17.2632 | 37.78
2020-12-16 19:30 | 44181.8125 | 0 | 17.1827 | 37.78
2020-12-16 20:00 | 44181.8333 | 0 | 16.7092 | 37.78
2020-12-16 20:30 | 44181.8542 | 0 | 16.0911 | 37.78
2020-12-16 21:00 | 44181.875 | 0 | 15.5148 | 37.78
2020-12-16 21:30 | 44181.8958 | 0 | 15.0276 | 37.78
2020-12-16 22:00 | 44181.9167 | 0 | 14.4879 | 37.78
2020-12-16 22:30 | 44181.9375 | 0 | 13.7229 | 37.78
2020-12-16 23:00 | 44181.9583 | 0 | 13.0766 | 37.78
2020-12-16 23:30 | 44181.9792 | 0 | 12.612 | 37.78
2020-12-17 | 44182 | 0 | 11.7346 | 37.78
2020-12-17 00:30 | 44182.0208 | 0 | 11.2418 | 37.78
2020-12-17 01:00 | 44182.0417 | 0 | 10.8564 | 37.78
2020-12-17 01:30 | 44182.0625 | 0 | 10.5624 | 37.78
2020-12-17 02:00 | 44182.0833 | 0 | 10.5676 | 37.78
2020-12-17 02:30 | 44182.1042 | 0 | 10.1864 | 37.78
2020-12-17 03:00 | 44182.125 | 0 | 10.1078 | 37.78
2020-12-17 03:30 | 44182.1458 | 0 | 10.3508 | 37.78
2020-12-17 04:00 | 44182.1667 | 0 | 10.5814 | 37.78
2020-12-17 04:30 | 44182.1875 | 0 | 10.9286 | 37.78
2020-12-17 05:00 | 44182.2083 | 0 | 11.3591 | 37.78
2020-12-17 05:30 | 44182.2292 | 0 | 11.7394 | 37.78
2020-12-17 06:00 | 44182.25 | 0 | 12.5172 | 37.78
2020-12-17 06:30 | 44182.2708 | 0 | 13.4349 | 37.78
2020-12-17 07:00 | 44182.2917 | 0 | 14.5911 | 37.78
2020-12-17 07:30 | 44182.3125 | 0 | 14.6587 | 37.78
2020-12-17 08:00 | 44182.3333 | 0 | 15.1928 | 37.78
2020-12-17 08:30 | 44182.3542 | 0 | 14.4945 | 37.78
2020-12-17 09:00 | 44182.375 | 0 | 14.6723 | 37.78
2020-12-17 09:30 | 44182.3958 | 0 | 16.7865 | 37.78
2020-12-17 10:00 | 44182.4167 | 0 | 15.1958 | 37.78
2020-12-17 10:30 | 44182.4375 | 0 | 14.1774 | 37.78
2020-12-17 11:00 | 44182.4583 | 0 | 13.9065 | 37.78
2020-12-17 11:30 | 44182.4792 | 0 | 16.6743 | 37.78
2020-12-17 12:00 | 44182.5 | 0 | 15.6909 | 37.78
2020-12-17 12:30 | 44182.5208 | 0 | 14.3312 | 37.78
2020-12-17 13:00 | 44182.5417 | 0 | 15.1504 | 37.78
2020-12-17 13:30 | 44182.5625 | 0 | 15.9999 | 37.78
2020-12-17 14:00 | 44182.5833 | 0 | 15.6387 | 37.78
2020-12-17 14:30 | 44182.6042 | 0 | 16.051 | 37.78
2020-12-17 15:00 | 44182.625 | 0 | 16.0414 | 37.78
2020-12-17 15:30 | 44182.6458 | 0 | 16.4591 | 37.78
2020-12-17 16:00 | 44182.6667 | 0 | 16.8306 | 37.78
2020-12-17 16:30 | 44182.6875 | 0 | 16.8224 | 37.78
2020-12-17 17:00 | 44182.7083 | 0 | 17.0947 | 37.78
2020-12-17 17:30 | 44182.7292 | 0 | 17.0114 | 37.78
2020-12-17 18:00 | 44182.75 | 0 | 16.595 | 37.78
2020-12-17 18:30 | 44182.7708 | 0 | 16.933 | 37.78
2020-12-17 19:00 | 44182.7917 | 0 | 17.0146 | 37.78
2020-12-17 19:30 | 44182.8125 | 0 | 17.253 | 37.78
2020-12-17 20:00 | 44182.8333 | 0 | 17.0421 | 37.78
2020-12-17 20:30 | 44182.8542 | 0 | 16.5138 | 37.78
2020-12-17 21:00 | 44182.875 | 0 | 15.917 | 37.78
2020-12-17 21:30 | 44182.8958 | 0 | 15.78 | 37.78
2020-12-17 22:00 | 44182.9167 | 0 | 15.0637 | 37.78
2020-12-17 22:30 | 44182.9375 | 0 | 13.9032 | 37.78
2020-12-17 23:00 | 44182.9583 | 0 | 13.149 | 37.78
2020-12-17 23:30 | 44182.9792 | 0 | 12.3216 | 37.78
2020-12-18 | 44183 | 0 | 11.6132 | 37.78
2020-12-18 00:30 | 44183.0208 | 0 | 11.1794 | 37.78
2020-12-18 01:00 | 44183.0417 | 0 | 10.7322 | 37.78
2020-12-18 01:30 | 44183.0625 | 0 | 10.7346 | 37.78
2020-12-18 02:00 | 44183.0833 | 0 | 10.6661 | 37.78
2020-12-18 02:30 | 44183.1042 | 0 | 10.6123 | 37.78
2020-12-18 03:00 | 44183.125 | 0 | 10.6615 | 37.78
2020-12-18 03:30 | 44183.1458 | 0 | 10.6038 | 37.78
2020-12-18 04:00 | 44183.1667 | 0 | 10.6796 | 37.78
2020-12-18 04:30 | 44183.1875 | 0 | 10.8612 | 37.78
2020-12-18 05:00 | 44183.2083 | 0 | 11.264 | 37.78
2020-12-18 05:30 | 44183.2292 | 0 | 11.7847 | 37.78
2020-12-18 06:00 | 44183.25 | 0 | 12.4437 | 37.78
2020-12-18 06:30 | 44183.2708 | 0 | 13.1823 | 37.78
2020-12-18 07:00 | 44183.2917 | 0 | 14.234 | 37.78
2020-12-18 07:30 | 44183.3125 | 0 | 15.0644 | 37.78
2020-12-18 08:00 | 44183.3333 | 0 | 15.4139 | 37.78
2020-12-18 08:30 | 44183.3542 | 0 | 15.0083 | 37.78
2020-12-18 09:00 | 44183.375 | 0 | 15.3418 | 37.78
2020-12-18 09:30 | 44183.3958 | 0 | 14.8922 | 37.78
2020-12-18 10:00 | 44183.4167 | 0 | 14.5995 | 37.78
2020-12-18 10:30 | 44183.4375 | 0 | 15.2599 | 37.78
2020-12-18 11:00 | 44183.4583 | 0 | 15.454 | 37.78
2020-12-18 11:30 | 44183.4792 | 0 | 15.2773 | 37.78
2020-12-18 12:00 | 44183.5 | 0 | 15.8842 | 37.78
2020-12-18 12:30 | 44183.5208 | 0 | 15.813 | 37.78
2020-12-18 13:00 | 44183.5417 | 0 | 16.6043 | 37.78
2020-12-18 13:30 | 44183.5625 | 0 | 16.8852 | 37.78
2020-12-18 14:00 | 44183.5833 | 0 | 16.9924 | 37.78
2020-12-18 14:30 | 44183.6042 | 0 | 17.0571 | 37.78
2020-12-18 15:00 | 44183.625 | 0 | 17.4928 | 37.78
2020-12-18 15:30 | 44183.6458 | 0 | 18.2849 | 37.78
2020-12-18 16:00 | 44183.6667 | 0 | 18.651 | 37.78
2020-12-18 16:30 | 44183.6875 | 0 | 18.9698 | 37.78
2020-12-18 17:00 | 44183.7083 | 0 | 18.8362 | 37.78
2020-12-18 17:30 | 44183.7292 | 0 | 18.5374 | 37.78
2020-12-18 18:00 | 44183.75 | 0 | 18.1181 | 37.78
2020-12-18 18:30 | 44183.7708 | 0 | 18.4332 | 37.78
2020-12-18 19:00 | 44183.7917 | 0 | 18.1924 | 37.78
2020-12-18 19:30 | 44183.8125 | 0 | 18.2113 | 37.78
2020-12-18 20:00 | 44183.8333 | 0 | 17.9611 | 37.78
2020-12-18 20:30 | 44183.8542 | 0 | 17.4816 | 37.78
2020-12-18 21:00 | 44183.875 | 0 | 16.8029 | 37.78
2020-12-18 21:30 | 44183.8958 | 0 | 16.286 | 37.78
2020-12-18 22:00 | 44183.9167 | 0 | 15.6548 | 37.78
2020-12-18 22:30 | 44183.9375 | 0 | 14.7998 | 37.78
2020-12-18 23:00 | 44183.9583 | 0 | 13.9454 | 37.78
2020-12-18 23:30 | 44183.9792 | 0 | 13.3171 | 37.78
2020-12-19 | 44184 | 0 | 12.4797 | 37.78
2020-12-19 00:30 | 44184.0208 | 0 | 11.9137 | 37.78
2020-12-19 01:00 | 44184.0417 | 0 | 11.5953 | 37.78
2020-12-19 01:30 | 44184.0625 | 0 | 11.437 | 37.78
2020-12-19 02:00 | 44184.0833 | 0 | 11.3553 | 37.78
2020-12-19 02:30 | 44184.1042 | 0 | 11.0361 | 37.78
2020-12-19 03:00 | 44184.125 | 0 | 10.7792 | 37.78
2020-12-19 03:30 | 44184.1458 | 0 | 10.8075 | 37.78
2020-12-19 04:00 | 44184.1667 | 0 | 10.9641 | 37.78
2020-12-19 04:30 | 44184.1875 | 0 | 10.8983 | 37.78
2020-12-19 05:00 | 44184.2083 | 0 | 10.943 | 37.78
2020-12-19 05:30 | 44184.2292 | 0 | 11.0235 | 37.78
2020-12-19 06:00 | 44184.25 | 0 | 11.3508 | 37.78
2020-12-19 06:30 | 44184.2708 | 0 | 11.3241 | 37.78
2020-12-19 07:00 | 44184.2917 | 0 | 12.1301 | 37.78
2020-12-19 07:30 | 44184.3125 | 0 | 12.3178 | 37.78
2020-12-19 08:00 | 44184.3333 | 0 | 13.1518 | 37.78
2020-12-19 08:30 | 44184.3542 | 0 | 12.4967 | 37.78
2020-12-19 09:00 | 44184.375 | 0 | 11.9659 | 37.78
2020-12-19 09:30 | 44184.3958 | 0 | 14.3982 | 37.78
2020-12-19 10:00 | 44184.4167 | 0 | 15.1933 | 37.78
2020-12-19 10:30 | 44184.4375 | 0 | 15.433 | 37.78
2020-12-19 11:00 | 44184.4583 | 0 | 14.6758 | 37.78
2020-12-19 11:30 | 44184.4792 | 0 | 14.0265 | 37.78
2020-12-19 12:00 | 44184.5 | 0 | 12.1941 | 37.78
2020-12-19 12:30 | 44184.5208 | 0 | 12.9845 | 37.78
2020-12-19 13:00 | 44184.5417 | 0 | 13.688 | 37.78
2020-12-19 13:30 | 44184.5625 | 0 | 13.8672 | 37.78
2020-12-19 14:00 | 44184.5833 | 0 | 14.3773 | 37.78
2020-12-19 14:30 | 44184.6042 | 0 | 14.9699 | 37.78
2020-12-19 15:00 | 44184.625 | 0 | 15.4843 | 37.78
2020-12-19 15:30 | 44184.6458 | 0 | 15.8777 | 37.78
2020-12-19 16:00 | 44184.6667 | 0 | 16.3923 | 37.78
2020-12-19 16:30 | 44184.6875 | 0 | 16.8601 | 37.78
2020-12-19 17:00 | 44184.7083 | 0 | 17.0786 | 37.78
2020-12-19 17:30 | 44184.7292 | 0 | 16.9342 | 37.78
2020-12-19 18:00 | 44184.75 | 0 | 16.6206 | 37.78
2020-12-19 18:30 | 44184.7708 | 0 | 16.6288 | 37.78
2020-12-19 19:00 | 44184.7917 | 0 | 16.523 | 37.78
2020-12-19 19:30 | 44184.8125 | 0 | 16.3833 | 37.78
2020-12-19 20:00 | 44184.8333 | 0 | 16.1162 | 37.78
2020-12-19 20:30 | 44184.8542 | 0 | 15.5006 | 37.78
2020-12-19 21:00 | 44184.875 | 0 | 14.8856 | 37.78
2020-12-19 21:30 | 44184.8958 | 0 | 14.2571 | 37.78
2020-12-19 22:00 | 44184.9167 | 0 | 13.8106 | 37.78
2020-12-19 22:30 | 44184.9375 | 0 | 13.142 | 37.78
2020-12-19 23:00 | 44184.9583 | 0 | 12.3578 | 37.78
2020-12-19 23:30 | 44184.9792 | 0 | 11.8989 | 37.78
2020-12-20 | 44185 | 0 | 11.3328 | 37.78
2020-12-20 00:30 | 44185.0208 | 0 | 10.9285 | 37.78
2020-12-20 01:00 | 44185.0417 | 0 | 10.7016 | 37.78
2020-12-20 01:30 | 44185.0625 | 0 | 10.3317 | 37.78
2020-12-20 02:00 | 44185.0833 | 0 | 10.2252 | 37.78
2020-12-20 02:30 | 44185.1042 | 0 | 9.8934 | 37.78
2020-12-20 03:00 | 44185.125 | 0 | 9.8069 | 37.78
2020-12-20 03:30 | 44185.1458 | 0 | 9.6802 | 37.78
2020-12-20 04:00 | 44185.1667 | 0 | 9.63 | 37.78
2020-12-20 04:30 | 44185.1875 | 0 | 9.4316 | 37.78
2020-12-20 05:00 | 44185.2083 | 0 | 9.3884 | 37.78
2020-12-20 05:30 | 44185.2292 | 0 | 9.1741 | 37.78
2020-12-20 06:00 | 44185.25 | 0 | 9.4588 | 37.78
2020-12-20 06:30 | 44185.2708 | 0 | 9.2728 | 37.78
2020-12-20 07:00 | 44185.2917 | 0 | 9.4633 | 37.78
2020-12-20 07:30 | 44185.3125 | 0 | 9.9752 | 37.78
2020-12-20 08:00 | 44185.3333 | 0 | 10.2832 | 37.78
2020-12-20 08:30 | 44185.3542 | 0 | 10.7826 | 37.78
2020-12-20 09:00 | 44185.375 | 0 | 11.9156 | 37.78
2020-12-20 09:30 | 44185.3958 | 0 | 11.9039 | 37.78
2020-12-20 10:00 | 44185.4167 | 0 | 11.5874 | 37.78
2020-12-20 10:30 | 44185.4375 | 0 | 11.4763 | 37.78
2020-12-20 11:00 | 44185.4583 | 0 | 11.5906 | 37.78
2020-12-20 11:30 | 44185.4792 | 0 | 11.8862 | 37.78
2020-12-20 12:00 | 44185.5 | 0 | 12.1309 | 37.78
2020-12-20 12:30 | 44185.5208 | 0 | 12.3415 | 37.78
2020-12-20 13:00 | 44185.5417 | 0 | 12.7332 | 37.78
2020-12-20 13:30 | 44185.5625 | 0 | 13.1397 | 37.78
2020-12-20 14:00 | 44185.5833 | 0 | 13.7635 | 37.78
2020-12-20 14:30 | 44185.6042 | 0 | 14.107 | 37.78
2020-12-20 15:00 | 44185.625 | 0 | 14.5598 | 37.78
2020-12-20 15:30 | 44185.6458 | 0 | 15.2912 | 37.78
2020-12-20 16:00 | 44185.6667 | 0 | 16.3074 | 37.78
2020-12-20 16:30 | 44185.6875 | 0 | 16.6056 | 37.78
2020-12-20 17:00 | 44185.7083 | 0 | 16.4977 | 37.78
2020-12-20 17:30 | 44185.7292 | 0 | 16.4593 | 37.78
2020-12-20 18:00 | 44185.75 | 0 | 16.2595 | 37.78
2020-12-20 18:30 | 44185.7708 | 0 | 16.4517 | 37.78
2020-12-20 19:00 | 44185.7917 | 0 | 16.4517 | 37.78
2020-12-20 19:30 | 44185.8125 | 0 | 16.3564 | 37.78
2020-12-20 20:00 | 44185.8333 | 0 | 16.2279 | 37.78
2020-12-20 20:30 | 44185.8542 | 0 | 15.5499 | 37.78
2020-12-20 21:00 | 44185.875 | 0 | 14.7041 | 37.78
2020-12-20 21:30 | 44185.8958 | 0 | 14.2269 | 37.78
2020-12-20 22:00 | 44185.9167 | 0 | 13.5293 | 37.78
2020-12-20 22:30 | 44185.9375 | 0 | 12.7871 | 37.78
2020-12-20 23:00 | 44185.9583 | 0 | 12.269 | 37.78
2020-12-20 23:30 | 44185.9792 | 0 | 11.6169 | 37.78
2020-12-21 | 44186 | 0 | 11.2663 | 37.78
2020-12-21 00:30 | 44186.0208 | 0 | 10.9383 | 37.78
2020-12-21 01:00 | 44186.0417 | 0 | 10.7239 | 37.78
2020-12-21 01:30 | 44186.0625 | 0 | 10.635 | 37.78
2020-12-21 02:00 | 44186.0833 | 0 | 10.6346 | 37.78
2020-12-21 02:30 | 44186.1042 | 0 | 10.389 | 37.78
2020-12-21 03:00 | 44186.125 | 0 | 10.2149 | 37.78
2020-12-21 03:30 | 44186.1458 | 0 | 10.2195 | 37.78
2020-12-21 04:00 | 44186.1667 | 0 | 10.4205 | 37.78
2020-12-21 04:30 | 44186.1875 | 0 | 10.8237 | 37.78
2020-12-21 05:00 | 44186.2083 | 0 | 11.1667 | 37.78
2020-12-21 05:30 | 44186.2292 | 0 | 11.5321 | 37.78
2020-12-21 06:00 | 44186.25 | 0 | 12.2924 | 37.78
2020-12-21 06:30 | 44186.2708 | 0 | 13.0298 | 37.78
2020-12-21 07:00 | 44186.2917 | 0 | 13.6004 | 37.78
2020-12-21 07:30 | 44186.3125 | 0 | 13.8521 | 37.78
2020-12-21 08:00 | 44186.3333 | 0 | 14.5743 | 37.78
2020-12-21 08:30 | 44186.3542 | 0 | 16.4535 | 37.78
2020-12-21 09:00 | 44186.375 | 0 | 16.5414 | 37.78
2020-12-21 09:30 | 44186.3958 | 0 | 16.6397 | 37.78
2020-12-21 10:00 | 44186.4167 | 0 | 16.8468 | 37.78
2020-12-21 10:30 | 44186.4375 | 0 | 15.3071 | 37.78
2020-12-21 11:00 | 44186.4583 | 0 | 16.2391 | 37.78
2020-12-21 11:30 | 44186.4792 | 0 | 16.9166 | 37.78
2020-12-21 12:00 | 44186.5 | 0 | 16.2817 | 37.78
2020-12-21 12:30 | 44186.5208 | 0 | 16.4595 | 37.78
2020-12-21 13:00 | 44186.5417 | 0 | 16.7999 | 37.78
2020-12-21 13:30 | 44186.5625 | 0 | 17.8393 | 37.78
2020-12-21 14:00 | 44186.5833 | 0 | 17.6328 | 37.78
2020-12-21 14:30 | 44186.6042 | 0 | 18.34 | 37.78
2020-12-21 15:00 | 44186.625 | 0 | 18.6766 | 37.78
2020-12-21 15:30 | 44186.6458 | 0 | 19.6467 | 37.78
2020-12-21 16:00 | 44186.6667 | 0 | 18.9022 | 37.78
2020-12-21 16:30 | 44186.6875 | 0 | 19.912 | 37.78
2020-12-21 17:00 | 44186.7083 | 0 | 19.0906 | 37.78
2020-12-21 17:30 | 44186.7292 | 0 | 18.8938 | 37.78
2020-12-21 18:00 | 44186.75 | 0 | 18.713 | 37.78
2020-12-21 18:30 | 44186.7708 | 0 | 18.7148 | 37.78
2020-12-21 19:00 | 44186.7917 | 0 | 18.7906 | 37.78
2020-12-21 19:30 | 44186.8125 | 0 | 18.6389 | 37.78
2020-12-21 20:00 | 44186.8333 | 0 | 18.4857 | 37.78
2020-12-21 20:30 | 44186.8542 | 0 | 17.6702 | 37.78
2020-12-21 21:00 | 44186.875 | 0 | 17.3455 | 37.78
2020-12-21 21:30 | 44186.8958 | 0 | 16.5423 | 37.78
2020-12-21 22:00 | 44186.9167 | 0 | 15.7625 | 37.78
2020-12-21 22:30 | 44186.9375 | 0 | 14.9652 | 37.78
2020-12-21 23:00 | 44186.9583 | 0 | 14.0621 | 37.78
2020-12-21 23:30 | 44186.9792 | 0 | 13.5643 | 37.78
2020-12-22 | 44187 | 0 | 12.6098 | 37.78
2020-12-22 00:30 | 44187.0208 | 0 | 11.8948 | 37.78
2020-12-22 01:00 | 44187.0417 | 0 | 11.4725 | 37.78
2020-12-22 01:30 | 44187.0625 | 0 | 11.2599 | 37.78
2020-12-22 02:00 | 44187.0833 | 0 | 10.936 | 37.78
2020-12-22 02:30 | 44187.1042 | 0 | 10.6047 | 37.78
2020-12-22 03:00 | 44187.125 | 0 | 10.4846 | 37.78
2020-12-22 03:30 | 44187.1458 | 0 | 10.4074 | 37.78
2020-12-22 04:00 | 44187.1667 | 0 | 10.8928 | 37.78
2020-12-22 04:30 | 44187.1875 | 0 | 11.1709 | 37.78
2020-12-22 05:00 | 44187.2083 | 0 | 11.4538 | 37.78
2020-12-22 05:30 | 44187.2292 | 0 | 11.7443 | 37.78
2020-12-22 06:00 | 44187.25 | 0 | 12.3728 | 37.78
2020-12-22 06:30 | 44187.2708 | 0 | 13.153 | 37.78
2020-12-22 07:00 | 44187.2917 | 0 | 13.8054 | 37.78
2020-12-22 07:30 | 44187.3125 | 0 | 13.5285 | 37.78
2020-12-22 08:00 | 44187.3333 | 0 | 13.1721 | 37.78
2020-12-22 08:30 | 44187.3542 | 0 | 14.0391 | 37.78
2020-12-22 09:00 | 44187.375 | 0 | 15.3768 | 37.78
2020-12-22 09:30 | 44187.3958 | 0 | 15.152 | 37.78
2020-12-22 10:00 | 44187.4167 | 0 | 16.5628 | 37.78
2020-12-22 10:30 | 44187.4375 | 0 | 17.6381 | 37.78
2020-12-22 11:00 | 44187.4583 | 0 | 17.8304 | 37.78
2020-12-22 11:30 | 44187.4792 | 0 | 18.2191 | 37.78
2020-12-22 12:00 | 44187.5 | 0 | 17.402 | 37.78
2020-12-22 12:30 | 44187.5208 | 0 | 17.0908 | 37.78
2020-12-22 13:00 | 44187.5417 | 0 | 18.2974 | 37.78
2020-12-22 13:30 | 44187.5625 | 0 | 18.3986 | 37.78
2020-12-22 14:00 | 44187.5833 | 0 | 19.5576 | 37.78
2020-12-22 14:30 | 44187.6042 | 0 | 20.238 | 37.78
2020-12-22 15:00 | 44187.625 | 0 | 21.3356 | 37.78
2020-12-22 15:30 | 44187.6458 | 0 | 21.6511 | 37.78
2020-12-22 16:00 | 44187.6667 | 0 | 20.9095 | 37.78
2020-12-22 16:30 | 44187.6875 | 0 | 21.1509 | 37.78
2020-12-22 17:00 | 44187.7083 | 0 | 21.1829 | 37.78
2020-12-22 17:30 | 44187.7292 | 0 | 20.8287 | 37.78
2020-12-22 18:00 | 44187.75 | 0 | 20.2585 | 37.78
2020-12-22 18:30 | 44187.7708 | 0 | 20.205 | 37.78
2020-12-22 19:00 | 44187.7917 | 0 | 20.0425 | 37.78
2020-12-22 19:30 | 44187.8125 | 0 | 19.924 | 37.78
2020-12-22 20:00 | 44187.8333 | 0 | 19.4113 | 37.78
2020-12-22 20:30 | 44187.8542 | 0 | 18.2037 | 37.78
2020-12-22 21:00 | 44187.875 | 0 | 17.4704 | 37.78
2020-12-22 21:30 | 44187.8958 | 0 | 16.6983 | 37.78
2020-12-22 22:00 | 44187.9167 | 0 | 15.6931 | 37.78
2020-12-22 22:30 | 44187.9375 | 0 | 14.8021 | 37.78
2020-12-22 23:00 | 44187.9583 | 0 | 13.617 | 37.78
2020-12-22 23:30 | 44187.9792 | 0 | 13.1986 | 37.78
2020-12-23 | 44188 | 0 | 12.2371 | 37.78
2020-12-23 00:30 | 44188.0208 | 0 | 11.8597 | 37.78
2020-12-23 01:00 | 44188.0417 | 0 | 11.4338 | 37.78
2020-12-23 01:30 | 44188.0625 | 0 | 11.0214 | 37.78
2020-12-23 02:00 | 44188.0833 | 0 | 10.889 | 37.78
2020-12-23 02:30 | 44188.1042 | 0 | 10.7331 | 37.78
2020-12-23 03:00 | 44188.125 | 0 | 10.6123 | 37.78
2020-12-23 03:30 | 44188.1458 | 0 | 10.6261 | 37.78
2020-12-23 04:00 | 44188.1667 | 0 | 10.9509 | 37.78
2020-12-23 04:30 | 44188.1875 | 0 | 11.0458 | 37.78
2020-12-23 05:00 | 44188.2083 | 0 | 11.184 | 37.78
2020-12-23 05:30 | 44188.2292 | 0 | 11.2264 | 37.78
2020-12-23 06:00 | 44188.25 | 0 | 11.853 | 37.78
2020-12-23 06:30 | 44188.2708 | 0 | 11.9425 | 37.78
2020-12-23 07:00 | 44188.2917 | 0 | 12.4414 | 37.78
2020-12-23 07:30 | 44188.3125 | 0 | 12.7263 | 37.78
2020-12-23 08:00 | 44188.3333 | 0 | 12.528 | 37.78
2020-12-23 08:30 | 44188.3542 | 0 | 12.8452 | 37.78
2020-12-23 09:00 | 44188.375 | 0 | 13.0984 | 37.78
2020-12-23 09:30 | 44188.3958 | 0 | 13.2329 | 37.78
2020-12-23 10:00 | 44188.4167 | 0 | 13.4401 | 37.78
2020-12-23 10:30 | 44188.4375 | 0 | 14.0469 | 37.78
2020-12-23 11:00 | 44188.4583 | 0 | 14.1142 | 37.78
2020-12-23 11:30 | 44188.4792 | 0 | 14.5859 | 37.78
2020-12-23 12:00 | 44188.5 | 0 | 14.9523 | 37.78
2020-12-23 12:30 | 44188.5208 | 0 | 15.5047 | 37.78
2020-12-23 13:00 | 44188.5417 | 0 | 15.5831 | 37.78
2020-12-23 13:30 | 44188.5625 | 0 | 16.2955 | 37.78
2020-12-23 14:00 | 44188.5833 | 0 | 16.5149 | 37.78
2020-12-23 14:30 | 44188.6042 | 0 | 17.1345 | 37.78
2020-12-23 15:00 | 44188.625 | 0 | 17.6388 | 37.78
2020-12-23 15:30 | 44188.6458 | 0 | 17.7586 | 37.78
2020-12-23 16:00 | 44188.6667 | 0 | 17.8341 | 37.78
2020-12-23 16:30 | 44188.6875 | 0 | 17.6255 | 37.78
2020-12-23 17:00 | 44188.7083 | 0 | 16.7315 | 37.78
2020-12-23 17:30 | 44188.7292 | 0 | 16.289 | 37.78
2020-12-23 18:00 | 44188.75 | 0 | 15.8178 | 37.78
2020-12-23 18:30 | 44188.7708 | 0 | 15.9799 | 37.78
2020-12-23 19:00 | 44188.7917 | 0 | 15.7887 | 37.78
2020-12-23 19:30 | 44188.8125 | 0 | 15.3244 | 37.78
2020-12-23 20:00 | 44188.8333 | 0 | 14.8574 | 37.78
2020-12-23 20:30 | 44188.8542 | 0 | 14.3179 | 37.78
2020-12-23 21:00 | 44188.875 | 0 | 13.8183 | 37.78
2020-12-23 21:30 | 44188.8958 | 0 | 13.4978 | 37.78
2020-12-23 22:00 | 44188.9167 | 0 | 13.1365 | 37.78
2020-12-23 22:30 | 44188.9375 | 0 | 12.5618 | 37.78
2020-12-23 23:00 | 44188.9583 | 0 | 11.6989 | 37.78
2020-12-23 23:30 | 44188.9792 | 0 | 11.2452 | 37.78
2020-12-24 | 44189 | 0 | 10.475 | 37.78
2020-12-24 00:30 | 44189.0208 | 0 | 9.8379 | 37.78
2020-12-24 01:00 | 44189.0417 | 0 | 9.4995 | 37.78
2020-12-24 01:30 | 44189.0625 | 0 | 9.2633 | 37.78
2020-12-24 02:00 | 44189.0833 | 0 | 9.0266 | 37.78
2020-12-24 02:30 | 44189.1042 | 0 | 8.9689 | 37.78
2020-12-24 03:00 | 44189.125 | 0 | 8.772 | 37.78
2020-12-24 03:30 | 44189.1458 | 0 | 8.9499 | 37.78
2020-12-24 04:00 | 44189.1667 | 0 | 9.1895 | 37.78
2020-12-24 04:30 | 44189.1875 | 0 | 9.3964 | 37.78
2020-12-24 05:00 | 44189.2083 | 0 | 9.7342 | 37.78
2020-12-24 05:30 | 44189.2292 | 0 | 10.0784 | 37.78
2020-12-24 06:00 | 44189.25 | 0 | 10.2986 | 37.78
2020-12-24 06:30 | 44189.2708 | 0 | 10.5057 | 37.78
2020-12-24 07:00 | 44189.2917 | 0 | 10.8359 | 37.78
2020-12-24 07:30 | 44189.3125 | 0 | 11.4566 | 37.78
2020-12-24 08:00 | 44189.3333 | 0 | 11.3632 | 37.78
2020-12-24 08:30 | 44189.3542 | 0 | 11.9994 | 37.78
2020-12-24 09:00 | 44189.375 | 0 | 13.3014 | 37.78
2020-12-24 09:30 | 44189.3958 | 0 | 13.1629 | 37.78
2020-12-24 10:00 | 44189.4167 | 0 | 13.3873 | 37.78
2020-12-24 10:30 | 44189.4375 | 0 | 12.9409 | 37.78
2020-12-24 11:00 | 44189.4583 | 0 | 12.5509 | 37.78
2020-12-24 11:30 | 44189.4792 | 0 | 11.9168 | 37.78
2020-12-24 12:00 | 44189.5 | 0 | 13.1909 | 37.78
2020-12-24 12:30 | 44189.5208 | 0 | 12.4572 | 37.78
2020-12-24 13:00 | 44189.5417 | 0 | 13.5017 | 37.78
2020-12-24 13:30 | 44189.5625 | 0 | 14.2788 | 37.78
2020-12-24 14:00 | 44189.5833 | 0 | 13.1533 | 37.78
2020-12-24 14:30 | 44189.6042 | 0 | 13.6708 | 37.78
2020-12-24 15:00 | 44189.625 | 0 | 14.0993 | 37.78
2020-12-24 15:30 | 44189.6458 | 0 | 13.9829 | 37.78
2020-12-24 16:00 | 44189.6667 | 0 | 14.0662 | 37.78
2020-12-24 16:30 | 44189.6875 | 0 | 14.4482 | 37.78
2020-12-24 17:00 | 44189.7083 | 0 | 13.7239 | 37.78
2020-12-24 17:30 | 44189.7292 | 0 | 13.5546 | 37.78
2020-12-24 18:00 | 44189.75 | 0 | 13.4558 | 37.78
2020-12-24 18:30 | 44189.7708 | 0 | 13.6174 | 37.78
2020-12-24 19:00 | 44189.7917 | 0 | 13.6494 | 37.78
2020-12-24 19:30 | 44189.8125 | 0 | 13.4591 | 37.78
2020-12-24 20:00 | 44189.8333 | 0 | 13.1816 | 37.78
2020-12-24 20:30 | 44189.8542 | 0 | 12.7296 | 37.78
2020-12-24 21:00 | 44189.875 | 0 | 12.3867 | 37.78
2020-12-24 21:30 | 44189.8958 | 0 | 12.1977 | 37.78
2020-12-24 22:00 | 44189.9167 | 0 | 11.9815 | 37.78
2020-12-24 22:30 | 44189.9375 | 0 | 11.3933 | 37.78
2020-12-24 23:00 | 44189.9583 | 0 | 10.7769 | 37.78
2020-12-24 23:30 | 44189.9792 | 0 | 10.2209 | 37.78
2020-12-25 | 44190 | 0 | 9.5674 | 37.78
2020-12-25 00:30 | 44190.0208 | 0 | 9.1429 | 37.78
2020-12-25 01:00 | 44190.0417 | 0 | 8.9774 | 37.78
2020-12-25 01:30 | 44190.0625 | 0 | 8.8661 | 37.78
2020-12-25 02:00 | 44190.0833 | 0 | 8.7766 | 37.78
2020-12-25 02:30 | 44190.1042 | 0 | 8.673 | 37.78
2020-12-25 03:00 | 44190.125 | 0 | 8.4417 | 37.78
2020-12-25 03:30 | 44190.1458 | 0 | 8.3836 | 37.78
2020-12-25 04:00 | 44190.1667 | 0 | 8.4641 | 37.78
2020-12-25 04:30 | 44190.1875 | 0 | 8.4598 | 37.78
2020-12-25 05:00 | 44190.2083 | 0 | 8.458 | 37.78
2020-12-25 05:30 | 44190.2292 | 0 | 8.4823 | 37.78
2020-12-25 06:00 | 44190.25 | 0 | 8.8174 | 37.78
2020-12-25 06:30 | 44190.2708 | 0 | 8.7673 | 37.78
2020-12-25 07:00 | 44190.2917 | 0 | 9.464 | 37.78
2020-12-25 07:30 | 44190.3125 | 0 | 8.8912 | 37.78
2020-12-25 08:00 | 44190.3333 | 0 | 8.5474 | 37.78
2020-12-25 08:30 | 44190.3542 | 0 | 9.8229 | 37.78
2020-12-25 09:00 | 44190.375 | 0 | 8.9193 | 37.78
2020-12-25 09:30 | 44190.3958 | 0 | 10.5425 | 37.78
2020-12-25 10:00 | 44190.4167 | 0 | 11.2255 | 37.78
2020-12-25 10:30 | 44190.4375 | 0 | 10.5137 | 37.78
2020-12-25 11:00 | 44190.4583 | 0 | 12.2029 | 37.78
2020-12-25 11:30 | 44190.4792 | 0 | 11.8262 | 37.78
2020-12-25 12:00 | 44190.5 | 0 | 9.5758 | 37.78
2020-12-25 12:30 | 44190.5208 | 0 | 8.9518 | 37.78
2020-12-25 13:00 | 44190.5417 | 0 | 10.8815 | 37.78
2020-12-25 13:30 | 44190.5625 | 0 | 11.3731 | 37.78
2020-12-25 14:00 | 44190.5833 | 0 | 9.2739 | 37.78
2020-12-25 14:30 | 44190.6042 | 0 | 9.837 | 37.78
2020-12-25 15:00 | 44190.625 | 0 | 10.0727 | 37.78
2020-12-25 15:30 | 44190.6458 | 0 | 10.628 | 37.78
2020-12-25 16:00 | 44190.6667 | 0 | 11.1749 | 37.78
2020-12-25 16:30 | 44190.6875 | 0 | 11.559 | 37.78
2020-12-25 17:00 | 44190.7083 | 0 | 11.7906 | 37.78
2020-12-25 17:30 | 44190.7292 | 0 | 11.5172 | 37.78
2020-12-25 18:00 | 44190.75 | 0 | 11.492 | 37.78
2020-12-25 18:30 | 44190.7708 | 0 | 11.6074 | 37.78
2020-12-25 19:00 | 44190.7917 | 0 | 11.7647 | 37.78
2020-12-25 19:30 | 44190.8125 | 0 | 11.8108 | 37.78
2020-12-25 20:00 | 44190.8333 | 0 | 11.6758 | 37.78
2020-12-25 20:30 | 44190.8542 | 0 | 11.3193 | 37.78
2020-12-25 21:00 | 44190.875 | 0 | 11.0277 | 37.78
2020-12-25 21:30 | 44190.8958 | 0 | 10.7217 | 37.78
2020-12-25 22:00 | 44190.9167 | 0 | 10.4287 | 37.78
2020-12-25 22:30 | 44190.9375 | 0 | 9.8664 | 37.78
2020-12-25 23:00 | 44190.9583 | 0 | 9.3523 | 37.78
2020-12-25 23:30 | 44190.9792 | 0 | 8.9596 | 37.78
2020-12-26 | 44191 | 0 | 8.6381 | 37.78
2020-12-26 00:30 | 44191.0208 | 0 | 8.4459 | 37.78
2020-12-26 01:00 | 44191.0417 | 0 | 8.2423 | 37.78
2020-12-26 01:30 | 44191.0625 | 0 | 8.1438 | 37.78
2020-12-26 02:00 | 44191.0833 | 0 | 8.1501 | 37.78
2020-12-26 02:30 | 44191.1042 | 0 | 7.9639 | 37.78
2020-12-26 03:00 | 44191.125 | 0 | 7.8565 | 37.78
2020-12-26 03:30 | 44191.1458 | 0 | 7.8028 | 37.78
2020-12-26 04:00 | 44191.1667 | 0 | 7.6243 | 37.78
2020-12-26 04:30 | 44191.1875 | 0 | 7.62 | 37.78
2020-12-26 05:00 | 44191.2083 | 0 | 7.5573 | 37.78
2020-12-26 05:30 | 44191.2292 | 0 | 7.4992 | 37.78
2020-12-26 06:00 | 44191.25 | 0 | 7.7528 | 37.78
2020-12-26 06:30 | 44191.2708 | 0 | 8.297 | 37.78
2020-12-26 07:00 | 44191.2917 | 0 | 7.4038 | 37.78
2020-12-26 07:30 | 44191.3125 | 0 | 6.9757 | 37.78
2020-12-26 08:00 | 44191.3333 | 0 | 8.8007 | 37.78
2020-12-26 08:30 | 44191.3542 | 0 | 8.5 | 37.78
2020-12-26 09:00 | 44191.375 | 0 | 7.4429 | 37.78
2020-12-26 09:30 | 44191.3958 | 0 | 9.1744 | 37.78
2020-12-26 10:00 | 44191.4167 | 0 | 9.0096 | 37.78
2020-12-26 10:30 | 44191.4375 | 0 | 7.3637 | 37.78
2020-12-26 11:00 | 44191.4583 | 0 | 7.8768 | 37.78
2020-12-26 11:30 | 44191.4792 | 0 | 9.1852 | 37.78
2020-12-26 12:00 | 44191.5 | 0 | 8.6317 | 37.78
2020-12-26 12:30 | 44191.5208 | 0 | 8.3775 | 37.78
2020-12-26 13:00 | 44191.5417 | 0 | 7.7564 | 37.78
2020-12-26 13:30 | 44191.5625 | 0 | 8.3276 | 37.78
2020-12-26 14:00 | 44191.5833 | 0 | 8.4455 | 37.78
2020-12-26 14:30 | 44191.6042 | 0 | 9.4338 | 37.78
2020-12-26 15:00 | 44191.625 | 0 | 9.8877 | 37.78
2020-12-26 15:30 | 44191.6458 | 0 | 10.1657 | 37.78
2020-12-26 16:00 | 44191.6667 | 0 | 10.4343 | 37.78
2020-12-26 16:30 | 44191.6875 | 0 | 10.902 | 37.78
2020-12-26 17:00 | 44191.7083 | 0 | 11.2942 | 37.78
2020-12-26 17:30 | 44191.7292 | 0 | 11.5273 | 37.78
2020-12-26 18:00 | 44191.75 | 0 | 11.9047 | 37.78
2020-12-26 18:30 | 44191.7708 | 0 | 11.9994 | 37.78
2020-12-26 19:00 | 44191.7917 | 0 | 12.1401 | 37.78
2020-12-26 19:30 | 44191.8125 | 0 | 12.1759 | 37.78
2020-12-26 20:00 | 44191.8333 | 0 | 11.852 | 37.78
2020-12-26 20:30 | 44191.8542 | 0 | 11.3714 | 37.78
2020-12-26 21:00 | 44191.875 | 0 | 11.0008 | 37.78
2020-12-26 21:30 | 44191.8958 | 0 | 10.7285 | 37.78
2020-12-26 22:00 | 44191.9167 | 0 | 10.3155 | 37.78
2020-12-26 22:30 | 44191.9375 | 0 | 9.7351 | 37.78
2020-12-26 23:00 | 44191.9583 | 0 | 9.3233 | 37.78
2020-12-26 23:30 | 44191.9792 | 0 | 8.8746 | 37.78
2020-12-27 | 44192 | 0 | 8.4636 | 37.78
2020-12-27 00:30 | 44192.0208 | 0 | 8.1458 | 37.78
2020-12-27 01:00 | 44192.0417 | 0 | 7.9681 | 37.78
2020-12-27 01:30 | 44192.0625 | 0 | 7.7969 | 37.78
2020-12-27 02:00 | 44192.0833 | 0 | 7.7493 | 37.78
2020-12-27 02:30 | 44192.1042 | 0 | 7.6509 | 37.78
2020-12-27 03:00 | 44192.125 | 0 | 7.4814 | 37.78
2020-12-27 03:30 | 44192.1458 | 0 | 7.4814 | 37.78
2020-12-27 04:00 | 44192.1667 | 0 | 7.4368 | 37.78
2020-12-27 04:30 | 44192.1875 | 0 | 7.3077 | 37.78
2020-12-27 05:00 | 44192.2083 | 0 | 7.2609 | 37.78
2020-12-27 05:30 | 44192.2292 | 0 | 7.1761 | 37.78
2020-12-27 06:00 | 44192.25 | 0 | 7.0614 | 37.78
2020-12-27 06:30 | 44192.2708 | 0 | 6.9186 | 37.78
2020-12-27 07:00 | 44192.2917 | 0 | 6.9277 | 37.78
2020-12-27 07:30 | 44192.3125 | 0 | 6.9947 | 37.78
2020-12-27 08:00 | 44192.3333 | 0 | 7.8064 | 37.78
2020-12-27 08:30 | 44192.3542 | 0 | 7.3248 | 37.78
2020-12-27 09:00 | 44192.375 | 0 | 8.1865 | 37.78
2020-12-27 09:30 | 44192.3958 | 0 | 8.143 | 37.78
2020-12-27 10:00 | 44192.4167 | 0 | 7.9143 | 37.78
2020-12-27 10:30 | 44192.4375 | 0 | 8.533 | 37.78
2020-12-27 11:00 | 44192.4583 | 0 | 9.1493 | 37.78
2020-12-27 11:30 | 44192.4792 | 0 | 8.7452 | 37.78
2020-12-27 12:00 | 44192.5 | 0 | 8.774 | 37.78
2020-12-27 12:30 | 44192.5208 | 0 | 8.2807 | 37.78
2020-12-27 13:00 | 44192.5417 | 0 | 8.2871 | 37.78
2020-12-27 13:30 | 44192.5625 | 0 | 9.0545 | 37.78
2020-12-27 14:00 | 44192.5833 | 0 | 9.3964 | 37.78
2020-12-27 14:30 | 44192.6042 | 0 | 9.8919 | 37.78
2020-12-27 15:00 | 44192.625 | 0 | 10.6361 | 37.78
2020-12-27 15:30 | 44192.6458 | 0 | 11.0739 | 37.78
2020-12-27 16:00 | 44192.6667 | 0 | 11.4274 | 37.78
2020-12-27 16:30 | 44192.6875 | 0 | 11.9721 | 37.78
2020-12-27 17:00 | 44192.7083 | 0 | 12.3918 | 37.78
2020-12-27 17:30 | 44192.7292 | 0 | 12.3962 | 37.78
2020-12-27 18:00 | 44192.75 | 0 | 12.4825 | 37.78
2020-12-27 18:30 | 44192.7708 | 0 | 12.761 | 37.78
2020-12-27 19:00 | 44192.7917 | 0 | 12.7966 | 37.78
2020-12-27 19:30 | 44192.8125 | 0 | 12.725 | 37.78
2020-12-27 20:00 | 44192.8333 | 0 | 12.6056 | 37.78
2020-12-27 20:30 | 44192.8542 | 0 | 11.915 | 37.78
2020-12-27 21:00 | 44192.875 | 0 | 11.6988 | 37.78
2020-12-27 21:30 | 44192.8958 | 0 | 11.3388 | 37.78
2020-12-27 22:00 | 44192.9167 | 0 | 10.9078 | 37.78
2020-12-27 22:30 | 44192.9375 | 0 | 10.4648 | 37.78
2020-12-27 23:00 | 44192.9583 | 0 | 9.9309 | 37.78
2020-12-27 23:30 | 44192.9792 | 0 | 9.3281 | 37.78
2020-12-28 | 44193 | 0 | 8.9705 | 37.78
2020-12-28 00:30 | 44193.0208 | 0 | 8.6441 | 37.78
2020-12-28 01:00 | 44193.0417 | 0 | 8.379 | 37.78
2020-12-28 01:30 | 44193.0625 | 0 | 8.33 | 37.78
2020-12-28 02:00 | 44193.0833 | 0 | 8.3376 | 37.78
2020-12-28 02:30 | 44193.1042 | 0 | 8.2197 | 37.78
2020-12-28 03:00 | 44193.125 | 0 | 8.0455 | 37.78
2020-12-28 03:30 | 44193.1458 | 0 | 8.022 | 37.78
2020-12-28 04:00 | 44193.1667 | 0 | 8.0132 | 37.78
2020-12-28 04:30 | 44193.1875 | 0 | 8.0933 | 37.78
2020-12-28 05:00 | 44193.2083 | 0 | 8.0798 | 37.78
2020-12-28 05:30 | 44193.2292 | 0 | 7.9908 | 37.78
2020-12-28 06:00 | 44193.25 | 0 | 8.2198 | 37.78
2020-12-28 06:30 | 44193.2708 | 0 | 8.1975 | 37.78
2020-12-28 07:00 | 44193.2917 | 0 | 8.3617 | 37.78
2020-12-28 07:30 | 44193.3125 | 0 | 8.6209 | 37.78
2020-12-28 08:00 | 44193.3333 | 0 | 8.8432 | 37.78
2020-12-28 08:30 | 44193.3542 | 0 | 9.0363 | 37.78
2020-12-28 09:00 | 44193.375 | 0 | 8.8359 | 37.78
2020-12-28 09:30 | 44193.3958 | 0 | 8.9496 | 37.78
2020-12-28 10:00 | 44193.4167 | 0 | 8.7524 | 37.78
2020-12-28 10:30 | 44193.4375 | 0 | 8.987 | 37.78
2020-12-28 11:00 | 44193.4583 | 0 | 8.9554 | 37.78
2020-12-28 11:30 | 44193.4792 | 0 | 9.2015 | 37.78
2020-12-28 12:00 | 44193.5 | 0 | 9.2205 | 37.78
2020-12-28 12:30 | 44193.5208 | 0 | 9.7549 | 37.78
2020-12-28 13:00 | 44193.5417 | 0 | 9.9109 | 37.78
2020-12-28 13:30 | 44193.5625 | 0 | 10.0277 | 37.78
2020-12-28 14:00 | 44193.5833 | 0 | 10.7379 | 37.78
2020-12-28 14:30 | 44193.6042 | 0 | 10.8974 | 37.78
2020-12-28 15:00 | 44193.625 | 0 | 11.3881 | 37.78
2020-12-28 15:30 | 44193.6458 | 0 | 11.9149 | 37.78
2020-12-28 16:00 | 44193.6667 | 0 | 12.939 | 37.78
2020-12-28 16:30 | 44193.6875 | 0 | 12.8694 | 37.78
2020-12-28 17:00 | 44193.7083 | 0 | 13.2782 | 37.78
2020-12-28 17:30 | 44193.7292 | 0 | 13.3921 | 37.78
2020-12-28 18:00 | 44193.75 | 0 | 13.4503 | 37.78
2020-12-28 18:30 | 44193.7708 | 0 | 13.8914 | 37.78
2020-12-28 19:00 | 44193.7917 | 0 | 14.1191 | 37.78
2020-12-28 19:30 | 44193.8125 | 0 | 13.8132 | 37.78
2020-12-28 20:00 | 44193.8333 | 0 | 13.5824 | 37.78
2020-12-28 20:30 | 44193.8542 | 0 | 13.0748 | 37.78
2020-12-28 21:00 | 44193.875 | 0 | 12.5999 | 37.78
2020-12-28 21:30 | 44193.8958 | 0 | 12.3317 | 37.78
2020-12-28 22:00 | 44193.9167 | 0 | 11.9644 | 37.78
2020-12-28 22:30 | 44193.9375 | 0 | 11.2664 | 37.78
2020-12-28 23:00 | 44193.9583 | 0 | 10.6746 | 37.78
2020-12-28 23:30 | 44193.9792 | 0 | 10.1706 | 37.78
2020-12-29 | 44194 | 0 | 9.6565 | 37.78
2020-12-29 00:30 | 44194.0208 | 0 | 9.32 | 37.78
2020-12-29 01:00 | 44194.0417 | 0 | 9.0266 | 37.78
2020-12-29 01:30 | 44194.0625 | 0 | 8.915 | 37.78
2020-12-29 02:00 | 44194.0833 | 0 | 8.8288 | 37.78
2020-12-29 02:30 | 44194.1042 | 0 | 8.8255 | 37.78
2020-12-29 03:00 | 44194.125 | 0 | 8.7978 | 37.78
2020-12-29 03:30 | 44194.1458 | 0 | 8.8241 | 37.78
2020-12-29 04:00 | 44194.1667 | 0 | 8.8112 | 37.78
2020-12-29 04:30 | 44194.1875 | 0 | 9.1531 | 37.78
2020-12-29 05:00 | 44194.2083 | 0 | 9.1564 | 37.78
2020-12-29 05:30 | 44194.2292 | 0 | 9.3965 | 37.78
2020-12-29 06:00 | 44194.25 | 0 | 9.8937 | 37.78
2020-12-29 06:30 | 44194.2708 | 0 | 10.1447 | 37.78
2020-12-29 07:00 | 44194.2917 | 0 | 10.8188 | 37.78
2020-12-29 07:30 | 44194.3125 | 0 | 11.3561 | 37.78
2020-12-29 08:00 | 44194.3333 | 0 | 12.2381 | 37.78
2020-12-29 08:30 | 44194.3542 | 0 | 12.6723 | 37.78
2020-12-29 09:00 | 44194.375 | 0 | 12.032 | 37.78
2020-12-29 09:30 | 44194.3958 | 0 | 13.0951 | 37.78
2020-12-29 10:00 | 44194.4167 | 0 | 13.6321 | 37.78
2020-12-29 10:30 | 44194.4375 | 0 | 13.187 | 37.78
2020-12-29 11:00 | 44194.4583 | 0 | 12.8925 | 37.78
2020-12-29 11:30 | 44194.4792 | 0 | 12.6095 | 37.78
2020-12-29 12:00 | 44194.5 | 0 | 12.8101 | 37.78
2020-12-29 12:30 | 44194.5208 | 0 | 13.2759 | 37.78
2020-12-29 13:00 | 44194.5417 | 0 | 13.355 | 37.78
2020-12-29 13:30 | 44194.5625 | 0 | 13.708 | 37.78
2020-12-29 14:00 | 44194.5833 | 0 | 14.5457 | 37.78
2020-12-29 14:30 | 44194.6042 | 0 | 15.3336 | 37.78
2020-12-29 15:00 | 44194.625 | 0 | 15.5915 | 37.78
2020-12-29 15:30 | 44194.6458 | 0 | 15.7851 | 37.78
2020-12-29 16:00 | 44194.6667 | 0 | 16.1309 | 37.78
2020-12-29 16:30 | 44194.6875 | 0 | 16.1316 | 37.78
2020-12-29 17:00 | 44194.7083 | 0 | 15.9097 | 37.78
2020-12-29 17:30 | 44194.7292 | 0 | 15.9281 | 37.78
2020-12-29 18:00 | 44194.75 | 0 | 15.9203 | 37.78
2020-12-29 18:30 | 44194.7708 | 0 | 16.4607 | 37.78
2020-12-29 19:00 | 44194.7917 | 0 | 16.3982 | 37.78
2020-12-29 19:30 | 44194.8125 | 0 | 16.3833 | 37.78
2020-12-29 20:00 | 44194.8333 | 0 | 16.0678 | 37.78
2020-12-29 20:30 | 44194.8542 | 0 | 15.5193 | 37.78
2020-12-29 21:00 | 44194.875 | 0 | 15.174 | 37.78
2020-12-29 21:30 | 44194.8958 | 0 | 14.5827 | 37.78
2020-12-29 22:00 | 44194.9167 | 0 | 14.1126 | 37.78
2020-12-29 22:30 | 44194.9375 | 0 | 13.2457 | 37.78
2020-12-29 23:00 | 44194.9583 | 0 | 12.6073 | 37.78
2020-12-29 23:30 | 44194.9792 | 0 | 12.1485 | 37.78
2020-12-30 | 44195 | 0 | 11.2708 | 37.78
2020-12-30 00:30 | 44195.0208 | 0 | 10.8874 | 37.78
2020-12-30 01:00 | 44195.0417 | 0 | 10.6047 | 37.78
2020-12-30 01:30 | 44195.0625 | 0 | 10.4247 | 37.78
2020-12-30 02:00 | 44195.0833 | 0 | 10.3622 | 37.78
2020-12-30 02:30 | 44195.1042 | 0 | 10.2982 | 37.78
2020-12-30 03:00 | 44195.125 | 0 | 10.151 | 37.78
2020-12-30 03:30 | 44195.1458 | 0 | 10.1078 | 37.78
2020-12-30 04:00 | 44195.1667 | 0 | 10.3104 | 37.78
2020-12-30 04:30 | 44195.1875 | 0 | 10.508 | 37.78
2020-12-30 05:00 | 44195.2083 | 0 | 10.7062 | 37.78
2020-12-30 05:30 | 44195.2292 | 0 | 10.9049 | 37.78
2020-12-30 06:00 | 44195.25 | 0 | 11.3277 | 37.78
2020-12-30 06:30 | 44195.2708 | 0 | 11.5673 | 37.78
2020-12-30 07:00 | 44195.2917 | 0 | 12.0188 | 37.78
2020-12-30 07:30 | 44195.3125 | 0 | 12.4983 | 37.78
2020-12-30 08:00 | 44195.3333 | 0 | 13.2704 | 37.78
2020-12-30 08:30 | 44195.3542 | 0 | 13.5234 | 37.78
2020-12-30 09:00 | 44195.375 | 0 | 13.4638 | 37.78
2020-12-30 09:30 | 44195.3958 | 0 | 13.5648 | 37.78
2020-12-30 10:00 | 44195.4167 | 0 | 13.7708 | 37.78
2020-12-30 10:30 | 44195.4375 | 0 | 13.8687 | 37.78
2020-12-30 11:00 | 44195.4583 | 0 | 13.766 | 37.78
2020-12-30 11:30 | 44195.4792 | 0 | 13.1362 | 37.78
2020-12-30 12:00 | 44195.5 | 0 | 13.0588 | 37.78
2020-12-30 12:30 | 44195.5208 | 0 | 12.8324 | 37.78
2020-12-30 13:00 | 44195.5417 | 0 | 12.8698 | 37.78
2020-12-30 13:30 | 44195.5625 | 0 | 13.4141 | 37.78
2020-12-30 14:00 | 44195.5833 | 0 | 13.3921 | 37.78
2020-12-30 14:30 | 44195.6042 | 0 | 13.2357 | 37.78
2020-12-30 15:00 | 44195.625 | 0 | 13.3907 | 37.78
2020-12-30 15:30 | 44195.6458 | 0 | 13.3685 | 37.78
2020-12-30 16:00 | 44195.6667 | 0 | 13.6722 | 37.78
2020-12-30 16:30 | 44195.6875 | 0 | 13.8794 | 37.78
2020-12-30 17:00 | 44195.7083 | 0 | 14.1185 | 37.78
2020-12-30 17:30 | 44195.7292 | 0 | 13.9876 | 37.78
2020-12-30 18:00 | 44195.75 | 0 | 13.7458 | 37.78
2020-12-30 18:30 | 44195.7708 | 0 | 14.0316 | 37.78
2020-12-30 19:00 | 44195.7917 | 0 | 14.0113 | 37.78
2020-12-30 19:30 | 44195.8125 | 0 | 13.9565 | 37.78
2020-12-30 20:00 | 44195.8333 | 0 | 13.8037 | 37.78
2020-12-30 20:30 | 44195.8542 | 0 | 13.4233 | 37.78
2020-12-30 21:00 | 44195.875 | 0 | 13.0819 | 37.78
2020-12-30 21:30 | 44195.8958 | 0 | 12.658 | 37.78
2020-12-30 22:00 | 44195.9167 | 0 | 12.1328 | 37.78
2020-12-30 22:30 | 44195.9375 | 0 | 11.7213 | 37.78
2020-12-30 23:00 | 44195.9583 | 0 | 11.3882 | 37.78
2020-12-30 23:30 | 44195.9792 | 0 | 10.706 | 37.78
2020-12-31 | 44196 | 0 | 10.0636 | 37.78
2020-12-31 00:30 | 44196.0208 | 0 | 9.7653 | 37.78
2020-12-31 01:00 | 44196.0417 | 0 | 9.3982 | 37.78
2020-12-31 01:30 | 44196.0625 | 0 | 9.2396 | 37.78
2020-12-31 02:00 | 44196.0833 | 0 | 9.2072 | 37.78
2020-12-31 02:30 | 44196.1042 | 0 | 8.9921 | 37.78
2020-12-31 03:00 | 44196.125 | 0 | 8.9465 | 37.78
2020-12-31 03:30 | 44196.1458 | 0 | 8.92 | 37.78
2020-12-31 04:00 | 44196.1667 | 0 | 9.1565 | 37.78
2020-12-31 04:30 | 44196.1875 | 0 | 9.4871 | 37.78
2020-12-31 05:00 | 44196.2083 | 0 | 9.6658 | 37.78
2020-12-31 05:30 | 44196.2292 | 0 | 9.8094 | 37.78
2020-12-31 06:00 | 44196.25 | 0 | 10.2195 | 37.78
2020-12-31 06:30 | 44196.2708 | 0 | 10.6879 | 37.78
2020-12-31 07:00 | 44196.2917 | 0 | 10.3978 | 37.78
2020-12-31 07:30 | 44196.3125 | 0 | 10.5069 | 37.78
2020-12-31 08:00 | 44196.3333 | 0 | 11.6871 | 37.78
2020-12-31 08:30 | 44196.3542 | 0 | 12.0681 | 37.78
2020-12-31 09:00 | 44196.375 | 0 | 12.3772 | 37.78
2020-12-31 09:30 | 44196.3958 | 0 | 11.0795 | 37.78
2020-12-31 10:00 | 44196.4167 | 0 | 12.1744 | 37.78
2020-12-31 10:30 | 44196.4375 | 0 | 12.117 | 37.78
2020-12-31 11:00 | 44196.4583 | 0 | 12.7695 | 37.78
2020-12-31 11:30 | 44196.4792 | 0 | 12.4585 | 37.78
2020-12-31 12:00 | 44196.5 | 0 | 12.5186 | 37.78
2020-12-31 12:30 | 44196.5208 | 0 | 13.7753 | 37.78
2020-12-31 13:00 | 44196.5417 | 0 | 12.1051 | 37.78
2020-12-31 13:30 | 44196.5625 | 0 | 12.787 | 37.78
2020-12-31 14:00 | 44196.5833 | 0 | 13.6455 | 37.78
2020-12-31 14:30 | 44196.6042 | 0 | 13.8282 | 37.78
2020-12-31 15:00 | 44196.625 | 0 | 14.1054 | 37.78
2020-12-31 15:30 | 44196.6458 | 0 | 14.3018 | 37.78
2020-12-31 16:00 | 44196.6667 | 0 | 14.4781 | 37.78
2020-12-31 16:30 | 44196.6875 | 0 | 15.1006 | 37.78
2020-12-31 17:00 | 44196.7083 | 0 | 15.2624 | 37.78
2020-12-31 17:30 | 44196.7292 | 0 | 15.2752 | 37.78
2020-12-31 18:00 | 44196.75 | 0 | 14.7989 | 37.78
2020-12-31 18:30 | 44196.7708 | 0 | 14.7665 | 37.78
2020-12-31 19:00 | 44196.7917 | 0 | 14.659 | 37.78
2020-12-31 19:30 | 44196.8125 | 0 | 14.3553 | 37.78
2020-12-31 20:00 | 44196.8333 | 0 | 14.0744 | 37.78
2020-12-31 20:30 | 44196.8542 | 0 | 13.7132 | 37.78
2020-12-31 21:00 | 44196.875 | 0 | 13.1505 | 37.78
2020-12-31 21:30 | 44196.8958 | 0 | 12.7086 | 37.78
2020-12-31 22:00 | 44196.9167 | 0 | 12.5297 | 37.78
2020-12-31 22:30 | 44196.9375 | 0 | 12.0131 | 37.78
2020-12-31 23:00 | 44196.9583 | 0 | 11.4607 | 37.78
2020-12-31 23:30 | 44196.9792 | 0 | 11.1351 | 37.78
2021-01-01 | 44197 | 0 | 10.3716 | 37.78
2021-01-01 00:30 | 44197.0208 | 0 | 10.0986 | 37.78
2021-01-01 01:00 | 44197.0417 | 0 | 10.0588 | 37.78
2021-01-01 01:30 | 44197.0625 | 0 | 9.8577 | 37.78
2021-01-01 02:00 | 44197.0833 | 0 | 9.6907 | 37.78
2021-01-01 02:30 | 44197.1042 | 0 | 9.4467 | 37.78
2021-01-01 03:00 | 44197.125 | 0 | 9.3243 | 37.78
2021-01-01 03:30 | 44197.1458 | 0 | 9.0499 | 37.78
2021-01-01 04:00 | 44197.1667 | 0 | 9.1713 | 37.78
2021-01-01 04:30 | 44197.1875 | 0 | 8.9419 | 37.78
2021-01-01 05:00 | 44197.2083 | 0 | 8.9107 | 37.78
2021-01-01 05:30 | 44197.2292 | 0 | 8.4873 | 37.78
2021-01-01 06:00 | 44197.25 | 0 | 8.545 | 37.78
2021-01-01 06:30 | 44197.2708 | 0 | 8.3395 | 37.78
2021-01-01 07:00 | 44197.2917 | 0 | 9.3842 | 37.78
2021-01-01 07:30 | 44197.3125 | 0 | 8.8638 | 37.78
2021-01-01 08:00 | 44197.3333 | 0 | 9.7524 | 37.78
2021-01-01 08:30 | 44197.3542 | 0 | 10.0631 | 37.78
2021-01-01 09:00 | 44197.375 | 0 | 9.1926 | 37.78
2021-01-01 09:30 | 44197.3958 | 0 | 8.6141 | 37.78
2021-01-01 10:00 | 44197.4167 | 0 | 8.5224 | 37.78
2021-01-01 10:30 | 44197.4375 | 0 | 8.783 | 37.78
2021-01-01 11:00 | 44197.4583 | 0 | 10.4908 | 37.78
2021-01-01 11:30 | 44197.4792 | 0 | 9.602 | 37.78
2021-01-01 12:00 | 44197.5 | 0 | 11.1246 | 37.78
2021-01-01 12:30 | 44197.5208 | 0 | 11.1955 | 37.78
2021-01-01 13:00 | 44197.5417 | 0 | 10.9983 | 37.78
2021-01-01 13:30 | 44197.5625 | 0 | 11.429 | 37.78
2021-01-01 14:00 | 44197.5833 | 0 | 12.3476 | 37.78
2021-01-01 14:30 | 44197.6042 | 0 | 12.2173 | 37.78
2021-01-01 15:00 | 44197.625 | 0 | 11.5139 | 37.78
2021-01-01 15:30 | 44197.6458 | 0 | 11.8702 | 37.78
2021-01-01 16:00 | 44197.6667 | 0 | 11.3788 | 37.78
2021-01-01 16:30 | 44197.6875 | 0 | 12.2741 | 37.78
2021-01-01 17:00 | 44197.7083 | 0 | 12.3452 | 37.78
2021-01-01 17:30 | 44197.7292 | 0 | 12.4779 | 37.78
2021-01-01 18:00 | 44197.75 | 0 | 12.6626 | 37.78
2021-01-01 18:30 | 44197.7708 | 0 | 13.1897 | 37.78
2021-01-01 19:00 | 44197.7917 | 0 | 13.261 | 37.78
2021-01-01 19:30 | 44197.8125 | 0 | 13.2982 | 37.78
2021-01-01 20:00 | 44197.8333 | 0 | 12.8898 | 37.78
2021-01-01 20:30 | 44197.8542 | 0 | 12.3236 | 37.78
2021-01-01 21:00 | 44197.875 | 0 | 11.8019 | 37.78
2021-01-01 21:30 | 44197.8958 | 0 | 11.5591 | 37.78
2021-01-01 22:00 | 44197.9167 | 0 | 11.1008 | 37.78
2021-01-01 22:30 | 44197.9375 | 0 | 10.4172 | 37.78
2021-01-01 23:00 | 44197.9583 | 0 | 9.8643 | 37.78
2021-01-01 23:30 | 44197.9792 | 0 | 9.4997 | 37.78
2021-01-02 | 44198 | 0 | 9.0112 | 37.78
2021-01-02 00:30 | 44198.0208 | 0 | 8.6855 | 37.78
2021-01-02 01:00 | 44198.0417 | 0 | 8.5086 | 37.78
2021-01-02 01:30 | 44198.0625 | 0 | 8.3273 | 37.78
2021-01-02 02:00 | 44198.0833 | 0 | 8.4139 | 37.78
2021-01-02 02:30 | 44198.1042 | 0 | 8.3747 | 37.78
2021-01-02 03:00 | 44198.125 | 0 | 8.3342 | 37.78
2021-01-02 03:30 | 44198.1458 | 0 | 8.1929 | 37.78
2021-01-02 04:00 | 44198.1667 | 0 | 8.2292 | 37.78
2021-01-02 04:30 | 44198.1875 | 0 | 8.4687 | 37.78
2021-01-02 05:00 | 44198.2083 | 0 | 8.5757 | 37.78
2021-01-02 05:30 | 44198.2292 | 0 | 8.4504 | 37.78
2021-01-02 06:00 | 44198.25 | 0 | 8.7884 | 37.78
2021-01-02 06:30 | 44198.2708 | 0 | 8.4987 | 37.78
2021-01-02 07:00 | 44198.2917 | 0 | 8.007 | 37.78
2021-01-02 07:30 | 44198.3125 | 0 | 8.7169 | 37.78
2021-01-02 08:00 | 44198.3333 | 0 | 9.676 | 37.78
2021-01-02 08:30 | 44198.3542 | 0 | 10.9239 | 37.78
2021-01-02 09:00 | 44198.375 | 0 | 10.7434 | 37.78
2021-01-02 09:30 | 44198.3958 | 0 | 9.5526 | 37.78
2021-01-02 10:00 | 44198.4167 | 0 | 10.0208 | 37.78
2021-01-02 10:30 | 44198.4375 | 0 | 10.0645 | 37.78
2021-01-02 11:00 | 44198.4583 | 0 | 10.8384 | 37.78
2021-01-02 11:30 | 44198.4792 | 0 | 11.2755 | 37.78
2021-01-02 12:00 | 44198.5 | 0 | 10.6221 | 37.78
2021-01-02 12:30 | 44198.5208 | 0 | 8.7568 | 37.78
2021-01-02 13:00 | 44198.5417 | 0 | 9.5085 | 37.78
2021-01-02 13:30 | 44198.5625 | 0 | 9.966 | 37.78
2021-01-02 14:00 | 44198.5833 | 0 | 10.5732 | 37.78
2021-01-02 14:30 | 44198.6042 | 0 | 10.8727 | 37.78
2021-01-02 15:00 | 44198.625 | 0 | 11.4744 | 37.78
2021-01-02 15:30 | 44198.6458 | 0 | 12.1457 | 37.78
2021-01-02 16:00 | 44198.6667 | 0 | 12.8894 | 37.78
2021-01-02 16:30 | 44198.6875 | 0 | 13.2309 | 37.78
2021-01-02 17:00 | 44198.7083 | 0 | 12.5422 | 37.78
2021-01-02 17:30 | 44198.7292 | 0 | 12.2741 | 37.78
2021-01-02 18:00 | 44198.75 | 0 | 12.6577 | 37.78
2021-01-02 18:30 | 44198.7708 | 0 | 14.0697 | 37.78
2021-01-02 19:00 | 44198.7917 | 0 | 14.1543 | 37.78
2021-01-02 19:30 | 44198.8125 | 0 | 13.7163 | 37.78
2021-01-02 20:00 | 44198.8333 | 0 | 13.4782 | 37.78
2021-01-02 20:30 | 44198.8542 | 0 | 13.0456 | 37.78
2021-01-02 21:00 | 44198.875 | 0 | 12.4746 | 37.78
2021-01-02 21:30 | 44198.8958 | 0 | 12.283 | 37.78
2021-01-02 22:00 | 44198.9167 | 0 | 11.8409 | 37.78
2021-01-02 22:30 | 44198.9375 | 0 | 11.0558 | 37.78
2021-01-02 23:00 | 44198.9583 | 0 | 10.5006 | 37.78
2021-01-02 23:30 | 44198.9792 | 0 | 10.0706 | 37.78
2021-01-03 | 44199 | 0 | 9.5726 | 37.78
2021-01-03 00:30 | 44199.0208 | 0 | 8.9639 | 37.78
2021-01-03 01:00 | 44199.0417 | 0 | 8.7305 | 37.78
2021-01-03 01:30 | 44199.0625 | 0 | 8.5725 | 37.78
2021-01-03 02:00 | 44199.0833 | 0 | 8.6339 | 37.78
2021-01-03 02:30 | 44199.1042 | 0 | 8.5222 | 37.78
2021-01-03 03:00 | 44199.125 | 0 | 8.3194 | 37.78
2021-01-03 03:30 | 44199.1458 | 0 | 8.3063 | 37.78
2021-01-03 04:00 | 44199.1667 | 0 | 8.3301 | 37.78
2021-01-03 04:30 | 44199.1875 | 0 | 8.3747 | 37.78
2021-01-03 05:00 | 44199.2083 | 0 | 8.1853 | 37.78
2021-01-03 05:30 | 44199.2292 | 0 | 7.8735 | 37.78
2021-01-03 06:00 | 44199.25 | 0 | 8.0626 | 37.78
2021-01-03 06:30 | 44199.2708 | 0 | 8.2912 | 37.78
2021-01-03 07:00 | 44199.2917 | 0 | 8.1827 | 37.78
2021-01-03 07:30 | 44199.3125 | 0 | 8.2516 | 37.78
2021-01-03 08:00 | 44199.3333 | 0 | 9.1665 | 37.78
2021-01-03 08:30 | 44199.3542 | 0 | 9.8345 | 37.78
2021-01-03 09:00 | 44199.375 | 0 | 10.0089 | 37.78
2021-01-03 09:30 | 44199.3958 | 0 | 10.7445 | 37.78
2021-01-03 10:00 | 44199.4167 | 0 | 11.6087 | 37.78
2021-01-03 10:30 | 44199.4375 | 0 | 9.8347 | 37.78
2021-01-03 11:00 | 44199.4583 | 0 | 9.0124 | 37.78
2021-01-03 11:30 | 44199.4792 | 0 | 9.2607 | 37.78
2021-01-03 12:00 | 44199.5 | 0 | 9.9696 | 37.78
2021-01-03 12:30 | 44199.5208 | 0 | 10.0941 | 37.78
2021-01-03 13:00 | 44199.5417 | 0 | 10.4159 | 37.78
2021-01-03 13:30 | 44199.5625 | 0 | 10.7637 | 37.78
2021-01-03 14:00 | 44199.5833 | 0 | 11.2614 | 37.78
2021-01-03 14:30 | 44199.6042 | 0 | 11.9664 | 37.78
2021-01-03 15:00 | 44199.625 | 0 | 12.1658 | 37.78
2021-01-03 15:30 | 44199.6458 | 0 | 13.2149 | 37.78
2021-01-03 16:00 | 44199.6667 | 0 | 13.7309 | 37.78
2021-01-03 16:30 | 44199.6875 | 0 | 13.5995 | 37.78
2021-01-03 17:00 | 44199.7083 | 0 | 13.8634 | 37.78
2021-01-03 17:30 | 44199.7292 | 0 | 14.3084 | 37.78
2021-01-03 18:00 | 44199.75 | 0 | 14.5651 | 37.78
2021-01-03 18:30 | 44199.7708 | 0 | 15.0692 | 37.78
2021-01-03 19:00 | 44199.7917 | 0 | 15.0582 | 37.78
2021-01-03 19:30 | 44199.8125 | 0 | 14.942 | 37.78
2021-01-03 20:00 | 44199.8333 | 0 | 14.8182 | 37.78
2021-01-03 20:30 | 44199.8542 | 0 | 14.2036 | 37.78
2021-01-03 21:00 | 44199.875 | 0 | 13.7404 | 37.78
2021-01-03 21:30 | 44199.8958 | 0 | 13.3326 | 37.78
2021-01-03 22:00 | 44199.9167 | 0 | 12.6421 | 37.78
2021-01-03 22:30 | 44199.9375 | 0 | 11.7664 | 37.78
2021-01-03 23:00 | 44199.9583 | 0 | 11.2715 | 37.78
2021-01-03 23:30 | 44199.9792 | 0 | 10.6838 | 37.78
2021-01-04 | 44200 | 0 | 10.2524 | 37.78
2021-01-04 00:30 | 44200.0208 | 0 | 10.018 | 37.78
2021-01-04 01:00 | 44200.0417 | 0 | 9.7519 | 37.78
2021-01-04 01:30 | 44200.0625 | 0 | 9.4597 | 37.78
2021-01-04 02:00 | 44200.0833 | 0 | 9.4779 | 37.78
2021-01-04 02:30 | 44200.1042 | 0 | 9.2856 | 37.78
2021-01-04 03:00 | 44200.125 | 0 | 9.3694 | 37.78
2021-01-04 03:30 | 44200.1458 | 0 | 9.377 | 37.78
2021-01-04 04:00 | 44200.1667 | 0 | 9.6347 | 37.78
2021-01-04 04:30 | 44200.1875 | 0 | 10.0393 | 37.78
2021-01-04 05:00 | 44200.2083 | 0 | 10.5032 | 37.78
2021-01-04 05:30 | 44200.2292 | 0 | 10.7556 | 37.78
2021-01-04 06:00 | 44200.25 | 0 | 11.3926 | 37.78
2021-01-04 06:30 | 44200.2708 | 0 | 12.1916 | 37.78
2021-01-04 07:00 | 44200.2917 | 0 | 12.8433 | 37.78
2021-01-04 07:30 | 44200.3125 | 0 | 13.4879 | 37.78
2021-01-04 08:00 | 44200.3333 | 0 | 13.8277 | 37.78
2021-01-04 08:30 | 44200.3542 | 0 | 13.5682 | 37.78
2021-01-04 09:00 | 44200.375 | 0 | 14.2699 | 37.78
2021-01-04 09:30 | 44200.3958 | 0 | 12.739 | 37.78
2021-01-04 10:00 | 44200.4167 | 0 | 12.9507 | 37.78
2021-01-04 10:30 | 44200.4375 | 0 | 12.9223 | 37.78
2021-01-04 11:00 | 44200.4583 | 0 | 13.8063 | 37.78
2021-01-04 11:30 | 44200.4792 | 0 | 14.8277 | 37.78
2021-01-04 12:00 | 44200.5 | 0 | 13.5178 | 37.78
2021-01-04 12:30 | 44200.5208 | 0 | 14.5298 | 37.78
2021-01-04 13:00 | 44200.5417 | 0 | 14.0336 | 37.78
2021-01-04 13:30 | 44200.5625 | 0 | 14.9461 | 37.78
2021-01-04 14:00 | 44200.5833 | 0 | 15.2497 | 37.78
2021-01-04 14:30 | 44200.6042 | 0 | 16.3382 | 37.78
2021-01-04 15:00 | 44200.625 | 0 | 17.3256 | 37.78
2021-01-04 15:30 | 44200.6458 | 0 | 16.8045 | 37.78
2021-01-04 16:00 | 44200.6667 | 0 | 17.6305 | 37.78
2021-01-04 16:30 | 44200.6875 | 0 | 17.0094 | 37.78
2021-01-04 17:00 | 44200.7083 | 0 | 17.0927 | 37.78
2021-01-04 17:30 | 44200.7292 | 0 | 17.091 | 37.78
2021-01-04 18:00 | 44200.75 | 0 | 17.285 | 37.78
2021-01-04 18:30 | 44200.7708 | 0 | 17.2036 | 37.78
2021-01-04 19:00 | 44200.7917 | 0 | 17.3065 | 37.78
2021-01-04 19:30 | 44200.8125 | 0 | 17.4599 | 37.78
2021-01-04 20:00 | 44200.8333 | 0 | 17.0005 | 37.78
2021-01-04 20:30 | 44200.8542 | 0 | 16.3619 | 37.78
2021-01-04 21:00 | 44200.875 | 0 | 15.7084 | 37.78
2021-01-04 21:30 | 44200.8958 | 0 | 15.0876 | 37.78
2021-01-04 22:00 | 44200.9167 | 0 | 14.4364 | 37.78
2021-01-04 22:30 | 44200.9375 | 0 | 13.554 | 37.78
2021-01-04 23:00 | 44200.9583 | 0 | 12.8279 | 37.78
2021-01-04 23:30 | 44200.9792 | 0 | 12.3163 | 37.78
2021-01-05 | 44201 | 0 | 11.5478 | 37.78
2021-01-05 00:30 | 44201.0208 | 0 | 10.9764 | 37.78
2021-01-05 01:00 | 44201.0417 | 0 | 10.3841 | 37.78
2021-01-05 01:30 | 44201.0625 | 0 | 10.1879 | 37.78
2021-01-05 02:00 | 44201.0833 | 0 | 10.1571 | 37.78
2021-01-05 02:30 | 44201.1042 | 0 | 10.1344 | 37.78
2021-01-05 03:00 | 44201.125 | 0 | 10.0274 | 37.78
2021-01-05 03:30 | 44201.1458 | 0 | 10.0231 | 37.78
2021-01-05 04:00 | 44201.1667 | 0 | 10.3476 | 37.78
2021-01-05 04:30 | 44201.1875 | 0 | 10.7189 | 37.78
2021-01-05 05:00 | 44201.2083 | 0 | 11.0327 | 37.78
2021-01-05 05:30 | 44201.2292 | 0 | 11.3113 | 37.78
2021-01-05 06:00 | 44201.25 | 0 | 11.661 | 37.78
2021-01-05 06:30 | 44201.2708 | 0 | 12.1177 | 37.78
2021-01-05 07:00 | 44201.2917 | 0 | 12.9761 | 37.78
2021-01-05 07:30 | 44201.3125 | 0 | 13.223 | 37.78
2021-01-05 08:00 | 44201.3333 | 0 | 13.8733 | 37.78
2021-01-05 08:30 | 44201.3542 | 0 | 14.0198 | 37.78
2021-01-05 09:00 | 44201.375 | 0 | 14.613 | 37.78
2021-01-05 09:30 | 44201.3958 | 0 | 14.8623 | 37.78
2021-01-05 10:00 | 44201.4167 | 0 | 15.3965 | 37.78
2021-01-05 10:30 | 44201.4375 | 0 | 15.5152 | 37.78
2021-01-05 11:00 | 44201.4583 | 0 | 15.8386 | 37.78
2021-01-05 11:30 | 44201.4792 | 0 | 16.4524 | 37.78
2021-01-05 12:00 | 44201.5 | 0 | 16.5724 | 37.78
2021-01-05 12:30 | 44201.5208 | 0 | 16.9872 | 37.78
2021-01-05 13:00 | 44201.5417 | 0 | 17.5581 | 37.78
2021-01-05 13:30 | 44201.5625 | 0 | 18.3965 | 37.78
2021-01-05 14:00 | 44201.5833 | 0 | 18.3761 | 37.78
2021-01-05 14:30 | 44201.6042 | 0 | 19.602 | 37.78
2021-01-05 15:00 | 44201.625 | 0 | 21.7679 | 37.78
2021-01-05 15:30 | 44201.6458 | 0 | 21.3219 | 37.78
2021-01-05 16:00 | 44201.6667 | 0 | 20.3977 | 37.78
2021-01-05 16:30 | 44201.6875 | 0 | 19.3262 | 37.78
2021-01-05 17:00 | 44201.7083 | 0 | 19.1095 | 37.78
2021-01-05 17:30 | 44201.7292 | 0 | 19.0424 | 37.78
2021-01-05 18:00 | 44201.75 | 0 | 18.9218 | 37.78
2021-01-05 18:30 | 44201.7708 | 0 | 19.4772 | 37.78
2021-01-05 19:00 | 44201.7917 | 0 | 19.6543 | 37.78
2021-01-05 19:30 | 44201.8125 | 0 | 19.5886 | 37.78
2021-01-05 20:00 | 44201.8333 | 0 | 18.9772 | 37.78
2021-01-05 20:30 | 44201.8542 | 0 | 18.0461 | 37.78
2021-01-05 21:00 | 44201.875 | 0 | 17.377 | 37.78
2021-01-05 21:30 | 44201.8958 | 0 | 16.5732 | 37.78
2021-01-05 22:00 | 44201.9167 | 0 | 15.8862 | 37.78
2021-01-05 22:30 | 44201.9375 | 0 | 14.9199 | 37.78
2021-01-05 23:00 | 44201.9583 | 0 | 14.0904 | 37.78
2021-01-05 23:30 | 44201.9792 | 0 | 13.1584 | 37.78
2021-01-06 | 44202 | 0 | 12.3357 | 37.78
2021-01-06 00:30 | 44202.0208 | 0 | 11.4596 | 37.78
2021-01-06 01:00 | 44202.0417 | 0 | 11.144 | 37.78
2021-01-06 01:30 | 44202.0625 | 0 | 10.8532 | 37.78
2021-01-06 02:00 | 44202.0833 | 0 | 10.5208 | 37.78
2021-01-06 02:30 | 44202.1042 | 0 | 10.3982 | 37.78
2021-01-06 03:00 | 44202.125 | 0 | 10.2488 | 37.78
2021-01-06 03:30 | 44202.1458 | 0 | 10.3075 | 37.78
2021-01-06 04:00 | 44202.1667 | 0 | 10.4967 | 37.78
2021-01-06 04:30 | 44202.1875 | 0 | 10.675 | 37.78
2021-01-06 05:00 | 44202.2083 | 0 | 11.165 | 37.78
2021-01-06 05:30 | 44202.2292 | 0 | 11.1663 | 37.78
2021-01-06 06:00 | 44202.25 | 0 | 12.1363 | 37.78
2021-01-06 06:30 | 44202.2708 | 0 | 13.0457 | 37.78
2021-01-06 07:00 | 44202.2917 | 0 | 13.6877 | 37.78
2021-01-06 07:30 | 44202.3125 | 0 | 14.2819 | 37.78
2021-01-06 08:00 | 44202.3333 | 0 | 15.4128 | 37.78
2021-01-06 08:30 | 44202.3542 | 0 | 14.9936 | 37.78
2021-01-06 09:00 | 44202.375 | 0 | 15.5588 | 37.78
2021-01-06 09:30 | 44202.3958 | 0 | 15.0313 | 37.78
2021-01-06 10:00 | 44202.4167 | 0 | 15.5187 | 37.78
2021-01-06 10:30 | 44202.4375 | 0 | 16.0873 | 37.78
2021-01-06 11:00 | 44202.4583 | 0 | 16.3982 | 37.78
2021-01-06 11:30 | 44202.4792 | 0 | 16.7166 | 37.78
2021-01-06 12:00 | 44202.5 | 0 | 17.0268 | 37.78
2021-01-06 12:30 | 44202.5208 | 0 | 17.4551 | 37.78
2021-01-06 13:00 | 44202.5417 | 0 | 17.9856 | 37.78
2021-01-06 13:30 | 44202.5625 | 0 | 18.5414 | 37.78
2021-01-06 14:00 | 44202.5833 | 0 | 19.1233 | 37.78
2021-01-06 14:30 | 44202.6042 | 0 | 19.511 | 37.78
2021-01-06 15:00 | 44202.625 | 0 | 20.3261 | 37.78
2021-01-06 15:30 | 44202.6458 | 0 | 21.0957 | 37.78
2021-01-06 16:00 | 44202.6667 | 0 | 20.907 | 37.78
2021-01-06 16:30 | 44202.6875 | 0 | 22.6503 | 37.78
2021-01-06 17:00 | 44202.7083 | 0 | 22.0266 | 37.78
2021-01-06 17:30 | 44202.7292 | 0 | 21.9441 | 37.78
2021-01-06 18:00 | 44202.75 | 0 | 21.6967 | 37.78
2021-01-06 18:30 | 44202.7708 | 0 | 21.8501 | 37.78
2021-01-06 19:00 | 44202.7917 | 0 | 21.2432 | 37.78
2021-01-06 19:30 | 44202.8125 | 0 | 20.2913 | 37.78
2021-01-06 20:00 | 44202.8333 | 0 | 18.9997 | 37.78
2021-01-06 20:30 | 44202.8542 | 0 | 17.7422 | 37.78
2021-01-06 21:00 | 44202.875 | 0 | 16.6932 | 37.78
2021-01-06 21:30 | 44202.8958 | 0 | 15.8146 | 37.78
2021-01-06 22:00 | 44202.9167 | 0 | 14.97 | 37.78
2021-01-06 22:30 | 44202.9375 | 0 | 13.8744 | 37.78
2021-01-06 23:00 | 44202.9583 | 0 | 13.1146 | 37.78
2021-01-06 23:30 | 44202.9792 | 0 | 12.4199 | 37.78
2021-01-07 | 44203 | 0 | 11.7151 | 37.78
2021-01-07 00:30 | 44203.0208 | 0 | 11.0474 | 37.78
2021-01-07 01:00 | 44203.0417 | 0 | 10.742 | 37.78
2021-01-07 01:30 | 44203.0625 | 0 | 10.541 | 37.78
2021-01-07 02:00 | 44203.0833 | 0 | 10.5945 | 37.78
2021-01-07 02:30 | 44203.1042 | 0 | 10.4201 | 37.78
2021-01-07 03:00 | 44203.125 | 0 | 10.367 | 37.78
2021-01-07 03:30 | 44203.1458 | 0 | 10.3475 | 37.78
2021-01-07 04:00 | 44203.1667 | 0 | 10.7755 | 37.78
2021-01-07 04:30 | 44203.1875 | 0 | 11.3224 | 37.78
2021-01-07 05:00 | 44203.2083 | 0 | 11.6534 | 37.78
2021-01-07 05:30 | 44203.2292 | 0 | 11.9263 | 37.78
2021-01-07 06:00 | 44203.25 | 0 | 12.6302 | 37.78
2021-01-07 06:30 | 44203.2708 | 0 | 13.3389 | 37.78
2021-01-07 07:00 | 44203.2917 | 0 | 13.5875 | 37.78
2021-01-07 07:30 | 44203.3125 | 0 | 13.8442 | 37.78
2021-01-07 08:00 | 44203.3333 | 0 | 14.0076 | 37.78
2021-01-07 08:30 | 44203.3542 | 0 | 14.3916 | 37.78
2021-01-07 09:00 | 44203.375 | 0 | 14.4513 | 37.78
2021-01-07 09:30 | 44203.3958 | 0 | 13.7917 | 37.78
2021-01-07 10:00 | 44203.4167 | 0 | 15.6743 | 37.78
2021-01-07 10:30 | 44203.4375 | 0 | 14.9828 | 37.78
2021-01-07 11:00 | 44203.4583 | 0 | 15.5703 | 37.78
2021-01-07 11:30 | 44203.4792 | 0 | 15.5407 | 37.78
2021-01-07 12:00 | 44203.5 | 0 | 15.8612 | 37.78
2021-01-07 12:30 | 44203.5208 | 0 | 14.912 | 37.78
2021-01-07 13:00 | 44203.5417 | 0 | 15.0711 | 37.78
2021-01-07 13:30 | 44203.5625 | 0 | 14.6575 | 37.78
2021-01-07 14:00 | 44203.5833 | 0 | 14.2837 | 37.78
2021-01-07 14:30 | 44203.6042 | 0 | 15.0664 | 37.78
2021-01-07 15:00 | 44203.625 | 0 | 15.1601 | 37.78
2021-01-07 15:30 | 44203.6458 | 0 | 15.232 | 37.78
2021-01-07 16:00 | 44203.6667 | 0 | 15.3742 | 37.78
2021-01-07 16:30 | 44203.6875 | 0 | 15.5545 | 37.78
2021-01-07 17:00 | 44203.7083 | 0 | 15.3385 | 37.78
2021-01-07 17:30 | 44203.7292 | 0 | 15.6144 | 37.78
2021-01-07 18:00 | 44203.75 | 0 | 15.2874 | 37.78
2021-01-07 18:30 | 44203.7708 | 0 | 15.4733 | 37.78
2021-01-07 19:00 | 44203.7917 | 0 | 15.4691 | 37.78
2021-01-07 19:30 | 44203.8125 | 0 | 15.2755 | 37.78
2021-01-07 20:00 | 44203.8333 | 0 | 14.8787 | 37.78
2021-01-07 20:30 | 44203.8542 | 0 | 14.2905 | 37.78
2021-01-07 21:00 | 44203.875 | 0 | 13.7594 | 37.78
2021-01-07 21:30 | 44203.8958 | 0 | 13.587 | 37.78
2021-01-07 22:00 | 44203.9167 | 0 | 12.8338 | 37.78
2021-01-07 22:30 | 44203.9375 | 0 | 11.9759 | 37.78
2021-01-07 23:00 | 44203.9583 | 0 | 11.4296 | 37.78
2021-01-07 23:30 | 44203.9792 | 0 | 10.7589 | 37.78
2021-01-08 | 44204 | 0 | 10.2457 | 37.78
2021-01-08 00:30 | 44204.0208 | 0 | 9.8934 | 37.78
2021-01-08 01:00 | 44204.0417 | 0 | 9.5563 | 37.78
2021-01-08 01:30 | 44204.0625 | 0 | 9.518 | 37.78
2021-01-08 02:00 | 44204.0833 | 0 | 9.4331 | 37.78
2021-01-08 02:30 | 44204.1042 | 0 | 9.2845 | 37.78
2021-01-08 03:00 | 44204.125 | 0 | 9.2754 | 37.78
2021-01-08 03:30 | 44204.1458 | 0 | 9.2606 | 37.78
2021-01-08 04:00 | 44204.1667 | 0 | 9.5933 | 37.78
2021-01-08 04:30 | 44204.1875 | 0 | 9.8549 | 37.78
2021-01-08 05:00 | 44204.2083 | 0 | 10.2597 | 37.78
2021-01-08 05:30 | 44204.2292 | 0 | 10.5817 | 37.78
2021-01-08 06:00 | 44204.25 | 0 | 11.0456 | 37.78
2021-01-08 06:30 | 44204.2708 | 0 | 11.8136 | 37.78
2021-01-08 07:00 | 44204.2917 | 0 | 12.4939 | 37.78
2021-01-08 07:30 | 44204.3125 | 0 | 12.8102 | 37.78
2021-01-08 08:00 | 44204.3333 | 0 | 13.5686 | 37.78
2021-01-08 08:30 | 44204.3542 | 0 | 13.369 | 37.78
2021-01-08 09:00 | 44204.375 | 0 | 13.1227 | 37.78
2021-01-08 09:30 | 44204.3958 | 0 | 13.461 | 37.78
2021-01-08 10:00 | 44204.4167 | 0 | 13.4558 | 37.78
2021-01-08 10:30 | 44204.4375 | 0 | 12.992 | 37.78
2021-01-08 11:00 | 44204.4583 | 0 | 12.5957 | 37.78
2021-01-08 11:30 | 44204.4792 | 0 | 12.8221 | 37.78
2021-01-08 12:00 | 44204.5 | 0 | 12.4142 | 37.78
2021-01-08 12:30 | 44204.5208 | 0 | 12.7877 | 37.78
2021-01-08 13:00 | 44204.5417 | 0 | 12.3016 | 37.78
2021-01-08 13:30 | 44204.5625 | 0 | 12.1034 | 37.78
2021-01-08 14:00 | 44204.5833 | 0 | 12.4788 | 37.78
2021-01-08 14:30 | 44204.6042 | 0 | 12.5611 | 37.78
2021-01-08 15:00 | 44204.625 | 0 | 12.6485 | 37.78
2021-01-08 15:30 | 44204.6458 | 0 | 12.7284 | 37.78
2021-01-08 16:00 | 44204.6667 | 0 | 12.6584 | 37.78
2021-01-08 16:30 | 44204.6875 | 0 | 13.0502 | 37.78
2021-01-08 17:00 | 44204.7083 | 0 | 13.127 | 37.78
2021-01-08 17:30 | 44204.7292 | 0 | 13.1493 | 37.78
2021-01-08 18:00 | 44204.75 | 0 | 13.0022 | 37.78
2021-01-08 18:30 | 44204.7708 | 0 | 13.7379 | 37.78
2021-01-08 19:00 | 44204.7917 | 0 | 13.5815 | 37.78
2021-01-08 19:30 | 44204.8125 | 0 | 13.2526 | 37.78
2021-01-08 20:00 | 44204.8333 | 0 | 13.1785 | 37.78
2021-01-08 20:30 | 44204.8542 | 0 | 12.323 | 37.78
2021-01-08 21:00 | 44204.875 | 0 | 11.7522 | 37.78
2021-01-08 21:30 | 44204.8958 | 0 | 11.5041 | 37.78
2021-01-08 22:00 | 44204.9167 | 0 | 11.2064 | 37.78
2021-01-08 22:30 | 44204.9375 | 0 | 10.4033 | 37.78
2021-01-08 23:00 | 44204.9583 | 0 | 10.0181 | 37.78
2021-01-08 23:30 | 44204.9792 | 0 | 9.5702 | 37.78
2021-01-09 | 44205 | 0 | 9.1859 | 37.78
2021-01-09 00:30 | 44205.0208 | 0 | 8.8349 | 37.78
2021-01-09 01:00 | 44205.0417 | 0 | 8.6171 | 37.78
2021-01-09 01:30 | 44205.0625 | 0 | 8.4548 | 37.78
2021-01-09 02:00 | 44205.0833 | 0 | 8.2649 | 37.78
2021-01-09 02:30 | 44205.1042 | 0 | 8.2392 | 37.78
2021-01-09 03:00 | 44205.125 | 0 | 8.2333 | 37.78
2021-01-09 03:30 | 44205.1458 | 0 | 8.1468 | 37.78
2021-01-09 04:00 | 44205.1667 | 0 | 8.2528 | 37.78
2021-01-09 04:30 | 44205.1875 | 0 | 8.1617 | 37.78
2021-01-09 05:00 | 44205.2083 | 0 | 8.1426 | 37.78
2021-01-09 05:30 | 44205.2292 | 0 | 8.3288 | 37.78
2021-01-09 06:00 | 44205.25 | 0 | 8.2212 | 37.78
2021-01-09 06:30 | 44205.2708 | 0 | 8.3022 | 37.78
2021-01-09 07:00 | 44205.2917 | 0 | 8.4278 | 37.78
2021-01-09 07:30 | 44205.3125 | 0 | 9.0676 | 37.78
2021-01-09 08:00 | 44205.3333 | 0 | 9.6829 | 37.78
2021-01-09 08:30 | 44205.3542 | 0 | 9.9725 | 37.78
2021-01-09 09:00 | 44205.375 | 0 | 10.1493 | 37.78
2021-01-09 09:30 | 44205.3958 | 0 | 9.9694 | 37.78
2021-01-09 10:00 | 44205.4167 | 0 | 8.6862 | 37.78
2021-01-09 10:30 | 44205.4375 | 0 | 8.2209 | 37.78
2021-01-09 11:00 | 44205.4583 | 0 | 10.32 | 37.78
2021-01-09 11:30 | 44205.4792 | 0 | 9.8467 | 37.78
2021-01-09 12:00 | 44205.5 | 0 | 10.2468 | 37.78
2021-01-09 12:30 | 44205.5208 | 0 | 10.0697 | 37.78
2021-01-09 13:00 | 44205.5417 | 0 | 9.0923 | 37.78
2021-01-09 13:30 | 44205.5625 | 0 | 9.7362 | 37.78
2021-01-09 14:00 | 44205.5833 | 0 | 10.4967 | 37.78
2021-01-09 14:30 | 44205.6042 | 0 | 10.4405 | 37.78
2021-01-09 15:00 | 44205.625 | 0 | 9.9814 | 37.78
2021-01-09 15:30 | 44205.6458 | 0 | 10.4134 | 37.78
2021-01-09 16:00 | 44205.6667 | 0 | 10.4251 | 37.78
2021-01-09 16:30 | 44205.6875 | 0 | 10.8163 | 37.78
2021-01-09 17:00 | 44205.7083 | 0 | 10.9299 | 37.78
2021-01-09 17:30 | 44205.7292 | 0 | 11.4097 | 37.78
2021-01-09 18:00 | 44205.75 | 0 | 11.519 | 37.78
2021-01-09 18:30 | 44205.7708 | 0 | 11.9678 | 37.78
2021-01-09 19:00 | 44205.7917 | 0 | 11.8005 | 37.78
2021-01-09 19:30 | 44205.8125 | 0 | 11.7661 | 37.78
2021-01-09 20:00 | 44205.8333 | 0 | 11.3892 | 37.78
2021-01-09 20:30 | 44205.8542 | 0 | 10.8892 | 37.78
2021-01-09 21:00 | 44205.875 | 0 | 10.3441 | 37.78
2021-01-09 21:30 | 44205.8958 | 0 | 10.1748 | 37.78
2021-01-09 22:00 | 44205.9167 | 0 | 9.9744 | 37.78
2021-01-09 22:30 | 44205.9375 | 0 | 9.415 | 37.78
2021-01-09 23:00 | 44205.9583 | 0 | 9.018 | 37.78
2021-01-09 23:30 | 44205.9792 | 0 | 8.6382 | 37.78
2021-01-10 | 44206 | 0 | 8.397 | 37.78
2021-01-10 00:30 | 44206.0208 | 0 | 8.017 | 37.78
2021-01-10 01:00 | 44206.0417 | 0 | 7.812 | 37.78
2021-01-10 01:30 | 44206.0625 | 0 | 7.748 | 37.78
2021-01-10 02:00 | 44206.0833 | 0 | 7.7062 | 37.78
2021-01-10 02:30 | 44206.1042 | 0 | 7.575 | 37.78
2021-01-10 03:00 | 44206.125 | 0 | 7.5442 | 37.78
2021-01-10 03:30 | 44206.1458 | 0 | 7.4768 | 37.78
2021-01-10 04:00 | 44206.1667 | 0 | 7.441 | 37.78
2021-01-10 04:30 | 44206.1875 | 0 | 7.2893 | 37.78
2021-01-10 05:00 | 44206.2083 | 0 | 7.3744 | 37.78
2021-01-10 05:30 | 44206.2292 | 0 | 7.183 | 37.78
2021-01-10 06:00 | 44206.25 | 0 | 7.3555 | 37.78
2021-01-10 06:30 | 44206.2708 | 0 | 7.1586 | 37.78
2021-01-10 07:00 | 44206.2917 | 0 | 7.6167 | 37.78
2021-01-10 07:30 | 44206.3125 | 0 | 7.338 | 37.78
2021-01-10 08:00 | 44206.3333 | 0 | 7.2314 | 37.78
2021-01-10 08:30 | 44206.3542 | 0 | 7.3638 | 37.78
2021-01-10 09:00 | 44206.375 | 0 | 8.3786 | 37.78
2021-01-10 09:30 | 44206.3958 | 0 | 8.2158 | 37.78
2021-01-10 10:00 | 44206.4167 | 0 | 7.7782 | 37.78
2021-01-10 10:30 | 44206.4375 | 0 | 8.232 | 37.78
2021-01-10 11:00 | 44206.4583 | 0 | 7.3576 | 37.78
2021-01-10 11:30 | 44206.4792 | 0 | 9.2253 | 37.78
2021-01-10 12:00 | 44206.5 | 0 | 9.0791 | 37.78
2021-01-10 12:30 | 44206.5208 | 0 | 10.1603 | 37.78
2021-01-10 13:00 | 44206.5417 | 0 | 9.9206 | 37.78
2021-01-10 13:30 | 44206.5625 | 0 | 9.2445 | 37.78
2021-01-10 14:00 | 44206.5833 | 0 | 9.093 | 37.78
2021-01-10 14:30 | 44206.6042 | 0 | 8.7805 | 37.78
2021-01-10 15:00 | 44206.625 | 0 | 8.8767 | 37.78
2021-01-10 15:30 | 44206.6458 | 0 | 10.1707 | 37.78
2021-01-10 16:00 | 44206.6667 | 0 | 10.0974 | 37.78
2021-01-10 16:30 | 44206.6875 | 0 | 10.5903 | 37.78
2021-01-10 17:00 | 44206.7083 | 0 | 10.938 | 37.78
2021-01-10 17:30 | 44206.7292 | 0 | 11.7653 | 37.78
2021-01-10 18:00 | 44206.75 | 0 | 11.9646 | 37.78
2021-01-10 18:30 | 44206.7708 | 0 | 12.2876 | 37.78
2021-01-10 19:00 | 44206.7917 | 0 | 12.5041 | 37.78
2021-01-10 19:30 | 44206.8125 | 0 | 12.4928 | 37.78
2021-01-10 20:00 | 44206.8333 | 0 | 12.3172 | 37.78
2021-01-10 20:30 | 44206.8542 | 0 | 11.702 | 37.78
2021-01-10 21:00 | 44206.875 | 0 | 11.1212 | 37.78
2021-01-10 21:30 | 44206.8958 | 0 | 10.7334 | 37.78
2021-01-10 22:00 | 44206.9167 | 0 | 10.3674 | 37.78
2021-01-10 22:30 | 44206.9375 | 0 | 9.6795 | 37.78
2021-01-10 23:00 | 44206.9583 | 0 | 9.0936 | 37.78
2021-01-10 23:30 | 44206.9792 | 0 | 8.7313 | 37.78
2021-01-11 | 44207 | 0 | 8.3877 | 37.78
2021-01-11 00:30 | 44207.0208 | 0 | 8.0288 | 37.78
2021-01-11 01:00 | 44207.0417 | 0 | 7.9015 | 37.78
2021-01-11 01:30 | 44207.0625 | 0 | 7.8653 | 37.78
2021-01-11 02:00 | 44207.0833 | 0 | 7.8521 | 37.78
2021-01-11 02:30 | 44207.1042 | 0 | 7.8002 | 37.78
2021-01-11 03:00 | 44207.125 | 0 | 7.8117 | 37.78
2021-01-11 03:30 | 44207.1458 | 0 | 7.9777 | 37.78
2021-01-11 04:00 | 44207.1667 | 0 | 8.2514 | 37.78
2021-01-11 04:30 | 44207.1875 | 0 | 8.3925 | 37.78
2021-01-11 05:00 | 44207.2083 | 0 | 8.5762 | 37.78
2021-01-11 05:30 | 44207.2292 | 0 | 9.0201 | 37.78
2021-01-11 06:00 | 44207.25 | 0 | 9.4323 | 37.78
2021-01-11 06:30 | 44207.2708 | 0 | 9.8118 | 37.78
2021-01-11 07:00 | 44207.2917 | 0 | 10.1903 | 37.78
2021-01-11 07:30 | 44207.3125 | 0 | 10.4995 | 37.78
2021-01-11 08:00 | 44207.3333 | 0 | 10.5593 | 37.78
2021-01-11 08:30 | 44207.3542 | 0 | 10.6258 | 37.78
2021-01-11 09:00 | 44207.375 | 0 | 10.4977 | 37.78
2021-01-11 09:30 | 44207.3958 | 0 | 10.6721 | 37.78
2021-01-11 10:00 | 44207.4167 | 0 | 11.0196 | 37.78
2021-01-11 10:30 | 44207.4375 | 0 | 10.8517 | 37.78
2021-01-11 11:00 | 44207.4583 | 0 | 12.1623 | 37.78
2021-01-11 11:30 | 44207.4792 | 0 | 11.5022 | 37.78
2021-01-11 12:00 | 44207.5 | 0 | 11.3953 | 37.78
2021-01-11 12:30 | 44207.5208 | 0 | 12.0553 | 37.78
2021-01-11 13:00 | 44207.5417 | 0 | 12.8681 | 37.78
2021-01-11 13:30 | 44207.5625 | 0 | 12.1181 | 37.78
2021-01-11 14:00 | 44207.5833 | 0 | 12.1033 | 37.78
2021-01-11 14:30 | 44207.6042 | 0 | 13.0069 | 37.78
2021-01-11 15:00 | 44207.625 | 0 | 13.1681 | 37.78
2021-01-11 15:30 | 44207.6458 | 0 | 13.4604 | 37.78
2021-01-11 16:00 | 44207.6667 | 0 | 13.514 | 37.78
2021-01-11 16:30 | 44207.6875 | 0 | 13.8753 | 37.78
2021-01-11 17:00 | 44207.7083 | 0 | 14.0014 | 37.78
2021-01-11 17:30 | 44207.7292 | 0 | 14.0862 | 37.78
2021-01-11 18:00 | 44207.75 | 0 | 14.1947 | 37.78
2021-01-11 18:30 | 44207.7708 | 0 | 14.3925 | 37.78
2021-01-11 19:00 | 44207.7917 | 0 | 14.5195 | 37.78
2021-01-11 19:30 | 44207.8125 | 0 | 14.4789 | 37.78
2021-01-11 20:00 | 44207.8333 | 0 | 14.2567 | 37.78
2021-01-11 20:30 | 44207.8542 | 0 | 13.6495 | 37.78
2021-01-11 21:00 | 44207.875 | 0 | 13.0637 | 37.78
2021-01-11 21:30 | 44207.8958 | 0 | 12.6357 | 37.78
2021-01-11 22:00 | 44207.9167 | 0 | 12.0592 | 37.78
2021-01-11 22:30 | 44207.9375 | 0 | 11.3293 | 37.78
2021-01-11 23:00 | 44207.9583 | 0 | 10.6265 | 37.78
2021-01-11 23:30 | 44207.9792 | 0 | 10.1726 | 37.78
2021-01-12 | 44208 | 0 | 9.4595 | 37.78
2021-01-12 00:30 | 44208.0208 | 0 | 9.1353 | 37.78
2021-01-12 01:00 | 44208.0417 | 0 | 8.8567 | 37.78
2021-01-12 01:30 | 44208.0625 | 0 | 8.6515 | 37.78
2021-01-12 02:00 | 44208.0833 | 0 | 8.6204 | 37.78
2021-01-12 02:30 | 44208.1042 | 0 | 8.4953 | 37.78
2021-01-12 03:00 | 44208.125 | 0 | 8.4417 | 37.78
2021-01-12 03:30 | 44208.1458 | 0 | 8.4552 | 37.78
2021-01-12 04:00 | 44208.1667 | 0 | 8.6609 | 37.78
2021-01-12 04:30 | 44208.1875 | 0 | 8.8526 | 37.78
2021-01-12 05:00 | 44208.2083 | 0 | 9.206 | 37.78
2021-01-12 05:30 | 44208.2292 | 0 | 9.5857 | 37.78
2021-01-12 06:00 | 44208.25 | 0 | 9.9044 | 37.78
2021-01-12 06:30 | 44208.2708 | 0 | 10.1751 | 37.78
2021-01-12 07:00 | 44208.2917 | 0 | 10.729 | 37.78
2021-01-12 07:30 | 44208.3125 | 0 | 11.3125 | 37.78
2021-01-12 08:00 | 44208.3333 | 0 | 11.1309 | 37.78
2021-01-12 08:30 | 44208.3542 | 0 | 11.3422 | 37.78
2021-01-12 09:00 | 44208.375 | 0 | 12.2105 | 37.78
2021-01-12 09:30 | 44208.3958 | 0 | 12.5409 | 37.78
2021-01-12 10:00 | 44208.4167 | 0 | 12.3966 | 37.78
2021-01-12 10:30 | 44208.4375 | 0 | 12.2633 | 37.78
2021-01-12 11:00 | 44208.4583 | 0 | 12.7128 | 37.78
2021-01-12 11:30 | 44208.4792 | 0 | 12.9942 | 37.78
2021-01-12 12:00 | 44208.5 | 0 | 13.9036 | 37.78
2021-01-12 12:30 | 44208.5208 | 0 | 12.4758 | 37.78
2021-01-12 13:00 | 44208.5417 | 0 | 12.7945 | 37.78
2021-01-12 13:30 | 44208.5625 | 0 | 14.2331 | 37.78
2021-01-12 14:00 | 44208.5833 | 0 | 14.7374 | 37.78
2021-01-12 14:30 | 44208.6042 | 0 | 14.6539 | 37.78
2021-01-12 15:00 | 44208.625 | 0 | 15.1733 | 37.78
2021-01-12 15:30 | 44208.6458 | 0 | 14.288 | 37.78
2021-01-12 16:00 | 44208.6667 | 0 | 15.0036 | 37.78
2021-01-12 16:30 | 44208.6875 | 0 | 15.1906 | 37.78
2021-01-12 17:00 | 44208.7083 | 0 | 15.3303 | 37.78
2021-01-12 17:30 | 44208.7292 | 0 | 15.496 | 37.78
2021-01-12 18:00 | 44208.75 | 0 | 15.5481 | 37.78
2021-01-12 18:30 | 44208.7708 | 0 | 16.0097 | 37.78
2021-01-12 19:00 | 44208.7917 | 0 | 16.1107 | 37.78
2021-01-12 19:30 | 44208.8125 | 0 | 16.003 | 37.78
2021-01-12 20:00 | 44208.8333 | 0 | 15.5788 | 37.78
2021-01-12 20:30 | 44208.8542 | 0 | 14.8631 | 37.78
2021-01-12 21:00 | 44208.875 | 0 | 14.1877 | 37.78
2021-01-12 21:30 | 44208.8958 | 0 | 13.7661 | 37.78
2021-01-12 22:00 | 44208.9167 | 0 | 13.1172 | 37.78
2021-01-12 22:30 | 44208.9375 | 0 | 12.1267 | 37.78
2021-01-12 23:00 | 44208.9583 | 0 | 11.3265 | 37.78
2021-01-12 23:30 | 44208.9792 | 0 | 10.8783 | 37.78
2021-01-13 | 44209 | 0 | 10.1885 | 37.78
2021-01-13 00:30 | 44209.0208 | 0 | 9.8617 | 37.78
2021-01-13 01:00 | 44209.0417 | 0 | 9.4421 | 37.78
2021-01-13 01:30 | 44209.0625 | 0 | 9.3091 | 37.78
2021-01-13 02:00 | 44209.0833 | 0 | 9.2754 | 37.78
2021-01-13 02:30 | 44209.1042 | 0 | 9.049 | 37.78
2021-01-13 03:00 | 44209.125 | 0 | 8.9419 | 37.78
2021-01-13 03:30 | 44209.1458 | 0 | 8.9107 | 37.78
2021-01-13 04:00 | 44209.1667 | 0 | 9.0763 | 37.78
2021-01-13 04:30 | 44209.1875 | 0 | 9.3696 | 37.78
2021-01-13 05:00 | 44209.2083 | 0 | 9.7335 | 37.78
2021-01-13 05:30 | 44209.2292 | 0 | 10.1706 | 37.78
2021-01-13 06:00 | 44209.25 | 0 | 10.6185 | 37.78
2021-01-13 06:30 | 44209.2708 | 0 | 11.0196 | 37.78
2021-01-13 07:00 | 44209.2917 | 0 | 11.7553 | 37.78
2021-01-13 07:30 | 44209.3125 | 0 | 12.0034 | 37.78
2021-01-13 08:00 | 44209.3333 | 0 | 12.3399 | 37.78
2021-01-13 08:30 | 44209.3542 | 0 | 12.4454 | 37.78
2021-01-13 09:00 | 44209.375 | 0 | 12.4593 | 37.78
2021-01-13 09:30 | 44209.3958 | 0 | 13.2669 | 37.78
2021-01-13 10:00 | 44209.4167 | 0 | 13.3805 | 37.78
2021-01-13 10:30 | 44209.4375 | 0 | 14.602 | 37.78
2021-01-13 11:00 | 44209.4583 | 0 | 13.6421 | 37.78
2021-01-13 11:30 | 44209.4792 | 0 | 13.5891 | 37.78
2021-01-13 12:00 | 44209.5 | 0 | 13.7907 | 37.78
2021-01-13 12:30 | 44209.5208 | 0 | 13.5708 | 37.78
2021-01-13 13:00 | 44209.5417 | 0 | 13.9475 | 37.78
2021-01-13 13:30 | 44209.5625 | 0 | 14.1382 | 37.78
2021-01-13 14:00 | 44209.5833 | 0 | 14.4284 | 37.78
2021-01-13 14:30 | 44209.6042 | 0 | 14.6545 | 37.78
2021-01-13 15:00 | 44209.625 | 0 | 15.3983 | 37.78
2021-01-13 15:30 | 44209.6458 | 0 | 15.8833 | 37.78
2021-01-13 16:00 | 44209.6667 | 0 | 16.3699 | 37.78
2021-01-13 16:30 | 44209.6875 | 0 | 16.5802 | 37.78
2021-01-13 17:00 | 44209.7083 | 0 | 16.6942 | 37.78
2021-01-13 17:30 | 44209.7292 | 0 | 16.4117 | 37.78
2021-01-13 18:00 | 44209.75 | 0 | 16.3526 | 37.78
2021-01-13 18:30 | 44209.7708 | 0 | 16.8895 | 37.78
2021-01-13 19:00 | 44209.7917 | 0 | 16.7035 | 37.78
2021-01-13 19:30 | 44209.8125 | 0 | 16.6825 | 37.78
2021-01-13 20:00 | 44209.8333 | 0 | 16.3608 | 37.78
2021-01-13 20:30 | 44209.8542 | 0 | 15.6455 | 37.78
2021-01-13 21:00 | 44209.875 | 0 | 15.0964 | 37.78
2021-01-13 21:30 | 44209.8958 | 0 | 14.5474 | 37.78
2021-01-13 22:00 | 44209.9167 | 0 | 13.9132 | 37.78
2021-01-13 22:30 | 44209.9375 | 0 | 12.9568 | 37.78
2021-01-13 23:00 | 44209.9583 | 0 | 12.3512 | 37.78
2021-01-13 23:30 | 44209.9792 | 0 | 11.7687 | 37.78
2021-01-14 | 44210 | 0 | 10.9238 | 37.78
2021-01-14 00:30 | 44210.0208 | 0 | 10.3763 | 37.78
2021-01-14 01:00 | 44210.0417 | 0 | 10.1121 | 37.78
2021-01-14 01:30 | 44210.0625 | 0 | 9.9111 | 37.78
2021-01-14 02:00 | 44210.0833 | 0 | 9.8064 | 37.78
2021-01-14 02:30 | 44210.1042 | 0 | 9.7654 | 37.78
2021-01-14 03:00 | 44210.125 | 0 | 9.6566 | 37.78
2021-01-14 03:30 | 44210.1458 | 0 | 9.6924 | 37.78
2021-01-14 04:00 | 44210.1667 | 0 | 9.8864 | 37.78
2021-01-14 04:30 | 44210.1875 | 0 | 10.1435 | 37.78
2021-01-14 05:00 | 44210.2083 | 0 | 10.4373 | 37.78
2021-01-14 05:30 | 44210.2292 | 0 | 10.8 | 37.78
2021-01-14 06:00 | 44210.25 | 0 | 11.5877 | 37.78
2021-01-14 06:30 | 44210.2708 | 0 | 11.9167 | 37.78
2021-01-14 07:00 | 44210.2917 | 0 | 12.4373 | 37.78
2021-01-14 07:30 | 44210.3125 | 0 | 12.903 | 37.78
2021-01-14 08:00 | 44210.3333 | 0 | 13.6633 | 37.78
2021-01-14 08:30 | 44210.3542 | 0 | 13.5418 | 37.78
2021-01-14 09:00 | 44210.375 | 0 | 14.5632 | 37.78
2021-01-14 09:30 | 44210.3958 | 0 | 14.6515 | 37.78
2021-01-14 10:00 | 44210.4167 | 0 | 15.1088 | 37.78
2021-01-14 10:30 | 44210.4375 | 0 | 14.6828 | 37.78
2021-01-14 11:00 | 44210.4583 | 0 | 15.8341 | 37.78
2021-01-14 11:30 | 44210.4792 | 0 | 14.5838 | 37.78
2021-01-14 12:00 | 44210.5 | 0 | 14.1963 | 37.78
2021-01-14 12:30 | 44210.5208 | 0 | 15.1021 | 37.78
2021-01-14 13:00 | 44210.5417 | 0 | 15.298 | 37.78
2021-01-14 13:30 | 44210.5625 | 0 | 16.041 | 37.78
2021-01-14 14:00 | 44210.5833 | 0 | 15.8799 | 37.78
2021-01-14 14:30 | 44210.6042 | 0 | 16.1586 | 37.78
2021-01-14 15:00 | 44210.625 | 0 | 16.5079 | 37.78
2021-01-14 15:30 | 44210.6458 | 0 | 16.7486 | 37.78
2021-01-14 16:00 | 44210.6667 | 0 | 17.019 | 37.78
2021-01-14 16:30 | 44210.6875 | 0 | 17.4557 | 37.78
2021-01-14 17:00 | 44210.7083 | 0 | 17.4549 | 37.78
2021-01-14 17:30 | 44210.7292 | 0 | 17.6148 | 37.78
2021-01-14 18:00 | 44210.75 | 0 | 17.3879 | 37.78
2021-01-14 18:30 | 44210.7708 | 0 | 17.3762 | 37.78
2021-01-14 19:00 | 44210.7917 | 0 | 17.439 | 37.78
2021-01-14 19:30 | 44210.8125 | 0 | 17.4166 | 37.78
2021-01-14 20:00 | 44210.8333 | 0 | 17.165 | 37.78
2021-01-14 20:30 | 44210.8542 | 0 | 16.3219 | 37.78
2021-01-14 21:00 | 44210.875 | 0 | 15.5919 | 37.78
2021-01-14 21:30 | 44210.8958 | 0 | 15.2621 | 37.78
2021-01-14 22:00 | 44210.9167 | 0 | 14.5235 | 37.78
2021-01-14 22:30 | 44210.9375 | 0 | 13.2748 | 37.78
2021-01-14 23:00 | 44210.9583 | 0 | 12.3482 | 37.78
2021-01-14 23:30 | 44210.9792 | 0 | 11.7723 | 37.78
2021-01-15 | 44211 | 0 | 11.0114 | 37.78
2021-01-15 00:30 | 44211.0208 | 0 | 10.5803 | 37.78
2021-01-15 01:00 | 44211.0417 | 0 | 10.2805 | 37.78
2021-01-15 01:30 | 44211.0625 | 0 | 10.0316 | 37.78
2021-01-15 02:00 | 44211.0833 | 0 | 9.938 | 37.78
2021-01-15 02:30 | 44211.1042 | 0 | 9.7441 | 37.78
2021-01-15 03:00 | 44211.125 | 0 | 9.5315 | 37.78
2021-01-15 03:30 | 44211.1458 | 0 | 9.6747 | 37.78
2021-01-15 04:00 | 44211.1667 | 0 | 9.9144 | 37.78
2021-01-15 04:30 | 44211.1875 | 0 | 10.0905 | 37.78
2021-01-15 05:00 | 44211.2083 | 0 | 10.4116 | 37.78
2021-01-15 05:30 | 44211.2292 | 0 | 10.9029 | 37.78
2021-01-15 06:00 | 44211.25 | 0 | 11.1807 | 37.78
2021-01-15 06:30 | 44211.2708 | 0 | 11.8317 | 37.78
2021-01-15 07:00 | 44211.2917 | 0 | 12.4308 | 37.78
2021-01-15 07:30 | 44211.3125 | 0 | 12.8265 | 37.78
2021-01-15 08:00 | 44211.3333 | 0 | 13.1362 | 37.78
2021-01-15 08:30 | 44211.3542 | 0 | 13.4639 | 37.78
2021-01-15 09:00 | 44211.375 | 0 | 13.9306 | 37.78
2021-01-15 09:30 | 44211.3958 | 0 | 14.1547 | 37.78
2021-01-15 10:00 | 44211.4167 | 0 | 14.185 | 37.78
2021-01-15 10:30 | 44211.4375 | 0 | 14.8528 | 37.78
2021-01-15 11:00 | 44211.4583 | 0 | 14.8424 | 37.78
2021-01-15 11:30 | 44211.4792 | 0 | 15.0387 | 37.78
2021-01-15 12:00 | 44211.5 | 0 | 15.429 | 37.78
2021-01-15 12:30 | 44211.5208 | 0 | 15.4007 | 37.78
2021-01-15 13:00 | 44211.5417 | 0 | 15.7122 | 37.78
2021-01-15 13:30 | 44211.5625 | 0 | 15.9379 | 37.78
2021-01-15 14:00 | 44211.5833 | 0 | 16.6758 | 37.78
2021-01-15 14:30 | 44211.6042 | 0 | 16.9547 | 37.78
2021-01-15 15:00 | 44211.625 | 0 | 17.2972 | 37.78
2021-01-15 15:30 | 44211.6458 | 0 | 17.5777 | 37.78
2021-01-15 16:00 | 44211.6667 | 0 | 18.0095 | 37.78
2021-01-15 16:30 | 44211.6875 | 0 | 18.3443 | 37.78
2021-01-15 17:00 | 44211.7083 | 0 | 18.5003 | 37.78
2021-01-15 17:30 | 44211.7292 | 0 | 18.6455 | 37.78
2021-01-15 18:00 | 44211.75 | 0 | 17.9509 | 37.78
2021-01-15 18:30 | 44211.7708 | 0 | 17.9257 | 37.78
2021-01-15 19:00 | 44211.7917 | 0 | 17.8707 | 37.78
2021-01-15 19:30 | 44211.8125 | 0 | 17.8991 | 37.78
2021-01-15 20:00 | 44211.8333 | 0 | 17.5139 | 37.78
2021-01-15 20:30 | 44211.8542 | 0 | 16.9965 | 37.78
2021-01-15 21:00 | 44211.875 | 0 | 16.4552 | 37.78
2021-01-15 21:30 | 44211.8958 | 0 | 15.984 | 37.78
2021-01-15 22:00 | 44211.9167 | 0 | 15.2259 | 37.78
2021-01-15 22:30 | 44211.9375 | 0 | 14.2347 | 37.78
2021-01-15 23:00 | 44211.9583 | 0 | 13.3996 | 37.78
2021-01-15 23:30 | 44211.9792 | 0 | 12.7308 | 37.78
2021-01-16 | 44212 | 0 | 11.8437 | 37.78
2021-01-16 00:30 | 44212.0208 | 0 | 11.4565 | 37.78
2021-01-16 01:00 | 44212.0417 | 0 | 11.1003 | 37.78
2021-01-16 01:30 | 44212.0625 | 0 | 10.7388 | 37.78
2021-01-16 02:00 | 44212.0833 | 0 | 10.6796 | 37.78
2021-01-16 02:30 | 44212.1042 | 0 | 10.5188 | 37.78
2021-01-16 03:00 | 44212.125 | 0 | 10.3576 | 37.78
2021-01-16 03:30 | 44212.1458 | 0 | 10.3387 | 37.78
2021-01-16 04:00 | 44212.1667 | 0 | 10.3982 | 37.78
2021-01-16 04:30 | 44212.1875 | 0 | 10.4428 | 37.78
2021-01-16 05:00 | 44212.2083 | 0 | 10.3847 | 37.78
2021-01-16 05:30 | 44212.2292 | 0 | 10.3712 | 37.78
2021-01-16 06:00 | 44212.25 | 0 | 10.407 | 37.78
2021-01-16 06:30 | 44212.2708 | 0 | 10.5139 | 37.78
2021-01-16 07:00 | 44212.2917 | 0 | 10.5473 | 37.78
2021-01-16 07:30 | 44212.3125 | 0 | 10.7216 | 37.78
2021-01-16 08:00 | 44212.3333 | 0 | 11.2515 | 37.78
2021-01-16 08:30 | 44212.3542 | 0 | 11.8007 | 37.78
2021-01-16 09:00 | 44212.375 | 0 | 11.9152 | 37.78
2021-01-16 09:30 | 44212.3958 | 0 | 12.9317 | 37.78
2021-01-16 10:00 | 44212.4167 | 0 | 12.8613 | 37.78
2021-01-16 10:30 | 44212.4375 | 0 | 13.4283 | 37.78
2021-01-16 11:00 | 44212.4583 | 0 | 14.2627 | 37.78
2021-01-16 11:30 | 44212.4792 | 0 | 14.6181 | 37.78
2021-01-16 12:00 | 44212.5 | 0 | 16.4641 | 37.78
2021-01-16 12:30 | 44212.5208 | 0 | 18.0289 | 37.78
2021-01-16 13:00 | 44212.5417 | 0 | 17.8601 | 37.78
2021-01-16 13:30 | 44212.5625 | 0 | 18.3267 | 37.78
2021-01-16 14:00 | 44212.5833 | 0 | 16.3339 | 37.78
2021-01-16 14:30 | 44212.6042 | 0 | 18.619 | 37.78
2021-01-16 15:00 | 44212.625 | 0 | 18.1516 | 37.78
2021-01-16 15:30 | 44212.6458 | 0 | 14.7571 | 37.78
2021-01-16 16:00 | 44212.6667 | 0 | 14.8711 | 37.78
2021-01-16 16:30 | 44212.6875 | 0 | 15.1165 | 37.78
2021-01-16 17:00 | 44212.7083 | 0 | 15.0628 | 37.78
2021-01-16 17:30 | 44212.7292 | 0 | 15.0582 | 37.78
2021-01-16 18:00 | 44212.75 | 0 | 15.4062 | 37.78
2021-01-16 18:30 | 44212.7708 | 0 | 15.4738 | 37.78
2021-01-16 19:00 | 44212.7917 | 0 | 15.5746 | 37.78
2021-01-16 19:30 | 44212.8125 | 0 | 15.2324 | 37.78
2021-01-16 20:00 | 44212.8333 | 0 | 14.9373 | 37.78
2021-01-16 20:30 | 44212.8542 | 0 | 14.2369 | 37.78
2021-01-16 21:00 | 44212.875 | 0 | 13.7158 | 37.78
2021-01-16 21:30 | 44212.8958 | 0 | 13.2437 | 37.78
2021-01-16 22:00 | 44212.9167 | 0 | 12.5282 | 37.78
2021-01-16 22:30 | 44212.9375 | 0 | 11.8708 | 37.78
2021-01-16 23:00 | 44212.9583 | 0 | 11.237 | 37.78
2021-01-16 23:30 | 44212.9792 | 0 | 10.7761 | 37.78
2021-01-17 | 44213 | 0 | 10.1551 | 37.78
2021-01-17 00:30 | 44213.0208 | 0 | 9.8975 | 37.78
2021-01-17 01:00 | 44213.0417 | 0 | 9.4687 | 37.78
2021-01-17 01:30 | 44213.0625 | 0 | 9.4083 | 37.78
2021-01-17 02:00 | 44213.0833 | 0 | 9.3573 | 37.78
2021-01-17 02:30 | 44213.1042 | 0 | 9.0936 | 37.78
2021-01-17 03:00 | 44213.125 | 0 | 8.915 | 37.78
2021-01-17 03:30 | 44213.1458 | 0 | 8.8213 | 37.78
2021-01-17 04:00 | 44213.1667 | 0 | 8.582 | 37.78
2021-01-17 04:30 | 44213.1875 | 0 | 8.6785 | 37.78
2021-01-17 05:00 | 44213.2083 | 0 | 8.6516 | 37.78
2021-01-17 05:30 | 44213.2292 | 0 | 8.692 | 37.78
2021-01-17 06:00 | 44213.25 | 0 | 8.8736 | 37.78
2021-01-17 06:30 | 44213.2708 | 0 | 8.9377 | 37.78
2021-01-17 07:00 | 44213.2917 | 0 | 9.2645 | 37.78
2021-01-17 07:30 | 44213.3125 | 0 | 9.4379 | 37.78
2021-01-17 08:00 | 44213.3333 | 0 | 9.4739 | 37.78
2021-01-17 08:30 | 44213.3542 | 0 | 9.5479 | 37.78
2021-01-17 09:00 | 44213.375 | 0 | 9.7794 | 37.78
2021-01-17 09:30 | 44213.3958 | 0 | 9.6798 | 37.78
2021-01-17 10:00 | 44213.4167 | 0 | 9.2358 | 37.78
2021-01-17 10:30 | 44213.4375 | 0 | 9.2702 | 37.78
2021-01-17 11:00 | 44213.4583 | 0 | 9.6549 | 37.78
2021-01-17 11:30 | 44213.4792 | 0 | 9.8252 | 37.78
2021-01-17 12:00 | 44213.5 | 0 | 10.0097 | 37.78
2021-01-17 12:30 | 44213.5208 | 0 | 10.7329 | 37.78
2021-01-17 13:00 | 44213.5417 | 0 | 9.9128 | 37.78
2021-01-17 13:30 | 44213.5625 | 0 | 10.9524 | 37.78
2021-01-17 14:00 | 44213.5833 | 0 | 11.4345 | 37.78
2021-01-17 14:30 | 44213.6042 | 0 | 11.8169 | 37.78
2021-01-17 15:00 | 44213.625 | 0 | 12.5841 | 37.78
2021-01-17 15:30 | 44213.6458 | 0 | 12.105 | 37.78
2021-01-17 16:00 | 44213.6667 | 0 | 12.6164 | 37.78
2021-01-17 16:30 | 44213.6875 | 0 | 13.5072 | 37.78
2021-01-17 17:00 | 44213.7083 | 0 | 14.3102 | 37.78
2021-01-17 17:30 | 44213.7292 | 0 | 14.8714 | 37.78
2021-01-17 18:00 | 44213.75 | 0 | 15.048 | 37.78
2021-01-17 18:30 | 44213.7708 | 0 | 15.5252 | 37.78
2021-01-17 19:00 | 44213.7917 | 0 | 15.806 | 37.78
2021-01-17 19:30 | 44213.8125 | 0 | 15.7803 | 37.78
2021-01-17 20:00 | 44213.8333 | 0 | 15.7305 | 37.78
2021-01-17 20:30 | 44213.8542 | 0 | 15.1403 | 37.78
2021-01-17 21:00 | 44213.875 | 0 | 14.6721 | 37.78
2021-01-17 21:30 | 44213.8958 | 0 | 14.2532 | 37.78
2021-01-17 22:00 | 44213.9167 | 0 | 13.5875 | 37.78
2021-01-17 22:30 | 44213.9375 | 0 | 12.6914 | 37.78
2021-01-17 23:00 | 44213.9583 | 0 | 12.0191 | 37.78
2021-01-17 23:30 | 44213.9792 | 0 | 11.3185 | 37.78
2021-01-18 | 44214 | 0 | 10.8918 | 37.78
2021-01-18 00:30 | 44214.0208 | 0 | 10.5899 | 37.78
2021-01-18 01:00 | 44214.0417 | 0 | 10.4056 | 37.78
2021-01-18 01:30 | 44214.0625 | 0 | 10.3516 | 37.78
2021-01-18 02:00 | 44214.0833 | 0 | 10.2939 | 37.78
2021-01-18 02:30 | 44214.1042 | 0 | 10.083 | 37.78
2021-01-18 03:00 | 44214.125 | 0 | 10.0809 | 37.78
2021-01-18 03:30 | 44214.1458 | 0 | 10.2288 | 37.78
2021-01-18 04:00 | 44214.1667 | 0 | 10.3847 | 37.78
2021-01-18 04:30 | 44214.1875 | 0 | 10.6983 | 37.78
2021-01-18 05:00 | 44214.2083 | 0 | 11.3054 | 37.78
2021-01-18 05:30 | 44214.2292 | 0 | 11.9914 | 37.78
2021-01-18 06:00 | 44214.25 | 0 | 12.4975 | 37.78
2021-01-18 06:30 | 44214.2708 | 0 | 13.2059 | 37.78
2021-01-18 07:00 | 44214.2917 | 0 | 14.7051 | 37.78
2021-01-18 07:30 | 44214.3125 | 0 | 14.1345 | 37.78
2021-01-18 08:00 | 44214.3333 | 0 | 15.6804 | 37.78
2021-01-18 08:30 | 44214.3542 | 0 | 15.8529 | 37.78
2021-01-18 09:00 | 44214.375 | 0 | 15.6079 | 37.78
2021-01-18 09:30 | 44214.3958 | 0 | 15.898 | 37.78
2021-01-18 10:00 | 44214.4167 | 0 | 15.2834 | 37.78
2021-01-18 10:30 | 44214.4375 | 0 | 17.0971 | 37.78
2021-01-18 11:00 | 44214.4583 | 0 | 15.4299 | 37.78
2021-01-18 11:30 | 44214.4792 | 0 | 16.7612 | 37.78
2021-01-18 12:00 | 44214.5 | 0 | 15.3753 | 37.78
2021-01-18 12:30 | 44214.5208 | 0 | 15.8504 | 37.78
2021-01-18 13:00 | 44214.5417 | 0 | 16.8679 | 37.78
2021-01-18 13:30 | 44214.5625 | 0 | 17.8801 | 37.78
2021-01-18 14:00 | 44214.5833 | 0 | 20.0379 | 37.78
2021-01-18 14:30 | 44214.6042 | 0 | 19.8415 | 37.78
2021-01-18 15:00 | 44214.625 | 0 | 19.1178 | 37.78
2021-01-18 15:30 | 44214.6458 | 0 | 18.3039 | 37.78
2021-01-18 16:00 | 44214.6667 | 0 | 18.3984 | 37.78
2021-01-18 16:30 | 44214.6875 | 0 | 18.7771 | 37.78
2021-01-18 17:00 | 44214.7083 | 0 | 18.403 | 37.78
2021-01-18 17:30 | 44214.7292 | 0 | 18.061 | 37.78
2021-01-18 18:00 | 44214.75 | 0 | 17.7911 | 37.78
2021-01-18 18:30 | 44214.7708 | 0 | 17.096 | 37.78
2021-01-18 19:00 | 44214.7917 | 0 | 16.4088 | 37.78
2021-01-18 19:30 | 44214.8125 | 0 | 16.0329 | 37.78
2021-01-18 20:00 | 44214.8333 | 0 | 15.7017 | 37.78
2021-01-18 20:30 | 44214.8542 | 0 | 14.8382 | 37.78
2021-01-18 21:00 | 44214.875 | 0 | 14.0689 | 37.78
2021-01-18 21:30 | 44214.8958 | 0 | 13.3383 | 37.78
2021-01-18 22:00 | 44214.9167 | 0 | 12.7012 | 37.78
2021-01-18 22:30 | 44214.9375 | 0 | 11.7184 | 37.78
2021-01-18 23:00 | 44214.9583 | 0 | 11.2358 | 37.78
2021-01-18 23:30 | 44214.9792 | 0 | 10.6049 | 37.78
2021-01-19 | 44215 | 0 | 10.0064 | 37.78
2021-01-19 00:30 | 44215.0208 | 0 | 9.6026 | 37.78
2021-01-19 01:00 | 44215.0417 | 0 | 9.3797 | 37.78
2021-01-19 01:30 | 44215.0625 | 0 | 9.2352 | 37.78
2021-01-19 02:00 | 44215.0833 | 0 | 9.1741 | 37.78
2021-01-19 02:30 | 44215.1042 | 0 | 9.1429 | 37.78
2021-01-19 03:00 | 44215.125 | 0 | 9.0135 | 37.78
2021-01-19 03:30 | 44215.1458 | 0 | 9.0982 | 37.78
2021-01-19 04:00 | 44215.1667 | 0 | 9.2015 | 37.78
2021-01-19 04:30 | 44215.1875 | 0 | 9.7045 | 37.78
2021-01-19 05:00 | 44215.2083 | 0 | 10.1484 | 37.78
2021-01-19 05:30 | 44215.2292 | 0 | 10.7399 | 37.78
2021-01-19 06:00 | 44215.25 | 0 | 11.3532 | 37.78
2021-01-19 06:30 | 44215.2708 | 0 | 12.0513 | 37.78
2021-01-19 07:00 | 44215.2917 | 0 | 12.7166 | 37.78
2021-01-19 07:30 | 44215.3125 | 0 | 12.7154 | 37.78
2021-01-19 08:00 | 44215.3333 | 0 | 13.0761 | 37.78
2021-01-19 08:30 | 44215.3542 | 0 | 12.1607 | 37.78
2021-01-19 09:00 | 44215.375 | 0 | 12.986 | 37.78
2021-01-19 09:30 | 44215.3958 | 0 | 13.0873 | 37.78
2021-01-19 10:00 | 44215.4167 | 0 | 12.7598 | 37.78
2021-01-19 10:30 | 44215.4375 | 0 | 12.8643 | 37.78
2021-01-19 11:00 | 44215.4583 | 0 | 11.668 | 37.78
2021-01-19 11:30 | 44215.4792 | 0 | 11.5164 | 37.78
2021-01-19 12:00 | 44215.5 | 0 | 12.8947 | 37.78
2021-01-19 12:30 | 44215.5208 | 0 | 13.401 | 37.78
2021-01-19 13:00 | 44215.5417 | 0 | 13.7262 | 37.78
2021-01-19 13:30 | 44215.5625 | 0 | 14.5942 | 37.78
2021-01-19 14:00 | 44215.5833 | 0 | 15.9424 | 37.78
2021-01-19 14:30 | 44215.6042 | 0 | 16.7837 | 37.78
2021-01-19 15:00 | 44215.625 | 0 | 17.8849 | 37.78
2021-01-19 15:30 | 44215.6458 | 0 | 17.3333 | 37.78
2021-01-19 16:00 | 44215.6667 | 0 | 17.4754 | 37.78
2021-01-19 16:30 | 44215.6875 | 0 | 17.5967 | 37.78
2021-01-19 17:00 | 44215.7083 | 0 | 18.0216 | 37.78
2021-01-19 17:30 | 44215.7292 | 0 | 18.2592 | 37.78
2021-01-19 18:00 | 44215.75 | 0 | 18.1784 | 37.78
2021-01-19 18:30 | 44215.7708 | 0 | 18.1788 | 37.78
2021-01-19 19:00 | 44215.7917 | 0 | 18.0462 | 37.78
2021-01-19 19:30 | 44215.8125 | 0 | 17.7881 | 37.78
2021-01-19 20:00 | 44215.8333 | 0 | 17.2275 | 37.78
2021-01-19 20:30 | 44215.8542 | 0 | 16.3198 | 37.78
2021-01-19 21:00 | 44215.875 | 0 | 15.7146 | 37.78
2021-01-19 21:30 | 44215.8958 | 0 | 15.0406 | 37.78
2021-01-19 22:00 | 44215.9167 | 0 | 14.3329 | 37.78
2021-01-19 22:30 | 44215.9375 | 0 | 13.1528 | 37.78
2021-01-19 23:00 | 44215.9583 | 0 | 12.3435 | 37.78
2021-01-19 23:30 | 44215.9792 | 0 | 11.5136 | 37.78
2021-01-20 | 44216 | 0 | 10.9154 | 37.78
2021-01-20 00:30 | 44216.0208 | 0 | 10.5721 | 37.78
2021-01-20 01:00 | 44216.0417 | 0 | 10.3982 | 37.78
2021-01-20 01:30 | 44216.0625 | 0 | 10.1384 | 37.78
2021-01-20 02:00 | 44216.0833 | 0 | 9.9111 | 37.78
2021-01-20 02:30 | 44216.1042 | 0 | 9.8487 | 37.78
2021-01-20 03:00 | 44216.125 | 0 | 9.8248 | 37.78
2021-01-20 03:30 | 44216.1458 | 0 | 9.7459 | 37.78
2021-01-20 04:00 | 44216.1667 | 0 | 9.9102 | 37.78
2021-01-20 04:30 | 44216.1875 | 0 | 10.1796 | 37.78
2021-01-20 05:00 | 44216.2083 | 0 | 10.5327 | 37.78
2021-01-20 05:30 | 44216.2292 | 0 | 11.1337 | 37.78
2021-01-20 06:00 | 44216.25 | 0 | 11.9776 | 37.78
2021-01-20 06:30 | 44216.2708 | 0 | 12.2338 | 37.78
2021-01-20 07:00 | 44216.2917 | 0 | 12.7422 | 37.78
2021-01-20 07:30 | 44216.3125 | 0 | 13.4149 | 37.78
2021-01-20 08:00 | 44216.3333 | 0 | 14.6224 | 37.78
2021-01-20 08:30 | 44216.3542 | 0 | 14.3738 | 37.78
2021-01-20 09:00 | 44216.375 | 0 | 14.7497 | 37.78
2021-01-20 09:30 | 44216.3958 | 0 | 14.8484 | 37.78
2021-01-20 10:00 | 44216.4167 | 0 | 14.2115 | 37.78
2021-01-20 10:30 | 44216.4375 | 0 | 13.8298 | 37.78
2021-01-20 11:00 | 44216.4583 | 0 | 15.3239 | 37.78
2021-01-20 11:30 | 44216.4792 | 0 | 13.7771 | 37.78
2021-01-20 12:00 | 44216.5 | 0 | 14.1449 | 37.78
2021-01-20 12:30 | 44216.5208 | 0 | 15.3146 | 37.78
2021-01-20 13:00 | 44216.5417 | 0 | 14.0928 | 37.78
2021-01-20 13:30 | 44216.5625 | 0 | 15.0784 | 37.78
2021-01-20 14:00 | 44216.5833 | 0 | 13.2678 | 37.78
2021-01-20 14:30 | 44216.6042 | 0 | 14.4574 | 37.78
2021-01-20 15:00 | 44216.625 | 0 | 14.6175 | 37.78
2021-01-20 15:30 | 44216.6458 | 0 | 14.538 | 37.78
2021-01-20 16:00 | 44216.6667 | 0 | 14.0776 | 37.78
2021-01-20 16:30 | 44216.6875 | 0 | 14.1876 | 37.78
2021-01-20 17:00 | 44216.7083 | 0 | 14.5652 | 37.78
2021-01-20 17:30 | 44216.7292 | 0 | 14.6826 | 37.78
2021-01-20 18:00 | 44216.75 | 0 | 14.969 | 37.78
2021-01-20 18:30 | 44216.7708 | 0 | 15.2131 | 37.78
2021-01-20 19:00 | 44216.7917 | 0 | 15.3606 | 37.78
2021-01-20 19:30 | 44216.8125 | 0 | 15.2263 | 37.78
2021-01-20 20:00 | 44216.8333 | 0 | 15.0113 | 37.78
2021-01-20 20:30 | 44216.8542 | 0 | 14.318 | 37.78
2021-01-20 21:00 | 44216.875 | 0 | 13.8367 | 37.78
2021-01-20 21:30 | 44216.8958 | 0 | 13.38 | 37.78
2021-01-20 22:00 | 44216.9167 | 0 | 12.7818 | 37.78
2021-01-20 22:30 | 44216.9375 | 0 | 11.8827 | 37.78
2021-01-20 23:00 | 44216.9583 | 0 | 11.3207 | 37.78
2021-01-20 23:30 | 44216.9792 | 0 | 10.7035 | 37.78
2021-01-21 | 44217 | 0 | 10.0667 | 37.78
2021-01-21 00:30 | 44217.0208 | 0 | 9.6265 | 37.78
2021-01-21 01:00 | 44217.0417 | 0 | 9.3932 | 37.78
2021-01-21 01:30 | 44217.0625 | 0 | 9.2991 | 37.78
2021-01-21 02:00 | 44217.0833 | 0 | 9.2574 | 37.78
2021-01-21 02:30 | 44217.1042 | 0 | 8.9643 | 37.78
2021-01-21 03:00 | 44217.125 | 0 | 8.9508 | 37.78
2021-01-21 03:30 | 44217.1458 | 0 | 9.0139 | 37.78
2021-01-21 04:00 | 44217.1667 | 0 | 9.3012 | 37.78
2021-01-21 04:30 | 44217.1875 | 0 | 9.5989 | 37.78
2021-01-21 05:00 | 44217.2083 | 0 | 10.0752 | 37.78
2021-01-21 05:30 | 44217.2292 | 0 | 10.477 | 37.78
2021-01-21 06:00 | 44217.25 | 0 | 11.1359 | 37.78
2021-01-21 06:30 | 44217.2708 | 0 | 11.7266 | 37.78
2021-01-21 07:00 | 44217.2917 | 0 | 12.355 | 37.78
2021-01-21 07:30 | 44217.3125 | 0 | 12.5947 | 37.78
2021-01-21 08:00 | 44217.3333 | 0 | 12.7624 | 37.78
2021-01-21 08:30 | 44217.3542 | 0 | 13.0013 | 37.78
2021-01-21 09:00 | 44217.375 | 0 | 13.3857 | 37.78
2021-01-21 09:30 | 44217.3958 | 0 | 13.089 | 37.78
2021-01-21 10:00 | 44217.4167 | 0 | 14.0453 | 37.78
2021-01-21 10:30 | 44217.4375 | 0 | 13.4688 | 37.78
2021-01-21 11:00 | 44217.4583 | 0 | 13.5586 | 37.78
2021-01-21 11:30 | 44217.4792 | 0 | 13.2403 | 37.78
2021-01-21 12:00 | 44217.5 | 0 | 12.6613 | 37.78
2021-01-21 12:30 | 44217.5208 | 0 | 13.4921 | 37.78
2021-01-21 13:00 | 44217.5417 | 0 | 13.5456 | 37.78
2021-01-21 13:30 | 44217.5625 | 0 | 14.1719 | 37.78
2021-01-21 14:00 | 44217.5833 | 0 | 14.1486 | 37.78
2021-01-21 14:30 | 44217.6042 | 0 | 12.6466 | 37.78
2021-01-21 15:00 | 44217.625 | 0 | 13.5957 | 37.78
2021-01-21 15:30 | 44217.6458 | 0 | 14.2022 | 37.78
2021-01-21 16:00 | 44217.6667 | 0 | 13.8822 | 37.78
2021-01-21 16:30 | 44217.6875 | 0 | 14.1152 | 37.78
2021-01-21 17:00 | 44217.7083 | 0 | 13.9877 | 37.78
2021-01-21 17:30 | 44217.7292 | 0 | 13.9007 | 37.78
2021-01-21 18:00 | 44217.75 | 0 | 13.9942 | 37.78
2021-01-21 18:30 | 44217.7708 | 0 | 14.6353 | 37.78
2021-01-21 19:00 | 44217.7917 | 0 | 14.5772 | 37.78
2021-01-21 19:30 | 44217.8125 | 0 | 14.5037 | 37.78
2021-01-21 20:00 | 44217.8333 | 0 | 14.4696 | 37.78
2021-01-21 20:30 | 44217.8542 | 0 | 14.0277 | 37.78
2021-01-21 21:00 | 44217.875 | 0 | 13.4564 | 37.78
2021-01-21 21:30 | 44217.8958 | 0 | 13.0562 | 37.78
2021-01-21 22:00 | 44217.9167 | 0 | 12.6837 | 37.78
2021-01-21 22:30 | 44217.9375 | 0 | 11.7993 | 37.78
2021-01-21 23:00 | 44217.9583 | 0 | 11.159 | 37.78
2021-01-21 23:30 | 44217.9792 | 0 | 10.534 | 37.78
2021-01-22 | 44218 | 0 | 9.6593 | 37.78
2021-01-22 00:30 | 44218.0208 | 0 | 9.4019 | 37.78
2021-01-22 01:00 | 44218.0417 | 0 | 9.1936 | 37.78
2021-01-22 01:30 | 44218.0625 | 0 | 8.9774 | 37.78
2021-01-22 02:00 | 44218.0833 | 0 | 8.7652 | 37.78
2021-01-22 02:30 | 44218.1042 | 0 | 8.7335 | 37.78
2021-01-22 03:00 | 44218.125 | 0 | 8.68 | 37.78
2021-01-22 03:30 | 44218.1458 | 0 | 8.7606 | 37.78
2021-01-22 04:00 | 44218.1667 | 0 | 9.0833 | 37.78
2021-01-22 04:30 | 44218.1875 | 0 | 9.4783 | 37.78
2021-01-22 05:00 | 44218.2083 | 0 | 9.785 | 37.78
2021-01-22 05:30 | 44218.2292 | 0 | 10.0236 | 37.78
2021-01-22 06:00 | 44218.25 | 0 | 10.6662 | 37.78
2021-01-22 06:30 | 44218.2708 | 0 | 11.1774 | 37.78
2021-01-22 07:00 | 44218.2917 | 0 | 11.9601 | 37.78
2021-01-22 07:30 | 44218.3125 | 0 | 12.1536 | 37.78
2021-01-22 08:00 | 44218.3333 | 0 | 11.9026 | 37.78
2021-01-22 08:30 | 44218.3542 | 0 | 12.1564 | 37.78
2021-01-22 09:00 | 44218.375 | 0 | 12.5537 | 37.78
2021-01-22 09:30 | 44218.3958 | 0 | 13.583 | 37.78
2021-01-22 10:00 | 44218.4167 | 0 | 13.7364 | 37.78
2021-01-22 10:30 | 44218.4375 | 0 | 12.4716 | 37.78
2021-01-22 11:00 | 44218.4583 | 0 | 11.9908 | 37.78
2021-01-22 11:30 | 44218.4792 | 0 | 12.3127 | 37.78
2021-01-22 12:00 | 44218.5 | 0 | 12.094 | 37.78
2021-01-22 12:30 | 44218.5208 | 0 | 12.3775 | 37.78
2021-01-22 13:00 | 44218.5417 | 0 | 12.4253 | 37.78
2021-01-22 13:30 | 44218.5625 | 0 | 12.9548 | 37.78
2021-01-22 14:00 | 44218.5833 | 0 | 13.2948 | 37.78
2021-01-22 14:30 | 44218.6042 | 0 | 14.1172 | 37.78
2021-01-22 15:00 | 44218.625 | 0 | 14.4552 | 37.78
2021-01-22 15:30 | 44218.6458 | 0 | 15.0226 | 37.78
2021-01-22 16:00 | 44218.6667 | 0 | 15.1545 | 37.78
2021-01-22 16:30 | 44218.6875 | 0 | 14.7463 | 37.78
2021-01-22 17:00 | 44218.7083 | 0 | 14.8078 | 37.78
2021-01-22 17:30 | 44218.7292 | 0 | 15.0094 | 37.78
2021-01-22 18:00 | 44218.75 | 0 | 15.1593 | 37.78
2021-01-22 18:30 | 44218.7708 | 0 | 15.2531 | 37.78
2021-01-22 19:00 | 44218.7917 | 0 | 15.2296 | 37.78
2021-01-22 19:30 | 44218.8125 | 0 | 15.289 | 37.78
2021-01-22 20:00 | 44218.8333 | 0 | 14.9847 | 37.78
2021-01-22 20:30 | 44218.8542 | 0 | 14.4498 | 37.78
2021-01-22 21:00 | 44218.875 | 0 | 14.0184 | 37.78
2021-01-22 21:30 | 44218.8958 | 0 | 13.5871 | 37.78
2021-01-22 22:00 | 44218.9167 | 0 | 13.1111 | 37.78
2021-01-22 22:30 | 44218.9375 | 0 | 12.0863 | 37.78
2021-01-22 23:00 | 44218.9583 | 0 | 11.3959 | 37.78
2021-01-22 23:30 | 44218.9792 | 0 | 10.8245 | 37.78
2021-01-23 | 44219 | 0 | 10.2183 | 37.78
2021-01-23 00:30 | 44219.0208 | 0 | 10.018 | 37.78
2021-01-23 01:00 | 44219.0417 | 0 | 9.6 | 37.78
2021-01-23 01:30 | 44219.0625 | 0 | 9.2108 | 37.78
2021-01-23 02:00 | 44219.0833 | 0 | 9.0805 | 37.78
2021-01-23 02:30 | 44219.1042 | 0 | 8.8669 | 37.78
2021-01-23 03:00 | 44219.125 | 0 | 8.6427 | 37.78
2021-01-23 03:30 | 44219.1458 | 0 | 8.6665 | 37.78
2021-01-23 04:00 | 44219.1667 | 0 | 8.7382 | 37.78
2021-01-23 04:30 | 44219.1875 | 0 | 8.644 | 37.78
2021-01-23 05:00 | 44219.2083 | 0 | 8.6711 | 37.78
2021-01-23 05:30 | 44219.2292 | 0 | 8.6605 | 37.78
2021-01-23 06:00 | 44219.25 | 0 | 8.625 | 37.78
2021-01-23 06:30 | 44219.2708 | 0 | 8.7754 | 37.78
2021-01-23 07:00 | 44219.2917 | 0 | 8.7517 | 37.78
2021-01-23 07:30 | 44219.3125 | 0 | 9.1003 | 37.78
2021-01-23 08:00 | 44219.3333 | 0 | 9.327 | 37.78
2021-01-23 08:30 | 44219.3542 | 0 | 9.8515 | 37.78
2021-01-23 09:00 | 44219.375 | 0 | 11.1006 | 37.78
2021-01-23 09:30 | 44219.3958 | 0 | 10.9852 | 37.78
2021-01-23 10:00 | 44219.4167 | 0 | 11.5143 | 37.78
2021-01-23 10:30 | 44219.4375 | 0 | 10.6447 | 37.78
2021-01-23 11:00 | 44219.4583 | 0 | 9.158 | 37.78
2021-01-23 11:30 | 44219.4792 | 0 | 8.9313 | 37.78
2021-01-23 12:00 | 44219.5 | 0 | 8.9236 | 37.78
2021-01-23 12:30 | 44219.5208 | 0 | 8.8661 | 37.78
2021-01-23 13:00 | 44219.5417 | 0 | 9.2498 | 37.78
2021-01-23 13:30 | 44219.5625 | 0 | 9.5141 | 37.78
2021-01-23 14:00 | 44219.5833 | 0 | 9.9159 | 37.78
2021-01-23 14:30 | 44219.6042 | 0 | 10.3104 | 37.78
2021-01-23 15:00 | 44219.625 | 0 | 10.7338 | 37.78
2021-01-23 15:30 | 44219.6458 | 0 | 11.3608 | 37.78
2021-01-23 16:00 | 44219.6667 | 0 | 11.8773 | 37.78
2021-01-23 16:30 | 44219.6875 | 0 | 12.443 | 37.78
2021-01-23 17:00 | 44219.7083 | 0 | 12.892 | 37.78
2021-01-23 17:30 | 44219.7292 | 0 | 13.3341 | 37.78
2021-01-23 18:00 | 44219.75 | 0 | 13.4246 | 37.78
2021-01-23 18:30 | 44219.7708 | 0 | 13.5187 | 37.78
2021-01-23 19:00 | 44219.7917 | 0 | 13.55 | 37.78
2021-01-23 19:30 | 44219.8125 | 0 | 13.4739 | 37.78
2021-01-23 20:00 | 44219.8333 | 0 | 13.2176 | 37.78
2021-01-23 20:30 | 44219.8542 | 0 | 12.6243 | 37.78
2021-01-23 21:00 | 44219.875 | 0 | 12.1755 | 37.78
2021-01-23 21:30 | 44219.8958 | 0 | 11.8599 | 37.78
2021-01-23 22:00 | 44219.9167 | 0 | 11.3674 | 37.78
2021-01-23 22:30 | 44219.9375 | 0 | 10.6658 | 37.78
2021-01-23 23:00 | 44219.9583 | 0 | 10.19 | 37.78
2021-01-23 23:30 | 44219.9792 | 0 | 9.7511 | 37.78
2021-01-24 | 44220 | 0 | 9.1396 | 37.78
2021-01-24 00:30 | 44220.0208 | 0 | 8.7545 | 37.78
2021-01-24 01:00 | 44220.0417 | 0 | 8.58 | 37.78
2021-01-24 01:30 | 44220.0625 | 0 | 8.3654 | 37.78
2021-01-24 02:00 | 44220.0833 | 0 | 8.2469 | 37.78
2021-01-24 02:30 | 44220.1042 | 0 | 8.0244 | 37.78
2021-01-24 03:00 | 44220.125 | 0 | 7.8965 | 37.78
2021-01-24 03:30 | 44220.1458 | 0 | 7.888 | 37.78
2021-01-24 04:00 | 44220.1667 | 0 | 7.803 | 37.78
2021-01-24 04:30 | 44220.1875 | 0 | 7.9373 | 37.78
2021-01-24 05:00 | 44220.2083 | 0 | 8.0128 | 37.78
2021-01-24 05:30 | 44220.2292 | 0 | 8.0263 | 37.78
2021-01-24 06:00 | 44220.25 | 0 | 7.8923 | 37.78
2021-01-24 06:30 | 44220.2708 | 0 | 7.8028 | 37.78
2021-01-24 07:00 | 44220.2917 | 0 | 7.2764 | 37.78
2021-01-24 07:30 | 44220.3125 | 0 | 7.8199 | 37.78
2021-01-24 08:00 | 44220.3333 | 0 | 7.293 | 37.78
2021-01-24 08:30 | 44220.3542 | 0 | 8.0813 | 37.78
2021-01-24 09:00 | 44220.375 | 0 | 8.0208 | 37.78
2021-01-24 09:30 | 44220.3958 | 0 | 8.0868 | 37.78
2021-01-24 10:00 | 44220.4167 | 0 | 8.6786 | 37.78
2021-01-24 10:30 | 44220.4375 | 0 | 8.3839 | 37.78
2021-01-24 11:00 | 44220.4583 | 0 | 8.3112 | 37.78
2021-01-24 11:30 | 44220.4792 | 0 | 8.251 | 37.78
2021-01-24 12:00 | 44220.5 | 0 | 8.4815 | 37.78
2021-01-24 12:30 | 44220.5208 | 0 | 8.747 | 37.78
2021-01-24 13:00 | 44220.5417 | 0 | 10.3331 | 37.78
2021-01-24 13:30 | 44220.5625 | 0 | 9.8371 | 37.78
2021-01-24 14:00 | 44220.5833 | 0 | 10.2051 | 37.78
2021-01-24 14:30 | 44220.6042 | 0 | 10.6717 | 37.78
2021-01-24 15:00 | 44220.625 | 0 | 11.4372 | 37.78
2021-01-24 15:30 | 44220.6458 | 0 | 11.8151 | 37.78
2021-01-24 16:00 | 44220.6667 | 0 | 13.2875 | 37.78
2021-01-24 16:30 | 44220.6875 | 0 | 13.8825 | 37.78
2021-01-24 17:00 | 44220.7083 | 0 | 13.9741 | 37.78
2021-01-24 17:30 | 44220.7292 | 0 | 14.0087 | 37.78
2021-01-24 18:00 | 44220.75 | 0 | 14.0338 | 37.78
2021-01-24 18:30 | 44220.7708 | 0 | 14.2659 | 37.78
2021-01-24 19:00 | 44220.7917 | 0 | 14.3656 | 37.78
2021-01-24 19:30 | 44220.8125 | 0 | 14.09 | 37.78
2021-01-24 20:00 | 44220.8333 | 0 | 13.6149 | 37.78
2021-01-24 20:30 | 44220.8542 | 0 | 13.1626 | 37.78
2021-01-24 21:00 | 44220.875 | 0 | 12.811 | 37.78
2021-01-24 21:30 | 44220.8958 | 0 | 12.4072 | 37.78
2021-01-24 22:00 | 44220.9167 | 0 | 11.9913 | 37.78
2021-01-24 22:30 | 44220.9375 | 0 | 11.058 | 37.78
2021-01-24 23:00 | 44220.9583 | 0 | 10.6089 | 37.78
2021-01-24 23:30 | 44220.9792 | 0 | 10.0665 | 37.78
2021-01-25 | 44221 | 0 | 9.6787 | 37.78
2021-01-25 00:30 | 44221.0208 | 0 | 9.3526 | 37.78
2021-01-25 01:00 | 44221.0417 | 0 | 9.2532 | 37.78
2021-01-25 01:30 | 44221.0625 | 0 | 9.1606 | 37.78
2021-01-25 02:00 | 44221.0833 | 0 | 9.1117 | 37.78
2021-01-25 02:30 | 44221.1042 | 0 | 9.0447 | 37.78
2021-01-25 03:00 | 44221.125 | 0 | 8.8847 | 37.78
2021-01-25 03:30 | 44221.1458 | 0 | 9.1121 | 37.78
2021-01-25 04:00 | 44221.1667 | 0 | 9.3095 | 37.78
2021-01-25 04:30 | 44221.1875 | 0 | 9.6793 | 37.78
2021-01-25 05:00 | 44221.2083 | 0 | 10.2309 | 37.78
2021-01-25 05:30 | 44221.2292 | 0 | 10.848 | 37.78
2021-01-25 06:00 | 44221.25 | 0 | 11.4998 | 37.78
2021-01-25 06:30 | 44221.2708 | 0 | 11.9602 | 37.78
2021-01-25 07:00 | 44221.2917 | 0 | 12.6151 | 37.78
2021-01-25 07:30 | 44221.3125 | 0 | 12.7353 | 37.78
2021-01-25 08:00 | 44221.3333 | 0 | 13.4014 | 37.78
2021-01-25 08:30 | 44221.3542 | 0 | 13.7169 | 37.78
2021-01-25 09:00 | 44221.375 | 0 | 14.4007 | 37.78
2021-01-25 09:30 | 44221.3958 | 0 | 13.8088 | 37.78
2021-01-25 10:00 | 44221.4167 | 0 | 12.9675 | 37.78
2021-01-25 10:30 | 44221.4375 | 0 | 14.0555 | 37.78
2021-01-25 11:00 | 44221.4583 | 0 | 14.6689 | 37.78
2021-01-25 11:30 | 44221.4792 | 0 | 13.2172 | 37.78
2021-01-25 12:00 | 44221.5 | 0 | 13.6853 | 37.78
2021-01-25 12:30 | 44221.5208 | 0 | 12.7265 | 37.78
2021-01-25 13:00 | 44221.5417 | 0 | 13.4193 | 37.78
2021-01-25 13:30 | 44221.5625 | 0 | 13.9948 | 37.78
2021-01-25 14:00 | 44221.5833 | 0 | 14.9191 | 37.78
2021-01-25 14:30 | 44221.6042 | 0 | 15.2168 | 37.78
2021-01-25 15:00 | 44221.625 | 0 | 15.704 | 37.78
2021-01-25 15:30 | 44221.6458 | 0 | 15.9373 | 37.78
2021-01-25 16:00 | 44221.6667 | 0 | 16.6899 | 37.78
2021-01-25 16:30 | 44221.6875 | 0 | 16.1971 | 37.78
2021-01-25 17:00 | 44221.7083 | 0 | 15.7404 | 37.78
2021-01-25 17:30 | 44221.7292 | 0 | 16.0375 | 37.78
2021-01-25 18:00 | 44221.75 | 0 | 15.6417 | 37.78
2021-01-25 18:30 | 44221.7708 | 0 | 15.8608 | 37.78
2021-01-25 19:00 | 44221.7917 | 0 | 16.0646 | 37.78
2021-01-25 19:30 | 44221.8125 | 0 | 15.8976 | 37.78
2021-01-25 20:00 | 44221.8333 | 0 | 15.4329 | 37.78
2021-01-25 20:30 | 44221.8542 | 0 | 14.8995 | 37.78
2021-01-25 21:00 | 44221.875 | 0 | 14.1673 | 37.78
2021-01-25 21:30 | 44221.8958 | 0 | 13.833 | 37.78
2021-01-25 22:00 | 44221.9167 | 0 | 13.3785 | 37.78
2021-01-25 22:30 | 44221.9375 | 0 | 12.5553 | 37.78
2021-01-25 23:00 | 44221.9583 | 0 | 11.7362 | 37.78
2021-01-25 23:30 | 44221.9792 | 0 | 11.2213 | 37.78
2021-01-26 | 44222 | 0 | 10.4923 | 37.78
2021-01-26 00:30 | 44222.0208 | 0 | 9.9198 | 37.78
2021-01-26 01:00 | 44222.0417 | 0 | 9.5377 | 37.78
2021-01-26 01:30 | 44222.0625 | 0 | 9.3258 | 37.78
2021-01-26 02:00 | 44222.0833 | 0 | 8.9443 | 37.78
2021-01-26 02:30 | 44222.1042 | 0 | 8.851 | 37.78
2021-01-26 03:00 | 44222.125 | 0 | 8.7545 | 37.78
2021-01-26 03:30 | 44222.1458 | 0 | 8.7036 | 37.78
2021-01-26 04:00 | 44222.1667 | 0 | 8.6381 | 37.78
2021-01-26 04:30 | 44222.1875 | 0 | 8.5715 | 37.78
2021-01-26 05:00 | 44222.2083 | 0 | 8.647 | 37.78
2021-01-26 05:30 | 44222.2292 | 0 | 8.7799 | 37.78
2021-01-26 06:00 | 44222.25 | 0 | 8.7693 | 37.78
2021-01-26 06:30 | 44222.2708 | 0 | 8.5265 | 37.78
2021-01-26 07:00 | 44222.2917 | 0 | 8.7889 | 37.78
2021-01-26 07:30 | 44222.3125 | 0 | 8.9465 | 37.78
2021-01-26 08:00 | 44222.3333 | 0 | 9.2601 | 37.78
2021-01-26 08:30 | 44222.3542 | 0 | 9.3681 | 37.78
2021-01-26 09:00 | 44222.375 | 0 | 9.8976 | 37.78
2021-01-26 09:30 | 44222.3958 | 0 | 10.2208 | 37.78
2021-01-26 10:00 | 44222.4167 | 0 | 10.1253 | 37.78
2021-01-26 10:30 | 44222.4375 | 0 | 10.1543 | 37.78
2021-01-26 11:00 | 44222.4583 | 0 | 10.1972 | 37.78
2021-01-26 11:30 | 44222.4792 | 0 | 10.5163 | 37.78
2021-01-26 12:00 | 44222.5 | 0 | 10.7033 | 37.78
2021-01-26 12:30 | 44222.5208 | 0 | 10.9476 | 37.78
2021-01-26 13:00 | 44222.5417 | 0 | 11.2756 | 37.78
2021-01-26 13:30 | 44222.5625 | 0 | 11.5687 | 37.78
2021-01-26 14:00 | 44222.5833 | 0 | 12.3647 | 37.78
2021-01-26 14:30 | 44222.6042 | 0 | 12.8258 | 37.78
2021-01-26 15:00 | 44222.625 | 0 | 13.4236 | 37.78
2021-01-26 15:30 | 44222.6458 | 0 | 14.0453 | 37.78
2021-01-26 16:00 | 44222.6667 | 0 | 14.7586 | 37.78
2021-01-26 16:30 | 44222.6875 | 0 | 15.7282 | 37.78
2021-01-26 17:00 | 44222.7083 | 0 | 16.3104 | 37.78
2021-01-26 17:30 | 44222.7292 | 0 | 16.7676 | 37.78
2021-01-26 18:00 | 44222.75 | 0 | 16.6779 | 37.78
2021-01-26 18:30 | 44222.7708 | 0 | 16.8169 | 37.78
2021-01-26 19:00 | 44222.7917 | 0 | 17.0565 | 37.78
2021-01-26 19:30 | 44222.8125 | 0 | 16.9515 | 37.78
2021-01-26 20:00 | 44222.8333 | 0 | 16.5318 | 37.78
2021-01-26 20:30 | 44222.8542 | 0 | 15.7651 | 37.78
2021-01-26 21:00 | 44222.875 | 0 | 15.1102 | 37.78
2021-01-26 21:30 | 44222.8958 | 0 | 14.4145 | 37.78
2021-01-26 22:00 | 44222.9167 | 0 | 13.5188 | 37.78
2021-01-26 22:30 | 44222.9375 | 0 | 12.4695 | 37.78
2021-01-26 23:00 | 44222.9583 | 0 | 11.6467 | 37.78
2021-01-26 23:30 | 44222.9792 | 0 | 11.1635 | 37.78
2021-01-27 | 44223 | 0 | 10.6842 | 37.78
2021-01-27 00:30 | 44223.0208 | 0 | 10.2702 | 37.78
2021-01-27 01:00 | 44223.0417 | 0 | 10.0763 | 37.78
2021-01-27 01:30 | 44223.0625 | 0 | 9.9288 | 37.78
2021-01-27 02:00 | 44223.0833 | 0 | 9.8115 | 37.78
2021-01-27 02:30 | 44223.1042 | 0 | 9.7755 | 37.78
2021-01-27 03:00 | 44223.125 | 0 | 9.5141 | 37.78
2021-01-27 03:30 | 44223.1458 | 0 | 9.603 | 37.78
2021-01-27 04:00 | 44223.1667 | 0 | 9.7255 | 37.78
2021-01-27 04:30 | 44223.1875 | 0 | 10.2437 | 37.78
2021-01-27 05:00 | 44223.2083 | 0 | 10.5102 | 37.78
2021-01-27 05:30 | 44223.2292 | 0 | 11.1162 | 37.78
2021-01-27 06:00 | 44223.25 | 0 | 12.1159 | 37.78
2021-01-27 06:30 | 44223.2708 | 0 | 12.7043 | 37.78
2021-01-27 07:00 | 44223.2917 | 0 | 13.4903 | 37.78
2021-01-27 07:30 | 44223.3125 | 0 | 14.142 | 37.78
2021-01-27 08:00 | 44223.3333 | 0 | 14.5864 | 37.78
2021-01-27 08:30 | 44223.3542 | 0 | 14.7729 | 37.78
2021-01-27 09:00 | 44223.375 | 0 | 15.2601 | 37.78
2021-01-27 09:30 | 44223.3958 | 0 | 16.0838 | 37.78
2021-01-27 10:00 | 44223.4167 | 0 | 16.9206 | 37.78
2021-01-27 10:30 | 44223.4375 | 0 | 16.1383 | 37.78
2021-01-27 11:00 | 44223.4583 | 0 | 16.3833 | 37.78
2021-01-27 11:30 | 44223.4792 | 0 | 16.4735 | 37.78
2021-01-27 12:00 | 44223.5 | 0 | 17.2178 | 37.78
2021-01-27 12:30 | 44223.5208 | 0 | 17.1483 | 37.78
2021-01-27 13:00 | 44223.5417 | 0 | 17.9935 | 37.78
2021-01-27 13:30 | 44223.5625 | 0 | 18.0523 | 37.78
2021-01-27 14:00 | 44223.5833 | 0 | 18.8214 | 37.78
2021-01-27 14:30 | 44223.6042 | 0 | 19.2995 | 37.78
2021-01-27 15:00 | 44223.625 | 0 | 19.375 | 37.78
2021-01-27 15:30 | 44223.6458 | 0 | 20.1584 | 37.78
2021-01-27 16:00 | 44223.6667 | 0 | 20.701 | 37.78
2021-01-27 16:30 | 44223.6875 | 0 | 21.1078 | 37.78
2021-01-27 17:00 | 44223.7083 | 0 | 21.1113 | 37.78
2021-01-27 17:30 | 44223.7292 | 0 | 21.2193 | 37.78
2021-01-27 18:00 | 44223.75 | 0 | 21.0052 | 37.78
2021-01-27 18:30 | 44223.7708 | 0 | 21.1941 | 37.78
2021-01-27 19:00 | 44223.7917 | 0 | 20.9573 | 37.78
2021-01-27 19:30 | 44223.8125 | 0 | 20.8317 | 37.78
2021-01-27 20:00 | 44223.8333 | 0 | 20.3752 | 37.78
2021-01-27 20:30 | 44223.8542 | 0 | 19.0416 | 37.78
2021-01-27 21:00 | 44223.875 | 0 | 17.9427 | 37.78
2021-01-27 21:30 | 44223.8958 | 0 | 17.123 | 37.78
2021-01-27 22:00 | 44223.9167 | 0 | 16.1292 | 37.78
2021-01-27 22:30 | 44223.9375 | 0 | 14.9627 | 37.78
2021-01-27 23:00 | 44223.9583 | 0 | 14.0541 | 37.78
2021-01-27 23:30 | 44223.9792 | 0 | 13.4251 | 37.78
2021-01-28 | 44224 | 0 | 12.5914 | 37.78
2021-01-28 00:30 | 44224.0208 | 0 | 11.8839 | 37.78
2021-01-28 01:00 | 44224.0417 | 0 | 11.4308 | 37.78
2021-01-28 01:30 | 44224.0625 | 0 | 11.2152 | 37.78
2021-01-28 02:00 | 44224.0833 | 0 | 11.0202 | 37.78
2021-01-28 02:30 | 44224.1042 | 0 | 10.8104 | 37.78
2021-01-28 03:00 | 44224.125 | 0 | 10.7805 | 37.78
2021-01-28 03:30 | 44224.1458 | 0 | 10.7392 | 37.78
2021-01-28 04:00 | 44224.1667 | 0 | 10.9552 | 37.78
2021-01-28 04:30 | 44224.1875 | 0 | 11.3307 | 37.78
2021-01-28 05:00 | 44224.2083 | 0 | 11.7386 | 37.78
2021-01-28 05:30 | 44224.2292 | 0 | 12.162 | 37.78
2021-01-28 06:00 | 44224.25 | 0 | 13.115 | 37.78
2021-01-28 06:30 | 44224.2708 | 0 | 13.749 | 37.78
2021-01-28 07:00 | 44224.2917 | 0 | 15.4464 | 37.78
2021-01-28 07:30 | 44224.3125 | 0 | 15.0922 | 37.78
2021-01-28 08:00 | 44224.3333 | 0 | 14.853 | 37.78
2021-01-28 08:30 | 44224.3542 | 0 | 14.6196 | 37.78
2021-01-28 09:00 | 44224.375 | 0 | 14.8463 | 37.78
2021-01-28 09:30 | 44224.3958 | 0 | 15.4723 | 37.78
2021-01-28 10:00 | 44224.4167 | 0 | 15.1331 | 37.78
2021-01-28 10:30 | 44224.4375 | 0 | 15.749 | 37.78
2021-01-28 11:00 | 44224.4583 | 0 | 16.2509 | 37.78
2021-01-28 11:30 | 44224.4792 | 0 | 15.2819 | 37.78
2021-01-28 12:00 | 44224.5 | 0 | 14.8606 | 37.78
2021-01-28 12:30 | 44224.5208 | 0 | 15.5783 | 37.78
2021-01-28 13:00 | 44224.5417 | 0 | 15.7142 | 37.78
2021-01-28 13:30 | 44224.5625 | 0 | 16.3699 | 37.78
2021-01-28 14:00 | 44224.5833 | 0 | 17.1509 | 37.78
2021-01-28 14:30 | 44224.6042 | 0 | 16.8356 | 37.78
2021-01-28 15:00 | 44224.625 | 0 | 18.1902 | 37.78
2021-01-28 15:30 | 44224.6458 | 0 | 17.2467 | 37.78
2021-01-28 16:00 | 44224.6667 | 0 | 17.7532 | 37.78
2021-01-28 16:30 | 44224.6875 | 0 | 18.0383 | 37.78
2021-01-28 17:00 | 44224.7083 | 0 | 17.929 | 37.78
2021-01-28 17:30 | 44224.7292 | 0 | 18.3516 | 37.78
2021-01-28 18:00 | 44224.75 | 0 | 17.9721 | 37.78
2021-01-28 18:30 | 44224.7708 | 0 | 18.262 | 37.78
2021-01-28 19:00 | 44224.7917 | 0 | 18.5258 | 37.78
2021-01-28 19:30 | 44224.8125 | 0 | 18.3484 | 37.78
2021-01-28 20:00 | 44224.8333 | 0 | 17.903 | 37.78
2021-01-28 20:30 | 44224.8542 | 0 | 17.0832 | 37.78
2021-01-28 21:00 | 44224.875 | 0 | 16.2531 | 37.78
2021-01-28 21:30 | 44224.8958 | 0 | 15.6053 | 37.78
2021-01-28 22:00 | 44224.9167 | 0 | 14.7413 | 37.78
2021-01-28 22:30 | 44224.9375 | 0 | 13.7034 | 37.78
2021-01-28 23:00 | 44224.9583 | 0 | 13.0489 | 37.78
2021-01-28 23:30 | 44224.9792 | 0 | 12.3013 | 37.78
2021-01-29 | 44225 | 0 | 11.556 | 37.78
2021-01-29 00:30 | 44225.0208 | 0 | 11.1516 | 37.78
2021-01-29 01:00 | 44225.0417 | 0 | 10.5777 | 37.78
2021-01-29 01:30 | 44225.0625 | 0 | 10.3712 | 37.78
2021-01-29 02:00 | 44225.0833 | 0 | 10.2753 | 37.78
2021-01-29 02:30 | 44225.1042 | 0 | 10.2372 | 37.78
2021-01-29 03:00 | 44225.125 | 0 | 10.2535 | 37.78
2021-01-29 03:30 | 44225.1458 | 0 | 10.2391 | 37.78
2021-01-29 04:00 | 44225.1667 | 0 | 10.3744 | 37.78
2021-01-29 04:30 | 44225.1875 | 0 | 10.7598 | 37.78
2021-01-29 05:00 | 44225.2083 | 0 | 11.1863 | 37.78
2021-01-29 05:30 | 44225.2292 | 0 | 11.6345 | 37.78
2021-01-29 06:00 | 44225.25 | 0 | 12.4777 | 37.78
2021-01-29 06:30 | 44225.2708 | 0 | 13.1695 | 37.78
2021-01-29 07:00 | 44225.2917 | 0 | 13.4381 | 37.78
2021-01-29 07:30 | 44225.3125 | 0 | 14.5458 | 37.78
2021-01-29 08:00 | 44225.3333 | 0 | 14.0589 | 37.78
2021-01-29 08:30 | 44225.3542 | 0 | 14.6754 | 37.78
2021-01-29 09:00 | 44225.375 | 0 | 14.5151 | 37.78
2021-01-29 09:30 | 44225.3958 | 0 | 14.9128 | 37.78
2021-01-29 10:00 | 44225.4167 | 0 | 15.635 | 37.78
2021-01-29 10:30 | 44225.4375 | 0 | 15.3785 | 37.78
2021-01-29 11:00 | 44225.4583 | 0 | 14.5611 | 37.78
2021-01-29 11:30 | 44225.4792 | 0 | 15.2143 | 37.78
2021-01-29 12:00 | 44225.5 | 0 | 14.8578 | 37.78
2021-01-29 12:30 | 44225.5208 | 0 | 15.2068 | 37.78
2021-01-29 13:00 | 44225.5417 | 0 | 15.4967 | 37.78
2021-01-29 13:30 | 44225.5625 | 0 | 16.0529 | 37.78
2021-01-29 14:00 | 44225.5833 | 0 | 16.2534 | 37.78
2021-01-29 14:30 | 44225.6042 | 0 | 16.7281 | 37.78
2021-01-29 15:00 | 44225.625 | 0 | 16.3165 | 37.78
2021-01-29 15:30 | 44225.6458 | 0 | 16.6374 | 37.78
2021-01-29 16:00 | 44225.6667 | 0 | 17.0971 | 37.78
2021-01-29 16:30 | 44225.6875 | 0 | 17.2998 | 37.78
2021-01-29 17:00 | 44225.7083 | 0 | 17.5956 | 37.78
2021-01-29 17:30 | 44225.7292 | 0 | 17.3046 | 37.78
2021-01-29 18:00 | 44225.75 | 0 | 16.7784 | 37.78
2021-01-29 18:30 | 44225.7708 | 0 | 16.81 | 37.78
2021-01-29 19:00 | 44225.7917 | 0 | 16.9016 | 37.78
2021-01-29 19:30 | 44225.8125 | 0 | 16.9438 | 37.78
2021-01-29 20:00 | 44225.8333 | 0 | 16.5833 | 37.78
2021-01-29 20:30 | 44225.8542 | 0 | 15.8971 | 37.78
2021-01-29 21:00 | 44225.875 | 0 | 15.3617 | 37.78
2021-01-29 21:30 | 44225.8958 | 0 | 14.6797 | 37.78
2021-01-29 22:00 | 44225.9167 | 0 | 14.3117 | 37.78
2021-01-29 22:30 | 44225.9375 | 0 | 13.3697 | 37.78
2021-01-29 23:00 | 44225.9583 | 0 | 12.5904 | 37.78
2021-01-29 23:30 | 44225.9792 | 0 | 11.9391 | 37.78
2021-01-30 | 44226 | 0 | 11.2366 | 37.78
2021-01-30 00:30 | 44226.0208 | 0 | 10.6663 | 37.78
2021-01-30 01:00 | 44226.0417 | 0 | 10.3529 | 37.78
2021-01-30 01:30 | 44226.0625 | 0 | 10.1073 | 37.78
2021-01-30 02:00 | 44226.0833 | 0 | 9.9795 | 37.78
2021-01-30 02:30 | 44226.1042 | 0 | 9.8148 | 37.78
2021-01-30 03:00 | 44226.125 | 0 | 9.7179 | 37.78
2021-01-30 03:30 | 44226.1458 | 0 | 9.8475 | 37.78
2021-01-30 04:00 | 44226.1667 | 0 | 9.8392 | 37.78
2021-01-30 04:30 | 44226.1875 | 0 | 9.6765 | 37.78
2021-01-30 05:00 | 44226.2083 | 0 | 9.5839 | 37.78
2021-01-30 05:30 | 44226.2292 | 0 | 9.4499 | 37.78
2021-01-30 06:00 | 44226.25 | 0 | 9.3234 | 37.78
2021-01-30 06:30 | 44226.2708 | 0 | 9.4665 | 37.78
2021-01-30 07:00 | 44226.2917 | 0 | 10.0576 | 37.78
2021-01-30 07:30 | 44226.3125 | 0 | 10.2919 | 37.78
2021-01-30 08:00 | 44226.3333 | 0 | 10.475 | 37.78
2021-01-30 08:30 | 44226.3542 | 0 | 11.023 | 37.78
2021-01-30 09:00 | 44226.375 | 0 | 11.1686 | 37.78
2021-01-30 09:30 | 44226.3958 | 0 | 11.3082 | 37.78
2021-01-30 10:00 | 44226.4167 | 0 | 11.3755 | 37.78
2021-01-30 10:30 | 44226.4375 | 0 | 11.2673 | 37.78
2021-01-30 11:00 | 44226.4583 | 0 | 11.8063 | 37.78
2021-01-30 11:30 | 44226.4792 | 0 | 11.9488 | 37.78
2021-01-30 12:00 | 44226.5 | 0 | 12.6989 | 37.78
2021-01-30 12:30 | 44226.5208 | 0 | 12.644 | 37.78
2021-01-30 13:00 | 44226.5417 | 0 | 12.9889 | 37.78
2021-01-30 13:30 | 44226.5625 | 0 | 13.0588 | 37.78
2021-01-30 14:00 | 44226.5833 | 0 | 14.0211 | 37.78
2021-01-30 14:30 | 44226.6042 | 0 | 14.2124 | 37.78
2021-01-30 15:00 | 44226.625 | 0 | 14.1554 | 37.78
2021-01-30 15:30 | 44226.6458 | 0 | 14.8848 | 37.78
2021-01-30 16:00 | 44226.6667 | 0 | 15.0036 | 37.78
2021-01-30 16:30 | 44226.6875 | 0 | 16.0097 | 37.78
2021-01-30 17:00 | 44226.7083 | 0 | 15.5332 | 37.78
2021-01-30 17:30 | 44226.7292 | 0 | 15.9222 | 37.78
2021-01-30 18:00 | 44226.75 | 0 | 15.7478 | 37.78
2021-01-30 18:30 | 44226.7708 | 0 | 15.9028 | 37.78
2021-01-30 19:00 | 44226.7917 | 0 | 15.7575 | 37.78
2021-01-30 19:30 | 44226.8125 | 0 | 15.4402 | 37.78
2021-01-30 20:00 | 44226.8333 | 0 | 15.3519 | 37.78
2021-01-30 20:30 | 44226.8542 | 0 | 15.1847 | 37.78
2021-01-30 21:00 | 44226.875 | 0 | 14.5689 | 37.78
2021-01-30 21:30 | 44226.8958 | 0 | 13.9644 | 37.78
2021-01-30 22:00 | 44226.9167 | 0 | 13.5797 | 37.78
2021-01-30 22:30 | 44226.9375 | 0 | 12.4222 | 37.78
2021-01-30 23:00 | 44226.9583 | 0 | 11.7784 | 37.78
2021-01-30 23:30 | 44226.9792 | 0 | 11.3113 | 37.78
2021-01-31 | 44227 | 0 | 10.7529 | 37.78
2021-01-31 00:30 | 44227.0208 | 0 | 10.308 | 37.78
2021-01-31 01:00 | 44227.0417 | 0 | 10.1146 | 37.78
2021-01-31 01:30 | 44227.0625 | 0 | 9.7705 | 37.78
2021-01-31 02:00 | 44227.0833 | 0 | 9.6695 | 37.78
2021-01-31 02:30 | 44227.1042 | 0 | 9.3856 | 37.78
2021-01-31 03:00 | 44227.125 | 0 | 9.3196 | 37.78
2021-01-31 03:30 | 44227.1458 | 0 | 9.2751 | 37.78
2021-01-31 04:00 | 44227.1667 | 0 | 9.1777 | 37.78
2021-01-31 04:30 | 44227.1875 | 0 | 9.1131 | 37.78
2021-01-31 05:00 | 44227.2083 | 0 | 9.0691 | 37.78
2021-01-31 05:30 | 44227.2292 | 0 | 9.0006 | 37.78
2021-01-31 06:00 | 44227.25 | 0 | 8.8055 | 37.78
2021-01-31 06:30 | 44227.2708 | 0 | 8.89 | 37.78
2021-01-31 07:00 | 44227.2917 | 0 | 9.277 | 37.78
2021-01-31 07:30 | 44227.3125 | 0 | 9.6044 | 37.78
2021-01-31 08:00 | 44227.3333 | 0 | 10.1231 | 37.78
2021-01-31 08:30 | 44227.3542 | 0 | 9.602 | 37.78
2021-01-31 09:00 | 44227.375 | 0 | 11.1957 | 37.78
2021-01-31 09:30 | 44227.3958 | 0 | 11.4782 | 37.78
2021-01-31 10:00 | 44227.4167 | 0 | 11.0979 | 37.78
2021-01-31 10:30 | 44227.4375 | 0 | 11.8817 | 37.78
2021-01-31 11:00 | 44227.4583 | 0 | 11.3133 | 37.78
2021-01-31 11:30 | 44227.4792 | 0 | 11.2783 | 37.78
2021-01-31 12:00 | 44227.5 | 0 | 11.1897 | 37.78
2021-01-31 12:30 | 44227.5208 | 0 | 11.4974 | 37.78
2021-01-31 13:00 | 44227.5417 | 0 | 12.1385 | 37.78
2021-01-31 13:30 | 44227.5625 | 0 | 12.4151 | 37.78
2021-01-31 14:00 | 44227.5833 | 0 | 13.1596 | 37.78
2021-01-31 14:30 | 44227.6042 | 0 | 14.5972 | 37.78
2021-01-31 15:00 | 44227.625 | 0 | 14.4978 | 37.78
2021-01-31 15:30 | 44227.6458 | 0 | 14.8444 | 37.78
2021-01-31 16:00 | 44227.6667 | 0 | 15.7938 | 37.78
2021-01-31 16:30 | 44227.6875 | 0 | 15.9314 | 37.78
2021-01-31 17:00 | 44227.7083 | 0 | 16.1981 | 37.78
2021-01-31 17:30 | 44227.7292 | 0 | 16.2358 | 37.78
2021-01-31 18:00 | 44227.75 | 0 | 16.1917 | 37.78
2021-01-31 18:30 | 44227.7708 | 0 | 16.5115 | 37.78
2021-01-31 19:00 | 44227.7917 | 0 | 16.621 | 37.78
2021-01-31 19:30 | 44227.8125 | 0 | 16.3002 | 37.78
2021-01-31 20:00 | 44227.8333 | 0 | 16.0597 | 37.78
2021-01-31 20:30 | 44227.8542 | 0 | 15.1441 | 37.78
2021-01-31 21:00 | 44227.875 | 0 | 14.6374 | 37.78
2021-01-31 21:30 | 44227.8958 | 0 | 13.6735 | 37.78
2021-01-31 22:00 | 44227.9167 | 0 | 12.8598 | 37.78
2021-01-31 22:30 | 44227.9375 | 0 | 12.0213 | 37.78
2021-01-31 23:00 | 44227.9583 | 0 | 11.1361 | 37.78
2021-01-31 23:30 | 44227.9792 | 0 | 10.4748 | 37.78
2021-02-01 | 44228 | 0 | 10.0918 | 37.78
2021-02-01 00:30 | 44228.0208 | 0 | 9.8925 | 37.78
2021-02-01 01:00 | 44228.0417 | 0 | 9.7422 | 37.78
2021-02-01 01:30 | 44228.0625 | 0 | 9.536 | 37.78
2021-02-01 02:00 | 44228.0833 | 0 | 9.535 | 37.78
2021-02-01 02:30 | 44228.1042 | 0 | 9.3132 | 37.78
2021-02-01 03:00 | 44228.125 | 0 | 9.342 | 37.78
2021-02-01 03:30 | 44228.1458 | 0 | 9.3808 | 37.78
2021-02-01 04:00 | 44228.1667 | 0 | 9.6427 | 37.78
2021-02-01 04:30 | 44228.1875 | 0 | 10.1594 | 37.78
2021-02-01 05:00 | 44228.2083 | 0 | 10.5426 | 37.78
2021-02-01 05:30 | 44228.2292 | 0 | 10.9067 | 37.78
2021-02-01 06:00 | 44228.25 | 0 | 11.7777 | 37.78
2021-02-01 06:30 | 44228.2708 | 0 | 12.2484 | 37.78
2021-02-01 07:00 | 44228.2917 | 0 | 13.2092 | 37.78
2021-02-01 07:30 | 44228.3125 | 0 | 13.8653 | 37.78
2021-02-01 08:00 | 44228.3333 | 0 | 13.6688 | 37.78
2021-02-01 08:30 | 44228.3542 | 0 | 15.1838 | 37.78
2021-02-01 09:00 | 44228.375 | 0 | 14.6087 | 37.78
2021-02-01 09:30 | 44228.3958 | 0 | 12.9765 | 37.78
2021-02-01 10:00 | 44228.4167 | 0 | 15.3213 | 37.78
2021-02-01 10:30 | 44228.4375 | 0 | 13.6752 | 37.78
2021-02-01 11:00 | 44228.4583 | 0 | 13.5693 | 37.78
2021-02-01 11:30 | 44228.4792 | 0 | 14.3988 | 37.78
2021-02-01 12:00 | 44228.5 | 0 | 14.0853 | 37.78
2021-02-01 12:30 | 44228.5208 | 0 | 14.7487 | 37.78
2021-02-01 13:00 | 44228.5417 | 0 | 14.411 | 37.78
2021-02-01 13:30 | 44228.5625 | 0 | 15.3843 | 37.78
2021-02-01 14:00 | 44228.5833 | 0 | 15.7752 | 37.78
2021-02-01 14:30 | 44228.6042 | 0 | 15.3576 | 37.78
2021-02-01 15:00 | 44228.625 | 0 | 15.6025 | 37.78
2021-02-01 15:30 | 44228.6458 | 0 | 15.6207 | 37.78
2021-02-01 16:00 | 44228.6667 | 0 | 16.2811 | 37.78
2021-02-01 16:30 | 44228.6875 | 0 | 16.8404 | 37.78
2021-02-01 17:00 | 44228.7083 | 0 | 16.6666 | 37.78
2021-02-01 17:30 | 44228.7292 | 0 | 16.9441 | 37.78
2021-02-01 18:00 | 44228.75 | 0 | 16.8929 | 37.78
2021-02-01 18:30 | 44228.7708 | 0 | 17.3817 | 37.78
2021-02-01 19:00 | 44228.7917 | 0 | 17.2185 | 37.78
2021-02-01 19:30 | 44228.8125 | 0 | 17.1172 | 37.78
2021-02-01 20:00 | 44228.8333 | 0 | 16.7461 | 37.78
2021-02-01 20:30 | 44228.8542 | 0 | 15.985 | 37.78
2021-02-01 21:00 | 44228.875 | 0 | 15.2121 | 37.78
2021-02-01 21:30 | 44228.8958 | 0 | 14.7813 | 37.78
2021-02-01 22:00 | 44228.9167 | 0 | 14.1257 | 37.78
2021-02-01 22:30 | 44228.9375 | 0 | 13.0918 | 37.78
2021-02-01 23:00 | 44228.9583 | 0 | 12.405 | 37.78
2021-02-01 23:30 | 44228.9792 | 0 | 11.7326 | 37.78
2021-02-02 | 44229 | 0 | 11.0189 | 37.78
2021-02-02 00:30 | 44229.0208 | 0 | 10.4934 | 37.78
2021-02-02 01:00 | 44229.0417 | 0 | 10.138 | 37.78
2021-02-02 01:30 | 44229.0625 | 0 | 9.9754 | 37.78
2021-02-02 02:00 | 44229.0833 | 0 | 9.857 | 37.78
2021-02-02 02:30 | 44229.1042 | 0 | 9.8106 | 37.78
2021-02-02 03:00 | 44229.125 | 0 | 9.7743 | 37.78
2021-02-02 03:30 | 44229.1458 | 0 | 9.8799 | 37.78
2021-02-02 04:00 | 44229.1667 | 0 | 10.1183 | 37.78
2021-02-02 04:30 | 44229.1875 | 0 | 10.3435 | 37.78
2021-02-02 05:00 | 44229.2083 | 0 | 11.0058 | 37.78
2021-02-02 05:30 | 44229.2292 | 0 | 11.5836 | 37.78
2021-02-02 06:00 | 44229.25 | 0 | 12.1112 | 37.78
2021-02-02 06:30 | 44229.2708 | 0 | 13.286 | 37.78
2021-02-02 07:00 | 44229.2917 | 0 | 13.8461 | 37.78
2021-02-02 07:30 | 44229.3125 | 0 | 13.9946 | 37.78
2021-02-02 08:00 | 44229.3333 | 0 | 14.7311 | 37.78
2021-02-02 08:30 | 44229.3542 | 0 | 15.322 | 37.78
2021-02-02 09:00 | 44229.375 | 0 | 15.551 | 37.78
2021-02-02 09:30 | 44229.3958 | 0 | 15.506 | 37.78
2021-02-02 10:00 | 44229.4167 | 0 | 15.2963 | 37.78
2021-02-02 10:30 | 44229.4375 | 0 | 14.8772 | 37.78
2021-02-02 11:00 | 44229.4583 | 0 | 14.4468 | 37.78
2021-02-02 11:30 | 44229.4792 | 0 | 14.9177 | 37.78
2021-02-02 12:00 | 44229.5 | 0 | 14.6303 | 37.78
2021-02-02 12:30 | 44229.5208 | 0 | 13.9901 | 37.78
2021-02-02 13:00 | 44229.5417 | 0 | 14.5517 | 37.78
2021-02-02 13:30 | 44229.5625 | 0 | 14.9243 | 37.78
2021-02-02 14:00 | 44229.5833 | 0 | 14.7226 | 37.78
2021-02-02 14:30 | 44229.6042 | 0 | 14.3713 | 37.78
2021-02-02 15:00 | 44229.625 | 0 | 13.903 | 37.78
2021-02-02 15:30 | 44229.6458 | 0 | 14.0016 | 37.78
2021-02-02 16:00 | 44229.6667 | 0 | 14.332 | 37.78
2021-02-02 16:30 | 44229.6875 | 0 | 14.2275 | 37.78
2021-02-02 17:00 | 44229.7083 | 0 | 14.4856 | 37.78
2021-02-02 17:30 | 44229.7292 | 0 | 14.6518 | 37.78
2021-02-02 18:00 | 44229.75 | 0 | 14.6984 | 37.78
2021-02-02 18:30 | 44229.7708 | 0 | 15.3056 | 37.78
2021-02-02 19:00 | 44229.7917 | 0 | 15.401 | 37.78
2021-02-02 19:30 | 44229.8125 | 0 | 15.3425 | 37.78
2021-02-02 20:00 | 44229.8333 | 0 | 14.9065 | 37.78
2021-02-02 20:30 | 44229.8542 | 0 | 14.3713 | 37.78
2021-02-02 21:00 | 44229.875 | 0 | 13.8617 | 37.78
2021-02-02 21:30 | 44229.8958 | 0 | 13.4454 | 37.78
2021-02-02 22:00 | 44229.9167 | 0 | 12.7447 | 37.78
2021-02-02 22:30 | 44229.9375 | 0 | 12.0854 | 37.78
2021-02-02 23:00 | 44229.9583 | 0 | 11.2899 | 37.78
2021-02-02 23:30 | 44229.9792 | 0 | 10.7969 | 37.78
2021-02-03 | 44230 | 0 | 10.0985 | 37.78
2021-02-03 00:30 | 44230.0208 | 0 | 9.7111 | 37.78
2021-02-03 01:00 | 44230.0417 | 0 | 9.3124 | 37.78
2021-02-03 01:30 | 44230.0625 | 0 | 9.261 | 37.78
2021-02-03 02:00 | 44230.0833 | 0 | 9.1862 | 37.78
2021-02-03 02:30 | 44230.1042 | 0 | 9.1117 | 37.78
2021-02-03 03:00 | 44230.125 | 0 | 8.9777 | 37.78
2021-02-03 03:30 | 44230.1458 | 0 | 9.0899 | 37.78
2021-02-03 04:00 | 44230.1667 | 0 | 9.2566 | 37.78
2021-02-03 04:30 | 44230.1875 | 0 | 9.7185 | 37.78
2021-02-03 05:00 | 44230.2083 | 0 | 10.1891 | 37.78
2021-02-03 05:30 | 44230.2292 | 0 | 10.4756 | 37.78
2021-02-03 06:00 | 44230.25 | 0 | 11.1019 | 37.78
2021-02-03 06:30 | 44230.2708 | 0 | 11.7737 | 37.78
2021-02-03 07:00 | 44230.2917 | 0 | 12.0913 | 37.78
2021-02-03 07:30 | 44230.3125 | 0 | 12.4805 | 37.78
2021-02-03 08:00 | 44230.3333 | 0 | 13.0254 | 37.78
2021-02-03 08:30 | 44230.3542 | 0 | 12.7868 | 37.78
2021-02-03 09:00 | 44230.375 | 0 | 12.8946 | 37.78
2021-02-03 09:30 | 44230.3958 | 0 | 12.8649 | 37.78
2021-02-03 10:00 | 44230.4167 | 0 | 13.3271 | 37.78
2021-02-03 10:30 | 44230.4375 | 0 | 13.921 | 37.78
2021-02-03 11:00 | 44230.4583 | 0 | 14.2753 | 37.78
2021-02-03 11:30 | 44230.4792 | 0 | 13.778 | 37.78
2021-02-03 12:00 | 44230.5 | 0 | 14.881 | 37.78
2021-02-03 12:30 | 44230.5208 | 0 | 13.0684 | 37.78
2021-02-03 13:00 | 44230.5417 | 0 | 13.7843 | 37.78
2021-02-03 13:30 | 44230.5625 | 0 | 13.3833 | 37.78
2021-02-03 14:00 | 44230.5833 | 0 | 12.5579 | 37.78
2021-02-03 14:30 | 44230.6042 | 0 | 13.1869 | 37.78
2021-02-03 15:00 | 44230.625 | 0 | 13.5088 | 37.78
2021-02-03 15:30 | 44230.6458 | 0 | 14.3846 | 37.78
2021-02-03 16:00 | 44230.6667 | 0 | 14.7369 | 37.78
2021-02-03 16:30 | 44230.6875 | 0 | 15.1552 | 37.78
2021-02-03 17:00 | 44230.7083 | 0 | 15.5903 | 37.78
2021-02-03 17:30 | 44230.7292 | 0 | 15.8882 | 37.78
2021-02-03 18:00 | 44230.75 | 0 | 15.8602 | 37.78
2021-02-03 18:30 | 44230.7708 | 0 | 16.2845 | 37.78
2021-02-03 19:00 | 44230.7917 | 0 | 16.4763 | 37.78
2021-02-03 19:30 | 44230.8125 | 0 | 16.1088 | 37.78
2021-02-03 20:00 | 44230.8333 | 0 | 15.6759 | 37.78
2021-02-03 20:30 | 44230.8542 | 0 | 14.951 | 37.78
2021-02-03 21:00 | 44230.875 | 0 | 14.3459 | 37.78
2021-02-03 21:30 | 44230.8958 | 0 | 13.6873 | 37.78
2021-02-03 22:00 | 44230.9167 | 0 | 12.8679 | 37.78
2021-02-03 22:30 | 44230.9375 | 0 | 12.0241 | 37.78
2021-02-03 23:00 | 44230.9583 | 0 | 11.0227 | 37.78
2021-02-03 23:30 | 44230.9792 | 0 | 10.7337 | 37.78
2021-02-04 | 44231 | 0 | 10.21 | 37.78
2021-02-04 00:30 | 44231.0208 | 0 | 9.8226 | 37.78
2021-02-04 01:00 | 44231.0417 | 0 | 9.5563 | 37.78
2021-02-04 01:30 | 44231.0625 | 0 | 9.2755 | 37.78
2021-02-04 02:00 | 44231.0833 | 0 | 9.3342 | 37.78
2021-02-04 02:30 | 44231.1042 | 0 | 9.0076 | 37.78
2021-02-04 03:00 | 44231.125 | 0 | 8.9533 | 37.78
2021-02-04 03:30 | 44231.1458 | 0 | 8.9367 | 37.78
2021-02-04 04:00 | 44231.1667 | 0 | 9.2168 | 37.78
2021-02-04 04:30 | 44231.1875 | 0 | 9.5019 | 37.78
2021-02-04 05:00 | 44231.2083 | 0 | 9.9183 | 37.78
2021-02-04 05:30 | 44231.2292 | 0 | 10.3505 | 37.78
2021-02-04 06:00 | 44231.25 | 0 | 10.9965 | 37.78
2021-02-04 06:30 | 44231.2708 | 0 | 11.4219 | 37.78
2021-02-04 07:00 | 44231.2917 | 0 | 11.9625 | 37.78
2021-02-04 07:30 | 44231.3125 | 0 | 12.3254 | 37.78
2021-02-04 08:00 | 44231.3333 | 0 | 12.2165 | 37.78
2021-02-04 08:30 | 44231.3542 | 0 | 12.414 | 37.78
2021-02-04 09:00 | 44231.375 | 0 | 13.0658 | 37.78
2021-02-04 09:30 | 44231.3958 | 0 | 13.24 | 37.78
2021-02-04 10:00 | 44231.4167 | 0 | 13.5362 | 37.78
2021-02-04 10:30 | 44231.4375 | 0 | 13.926 | 37.78
2021-02-04 11:00 | 44231.4583 | 0 | 14.5321 | 37.78
2021-02-04 11:30 | 44231.4792 | 0 | 15.1063 | 37.78
2021-02-04 12:00 | 44231.5 | 0 | 14.7526 | 37.78
2021-02-04 12:30 | 44231.5208 | 0 | 14.705 | 37.78
2021-02-04 13:00 | 44231.5417 | 0 | 15.2678 | 37.78
2021-02-04 13:30 | 44231.5625 | 0 | 15.4453 | 37.78
2021-02-04 14:00 | 44231.5833 | 0 | 15.4001 | 37.78
2021-02-04 14:30 | 44231.6042 | 0 | 15.7504 | 37.78
2021-02-04 15:00 | 44231.625 | 0 | 15.1901 | 37.78
2021-02-04 15:30 | 44231.6458 | 0 | 16.0025 | 37.78
2021-02-04 16:00 | 44231.6667 | 0 | 17.0873 | 37.78
2021-02-04 16:30 | 44231.6875 | 0 | 17.1781 | 37.78
2021-02-04 17:00 | 44231.7083 | 0 | 17.5494 | 37.78
2021-02-04 17:30 | 44231.7292 | 0 | 17.7316 | 37.78
2021-02-04 18:00 | 44231.75 | 0 | 17.5019 | 37.78
2021-02-04 18:30 | 44231.7708 | 0 | 17.755 | 37.78
2021-02-04 19:00 | 44231.7917 | 0 | 17.625 | 37.78
2021-02-04 19:30 | 44231.8125 | 0 | 17.4344 | 37.78
2021-02-04 20:00 | 44231.8333 | 0 | 17.0959 | 37.78
2021-02-04 20:30 | 44231.8542 | 0 | 16.2057 | 37.78
2021-02-04 21:00 | 44231.875 | 0 | 15.4766 | 37.78
2021-02-04 21:30 | 44231.8958 | 0 | 14.8259 | 37.78
2021-02-04 22:00 | 44231.9167 | 0 | 13.8466 | 37.78
2021-02-04 22:30 | 44231.9375 | 0 | 12.7838 | 37.78
2021-02-04 23:00 | 44231.9583 | 0 | 12.0611 | 37.78
2021-02-04 23:30 | 44231.9792 | 0 | 11.4025 | 37.78
2021-02-05 | 44232 | 0 | 10.6074 | 37.78
2021-02-05 00:30 | 44232.0208 | 0 | 10.1044 | 37.78
2021-02-05 01:00 | 44232.0417 | 0 | 9.8338 | 37.78
2021-02-05 01:30 | 44232.0625 | 0 | 9.8542 | 37.78
2021-02-05 02:00 | 44232.0833 | 0 | 9.6403 | 37.78
2021-02-05 02:30 | 44232.1042 | 0 | 9.5802 | 37.78
2021-02-05 03:00 | 44232.125 | 0 | 9.5802 | 37.78
2021-02-05 03:30 | 44232.1458 | 0 | 9.6849 | 37.78
2021-02-05 04:00 | 44232.1667 | 0 | 9.7092 | 37.78
2021-02-05 04:30 | 44232.1875 | 0 | 9.9133 | 37.78
2021-02-05 05:00 | 44232.2083 | 0 | 10.5218 | 37.78
2021-02-05 05:30 | 44232.2292 | 0 | 10.9399 | 37.78
2021-02-05 06:00 | 44232.25 | 0 | 11.5534 | 37.78
2021-02-05 06:30 | 44232.2708 | 0 | 12.3411 | 37.78
2021-02-05 07:00 | 44232.2917 | 0 | 12.5733 | 37.78
2021-02-05 07:30 | 44232.3125 | 0 | 12.9872 | 37.78
2021-02-05 08:00 | 44232.3333 | 0 | 13.2263 | 37.78
2021-02-05 08:30 | 44232.3542 | 0 | 13.5827 | 37.78
2021-02-05 09:00 | 44232.375 | 0 | 14.5135 | 37.78
2021-02-05 09:30 | 44232.3958 | 0 | 14.8347 | 37.78
2021-02-05 10:00 | 44232.4167 | 0 | 14.3462 | 37.78
2021-02-05 10:30 | 44232.4375 | 0 | 14.394 | 37.78
2021-02-05 11:00 | 44232.4583 | 0 | 14.7989 | 37.78
2021-02-05 11:30 | 44232.4792 | 0 | 15.5718 | 37.78
2021-02-05 12:00 | 44232.5 | 0 | 15.0189 | 37.78
2021-02-05 12:30 | 44232.5208 | 0 | 14.853 | 37.78
2021-02-05 13:00 | 44232.5417 | 0 | 15.1796 | 37.78
2021-02-05 13:30 | 44232.5625 | 0 | 15.8317 | 37.78
2021-02-05 14:00 | 44232.5833 | 0 | 16.5458 | 37.78
2021-02-05 14:30 | 44232.6042 | 0 | 15.3913 | 37.78
2021-02-05 15:00 | 44232.625 | 0 | 16.5457 | 37.78
2021-02-05 15:30 | 44232.6458 | 0 | 16.8491 | 37.78
2021-02-05 16:00 | 44232.6667 | 0 | 17.8113 | 37.78
2021-02-05 16:30 | 44232.6875 | 0 | 16.9005 | 37.78
2021-02-05 17:00 | 44232.7083 | 0 | 16.7734 | 37.78
2021-02-05 17:30 | 44232.7292 | 0 | 16.7952 | 37.78
2021-02-05 18:00 | 44232.75 | 0 | 16.6193 | 37.78
2021-02-05 18:30 | 44232.7708 | 0 | 16.4526 | 37.78
2021-02-05 19:00 | 44232.7917 | 0 | 16.4652 | 37.78
2021-02-05 19:30 | 44232.8125 | 0 | 16.1158 | 37.78
2021-02-05 20:00 | 44232.8333 | 0 | 16.1325 | 37.78
2021-02-05 20:30 | 44232.8542 | 0 | 15.7524 | 37.78
2021-02-05 21:00 | 44232.875 | 0 | 14.9226 | 37.78
2021-02-05 21:30 | 44232.8958 | 0 | 14.3133 | 37.78
2021-02-05 22:00 | 44232.9167 | 0 | 13.7483 | 37.78
2021-02-05 22:30 | 44232.9375 | 0 | 12.6903 | 37.78
2021-02-05 23:00 | 44232.9583 | 0 | 11.9747 | 37.78
2021-02-05 23:30 | 44232.9792 | 0 | 11.3755 | 37.78
2021-02-06 | 44233 | 0 | 10.6417 | 37.78
2021-02-06 00:30 | 44233.0208 | 0 | 10.3083 | 37.78
2021-02-06 01:00 | 44233.0417 | 0 | 10.071 | 37.78
2021-02-06 01:30 | 44233.0625 | 0 | 9.8988 | 37.78
2021-02-06 02:00 | 44233.0833 | 0 | 9.6924 | 37.78
2021-02-06 02:30 | 44233.1042 | 0 | 9.601 | 37.78
2021-02-06 03:00 | 44233.125 | 0 | 9.401 | 37.78
2021-02-06 03:30 | 44233.1458 | 0 | 9.3813 | 37.78
2021-02-06 04:00 | 44233.1667 | 0 | 9.4467 | 37.78
2021-02-06 04:30 | 44233.1875 | 0 | 9.469 | 37.78
2021-02-06 05:00 | 44233.2083 | 0 | 9.5807 | 37.78
2021-02-06 05:30 | 44233.2292 | 0 | 9.5573 | 37.78
2021-02-06 06:00 | 44233.25 | 0 | 9.4696 | 37.78
2021-02-06 06:30 | 44233.2708 | 0 | 9.5823 | 37.78
2021-02-06 07:00 | 44233.2917 | 0 | 9.6243 | 37.78
2021-02-06 07:30 | 44233.3125 | 0 | 9.7504 | 37.78
2021-02-06 08:00 | 44233.3333 | 0 | 10.3627 | 37.78
2021-02-06 08:30 | 44233.3542 | 0 | 10.6979 | 37.78
2021-02-06 09:00 | 44233.375 | 0 | 11.2693 | 37.78
2021-02-06 09:30 | 44233.3958 | 0 | 10.9352 | 37.78
2021-02-06 10:00 | 44233.4167 | 0 | 11.4367 | 37.78
2021-02-06 10:30 | 44233.4375 | 0 | 11.5864 | 37.78
2021-02-06 11:00 | 44233.4583 | 0 | 11.8079 | 37.78
2021-02-06 11:30 | 44233.4792 | 0 | 12.9758 | 37.78
2021-02-06 12:00 | 44233.5 | 0 | 13.5133 | 37.78
2021-02-06 12:30 | 44233.5208 | 0 | 13.3464 | 37.78
2021-02-06 13:00 | 44233.5417 | 0 | 13.0535 | 37.78
2021-02-06 13:30 | 44233.5625 | 0 | 13.3309 | 37.78
2021-02-06 14:00 | 44233.5833 | 0 | 13.8066 | 37.78
2021-02-06 14:30 | 44233.6042 | 0 | 14.1305 | 37.78
2021-02-06 15:00 | 44233.625 | 0 | 14.8337 | 37.78
2021-02-06 15:30 | 44233.6458 | 0 | 15.3185 | 37.78
2021-02-06 16:00 | 44233.6667 | 0 | 15.2981 | 37.78
2021-02-06 16:30 | 44233.6875 | 0 | 16.1328 | 37.78
2021-02-06 17:00 | 44233.7083 | 0 | 16.5383 | 37.78
2021-02-06 17:30 | 44233.7292 | 0 | 16.9207 | 37.78
2021-02-06 18:00 | 44233.75 | 0 | 16.5623 | 37.78
2021-02-06 18:30 | 44233.7708 | 0 | 16.7723 | 37.78
2021-02-06 19:00 | 44233.7917 | 0 | 16.422 | 37.78
2021-02-06 19:30 | 44233.8125 | 0 | 16.3236 | 37.78
2021-02-06 20:00 | 44233.8333 | 0 | 15.9554 | 37.78
2021-02-06 20:30 | 44233.8542 | 0 | 15.2958 | 37.78
2021-02-06 21:00 | 44233.875 | 0 | 14.8285 | 37.78
2021-02-06 21:30 | 44233.8958 | 0 | 14.2707 | 37.78
2021-02-06 22:00 | 44233.9167 | 0 | 13.7834 | 37.78
2021-02-06 22:30 | 44233.9375 | 0 | 12.7069 | 37.78
2021-02-06 23:00 | 44233.9583 | 0 | 12.1474 | 37.78
2021-02-06 23:30 | 44233.9792 | 0 | 11.5782 | 37.78
2021-02-07 | 44234 | 0 | 10.9677 | 37.78
2021-02-07 00:30 | 44234.0208 | 0 | 10.4903 | 37.78
2021-02-07 01:00 | 44234.0417 | 0 | 10.2791 | 37.78
2021-02-07 01:30 | 44234.0625 | 0 | 10.0929 | 37.78
2021-02-07 02:00 | 44234.0833 | 0 | 9.9237 | 37.78
2021-02-07 02:30 | 44234.1042 | 0 | 9.6591 | 37.78
2021-02-07 03:00 | 44234.125 | 0 | 9.4228 | 37.78
2021-02-07 03:30 | 44234.1458 | 0 | 9.3127 | 37.78
2021-02-07 04:00 | 44234.1667 | 0 | 9.1172 | 37.78
2021-02-07 04:30 | 44234.1875 | 0 | 9.1112 | 37.78
2021-02-07 05:00 | 44234.2083 | 0 | 9.1941 | 37.78
2021-02-07 05:30 | 44234.2292 | 0 | 9.2388 | 37.78
2021-02-07 06:00 | 44234.25 | 0 | 9.2987 | 37.78
2021-02-07 06:30 | 44234.2708 | 0 | 9.3419 | 37.78
2021-02-07 07:00 | 44234.2917 | 0 | 9.7748 | 37.78
2021-02-07 07:30 | 44234.3125 | 0 | 9.5172 | 37.78
2021-02-07 08:00 | 44234.3333 | 0 | 10.4113 | 37.78
2021-02-07 08:30 | 44234.3542 | 0 | 10.6551 | 37.78
2021-02-07 09:00 | 44234.375 | 0 | 10.7539 | 37.78
2021-02-07 09:30 | 44234.3958 | 0 | 10.512 | 37.78
2021-02-07 10:00 | 44234.4167 | 0 | 10.9462 | 37.78
2021-02-07 10:30 | 44234.4375 | 0 | 11.2996 | 37.78
2021-02-07 11:00 | 44234.4583 | 0 | 11.7683 | 37.78
2021-02-07 11:30 | 44234.4792 | 0 | 12.7619 | 37.78
2021-02-07 12:00 | 44234.5 | 0 | 13.767 | 37.78
2021-02-07 12:30 | 44234.5208 | 0 | 14.4918 | 37.78
2021-02-07 13:00 | 44234.5417 | 0 | 16.0199 | 37.78
2021-02-07 13:30 | 44234.5625 | 0 | 16.1103 | 37.78
2021-02-07 14:00 | 44234.5833 | 0 | 18.1493 | 37.78
2021-02-07 14:30 | 44234.6042 | 0 | 17.1342 | 37.78
2021-02-07 15:00 | 44234.625 | 0 | 18.8129 | 37.78
2021-02-07 15:30 | 44234.6458 | 0 | 19.0486 | 37.78
2021-02-07 16:00 | 44234.6667 | 0 | 18.5573 | 37.78
2021-02-07 16:30 | 44234.6875 | 0 | 19.7871 | 37.78
2021-02-07 17:00 | 44234.7083 | 0 | 20.3018 | 37.78
2021-02-07 17:30 | 44234.7292 | 0 | 20.7486 | 37.78
2021-02-07 18:00 | 44234.75 | 0 | 20.6928 | 37.78
2021-02-07 18:30 | 44234.7708 | 0 | 20.8161 | 37.78
2021-02-07 19:00 | 44234.7917 | 0 | 20.9231 | 37.78
2021-02-07 19:30 | 44234.8125 | 0 | 20.6786 | 37.78
2021-02-07 20:00 | 44234.8333 | 0 | 20.0151 | 37.78
2021-02-07 20:30 | 44234.8542 | 0 | 18.71 | 37.78
2021-02-07 21:00 | 44234.875 | 0 | 17.7567 | 37.78
2021-02-07 21:30 | 44234.8958 | 0 | 16.2935 | 37.78
2021-02-07 22:00 | 44234.9167 | 0 | 15.0579 | 37.78
2021-02-07 22:30 | 44234.9375 | 0 | 14.3293 | 37.78
2021-02-07 23:00 | 44234.9583 | 0 | 13.8057 | 37.78
2021-02-07 23:30 | 44234.9792 | 0 | 13.3333 | 37.78
2021-02-08 | 44235 | 0 | 12.6733 | 37.78
2021-02-08 00:30 | 44235.0208 | 0 | 12.2294 | 37.78
2021-02-08 01:00 | 44235.0417 | 0 | 11.7053 | 37.78
2021-02-08 01:30 | 44235.0625 | 0 | 11.4842 | 37.78
2021-02-08 02:00 | 44235.0833 | 0 | 11.274 | 37.78
2021-02-08 02:30 | 44235.1042 | 0 | 10.9953 | 37.78
2021-02-08 03:00 | 44235.125 | 0 | 10.7046 | 37.78
2021-02-08 03:30 | 44235.1458 | 0 | 10.6242 | 37.78
2021-02-08 04:00 | 44235.1667 | 0 | 10.658 | 37.78
2021-02-08 04:30 | 44235.1875 | 0 | 10.9107 | 37.78
2021-02-08 05:00 | 44235.2083 | 0 | 11.4356 | 37.78
2021-02-08 05:30 | 44235.2292 | 0 | 12.0048 | 37.78
2021-02-08 06:00 | 44235.25 | 0 | 12.7237 | 37.78
2021-02-08 06:30 | 44235.2708 | 0 | 13.6018 | 37.78
2021-02-08 07:00 | 44235.2917 | 0 | 13.7641 | 37.78
2021-02-08 07:30 | 44235.3125 | 0 | 14.7465 | 37.78
2021-02-08 08:00 | 44235.3333 | 0 | 15.3415 | 37.78
2021-02-08 08:30 | 44235.3542 | 0 | 15.1293 | 37.78
2021-02-08 09:00 | 44235.375 | 0 | 14.2944 | 37.78
2021-02-08 09:30 | 44235.3958 | 0 | 14.8142 | 37.78
2021-02-08 10:00 | 44235.4167 | 0 | 14.9459 | 37.78
2021-02-08 10:30 | 44235.4375 | 0 | 15.3416 | 37.78
2021-02-08 11:00 | 44235.4583 | 0 | 17.3974 | 37.78
2021-02-08 11:30 | 44235.4792 | 0 | 17.9046 | 37.78
2021-02-08 12:00 | 44235.5 | 0 | 17.0102 | 37.78
2021-02-08 12:30 | 44235.5208 | 0 | 16.5812 | 37.78
2021-02-08 13:00 | 44235.5417 | 0 | 16.8111 | 37.78
2021-02-08 13:30 | 44235.5625 | 0 | 16.1444 | 37.78
2021-02-08 14:00 | 44235.5833 | 0 | 15.2653 | 37.78
2021-02-08 14:30 | 44235.6042 | 0 | 16.4684 | 37.78
2021-02-08 15:00 | 44235.625 | 0 | 15.6208 | 37.78
2021-02-08 15:30 | 44235.6458 | 0 | 16.3484 | 37.78
2021-02-08 16:00 | 44235.6667 | 0 | 16.0576 | 37.78
2021-02-08 16:30 | 44235.6875 | 0 | 15.943 | 37.78
2021-02-08 17:00 | 44235.7083 | 0 | 16.4142 | 37.78
2021-02-08 17:30 | 44235.7292 | 0 | 16.6542 | 37.78
2021-02-08 18:00 | 44235.75 | 0 | 16.7468 | 37.78
2021-02-08 18:30 | 44235.7708 | 0 | 17.1555 | 37.78
2021-02-08 19:00 | 44235.7917 | 0 | 17.022 | 37.78
2021-02-08 19:30 | 44235.8125 | 0 | 16.7245 | 37.78
2021-02-08 20:00 | 44235.8333 | 0 | 16.4788 | 37.78
2021-02-08 20:30 | 44235.8542 | 0 | 15.8911 | 37.78
2021-02-08 21:00 | 44235.875 | 0 | 14.9638 | 37.78
2021-02-08 21:30 | 44235.8958 | 0 | 14.3588 | 37.78
2021-02-08 22:00 | 44235.9167 | 0 | 13.804 | 37.78
2021-02-08 22:30 | 44235.9375 | 0 | 12.7125 | 37.78
2021-02-08 23:00 | 44235.9583 | 0 | 12.2294 | 37.78
2021-02-08 23:30 | 44235.9792 | 0 | 11.5953 | 37.78
2021-02-09 | 44236 | 0 | 11.0713 | 37.78
2021-02-09 00:30 | 44236.0208 | 0 | 10.54 | 37.78
2021-02-09 01:00 | 44236.0417 | 0 | 10.0037 | 37.78
2021-02-09 01:30 | 44236.0625 | 0 | 10.0023 | 37.78
2021-02-09 02:00 | 44236.0833 | 0 | 9.8465 | 37.78
2021-02-09 02:30 | 44236.1042 | 0 | 9.7357 | 37.78
2021-02-09 03:00 | 44236.125 | 0 | 9.6426 | 37.78
2021-02-09 03:30 | 44236.1458 | 0 | 9.6429 | 37.78
2021-02-09 04:00 | 44236.1667 | 0 | 9.7135 | 37.78
2021-02-09 04:30 | 44236.1875 | 0 | 9.9531 | 37.78
2021-02-09 05:00 | 44236.2083 | 0 | 10.5607 | 37.78
2021-02-09 05:30 | 44236.2292 | 0 | 10.9287 | 37.78
2021-02-09 06:00 | 44236.25 | 0 | 11.7117 | 37.78
2021-02-09 06:30 | 44236.2708 | 0 | 12.2489 | 37.78
2021-02-09 07:00 | 44236.2917 | 0 | 13.0476 | 37.78
2021-02-09 07:30 | 44236.3125 | 0 | 13.2196 | 37.78
2021-02-09 08:00 | 44236.3333 | 0 | 13.0394 | 37.78
2021-02-09 08:30 | 44236.3542 | 0 | 12.9359 | 37.78
2021-02-09 09:00 | 44236.375 | 0 | 13.0735 | 37.78
2021-02-09 09:30 | 44236.3958 | 0 | 13.7176 | 37.78
2021-02-09 10:00 | 44236.4167 | 0 | 14.0404 | 37.78
2021-02-09 10:30 | 44236.4375 | 0 | 14.3632 | 37.78
2021-02-09 11:00 | 44236.4583 | 0 | 14.1216 | 37.78
2021-02-09 11:30 | 44236.4792 | 0 | 14.4339 | 37.78
2021-02-09 12:00 | 44236.5 | 0 | 14.2591 | 37.78
2021-02-09 12:30 | 44236.5208 | 0 | 14.8249 | 37.78
2021-02-09 13:00 | 44236.5417 | 0 | 14.3877 | 37.78
2021-02-09 13:30 | 44236.5625 | 0 | 15.2492 | 37.78
2021-02-09 14:00 | 44236.5833 | 0 | 14.9537 | 37.78
2021-02-09 14:30 | 44236.6042 | 0 | 14.0665 | 37.78
2021-02-09 15:00 | 44236.625 | 0 | 14.6237 | 37.78
2021-02-09 15:30 | 44236.6458 | 0 | 15.2352 | 37.78
2021-02-09 16:00 | 44236.6667 | 0 | 15.4712 | 37.78
2021-02-09 16:30 | 44236.6875 | 0 | 15.852 | 37.78
2021-02-09 17:00 | 44236.7083 | 0 | 16.2514 | 37.78
2021-02-09 17:30 | 44236.7292 | 0 | 16.0391 | 37.78
2021-02-09 18:00 | 44236.75 | 0 | 15.639 | 37.78
2021-02-09 18:30 | 44236.7708 | 0 | 15.7709 | 37.78
2021-02-09 19:00 | 44236.7917 | 0 | 15.8312 | 37.78
2021-02-09 19:30 | 44236.8125 | 0 | 15.8522 | 37.78
2021-02-09 20:00 | 44236.8333 | 0 | 15.4226 | 37.78
2021-02-09 20:30 | 44236.8542 | 0 | 14.7575 | 37.78
2021-02-09 21:00 | 44236.875 | 0 | 13.9814 | 37.78
2021-02-09 21:30 | 44236.8958 | 0 | 13.3899 | 37.78
2021-02-09 22:00 | 44236.9167 | 0 | 12.6182 | 37.78
2021-02-09 22:30 | 44236.9375 | 0 | 11.6117 | 37.78
2021-02-09 23:00 | 44236.9583 | 0 | 10.8887 | 37.78
2021-02-09 23:30 | 44236.9792 | 0 | 10.4719 | 37.78
2021-02-10 | 44237 | 0 | 9.8695 | 37.78
2021-02-10 00:30 | 44237.0208 | 0 | 9.6062 | 37.78
2021-02-10 01:00 | 44237.0417 | 0 | 9.4413 | 37.78
2021-02-10 01:30 | 44237.0625 | 0 | 9.2124 | 37.78
2021-02-10 02:00 | 44237.0833 | 0 | 9.1131 | 37.78
2021-02-10 02:30 | 44237.1042 | 0 | 9.0015 | 37.78
2021-02-10 03:00 | 44237.125 | 0 | 8.7833 | 37.78
2021-02-10 03:30 | 44237.1458 | 0 | 8.8101 | 37.78
2021-02-10 04:00 | 44237.1667 | 0 | 8.9567 | 37.78
2021-02-10 04:30 | 44237.1875 | 0 | 9.258 | 37.78
2021-02-10 05:00 | 44237.2083 | 0 | 9.7449 | 37.78
2021-02-10 05:30 | 44237.2292 | 0 | 10.3341 | 37.78
2021-02-10 06:00 | 44237.25 | 0 | 10.8066 | 37.78
2021-02-10 06:30 | 44237.2708 | 0 | 11.3435 | 37.78
2021-02-10 07:00 | 44237.2917 | 0 | 11.7497 | 37.78
2021-02-10 07:30 | 44237.3125 | 0 | 11.8682 | 37.78
2021-02-10 08:00 | 44237.3333 | 0 | 11.5982 | 37.78
2021-02-10 08:30 | 44237.3542 | 0 | 12.5579 | 37.78
2021-02-10 09:00 | 44237.375 | 0 | 12.4185 | 37.78
2021-02-10 09:30 | 44237.3958 | 0 | 13.5209 | 37.78
2021-02-10 10:00 | 44237.4167 | 0 | 14.0741 | 37.78
2021-02-10 10:30 | 44237.4375 | 0 | 13.8517 | 37.78
2021-02-10 11:00 | 44237.4583 | 0 | 14.3722 | 37.78
2021-02-10 11:30 | 44237.4792 | 0 | 14.2942 | 37.78
2021-02-10 12:00 | 44237.5 | 0 | 13.4601 | 37.78
2021-02-10 12:30 | 44237.5208 | 0 | 11.8962 | 37.78
2021-02-10 13:00 | 44237.5417 | 0 | 12.7126 | 37.78
2021-02-10 13:30 | 44237.5625 | 0 | 13.0268 | 37.78
2021-02-10 14:00 | 44237.5833 | 0 | 13.9134 | 37.78
2021-02-10 14:30 | 44237.6042 | 0 | 13.1559 | 37.78
2021-02-10 15:00 | 44237.625 | 0 | 14.236 | 37.78
2021-02-10 15:30 | 44237.6458 | 0 | 14.3426 | 37.78
2021-02-10 16:00 | 44237.6667 | 0 | 15.1964 | 37.78
2021-02-10 16:30 | 44237.6875 | 0 | 15.761 | 37.78
2021-02-10 17:00 | 44237.7083 | 0 | 15.6236 | 37.78
2021-02-10 17:30 | 44237.7292 | 0 | 15.2621 | 37.78
2021-02-10 18:00 | 44237.75 | 0 | 15.4704 | 37.78
2021-02-10 18:30 | 44237.7708 | 0 | 15.7695 | 37.78
2021-02-10 19:00 | 44237.7917 | 0 | 15.9051 | 37.78
2021-02-10 19:30 | 44237.8125 | 0 | 15.4265 | 37.78
2021-02-10 20:00 | 44237.8333 | 0 | 15.1875 | 37.78
2021-02-10 20:30 | 44237.8542 | 0 | 14.7023 | 37.78
2021-02-10 21:00 | 44237.875 | 0 | 13.9484 | 37.78
2021-02-10 21:30 | 44237.8958 | 0 | 13.5731 | 37.78
2021-02-10 22:00 | 44237.9167 | 0 | 12.98 | 37.78
2021-02-10 22:30 | 44237.9375 | 0 | 11.9726 | 37.78
2021-02-10 23:00 | 44237.9583 | 0 | 11.3353 | 37.78
2021-02-10 23:30 | 44237.9792 | 0 | 10.5933 | 37.78
2021-02-11 | 44238 | 0 | 9.8946 | 37.78
2021-02-11 00:30 | 44238.0208 | 0 | 9.5097 | 37.78
2021-02-11 01:00 | 44238.0417 | 0 | 9.2473 | 37.78
2021-02-11 01:30 | 44238.0625 | 0 | 9.1314 | 37.78
2021-02-11 02:00 | 44238.0833 | 0 | 9.2195 | 37.78
2021-02-11 02:30 | 44238.1042 | 0 | 9.1874 | 37.78
2021-02-11 03:00 | 44238.125 | 0 | 9.0671 | 37.78
2021-02-11 03:30 | 44238.1458 | 0 | 9.0947 | 37.78
2021-02-11 04:00 | 44238.1667 | 0 | 9.3669 | 37.78
2021-02-11 04:30 | 44238.1875 | 0 | 9.6821 | 37.78
2021-02-11 05:00 | 44238.2083 | 0 | 10.0683 | 37.78
2021-02-11 05:30 | 44238.2292 | 0 | 10.6119 | 37.78
2021-02-11 06:00 | 44238.25 | 0 | 11.1011 | 37.78
2021-02-11 06:30 | 44238.2708 | 0 | 11.8907 | 37.78
2021-02-11 07:00 | 44238.2917 | 0 | 12.2955 | 37.78
2021-02-11 07:30 | 44238.3125 | 0 | 12.1726 | 37.78
2021-02-11 08:00 | 44238.3333 | 0 | 12.0117 | 37.78
2021-02-11 08:30 | 44238.3542 | 0 | 12.3174 | 37.78
2021-02-11 09:00 | 44238.375 | 0 | 12.8291 | 37.78
2021-02-11 09:30 | 44238.3958 | 0 | 12.8522 | 37.78
2021-02-11 10:00 | 44238.4167 | 0 | 13.3813 | 37.78
2021-02-11 10:30 | 44238.4375 | 0 | 13.7944 | 37.78
2021-02-11 11:00 | 44238.4583 | 0 | 14.6529 | 37.78
2021-02-11 11:30 | 44238.4792 | 0 | 14.762 | 37.78
2021-02-11 12:00 | 44238.5 | 0 | 14.1147 | 37.78
2021-02-11 12:30 | 44238.5208 | 0 | 14.5763 | 37.78
2021-02-11 13:00 | 44238.5417 | 0 | 13.3088 | 37.78
2021-02-11 13:30 | 44238.5625 | 0 | 13.6322 | 37.78
2021-02-11 14:00 | 44238.5833 | 0 | 14.5368 | 37.78
2021-02-11 14:30 | 44238.6042 | 0 | 14.9547 | 37.78
2021-02-11 15:00 | 44238.625 | 0 | 14.5184 | 37.78
2021-02-11 15:30 | 44238.6458 | 0 | 14.5288 | 37.78
2021-02-11 16:00 | 44238.6667 | 0 | 14.4854 | 37.78
2021-02-11 16:30 | 44238.6875 | 0 | 14.7923 | 37.78
2021-02-11 17:00 | 44238.7083 | 0 | 14.9865 | 37.78
2021-02-11 17:30 | 44238.7292 | 0 | 14.9035 | 37.78
2021-02-11 18:00 | 44238.75 | 0 | 15.057 | 37.78
2021-02-11 18:30 | 44238.7708 | 0 | 15.3958 | 37.78
2021-02-11 19:00 | 44238.7917 | 0 | 15.5386 | 37.78
2021-02-11 19:30 | 44238.8125 | 0 | 15.4231 | 37.78
2021-02-11 20:00 | 44238.8333 | 0 | 15.1476 | 37.78
2021-02-11 20:30 | 44238.8542 | 0 | 14.6645 | 37.78
2021-02-11 21:00 | 44238.875 | 0 | 14.1678 | 37.78
2021-02-11 21:30 | 44238.8958 | 0 | 13.6189 | 37.78
2021-02-11 22:00 | 44238.9167 | 0 | 12.8034 | 37.78
2021-02-11 22:30 | 44238.9375 | 0 | 11.8269 | 37.78
2021-02-11 23:00 | 44238.9583 | 0 | 11.3161 | 37.78
2021-02-11 23:30 | 44238.9792 | 0 | 10.7627 | 37.78
2021-02-12 | 44239 | 0 | 10.2526 | 37.78
2021-02-12 00:30 | 44239.0208 | 0 | 9.8247 | 37.78
2021-02-12 01:00 | 44239.0417 | 0 | 9.649 | 37.78
2021-02-12 01:30 | 44239.0625 | 0 | 9.645 | 37.78
2021-02-12 02:00 | 44239.0833 | 0 | 9.5544 | 37.78
2021-02-12 02:30 | 44239.1042 | 0 | 9.2201 | 37.78
2021-02-12 03:00 | 44239.125 | 0 | 9.1826 | 37.78
2021-02-12 03:30 | 44239.1458 | 0 | 9.2581 | 37.78
2021-02-12 04:00 | 44239.1667 | 0 | 9.3851 | 37.78
2021-02-12 04:30 | 44239.1875 | 0 | 9.7425 | 37.78
2021-02-12 05:00 | 44239.2083 | 0 | 10.1724 | 37.78
2021-02-12 05:30 | 44239.2292 | 0 | 10.6826 | 37.78
2021-02-12 06:00 | 44239.25 | 0 | 11.3613 | 37.78
2021-02-12 06:30 | 44239.2708 | 0 | 12.3934 | 37.78
2021-02-12 07:00 | 44239.2917 | 0 | 13.2794 | 37.78
2021-02-12 07:30 | 44239.3125 | 0 | 13.6689 | 37.78
2021-02-12 08:00 | 44239.3333 | 0 | 13.2541 | 37.78
2021-02-12 08:30 | 44239.3542 | 0 | 13.2651 | 37.78
2021-02-12 09:00 | 44239.375 | 0 | 14.2143 | 37.78
2021-02-12 09:30 | 44239.3958 | 0 | 14.8019 | 37.78
2021-02-12 10:00 | 44239.4167 | 0 | 13.3716 | 37.78
2021-02-12 10:30 | 44239.4375 | 0 | 13.217 | 37.78
2021-02-12 11:00 | 44239.4583 | 0 | 13.444 | 37.78
2021-02-12 11:30 | 44239.4792 | 0 | 13.5046 | 37.78
2021-02-12 12:00 | 44239.5 | 0 | 14.4423 | 37.78
2021-02-12 12:30 | 44239.5208 | 0 | 14.0126 | 37.78
2021-02-12 13:00 | 44239.5417 | 0 | 14.6239 | 37.78
2021-02-12 13:30 | 44239.5625 | 0 | 14.0041 | 37.78
2021-02-12 14:00 | 44239.5833 | 0 | 14.4275 | 37.78
2021-02-12 14:30 | 44239.6042 | 0 | 14.538 | 37.78
2021-02-12 15:00 | 44239.625 | 0 | 15.1999 | 37.78
2021-02-12 15:30 | 44239.6458 | 0 | 15.6615 | 37.78
2021-02-12 16:00 | 44239.6667 | 0 | 16.2033 | 37.78
2021-02-12 16:30 | 44239.6875 | 0 | 16.7654 | 37.78
2021-02-12 17:00 | 44239.7083 | 0 | 16.6899 | 37.78
2021-02-12 17:30 | 44239.7292 | 0 | 16.5449 | 37.78
2021-02-12 18:00 | 44239.75 | 0 | 16.2332 | 37.78
2021-02-12 18:30 | 44239.7708 | 0 | 16.3962 | 37.78
2021-02-12 19:00 | 44239.7917 | 0 | 16.6018 | 37.78
2021-02-12 19:30 | 44239.8125 | 0 | 16.1849 | 37.78
2021-02-12 20:00 | 44239.8333 | 0 | 15.7548 | 37.78
2021-02-12 20:30 | 44239.8542 | 0 | 15.1964 | 37.78
2021-02-12 21:00 | 44239.875 | 0 | 14.7739 | 37.78
2021-02-12 21:30 | 44239.8958 | 0 | 14.0427 | 37.78
2021-02-12 22:00 | 44239.9167 | 0 | 13.2773 | 37.78
2021-02-12 22:30 | 44239.9375 | 0 | 12.5864 | 37.78
2021-02-12 23:00 | 44239.9583 | 0 | 12.2693 | 37.78
2021-02-12 23:30 | 44239.9792 | 0 | 11.7308 | 37.78
2021-02-13 | 44240 | 0 | 10.8895 | 37.78
2021-02-13 00:30 | 44240.0208 | 0 | 10.6656 | 37.78
2021-02-13 01:00 | 44240.0417 | 0 | 10.3077 | 37.78
2021-02-13 01:30 | 44240.0625 | 0 | 9.9317 | 37.78
2021-02-13 02:00 | 44240.0833 | 0 | 9.712 | 37.78
2021-02-13 02:30 | 44240.1042 | 0 | 9.3695 | 37.78
2021-02-13 03:00 | 44240.125 | 0 | 9.0827 | 37.78
2021-02-13 03:30 | 44240.1458 | 0 | 8.9858 | 37.78
2021-02-13 04:00 | 44240.1667 | 0 | 9.1077 | 37.78
2021-02-13 04:30 | 44240.1875 | 0 | 9.0264 | 37.78
2021-02-13 05:00 | 44240.2083 | 0 | 9.2158 | 37.78
2021-02-13 05:30 | 44240.2292 | 0 | 9.1796 | 37.78
2021-02-13 06:00 | 44240.25 | 0 | 9.3127 | 37.78
2021-02-13 06:30 | 44240.2708 | 0 | 9.4372 | 37.78
2021-02-13 07:00 | 44240.2917 | 0 | 9.4062 | 37.78
2021-02-13 07:30 | 44240.3125 | 0 | 9.2402 | 37.78
2021-02-13 08:00 | 44240.3333 | 0 | 10.1974 | 37.78
2021-02-13 08:30 | 44240.3542 | 0 | 10.401 | 37.78
2021-02-13 09:00 | 44240.375 | 0 | 10.2506 | 37.78
2021-02-13 09:30 | 44240.3958 | 0 | 9.9467 | 37.78
2021-02-13 10:00 | 44240.4167 | 0 | 10.3259 | 37.78
2021-02-13 10:30 | 44240.4375 | 0 | 9.9711 | 37.78
2021-02-13 11:00 | 44240.4583 | 0 | 10.5321 | 37.78
2021-02-13 11:30 | 44240.4792 | 0 | 10.7015 | 37.78
2021-02-13 12:00 | 44240.5 | 0 | 10.9657 | 37.78
2021-02-13 12:30 | 44240.5208 | 0 | 11.4507 | 37.78
2021-02-13 13:00 | 44240.5417 | 0 | 12.4569 | 37.78
2021-02-13 13:30 | 44240.5625 | 0 | 13.3158 | 37.78
2021-02-13 14:00 | 44240.5833 | 0 | 13.742 | 37.78
2021-02-13 14:30 | 44240.6042 | 0 | 14.9992 | 37.78
2021-02-13 15:00 | 44240.625 | 0 | 14.6973 | 37.78
2021-02-13 15:30 | 44240.6458 | 0 | 15.4408 | 37.78
2021-02-13 16:00 | 44240.6667 | 0 | 14.9973 | 37.78
2021-02-13 16:30 | 44240.6875 | 0 | 15.3235 | 37.78
2021-02-13 17:00 | 44240.7083 | 0 | 15.7995 | 37.78
2021-02-13 17:30 | 44240.7292 | 0 | 16.0037 | 37.78
2021-02-13 18:00 | 44240.75 | 0 | 15.7378 | 37.78
2021-02-13 18:30 | 44240.7708 | 0 | 15.8405 | 37.78
2021-02-13 19:00 | 44240.7917 | 0 | 15.9327 | 37.78
2021-02-13 19:30 | 44240.8125 | 0 | 15.7856 | 37.78
2021-02-13 20:00 | 44240.8333 | 0 | 15.4561 | 37.78
2021-02-13 20:30 | 44240.8542 | 0 | 14.8598 | 37.78
2021-02-13 21:00 | 44240.875 | 0 | 14.5479 | 37.78
2021-02-13 21:30 | 44240.8958 | 0 | 14.2603 | 37.78
2021-02-13 22:00 | 44240.9167 | 0 | 13.6179 | 37.78
2021-02-13 22:30 | 44240.9375 | 0 | 12.8858 | 37.78
2021-02-13 23:00 | 44240.9583 | 0 | 12.1277 | 37.78
2021-02-13 23:30 | 44240.9792 | 0 | 11.6075 | 37.78
2021-02-14 | 44241 | 0 | 11.0273 | 37.78
2021-02-14 00:30 | 44241.0208 | 0 | 10.6696 | 37.78
2021-02-14 01:00 | 44241.0417 | 0 | 10.47 | 37.78
2021-02-14 01:30 | 44241.0625 | 0 | 10.2081 | 37.78
2021-02-14 02:00 | 44241.0833 | 0 | 10.0944 | 37.78
2021-02-14 02:30 | 44241.1042 | 0 | 9.955 | 37.78
2021-02-14 03:00 | 44241.125 | 0 | 9.7064 | 37.78
2021-02-14 03:30 | 44241.1458 | 0 | 9.7716 | 37.78
2021-02-14 04:00 | 44241.1667 | 0 | 9.6004 | 37.78
2021-02-14 04:30 | 44241.1875 | 0 | 9.4914 | 37.78
2021-02-14 05:00 | 44241.2083 | 0 | 9.3979 | 37.78
2021-02-14 05:30 | 44241.2292 | 0 | 9.4257 | 37.78
2021-02-14 06:00 | 44241.25 | 0 | 9.49 | 37.78
2021-02-14 06:30 | 44241.2708 | 0 | 9.5213 | 37.78
2021-02-14 07:00 | 44241.2917 | 0 | 9.7549 | 37.78
2021-02-14 07:30 | 44241.3125 | 0 | 10.1877 | 37.78
2021-02-14 08:00 | 44241.3333 | 0 | 9.959 | 37.78
2021-02-14 08:30 | 44241.3542 | 0 | 9.9895 | 37.78
2021-02-14 09:00 | 44241.375 | 0 | 10.3391 | 37.78
2021-02-14 09:30 | 44241.3958 | 0 | 9.9822 | 37.78
2021-02-14 10:00 | 44241.4167 | 0 | 10.0152 | 37.78
2021-02-14 10:30 | 44241.4375 | 0 | 10.9097 | 37.78
2021-02-14 11:00 | 44241.4583 | 0 | 11.4751 | 37.78
2021-02-14 11:30 | 44241.4792 | 0 | 11.7151 | 37.78
2021-02-14 12:00 | 44241.5 | 0 | 10.8328 | 37.78
2021-02-14 12:30 | 44241.5208 | 0 | 12.6873 | 37.78
2021-02-14 13:00 | 44241.5417 | 0 | 12.9576 | 37.78
2021-02-14 13:30 | 44241.5625 | 0 | 12.2538 | 37.78
2021-02-14 14:00 | 44241.5833 | 0 | 14.8245 | 37.78
2021-02-14 14:30 | 44241.6042 | 0 | 13.2214 | 37.78
2021-02-14 15:00 | 44241.625 | 0 | 13.3475 | 37.78
2021-02-14 15:30 | 44241.6458 | 0 | 14.4418 | 37.78
2021-02-14 16:00 | 44241.6667 | 0 | 14.1336 | 37.78
2021-02-14 16:30 | 44241.6875 | 0 | 14.3999 | 37.78
2021-02-14 17:00 | 44241.7083 | 0 | 14.5371 | 37.78
2021-02-14 17:30 | 44241.7292 | 0 | 14.3166 | 37.78
2021-02-14 18:00 | 44241.75 | 0 | 14.1026 | 37.78
2021-02-14 18:30 | 44241.7708 | 0 | 14.015 | 37.78
2021-02-14 19:00 | 44241.7917 | 0 | 13.8555 | 37.78
2021-02-14 19:30 | 44241.8125 | 0 | 13.5025 | 37.78
2021-02-14 20:00 | 44241.8333 | 0 | 13.2042 | 37.78
2021-02-14 20:30 | 44241.8542 | 0 | 12.63 | 37.78
2021-02-14 21:00 | 44241.875 | 0 | 11.953 | 37.78
2021-02-14 21:30 | 44241.8958 | 0 | 11.5788 | 37.78
2021-02-14 22:00 | 44241.9167 | 0 | 11.1288 | 37.78
2021-02-14 22:30 | 44241.9375 | 0 | 10.2646 | 37.78
2021-02-14 23:00 | 44241.9583 | 0 | 9.9318 | 37.78
2021-02-14 23:30 | 44241.9792 | 0 | 9.4263 | 37.78
2021-02-15 | 44242 | 0 | 9.2293 | 37.78
2021-02-15 00:30 | 44242.0208 | 0 | 8.9121 | 37.78
2021-02-15 01:00 | 44242.0417 | 0 | 8.8036 | 37.78
2021-02-15 01:30 | 44242.0625 | 0 | 8.6813 | 37.78
2021-02-15 02:00 | 44242.0833 | 0 | 8.7583 | 37.78
2021-02-15 02:30 | 44242.1042 | 0 | 8.4614 | 37.78
2021-02-15 03:00 | 44242.125 | 0 | 8.4864 | 37.78
2021-02-15 03:30 | 44242.1458 | 0 | 8.603 | 37.78
2021-02-15 04:00 | 44242.1667 | 0 | 8.8477 | 37.78
2021-02-15 04:30 | 44242.1875 | 0 | 9.1745 | 37.78
2021-02-15 05:00 | 44242.2083 | 0 | 9.7375 | 37.78
2021-02-15 05:30 | 44242.2292 | 0 | 10.3524 | 37.78
2021-02-15 06:00 | 44242.25 | 0 | 11.1933 | 37.78
2021-02-15 06:30 | 44242.2708 | 0 | 11.8373 | 37.78
2021-02-15 07:00 | 44242.2917 | 0 | 12.2486 | 37.78
2021-02-15 07:30 | 44242.3125 | 0 | 12.3858 | 37.78
2021-02-15 08:00 | 44242.3333 | 0 | 12.3885 | 37.78
2021-02-15 08:30 | 44242.3542 | 0 | 12.4917 | 37.78
2021-02-15 09:00 | 44242.375 | 0 | 13.3999 | 37.78
2021-02-15 09:30 | 44242.3958 | 0 | 12.9557 | 37.78
2021-02-15 10:00 | 44242.4167 | 0 | 13.31 | 37.78
2021-02-15 10:30 | 44242.4375 | 0 | 13.599 | 37.78
2021-02-15 11:00 | 44242.4583 | 0 | 14.2617 | 37.78
2021-02-15 11:30 | 44242.4792 | 0 | 14.3523 | 37.78
2021-02-15 12:00 | 44242.5 | 0 | 14.3512 | 37.78
2021-02-15 12:30 | 44242.5208 | 0 | 14.0138 | 37.78
2021-02-15 13:00 | 44242.5417 | 0 | 15.5104 | 37.78
2021-02-15 13:30 | 44242.5625 | 0 | 14.7017 | 37.78
2021-02-15 14:00 | 44242.5833 | 0 | 14.3084 | 37.78
2021-02-15 14:30 | 44242.6042 | 0 | 13.9477 | 37.78
2021-02-15 15:00 | 44242.625 | 0 | 14.1692 | 37.78
2021-02-15 15:30 | 44242.6458 | 0 | 14.8487 | 37.78
2021-02-15 16:00 | 44242.6667 | 0 | 15.5301 | 37.78
2021-02-15 16:30 | 44242.6875 | 0 | 15.9894 | 37.78
2021-02-15 17:00 | 44242.7083 | 0 | 16.3225 | 37.78
2021-02-15 17:30 | 44242.7292 | 0 | 16.4181 | 37.78
2021-02-15 18:00 | 44242.75 | 0 | 16.5613 | 37.78
2021-02-15 18:30 | 44242.7708 | 0 | 17.0442 | 37.78
2021-02-15 19:00 | 44242.7917 | 0 | 16.8062 | 37.78
2021-02-15 19:30 | 44242.8125 | 0 | 16.2975 | 37.78
2021-02-15 20:00 | 44242.8333 | 0 | 15.895 | 37.78
2021-02-15 20:30 | 44242.8542 | 0 | 14.9603 | 37.78
2021-02-15 21:00 | 44242.875 | 0 | 14.6187 | 37.78
2021-02-15 21:30 | 44242.8958 | 0 | 13.8701 | 37.78
2021-02-15 22:00 | 44242.9167 | 0 | 13.1345 | 37.78
2021-02-15 22:30 | 44242.9375 | 0 | 12.1954 | 37.78
2021-02-15 23:00 | 44242.9583 | 0 | 11.4802 | 37.78
2021-02-15 23:30 | 44242.9792 | 0 | 11.0293 | 37.78
2021-02-16 | 44243 | 0 | 10.3187 | 37.78
2021-02-16 00:30 | 44243.0208 | 0 | 9.8893 | 37.78
2021-02-16 01:00 | 44243.0417 | 0 | 9.743 | 37.78
2021-02-16 01:30 | 44243.0625 | 0 | 9.3618 | 37.78
2021-02-16 02:00 | 44243.0833 | 0 | 9.3635 | 37.78
2021-02-16 02:30 | 44243.1042 | 0 | 9.2146 | 37.78
2021-02-16 03:00 | 44243.125 | 0 | 9.052 | 37.78
2021-02-16 03:30 | 44243.1458 | 0 | 9.0514 | 37.78
2021-02-16 04:00 | 44243.1667 | 0 | 9.2642 | 37.78
2021-02-16 04:30 | 44243.1875 | 0 | 9.4981 | 37.78
2021-02-16 05:00 | 44243.2083 | 0 | 10.2759 | 37.78
2021-02-16 05:30 | 44243.2292 | 0 | 10.7408 | 37.78
2021-02-16 06:00 | 44243.25 | 0 | 11.439 | 37.78
2021-02-16 06:30 | 44243.2708 | 0 | 12.1816 | 37.78
2021-02-16 07:00 | 44243.2917 | 0 | 12.6164 | 37.78
2021-02-16 07:30 | 44243.3125 | 0 | 13.1687 | 37.78
2021-02-16 08:00 | 44243.3333 | 0 | 13.1582 | 37.78
2021-02-16 08:30 | 44243.3542 | 0 | 13.9272 | 37.78
2021-02-16 09:00 | 44243.375 | 0 | 14.8484 | 37.78
2021-02-16 09:30 | 44243.3958 | 0 | 14.3576 | 37.78
2021-02-16 10:00 | 44243.4167 | 0 | 14.662 | 37.78
2021-02-16 10:30 | 44243.4375 | 0 | 13.8396 | 37.78
2021-02-16 11:00 | 44243.4583 | 0 | 14.7614 | 37.78
2021-02-16 11:30 | 44243.4792 | 0 | 15.2344 | 37.78
2021-02-16 12:00 | 44243.5 | 0 | 15.383 | 37.78
2021-02-16 12:30 | 44243.5208 | 0 | 14.1792 | 37.78
2021-02-16 13:00 | 44243.5417 | 0 | 16.8243 | 37.78
2021-02-16 13:30 | 44243.5625 | 0 | 13.6238 | 37.78
2021-02-16 14:00 | 44243.5833 | 0 | 14.4435 | 37.78
2021-02-16 14:30 | 44243.6042 | 0 | 14.6315 | 37.78
2021-02-16 15:00 | 44243.625 | 0 | 15.8759 | 37.78
2021-02-16 15:30 | 44243.6458 | 0 | 15.0842 | 37.78
2021-02-16 16:00 | 44243.6667 | 0 | 14.5213 | 37.78
2021-02-16 16:30 | 44243.6875 | 0 | 13.951 | 37.78
2021-02-16 17:00 | 44243.7083 | 0 | 15.0547 | 37.78
2021-02-16 17:30 | 44243.7292 | 0 | 15.3931 | 37.78
2021-02-16 18:00 | 44243.75 | 0 | 15.0041 | 37.78
2021-02-16 18:30 | 44243.7708 | 0 | 15.5755 | 37.78
2021-02-16 19:00 | 44243.7917 | 0 | 15.5198 | 37.78
2021-02-16 19:30 | 44243.8125 | 0 | 15.2286 | 37.78
2021-02-16 20:00 | 44243.8333 | 0 | 14.6895 | 37.78
2021-02-16 20:30 | 44243.8542 | 0 | 14.1181 | 37.78
2021-02-16 21:00 | 44243.875 | 0 | 13.6365 | 37.78
2021-02-16 21:30 | 44243.8958 | 0 | 13.0387 | 37.78
2021-02-16 22:00 | 44243.9167 | 0 | 12.4336 | 37.78
2021-02-16 22:30 | 44243.9375 | 0 | 11.4197 | 37.78
2021-02-16 23:00 | 44243.9583 | 0 | 10.7661 | 37.78
2021-02-16 23:30 | 44243.9792 | 0 | 10.1553 | 37.78
2021-02-17 | 44244 | 0 | 9.4561 | 37.78
2021-02-17 00:30 | 44244.0208 | 0 | 9.0946 | 37.78
2021-02-17 01:00 | 44244.0417 | 0 | 9.0447 | 37.78
2021-02-17 01:30 | 44244.0625 | 0 | 8.8659 | 37.78
2021-02-17 02:00 | 44244.0833 | 0 | 8.7111 | 37.78
2021-02-17 02:30 | 44244.1042 | 0 | 8.4353 | 37.78
2021-02-17 03:00 | 44244.125 | 0 | 8.4891 | 37.78
2021-02-17 03:30 | 44244.1458 | 0 | 8.7408 | 37.78
2021-02-17 04:00 | 44244.1667 | 0 | 9.0237 | 37.78
2021-02-17 04:30 | 44244.1875 | 0 | 9.2089 | 37.78
2021-02-17 05:00 | 44244.2083 | 0 | 9.7149 | 37.78
2021-02-17 05:30 | 44244.2292 | 0 | 10.317 | 37.78
2021-02-17 06:00 | 44244.25 | 0 | 10.916 | 37.78
2021-02-17 06:30 | 44244.2708 | 0 | 11.5129 | 37.78
2021-02-17 07:00 | 44244.2917 | 0 | 12.0366 | 37.78
2021-02-17 07:30 | 44244.3125 | 0 | 12.2443 | 37.78
2021-02-17 08:00 | 44244.3333 | 0 | 12.3294 | 37.78
2021-02-17 08:30 | 44244.3542 | 0 | 12.1596 | 37.78
2021-02-17 09:00 | 44244.375 | 0 | 14.3067 | 37.78
2021-02-17 09:30 | 44244.3958 | 0 | 13.6218 | 37.78
2021-02-17 10:00 | 44244.4167 | 0 | 13.5363 | 37.78
2021-02-17 10:30 | 44244.4375 | 0 | 13.1598 | 37.78
2021-02-17 11:00 | 44244.4583 | 0 | 13.2665 | 37.78
2021-02-17 11:30 | 44244.4792 | 0 | 11.9731 | 37.78
2021-02-17 12:00 | 44244.5 | 0 | 12.8953 | 37.78
2021-02-17 12:30 | 44244.5208 | 0 | 12.8662 | 37.78
2021-02-17 13:00 | 44244.5417 | 0 | 13.9128 | 37.78
2021-02-17 13:30 | 44244.5625 | 0 | 12.7459 | 37.78
2021-02-17 14:00 | 44244.5833 | 0 | 13.9536 | 37.78
2021-02-17 14:30 | 44244.6042 | 0 | 13.6235 | 37.78
2021-02-17 15:00 | 44244.625 | 0 | 14.0525 | 37.78
2021-02-17 15:30 | 44244.6458 | 0 | 13.979 | 37.78
2021-02-17 16:00 | 44244.6667 | 0 | 13.8176 | 37.78
2021-02-17 16:30 | 44244.6875 | 0 | 14.308 | 37.78
2021-02-17 17:00 | 44244.7083 | 0 | 14.7815 | 37.78
2021-02-17 17:30 | 44244.7292 | 0 | 14.8201 | 37.78
2021-02-17 18:00 | 44244.75 | 0 | 14.8798 | 37.78
2021-02-17 18:30 | 44244.7708 | 0 | 15.4305 | 37.78
2021-02-17 19:00 | 44244.7917 | 0 | 15.2324 | 37.78
2021-02-17 19:30 | 44244.8125 | 0 | 14.9318 | 37.78
2021-02-17 20:00 | 44244.8333 | 0 | 14.7342 | 37.78
2021-02-17 20:30 | 44244.8542 | 0 | 14.0517 | 37.78
2021-02-17 21:00 | 44244.875 | 0 | 13.6174 | 37.78
2021-02-17 21:30 | 44244.8958 | 0 | 13.124 | 37.78
2021-02-17 22:00 | 44244.9167 | 0 | 12.4046 | 37.78
2021-02-17 22:30 | 44244.9375 | 0 | 11.3928 | 37.78
2021-02-17 23:00 | 44244.9583 | 0 | 10.7275 | 37.78
2021-02-17 23:30 | 44244.9792 | 0 | 10.2898 | 37.78
2021-02-18 | 44245 | 0 | 9.697 | 37.78
2021-02-18 00:30 | 44245.0208 | 0 | 9.2734 | 37.78
2021-02-18 01:00 | 44245.0417 | 0 | 9.0907 | 37.78
2021-02-18 01:30 | 44245.0625 | 0 | 9.105 | 37.78
2021-02-18 02:00 | 44245.0833 | 0 | 8.8266 | 37.78
2021-02-18 02:30 | 44245.1042 | 0 | 8.712 | 37.78
2021-02-18 03:00 | 44245.125 | 0 | 8.7592 | 37.78
2021-02-18 03:30 | 44245.1458 | 0 | 8.6779 | 37.78
2021-02-18 04:00 | 44245.1667 | 0 | 8.9928 | 37.78
2021-02-18 04:30 | 44245.1875 | 0 | 9.3961 | 37.78
2021-02-18 05:00 | 44245.2083 | 0 | 10.0256 | 37.78
2021-02-18 05:30 | 44245.2292 | 0 | 10.5397 | 37.78
2021-02-18 06:00 | 44245.25 | 0 | 11.3067 | 37.78
2021-02-18 06:30 | 44245.2708 | 0 | 12.2757 | 37.78
2021-02-18 07:00 | 44245.2917 | 0 | 12.9578 | 37.78
2021-02-18 07:30 | 44245.3125 | 0 | 13.3913 | 37.78
2021-02-18 08:00 | 44245.3333 | 0 | 12.6124 | 37.78
2021-02-18 08:30 | 44245.3542 | 0 | 14.3664 | 37.78
2021-02-18 09:00 | 44245.375 | 0 | 14.444 | 37.78
2021-02-18 09:30 | 44245.3958 | 0 | 14.7168 | 37.78
2021-02-18 10:00 | 44245.4167 | 0 | 14.0115 | 37.78
2021-02-18 10:30 | 44245.4375 | 0 | 13.1903 | 37.78
2021-02-18 11:00 | 44245.4583 | 0 | 13.2282 | 37.78
2021-02-18 11:30 | 44245.4792 | 0 | 13.1716 | 37.78
2021-02-18 12:00 | 44245.5 | 0 | 14.2501 | 37.78
2021-02-18 12:30 | 44245.5208 | 0 | 13.7559 | 37.78
2021-02-18 13:00 | 44245.5417 | 0 | 14.0849 | 37.78
2021-02-18 13:30 | 44245.5625 | 0 | 13.2236 | 37.78
2021-02-18 14:00 | 44245.5833 | 0 | 12.2252 | 37.78
2021-02-18 14:30 | 44245.6042 | 0 | 12.6021 | 37.78
2021-02-18 15:00 | 44245.625 | 0 | 12.8544 | 37.78
2021-02-18 15:30 | 44245.6458 | 0 | 14.3621 | 37.78
2021-02-18 16:00 | 44245.6667 | 0 | 13.8676 | 37.78
2021-02-18 16:30 | 44245.6875 | 0 | 14.8067 | 37.78
2021-02-18 17:00 | 44245.7083 | 0 | 15.0063 | 37.78
2021-02-18 17:30 | 44245.7292 | 0 | 15.2948 | 37.78
2021-02-18 18:00 | 44245.75 | 0 | 15.111 | 37.78
2021-02-18 18:30 | 44245.7708 | 0 | 15.6872 | 37.78
2021-02-18 19:00 | 44245.7917 | 0 | 15.6538 | 37.78
2021-02-18 19:30 | 44245.8125 | 0 | 15.586 | 37.78
2021-02-18 20:00 | 44245.8333 | 0 | 15.0533 | 37.78
2021-02-18 20:30 | 44245.8542 | 0 | 14.5424 | 37.78
2021-02-18 21:00 | 44245.875 | 0 | 13.8886 | 37.78
2021-02-18 21:30 | 44245.8958 | 0 | 13.4321 | 37.78
2021-02-18 22:00 | 44245.9167 | 0 | 12.7746 | 37.78
2021-02-18 22:30 | 44245.9375 | 0 | 11.9215 | 37.78
2021-02-18 23:00 | 44245.9583 | 0 | 11.2192 | 37.78
2021-02-18 23:30 | 44245.9792 | 0 | 10.7139 | 37.78
2021-02-19 | 44246 | 0 | 10.1429 | 37.78
2021-02-19 00:30 | 44246.0208 | 0 | 9.6633 | 37.78
2021-02-19 01:00 | 44246.0417 | 0 | 9.2527 | 37.78
2021-02-19 01:30 | 44246.0625 | 0 | 9.1963 | 37.78
2021-02-19 02:00 | 44246.0833 | 0 | 9.2329 | 37.78
2021-02-19 02:30 | 44246.1042 | 0 | 8.9554 | 37.78
2021-02-19 03:00 | 44246.125 | 0 | 8.8958 | 37.78
2021-02-19 03:30 | 44246.1458 | 0 | 9.0487 | 37.78
2021-02-19 04:00 | 44246.1667 | 0 | 9.2209 | 37.78
2021-02-19 04:30 | 44246.1875 | 0 | 9.6502 | 37.78
2021-02-19 05:00 | 44246.2083 | 0 | 10.2495 | 37.78
2021-02-19 05:30 | 44246.2292 | 0 | 10.7068 | 37.78
2021-02-19 06:00 | 44246.25 | 0 | 11.3271 | 37.78
2021-02-19 06:30 | 44246.2708 | 0 | 11.9298 | 37.78
2021-02-19 07:00 | 44246.2917 | 0 | 12.6689 | 37.78
2021-02-19 07:30 | 44246.3125 | 0 | 13.4137 | 37.78
2021-02-19 08:00 | 44246.3333 | 0 | 13.7825 | 37.78
2021-02-19 08:30 | 44246.3542 | 0 | 13.9921 | 37.78
2021-02-19 09:00 | 44246.375 | 0 | 13.9279 | 37.78
2021-02-19 09:30 | 44246.3958 | 0 | 13.4963 | 37.78
2021-02-19 10:00 | 44246.4167 | 0 | 13.6549 | 37.78
2021-02-19 10:30 | 44246.4375 | 0 | 13.7017 | 37.78
2021-02-19 11:00 | 44246.4583 | 0 | 13.4486 | 37.78
2021-02-19 11:30 | 44246.4792 | 0 | 14.808 | 37.78
2021-02-19 12:00 | 44246.5 | 0 | 14.4325 | 37.78
2021-02-19 12:30 | 44246.5208 | 0 | 14.4612 | 37.78
2021-02-19 13:00 | 44246.5417 | 0 | 15.3026 | 37.78
2021-02-19 13:30 | 44246.5625 | 0 | 15.7776 | 37.78
2021-02-19 14:00 | 44246.5833 | 0 | 15.9651 | 37.78
2021-02-19 14:30 | 44246.6042 | 0 | 16.0217 | 37.78
2021-02-19 15:00 | 44246.625 | 0 | 15.5213 | 37.78
2021-02-19 15:30 | 44246.6458 | 0 | 15.9621 | 37.78
2021-02-19 16:00 | 44246.6667 | 0 | 15.6416 | 37.78
2021-02-19 16:30 | 44246.6875 | 0 | 15.6275 | 37.78
2021-02-19 17:00 | 44246.7083 | 0 | 15.2672 | 37.78
2021-02-19 17:30 | 44246.7292 | 0 | 15.4901 | 37.78
2021-02-19 18:00 | 44246.75 | 0 | 15.2715 | 37.78
2021-02-19 18:30 | 44246.7708 | 0 | 15.6046 | 37.78
2021-02-19 19:00 | 44246.7917 | 0 | 15.6775 | 37.78
2021-02-19 19:30 | 44246.8125 | 0 | 15.5447 | 37.78
2021-02-19 20:00 | 44246.8333 | 0 | 15.2063 | 37.78
2021-02-19 20:30 | 44246.8542 | 0 | 14.6909 | 37.78
2021-02-19 21:00 | 44246.875 | 0 | 14.2951 | 37.78
2021-02-19 21:30 | 44246.8958 | 0 | 14.0633 | 37.78
2021-02-19 22:00 | 44246.9167 | 0 | 13.2283 | 37.78
2021-02-19 22:30 | 44246.9375 | 0 | 12.2961 | 37.78
2021-02-19 23:00 | 44246.9583 | 0 | 11.6059 | 37.78
2021-02-19 23:30 | 44246.9792 | 0 | 11.2192 | 37.78
2021-02-20 | 44247 | 0 | 10.5616 | 37.78
2021-02-20 00:30 | 44247.0208 | 0 | 10.0087 | 37.78
2021-02-20 01:00 | 44247.0417 | 0 | 9.7436 | 37.78
2021-02-20 01:30 | 44247.0625 | 0 | 9.6227 | 37.78
2021-02-20 02:00 | 44247.0833 | 0 | 9.62 | 37.78
2021-02-20 02:30 | 44247.1042 | 0 | 9.3022 | 37.78
2021-02-20 03:00 | 44247.125 | 0 | 9.3126 | 37.78
2021-02-20 03:30 | 44247.1458 | 0 | 9.3041 | 37.78
2021-02-20 04:00 | 44247.1667 | 0 | 9.444 | 37.78
2021-02-20 04:30 | 44247.1875 | 0 | 9.3614 | 37.78
2021-02-20 05:00 | 44247.2083 | 0 | 9.5191 | 37.78
2021-02-20 05:30 | 44247.2292 | 0 | 9.5977 | 37.78
2021-02-20 06:00 | 44247.25 | 0 | 9.5177 | 37.78
2021-02-20 06:30 | 44247.2708 | 0 | 9.6907 | 37.78
2021-02-20 07:00 | 44247.2917 | 0 | 9.9814 | 37.78
2021-02-20 07:30 | 44247.3125 | 0 | 10.2766 | 37.78
2021-02-20 08:00 | 44247.3333 | 0 | 10.3408 | 37.78
2021-02-20 08:30 | 44247.3542 | 0 | 11.041 | 37.78
2021-02-20 09:00 | 44247.375 | 0 | 10.8306 | 37.78
2021-02-20 09:30 | 44247.3958 | 0 | 10.8266 | 37.78
2021-02-20 10:00 | 44247.4167 | 0 | 10.5099 | 37.78
2021-02-20 10:30 | 44247.4375 | 0 | 10.0752 | 37.78
2021-02-20 11:00 | 44247.4583 | 0 | 10.9894 | 37.78
2021-02-20 11:30 | 44247.4792 | 0 | 12.6036 | 37.78
2021-02-20 12:00 | 44247.5 | 0 | 12.6903 | 37.78
2021-02-20 12:30 | 44247.5208 | 0 | 12.6396 | 37.78
2021-02-20 13:00 | 44247.5417 | 0 | 12.4135 | 37.78
2021-02-20 13:30 | 44247.5625 | 0 | 12.5252 | 37.78
2021-02-20 14:00 | 44247.5833 | 0 | 12.9666 | 37.78
2021-02-20 14:30 | 44247.6042 | 0 | 13.0948 | 37.78
2021-02-20 15:00 | 44247.625 | 0 | 13.0636 | 37.78
2021-02-20 15:30 | 44247.6458 | 0 | 12.7268 | 37.78
2021-02-20 16:00 | 44247.6667 | 0 | 12.8971 | 37.78
2021-02-20 16:30 | 44247.6875 | 0 | 13.8056 | 37.78
2021-02-20 17:00 | 44247.7083 | 0 | 14.4251 | 37.78
2021-02-20 17:30 | 44247.7292 | 0 | 15.2642 | 37.78
2021-02-20 18:00 | 44247.75 | 0 | 15.0759 | 37.78
2021-02-20 18:30 | 44247.7708 | 0 | 15.5037 | 37.78
2021-02-20 19:00 | 44247.7917 | 0 | 15.1011 | 37.78
2021-02-20 19:30 | 44247.8125 | 0 | 14.9681 | 37.78
2021-02-20 20:00 | 44247.8333 | 0 | 14.6117 | 37.78
2021-02-20 20:30 | 44247.8542 | 0 | 14.1053 | 37.78
2021-02-20 21:00 | 44247.875 | 0 | 13.5467 | 37.78
2021-02-20 21:30 | 44247.8958 | 0 | 13.2236 | 37.78
2021-02-20 22:00 | 44247.9167 | 0 | 12.6943 | 37.78
2021-02-20 22:30 | 44247.9375 | 0 | 11.8924 | 37.78
2021-02-20 23:00 | 44247.9583 | 0 | 11.3308 | 37.78
2021-02-20 23:30 | 44247.9792 | 0 | 10.7722 | 37.78
2021-02-21 | 44248 | 0 | 10.1357 | 37.78
2021-02-21 00:30 | 44248.0208 | 0 | 9.8472 | 37.78
2021-02-21 01:00 | 44248.0417 | 0 | 9.3412 | 37.78
2021-02-21 01:30 | 44248.0625 | 0 | 9.2343 | 37.78
2021-02-21 02:00 | 44248.0833 | 0 | 9.1562 | 37.78
2021-02-21 02:30 | 44248.1042 | 0 | 8.8512 | 37.78
2021-02-21 03:00 | 44248.125 | 0 | 8.8262 | 37.78
2021-02-21 03:30 | 44248.1458 | 0 | 8.7483 | 37.78
2021-02-21 04:00 | 44248.1667 | 0 | 8.7819 | 37.78
2021-02-21 04:30 | 44248.1875 | 0 | 8.7842 | 37.78
2021-02-21 05:00 | 44248.2083 | 0 | 8.7023 | 37.78
2021-02-21 05:30 | 44248.2292 | 0 | 8.4898 | 37.78
2021-02-21 06:00 | 44248.25 | 0 | 8.5534 | 37.78
2021-02-21 06:30 | 44248.2708 | 0 | 8.7312 | 37.78
2021-02-21 07:00 | 44248.2917 | 0 | 9.119 | 37.78
2021-02-21 07:30 | 44248.3125 | 0 | 9.0264 | 37.78
2021-02-21 08:00 | 44248.3333 | 0 | 9.2249 | 37.78
2021-02-21 08:30 | 44248.3542 | 0 | 9.4968 | 37.78
2021-02-21 09:00 | 44248.375 | 0 | 9.6553 | 37.78
2021-02-21 09:30 | 44248.3958 | 0 | 10.0475 | 37.78
2021-02-21 10:00 | 44248.4167 | 0 | 10.4732 | 37.78
2021-02-21 10:30 | 44248.4375 | 0 | 11.5805 | 37.78
2021-02-21 11:00 | 44248.4583 | 0 | 11.3521 | 37.78
2021-02-21 11:30 | 44248.4792 | 0 | 12.8598 | 37.78
2021-02-21 12:00 | 44248.5 | 0 | 13.0825 | 37.78
2021-02-21 12:30 | 44248.5208 | 0 | 13.4435 | 37.78
2021-02-21 13:00 | 44248.5417 | 0 | 13.721 | 37.78
2021-02-21 13:30 | 44248.5625 | 0 | 14.3088 | 37.78
2021-02-21 14:00 | 44248.5833 | 0 | 15.8085 | 37.78
2021-02-21 14:30 | 44248.6042 | 0 | 15.4125 | 37.78
2021-02-21 15:00 | 44248.625 | 0 | 15.89 | 37.78
2021-02-21 15:30 | 44248.6458 | 0 | 16.994 | 37.78
2021-02-21 16:00 | 44248.6667 | 0 | 18.9202 | 37.78
2021-02-21 16:30 | 44248.6875 | 0 | 19.2555 | 37.78
2021-02-21 17:00 | 44248.7083 | 0 | 18.8081 | 37.78
2021-02-21 17:30 | 44248.7292 | 0 | 19.0423 | 37.78
2021-02-21 18:00 | 44248.75 | 0 | 18.9801 | 37.78
2021-02-21 18:30 | 44248.7708 | 0 | 19.0389 | 37.78
2021-02-21 19:00 | 44248.7917 | 0 | 18.8101 | 37.78
2021-02-21 19:30 | 44248.8125 | 0 | 18.4764 | 37.78
2021-02-21 20:00 | 44248.8333 | 0 | 18.1015 | 37.78
2021-02-21 20:30 | 44248.8542 | 0 | 17.0687 | 37.78
2021-02-21 21:00 | 44248.875 | 0 | 16.0058 | 37.78
2021-02-21 21:30 | 44248.8958 | 0 | 15.069 | 37.78
2021-02-21 22:00 | 44248.9167 | 0 | 13.8755 | 37.78
2021-02-21 22:30 | 44248.9375 | 0 | 12.7776 | 37.78
2021-02-21 23:00 | 44248.9583 | 0 | 12.0259 | 37.78
2021-02-21 23:30 | 44248.9792 | 0 | 11.5065 | 37.78
2021-02-22 | 44249 | 0 | 11.2366 | 37.78
2021-02-22 00:30 | 44249.0208 | 0 | 10.5946 | 37.78
2021-02-22 01:00 | 44249.0417 | 0 | 10.4095 | 37.78
2021-02-22 01:30 | 44249.0625 | 0 | 10.2866 | 37.78
2021-02-22 02:00 | 44249.0833 | 0 | 10.1427 | 37.78
2021-02-22 02:30 | 44249.1042 | 0 | 9.6773 | 37.78
2021-02-22 03:00 | 44249.125 | 0 | 9.5557 | 37.78
2021-02-22 03:30 | 44249.1458 | 0 | 9.612 | 37.78
2021-02-22 04:00 | 44249.1667 | 0 | 9.8418 | 37.78
2021-02-22 04:30 | 44249.1875 | 0 | 10.321 | 37.78
2021-02-22 05:00 | 44249.2083 | 0 | 10.8012 | 37.78
2021-02-22 05:30 | 44249.2292 | 0 | 11.5469 | 37.78
2021-02-22 06:00 | 44249.25 | 0 | 12.5425 | 37.78
2021-02-22 06:30 | 44249.2708 | 0 | 13.2833 | 37.78
2021-02-22 07:00 | 44249.2917 | 0 | 14.0458 | 37.78
2021-02-22 07:30 | 44249.3125 | 0 | 14.7536 | 37.78
2021-02-22 08:00 | 44249.3333 | 0 | 14.8155 | 37.78
2021-02-22 08:30 | 44249.3542 | 0 | 15.488 | 37.78
2021-02-22 09:00 | 44249.375 | 0 | 15.9358 | 37.78
2021-02-22 09:30 | 44249.3958 | 0 | 16.2859 | 37.78
2021-02-22 10:00 | 44249.4167 | 0 | 16.3252 | 37.78
2021-02-22 10:30 | 44249.4375 | 0 | 16.749 | 37.78
2021-02-22 11:00 | 44249.4583 | 0 | 17.3653 | 37.78
2021-02-22 11:30 | 44249.4792 | 0 | 17.7437 | 37.78
2021-02-22 12:00 | 44249.5 | 0 | 18.0683 | 37.78
2021-02-22 12:30 | 44249.5208 | 0 | 18.3021 | 37.78
2021-02-22 13:00 | 44249.5417 | 0 | 18.9557 | 37.78
2021-02-22 13:30 | 44249.5625 | 0 | 19.5908 | 37.78
2021-02-22 14:00 | 44249.5833 | 0 | 20.4804 | 37.78
2021-02-22 14:30 | 44249.6042 | 0 | 20.5199 | 37.78
2021-02-22 15:00 | 44249.625 | 0 | 21.0299 | 37.78
2021-02-22 15:30 | 44249.6458 | 0 | 21.181 | 37.78
2021-02-22 16:00 | 44249.6667 | 0 | 22.0695 | 37.78
2021-02-22 16:30 | 44249.6875 | 0 | 22.4973 | 37.78
2021-02-22 17:00 | 44249.7083 | 0 | 22.5359 | 37.78
2021-02-22 17:30 | 44249.7292 | 0 | 22.8756 | 37.78
2021-02-22 18:00 | 44249.75 | 0 | 22.3983 | 37.78
2021-02-22 18:30 | 44249.7708 | 0 | 22.6195 | 37.78
2021-02-22 19:00 | 44249.7917 | 0 | 22.7205 | 37.78
2021-02-22 19:30 | 44249.8125 | 0 | 22.1106 | 37.78
2021-02-22 20:00 | 44249.8333 | 0 | 21.7455 | 37.78
2021-02-22 20:30 | 44249.8542 | 0 | 20.9759 | 37.78
2021-02-22 21:00 | 44249.875 | 0 | 18.4201 | 37.78
2021-02-22 21:30 | 44249.8958 | 0 | 17.9823 | 37.78
2021-02-22 22:00 | 44249.9167 | 0 | 16.568 | 37.78
2021-02-22 22:30 | 44249.9375 | 0 | 15.5064 | 37.78
2021-02-22 23:00 | 44249.9583 | 0 | 14.3129 | 37.78
2021-02-22 23:30 | 44249.9792 | 0 | 13.7669 | 37.78
2021-02-23 | 44250 | 0 | 13.1476 | 37.78
2021-02-23 00:30 | 44250.0208 | 0 | 12.3741 | 37.78
2021-02-23 01:00 | 44250.0417 | 0 | 11.9715 | 37.78
2021-02-23 01:30 | 44250.0625 | 0 | 11.5773 | 37.78
2021-02-23 02:00 | 44250.0833 | 0 | 11.4727 | 37.78
2021-02-23 02:30 | 44250.1042 | 0 | 11.098 | 37.78
2021-02-23 03:00 | 44250.125 | 0 | 11.0743 | 37.78
2021-02-23 03:30 | 44250.1458 | 0 | 11.0824 | 37.78
2021-02-23 04:00 | 44250.1667 | 0 | 11.494 | 37.78
2021-02-23 04:30 | 44250.1875 | 0 | 11.7149 | 37.78
2021-02-23 05:00 | 44250.2083 | 0 | 12.076 | 37.78
2021-02-23 05:30 | 44250.2292 | 0 | 12.6031 | 37.78
2021-02-23 06:00 | 44250.25 | 0 | 13.3907 | 37.78
2021-02-23 06:30 | 44250.2708 | 0 | 14.1269 | 37.78
2021-02-23 07:00 | 44250.2917 | 0 | 15.3178 | 37.78
2021-02-23 07:30 | 44250.3125 | 0 | 15.7259 | 37.78
2021-02-23 08:00 | 44250.3333 | 0 | 16.2245 | 37.78
2021-02-23 08:30 | 44250.3542 | 0 | 16.7179 | 37.78
2021-02-23 09:00 | 44250.375 | 0 | 17.4048 | 37.78
2021-02-23 09:30 | 44250.3958 | 0 | 16.855 | 37.78
2021-02-23 10:00 | 44250.4167 | 0 | 16.5349 | 37.78
2021-02-23 10:30 | 44250.4375 | 0 | 16.7461 | 37.78
2021-02-23 11:00 | 44250.4583 | 0 | 17.0696 | 37.78
2021-02-23 11:30 | 44250.4792 | 0 | 17.4393 | 37.78
2021-02-23 12:00 | 44250.5 | 0 | 17.7321 | 37.78
2021-02-23 12:30 | 44250.5208 | 0 | 17.9319 | 37.78
2021-02-23 13:00 | 44250.5417 | 0 | 18.424 | 37.78
2021-02-23 13:30 | 44250.5625 | 0 | 18.8535 | 37.78
2021-02-23 14:00 | 44250.5833 | 0 | 19.1681 | 37.78
2021-02-23 14:30 | 44250.6042 | 0 | 20.1208 | 37.78
2021-02-23 15:00 | 44250.625 | 0 | 20.5725 | 37.78
2021-02-23 15:30 | 44250.6458 | 0 | 20.6293 | 37.78
2021-02-23 16:00 | 44250.6667 | 0 | 21.0991 | 37.78
2021-02-23 16:30 | 44250.6875 | 0 | 21.9719 | 37.78
2021-02-23 17:00 | 44250.7083 | 0 | 21.9018 | 37.78
2021-02-23 17:30 | 44250.7292 | 0 | 21.505 | 37.78
2021-02-23 18:00 | 44250.75 | 0 | 21.4502 | 37.78
2021-02-23 18:30 | 44250.7708 | 0 | 21.0265 | 37.78
2021-02-23 19:00 | 44250.7917 | 0 | 19.477 | 37.78
2021-02-23 19:30 | 44250.8125 | 0 | 18.4344 | 37.78
2021-02-23 20:00 | 44250.8333 | 0 | 17.61 | 37.78
2021-02-23 20:30 | 44250.8542 | 0 | 16.6195 | 37.78
2021-02-23 21:00 | 44250.875 | 0 | 15.6455 | 37.78
2021-02-23 21:30 | 44250.8958 | 0 | 14.9128 | 37.78
2021-02-23 22:00 | 44250.9167 | 0 | 13.9381 | 37.78
2021-02-23 22:30 | 44250.9375 | 0 | 13.0475 | 37.78
2021-02-23 23:00 | 44250.9583 | 0 | 12.3948 | 37.78
2021-02-23 23:30 | 44250.9792 | 0 | 11.8463 | 37.78
2021-02-24 | 44251 | 0 | 11.3063 | 37.78
2021-02-24 00:30 | 44251.0208 | 0 | 10.7627 | 37.78
2021-02-24 01:00 | 44251.0417 | 0 | 10.3872 | 37.78
2021-02-24 01:30 | 44251.0625 | 0 | 10.0496 | 37.78
2021-02-24 02:00 | 44251.0833 | 0 | 10.001 | 37.78
2021-02-24 02:30 | 44251.1042 | 0 | 9.7856 | 37.78
2021-02-24 03:00 | 44251.125 | 0 | 9.5584 | 37.78
2021-02-24 03:30 | 44251.1458 | 0 | 9.6504 | 37.78
2021-02-24 04:00 | 44251.1667 | 0 | 9.9781 | 37.78
2021-02-24 04:30 | 44251.1875 | 0 | 10.3944 | 37.78
2021-02-24 05:00 | 44251.2083 | 0 | 10.845 | 37.78
2021-02-24 05:30 | 44251.2292 | 0 | 11.387 | 37.78
2021-02-24 06:00 | 44251.25 | 0 | 12.146 | 37.78
2021-02-24 06:30 | 44251.2708 | 0 | 12.8292 | 37.78
2021-02-24 07:00 | 44251.2917 | 0 | 13.2296 | 37.78
2021-02-24 07:30 | 44251.3125 | 0 | 13.5596 | 37.78
2021-02-24 08:00 | 44251.3333 | 0 | 14.6455 | 37.78
2021-02-24 08:30 | 44251.3542 | 0 | 14.1958 | 37.78
2021-02-24 09:00 | 44251.375 | 0 | 14.8099 | 37.78
2021-02-24 09:30 | 44251.3958 | 0 | 13.8003 | 37.78
2021-02-24 10:00 | 44251.4167 | 0 | 15.276 | 37.78
2021-02-24 10:30 | 44251.4375 | 0 | 14.6163 | 37.78
2021-02-24 11:00 | 44251.4583 | 0 | 14.6093 | 37.78
2021-02-24 11:30 | 44251.4792 | 0 | 15.1633 | 37.78
2021-02-24 12:00 | 44251.5 | 0 | 14.5349 | 37.78
2021-02-24 12:30 | 44251.5208 | 0 | 14.7765 | 37.78
2021-02-24 13:00 | 44251.5417 | 0 | 15.2484 | 37.78
2021-02-24 13:30 | 44251.5625 | 0 | 15.4767 | 37.78
2021-02-24 14:00 | 44251.5833 | 0 | 16.0025 | 37.78
2021-02-24 14:30 | 44251.6042 | 0 | 16.6738 | 37.78
2021-02-24 15:00 | 44251.625 | 0 | 17.1717 | 37.78
2021-02-24 15:30 | 44251.6458 | 0 | 17.7867 | 37.78
2021-02-24 16:00 | 44251.6667 | 0 | 19.1629 | 37.78
2021-02-24 16:30 | 44251.6875 | 0 | 19.3423 | 37.78
2021-02-24 17:00 | 44251.7083 | 0 | 19.3088 | 37.78
2021-02-24 17:30 | 44251.7292 | 0 | 19.0821 | 37.78
2021-02-24 18:00 | 44251.75 | 0 | 18.6362 | 37.78
2021-02-24 18:30 | 44251.7708 | 0 | 19.2415 | 37.78
2021-02-24 19:00 | 44251.7917 | 0 | 19.1802 | 37.78
2021-02-24 19:30 | 44251.8125 | 0 | 18.9896 | 37.78
2021-02-24 20:00 | 44251.8333 | 0 | 18.2233 | 37.78
2021-02-24 20:30 | 44251.8542 | 0 | 17.6879 | 37.78
2021-02-24 21:00 | 44251.875 | 0 | 17.0282 | 37.78
2021-02-24 21:30 | 44251.8958 | 0 | 16.3484 | 37.78
2021-02-24 22:00 | 44251.9167 | 0 | 15.3484 | 37.78
2021-02-24 22:30 | 44251.9375 | 0 | 14.2862 | 37.78
2021-02-24 23:00 | 44251.9583 | 0 | 13.5488 | 37.78
2021-02-24 23:30 | 44251.9792 | 0 | 13.0879 | 37.78
2021-02-25 | 44252 | 0 | 12.1458 | 37.78
2021-02-25 00:30 | 44252.0208 | 0 | 11.5472 | 37.78
2021-02-25 01:00 | 44252.0417 | 0 | 11.0102 | 37.78
2021-02-25 01:30 | 44252.0625 | 0 | 10.7157 | 37.78
2021-02-25 02:00 | 44252.0833 | 0 | 10.4923 | 37.78
2021-02-25 02:30 | 44252.1042 | 0 | 10.3378 | 37.78
2021-02-25 03:00 | 44252.125 | 0 | 10.2915 | 37.78
2021-02-25 03:30 | 44252.1458 | 0 | 10.3448 | 37.78
2021-02-25 04:00 | 44252.1667 | 0 | 10.4394 | 37.78
2021-02-25 04:30 | 44252.1875 | 0 | 10.9225 | 37.78
2021-02-25 05:00 | 44252.2083 | 0 | 11.494 | 37.78
2021-02-25 05:30 | 44252.2292 | 0 | 11.9057 | 37.78
2021-02-25 06:00 | 44252.25 | 0 | 12.9761 | 37.78
2021-02-25 06:30 | 44252.2708 | 0 | 13.5697 | 37.78
2021-02-25 07:00 | 44252.2917 | 0 | 14.3733 | 37.78
2021-02-25 07:30 | 44252.3125 | 0 | 14.7093 | 37.78
2021-02-25 08:00 | 44252.3333 | 0 | 15.7051 | 37.78
2021-02-25 08:30 | 44252.3542 | 0 | 15.306 | 37.78
2021-02-25 09:00 | 44252.375 | 0 | 14.8776 | 37.78
2021-02-25 09:30 | 44252.3958 | 0 | 14.4615 | 37.78
2021-02-25 10:00 | 44252.4167 | 0 | 14.6516 | 37.78
2021-02-25 10:30 | 44252.4375 | 0 | 14.4795 | 37.78
2021-02-25 11:00 | 44252.4583 | 0 | 16.5226 | 37.78
2021-02-25 11:30 | 44252.4792 | 0 | 16.0525 | 37.78
2021-02-25 12:00 | 44252.5 | 0 | 16.5776 | 37.78
2021-02-25 12:30 | 44252.5208 | 0 | 15.9822 | 37.78
2021-02-25 13:00 | 44252.5417 | 0 | 15.2922 | 37.78
2021-02-25 13:30 | 44252.5625 | 0 | 15.1895 | 37.78
2021-02-25 14:00 | 44252.5833 | 0 | 15.9183 | 37.78
2021-02-25 14:30 | 44252.6042 | 0 | 16.1097 | 37.78
2021-02-25 15:00 | 44252.625 | 0 | 15.9389 | 37.78
2021-02-25 15:30 | 44252.6458 | 0 | 16.9103 | 37.78
2021-02-25 16:00 | 44252.6667 | 0 | 17.2724 | 37.78
2021-02-25 16:30 | 44252.6875 | 0 | 18.1205 | 37.78
2021-02-25 17:00 | 44252.7083 | 0 | 18.2709 | 37.78
2021-02-25 17:30 | 44252.7292 | 0 | 18.5012 | 37.78
2021-02-25 18:00 | 44252.75 | 0 | 18.2878 | 37.78
2021-02-25 18:30 | 44252.7708 | 0 | 18.6431 | 37.78
2021-02-25 19:00 | 44252.7917 | 0 | 18.6909 | 37.78
2021-02-25 19:30 | 44252.8125 | 0 | 18.3967 | 37.78
2021-02-25 20:00 | 44252.8333 | 0 | 17.8634 | 37.78
2021-02-25 20:30 | 44252.8542 | 0 | 17.2502 | 37.78
2021-02-25 21:00 | 44252.875 | 0 | 16.6776 | 37.78
2021-02-25 21:30 | 44252.8958 | 0 | 15.8118 | 37.78
2021-02-25 22:00 | 44252.9167 | 0 | 14.5876 | 37.78
2021-02-25 22:30 | 44252.9375 | 0 | 13.3516 | 37.78
2021-02-25 23:00 | 44252.9583 | 0 | 12.6307 | 37.78
2021-02-25 23:30 | 44252.9792 | 0 | 12.0057 | 37.78
2021-02-26 | 44253 | 0 | 10.3829 | 37.78
2021-02-26 00:30 | 44253.0208 | 0 | 10.1006 | 37.78
2021-02-26 01:00 | 44253.0417 | 0 | 10.3833 | 37.78
2021-02-26 01:30 | 44253.0625 | 0 | 10.319 | 37.78
2021-02-26 02:00 | 44253.0833 | 0 | 10.1963 | 37.78
2021-02-26 02:30 | 44253.1042 | 0 | 10.1323 | 37.78
2021-02-26 03:00 | 44253.125 | 0 | 10.1444 | 37.78
2021-02-26 03:30 | 44253.1458 | 0 | 10.1426 | 37.78
2021-02-26 04:00 | 44253.1667 | 0 | 10.4435 | 37.78
2021-02-26 04:30 | 44253.1875 | 0 | 10.926 | 37.78
2021-02-26 05:00 | 44253.2083 | 0 | 11.2337 | 37.78
2021-02-26 05:30 | 44253.2292 | 0 | 11.7102 | 37.78
2021-02-26 06:00 | 44253.25 | 0 | 12.6569 | 37.78
2021-02-26 06:30 | 44253.2708 | 0 | 13.6119 | 37.78
2021-02-26 07:00 | 44253.2917 | 0 | 14.5381 | 37.78
2021-02-26 07:30 | 44253.3125 | 0 | 14.8899 | 37.78
2021-02-26 08:00 | 44253.3333 | 0 | 15.3755 | 37.78
2021-02-26 08:30 | 44253.3542 | 0 | 16.0416 | 37.78
2021-02-26 09:00 | 44253.375 | 0 | 15.9809 | 37.78
2021-02-26 09:30 | 44253.3958 | 0 | 17.1103 | 37.78
2021-02-26 10:00 | 44253.4167 | 0 | 16.6189 | 37.78
2021-02-26 10:30 | 44253.4375 | 0 | 17.1829 | 37.78
2021-02-26 11:00 | 44253.4583 | 0 | 17.5669 | 37.78
2021-02-26 11:30 | 44253.4792 | 0 | 17.8432 | 37.78
2021-02-26 12:00 | 44253.5 | 0 | 16.4918 | 37.78
2021-02-26 12:30 | 44253.5208 | 0 | 17.033 | 37.78
2021-02-26 13:00 | 44253.5417 | 0 | 17.6233 | 37.78
2021-02-26 13:30 | 44253.5625 | 0 | 17.8728 | 37.78
2021-02-26 14:00 | 44253.5833 | 0 | 18.3493 | 37.78
2021-02-26 14:30 | 44253.6042 | 0 | 18.8165 | 37.78
2021-02-26 15:00 | 44253.625 | 0 | 18.9667 | 37.78
2021-02-26 15:30 | 44253.6458 | 0 | 19.5187 | 37.78
2021-02-26 16:00 | 44253.6667 | 0 | 20.2472 | 37.78
2021-02-26 16:30 | 44253.6875 | 0 | 20.6342 | 37.78
2021-02-26 17:00 | 44253.7083 | 0 | 20.3916 | 37.78
2021-02-26 17:30 | 44253.7292 | 0 | 20.1283 | 37.78
2021-02-26 18:00 | 44253.75 | 0 | 19.5562 | 37.78
2021-02-26 18:30 | 44253.7708 | 0 | 19.6629 | 37.78
2021-02-26 19:00 | 44253.7917 | 0 | 19.3966 | 37.78
2021-02-26 19:30 | 44253.8125 | 0 | 19.0142 | 37.78
2021-02-26 20:00 | 44253.8333 | 0 | 18.3324 | 37.78
2021-02-26 20:30 | 44253.8542 | 0 | 17.7501 | 37.78
2021-02-26 21:00 | 44253.875 | 0 | 17.1368 | 37.78
2021-02-26 21:30 | 44253.8958 | 0 | 16.484 | 37.78
2021-02-26 22:00 | 44253.9167 | 0 | 15.7215 | 37.78
2021-02-26 22:30 | 44253.9375 | 0 | 14.4352 | 37.78
2021-02-26 23:00 | 44253.9583 | 0 | 13.8185 | 37.78
2021-02-26 23:30 | 44253.9792 | 0 | 13.1192 | 37.78
2021-02-27 | 44254 | 0 | 12.2019 | 37.78
2021-02-27 00:30 | 44254.0208 | 0 | 11.5527 | 37.78
2021-02-27 01:00 | 44254.0417 | 0 | 11.228 | 37.78
2021-02-27 01:30 | 44254.0625 | 0 | 10.9174 | 37.78
2021-02-27 02:00 | 44254.0833 | 0 | 10.7407 | 37.78
2021-02-27 02:30 | 44254.1042 | 0 | 10.671 | 37.78
2021-02-27 03:00 | 44254.125 | 0 | 10.495 | 37.78
2021-02-27 03:30 | 44254.1458 | 0 | 10.4097 | 37.78
2021-02-27 04:00 | 44254.1667 | 0 | 10.5593 | 37.78
2021-02-27 04:30 | 44254.1875 | 0 | 10.3873 | 37.78
2021-02-27 05:00 | 44254.2083 | 0 | 10.6093 | 37.78
2021-02-27 05:30 | 44254.2292 | 0 | 10.5423 | 37.78
2021-02-27 06:00 | 44254.25 | 0 | 10.587 | 37.78
2021-02-27 06:30 | 44254.2708 | 0 | 10.6783 | 37.78
2021-02-27 07:00 | 44254.2917 | 0 | 10.1309 | 37.78
2021-02-27 07:30 | 44254.3125 | 0 | 10.5613 | 37.78
2021-02-27 08:00 | 44254.3333 | 0 | 11.8712 | 37.78
2021-02-27 08:30 | 44254.3542 | 0 | 11.5855 | 37.78
2021-02-27 09:00 | 44254.375 | 0 | 12.4338 | 37.78
2021-02-27 09:30 | 44254.3958 | 0 | 12.6492 | 37.78
2021-02-27 10:00 | 44254.4167 | 0 | 11.9866 | 37.78
2021-02-27 10:30 | 44254.4375 | 0 | 12.0681 | 37.78
2021-02-27 11:00 | 44254.4583 | 0 | 13.4605 | 37.78
2021-02-27 11:30 | 44254.4792 | 0 | 13.3629 | 37.78
2021-02-27 12:00 | 44254.5 | 0 | 12.5172 | 37.78
2021-02-27 12:30 | 44254.5208 | 0 | 13.1355 | 37.78
2021-02-27 13:00 | 44254.5417 | 0 | 15.019 | 37.78
2021-02-27 13:30 | 44254.5625 | 0 | 15.7707 | 37.78
2021-02-27 14:00 | 44254.5833 | 0 | 17.2408 | 37.78
2021-02-27 14:30 | 44254.6042 | 0 | 16.9963 | 37.78
2021-02-27 15:00 | 44254.625 | 0 | 17.0768 | 37.78
2021-02-27 15:30 | 44254.6458 | 0 | 17.3681 | 37.78
2021-02-27 16:00 | 44254.6667 | 0 | 16.7567 | 37.78
2021-02-27 16:30 | 44254.6875 | 0 | 16.1506 | 37.78
2021-02-27 17:00 | 44254.7083 | 0 | 16.6835 | 37.78
2021-02-27 17:30 | 44254.7292 | 0 | 16.6451 | 37.78
2021-02-27 18:00 | 44254.75 | 0 | 16.7772 | 37.78
2021-02-27 18:30 | 44254.7708 | 0 | 17.1612 | 37.78
2021-02-27 19:00 | 44254.7917 | 0 | 16.953 | 37.78
2021-02-27 19:30 | 44254.8125 | 0 | 16.9528 | 37.78
2021-02-27 20:00 | 44254.8333 | 0 | 16.2148 | 37.78
2021-02-27 20:30 | 44254.8542 | 0 | 15.8793 | 37.78
2021-02-27 21:00 | 44254.875 | 0 | 15.3498 | 37.78
2021-02-27 21:30 | 44254.8958 | 0 | 14.9763 | 37.78
2021-02-27 22:00 | 44254.9167 | 0 | 14.1391 | 37.78
2021-02-27 22:30 | 44254.9375 | 0 | 13.2491 | 37.78
2021-02-27 23:00 | 44254.9583 | 0 | 12.6776 | 37.78
2021-02-27 23:30 | 44254.9792 | 0 | 12.2639 | 37.78
2021-02-28 | 44255 | 0 | 11.4041 | 37.78
2021-02-28 00:30 | 44255.0208 | 0 | 11.1623 | 37.78
2021-02-28 01:00 | 44255.0417 | 0 | 10.8549 | 37.78
2021-02-28 01:30 | 44255.0625 | 0 | 10.6566 | 37.78
2021-02-28 02:00 | 44255.0833 | 0 | 10.5397 | 37.78
2021-02-28 02:30 | 44255.1042 | 0 | 10.3847 | 37.78
2021-02-28 03:00 | 44255.125 | 0 | 10.2173 | 37.78
2021-02-28 03:30 | 44255.1458 | 0 | 10.1837 | 37.78
2021-02-28 04:00 | 44255.1667 | 0 | 10.1722 | 37.78
2021-02-28 04:30 | 44255.1875 | 0 | 10.0537 | 37.78
2021-02-28 05:00 | 44255.2083 | 0 | 10.1127 | 37.78
2021-02-28 05:30 | 44255.2292 | 0 | 10.0747 | 37.78
2021-02-28 06:00 | 44255.25 | 0 | 10.093 | 37.78
2021-02-28 06:30 | 44255.2708 | 0 | 10.2258 | 37.78
2021-02-28 07:00 | 44255.2917 | 0 | 10.4374 | 37.78
2021-02-28 07:30 | 44255.3125 | 0 | 10.6336 | 37.78
2021-02-28 08:00 | 44255.3333 | 0 | 10.8355 | 37.78
2021-02-28 08:30 | 44255.3542 | 0 | 11.4665 | 37.78
2021-02-28 09:00 | 44255.375 | 0 | 11.471 | 37.78
2021-02-28 09:30 | 44255.3958 | 0 | 11.5599 | 37.78
2021-02-28 10:00 | 44255.4167 | 0 | 12.366 | 37.78
2021-02-28 10:30 | 44255.4375 | 0 | 13.1131 | 37.78
2021-02-28 11:00 | 44255.4583 | 0 | 13.6344 | 37.78
2021-02-28 11:30 | 44255.4792 | 0 | 13.1491 | 37.78
2021-02-28 12:00 | 44255.5 | 0 | 13.1131 | 37.78
2021-02-28 12:30 | 44255.5208 | 0 | 14.3329 | 37.78
2021-02-28 13:00 | 44255.5417 | 0 | 14.7676 | 37.78
2021-02-28 13:30 | 44255.5625 | 0 | 14.8064 | 37.78
2021-02-28 14:00 | 44255.5833 | 0 | 14.942 | 37.78
2021-02-28 14:30 | 44255.6042 | 0 | 15.8011 | 37.78
2021-02-28 15:00 | 44255.625 | 0 | 16.8301 | 37.78
2021-02-28 15:30 | 44255.6458 | 0 | 17.3245 | 37.78
2021-02-28 16:00 | 44255.6667 | 0 | 17.387 | 37.78
2021-02-28 16:30 | 44255.6875 | 0 | 17.4726 | 37.78
2021-02-28 17:00 | 44255.7083 | 0 | 17.6191 | 37.78
2021-02-28 17:30 | 44255.7292 | 0 | 17.7125 | 37.78
2021-02-28 18:00 | 44255.75 | 0 | 17.843 | 37.78
2021-02-28 18:30 | 44255.7708 | 0 | 18.3208 | 37.78
2021-02-28 19:00 | 44255.7917 | 0 | 18.1935 | 37.78
2021-02-28 19:30 | 44255.8125 | 0 | 17.68 | 37.78
2021-02-28 20:00 | 44255.8333 | 0 | 17.1787 | 37.78
2021-02-28 20:30 | 44255.8542 | 0 | 16.3484 | 37.78
2021-02-28 21:00 | 44255.875 | 0 | 15.4896 | 37.78
2021-02-28 21:30 | 44255.8958 | 0 | 14.6968 | 37.78
2021-02-28 22:00 | 44255.9167 | 0 | 13.781 | 37.78
2021-02-28 22:30 | 44255.9375 | 0 | 12.5794 | 37.78
2021-02-28 23:00 | 44255.9583 | 0 | 12.0744 | 37.78
2021-02-28 23:30 | 44255.9792 | 0 | 11.4641 | 37.78
2021-03-01 | 44256 | 0 | 11.0917 | 37.78
2021-03-01 00:30 | 44256.0208 | 0 | 10.7433 | 37.78
2021-03-01 01:00 | 44256.0417 | 0 | 10.5566 | 37.78
2021-03-01 01:30 | 44256.0625 | 0 | 10.4713 | 37.78
2021-03-01 02:00 | 44256.0833 | 0 | 10.3623 | 37.78
2021-03-01 02:30 | 44256.1042 | 0 | 10.3168 | 37.78
2021-03-01 03:00 | 44256.125 | 0 | 10.0652 | 37.78
2021-03-01 03:30 | 44256.1458 | 0 | 10.2137 | 37.78
2021-03-01 04:00 | 44256.1667 | 0 | 10.6973 | 37.78
2021-03-01 04:30 | 44256.1875 | 0 | 11.066 | 37.78
2021-03-01 05:00 | 44256.2083 | 0 | 11.6972 | 37.78
2021-03-01 05:30 | 44256.2292 | 0 | 12.2661 | 37.78
2021-03-01 06:00 | 44256.25 | 0 | 13.1888 | 37.78
2021-03-01 06:30 | 44256.2708 | 0 | 14.0876 | 37.78
2021-03-01 07:00 | 44256.2917 | 0 | 15.1804 | 37.78
2021-03-01 07:30 | 44256.3125 | 0 | 16.0885 | 37.78
2021-03-01 08:00 | 44256.3333 | 0 | 15.9357 | 37.78
2021-03-01 08:30 | 44256.3542 | 0 | 16.3604 | 37.78
2021-03-01 09:00 | 44256.375 | 0 | 16.5241 | 37.78
2021-03-01 09:30 | 44256.3958 | 0 | 16.7338 | 37.78
2021-03-01 10:00 | 44256.4167 | 0 | 16.9491 | 37.78
2021-03-01 10:30 | 44256.4375 | 0 | 17.0443 | 37.78
2021-03-01 11:00 | 44256.4583 | 0 | 17.4531 | 37.78
2021-03-01 11:30 | 44256.4792 | 0 | 17.6684 | 37.78
2021-03-01 12:00 | 44256.5 | 0 | 17.2337 | 37.78
2021-03-01 12:30 | 44256.5208 | 0 | 17.3382 | 37.78
2021-03-01 13:00 | 44256.5417 | 0 | 16.9581 | 37.78
2021-03-01 13:30 | 44256.5625 | 0 | 17.3939 | 37.78
2021-03-01 14:00 | 44256.5833 | 0 | 16.776 | 37.78
2021-03-01 14:30 | 44256.6042 | 0 | 17.3929 | 37.78
2021-03-01 15:00 | 44256.625 | 0 | 18.1703 | 37.78
2021-03-01 15:30 | 44256.6458 | 0 | 18.8449 | 37.78
2021-03-01 16:00 | 44256.6667 | 0 | 18.8856 | 37.78
2021-03-01 16:30 | 44256.6875 | 0 | 19.0071 | 37.78
2021-03-01 17:00 | 44256.7083 | 0 | 18.923 | 37.78
2021-03-01 17:30 | 44256.7292 | 0 | 18.8988 | 37.78
2021-03-01 18:00 | 44256.75 | 0 | 19.0486 | 37.78
2021-03-01 18:30 | 44256.7708 | 0 | 19.9104 | 37.78
2021-03-01 19:00 | 44256.7917 | 0 | 19.6093 | 37.78
2021-03-01 19:30 | 44256.8125 | 0 | 19.3607 | 37.78
2021-03-01 20:00 | 44256.8333 | 0 | 18.9553 | 37.78
2021-03-01 20:30 | 44256.8542 | 0 | 18.1011 | 37.78
2021-03-01 21:00 | 44256.875 | 0 | 17.0383 | 37.78
2021-03-01 21:30 | 44256.8958 | 0 | 16.3351 | 37.78
2021-03-01 22:00 | 44256.9167 | 0 | 15.3536 | 37.78
2021-03-01 22:30 | 44256.9375 | 0 | 14.075 | 37.78
2021-03-01 23:00 | 44256.9583 | 0 | 13.2532 | 37.78
2021-03-01 23:30 | 44256.9792 | 0 | 12.875 | 37.78
2021-03-02 | 44257 | 0 | 12.2039 | 37.78
2021-03-02 00:30 | 44257.0208 | 0 | 11.5399 | 37.78
2021-03-02 01:00 | 44257.0417 | 0 | 11.2379 | 37.78
2021-03-02 01:30 | 44257.0625 | 0 | 10.8997 | 37.78
2021-03-02 02:00 | 44257.0833 | 0 | 10.7596 | 37.78
2021-03-02 02:30 | 44257.1042 | 0 | 10.5804 | 37.78
2021-03-02 03:00 | 44257.125 | 0 | 10.3488 | 37.78
2021-03-02 03:30 | 44257.1458 | 0 | 10.407 | 37.78
2021-03-02 04:00 | 44257.1667 | 0 | 10.6764 | 37.78
2021-03-02 04:30 | 44257.1875 | 0 | 10.9497 | 37.78
2021-03-02 05:00 | 44257.2083 | 0 | 11.5514 | 37.78
2021-03-02 05:30 | 44257.2292 | 0 | 12.0991 | 37.78
2021-03-02 06:00 | 44257.25 | 0 | 12.5904 | 37.78
2021-03-02 06:30 | 44257.2708 | 0 | 13.2708 | 37.78
2021-03-02 07:00 | 44257.2917 | 0 | 13.9892 | 37.78
2021-03-02 07:30 | 44257.3125 | 0 | 14.1879 | 37.78
2021-03-02 08:00 | 44257.3333 | 0 | 14.5898 | 37.78
2021-03-02 08:30 | 44257.3542 | 0 | 14.8987 | 37.78
2021-03-02 09:00 | 44257.375 | 0 | 15.0786 | 37.78
2021-03-02 09:30 | 44257.3958 | 0 | 15.5223 | 37.78
2021-03-02 10:00 | 44257.4167 | 0 | 15.8785 | 37.78
2021-03-02 10:30 | 44257.4375 | 0 | 16.2423 | 37.78
2021-03-02 11:00 | 44257.4583 | 0 | 16.7016 | 37.78
2021-03-02 11:30 | 44257.4792 | 0 | 17.7471 | 37.78
2021-03-02 12:00 | 44257.5 | 0 | 17.6319 | 37.78
2021-03-02 12:30 | 44257.5208 | 0 | 18.2367 | 37.78
2021-03-02 13:00 | 44257.5417 | 0 | 18.6427 | 37.78
2021-03-02 13:30 | 44257.5625 | 0 | 19.4155 | 37.78
2021-03-02 14:00 | 44257.5833 | 0 | 19.99 | 37.78
2021-03-02 14:30 | 44257.6042 | 0 | 20.3618 | 37.78
2021-03-02 15:00 | 44257.625 | 0 | 20.4237 | 37.78
2021-03-02 15:30 | 44257.6458 | 0 | 21.4875 | 37.78
2021-03-02 16:00 | 44257.6667 | 0 | 22.235 | 37.78
2021-03-02 16:30 | 44257.6875 | 0 | 23.4567 | 37.78
2021-03-02 17:00 | 44257.7083 | 0 | 23.17 | 37.78
2021-03-02 17:30 | 44257.7292 | 0 | 21.7312 | 37.78
2021-03-02 18:00 | 44257.75 | 0 | 21.1608 | 37.78
2021-03-02 18:30 | 44257.7708 | 0 | 20.9589 | 37.78
2021-03-02 19:00 | 44257.7917 | 0 | 20.6839 | 37.78
2021-03-02 19:30 | 44257.8125 | 0 | 20.4644 | 37.78
2021-03-02 20:00 | 44257.8333 | 0 | 19.708 | 37.78
2021-03-02 20:30 | 44257.8542 | 0 | 18.8437 | 37.78
2021-03-02 21:00 | 44257.875 | 0 | 17.5448 | 37.78
2021-03-02 21:30 | 44257.8958 | 0 | 16.6178 | 37.78
2021-03-02 22:00 | 44257.9167 | 0 | 15.7195 | 37.78
2021-03-02 22:30 | 44257.9375 | 0 | 14.1637 | 37.78
2021-03-02 23:00 | 44257.9583 | 0 | 13.5876 | 37.78
2021-03-02 23:30 | 44257.9792 | 0 | 13.033 | 37.78
2021-03-03 | 44258 | 0 | 12.1757 | 37.78
2021-03-03 00:30 | 44258.0208 | 0 | 11.4816 | 37.78
2021-03-03 01:00 | 44258.0417 | 0 | 11.1873 | 37.78
2021-03-03 01:30 | 44258.0625 | 0 | 11.1636 | 37.78
2021-03-03 02:00 | 44258.0833 | 0 | 10.8594 | 37.78
2021-03-03 02:30 | 44258.1042 | 0 | 10.7157 | 37.78
2021-03-03 03:00 | 44258.125 | 0 | 10.474 | 37.78
2021-03-03 03:30 | 44258.1458 | 0 | 10.545 | 37.78
2021-03-03 04:00 | 44258.1667 | 0 | 10.8998 | 37.78
2021-03-03 04:30 | 44258.1875 | 0 | 11.3122 | 37.78
2021-03-03 05:00 | 44258.2083 | 0 | 11.8365 | 37.78
2021-03-03 05:30 | 44258.2292 | 0 | 12.2505 | 37.78
2021-03-03 06:00 | 44258.25 | 0 | 13.2194 | 37.78
2021-03-03 06:30 | 44258.2708 | 0 | 13.768 | 37.78
2021-03-03 07:00 | 44258.2917 | 0 | 14.4168 | 37.78
2021-03-03 07:30 | 44258.3125 | 0 | 14.2904 | 37.78
2021-03-03 08:00 | 44258.3333 | 0 | 15.003 | 37.78
2021-03-03 08:30 | 44258.3542 | 0 | 15.0347 | 37.78
2021-03-03 09:00 | 44258.375 | 0 | 16.2951 | 37.78
2021-03-03 09:30 | 44258.3958 | 0 | 16.4151 | 37.78
2021-03-03 10:00 | 44258.4167 | 0 | 15.4759 | 37.78
2021-03-03 10:30 | 44258.4375 | 0 | 14.9388 | 37.78
2021-03-03 11:00 | 44258.4583 | 0 | 15.2626 | 37.78
2021-03-03 11:30 | 44258.4792 | 0 | 15.594 | 37.78
2021-03-03 12:00 | 44258.5 | 0 | 14.7157 | 37.78
2021-03-03 12:30 | 44258.5208 | 0 | 13.4292 | 37.78
2021-03-03 13:00 | 44258.5417 | 0 | 13.1348 | 37.78
2021-03-03 13:30 | 44258.5625 | 0 | 15.2268 | 37.78
2021-03-03 14:00 | 44258.5833 | 0 | 14.5918 | 37.78
2021-03-03 14:30 | 44258.6042 | 0 | 14.381 | 37.78
2021-03-03 15:00 | 44258.625 | 0 | 15.5953 | 37.78
2021-03-03 15:30 | 44258.6458 | 0 | 14.826 | 37.78
2021-03-03 16:00 | 44258.6667 | 0 | 15.1219 | 37.78
2021-03-03 16:30 | 44258.6875 | 0 | 15.3162 | 37.78
2021-03-03 17:00 | 44258.7083 | 0 | 15.2782 | 37.78
2021-03-03 17:30 | 44258.7292 | 0 | 15.5162 | 37.78
2021-03-03 18:00 | 44258.75 | 0 | 15.5313 | 37.78
2021-03-03 18:30 | 44258.7708 | 0 | 16.192 | 37.78
2021-03-03 19:00 | 44258.7917 | 0 | 15.8115 | 37.78
2021-03-03 19:30 | 44258.8125 | 0 | 15.8934 | 37.78
2021-03-03 20:00 | 44258.8333 | 0 | 15.5094 | 37.78
2021-03-03 20:30 | 44258.8542 | 0 | 15.0547 | 37.78
2021-03-03 21:00 | 44258.875 | 0 | 14.5833 | 37.78
2021-03-03 21:30 | 44258.8958 | 0 | 13.9271 | 37.78
2021-03-03 22:00 | 44258.9167 | 0 | 13.4195 | 37.78
2021-03-03 22:30 | 44258.9375 | 0 | 12.4749 | 37.78
2021-03-03 23:00 | 44258.9583 | 0 | 11.6423 | 37.78
2021-03-03 23:30 | 44258.9792 | 0 | 11.1728 | 37.78
2021-03-04 | 44259 | 0 | 10.2395 | 37.78
2021-03-04 00:30 | 44259.0208 | 0 | 9.7816 | 37.78
2021-03-04 01:00 | 44259.0417 | 0 | 9.5204 | 37.78
2021-03-04 01:30 | 44259.0625 | 0 | 9.2782 | 37.78
2021-03-04 02:00 | 44259.0833 | 0 | 9.3153 | 37.78
2021-03-04 02:30 | 44259.1042 | 0 | 9.1288 | 37.78
2021-03-04 03:00 | 44259.125 | 0 | 8.9526 | 37.78
2021-03-04 03:30 | 44259.1458 | 0 | 8.9008 | 37.78
2021-03-04 04:00 | 44259.1667 | 0 | 9.2343 | 37.78
2021-03-04 04:30 | 44259.1875 | 0 | 9.7484 | 37.78
2021-03-04 05:00 | 44259.2083 | 0 | 10.4764 | 37.78
2021-03-04 05:30 | 44259.2292 | 0 | 10.9395 | 37.78
2021-03-04 06:00 | 44259.25 | 0 | 12.0847 | 37.78
2021-03-04 06:30 | 44259.2708 | 0 | 12.6005 | 37.78
2021-03-04 07:00 | 44259.2917 | 0 | 13.266 | 37.78
2021-03-04 07:30 | 44259.3125 | 0 | 13.3118 | 37.78
2021-03-04 08:00 | 44259.3333 | 0 | 13.8604 | 37.78
2021-03-04 08:30 | 44259.3542 | 0 | 14.0739 | 37.78
2021-03-04 09:00 | 44259.375 | 0 | 12.9071 | 37.78
2021-03-04 09:30 | 44259.3958 | 0 | 13.7571 | 37.78
2021-03-04 10:00 | 44259.4167 | 0 | 13.628 | 37.78
2021-03-04 10:30 | 44259.4375 | 0 | 12.5408 | 37.78
2021-03-04 11:00 | 44259.4583 | 0 | 12.0064 | 37.78
2021-03-04 11:30 | 44259.4792 | 0 | 13.166 | 37.78
2021-03-04 12:00 | 44259.5 | 0 | 12.651 | 37.78
2021-03-04 12:30 | 44259.5208 | 0 | 12.6638 | 37.78
2021-03-04 13:00 | 44259.5417 | 0 | 12.8662 | 37.78
2021-03-04 13:30 | 44259.5625 | 0 | 13.3653 | 37.78
2021-03-04 14:00 | 44259.5833 | 0 | 12.9715 | 37.78
2021-03-04 14:30 | 44259.6042 | 0 | 13.6042 | 37.78
2021-03-04 15:00 | 44259.625 | 0 | 13.5344 | 37.78
2021-03-04 15:30 | 44259.6458 | 0 | 13.1537 | 37.78
2021-03-04 16:00 | 44259.6667 | 0 | 13.3905 | 37.78
2021-03-04 16:30 | 44259.6875 | 0 | 14.0585 | 37.78
2021-03-04 17:00 | 44259.7083 | 0 | 14.6069 | 37.78
2021-03-04 17:30 | 44259.7292 | 0 | 15.035 | 37.78
2021-03-04 18:00 | 44259.75 | 0 | 14.8487 | 37.78
2021-03-04 18:30 | 44259.7708 | 0 | 15.3032 | 37.78
2021-03-04 19:00 | 44259.7917 | 0 | 15.3365 | 37.78
2021-03-04 19:30 | 44259.8125 | 0 | 15.0446 | 37.78
2021-03-04 20:00 | 44259.8333 | 0 | 14.6076 | 37.78
2021-03-04 20:30 | 44259.8542 | 0 | 14.0425 | 37.78
2021-03-04 21:00 | 44259.875 | 0 | 13.2878 | 37.78
2021-03-04 21:30 | 44259.8958 | 0 | 12.8298 | 37.78
2021-03-04 22:00 | 44259.9167 | 0 | 12.1026 | 37.78
2021-03-04 22:30 | 44259.9375 | 0 | 11.2102 | 37.78
2021-03-04 23:00 | 44259.9583 | 0 | 10.4588 | 37.78
2021-03-04 23:30 | 44259.9792 | 0 | 10.0184 | 37.78
2021-03-05 | 44260 | 0 | 9.4766 | 37.78
2021-03-05 00:30 | 44260.0208 | 0 | 9.2404 | 37.78
2021-03-05 01:00 | 44260.0417 | 0 | 8.908 | 37.78
2021-03-05 01:30 | 44260.0625 | 0 | 8.7478 | 37.78
2021-03-05 02:00 | 44260.0833 | 0 | 8.6861 | 37.78
2021-03-05 02:30 | 44260.1042 | 0 | 8.502 | 37.78
2021-03-05 03:00 | 44260.125 | 0 | 8.4444 | 37.78
2021-03-05 03:30 | 44260.1458 | 0 | 8.5588 | 37.78
2021-03-05 04:00 | 44260.1667 | 0 | 8.8676 | 37.78
2021-03-05 04:30 | 44260.1875 | 0 | 9.3373 | 37.78
2021-03-05 05:00 | 44260.2083 | 0 | 9.7385 | 37.78
2021-03-05 05:30 | 44260.2292 | 0 | 10.3774 | 37.78
2021-03-05 06:00 | 44260.25 | 0 | 10.7864 | 37.78
2021-03-05 06:30 | 44260.2708 | 0 | 11.3007 | 37.78
2021-03-05 07:00 | 44260.2917 | 0 | 11.546 | 37.78
2021-03-05 07:30 | 44260.3125 | 0 | 11.5263 | 37.78
2021-03-05 08:00 | 44260.3333 | 0 | 11.609 | 37.78
2021-03-05 08:30 | 44260.3542 | 0 | 11.4097 | 37.78
2021-03-05 09:00 | 44260.375 | 0 | 11.356 | 37.78
2021-03-05 09:30 | 44260.3958 | 0 | 11.2746 | 37.78
2021-03-05 10:00 | 44260.4167 | 0 | 11.0337 | 37.78
2021-03-05 10:30 | 44260.4375 | 0 | 11.4959 | 37.78
2021-03-05 11:00 | 44260.4583 | 0 | 11.9428 | 37.78
2021-03-05 11:30 | 44260.4792 | 0 | 12.8706 | 37.78
2021-03-05 12:00 | 44260.5 | 0 | 13.0372 | 37.78
2021-03-05 12:30 | 44260.5208 | 0 | 13.0196 | 37.78
2021-03-05 13:00 | 44260.5417 | 0 | 12.976 | 37.78
2021-03-05 13:30 | 44260.5625 | 0 | 13.8804 | 37.78
2021-03-05 14:00 | 44260.5833 | 0 | 14.7917 | 37.78
2021-03-05 14:30 | 44260.6042 | 0 | 15.7238 | 37.78
2021-03-05 15:00 | 44260.625 | 0 | 14.9645 | 37.78
2021-03-05 15:30 | 44260.6458 | 0 | 15.9695 | 37.78
2021-03-05 16:00 | 44260.6667 | 0 | 16.4458 | 37.78
2021-03-05 16:30 | 44260.6875 | 0 | 16.9624 | 37.78
2021-03-05 17:00 | 44260.7083 | 0 | 17.1093 | 37.78
2021-03-05 17:30 | 44260.7292 | 0 | 16.9491 | 37.78
2021-03-05 18:00 | 44260.75 | 0 | 16.7718 | 37.78
2021-03-05 18:30 | 44260.7708 | 0 | 17.0249 | 37.78
2021-03-05 19:00 | 44260.7917 | 0 | 16.7853 | 37.78
2021-03-05 19:30 | 44260.8125 | 0 | 16.736 | 37.78
2021-03-05 20:00 | 44260.8333 | 0 | 16.2926 | 37.78
2021-03-05 20:30 | 44260.8542 | 0 | 15.5654 | 37.78
2021-03-05 21:00 | 44260.875 | 0 | 15.0212 | 37.78
2021-03-05 21:30 | 44260.8958 | 0 | 14.4899 | 37.78
2021-03-05 22:00 | 44260.9167 | 0 | 13.8716 | 37.78
2021-03-05 22:30 | 44260.9375 | 0 | 12.8045 | 37.78
2021-03-05 23:00 | 44260.9583 | 0 | 11.9527 | 37.78
2021-03-05 23:30 | 44260.9792 | 0 | 11.5643 | 37.78
2021-03-06 | 44261 | 0 | 10.9203 | 37.78
2021-03-06 00:30 | 44261.0208 | 0 | 10.3757 | 37.78
2021-03-06 01:00 | 44261.0417 | 0 | 10.0467 | 37.78
2021-03-06 01:30 | 44261.0625 | 0 | 9.8499 | 37.78
2021-03-06 02:00 | 44261.0833 | 0 | 9.6647 | 37.78
2021-03-06 02:30 | 44261.1042 | 0 | 9.4064 | 37.78
2021-03-06 03:00 | 44261.125 | 0 | 9.2767 | 37.78
2021-03-06 03:30 | 44261.1458 | 0 | 9.2554 | 37.78
2021-03-06 04:00 | 44261.1667 | 0 | 9.2597 | 37.78
2021-03-06 04:30 | 44261.1875 | 0 | 9.3934 | 37.78
2021-03-06 05:00 | 44261.2083 | 0 | 9.536 | 37.78
2021-03-06 05:30 | 44261.2292 | 0 | 9.5633 | 37.78
2021-03-06 06:00 | 44261.25 | 0 | 9.7023 | 37.78
2021-03-06 06:30 | 44261.2708 | 0 | 9.628 | 37.78
2021-03-06 07:00 | 44261.2917 | 0 | 10.3089 | 37.78
2021-03-06 07:30 | 44261.3125 | 0 | 9.789 | 37.78
2021-03-06 08:00 | 44261.3333 | 0 | 9.9004 | 37.78
2021-03-06 08:30 | 44261.3542 | 0 | 10.3505 | 37.78
2021-03-06 09:00 | 44261.375 | 0 | 10.7819 | 37.78
2021-03-06 09:30 | 44261.3958 | 0 | 10.9663 | 37.78
2021-03-06 10:00 | 44261.4167 | 0 | 10.8901 | 37.78
2021-03-06 10:30 | 44261.4375 | 0 | 11.4168 | 37.78
2021-03-06 11:00 | 44261.4583 | 0 | 10.7696 | 37.78
2021-03-06 11:30 | 44261.4792 | 0 | 9.7863 | 37.78
2021-03-06 12:00 | 44261.5 | 0 | 10.6269 | 37.78
2021-03-06 12:30 | 44261.5208 | 0 | 11.4667 | 37.78
2021-03-06 13:00 | 44261.5417 | 0 | 12.2182 | 37.78
2021-03-06 13:30 | 44261.5625 | 0 | 11.9745 | 37.78
2021-03-06 14:00 | 44261.5833 | 0 | 11.4005 | 37.78
2021-03-06 14:30 | 44261.6042 | 0 | 12.419 | 37.78
2021-03-06 15:00 | 44261.625 | 0 | 12.7244 | 37.78
2021-03-06 15:30 | 44261.6458 | 0 | 11.4878 | 37.78
2021-03-06 16:00 | 44261.6667 | 0 | 11.9328 | 37.78
2021-03-06 16:30 | 44261.6875 | 0 | 12.6452 | 37.78
2021-03-06 17:00 | 44261.7083 | 0 | 12.6313 | 37.78
2021-03-06 17:30 | 44261.7292 | 0 | 12.7004 | 37.78
2021-03-06 18:00 | 44261.75 | 0 | 12.9604 | 37.78
2021-03-06 18:30 | 44261.7708 | 0 | 13.2223 | 37.78
2021-03-06 19:00 | 44261.7917 | 0 | 13.0631 | 37.78
2021-03-06 19:30 | 44261.8125 | 0 | 12.8562 | 37.78
2021-03-06 20:00 | 44261.8333 | 0 | 12.6983 | 37.78
2021-03-06 20:30 | 44261.8542 | 0 | 12.1294 | 37.78
2021-03-06 21:00 | 44261.875 | 0 | 11.8065 | 37.78
2021-03-06 21:30 | 44261.8958 | 0 | 11.479 | 37.78
2021-03-06 22:00 | 44261.9167 | 0 | 11.1378 | 37.78
2021-03-06 22:30 | 44261.9375 | 0 | 10.6264 | 37.78
2021-03-06 23:00 | 44261.9583 | 0 | 10.2681 | 37.78
2021-03-06 23:30 | 44261.9792 | 0 | 9.7829 | 37.78
2021-03-07 | 44262 | 0 | 9.3648 | 37.78
2021-03-07 00:30 | 44262.0208 | 0 | 9.0197 | 37.78
2021-03-07 01:00 | 44262.0417 | 0 | 8.9054 | 37.78
2021-03-07 01:30 | 44262.0625 | 0 | 8.6433 | 37.78
2021-03-07 02:00 | 44262.0833 | 0 | 8.6603 | 37.78
2021-03-07 02:30 | 44262.1042 | 0 | 8.5914 | 37.78
2021-03-07 03:00 | 44262.125 | 0 | 8.4194 | 37.78
2021-03-07 03:30 | 44262.1458 | 0 | 8.3524 | 37.78
2021-03-07 04:00 | 44262.1667 | 0 | 8.3198 | 37.78
2021-03-07 04:30 | 44262.1875 | 0 | 8.3564 | 37.78
2021-03-07 05:00 | 44262.2083 | 0 | 8.3992 | 37.78
2021-03-07 05:30 | 44262.2292 | 0 | 8.3091 | 37.78
2021-03-07 06:00 | 44262.25 | 0 | 8.3747 | 37.78
2021-03-07 06:30 | 44262.2708 | 0 | 8.5338 | 37.78
2021-03-07 07:00 | 44262.2917 | 0 | 8.7706 | 37.78
2021-03-07 07:30 | 44262.3125 | 0 | 9.436 | 37.78
2021-03-07 08:00 | 44262.3333 | 0 | 9.605 | 37.78
2021-03-07 08:30 | 44262.3542 | 0 | 8.8664 | 37.78
2021-03-07 09:00 | 44262.375 | 0 | 8.3165 | 37.78
2021-03-07 09:30 | 44262.3958 | 0 | 9.6191 | 37.78
2021-03-07 10:00 | 44262.4167 | 0 | 8.9098 | 37.78
2021-03-07 10:30 | 44262.4375 | 0 | 9.7394 | 37.78
2021-03-07 11:00 | 44262.4583 | 0 | 11.0874 | 37.78
2021-03-07 11:30 | 44262.4792 | 0 | 10.5297 | 37.78
2021-03-07 12:00 | 44262.5 | 0 | 8.8851 | 37.78
2021-03-07 12:30 | 44262.5208 | 0 | 9.1143 | 37.78
2021-03-07 13:00 | 44262.5417 | 0 | 9.22 | 37.78
2021-03-07 13:30 | 44262.5625 | 0 | 9.733 | 37.78
2021-03-07 14:00 | 44262.5833 | 0 | 10.3304 | 37.78
2021-03-07 14:30 | 44262.6042 | 0 | 11.2147 | 37.78
2021-03-07 15:00 | 44262.625 | 0 | 11.7495 | 37.78
2021-03-07 15:30 | 44262.6458 | 0 | 12.7525 | 37.78
2021-03-07 16:00 | 44262.6667 | 0 | 12.8244 | 37.78
2021-03-07 16:30 | 44262.6875 | 0 | 13.5851 | 37.78
2021-03-07 17:00 | 44262.7083 | 0 | 13.8462 | 37.78
2021-03-07 17:30 | 44262.7292 | 0 | 14.0122 | 37.78
2021-03-07 18:00 | 44262.75 | 0 | 13.9877 | 37.78
2021-03-07 18:30 | 44262.7708 | 0 | 14.355 | 37.78
2021-03-07 19:00 | 44262.7917 | 0 | 14.2196 | 37.78
2021-03-07 19:30 | 44262.8125 | 0 | 13.9913 | 37.78
2021-03-07 20:00 | 44262.8333 | 0 | 13.623 | 37.78
2021-03-07 20:30 | 44262.8542 | 0 | 13.0227 | 37.78
2021-03-07 21:00 | 44262.875 | 0 | 12.53 | 37.78
2021-03-07 21:30 | 44262.8958 | 0 | 12.1016 | 37.78
2021-03-07 22:00 | 44262.9167 | 0 | 11.6345 | 37.78
2021-03-07 22:30 | 44262.9375 | 0 | 10.7738 | 37.78
2021-03-07 23:00 | 44262.9583 | 0 | 10.2481 | 37.78
2021-03-07 23:30 | 44262.9792 | 0 | 9.8499 | 37.78
2021-03-08 | 44263 | 0 | 9.5359 | 37.78
2021-03-08 00:30 | 44263.0208 | 0 | 9.3389 | 37.78
2021-03-08 01:00 | 44263.0417 | 0 | 9.2742 | 37.78
2021-03-08 01:30 | 44263.0625 | 0 | 9.1104 | 37.78
2021-03-08 02:00 | 44263.0833 | 0 | 8.996 | 37.78
2021-03-08 02:30 | 44263.1042 | 0 | 8.7725 | 37.78
2021-03-08 03:00 | 44263.125 | 0 | 8.6847 | 37.78
2021-03-08 03:30 | 44263.1458 | 0 | 8.7668 | 37.78
2021-03-08 04:00 | 44263.1667 | 0 | 9.1033 | 37.78
2021-03-08 04:30 | 44263.1875 | 0 | 9.7053 | 37.78
2021-03-08 05:00 | 44263.2083 | 0 | 10.2799 | 37.78
2021-03-08 05:30 | 44263.2292 | 0 | 10.9032 | 37.78
2021-03-08 06:00 | 44263.25 | 0 | 11.7665 | 37.78
2021-03-08 06:30 | 44263.2708 | 0 | 12.6406 | 37.78
2021-03-08 07:00 | 44263.2917 | 0 | 13.1294 | 37.78
2021-03-08 07:30 | 44263.3125 | 0 | 13.1256 | 37.78
2021-03-08 08:00 | 44263.3333 | 0 | 13.5508 | 37.78
2021-03-08 08:30 | 44263.3542 | 0 | 13.2692 | 37.78
2021-03-08 09:00 | 44263.375 | 0 | 13.6569 | 37.78
2021-03-08 09:30 | 44263.3958 | 0 | 13.941 | 37.78
2021-03-08 10:00 | 44263.4167 | 0 | 13.8827 | 37.78
2021-03-08 10:30 | 44263.4375 | 0 | 14.1014 | 37.78
2021-03-08 11:00 | 44263.4583 | 0 | 13.7873 | 37.78
2021-03-08 11:30 | 44263.4792 | 0 | 14.088 | 37.78
2021-03-08 12:00 | 44263.5 | 0 | 14.2327 | 37.78
2021-03-08 12:30 | 44263.5208 | 0 | 14.563 | 37.78
2021-03-08 13:00 | 44263.5417 | 0 | 16.2544 | 37.78
2021-03-08 13:30 | 44263.5625 | 0 | 15.0271 | 37.78
2021-03-08 14:00 | 44263.5833 | 0 | 16.4531 | 37.78
2021-03-08 14:30 | 44263.6042 | 0 | 15.4787 | 37.78
2021-03-08 15:00 | 44263.625 | 0 | 16.7271 | 37.78
2021-03-08 15:30 | 44263.6458 | 0 | 17.2434 | 37.78
2021-03-08 16:00 | 44263.6667 | 0 | 17.287 | 37.78
2021-03-08 16:30 | 44263.6875 | 0 | 17.0872 | 37.78
2021-03-08 17:00 | 44263.7083 | 0 | 16.9354 | 37.78
2021-03-08 17:30 | 44263.7292 | 0 | 17.0176 | 37.78
2021-03-08 18:00 | 44263.75 | 0 | 17.1765 | 37.78
2021-03-08 18:30 | 44263.7708 | 0 | 17.537 | 37.78
2021-03-08 19:00 | 44263.7917 | 0 | 17.2741 | 37.78
2021-03-08 19:30 | 44263.8125 | 0 | 17.0607 | 37.78
2021-03-08 20:00 | 44263.8333 | 0 | 16.4857 | 37.78
2021-03-08 20:30 | 44263.8542 | 0 | 15.8197 | 37.78
2021-03-08 21:00 | 44263.875 | 0 | 15.1817 | 37.78
2021-03-08 21:30 | 44263.8958 | 0 | 14.5369 | 37.78
2021-03-08 22:00 | 44263.9167 | 0 | 13.9388 | 37.78
2021-03-08 22:30 | 44263.9375 | 0 | 12.8181 | 37.78
2021-03-08 23:00 | 44263.9583 | 0 | 12.105 | 37.78
2021-03-08 23:30 | 44263.9792 | 0 | 11.7296 | 37.78
2021-03-09 | 44264 | 0 | 11.0117 | 37.78
2021-03-09 00:30 | 44264.0208 | 0 | 10.4901 | 37.78
2021-03-09 01:00 | 44264.0417 | 0 | 10.0324 | 37.78
2021-03-09 01:30 | 44264.0625 | 0 | 10.0274 | 37.78
2021-03-09 02:00 | 44264.0833 | 0 | 9.9616 | 37.78
2021-03-09 02:30 | 44264.1042 | 0 | 9.6674 | 37.78
2021-03-09 03:00 | 44264.125 | 0 | 9.6075 | 37.78
2021-03-09 03:30 | 44264.1458 | 0 | 9.5454 | 37.78
2021-03-09 04:00 | 44264.1667 | 0 | 9.9902 | 37.78
2021-03-09 04:30 | 44264.1875 | 0 | 10.4051 | 37.78
2021-03-09 05:00 | 44264.2083 | 0 | 11.0027 | 37.78
2021-03-09 05:30 | 44264.2292 | 0 | 11.8229 | 37.78
2021-03-09 06:00 | 44264.25 | 0 | 12.4789 | 37.78
2021-03-09 06:30 | 44264.2708 | 0 | 12.9151 | 37.78
2021-03-09 07:00 | 44264.2917 | 0 | 13.513 | 37.78
2021-03-09 07:30 | 44264.3125 | 0 | 13.8117 | 37.78
2021-03-09 08:00 | 44264.3333 | 0 | 13.6531 | 37.78
2021-03-09 08:30 | 44264.3542 | 0 | 14.3201 | 37.78
2021-03-09 09:00 | 44264.375 | 0 | 14.3239 | 37.78
2021-03-09 09:30 | 44264.3958 | 0 | 13.5782 | 37.78
2021-03-09 10:00 | 44264.4167 | 0 | 13.3666 | 37.78
2021-03-09 10:30 | 44264.4375 | 0 | 14.3259 | 37.78
2021-03-09 11:00 | 44264.4583 | 0 | 16.4431 | 37.78
2021-03-09 11:30 | 44264.4792 | 0 | 16.0104 | 37.78
2021-03-09 12:00 | 44264.5 | 0 | 15.9475 | 37.78
2021-03-09 12:30 | 44264.5208 | 0 | 15.1758 | 37.78
2021-03-09 13:00 | 44264.5417 | 0 | 15.4978 | 37.78
2021-03-09 13:30 | 44264.5625 | 0 | 16.0132 | 37.78
2021-03-09 14:00 | 44264.5833 | 0 | 15.634 | 37.78
2021-03-09 14:30 | 44264.6042 | 0 | 16.1976 | 37.78
2021-03-09 15:00 | 44264.625 | 0 | 16.5877 | 37.78
2021-03-09 15:30 | 44264.6458 | 0 | 17.4473 | 37.78
2021-03-09 16:00 | 44264.6667 | 0 | 17.9587 | 37.78
2021-03-09 16:30 | 44264.6875 | 0 | 18.522 | 37.78
2021-03-09 17:00 | 44264.7083 | 0 | 18.6775 | 37.78
2021-03-09 17:30 | 44264.7292 | 0 | 19.0238 | 37.78
2021-03-09 18:00 | 44264.75 | 0 | 18.7855 | 37.78
2021-03-09 18:30 | 44264.7708 | 0 | 19.3403 | 37.78
2021-03-09 19:00 | 44264.7917 | 0 | 18.8344 | 37.78
2021-03-09 19:30 | 44264.8125 | 0 | 18.4374 | 37.78
2021-03-09 20:00 | 44264.8333 | 0 | 17.7264 | 37.78
2021-03-09 20:30 | 44264.8542 | 0 | 17.0654 | 37.78
2021-03-09 21:00 | 44264.875 | 0 | 16.1874 | 37.78
2021-03-09 21:30 | 44264.8958 | 0 | 15.4275 | 37.78
2021-03-09 22:00 | 44264.9167 | 0 | 14.3376 | 37.78
2021-03-09 22:30 | 44264.9375 | 0 | 13.3647 | 37.78
2021-03-09 23:00 | 44264.9583 | 0 | 12.7488 | 37.78
2021-03-09 23:30 | 44264.9792 | 0 | 12.207 | 37.78
2021-03-10 | 44265 | 0 | 11.4069 | 37.78
2021-03-10 00:30 | 44265.0208 | 0 | 10.9193 | 37.78
2021-03-10 01:00 | 44265.0417 | 0 | 10.7506 | 37.78
2021-03-10 01:30 | 44265.0625 | 0 | 10.3649 | 37.78
2021-03-10 02:00 | 44265.0833 | 0 | 10.2397 | 37.78
2021-03-10 02:30 | 44265.1042 | 0 | 10.0457 | 37.78
2021-03-10 03:00 | 44265.125 | 0 | 9.8684 | 37.78
2021-03-10 03:30 | 44265.1458 | 0 | 9.7533 | 37.78
2021-03-10 04:00 | 44265.1667 | 0 | 10.0341 | 37.78
2021-03-10 04:30 | 44265.1875 | 0 | 10.2109 | 37.78
2021-03-10 05:00 | 44265.2083 | 0 | 10.7479 | 37.78
2021-03-10 05:30 | 44265.2292 | 0 | 11.3773 | 37.78
2021-03-10 06:00 | 44265.25 | 0 | 12.0504 | 37.78
2021-03-10 06:30 | 44265.2708 | 0 | 12.583 | 37.78
2021-03-10 07:00 | 44265.2917 | 0 | 12.8991 | 37.78
2021-03-10 07:30 | 44265.3125 | 0 | 13.8537 | 37.78
2021-03-10 08:00 | 44265.3333 | 0 | 13.8782 | 37.78
2021-03-10 08:30 | 44265.3542 | 0 | 13.4351 | 37.78
2021-03-10 09:00 | 44265.375 | 0 | 13.9236 | 37.78
2021-03-10 09:30 | 44265.3958 | 0 | 14.415 | 37.78
2021-03-10 10:00 | 44265.4167 | 0 | 15.2686 | 37.78
2021-03-10 10:30 | 44265.4375 | 0 | 14.8062 | 37.78
2021-03-10 11:00 | 44265.4583 | 0 | 15.1684 | 37.78
2021-03-10 11:30 | 44265.4792 | 0 | 16.977 | 37.78
2021-03-10 12:00 | 44265.5 | 0 | 15.523 | 37.78
2021-03-10 12:30 | 44265.5208 | 0 | 15.5722 | 37.78
2021-03-10 13:00 | 44265.5417 | 0 | 16.1716 | 37.78
2021-03-10 13:30 | 44265.5625 | 0 | 16.9696 | 37.78
2021-03-10 14:00 | 44265.5833 | 0 | 17.4188 | 37.78
2021-03-10 14:30 | 44265.6042 | 0 | 17.1233 | 37.78
2021-03-10 15:00 | 44265.625 | 0 | 17.6216 | 37.78
2021-03-10 15:30 | 44265.6458 | 0 | 18.4448 | 37.78
2021-03-10 16:00 | 44265.6667 | 0 | 18.708 | 37.78
2021-03-10 16:30 | 44265.6875 | 0 | 19.3657 | 37.78
2021-03-10 17:00 | 44265.7083 | 0 | 18.4777 | 37.78
2021-03-10 17:30 | 44265.7292 | 0 | 18.6615 | 37.78
2021-03-10 18:00 | 44265.75 | 0 | 18.6964 | 37.78
2021-03-10 18:30 | 44265.7708 | 0 | 19.4762 | 37.78
2021-03-10 19:00 | 44265.7917 | 0 | 19.3223 | 37.78
2021-03-10 19:30 | 44265.8125 | 0 | 18.7545 | 37.78
2021-03-10 20:00 | 44265.8333 | 0 | 18.3057 | 37.78
2021-03-10 20:30 | 44265.8542 | 0 | 17.5867 | 37.78
2021-03-10 21:00 | 44265.875 | 0 | 16.7205 | 37.78
2021-03-10 21:30 | 44265.8958 | 0 | 15.7988 | 37.78
2021-03-10 22:00 | 44265.9167 | 0 | 14.7168 | 37.78
2021-03-10 22:30 | 44265.9375 | 0 | 13.2972 | 37.78
2021-03-10 23:00 | 44265.9583 | 0 | 12.7117 | 37.78
2021-03-10 23:30 | 44265.9792 | 0 | 11.9168 | 37.78
2021-03-11 | 44266 | 0 | 11.1329 | 37.78
2021-03-11 00:30 | 44266.0208 | 0 | 10.7743 | 37.78
2021-03-11 01:00 | 44266.0417 | 0 | 10.5356 | 37.78
2021-03-11 01:30 | 44266.0625 | 0 | 10.4212 | 37.78
2021-03-11 02:00 | 44266.0833 | 0 | 10.1153 | 37.78
2021-03-11 02:30 | 44266.1042 | 0 | 10.0233 | 37.78
2021-03-11 03:00 | 44266.125 | 0 | 9.8684 | 37.78
2021-03-11 03:30 | 44266.1458 | 0 | 9.9867 | 37.78
2021-03-11 04:00 | 44266.1667 | 0 | 10.1825 | 37.78
2021-03-11 04:30 | 44266.1875 | 0 | 10.5714 | 37.78
2021-03-11 05:00 | 44266.2083 | 0 | 11.1227 | 37.78
2021-03-11 05:30 | 44266.2292 | 0 | 11.7782 | 37.78
2021-03-11 06:00 | 44266.25 | 0 | 12.6051 | 37.78
2021-03-11 06:30 | 44266.2708 | 0 | 13.2103 | 37.78
2021-03-11 07:00 | 44266.2917 | 0 | 14.0213 | 37.78
2021-03-11 07:30 | 44266.3125 | 0 | 14.6752 | 37.78
2021-03-11 08:00 | 44266.3333 | 0 | 14.5657 | 37.78
2021-03-11 08:30 | 44266.3542 | 0 | 14.4638 | 37.78
2021-03-11 09:00 | 44266.375 | 0 | 14.3171 | 37.78
2021-03-11 09:30 | 44266.3958 | 0 | 15.6228 | 37.78
2021-03-11 10:00 | 44266.4167 | 0 | 14.4172 | 37.78
2021-03-11 10:30 | 44266.4375 | 0 | 15.6892 | 37.78
2021-03-11 11:00 | 44266.4583 | 0 | 16.1886 | 37.78
2021-03-11 11:30 | 44266.4792 | 0 | 15.4764 | 37.78
2021-03-11 12:00 | 44266.5 | 0 | 15.5035 | 37.78
2021-03-11 12:30 | 44266.5208 | 0 | 16.0086 | 37.78
2021-03-11 13:00 | 44266.5417 | 0 | 15.8215 | 37.78
2021-03-11 13:30 | 44266.5625 | 0 | 15.7356 | 37.78
2021-03-11 14:00 | 44266.5833 | 0 | 15.2009 | 37.78
2021-03-11 14:30 | 44266.6042 | 0 | 14.8205 | 37.78
2021-03-11 15:00 | 44266.625 | 0 | 14.5027 | 37.78
2021-03-11 15:30 | 44266.6458 | 0 | 14.6243 | 37.78
2021-03-11 16:00 | 44266.6667 | 0 | 14.5509 | 37.78
2021-03-11 16:30 | 44266.6875 | 0 | 14.8861 | 37.78
2021-03-11 17:00 | 44266.7083 | 0 | 15.2112 | 37.78
2021-03-11 17:30 | 44266.7292 | 0 | 15.4144 | 37.78
2021-03-11 18:00 | 44266.75 | 0 | 15.6034 | 37.78
2021-03-11 18:30 | 44266.7708 | 0 | 16.0274 | 37.78
2021-03-11 19:00 | 44266.7917 | 0 | 15.8732 | 37.78
2021-03-11 19:30 | 44266.8125 | 0 | 15.6963 | 37.78
2021-03-11 20:00 | 44266.8333 | 0 | 15.2207 | 37.78
2021-03-11 20:30 | 44266.8542 | 0 | 14.7722 | 37.78
2021-03-11 21:00 | 44266.875 | 0 | 14.3596 | 37.78
2021-03-11 21:30 | 44266.8958 | 0 | 13.7317 | 37.78
2021-03-11 22:00 | 44266.9167 | 0 | 12.9226 | 37.78
2021-03-11 22:30 | 44266.9375 | 0 | 11.893 | 37.78
2021-03-11 23:00 | 44266.9583 | 0 | 11.2954 | 37.78
2021-03-11 23:30 | 44266.9792 | 0 | 10.6969 | 37.78
2021-03-12 | 44267 | 0 | 9.9311 | 37.78
2021-03-12 00:30 | 44267.0208 | 0 | 9.5753 | 37.78
2021-03-12 01:00 | 44267.0417 | 0 | 9.4034 | 37.78
2021-03-12 01:30 | 44267.0625 | 0 | 9.3547 | 37.78
2021-03-12 02:00 | 44267.0833 | 0 | 9.3105 | 37.78
2021-03-12 02:30 | 44267.1042 | 0 | 9.1588 | 37.78
2021-03-12 03:00 | 44267.125 | 0 | 8.8897 | 37.78
2021-03-12 03:30 | 44267.1458 | 0 | 9.1157 | 37.78
2021-03-12 04:00 | 44267.1667 | 0 | 9.4458 | 37.78
2021-03-12 04:30 | 44267.1875 | 0 | 9.8866 | 37.78
2021-03-12 05:00 | 44267.2083 | 0 | 10.3153 | 37.78
2021-03-12 05:30 | 44267.2292 | 0 | 11.1405 | 37.78
2021-03-12 06:00 | 44267.25 | 0 | 11.7958 | 37.78
2021-03-12 06:30 | 44267.2708 | 0 | 12.4174 | 37.78
2021-03-12 07:00 | 44267.2917 | 0 | 12.4494 | 37.78
2021-03-12 07:30 | 44267.3125 | 0 | 12.5237 | 37.78
2021-03-12 08:00 | 44267.3333 | 0 | 12.8288 | 37.78
2021-03-12 08:30 | 44267.3542 | 0 | 12.831 | 37.78
2021-03-12 09:00 | 44267.375 | 0 | 12.9628 | 37.78
2021-03-12 09:30 | 44267.3958 | 0 | 13.4489 | 37.78
2021-03-12 10:00 | 44267.4167 | 0 | 14.3738 | 37.78
2021-03-12 10:30 | 44267.4375 | 0 | 15.5811 | 37.78
2021-03-12 11:00 | 44267.4583 | 0 | 14.9449 | 37.78
2021-03-12 11:30 | 44267.4792 | 0 | 16.0862 | 37.78
2021-03-12 12:00 | 44267.5 | 0 | 14.5253 | 37.78
2021-03-12 12:30 | 44267.5208 | 0 | 14.174 | 37.78
2021-03-12 13:00 | 44267.5417 | 0 | 12.8519 | 37.78
2021-03-12 13:30 | 44267.5625 | 0 | 15.2584 | 37.78
2021-03-12 14:00 | 44267.5833 | 0 | 15.2268 | 37.78
2021-03-12 14:30 | 44267.6042 | 0 | 14.7228 | 37.78
2021-03-12 15:00 | 44267.625 | 0 | 14.6868 | 37.78
2021-03-12 15:30 | 44267.6458 | 0 | 13.8457 | 37.78
2021-03-12 16:00 | 44267.6667 | 0 | 15.2274 | 37.78
2021-03-12 16:30 | 44267.6875 | 0 | 15.7945 | 37.78
2021-03-12 17:00 | 44267.7083 | 0 | 15.9888 | 37.78
2021-03-12 17:30 | 44267.7292 | 0 | 15.6972 | 37.78
2021-03-12 18:00 | 44267.75 | 0 | 15.5807 | 37.78
2021-03-12 18:30 | 44267.7708 | 0 | 15.8934 | 37.78
2021-03-12 19:00 | 44267.7917 | 0 | 15.7392 | 37.78
2021-03-12 19:30 | 44267.8125 | 0 | 15.6083 | 37.78
2021-03-12 20:00 | 44267.8333 | 0 | 15.0901 | 37.78
2021-03-12 20:30 | 44267.8542 | 0 | 14.2975 | 37.78
2021-03-12 21:00 | 44267.875 | 0 | 13.8366 | 37.78
2021-03-12 21:30 | 44267.8958 | 0 | 13.5151 | 37.78
2021-03-12 22:00 | 44267.9167 | 0 | 12.9571 | 37.78
2021-03-12 22:30 | 44267.9375 | 0 | 11.974 | 37.78
2021-03-12 23:00 | 44267.9583 | 0 | 11.3833 | 37.78
2021-03-12 23:30 | 44267.9792 | 0 | 10.9314 | 37.78
2021-03-13 | 44268 | 0 | 10.2355 | 37.78
2021-03-13 00:30 | 44268.0208 | 0 | 9.7952 | 37.78
2021-03-13 01:00 | 44268.0417 | 0 | 9.5753 | 37.78
2021-03-13 01:30 | 44268.0625 | 0 | 9.574 | 37.78
2021-03-13 02:00 | 44268.0833 | 0 | 9.3152 | 37.78
2021-03-13 02:30 | 44268.1042 | 0 | 9.1949 | 37.78
2021-03-13 03:00 | 44268.125 | 0 | 9.1104 | 37.78
2021-03-13 03:30 | 44268.1458 | 0 | 9.1104 | 37.78
2021-03-13 04:00 | 44268.1667 | 0 | 9.1552 | 37.78
2021-03-13 04:30 | 44268.1875 | 0 | 9.3898 | 37.78
2021-03-13 05:00 | 44268.2083 | 0 | 9.6279 | 37.78
2021-03-13 05:30 | 44268.2292 | 0 | 9.624 | 37.78
2021-03-13 06:00 | 44268.25 | 0 | 9.6626 | 37.78
2021-03-13 06:30 | 44268.2708 | 0 | 9.8874 | 37.78
2021-03-13 07:00 | 44268.2917 | 0 | 10.1275 | 37.78
2021-03-13 07:30 | 44268.3125 | 0 | 10.1453 | 37.78
2021-03-13 08:00 | 44268.3333 | 0 | 11.3718 | 37.78
2021-03-13 08:30 | 44268.3542 | 0 | 11.9612 | 37.78
2021-03-13 09:00 | 44268.375 | 0 | 11.3323 | 37.78
2021-03-13 09:30 | 44268.3958 | 0 | 11.7753 | 37.78
2021-03-13 10:00 | 44268.4167 | 0 | 11.3325 | 37.78
2021-03-13 10:30 | 44268.4375 | 0 | 10.6799 | 37.78
2021-03-13 11:00 | 44268.4583 | 0 | 9.5578 | 37.78
2021-03-13 11:30 | 44268.4792 | 0 | 10.7023 | 37.78
2021-03-13 12:00 | 44268.5 | 0 | 11.3387 | 37.78
2021-03-13 12:30 | 44268.5208 | 0 | 11.5701 | 37.78
2021-03-13 13:00 | 44268.5417 | 0 | 11.1549 | 37.78
2021-03-13 13:30 | 44268.5625 | 0 | 11.4583 | 37.78
2021-03-13 14:00 | 44268.5833 | 0 | 12.2421 | 37.78
2021-03-13 14:30 | 44268.6042 | 0 | 13.6364 | 37.78
2021-03-13 15:00 | 44268.625 | 0 | 13.1316 | 37.78
2021-03-13 15:30 | 44268.6458 | 0 | 13.1769 | 37.78
2021-03-13 16:00 | 44268.6667 | 0 | 13.6263 | 37.78
2021-03-13 16:30 | 44268.6875 | 0 | 14.2089 | 37.78
2021-03-13 17:00 | 44268.7083 | 0 | 14.5482 | 37.78
2021-03-13 17:30 | 44268.7292 | 0 | 14.5819 | 37.78
2021-03-13 18:00 | 44268.75 | 0 | 14.5027 | 37.78
2021-03-13 18:30 | 44268.7708 | 0 | 14.8092 | 37.78
2021-03-13 19:00 | 44268.7917 | 0 | 14.6 | 37.78
2021-03-13 19:30 | 44268.8125 | 0 | 14.3328 | 37.78
2021-03-13 20:00 | 44268.8333 | 0 | 13.898 | 37.78
2021-03-13 20:30 | 44268.8542 | 0 | 13.4591 | 37.78
2021-03-13 21:00 | 44268.875 | 0 | 13.0123 | 37.78
2021-03-13 21:30 | 44268.8958 | 0 | 12.7296 | 37.78
2021-03-13 22:00 | 44268.9167 | 0 | 12.1473 | 37.78
2021-03-13 22:30 | 44268.9375 | 0 | 11.368 | 37.78
2021-03-13 23:00 | 44268.9583 | 0 | 10.8915 | 37.78
2021-03-13 23:30 | 44268.9792 | 0 | 10.3076 | 37.78
2021-03-14 | 44269 | 0 | 9.8823 | 37.78
2021-03-14 00:30 | 44269.0208 | 0 | 9.553 | 37.78
2021-03-14 01:00 | 44269.0417 | 0 | 9.2978 | 37.78
2021-03-14 01:30 | 44269.0625 | 0 | 9.211 | 37.78
2021-03-14 02:00 | 44269.0833 | 0 | 9.0407 | 37.78
2021-03-14 02:30 | 44269.1042 | 0 | 8.8232 | 37.78
2021-03-14 03:00 | 44269.125 | 0 | 8.6576 | 37.78
2021-03-14 03:30 | 44269.1458 | 0 | 8.6554 | 37.78
2021-03-14 04:00 | 44269.1667 | 0 | 8.5507 | 37.78
2021-03-14 04:30 | 44269.1875 | 0 | 8.4864 | 37.78
2021-03-14 05:00 | 44269.2083 | 0 | 8.5324 | 37.78
2021-03-14 05:30 | 44269.2292 | 0 | 8.5271 | 37.78
2021-03-14 06:00 | 44269.25 | 0 | 8.5114 | 37.78
2021-03-14 06:30 | 44269.2708 | 0 | 8.5807 | 37.78
2021-03-14 07:00 | 44269.2917 | 0 | 8.7483 | 37.78
2021-03-14 07:30 | 44269.3125 | 0 | 8.8241 | 37.78
2021-03-14 08:00 | 44269.3333 | 0 | 8.9581 | 37.78
2021-03-14 08:30 | 44269.3542 | 0 | 9.416 | 37.78
2021-03-14 09:00 | 44269.375 | 0 | 10.001 | 37.78
2021-03-14 09:30 | 44269.3958 | 0 | 10.1719 | 37.78
2021-03-14 10:00 | 44269.4167 | 0 | 9.7257 | 37.78
2021-03-14 10:30 | 44269.4375 | 0 | 10.7889 | 37.78
2021-03-14 11:00 | 44269.4583 | 0 | 10.5577 | 37.78
2021-03-14 11:30 | 44269.4792 | 0 | 10.3704 | 37.78
2021-03-14 12:00 | 44269.5 | 0 | 10.762 | 37.78
2021-03-14 12:30 | 44269.5208 | 0 | 10.8692 | 37.78
2021-03-14 13:00 | 44269.5417 | 0 | 11.4428 | 37.78
2021-03-14 13:30 | 44269.5625 | 0 | 11.967 | 37.78
2021-03-14 14:00 | 44269.5833 | 0 | 12.5798 | 37.78
2021-03-14 14:30 | 44269.6042 | 0 | 13.2499 | 37.78
2021-03-14 15:00 | 44269.625 | 0 | 13.8538 | 37.78
2021-03-14 15:30 | 44269.6458 | 0 | 14.4159 | 37.78
2021-03-14 16:00 | 44269.6667 | 0 | 14.9603 | 37.78
2021-03-14 16:30 | 44269.6875 | 0 | 15.7645 | 37.78
2021-03-14 17:00 | 44269.7083 | 0 | 16.4188 | 37.78
2021-03-14 17:30 | 44269.7292 | 0 | 16.7239 | 37.78
2021-03-14 18:00 | 44269.75 | 0 | 17.0994 | 37.78
2021-03-14 18:30 | 44269.7708 | 0 | 17.3709 | 37.78
2021-03-14 19:00 | 44269.7917 | 0 | 17.1567 | 37.78
2021-03-14 19:30 | 44269.8125 | 0 | 16.8743 | 37.78
2021-03-14 20:00 | 44269.8333 | 0 | 16.2993 | 37.78
2021-03-14 20:30 | 44269.8542 | 0 | 15.7174 | 37.78
2021-03-14 21:00 | 44269.875 | 0 | 14.9948 | 37.78
2021-03-14 21:30 | 44269.8958 | 0 | 14.3198 | 37.78
2021-03-14 22:00 | 44269.9167 | 0 | 13.5486 | 37.78
2021-03-14 22:30 | 44269.9375 | 0 | 12.4063 | 37.78
2021-03-14 23:00 | 44269.9583 | 0 | 11.6487 | 37.78
2021-03-14 23:30 | 44269.9792 | 0 | 11.1209 | 37.78
2021-03-15 | 44270 | 0 | 10.5892 | 37.78
2021-03-15 00:30 | 44270.0208 | 0 | 10.1993 | 37.78
2021-03-15 01:00 | 44270.0417 | 0 | 9.9604 | 37.78
2021-03-15 01:30 | 44270.0625 | 0 | 9.8311 | 37.78
2021-03-15 02:00 | 44270.0833 | 0 | 9.8092 | 37.78
2021-03-15 02:30 | 44270.1042 | 0 | 9.6871 | 37.78
2021-03-15 03:00 | 44270.125 | 0 | 9.5584 | 37.78
2021-03-15 03:30 | 44270.1458 | 0 | 9.7149 | 37.78
2021-03-15 04:00 | 44270.1667 | 0 | 10.127 | 37.78
2021-03-15 04:30 | 44270.1875 | 0 | 10.5486 | 37.78
2021-03-15 05:00 | 44270.2083 | 0 | 11.0191 | 37.78
2021-03-15 05:30 | 44270.2292 | 0 | 11.8056 | 37.78
2021-03-15 06:00 | 44270.25 | 0 | 12.8215 | 37.78
2021-03-15 06:30 | 44270.2708 | 0 | 13.7072 | 37.78
2021-03-15 07:00 | 44270.2917 | 0 | 14.4984 | 37.78
2021-03-15 07:30 | 44270.3125 | 0 | 15.1648 | 37.78
2021-03-15 08:00 | 44270.3333 | 0 | 15.1456 | 37.78
2021-03-15 08:30 | 44270.3542 | 0 | 15.17 | 37.78
2021-03-15 09:00 | 44270.375 | 0 | 15.166 | 37.78
2021-03-15 09:30 | 44270.3958 | 0 | 15.2721 | 37.78
2021-03-15 10:00 | 44270.4167 | 0 | 14.9097 | 37.78
2021-03-15 10:30 | 44270.4375 | 0 | 14.5449 | 37.78
2021-03-15 11:00 | 44270.4583 | 0 | 13.7571 | 37.78
2021-03-15 11:30 | 44270.4792 | 0 | 14.3598 | 37.78
2021-03-15 12:00 | 44270.5 | 0 | 14.344 | 37.78
2021-03-15 12:30 | 44270.5208 | 0 | 13.4673 | 37.78
2021-03-15 13:00 | 44270.5417 | 0 | 13.7559 | 37.78
2021-03-15 13:30 | 44270.5625 | 0 | 13.6069 | 37.78
2021-03-15 14:00 | 44270.5833 | 0 | 14.3475 | 37.78
2021-03-15 14:30 | 44270.6042 | 0 | 14.0929 | 37.78
2021-03-15 15:00 | 44270.625 | 0 | 13.6676 | 37.78
2021-03-15 15:30 | 44270.6458 | 0 | 13.7609 | 37.78
2021-03-15 16:00 | 44270.6667 | 0 | 13.9378 | 37.78
2021-03-15 16:30 | 44270.6875 | 0 | 14.2758 | 37.78
2021-03-15 17:00 | 44270.7083 | 0 | 14.3572 | 37.78
2021-03-15 17:30 | 44270.7292 | 0 | 14.4047 | 37.78
2021-03-15 18:00 | 44270.75 | 0 | 14.7422 | 37.78
2021-03-15 18:30 | 44270.7708 | 0 | 15.0726 | 37.78
2021-03-15 19:00 | 44270.7917 | 0 | 14.5317 | 37.78
2021-03-15 19:30 | 44270.8125 | 0 | 14.2391 | 37.78
2021-03-15 20:00 | 44270.8333 | 0 | 13.8436 | 37.78
2021-03-15 20:30 | 44270.8542 | 0 | 13.3449 | 37.78
2021-03-15 21:00 | 44270.875 | 0 | 12.7023 | 37.78
2021-03-15 21:30 | 44270.8958 | 0 | 12.4452 | 37.78
2021-03-15 22:00 | 44270.9167 | 0 | 11.8316 | 37.78
2021-03-15 22:30 | 44270.9375 | 0 | 11.0124 | 37.78
2021-03-15 23:00 | 44270.9583 | 0 | 10.414 | 37.78
2021-03-15 23:30 | 44270.9792 | 0 | 9.8964 | 37.78
2021-03-16 | 44271 | 0 | 9.4189 | 37.78
2021-03-16 00:30 | 44271.0208 | 0 | 8.9525 | 37.78
2021-03-16 01:00 | 44271.0417 | 0 | 8.8871 | 37.78
2021-03-16 01:30 | 44271.0625 | 0 | 8.8611 | 37.78
2021-03-16 02:00 | 44271.0833 | 0 | 8.726 | 37.78
2021-03-16 02:30 | 44271.1042 | 0 | 8.6401 | 37.78
2021-03-16 03:00 | 44271.125 | 0 | 8.6651 | 37.78
2021-03-16 03:30 | 44271.1458 | 0 | 8.691 | 37.78
2021-03-16 04:00 | 44271.1667 | 0 | 8.9621 | 37.78
2021-03-16 04:30 | 44271.1875 | 0 | 9.251 | 37.78
2021-03-16 05:00 | 44271.2083 | 0 | 9.9778 | 37.78
2021-03-16 05:30 | 44271.2292 | 0 | 10.6499 | 37.78
2021-03-16 06:00 | 44271.25 | 0 | 11.3493 | 37.78
2021-03-16 06:30 | 44271.2708 | 0 | 12.3068 | 37.78
2021-03-16 07:00 | 44271.2917 | 0 | 12.9323 | 37.78
2021-03-16 07:30 | 44271.3125 | 0 | 13.1763 | 37.78
2021-03-16 08:00 | 44271.3333 | 0 | 13.1825 | 37.78
2021-03-16 08:30 | 44271.3542 | 0 | 13.3296 | 37.78
2021-03-16 09:00 | 44271.375 | 0 | 12.9527 | 37.78
2021-03-16 09:30 | 44271.3958 | 0 | 12.3724 | 37.78
2021-03-16 10:00 | 44271.4167 | 0 | 12.0001 | 37.78
2021-03-16 10:30 | 44271.4375 | 0 | 13.0272 | 37.78
2021-03-16 11:00 | 44271.4583 | 0 | 12.8623 | 37.78
2021-03-16 11:30 | 44271.4792 | 0 | 13.6237 | 37.78
2021-03-16 12:00 | 44271.5 | 0 | 14.0856 | 37.78
2021-03-16 12:30 | 44271.5208 | 0 | 14.119 | 37.78
2021-03-16 13:00 | 44271.5417 | 0 | 13.6493 | 37.78
2021-03-16 13:30 | 44271.5625 | 0 | 13.7766 | 37.78
2021-03-16 14:00 | 44271.5833 | 0 | 13.8558 | 37.78
2021-03-16 14:30 | 44271.6042 | 0 | 13.2548 | 37.78
2021-03-16 15:00 | 44271.625 | 0 | 13.1803 | 37.78
2021-03-16 15:30 | 44271.6458 | 0 | 13.3572 | 37.78
2021-03-16 16:00 | 44271.6667 | 0 | 13.4571 | 37.78
2021-03-16 16:30 | 44271.6875 | 0 | 13.747 | 37.78
2021-03-16 17:00 | 44271.7083 | 0 | 13.8002 | 37.78
2021-03-16 17:30 | 44271.7292 | 0 | 14.111 | 37.78
2021-03-16 18:00 | 44271.75 | 0 | 14.3139 | 37.78
2021-03-16 18:30 | 44271.7708 | 0 | 14.5654 | 37.78
2021-03-16 19:00 | 44271.7917 | 0 | 14.137 | 37.78
2021-03-16 19:30 | 44271.8125 | 0 | 13.8226 | 37.78
2021-03-16 20:00 | 44271.8333 | 0 | 13.43 | 37.78
2021-03-16 20:30 | 44271.8542 | 0 | 12.9319 | 37.78
2021-03-16 21:00 | 44271.875 | 0 | 12.542 | 37.78
2021-03-16 21:30 | 44271.8958 | 0 | 12.1141 | 37.78
2021-03-16 22:00 | 44271.9167 | 0 | 11.5212 | 37.78
2021-03-16 22:30 | 44271.9375 | 0 | 10.727 | 37.78
2021-03-16 23:00 | 44271.9583 | 0 | 10.1951 | 37.78
2021-03-16 23:30 | 44271.9792 | 0 | 9.6796 | 37.78
2021-03-17 | 44272 | 0 | 9.1794 | 37.78
2021-03-17 00:30 | 44272.0208 | 0 | 8.971 | 37.78
2021-03-17 01:00 | 44272.0417 | 0 | 8.8043 | 37.78
2021-03-17 01:30 | 44272.0625 | 0 | 8.6637 | 37.78
2021-03-17 02:00 | 44272.0833 | 0 | 8.6177 | 37.78
2021-03-17 02:30 | 44272.1042 | 0 | 8.3673 | 37.78
2021-03-17 03:00 | 44272.125 | 0 | 8.4641 | 37.78
2021-03-17 03:30 | 44272.1458 | 0 | 8.5351 | 37.78
2021-03-17 04:00 | 44272.1667 | 0 | 8.798 | 37.78
2021-03-17 04:30 | 44272.1875 | 0 | 9.1159 | 37.78
2021-03-17 05:00 | 44272.2083 | 0 | 9.7338 | 37.78
2021-03-17 05:30 | 44272.2292 | 0 | 10.4122 | 37.78
2021-03-17 06:00 | 44272.25 | 0 | 11.2004 | 37.78
2021-03-17 06:30 | 44272.2708 | 0 | 12.0964 | 37.78
2021-03-17 07:00 | 44272.2917 | 0 | 13.0391 | 37.78
2021-03-17 07:30 | 44272.3125 | 0 | 13.3354 | 37.78
2021-03-17 08:00 | 44272.3333 | 0 | 13.8187 | 37.78
2021-03-17 08:30 | 44272.3542 | 0 | 13.8409 | 37.78
2021-03-17 09:00 | 44272.375 | 0 | 13.7995 | 37.78
2021-03-17 09:30 | 44272.3958 | 0 | 13.5248 | 37.78
2021-03-17 10:00 | 44272.4167 | 0 | 13.1725 | 37.78
2021-03-17 10:30 | 44272.4375 | 0 | 13.7219 | 37.78
2021-03-17 11:00 | 44272.4583 | 0 | 14.0029 | 37.78
2021-03-17 11:30 | 44272.4792 | 0 | 13.9464 | 37.78
2021-03-17 12:00 | 44272.5 | 0 | 13.6464 | 37.78
2021-03-17 12:30 | 44272.5208 | 0 | 13.4305 | 37.78
2021-03-17 13:00 | 44272.5417 | 0 | 13.3984 | 37.78
2021-03-17 13:30 | 44272.5625 | 0 | 13.4481 | 37.78
2021-03-17 14:00 | 44272.5833 | 0 | 13.3692 | 37.78
2021-03-17 14:30 | 44272.6042 | 0 | 12.938 | 37.78
2021-03-17 15:00 | 44272.625 | 0 | 12.7109 | 37.78
2021-03-17 15:30 | 44272.6458 | 0 | 13.2788 | 37.78
2021-03-17 16:00 | 44272.6667 | 0 | 13.3327 | 37.78
2021-03-17 16:30 | 44272.6875 | 0 | 13.8261 | 37.78
2021-03-17 17:00 | 44272.7083 | 0 | 14.0038 | 37.78
2021-03-17 17:30 | 44272.7292 | 0 | 13.8727 | 37.78
2021-03-17 18:00 | 44272.75 | 0 | 14.1217 | 37.78
2021-03-17 18:30 | 44272.7708 | 0 | 14.43 | 37.78
2021-03-17 19:00 | 44272.7917 | 0 | 14.1934 | 37.78
2021-03-17 19:30 | 44272.8125 | 0 | 13.6872 | 37.78
2021-03-17 20:00 | 44272.8333 | 0 | 13.583 | 37.78
2021-03-17 20:30 | 44272.8542 | 0 | 12.99 | 37.78
2021-03-17 21:00 | 44272.875 | 0 | 12.3931 | 37.78
2021-03-17 21:30 | 44272.8958 | 0 | 11.966 | 37.78
2021-03-17 22:00 | 44272.9167 | 0 | 11.468 | 37.78
2021-03-17 22:30 | 44272.9375 | 0 | 10.553 | 37.78
2021-03-17 23:00 | 44272.9583 | 0 | 9.8973 | 37.78
2021-03-17 23:30 | 44272.9792 | 0 | 9.4811 | 37.78
2021-03-18 | 44273 | 0 | 9.0328 | 37.78
2021-03-18 00:30 | 44273.0208 | 0 | 8.5981 | 37.78
2021-03-18 01:00 | 44273.0417 | 0 | 8.5297 | 37.78
2021-03-18 01:30 | 44273.0625 | 0 | 8.3944 | 37.78
2021-03-18 02:00 | 44273.0833 | 0 | 8.2764 | 37.78
2021-03-18 02:30 | 44273.1042 | 0 | 8.267 | 37.78
2021-03-18 03:00 | 44273.125 | 0 | 8.1514 | 37.78
2021-03-18 03:30 | 44273.1458 | 0 | 8.3018 | 37.78
2021-03-18 04:00 | 44273.1667 | 0 | 8.6217 | 37.78
2021-03-18 04:30 | 44273.1875 | 0 | 8.9998 | 37.78
2021-03-18 05:00 | 44273.2083 | 0 | 9.5588 | 37.78
2021-03-18 05:30 | 44273.2292 | 0 | 10.1477 | 37.78
2021-03-18 06:00 | 44273.25 | 0 | 10.8938 | 37.78
2021-03-18 06:30 | 44273.2708 | 0 | 11.8476 | 37.78
2021-03-18 07:00 | 44273.2917 | 0 | 12.6492 | 37.78
2021-03-18 07:30 | 44273.3125 | 0 | 13.0723 | 37.78
2021-03-18 08:00 | 44273.3333 | 0 | 13.0457 | 37.78
2021-03-18 08:30 | 44273.3542 | 0 | 12.4276 | 37.78
2021-03-18 09:00 | 44273.375 | 0 | 12.0693 | 37.78
2021-03-18 09:30 | 44273.3958 | 0 | 12.4302 | 37.78
2021-03-18 10:00 | 44273.4167 | 0 | 11.0296 | 37.78
2021-03-18 10:30 | 44273.4375 | 0 | 11.6332 | 37.78
2021-03-18 11:00 | 44273.4583 | 0 | 12.5503 | 37.78
2021-03-18 11:30 | 44273.4792 | 0 | 13.4388 | 37.78
2021-03-18 12:00 | 44273.5 | 0 | 13.7658 | 37.78
2021-03-18 12:30 | 44273.5208 | 0 | 14.1643 | 37.78
2021-03-18 13:00 | 44273.5417 | 0 | 14.2862 | 37.78
2021-03-18 13:30 | 44273.5625 | 0 | 13.9219 | 37.78
2021-03-18 14:00 | 44273.5833 | 0 | 13.3327 | 37.78
2021-03-18 14:30 | 44273.6042 | 0 | 14.1353 | 37.78
2021-03-18 15:00 | 44273.625 | 0 | 14.2029 | 37.78
2021-03-18 15:30 | 44273.6458 | 0 | 14.7226 | 37.78
2021-03-18 16:00 | 44273.6667 | 0 | 14.4897 | 37.78
2021-03-18 16:30 | 44273.6875 | 0 | 14.2746 | 37.78
2021-03-18 17:00 | 44273.7083 | 0 | 14.4217 | 37.78
2021-03-18 17:30 | 44273.7292 | 0 | 14.7065 | 37.78
2021-03-18 18:00 | 44273.75 | 0 | 15.2206 | 37.78
2021-03-18 18:30 | 44273.7708 | 0 | 15.6925 | 37.78
2021-03-18 19:00 | 44273.7917 | 0 | 15.3385 | 37.78
2021-03-18 19:30 | 44273.8125 | 0 | 15.0324 | 37.78
2021-03-18 20:00 | 44273.8333 | 0 | 14.5476 | 37.78
2021-03-18 20:30 | 44273.8542 | 0 | 13.9111 | 37.78
2021-03-18 21:00 | 44273.875 | 0 | 13.3097 | 37.78
2021-03-18 21:30 | 44273.8958 | 0 | 12.8819 | 37.78
2021-03-18 22:00 | 44273.9167 | 0 | 12.2148 | 37.78
2021-03-18 22:30 | 44273.9375 | 0 | 11.2535 | 37.78
2021-03-18 23:00 | 44273.9583 | 0 | 10.4804 | 37.78
2021-03-18 23:30 | 44273.9792 | 0 | 10.057 | 37.78
2021-03-19 | 44274 | 0 | 9.5954 | 37.78
2021-03-19 00:30 | 44274.0208 | 0 | 9.2593 | 37.78
2021-03-19 01:00 | 44274.0417 | 0 | 9.1027 | 37.78
2021-03-19 01:30 | 44274.0625 | 0 | 8.8821 | 37.78
2021-03-19 02:00 | 44274.0833 | 0 | 8.7618 | 37.78
2021-03-19 02:30 | 44274.1042 | 0 | 8.6637 | 37.78
2021-03-19 03:00 | 44274.125 | 0 | 8.6454 | 37.78
2021-03-19 03:30 | 44274.1458 | 0 | 8.8338 | 37.78
2021-03-19 04:00 | 44274.1667 | 0 | 9.0251 | 37.78
2021-03-19 04:30 | 44274.1875 | 0 | 9.1999 | 37.78
2021-03-19 05:00 | 44274.2083 | 0 | 9.8859 | 37.78
2021-03-19 05:30 | 44274.2292 | 0 | 10.6217 | 37.78
2021-03-19 06:00 | 44274.25 | 0 | 11.0171 | 37.78
2021-03-19 06:30 | 44274.2708 | 0 | 11.5678 | 37.78
2021-03-19 07:00 | 44274.2917 | 0 | 12.0026 | 37.78
2021-03-19 07:30 | 44274.3125 | 0 | 12.8357 | 37.78
2021-03-19 08:00 | 44274.3333 | 0 | 13.1216 | 37.78
2021-03-19 08:30 | 44274.3542 | 0 | 12.2306 | 37.78
2021-03-19 09:00 | 44274.375 | 0 | 12.7417 | 37.78
2021-03-19 09:30 | 44274.3958 | 0 | 12.9528 | 37.78
2021-03-19 10:00 | 44274.4167 | 0 | 11.6654 | 37.78
2021-03-19 10:30 | 44274.4375 | 0 | 12.39 | 37.78
2021-03-19 11:00 | 44274.4583 | 0 | 12.8505 | 37.78
2021-03-19 11:30 | 44274.4792 | 0 | 13.2765 | 37.78
2021-03-19 12:00 | 44274.5 | 0 | 13.2584 | 37.78
2021-03-19 12:30 | 44274.5208 | 0 | 14.787 | 37.78
2021-03-19 13:00 | 44274.5417 | 0 | 16.0057 | 37.78
2021-03-19 13:30 | 44274.5625 | 0 | 15.1104 | 37.78
2021-03-19 14:00 | 44274.5833 | 0 | 15.6963 | 37.78
2021-03-19 14:30 | 44274.6042 | 0 | 15.23 | 37.78
2021-03-19 15:00 | 44274.625 | 0 | 15.3725 | 37.78
2021-03-19 15:30 | 44274.6458 | 0 | 15.3879 | 37.78
2021-03-19 16:00 | 44274.6667 | 0 | 16.1614 | 37.78
2021-03-19 16:30 | 44274.6875 | 0 | 16.5524 | 37.78
2021-03-19 17:00 | 44274.7083 | 0 | 16.0881 | 37.78
2021-03-19 17:30 | 44274.7292 | 0 | 15.7709 | 37.78
2021-03-19 18:00 | 44274.75 | 0 | 15.9875 | 37.78
2021-03-19 18:30 | 44274.7708 | 0 | 16.1849 | 37.78
2021-03-19 19:00 | 44274.7917 | 0 | 15.6832 | 37.78
2021-03-19 19:30 | 44274.8125 | 0 | 15.5532 | 37.78
2021-03-19 20:00 | 44274.8333 | 0 | 15.1741 | 37.78
2021-03-19 20:30 | 44274.8542 | 0 | 14.4853 | 37.78
2021-03-19 21:00 | 44274.875 | 0 | 13.9837 | 37.78
2021-03-19 21:30 | 44274.8958 | 0 | 13.4973 | 37.78
2021-03-19 22:00 | 44274.9167 | 0 | 12.9807 | 37.78
2021-03-19 22:30 | 44274.9375 | 0 | 11.994 | 37.78
2021-03-19 23:00 | 44274.9583 | 0 | 11.487 | 37.78
2021-03-19 23:30 | 44274.9792 | 0 | 10.7716 | 37.78
2021-03-20 | 44275 | 0 | 10.426 | 37.78
2021-03-20 00:30 | 44275.0208 | 0 | 9.8718 | 37.78
2021-03-20 01:00 | 44275.0417 | 0 | 9.659 | 37.78
2021-03-20 01:30 | 44275.0625 | 0 | 9.4466 | 37.78
2021-03-20 02:00 | 44275.0833 | 0 | 9.2124 | 37.78
2021-03-20 02:30 | 44275.1042 | 0 | 9.13 | 37.78
2021-03-20 03:00 | 44275.125 | 0 | 8.8938 | 37.78
2021-03-20 03:30 | 44275.1458 | 0 | 9.1117 | 37.78
2021-03-20 04:00 | 44275.1667 | 0 | 9.0184 | 37.78
2021-03-20 04:30 | 44275.1875 | 0 | 9.0027 | 37.78
2021-03-20 05:00 | 44275.2083 | 0 | 9.16 | 37.78
2021-03-20 05:30 | 44275.2292 | 0 | 9.2545 | 37.78
2021-03-20 06:00 | 44275.25 | 0 | 9.4556 | 37.78
2021-03-20 06:30 | 44275.2708 | 0 | 9.79 | 37.78
2021-03-20 07:00 | 44275.2917 | 0 | 10.0302 | 37.78
2021-03-20 07:30 | 44275.3125 | 0 | 10.8727 | 37.78
2021-03-20 08:00 | 44275.3333 | 0 | 10.8468 | 37.78
2021-03-20 08:30 | 44275.3542 | 0 | 10.9335 | 37.78
2021-03-20 09:00 | 44275.375 | 0 | 10.7337 | 37.78
2021-03-20 09:30 | 44275.3958 | 0 | 11.0708 | 37.78
2021-03-20 10:00 | 44275.4167 | 0 | 10.0077 | 37.78
2021-03-20 10:30 | 44275.4375 | 0 | 9.9074 | 37.78
2021-03-20 11:00 | 44275.4583 | 0 | 10.8775 | 37.78
2021-03-20 11:30 | 44275.4792 | 0 | 10.717 | 37.78
2021-03-20 12:00 | 44275.5 | 0 | 10.0933 | 37.78
2021-03-20 12:30 | 44275.5208 | 0 | 9.8784 | 37.78
2021-03-20 13:00 | 44275.5417 | 0 | 11.2589 | 37.78
2021-03-20 13:30 | 44275.5625 | 0 | 12.0844 | 37.78
2021-03-20 14:00 | 44275.5833 | 0 | 12.454 | 37.78
2021-03-20 14:30 | 44275.6042 | 0 | 12.8621 | 37.78
2021-03-20 15:00 | 44275.625 | 0 | 12.6385 | 37.78
2021-03-20 15:30 | 44275.6458 | 0 | 12.6835 | 37.78
2021-03-20 16:00 | 44275.6667 | 0 | 13.3205 | 37.78
2021-03-20 16:30 | 44275.6875 | 0 | 13.8611 | 37.78
2021-03-20 17:00 | 44275.7083 | 0 | 13.9262 | 37.78
2021-03-20 17:30 | 44275.7292 | 0 | 13.9042 | 37.78
2021-03-20 18:00 | 44275.75 | 0 | 14.1156 | 37.78
2021-03-20 18:30 | 44275.7708 | 0 | 14.2643 | 37.78
2021-03-20 19:00 | 44275.7917 | 0 | 13.6525 | 37.78
2021-03-20 19:30 | 44275.8125 | 0 | 13.4139 | 37.78
2021-03-20 20:00 | 44275.8333 | 0 | 12.9963 | 37.78
2021-03-20 20:30 | 44275.8542 | 0 | 12.7507 | 37.78
2021-03-20 21:00 | 44275.875 | 0 | 12.2224 | 37.78
2021-03-20 21:30 | 44275.8958 | 0 | 11.9343 | 37.78
2021-03-20 22:00 | 44275.9167 | 0 | 11.4899 | 37.78
2021-03-20 22:30 | 44275.9375 | 0 | 10.9607 | 37.78
2021-03-20 23:00 | 44275.9583 | 0 | 10.4244 | 37.78
2021-03-20 23:30 | 44275.9792 | 0 | 10.0525 | 37.78
2021-03-21 | 44276 | 0 | 9.4352 | 37.78
2021-03-21 00:30 | 44276.0208 | 0 | 9.2245 | 37.78
2021-03-21 01:00 | 44276.0417 | 0 | 9.0001 | 37.78
2021-03-21 01:30 | 44276.0625 | 0 | 8.8661 | 37.78
2021-03-21 02:00 | 44276.0833 | 0 | 8.9093 | 37.78
2021-03-21 02:30 | 44276.1042 | 0 | 8.8016 | 37.78
2021-03-21 03:00 | 44276.125 | 0 | 8.489 | 37.78
2021-03-21 03:30 | 44276.1458 | 0 | 8.5467 | 37.78
2021-03-21 04:00 | 44276.1667 | 0 | 8.3788 | 37.78
2021-03-21 04:30 | 44276.1875 | 0 | 8.4825 | 37.78
2021-03-21 05:00 | 44276.2083 | 0 | 8.4694 | 37.78
2021-03-21 05:30 | 44276.2292 | 0 | 8.5731 | 37.78
2021-03-21 06:00 | 44276.25 | 0 | 8.6007 | 37.78
2021-03-21 06:30 | 44276.2708 | 0 | 8.5561 | 37.78
2021-03-21 07:00 | 44276.2917 | 0 | 8.7925 | 37.78
2021-03-21 07:30 | 44276.3125 | 0 | 9.1114 | 37.78
2021-03-21 08:00 | 44276.3333 | 0 | 9.8739 | 37.78
2021-03-21 08:30 | 44276.3542 | 0 | 10.5574 | 37.78
2021-03-21 09:00 | 44276.375 | 0 | 10.4206 | 37.78
2021-03-21 09:30 | 44276.3958 | 0 | 10.6006 | 37.78
2021-03-21 10:00 | 44276.4167 | 0 | 11.5057 | 37.78
2021-03-21 10:30 | 44276.4375 | 0 | 11.1326 | 37.78
2021-03-21 11:00 | 44276.4583 | 0 | 9.7403 | 37.78
2021-03-21 11:30 | 44276.4792 | 0 | 11.039 | 37.78
2021-03-21 12:00 | 44276.5 | 0 | 11.517 | 37.78
2021-03-21 12:30 | 44276.5208 | 0 | 9.2378 | 37.78
2021-03-21 13:00 | 44276.5417 | 0 | 12.3789 | 37.78
2021-03-21 13:30 | 44276.5625 | 0 | 13.2618 | 37.78
2021-03-21 14:00 | 44276.5833 | 0 | 13.0399 | 37.78
2021-03-21 14:30 | 44276.6042 | 0 | 13.042 | 37.78
2021-03-21 15:00 | 44276.625 | 0 | 13.379 | 37.78
2021-03-21 15:30 | 44276.6458 | 0 | 12.8263 | 37.78
2021-03-21 16:00 | 44276.6667 | 0 | 12.9372 | 37.78
2021-03-21 16:30 | 44276.6875 | 0 | 13.0756 | 37.78
2021-03-21 17:00 | 44276.7083 | 0 | 13.1566 | 37.78
2021-03-21 17:30 | 44276.7292 | 0 | 13.4273 | 37.78
2021-03-21 18:00 | 44276.75 | 0 | 13.7177 | 37.78
2021-03-21 18:30 | 44276.7708 | 0 | 13.9857 | 37.78
2021-03-21 19:00 | 44276.7917 | 0 | 13.3521 | 37.78
2021-03-21 19:30 | 44276.8125 | 0 | 12.9399 | 37.78
2021-03-21 20:00 | 44276.8333 | 0 | 12.7667 | 37.78
2021-03-21 20:30 | 44276.8542 | 0 | 12.0826 | 37.78
2021-03-21 21:00 | 44276.875 | 0 | 11.5186 | 37.78
2021-03-21 21:30 | 44276.8958 | 0 | 11.2963 | 37.78
2021-03-21 22:00 | 44276.9167 | 0 | 10.6962 | 37.78
2021-03-21 22:30 | 44276.9375 | 0 | 9.9563 | 37.78
2021-03-21 23:00 | 44276.9583 | 0 | 9.3956 | 37.78
2021-03-21 23:30 | 44276.9792 | 0 | 9.19 | 37.78
2021-03-22 | 44277 | 0 | 9.0154 | 37.78
2021-03-22 00:30 | 44277.0208 | 0 | 8.7828 | 37.78
2021-03-22 01:00 | 44277.0417 | 0 | 8.6401 | 37.78
2021-03-22 01:30 | 44277.0625 | 0 | 8.5297 | 37.78
2021-03-22 02:00 | 44277.0833 | 0 | 8.5311 | 37.78
2021-03-22 02:30 | 44277.1042 | 0 | 8.5271 | 37.78
2021-03-22 03:00 | 44277.125 | 0 | 8.3564 | 37.78
2021-03-22 03:30 | 44277.1458 | 0 | 8.5561 | 37.78
2021-03-22 04:00 | 44277.1667 | 0 | 8.8318 | 37.78
2021-03-22 04:30 | 44277.1875 | 0 | 9.2858 | 37.78
2021-03-22 05:00 | 44277.2083 | 0 | 9.8877 | 37.78
2021-03-22 05:30 | 44277.2292 | 0 | 10.5857 | 37.78
2021-03-22 06:00 | 44277.25 | 0 | 11.5245 | 37.78
2021-03-22 06:30 | 44277.2708 | 0 | 12.5626 | 37.78
2021-03-22 07:00 | 44277.2917 | 0 | 13.6171 | 37.78
2021-03-22 07:30 | 44277.3125 | 0 | 13.9604 | 37.78
2021-03-22 08:00 | 44277.3333 | 0 | 13.8911 | 37.78
2021-03-22 08:30 | 44277.3542 | 0 | 14.2022 | 37.78
2021-03-22 09:00 | 44277.375 | 0 | 14.2326 | 37.78
2021-03-22 09:30 | 44277.3958 | 0 | 14.1757 | 37.78
2021-03-22 10:00 | 44277.4167 | 0 | 13.9187 | 37.78
2021-03-22 10:30 | 44277.4375 | 0 | 14.1933 | 37.78
2021-03-22 11:00 | 44277.4583 | 0 | 13.8748 | 37.78
2021-03-22 11:30 | 44277.4792 | 0 | 14.0471 | 37.78
2021-03-22 12:00 | 44277.5 | 0 | 14.0359 | 37.78
2021-03-22 12:30 | 44277.5208 | 0 | 13.9051 | 37.78
2021-03-22 13:00 | 44277.5417 | 0 | 13.9556 | 37.78
2021-03-22 13:30 | 44277.5625 | 0 | 13.8394 | 37.78
2021-03-22 14:00 | 44277.5833 | 0 | 14.4838 | 37.78
2021-03-22 14:30 | 44277.6042 | 0 | 14.5161 | 37.78
2021-03-22 15:00 | 44277.625 | 0 | 13.9604 | 37.78
2021-03-22 15:30 | 44277.6458 | 0 | 14.2755 | 37.78
2021-03-22 16:00 | 44277.6667 | 0 | 14.014 | 37.78
2021-03-22 16:30 | 44277.6875 | 0 | 14.5732 | 37.78
2021-03-22 17:00 | 44277.7083 | 0 | 14.5277 | 37.78
2021-03-22 17:30 | 44277.7292 | 0 | 14.7666 | 37.78
2021-03-22 18:00 | 44277.75 | 0 | 15.0549 | 37.78
2021-03-22 18:30 | 44277.7708 | 0 | 15.2378 | 37.78
2021-03-22 19:00 | 44277.7917 | 0 | 14.7369 | 37.78
2021-03-22 19:30 | 44277.8125 | 0 | 14.4912 | 37.78
2021-03-22 20:00 | 44277.8333 | 0 | 14.2555 | 37.78
2021-03-22 20:30 | 44277.8542 | 0 | 13.5969 | 37.78
2021-03-22 21:00 | 44277.875 | 0 | 13.1597 | 37.78
2021-03-22 21:30 | 44277.8958 | 0 | 12.8373 | 37.78
2021-03-22 22:00 | 44277.9167 | 0 | 12.3133 | 37.78
2021-03-22 22:30 | 44277.9375 | 0 | 11.3521 | 37.78
2021-03-22 23:00 | 44277.9583 | 0 | 10.8333 | 37.78
2021-03-22 23:30 | 44277.9792 | 0 | 10.4442 | 37.78
2021-03-23 | 44278 | 0 | 9.9229 | 37.78
2021-03-23 00:30 | 44278.0208 | 0 | 9.409 | 37.78
2021-03-23 01:00 | 44278.0417 | 0 | 9.139 | 37.78
2021-03-23 01:30 | 44278.0625 | 0 | 9.215 | 37.78
2021-03-23 02:00 | 44278.0833 | 0 | 9.176 | 37.78
2021-03-23 02:30 | 44278.1042 | 0 | 9.017 | 37.78
2021-03-23 03:00 | 44278.125 | 0 | 8.8911 | 37.78
2021-03-23 03:30 | 44278.1458 | 0 | 9.1293 | 37.78
2021-03-23 04:00 | 44278.1667 | 0 | 9.2946 | 37.78
2021-03-23 04:30 | 44278.1875 | 0 | 9.8817 | 37.78
2021-03-23 05:00 | 44278.2083 | 0 | 10.7882 | 37.78
2021-03-23 05:30 | 44278.2292 | 0 | 11.5473 | 37.78
2021-03-23 06:00 | 44278.25 | 0 | 12.5967 | 37.78
2021-03-23 06:30 | 44278.2708 | 0 | 13.1515 | 37.78
2021-03-23 07:00 | 44278.2917 | 0 | 13.8671 | 37.78
2021-03-23 07:30 | 44278.3125 | 0 | 14.6737 | 37.78
2021-03-23 08:00 | 44278.3333 | 0 | 14.9739 | 37.78
2021-03-23 08:30 | 44278.3542 | 0 | 15.0337 | 37.78
2021-03-23 09:00 | 44278.375 | 0 | 15.2777 | 37.78
2021-03-23 09:30 | 44278.3958 | 0 | 15.4713 | 37.78
2021-03-23 10:00 | 44278.4167 | 0 | 15.5197 | 37.78
2021-03-23 10:30 | 44278.4375 | 0 | 15.1353 | 37.78
2021-03-23 11:00 | 44278.4583 | 0 | 14.4843 | 37.78
2021-03-23 11:30 | 44278.4792 | 0 | 14.5975 | 37.78
2021-03-23 12:00 | 44278.5 | 0 | 14.9877 | 37.78
2021-03-23 12:30 | 44278.5208 | 0 | 14.4014 | 37.78
2021-03-23 13:00 | 44278.5417 | 0 | 14.2375 | 37.78
2021-03-23 13:30 | 44278.5625 | 0 | 14.588 | 37.78
2021-03-23 14:00 | 44278.5833 | 0 | 14.3105 | 37.78
2021-03-23 14:30 | 44278.6042 | 0 | 14.5762 | 37.78
2021-03-23 15:00 | 44278.625 | 0 | 14.9115 | 37.78
2021-03-23 15:30 | 44278.6458 | 0 | 14.8505 | 37.78
2021-03-23 16:00 | 44278.6667 | 0 | 14.6672 | 37.78
2021-03-23 16:30 | 44278.6875 | 0 | 14.7672 | 37.78
2021-03-23 17:00 | 44278.7083 | 0 | 15.0037 | 37.78
2021-03-23 17:30 | 44278.7292 | 0 | 15.4749 | 37.78
2021-03-23 18:00 | 44278.75 | 0 | 16.1101 | 37.78
2021-03-23 18:30 | 44278.7708 | 0 | 16.315 | 37.78
2021-03-23 19:00 | 44278.7917 | 0 | 16.082 | 37.78
2021-03-23 19:30 | 44278.8125 | 0 | 15.823 | 37.78
2021-03-23 20:00 | 44278.8333 | 0 | 15.5447 | 37.78
2021-03-23 20:30 | 44278.8542 | 0 | 14.9076 | 37.78
2021-03-23 21:00 | 44278.875 | 0 | 14.3666 | 37.78
2021-03-23 21:30 | 44278.8958 | 0 | 13.8869 | 37.78
2021-03-23 22:00 | 44278.9167 | 0 | 13.1457 | 37.78
2021-03-23 22:30 | 44278.9375 | 0 | 12.2593 | 37.78
2021-03-23 23:00 | 44278.9583 | 0 | 11.7072 | 37.78
2021-03-23 23:30 | 44278.9792 | 0 | 11.2226 | 37.78
2021-03-24 | 44279 | 0 | 10.6013 | 37.78
2021-03-24 00:30 | 44279.0208 | 0 | 9.972 | 37.78
2021-03-24 01:00 | 44279.0417 | 0 | 9.7296 | 37.78
2021-03-24 01:30 | 44279.0625 | 0 | 9.6004 | 37.78
2021-03-24 02:00 | 44279.0833 | 0 | 9.4944 | 37.78
2021-03-24 02:30 | 44279.1042 | 0 | 9.2916 | 37.78
2021-03-24 03:00 | 44279.125 | 0 | 9.1476 | 37.78
2021-03-24 03:30 | 44279.1458 | 0 | 9.3027 | 37.78
2021-03-24 04:00 | 44279.1667 | 0 | 9.5441 | 37.78
2021-03-24 04:30 | 44279.1875 | 0 | 9.886 | 37.78
2021-03-24 05:00 | 44279.2083 | 0 | 10.4336 | 37.78
2021-03-24 05:30 | 44279.2292 | 0 | 10.9411 | 37.78
2021-03-24 06:00 | 44279.25 | 0 | 11.9424 | 37.78
2021-03-24 06:30 | 44279.2708 | 0 | 12.7967 | 37.78
2021-03-24 07:00 | 44279.2917 | 0 | 12.9647 | 37.78
2021-03-24 07:30 | 44279.3125 | 0 | 14.2766 | 37.78
2021-03-24 08:00 | 44279.3333 | 0 | 13.9306 | 37.78
2021-03-24 08:30 | 44279.3542 | 0 | 14.0313 | 37.78
2021-03-24 09:00 | 44279.375 | 0 | 14.0237 | 37.78
2021-03-24 09:30 | 44279.3958 | 0 | 15.0011 | 37.78
2021-03-24 10:00 | 44279.4167 | 0 | 14.4642 | 37.78
2021-03-24 10:30 | 44279.4375 | 0 | 15.7973 | 37.78
2021-03-24 11:00 | 44279.4583 | 0 | 16.1378 | 37.78
2021-03-24 11:30 | 44279.4792 | 0 | 14.0975 | 37.78
2021-03-24 12:00 | 44279.5 | 0 | 14.8264 | 37.78
2021-03-24 12:30 | 44279.5208 | 0 | 15.589 | 37.78
2021-03-24 13:00 | 44279.5417 | 0 | 15.7945 | 37.78
2021-03-24 13:30 | 44279.5625 | 0 | 16.6469 | 37.78
2021-03-24 14:00 | 44279.5833 | 0 | 15.8001 | 37.78
2021-03-24 14:30 | 44279.6042 | 0 | 15.5145 | 37.78
2021-03-24 15:00 | 44279.625 | 0 | 15.6536 | 37.78
2021-03-24 15:30 | 44279.6458 | 0 | 16.3475 | 37.78
2021-03-24 16:00 | 44279.6667 | 0 | 16.4681 | 37.78
2021-03-24 16:30 | 44279.6875 | 0 | 16.8963 | 37.78
2021-03-24 17:00 | 44279.7083 | 0 | 17.0897 | 37.78
2021-03-24 17:30 | 44279.7292 | 0 | 17.0324 | 37.78
2021-03-24 18:00 | 44279.75 | 0 | 17.0359 | 37.78
2021-03-24 18:30 | 44279.7708 | 0 | 17.2346 | 37.78
2021-03-24 19:00 | 44279.7917 | 0 | 16.8367 | 37.78
2021-03-24 19:30 | 44279.8125 | 0 | 16.2975 | 37.78
2021-03-24 20:00 | 44279.8333 | 0 | 15.76 | 37.78
2021-03-24 20:30 | 44279.8542 | 0 | 15.2679 | 37.78
2021-03-24 21:00 | 44279.875 | 0 | 14.5124 | 37.78
2021-03-24 21:30 | 44279.8958 | 0 | 13.7929 | 37.78
2021-03-24 22:00 | 44279.9167 | 0 | 13.0931 | 37.78
2021-03-24 22:30 | 44279.9375 | 0 | 11.9888 | 37.78
2021-03-24 23:00 | 44279.9583 | 0 | 11.1013 | 37.78
2021-03-24 23:30 | 44279.9792 | 0 | 10.6195 | 37.78
2021-03-25 | 44280 | 0 | 9.8434 | 37.78
2021-03-25 00:30 | 44280.0208 | 0 | 9.4217 | 37.78
2021-03-25 01:00 | 44280.0417 | 0 | 9.2719 | 37.78
2021-03-25 01:30 | 44280.0625 | 0 | 8.9568 | 37.78
2021-03-25 02:00 | 44280.0833 | 0 | 8.9094 | 37.78
2021-03-25 02:30 | 44280.1042 | 0 | 8.7819 | 37.78
2021-03-25 03:00 | 44280.125 | 0 | 8.6177 | 37.78
2021-03-25 03:30 | 44280.1458 | 0 | 8.7632 | 37.78
2021-03-25 04:00 | 44280.1667 | 0 | 8.8824 | 37.78
2021-03-25 04:30 | 44280.1875 | 0 | 9.2953 | 37.78
2021-03-25 05:00 | 44280.2083 | 0 | 9.7877 | 37.78
2021-03-25 05:30 | 44280.2292 | 0 | 10.3801 | 37.78
2021-03-25 06:00 | 44280.25 | 0 | 11.2314 | 37.78
2021-03-25 06:30 | 44280.2708 | 0 | 11.6183 | 37.78
2021-03-25 07:00 | 44280.2917 | 0 | 12.0519 | 37.78
2021-03-25 07:30 | 44280.3125 | 0 | 12.1266 | 37.78
2021-03-25 08:00 | 44280.3333 | 0 | 12.107 | 37.78
2021-03-25 08:30 | 44280.3542 | 0 | 11.9602 | 37.78
2021-03-25 09:00 | 44280.375 | 0 | 11.9001 | 37.78
2021-03-25 09:30 | 44280.3958 | 0 | 12.2018 | 37.78
2021-03-25 10:00 | 44280.4167 | 0 | 11.6642 | 37.78
2021-03-25 10:30 | 44280.4375 | 0 | 11.772 | 37.78
2021-03-25 11:00 | 44280.4583 | 0 | 11.7456 | 37.78
2021-03-25 11:30 | 44280.4792 | 0 | 11.892 | 37.78
2021-03-25 12:00 | 44280.5 | 0 | 12.031 | 37.78
2021-03-25 12:30 | 44280.5208 | 0 | 12.2349 | 37.78
2021-03-25 13:00 | 44280.5417 | 0 | 12.4533 | 37.78
2021-03-25 13:30 | 44280.5625 | 0 | 13.2256 | 37.78
2021-03-25 14:00 | 44280.5833 | 0 | 13.7189 | 37.78
2021-03-25 14:30 | 44280.6042 | 0 | 14.1608 | 37.78
2021-03-25 15:00 | 44280.625 | 0 | 14.693 | 37.78
2021-03-25 15:30 | 44280.6458 | 0 | 15.4536 | 37.78
2021-03-25 16:00 | 44280.6667 | 0 | 15.947 | 37.78
2021-03-25 16:30 | 44280.6875 | 0 | 16.5606 | 37.78
2021-03-25 17:00 | 44280.7083 | 0 | 16.6636 | 37.78
2021-03-25 17:30 | 44280.7292 | 0 | 16.5065 | 37.78
2021-03-25 18:00 | 44280.75 | 0 | 16.5276 | 37.78
2021-03-25 18:30 | 44280.7708 | 0 | 16.8747 | 37.78
2021-03-25 19:00 | 44280.7917 | 0 | 16.3745 | 37.78
2021-03-25 19:30 | 44280.8125 | 0 | 15.8758 | 37.78
2021-03-25 20:00 | 44280.8333 | 0 | 15.4915 | 37.78
2021-03-25 20:30 | 44280.8542 | 0 | 14.7063 | 37.78
2021-03-25 21:00 | 44280.875 | 0 | 14.2457 | 37.78
2021-03-25 21:30 | 44280.8958 | 0 | 13.5519 | 37.78
2021-03-25 22:00 | 44280.9167 | 0 | 12.9303 | 37.78
2021-03-25 22:30 | 44280.9375 | 0 | 11.8712 | 37.78
2021-03-25 23:00 | 44280.9583 | 0 | 10.9896 | 37.78
2021-03-25 23:30 | 44280.9792 | 0 | 10.4869 | 37.78
2021-03-26 | 44281 | 0 | 9.6958 | 37.78
2021-03-26 00:30 | 44281.0208 | 0 | 9.2755 | 37.78
2021-03-26 01:00 | 44281.0417 | 0 | 9.1664 | 37.78
2021-03-26 01:30 | 44281.0625 | 0 | 8.896 | 37.78
2021-03-26 02:00 | 44281.0833 | 0 | 8.8424 | 37.78
2021-03-26 02:30 | 44281.1042 | 0 | 8.6926 | 37.78
2021-03-26 03:00 | 44281.125 | 0 | 8.5981 | 37.78
2021-03-26 03:30 | 44281.1458 | 0 | 8.6686 | 37.78
2021-03-26 04:00 | 44281.1667 | 0 | 8.9817 | 37.78
2021-03-26 04:30 | 44281.1875 | 0 | 9.3271 | 37.78
2021-03-26 05:00 | 44281.2083 | 0 | 9.8057 | 37.78
2021-03-26 05:30 | 44281.2292 | 0 | 10.489 | 37.78
2021-03-26 06:00 | 44281.25 | 0 | 11.0673 | 37.78
2021-03-26 06:30 | 44281.2708 | 0 | 11.5053 | 37.78
2021-03-26 07:00 | 44281.2917 | 0 | 11.8723 | 37.78
2021-03-26 07:30 | 44281.3125 | 0 | 11.9308 | 37.78
2021-03-26 08:00 | 44281.3333 | 0 | 11.9576 | 37.78
2021-03-26 08:30 | 44281.3542 | 0 | 11.8476 | 37.78
2021-03-26 09:00 | 44281.375 | 0 | 11.6523 | 37.78
2021-03-26 09:30 | 44281.3958 | 0 | 11.5424 | 37.78
2021-03-26 10:00 | 44281.4167 | 0 | 11.3844 | 37.78
2021-03-26 10:30 | 44281.4375 | 0 | 11.529 | 37.78
2021-03-26 11:00 | 44281.4583 | 0 | 11.7282 | 37.78
2021-03-26 11:30 | 44281.4792 | 0 | 12.0587 | 37.78
2021-03-26 12:00 | 44281.5 | 0 | 12.2411 | 37.78
2021-03-26 12:30 | 44281.5208 | 0 | 13.523 | 37.78
2021-03-26 13:00 | 44281.5417 | 0 | 13.1544 | 37.78
2021-03-26 13:30 | 44281.5625 | 0 | 14.0596 | 37.78
2021-03-26 14:00 | 44281.5833 | 0 | 13.3903 | 37.78
2021-03-26 14:30 | 44281.6042 | 0 | 13.6913 | 37.78
2021-03-26 15:00 | 44281.625 | 0 | 13.8592 | 37.78
2021-03-26 15:30 | 44281.6458 | 0 | 15.1459 | 37.78
2021-03-26 16:00 | 44281.6667 | 0 | 15.7369 | 37.78
2021-03-26 16:30 | 44281.6875 | 0 | 15.6913 | 37.78
2021-03-26 17:00 | 44281.7083 | 0 | 15.9345 | 37.78
2021-03-26 17:30 | 44281.7292 | 0 | 15.8088 | 37.78
2021-03-26 18:00 | 44281.75 | 0 | 15.6592 | 37.78
2021-03-26 18:30 | 44281.7708 | 0 | 16.001 | 37.78
2021-03-26 19:00 | 44281.7917 | 0 | 15.7029 | 37.78
2021-03-26 19:30 | 44281.8125 | 0 | 15.3582 | 37.78
2021-03-26 20:00 | 44281.8333 | 0 | 14.9958 | 37.78
2021-03-26 20:30 | 44281.8542 | 0 | 14.3949 | 37.78
2021-03-26 21:00 | 44281.875 | 0 | 13.8145 | 37.78
2021-03-26 21:30 | 44281.8958 | 0 | 13.3771 | 37.78
2021-03-26 22:00 | 44281.9167 | 0 | 12.6597 | 37.78
2021-03-26 22:30 | 44281.9375 | 0 | 11.8553 | 37.78
2021-03-26 23:00 | 44281.9583 | 0 | 11.2579 | 37.78
2021-03-26 23:30 | 44281.9792 | 0 | 10.7448 | 37.78
2021-03-27 | 44282 | 0 | 10.0238 | 37.78
2021-03-27 00:30 | 44282.0208 | 0 | 9.3635 | 37.78
2021-03-27 01:00 | 44282.0417 | 0 | 9.3376 | 37.78
2021-03-27 01:30 | 44282.0625 | 0 | 9.1349 | 37.78
2021-03-27 02:00 | 44282.0833 | 0 | 9.2221 | 37.78
2021-03-27 02:30 | 44282.1042 | 0 | 8.8857 | 37.78
2021-03-27 03:00 | 44282.125 | 0 | 8.8939 | 37.78
2021-03-27 03:30 | 44282.1458 | 0 | 9.0697 | 37.78
2021-03-27 04:00 | 44282.1667 | 0 | 9.13 | 37.78
2021-03-27 04:30 | 44282.1875 | 0 | 9.1604 | 37.78
2021-03-27 05:00 | 44282.2083 | 0 | 9.2606 | 37.78
2021-03-27 05:30 | 44282.2292 | 0 | 9.3237 | 37.78
2021-03-27 06:00 | 44282.25 | 0 | 9.4936 | 37.78
2021-03-27 06:30 | 44282.2708 | 0 | 9.6553 | 37.78
2021-03-27 07:00 | 44282.2917 | 0 | 9.7362 | 37.78
2021-03-27 07:30 | 44282.3125 | 0 | 9.5421 | 37.78
2021-03-27 08:00 | 44282.3333 | 0 | 9.5861 | 37.78
2021-03-27 08:30 | 44282.3542 | 0 | 9.6017 | 37.78
2021-03-27 09:00 | 44282.375 | 0 | 9.7202 | 37.78
2021-03-27 09:30 | 44282.3958 | 0 | 10.2084 | 37.78
2021-03-27 10:00 | 44282.4167 | 0 | 10.526 | 37.78
2021-03-27 10:30 | 44282.4375 | 0 | 10.4984 | 37.78
2021-03-27 11:00 | 44282.4583 | 0 | 11.8214 | 37.78
2021-03-27 11:30 | 44282.4792 | 0 | 10.7775 | 37.78
2021-03-27 12:00 | 44282.5 | 0 | 12.0425 | 37.78
2021-03-27 12:30 | 44282.5208 | 0 | 10.6669 | 37.78
2021-03-27 13:00 | 44282.5417 | 0 | 11.9983 | 37.78
2021-03-27 13:30 | 44282.5625 | 0 | 11.201 | 37.78
2021-03-27 14:00 | 44282.5833 | 0 | 11.9112 | 37.78
2021-03-27 14:30 | 44282.6042 | 0 | 13.5443 | 37.78
2021-03-27 15:00 | 44282.625 | 0 | 13.2956 | 37.78
2021-03-27 15:30 | 44282.6458 | 0 | 12.5567 | 37.78
2021-03-27 16:00 | 44282.6667 | 0 | 13.3125 | 37.78
2021-03-27 16:30 | 44282.6875 | 0 | 13.6689 | 37.78
2021-03-27 17:00 | 44282.7083 | 0 | 13.8002 | 37.78
2021-03-27 17:30 | 44282.7292 | 0 | 13.9147 | 37.78
2021-03-27 18:00 | 44282.75 | 0 | 14.2783 | 37.78
2021-03-27 18:30 | 44282.7708 | 0 | 14.2469 | 37.78
2021-03-27 19:00 | 44282.7917 | 0 | 13.9619 | 37.78
2021-03-27 19:30 | 44282.8125 | 0 | 13.8029 | 37.78
2021-03-27 20:00 | 44282.8333 | 0 | 13.4469 | 37.78
2021-03-27 20:30 | 44282.8542 | 0 | 12.9339 | 37.78
2021-03-27 21:00 | 44282.875 | 0 | 12.2072 | 37.78
2021-03-27 21:30 | 44282.8958 | 0 | 11.8755 | 37.78
2021-03-27 22:00 | 44282.9167 | 0 | 11.6781 | 37.78
2021-03-27 22:30 | 44282.9375 | 0 | 10.8705 | 37.78
2021-03-27 23:00 | 44282.9583 | 0 | 10.2263 | 37.78
2021-03-27 23:30 | 44282.9792 | 0 | 9.6632 | 37.78
2021-03-28 | 44283 | 0 | 9.2334 | 37.78
2021-03-28 00:30 | 44283.0208 | 0 | 8.9314 | 37.78
2021-03-28 01:00 | 44283.0417 | 0 | 8.6597 | 37.78
2021-03-28 01:30 | 44283.0625 | 0 | 8.3558 | 37.78
2021-03-28 02:00 | 44283.0833 | 0 | 8.3551 | 37.78
2021-03-28 02:30 | 44283.1042 | 0 | 8.2656 | 37.78
2021-03-28 03:00 | 44283.125 | 0 | 8.0134 | 37.78
2021-03-28 03:30 | 44283.1458 | 0 | 7.9294 | 37.78
2021-03-28 04:00 | 44283.1667 | 0 | 7.8807 | 37.78
2021-03-28 04:30 | 44283.1875 | 0 | 7.8848 | 37.78
2021-03-28 05:00 | 44283.2083 | 0 | 7.8611 | 37.78
2021-03-28 05:30 | 44283.2292 | 0 | 7.9937 | 37.78
2021-03-28 06:00 | 44283.25 | 0 | 7.9294 | 37.78
2021-03-28 06:30 | 44283.2708 | 0 | 7.9701 | 37.78
2021-03-28 07:00 | 44283.2917 | 0 | 7.7805 | 37.78
2021-03-28 07:30 | 44283.3125 | 0 | 7.8562 | 37.78
2021-03-28 08:00 | 44283.3333 | 0 | 7.8538 | 37.78
2021-03-28 08:30 | 44283.3542 | 0 | 8.0371 | 37.78
2021-03-28 09:00 | 44283.375 | 0 | 7.8807 | 37.78
2021-03-28 09:30 | 44283.3958 | 0 | 7.8834 | 37.78
2021-03-28 10:00 | 44283.4167 | 0 | 7.7176 | 37.78
2021-03-28 10:30 | 44283.4375 | 0 | 7.8633 | 37.78
2021-03-28 11:00 | 44283.4583 | 0 | 8.0993 | 37.78
2021-03-28 11:30 | 44283.4792 | 0 | 9.1136 | 37.78
2021-03-28 12:00 | 44283.5 | 0 | 8.6225 | 37.78
2021-03-28 12:30 | 44283.5208 | 0 | 8.3755 | 37.78
2021-03-28 13:00 | 44283.5417 | 0 | 9.0014 | 37.78
2021-03-28 13:30 | 44283.5625 | 0 | 9.701 | 37.78
2021-03-28 14:00 | 44283.5833 | 0 | 10.7633 | 37.78
2021-03-28 14:30 | 44283.6042 | 0 | 12.4915 | 37.78
2021-03-28 15:00 | 44283.625 | 0 | 12.0242 | 37.78
2021-03-28 15:30 | 44283.6458 | 0 | 12.4946 | 37.78
2021-03-28 16:00 | 44283.6667 | 0 | 12.9606 | 37.78
2021-03-28 16:30 | 44283.6875 | 0 | 13.6771 | 37.78
2021-03-28 17:00 | 44283.7083 | 0 | 13.9863 | 37.78
2021-03-28 17:30 | 44283.7292 | 0 | 14.3261 | 37.78
2021-03-28 18:00 | 44283.75 | 0 | 14.8106 | 37.78
2021-03-28 18:30 | 44283.7708 | 0 | 14.8249 | 37.78
2021-03-28 19:00 | 44283.7917 | 0 | 14.644 | 37.78
2021-03-28 19:30 | 44283.8125 | 0 | 14.2323 | 37.78
2021-03-28 20:00 | 44283.8333 | 0 | 13.8136 | 37.78
2021-03-28 20:30 | 44283.8542 | 0 | 13.1923 | 37.78
2021-03-28 21:00 | 44283.875 | 0 | 12.7713 | 37.78
2021-03-28 21:30 | 44283.8958 | 0 | 12.2303 | 37.78
2021-03-28 22:00 | 44283.9167 | 0 | 11.5559 | 37.78
2021-03-28 22:30 | 44283.9375 | 0 | 10.6211 | 37.78
2021-03-28 23:00 | 44283.9583 | 0 | 10.0417 | 37.78
2021-03-28 23:30 | 44283.9792 | 0 | 9.6844 | 37.78
2021-03-29 | 44284 | 0 | 9.4235 | 37.78
2021-03-29 00:30 | 44284.0208 | 0 | 9.16 | 37.78
2021-03-29 01:00 | 44284.0417 | 0 | 8.9514 | 37.78
2021-03-29 01:30 | 44284.0625 | 0 | 8.7596 | 37.78
2021-03-29 02:00 | 44284.0833 | 0 | 8.6427 | 37.78
2021-03-29 02:30 | 44284.1042 | 0 | 8.5704 | 37.78
2021-03-29 03:00 | 44284.125 | 0 | 8.3021 | 37.78
2021-03-29 03:30 | 44284.1458 | 0 | 8.5561 | 37.78
2021-03-29 04:00 | 44284.1667 | 0 | 8.6007 | 37.78
2021-03-29 04:30 | 44284.1875 | 0 | 9.0449 | 37.78
2021-03-29 05:00 | 44284.2083 | 0 | 9.4681 | 37.78
2021-03-29 05:30 | 44284.2292 | 0 | 10.0797 | 37.78
2021-03-29 06:00 | 44284.25 | 0 | 10.883 | 37.78
2021-03-29 06:30 | 44284.2708 | 0 | 11.6393 | 37.78
2021-03-29 07:00 | 44284.2917 | 0 | 12.0997 | 37.78
2021-03-29 07:30 | 44284.3125 | 0 | 12.3211 | 37.78
2021-03-29 08:00 | 44284.3333 | 0 | 12.1936 | 37.78
2021-03-29 08:30 | 44284.3542 | 0 | 11.9221 | 37.78
2021-03-29 09:00 | 44284.375 | 0 | 12.2037 | 37.78
2021-03-29 09:30 | 44284.3958 | 0 | 12.3229 | 37.78
2021-03-29 10:00 | 44284.4167 | 0 | 12.4758 | 37.78
2021-03-29 10:30 | 44284.4375 | 0 | 13.2814 | 37.78
2021-03-29 11:00 | 44284.4583 | 0 | 13.2646 | 37.78
2021-03-29 11:30 | 44284.4792 | 0 | 13.172 | 37.78
2021-03-29 12:00 | 44284.5 | 0 | 13.9159 | 37.78
2021-03-29 12:30 | 44284.5208 | 0 | 14.5162 | 37.78
2021-03-29 13:00 | 44284.5417 | 0 | 14.8583 | 37.78
2021-03-29 13:30 | 44284.5625 | 0 | 13.728 | 37.78
2021-03-29 14:00 | 44284.5833 | 0 | 15.1083 | 37.78
2021-03-29 14:30 | 44284.6042 | 0 | 15.5384 | 37.78
2021-03-29 15:00 | 44284.625 | 0 | 16.7993 | 37.78
2021-03-29 15:30 | 44284.6458 | 0 | 15.1268 | 37.78
2021-03-29 16:00 | 44284.6667 | 0 | 15.703 | 37.78
2021-03-29 16:30 | 44284.6875 | 0 | 16.0776 | 37.78
2021-03-29 17:00 | 44284.7083 | 0 | 16.2284 | 37.78
2021-03-29 17:30 | 44284.7292 | 0 | 15.9504 | 37.78
2021-03-29 18:00 | 44284.75 | 0 | 16.1106 | 37.78
2021-03-29 18:30 | 44284.7708 | 0 | 16.2912 | 37.78
2021-03-29 19:00 | 44284.7917 | 0 | 15.5973 | 37.78
2021-03-29 19:30 | 44284.8125 | 0 | 15.2876 | 37.78
2021-03-29 20:00 | 44284.8333 | 0 | 14.5866 | 37.78
2021-03-29 20:30 | 44284.8542 | 0 | 14.1207 | 37.78
2021-03-29 21:00 | 44284.875 | 0 | 13.3449 | 37.78
2021-03-29 21:30 | 44284.8958 | 0 | 13.0645 | 37.78
2021-03-29 22:00 | 44284.9167 | 0 | 12.4367 | 37.78
2021-03-29 22:30 | 44284.9375 | 0 | 11.5791 | 37.78
2021-03-29 23:00 | 44284.9583 | 0 | 10.882 | 37.78
2021-03-29 23:30 | 44284.9792 | 0 | 10.5325 | 37.78
2021-03-30 | 44285 | 0 | 9.9636 | 37.78
2021-03-30 00:30 | 44285.0208 | 0 | 9.5517 | 37.78
2021-03-30 01:00 | 44285.0417 | 0 | 9.1678 | 37.78
2021-03-30 01:30 | 44285.0625 | 0 | 9.1327 | 37.78
2021-03-30 02:00 | 44285.0833 | 0 | 9.0434 | 37.78
2021-03-30 02:30 | 44285.1042 | 0 | 8.9317 | 37.78
2021-03-30 03:00 | 44285.125 | 0 | 8.8424 | 37.78
2021-03-30 03:30 | 44285.1458 | 0 | 8.9803 | 37.78
2021-03-30 04:00 | 44285.1667 | 0 | 9.055 | 37.78
2021-03-30 04:30 | 44285.1875 | 0 | 9.6926 | 37.78
2021-03-30 05:00 | 44285.2083 | 0 | 10.0562 | 37.78
2021-03-30 05:30 | 44285.2292 | 0 | 10.436 | 37.78
2021-03-30 06:00 | 44285.25 | 0 | 11.0051 | 37.78
2021-03-30 06:30 | 44285.2708 | 0 | 11.4473 | 37.78
2021-03-30 07:00 | 44285.2917 | 0 | 11.5723 | 37.78
2021-03-30 07:30 | 44285.3125 | 0 | 12.1747 | 37.78
2021-03-30 08:00 | 44285.3333 | 0 | 11.5644 | 37.78
2021-03-30 08:30 | 44285.3542 | 0 | 13.3934 | 37.78
2021-03-30 09:00 | 44285.375 | 0 | 13.3023 | 37.78
2021-03-30 09:30 | 44285.3958 | 0 | 12.5353 | 37.78
2021-03-30 10:00 | 44285.4167 | 0 | 12.7662 | 37.78
2021-03-30 10:30 | 44285.4375 | 0 | 11.9413 | 37.78
2021-03-30 11:00 | 44285.4583 | 0 | 11.6251 | 37.78
2021-03-30 11:30 | 44285.4792 | 0 | 10.969 | 37.78
2021-03-30 12:00 | 44285.5 | 0 | 11.8563 | 37.78
2021-03-30 12:30 | 44285.5208 | 0 | 13.0737 | 37.78
2021-03-30 13:00 | 44285.5417 | 0 | 13.1083 | 37.78
2021-03-30 13:30 | 44285.5625 | 0 | 13.3324 | 37.78
2021-03-30 14:00 | 44285.5833 | 0 | 12.7637 | 37.78
2021-03-30 14:30 | 44285.6042 | 0 | 12.0506 | 37.78
2021-03-30 15:00 | 44285.625 | 0 | 12.4118 | 37.78
2021-03-30 15:30 | 44285.6458 | 0 | 13.6573 | 37.78
2021-03-30 16:00 | 44285.6667 | 0 | 13.3868 | 37.78
2021-03-30 16:30 | 44285.6875 | 0 | 13.426 | 37.78
2021-03-30 17:00 | 44285.7083 | 0 | 13.9841 | 37.78
2021-03-30 17:30 | 44285.7292 | 0 | 14.0413 | 37.78
2021-03-30 18:00 | 44285.75 | 0 | 14.4834 | 37.78
2021-03-30 18:30 | 44285.7708 | 0 | 14.7516 | 37.78
2021-03-30 19:00 | 44285.7917 | 0 | 14.1509 | 37.78
2021-03-30 19:30 | 44285.8125 | 0 | 13.7283 | 37.78
2021-03-30 20:00 | 44285.8333 | 0 | 13.2751 | 37.78
2021-03-30 20:30 | 44285.8542 | 0 | 12.7174 | 37.78
2021-03-30 21:00 | 44285.875 | 0 | 12.2742 | 37.78
2021-03-30 21:30 | 44285.8958 | 0 | 11.7693 | 37.78
2021-03-30 22:00 | 44285.9167 | 0 | 11.3815 | 37.78
2021-03-30 22:30 | 44285.9375 | 0 | 10.4835 | 37.78
2021-03-30 23:00 | 44285.9583 | 0 | 9.9937 | 37.78
2021-03-30 23:30 | 44285.9792 | 0 | 9.7123 | 37.78
2021-03-31 | 44286 | 0 | 8.9974 | 37.78
2021-03-31 00:30 | 44286.0208 | 0 | 8.8065 | 37.78
2021-03-31 01:00 | 44286.0417 | 0 | 8.5406 | 37.78
2021-03-31 01:30 | 44286.0625 | 0 | 8.2977 | 37.78
2021-03-31 02:00 | 44286.0833 | 0 | 8.2193 | 37.78
2021-03-31 02:30 | 44286.1042 | 0 | 8.2705 | 37.78
2021-03-31 03:00 | 44286.125 | 0 | 8.1654 | 37.78
2021-03-31 03:30 | 44286.1458 | 0 | 8.2491 | 37.78
2021-03-31 04:00 | 44286.1667 | 0 | 8.3578 | 37.78
2021-03-31 04:30 | 44286.1875 | 0 | 8.6861 | 37.78
2021-03-31 05:00 | 44286.2083 | 0 | 9.1421 | 37.78
2021-03-31 05:30 | 44286.2292 | 0 | 9.5949 | 37.78
2021-03-31 06:00 | 44286.25 | 0 | 10.2409 | 37.78
2021-03-31 06:30 | 44286.2708 | 0 | 10.4457 | 37.78
2021-03-31 07:00 | 44286.2917 | 0 | 10.7122 | 37.78
2021-03-31 07:30 | 44286.3125 | 0 | 10.7 | 37.78
2021-03-31 08:00 | 44286.3333 | 0 | 10.7569 | 37.78
2021-03-31 08:30 | 44286.3542 | 0 | 10.6955 | 37.78
2021-03-31 09:00 | 44286.375 | 0 | 10.2166 | 37.78
2021-03-31 09:30 | 44286.3958 | 0 | 10.4026 | 37.78
2021-03-31 10:00 | 44286.4167 | 0 | 10.8059 | 37.78
2021-03-31 10:30 | 44286.4375 | 0 | 10.9732 | 37.78
2021-03-31 11:00 | 44286.4583 | 0 | 11.5719 | 37.78
2021-03-31 11:30 | 44286.4792 | 0 | 11.1239 | 37.78
2021-03-31 12:00 | 44286.5 | 0 | 11.7465 | 37.78
2021-03-31 12:30 | 44286.5208 | 0 | 12.7739 | 37.78
2021-03-31 13:00 | 44286.5417 | 0 | 13.0582 | 37.78
2021-03-31 13:30 | 44286.5625 | 0 | 10.4385 | 37.78
2021-03-31 14:00 | 44286.5833 | 0 | 11.8583 | 37.78
2021-03-31 14:30 | 44286.6042 | 0 | 12.1087 | 37.78
2021-03-31 15:00 | 44286.625 | 0 | 12.8268 | 37.78
2021-03-31 15:30 | 44286.6458 | 0 | 12.0672 | 37.78
2021-03-31 16:00 | 44286.6667 | 0 | 12.9764 | 37.78
2021-03-31 16:30 | 44286.6875 | 0 | 13.1204 | 37.78
2021-03-31 17:00 | 44286.7083 | 0 | 13.7394 | 37.78
2021-03-31 17:30 | 44286.7292 | 0 | 14.0037 | 37.78
2021-03-31 18:00 | 44286.75 | 0 | 14.2937 | 37.78
2021-03-31 18:30 | 44286.7708 | 0 | 14.4818 | 37.78
2021-03-31 19:00 | 44286.7917 | 0 | 13.8603 | 37.78
2021-03-31 19:30 | 44286.8125 | 0 | 13.4237 | 37.78
2021-03-31 20:00 | 44286.8333 | 0 | 12.9915 | 37.78
2021-03-31 20:30 | 44286.8542 | 0 | 12.2443 | 37.78
2021-03-31 21:00 | 44286.875 | 0 | 11.9826 | 37.78
2021-03-31 21:30 | 44286.8958 | 0 | 11.8269 | 37.78
2021-03-31 22:00 | 44286.9167 | 0 | 11.3859 | 37.78
2021-03-31 22:30 | 44286.9375 | 0 | 10.4582 | 37.78
2021-03-31 23:00 | 44286.9583 | 0 | 9.9477 | 37.78
2021-03-31 23:30 | 44286.9792 | 0 | 9.4845 | 37.78
2021-04-01 | 44287 | 0 | 9.1019 | 37.78
2021-04-01 00:30 | 44287.0208 | 0 | 8.8638 | 37.78
2021-04-01 01:00 | 44287.0417 | 0 | 8.6545 | 37.78
2021-04-01 01:30 | 44287.0625 | 0 | 8.403 | 37.78
2021-04-01 02:00 | 44287.0833 | 0 | 8.3489 | 37.78
2021-04-01 02:30 | 44287.1042 | 0 | 8.2382 | 37.78
2021-04-01 03:00 | 44287.125 | 0 | 8.1909 | 37.78
2021-04-01 03:30 | 44287.1458 | 0 | 8.3289 | 37.78
2021-04-01 04:00 | 44287.1667 | 0 | 8.3782 | 37.78
2021-04-01 04:30 | 44287.1875 | 0 | 8.7617 | 37.78
2021-04-01 05:00 | 44287.2083 | 0 | 9.3397 | 37.78
2021-04-01 05:30 | 44287.2292 | 0 | 9.66 | 37.78
2021-04-01 06:00 | 44287.25 | 0 | 10.3408 | 37.78
2021-04-01 06:30 | 44287.2708 | 0 | 10.8928 | 37.78
2021-04-01 07:00 | 44287.2917 | 0 | 10.6469 | 37.78
2021-04-01 07:30 | 44287.3125 | 0 | 11.0924 | 37.78
2021-04-01 08:00 | 44287.3333 | 0 | 10.6013 | 37.78
2021-04-01 08:30 | 44287.3542 | 0 | 11.1792 | 37.78
2021-04-01 09:00 | 44287.375 | 0 | 10.5974 | 37.78
2021-04-01 09:30 | 44287.3958 | 0 | 11.9858 | 37.78
2021-04-01 10:00 | 44287.4167 | 0 | 11.0245 | 37.78
2021-04-01 10:30 | 44287.4375 | 0 | 12.1288 | 37.78
2021-04-01 11:00 | 44287.4583 | 0 | 12.3572 | 37.78
2021-04-01 11:30 | 44287.4792 | 0 | 12.3655 | 37.78
2021-04-01 12:00 | 44287.5 | 0 | 11.2547 | 37.78
2021-04-01 12:30 | 44287.5208 | 0 | 12.1154 | 37.78
2021-04-01 13:00 | 44287.5417 | 0 | 12.8107 | 37.78
2021-04-01 13:30 | 44287.5625 | 0 | 11.8629 | 37.78
2021-04-01 14:00 | 44287.5833 | 0 | 11.5718 | 37.78
2021-04-01 14:30 | 44287.6042 | 0 | 12.1915 | 37.78
2021-04-01 15:00 | 44287.625 | 0 | 12.9968 | 37.78
2021-04-01 15:30 | 44287.6458 | 0 | 11.7097 | 37.78
2021-04-01 16:00 | 44287.6667 | 0 | 12.5343 | 37.78
2021-04-01 16:30 | 44287.6875 | 0 | 12.6824 | 37.78
2021-04-01 17:00 | 44287.7083 | 0 | 13.3515 | 37.78
2021-04-01 17:30 | 44287.7292 | 0 | 13.3305 | 37.78
2021-04-01 18:00 | 44287.75 | 0 | 13.604 | 37.78
2021-04-01 18:30 | 44287.7708 | 0 | 13.9016 | 37.78
2021-04-01 19:00 | 44287.7917 | 0 | 13.2823 | 37.78
2021-04-01 19:30 | 44287.8125 | 0 | 13.1012 | 37.78
2021-04-01 20:00 | 44287.8333 | 0 | 12.8627 | 37.78
2021-04-01 20:30 | 44287.8542 | 0 | 12.2483 | 37.78
2021-04-01 21:00 | 44287.875 | 0 | 11.6711 | 37.78
2021-04-01 21:30 | 44287.8958 | 0 | 11.2753 | 37.78
2021-04-01 22:00 | 44287.9167 | 0 | 10.9669 | 37.78
2021-04-01 22:30 | 44287.9375 | 0 | 10.2132 | 37.78
2021-04-01 23:00 | 44287.9583 | 0 | 9.7384 | 37.78
2021-04-01 23:30 | 44287.9792 | 0 | 9.3997 | 37.78
2021-04-02 | 44288 | 0 | 8.8907 | 37.78
2021-04-02 00:30 | 44288.0208 | 0 | 8.4177 | 37.78
2021-04-02 01:00 | 44288.0417 | 0 | 8.2941 | 37.78
2021-04-02 01:30 | 44288.0625 | 0 | 7.9739 | 37.78
2021-04-02 02:00 | 44288.0833 | 0 | 8.1503 | 37.78
2021-04-02 02:30 | 44288.1042 | 0 | 7.9023 | 37.78
2021-04-02 03:00 | 44288.125 | 0 | 7.7741 | 37.78
2021-04-02 03:30 | 44288.1458 | 0 | 7.9081 | 37.78
2021-04-02 04:00 | 44288.1667 | 0 | 8.1302 | 37.78
2021-04-02 04:30 | 44288.1875 | 0 | 8.1087 | 37.78
2021-04-02 05:00 | 44288.2083 | 0 | 8.1793 | 37.78
2021-04-02 05:30 | 44288.2292 | 0 | 8.227 | 37.78
2021-04-02 06:00 | 44288.25 | 0 | 8.2736 | 37.78
2021-04-02 06:30 | 44288.2708 | 0 | 8.1151 | 37.78
2021-04-02 07:00 | 44288.2917 | 0 | 8.2024 | 37.78
2021-04-02 07:30 | 44288.3125 | 0 | 7.8384 | 37.78
2021-04-02 08:00 | 44288.3333 | 0 | 8.5681 | 37.78
2021-04-02 08:30 | 44288.3542 | 0 | 7.9918 | 37.78
2021-04-02 09:00 | 44288.375 | 0 | 8.2336 | 37.78
2021-04-02 09:30 | 44288.3958 | 0 | 8.341 | 37.78
2021-04-02 10:00 | 44288.4167 | 0 | 7.1329 | 37.78
2021-04-02 10:30 | 44288.4375 | 0 | 7.664 | 37.78
2021-04-02 11:00 | 44288.4583 | 0 | 7.4019 | 37.78
2021-04-02 11:30 | 44288.4792 | 0 | 7.7283 | 37.78
2021-04-02 12:00 | 44288.5 | 0 | 8.0348 | 37.78
2021-04-02 12:30 | 44288.5208 | 0 | 7.036 | 37.78
2021-04-02 13:00 | 44288.5417 | 0 | 7.5292 | 37.78
2021-04-02 13:30 | 44288.5625 | 0 | 8.3772 | 37.78
2021-04-02 14:00 | 44288.5833 | 0 | 7.9332 | 37.78
2021-04-02 14:30 | 44288.6042 | 0 | 10.0763 | 37.78
2021-04-02 15:00 | 44288.625 | 0 | 9.561 | 37.78
2021-04-02 15:30 | 44288.6458 | 0 | 9.4921 | 37.78
2021-04-02 16:00 | 44288.6667 | 0 | 9.5595 | 37.78
2021-04-02 16:30 | 44288.6875 | 0 | 10.1654 | 37.78
2021-04-02 17:00 | 44288.7083 | 0 | 10.5622 | 37.78
2021-04-02 17:30 | 44288.7292 | 0 | 10.9945 | 37.78
2021-04-02 18:00 | 44288.75 | 0 | 11.3129 | 37.78
2021-04-02 18:30 | 44288.7708 | 0 | 11.5366 | 37.78
2021-04-02 19:00 | 44288.7917 | 0 | 11.227 | 37.78
2021-04-02 19:30 | 44288.8125 | 0 | 11.0266 | 37.78
2021-04-02 20:00 | 44288.8333 | 0 | 10.7938 | 37.78
2021-04-02 20:30 | 44288.8542 | 0 | 10.3633 | 37.78
2021-04-02 21:00 | 44288.875 | 0 | 9.9988 | 37.78
2021-04-02 21:30 | 44288.8958 | 0 | 9.7785 | 37.78
2021-04-02 22:00 | 44288.9167 | 0 | 9.6718 | 37.78
2021-04-02 22:30 | 44288.9375 | 0 | 9.0087 | 37.78
2021-04-02 23:00 | 44288.9583 | 0 | 8.5145 | 37.78
2021-04-02 23:30 | 44288.9792 | 0 | 8.2651 | 37.78
2021-04-03 | 44289 | 0 | 7.9042 | 37.78
2021-04-03 00:30 | 44289.0208 | 0 | 7.6942 | 37.78
2021-04-03 01:00 | 44289.0417 | 0 | 7.5249 | 37.78
2021-04-03 01:30 | 44289.0625 | 0 | 7.4356 | 37.78
2021-04-03 02:00 | 44289.0833 | 0 | 7.3686 | 37.78
2021-04-03 02:30 | 44289.1042 | 0 | 7.3028 | 37.78
2021-04-03 03:00 | 44289.125 | 0 | 7.4144 | 37.78
2021-04-03 03:30 | 44289.1458 | 0 | 7.4133 | 37.78
2021-04-03 04:00 | 44289.1667 | 0 | 7.4179 | 37.78
2021-04-03 04:30 | 44289.1875 | 0 | 7.5284 | 37.78
2021-04-03 05:00 | 44289.2083 | 0 | 7.6397 | 37.78
2021-04-03 05:30 | 44289.2292 | 0 | 7.8388 | 37.78
2021-04-03 06:00 | 44289.25 | 0 | 7.7787 | 37.78
2021-04-03 06:30 | 44289.2708 | 0 | 8.2357 | 37.78
2021-04-03 07:00 | 44289.2917 | 0 | 8.4922 | 37.78
2021-04-03 07:30 | 44289.3125 | 0 | 8.6811 | 37.78
2021-04-03 08:00 | 44289.3333 | 0 | 8.7398 | 37.78
2021-04-03 08:30 | 44289.3542 | 0 | 9.0694 | 37.78
2021-04-03 09:00 | 44289.375 | 0 | 9.0881 | 37.78
2021-04-03 09:30 | 44289.3958 | 0 | 10.118 | 37.78
2021-04-03 10:00 | 44289.4167 | 0 | 9.3324 | 37.78
2021-04-03 10:30 | 44289.4375 | 0 | 8.9295 | 37.78
2021-04-03 11:00 | 44289.4583 | 0 | 9.2697 | 37.78
2021-04-03 11:30 | 44289.4792 | 0 | 8.9303 | 37.78
2021-04-03 12:00 | 44289.5 | 0 | 9.4688 | 37.78
2021-04-03 12:30 | 44289.5208 | 0 | 9.1012 | 37.78
2021-04-03 13:00 | 44289.5417 | 0 | 8.5392 | 37.78
2021-04-03 13:30 | 44289.5625 | 0 | 8.6113 | 37.78
2021-04-03 14:00 | 44289.5833 | 0 | 9.5282 | 37.78
2021-04-03 14:30 | 44289.6042 | 0 | 9.7494 | 37.78
2021-04-03 15:00 | 44289.625 | 0 | 9.1355 | 37.78
2021-04-03 15:30 | 44289.6458 | 0 | 9.0913 | 37.78
2021-04-03 16:00 | 44289.6667 | 0 | 9.2829 | 37.78
2021-04-03 16:30 | 44289.6875 | 0 | 10.0085 | 37.78
2021-04-03 17:00 | 44289.7083 | 0 | 10.1879 | 37.78
2021-04-03 17:30 | 44289.7292 | 0 | 10.9513 | 37.78
2021-04-03 18:00 | 44289.75 | 0 | 11.3458 | 37.78
2021-04-03 18:30 | 44289.7708 | 0 | 11.4822 | 37.78
2021-04-03 19:00 | 44289.7917 | 0 | 11.0712 | 37.78
2021-04-03 19:30 | 44289.8125 | 0 | 10.7942 | 37.78
2021-04-03 20:00 | 44289.8333 | 0 | 10.6425 | 37.78
2021-04-03 20:30 | 44289.8542 | 0 | 10.2613 | 37.78
2021-04-03 21:00 | 44289.875 | 0 | 9.8934 | 37.78
2021-04-03 21:30 | 44289.8958 | 0 | 9.7508 | 37.78
2021-04-03 22:00 | 44289.9167 | 0 | 9.4284 | 37.78
2021-04-03 22:30 | 44289.9375 | 0 | 8.9317 | 37.78
2021-04-03 23:00 | 44289.9583 | 0 | 8.4977 | 37.78
2021-04-03 23:30 | 44289.9792 | 0 | 8.3024 | 37.78
2021-04-04 | 44290 | 0 | 7.9545 | 37.78
2021-04-04 00:30 | 44290.0208 | 0 | 7.6996 | 37.78
2021-04-04 01:00 | 44290.0417 | 0 | 7.5226 | 37.78
2021-04-04 01:30 | 44290.0625 | 0 | 7.458 | 37.78
2021-04-04 02:00 | 44290.0833 | 0 | 7.4121 | 37.78
2021-04-04 02:30 | 44290.1042 | 0 | 7.2656 | 37.78
2021-04-04 03:00 | 44290.125 | 0 | 7.199 | 37.78
2021-04-04 03:30 | 44290.1458 | 0 | 7.219 | 37.78
2021-04-04 04:00 | 44290.1667 | 0 | 7.2898 | 37.78
2021-04-04 04:30 | 44290.1875 | 0 | 7.3486 | 37.78
2021-04-04 05:00 | 44290.2083 | 0 | 7.3486 | 37.78
2021-04-04 05:30 | 44290.2292 | 0 | 7.5279 | 37.78
2021-04-04 06:00 | 44290.25 | 0 | 7.575 | 37.78
2021-04-04 06:30 | 44290.2708 | 0 | 7.9127 | 37.78
2021-04-04 07:00 | 44290.2917 | 0 | 8.4191 | 37.78
2021-04-04 07:30 | 44290.3125 | 0 | 8.8501 | 37.78
2021-04-04 08:00 | 44290.3333 | 0 | 9.2571 | 37.78
2021-04-04 08:30 | 44290.3542 | 0 | 9.3302 | 37.78
2021-04-04 09:00 | 44290.375 | 0 | 9.8727 | 37.78
2021-04-04 09:30 | 44290.3958 | 0 | 9.6556 | 37.78
2021-04-04 10:00 | 44290.4167 | 0 | 9.1306 | 37.78
2021-04-04 10:30 | 44290.4375 | 0 | 9.9626 | 37.78
2021-04-04 11:00 | 44290.4583 | 0 | 9.8808 | 37.78
2021-04-04 11:30 | 44290.4792 | 0 | 10.4012 | 37.78
2021-04-04 12:00 | 44290.5 | 0 | 9.9609 | 37.78
2021-04-04 12:30 | 44290.5208 | 0 | 9.3564 | 37.78
2021-04-04 13:00 | 44290.5417 | 0 | 9.8799 | 37.78
2021-04-04 13:30 | 44290.5625 | 0 | 10.0686 | 37.78
2021-04-04 14:00 | 44290.5833 | 0 | 9.8287 | 37.78
2021-04-04 14:30 | 44290.6042 | 0 | 9.9403 | 37.78
2021-04-04 15:00 | 44290.625 | 0 | 9.9569 | 37.78
2021-04-04 15:30 | 44290.6458 | 0 | 9.9638 | 37.78
2021-04-04 16:00 | 44290.6667 | 0 | 10.2103 | 37.78
2021-04-04 16:30 | 44290.6875 | 0 | 10.3612 | 37.78
2021-04-04 17:00 | 44290.7083 | 0 | 10.664 | 37.78
2021-04-04 17:30 | 44290.7292 | 0 | 10.831 | 37.78
2021-04-04 18:00 | 44290.75 | 0 | 10.9877 | 37.78
2021-04-04 18:30 | 44290.7708 | 0 | 11.0768 | 37.78
2021-04-04 19:00 | 44290.7917 | 0 | 10.9157 | 37.78
2021-04-04 19:30 | 44290.8125 | 0 | 10.6026 | 37.78
2021-04-04 20:00 | 44290.8333 | 0 | 10.1144 | 37.78
2021-04-04 20:30 | 44290.8542 | 0 | 9.8728 | 37.78
2021-04-04 21:00 | 44290.875 | 0 | 9.4656 | 37.78
2021-04-04 21:30 | 44290.8958 | 0 | 9.3671 | 37.78
2021-04-04 22:00 | 44290.9167 | 0 | 9.2978 | 37.78
2021-04-04 22:30 | 44290.9375 | 0 | 8.7276 | 37.78
2021-04-04 23:00 | 44290.9583 | 0 | 8.3258 | 37.78
2021-04-04 23:30 | 44290.9792 | 0 | 8.0128 | 37.78
2021-04-05 | 44291 | 0 | 7.7994 | 37.78
2021-04-05 00:30 | 44291.0208 | 0 | 7.5144 | 37.78
2021-04-05 01:00 | 44291.0417 | 0 | 7.3526 | 37.78
2021-04-05 01:30 | 44291.0625 | 0 | 7.2781 | 37.78
2021-04-05 02:00 | 44291.0833 | 0 | 7.2593 | 37.78
2021-04-05 02:30 | 44291.1042 | 0 | 7.2421 | 37.78
2021-04-05 03:00 | 44291.125 | 0 | 7.1439 | 37.78
2021-04-05 03:30 | 44291.1458 | 0 | 7.4379 | 37.78
2021-04-05 04:00 | 44291.1667 | 0 | 7.3486 | 37.78
2021-04-05 04:30 | 44291.1875 | 0 | 7.4829 | 37.78
2021-04-05 05:00 | 44291.2083 | 0 | 7.5273 | 37.78
2021-04-05 05:30 | 44291.2292 | 0 | 7.6792 | 37.78
2021-04-05 06:00 | 44291.25 | 0 | 7.8434 | 37.78
2021-04-05 06:30 | 44291.2708 | 0 | 8.1995 | 37.78
2021-04-05 07:00 | 44291.2917 | 0 | 8.7734 | 37.78
2021-04-05 07:30 | 44291.3125 | 0 | 8.9608 | 37.78
2021-04-05 08:00 | 44291.3333 | 0 | 9.3977 | 37.78
2021-04-05 08:30 | 44291.3542 | 0 | 9.6618 | 37.78
2021-04-05 09:00 | 44291.375 | 0 | 9.8392 | 37.78
2021-04-05 09:30 | 44291.3958 | 0 | 10.3061 | 37.78
2021-04-05 10:00 | 44291.4167 | 0 | 9.977 | 37.78
2021-04-05 10:30 | 44291.4375 | 0 | 10.0919 | 37.78
2021-04-05 11:00 | 44291.4583 | 0 | 9.9182 | 37.78
2021-04-05 11:30 | 44291.4792 | 0 | 10.2219 | 37.78
2021-04-05 12:00 | 44291.5 | 0 | 10.3225 | 37.78
2021-04-05 12:30 | 44291.5208 | 0 | 9.965 | 37.78
2021-04-05 13:00 | 44291.5417 | 0 | 10.3712 | 37.78
2021-04-05 13:30 | 44291.5625 | 0 | 10.5273 | 37.78
2021-04-05 14:00 | 44291.5833 | 0 | 10.5857 | 37.78
2021-04-05 14:30 | 44291.6042 | 0 | 10.8777 | 37.78
2021-04-05 15:00 | 44291.625 | 0 | 10.6552 | 37.78
2021-04-05 15:30 | 44291.6458 | 0 | 11.1891 | 37.78
2021-04-05 16:00 | 44291.6667 | 0 | 11.0858 | 37.78
2021-04-05 16:30 | 44291.6875 | 0 | 11.7873 | 37.78
2021-04-05 17:00 | 44291.7083 | 0 | 12.1054 | 37.78
2021-04-05 17:30 | 44291.7292 | 0 | 12.5331 | 37.78
2021-04-05 18:00 | 44291.75 | 0 | 12.5275 | 37.78
2021-04-05 18:30 | 44291.7708 | 0 | 12.5287 | 37.78
2021-04-05 19:00 | 44291.7917 | 0 | 12.1129 | 37.78
2021-04-05 19:30 | 44291.8125 | 0 | 11.9708 | 37.78
2021-04-05 20:00 | 44291.8333 | 0 | 11.3845 | 37.78
2021-04-05 20:30 | 44291.8542 | 0 | 11.0023 | 37.78
2021-04-05 21:00 | 44291.875 | 0 | 10.563 | 37.78
2021-04-05 21:30 | 44291.8958 | 0 | 10.4282 | 37.78
2021-04-05 22:00 | 44291.9167 | 0 | 9.986 | 37.78
2021-04-05 22:30 | 44291.9375 | 0 | 9.5765 | 37.78
2021-04-05 23:00 | 44291.9583 | 0 | 9.1699 | 37.78
2021-04-05 23:30 | 44291.9792 | 0 | 8.8103 | 37.78
2021-04-06 | 44292 | 0 | 8.2863 | 37.78
2021-04-06 00:30 | 44292.0208 | 0 | 8.0758 | 37.78
2021-04-06 01:00 | 44292.0417 | 0 | 7.9527 | 37.78
2021-04-06 01:30 | 44292.0625 | 0 | 7.8209 | 37.78
2021-04-06 02:00 | 44292.0833 | 0 | 7.7451 | 37.78
2021-04-06 02:30 | 44292.1042 | 0 | 7.8622 | 37.78
2021-04-06 03:00 | 44292.125 | 0 | 7.7569 | 37.78
2021-04-06 03:30 | 44292.1458 | 0 | 7.8388 | 37.78
2021-04-06 04:00 | 44292.1667 | 0 | 8.1443 | 37.78
2021-04-06 04:30 | 44292.1875 | 0 | 8.7959 | 37.78
2021-04-06 05:00 | 44292.2083 | 0 | 9.4093 | 37.78
2021-04-06 05:30 | 44292.2292 | 0 | 10.0967 | 37.78
2021-04-06 06:00 | 44292.25 | 0 | 10.8391 | 37.78
2021-04-06 06:30 | 44292.2708 | 0 | 11.7609 | 37.78
2021-04-06 07:00 | 44292.2917 | 0 | 12.4475 | 37.78
2021-04-06 07:30 | 44292.3125 | 0 | 12.6949 | 37.78
2021-04-06 08:00 | 44292.3333 | 0 | 13.0569 | 37.78
2021-04-06 08:30 | 44292.3542 | 0 | 12.4118 | 37.78
2021-04-06 09:00 | 44292.375 | 0 | 13.4281 | 37.78
2021-04-06 09:30 | 44292.3958 | 0 | 13.6246 | 37.78
2021-04-06 10:00 | 44292.4167 | 0 | 13.0985 | 37.78
2021-04-06 10:30 | 44292.4375 | 0 | 12.842 | 37.78
2021-04-06 11:00 | 44292.4583 | 0 | 12.4824 | 37.78
2021-04-06 11:30 | 44292.4792 | 0 | 12.9735 | 37.78
2021-04-06 12:00 | 44292.5 | 0 | 12.5044 | 37.78
2021-04-06 12:30 | 44292.5208 | 0 | 11.7997 | 37.78
2021-04-06 13:00 | 44292.5417 | 0 | 12.9218 | 37.78
2021-04-06 13:30 | 44292.5625 | 0 | 12.7917 | 37.78
2021-04-06 14:00 | 44292.5833 | 0 | 12.2972 | 37.78
2021-04-06 14:30 | 44292.6042 | 0 | 13.6319 | 37.78
2021-04-06 15:00 | 44292.625 | 0 | 13.286 | 37.78
2021-04-06 15:30 | 44292.6458 | 0 | 13.4938 | 37.78
2021-04-06 16:00 | 44292.6667 | 0 | 13.5198 | 37.78
2021-04-06 16:30 | 44292.6875 | 0 | 13.5698 | 37.78
2021-04-06 17:00 | 44292.7083 | 0 | 13.82 | 37.78
2021-04-06 17:30 | 44292.7292 | 0 | 14.0859 | 37.78
2021-04-06 18:00 | 44292.75 | 0 | 14.3948 | 37.78
2021-04-06 18:30 | 44292.7708 | 0 | 14.2663 | 37.78
2021-04-06 19:00 | 44292.7917 | 0 | 13.9584 | 37.78
2021-04-06 19:30 | 44292.8125 | 0 | 13.5794 | 37.78
2021-04-06 20:00 | 44292.8333 | 0 | 13.2163 | 37.78
2021-04-06 20:30 | 44292.8542 | 0 | 12.7073 | 37.78
2021-04-06 21:00 | 44292.875 | 0 | 12.2394 | 37.78
2021-04-06 21:30 | 44292.8958 | 0 | 11.9838 | 37.78
2021-04-06 22:00 | 44292.9167 | 0 | 11.2415 | 37.78
2021-04-06 22:30 | 44292.9375 | 0 | 10.6391 | 37.78
2021-04-06 23:00 | 44292.9583 | 0 | 10.1697 | 37.78
2021-04-06 23:30 | 44292.9792 | 0 | 9.7334 | 37.78
2021-04-07 | 44293 | 0 | 9.4068 | 37.78
2021-04-07 00:30 | 44293.0208 | 0 | 8.8712 | 37.78
2021-04-07 01:00 | 44293.0417 | 0 | 8.7674 | 37.78
2021-04-07 01:30 | 44293.0625 | 0 | 8.5935 | 37.78
2021-04-07 02:00 | 44293.0833 | 0 | 8.4365 | 37.78
2021-04-07 02:30 | 44293.1042 | 0 | 8.2344 | 37.78
2021-04-07 03:00 | 44293.125 | 0 | 8.2345 | 37.78
2021-04-07 03:30 | 44293.1458 | 0 | 8.4229 | 37.78
2021-04-07 04:00 | 44293.1667 | 0 | 8.8265 | 37.78
2021-04-07 04:30 | 44293.1875 | 0 | 9.0513 | 37.78
2021-04-07 05:00 | 44293.2083 | 0 | 9.8641 | 37.78
2021-04-07 05:30 | 44293.2292 | 0 | 10.241 | 37.78
2021-04-07 06:00 | 44293.25 | 0 | 11.093 | 37.78
2021-04-07 06:30 | 44293.2708 | 0 | 11.4621 | 37.78
2021-04-07 07:00 | 44293.2917 | 0 | 12.1606 | 37.78
2021-04-07 07:30 | 44293.3125 | 0 | 12.5753 | 37.78
2021-04-07 08:00 | 44293.3333 | 0 | 12.0913 | 37.78
2021-04-07 08:30 | 44293.3542 | 0 | 12.1078 | 37.78
2021-04-07 09:00 | 44293.375 | 0 | 12.4035 | 37.78
2021-04-07 09:30 | 44293.3958 | 0 | 12.3806 | 37.78
2021-04-07 10:00 | 44293.4167 | 0 | 11.8857 | 37.78
2021-04-07 10:30 | 44293.4375 | 0 | 12.0162 | 37.78
2021-04-07 11:00 | 44293.4583 | 0 | 11.2279 | 37.78
2021-04-07 11:30 | 44293.4792 | 0 | 12.6901 | 37.78
2021-04-07 12:00 | 44293.5 | 0 | 11.6006 | 37.78
2021-04-07 12:30 | 44293.5208 | 0 | 12.8084 | 37.78
2021-04-07 13:00 | 44293.5417 | 0 | 11.482 | 37.78
2021-04-07 13:30 | 44293.5625 | 0 | 11.9487 | 37.78
2021-04-07 14:00 | 44293.5833 | 0 | 13.5445 | 37.78
2021-04-07 14:30 | 44293.6042 | 0 | 11.7247 | 37.78
2021-04-07 15:00 | 44293.625 | 0 | 13.6463 | 37.78
2021-04-07 15:30 | 44293.6458 | 0 | 13.9716 | 37.78
2021-04-07 16:00 | 44293.6667 | 0 | 14.0343 | 37.78
2021-04-07 16:30 | 44293.6875 | 0 | 13.943 | 37.78
2021-04-07 17:00 | 44293.7083 | 0 | 13.9888 | 37.78
2021-04-07 17:30 | 44293.7292 | 0 | 14.2812 | 37.78
2021-04-07 18:00 | 44293.75 | 0 | 14.6926 | 37.78
2021-04-07 18:30 | 44293.7708 | 0 | 14.8438 | 37.78
2021-04-07 19:00 | 44293.7917 | 0 | 14.4102 | 37.78
2021-04-07 19:30 | 44293.8125 | 0 | 14.1065 | 37.78
2021-04-07 20:00 | 44293.8333 | 0 | 13.6399 | 37.78
2021-04-07 20:30 | 44293.8542 | 0 | 13.1082 | 37.78
2021-04-07 21:00 | 44293.875 | 0 | 12.5052 | 37.78
2021-04-07 21:30 | 44293.8958 | 0 | 12.1678 | 37.78
2021-04-07 22:00 | 44293.9167 | 0 | 11.6634 | 37.78
2021-04-07 22:30 | 44293.9375 | 0 | 10.8177 | 37.78
2021-04-07 23:00 | 44293.9583 | 0 | 10.3993 | 37.78
2021-04-07 23:30 | 44293.9792 | 0 | 9.9791 | 37.78
2021-04-08 | 44294 | 0 | 9.3885 | 37.78
2021-04-08 00:30 | 44294.0208 | 0 | 8.9754 | 37.78
2021-04-08 01:00 | 44294.0417 | 0 | 8.7011 | 37.78
2021-04-08 01:30 | 44294.0625 | 0 | 8.5654 | 37.78
2021-04-08 02:00 | 44294.0833 | 0 | 8.3559 | 37.78
2021-04-08 02:30 | 44294.1042 | 0 | 8.3726 | 37.78
2021-04-08 03:00 | 44294.125 | 0 | 8.2599 | 37.78
2021-04-08 03:30 | 44294.1458 | 0 | 8.4429 | 37.78
2021-04-08 04:00 | 44294.1667 | 0 | 8.7234 | 37.78
2021-04-08 04:30 | 44294.1875 | 0 | 9.0035 | 37.78
2021-04-08 05:00 | 44294.2083 | 0 | 9.3772 | 37.78
2021-04-08 05:30 | 44294.2292 | 0 | 9.905 | 37.78
2021-04-08 06:00 | 44294.25 | 0 | 10.531 | 37.78
2021-04-08 06:30 | 44294.2708 | 0 | 11.048 | 37.78
2021-04-08 07:00 | 44294.2917 | 0 | 11.4065 | 37.78
2021-04-08 07:30 | 44294.3125 | 0 | 11.5013 | 37.78
2021-04-08 08:00 | 44294.3333 | 0 | 11.4324 | 37.78
2021-04-08 08:30 | 44294.3542 | 0 | 11.5927 | 37.78
2021-04-08 09:00 | 44294.375 | 0 | 11.2777 | 37.78
2021-04-08 09:30 | 44294.3958 | 0 | 11.4415 | 37.78
2021-04-08 10:00 | 44294.4167 | 0 | 10.8258 | 37.78
2021-04-08 10:30 | 44294.4375 | 0 | 10.8869 | 37.78
2021-04-08 11:00 | 44294.4583 | 0 | 11.4709 | 37.78
2021-04-08 11:30 | 44294.4792 | 0 | 11.7569 | 37.78
2021-04-08 12:00 | 44294.5 | 0 | 11.712 | 37.78
2021-04-08 12:30 | 44294.5208 | 0 | 11.8664 | 37.78
2021-04-08 13:00 | 44294.5417 | 0 | 13.3449 | 37.78
2021-04-08 13:30 | 44294.5625 | 0 | 13.1447 | 37.78
2021-04-08 14:00 | 44294.5833 | 0 | 12.982 | 37.78
2021-04-08 14:30 | 44294.6042 | 0 | 12.4318 | 37.78
2021-04-08 15:00 | 44294.625 | 0 | 13.2962 | 37.78
2021-04-08 15:30 | 44294.6458 | 0 | 13.4825 | 37.78
2021-04-08 16:00 | 44294.6667 | 0 | 13.9304 | 37.78
2021-04-08 16:30 | 44294.6875 | 0 | 14.6002 | 37.78
2021-04-08 17:00 | 44294.7083 | 0 | 14.5864 | 37.78
2021-04-08 17:30 | 44294.7292 | 0 | 14.5401 | 37.78
2021-04-08 18:00 | 44294.75 | 0 | 14.8289 | 37.78
2021-04-08 18:30 | 44294.7708 | 0 | 14.9554 | 37.78
2021-04-08 19:00 | 44294.7917 | 0 | 14.65 | 37.78
2021-04-08 19:30 | 44294.8125 | 0 | 14.3861 | 37.78
2021-04-08 20:00 | 44294.8333 | 0 | 13.9811 | 37.78
2021-04-08 20:30 | 44294.8542 | 0 | 13.5956 | 37.78
2021-04-08 21:00 | 44294.875 | 0 | 13.0893 | 37.78
2021-04-08 21:30 | 44294.8958 | 0 | 12.5509 | 37.78
2021-04-08 22:00 | 44294.9167 | 0 | 12.0161 | 37.78
2021-04-08 22:30 | 44294.9375 | 0 | 11.2058 | 37.78
2021-04-08 23:00 | 44294.9583 | 0 | 10.4503 | 37.78
2021-04-08 23:30 | 44294.9792 | 0 | 9.8866 | 37.78
2021-04-09 | 44295 | 0 | 9.0601 | 37.78
2021-04-09 00:30 | 44295.0208 | 0 | 8.91 | 37.78
2021-04-09 01:00 | 44295.0417 | 0 | 8.7235 | 37.78
2021-04-09 01:30 | 44295.0625 | 0 | 8.5009 | 37.78
2021-04-09 02:00 | 44295.0833 | 0 | 8.4417 | 37.78
2021-04-09 02:30 | 44295.1042 | 0 | 8.3971 | 37.78
2021-04-09 03:00 | 44295.125 | 0 | 8.3071 | 37.78
2021-04-09 03:30 | 44295.1458 | 0 | 8.558 | 37.78
2021-04-09 04:00 | 44295.1667 | 0 | 8.6882 | 37.78
2021-04-09 04:30 | 44295.1875 | 0 | 9.0392 | 37.78
2021-04-09 05:00 | 44295.2083 | 0 | 9.282 | 37.78
2021-04-09 05:30 | 44295.2292 | 0 | 9.8914 | 37.78
2021-04-09 06:00 | 44295.25 | 0 | 10.4796 | 37.78
2021-04-09 06:30 | 44295.2708 | 0 | 11.0198 | 37.78
2021-04-09 07:00 | 44295.2917 | 0 | 11.1475 | 37.78
2021-04-09 07:30 | 44295.3125 | 0 | 11.2791 | 37.78
2021-04-09 08:00 | 44295.3333 | 0 | 11.3748 | 37.78
2021-04-09 08:30 | 44295.3542 | 0 | 11.2264 | 37.78
2021-04-09 09:00 | 44295.375 | 0 | 10.9676 | 37.78
2021-04-09 09:30 | 44295.3958 | 0 | 11.0013 | 37.78
2021-04-09 10:00 | 44295.4167 | 0 | 10.6126 | 37.78
2021-04-09 10:30 | 44295.4375 | 0 | 10.78 | 37.78
2021-04-09 11:00 | 44295.4583 | 0 | 10.997 | 37.78
2021-04-09 11:30 | 44295.4792 | 0 | 11.1428 | 37.78
2021-04-09 12:00 | 44295.5 | 0 | 11.4504 | 37.78
2021-04-09 12:30 | 44295.5208 | 0 | 11.4872 | 37.78
2021-04-09 13:00 | 44295.5417 | 0 | 11.7408 | 37.78
2021-04-09 13:30 | 44295.5625 | 0 | 12.4474 | 37.78
2021-04-09 14:00 | 44295.5833 | 0 | 13.424 | 37.78
2021-04-09 14:30 | 44295.6042 | 0 | 13.9599 | 37.78
2021-04-09 15:00 | 44295.625 | 0 | 14.4632 | 37.78
2021-04-09 15:30 | 44295.6458 | 0 | 15.4626 | 37.78
2021-04-09 16:00 | 44295.6667 | 0 | 15.9142 | 37.78
2021-04-09 16:30 | 44295.6875 | 0 | 15.5329 | 37.78
2021-04-09 17:00 | 44295.7083 | 0 | 15.5433 | 37.78
2021-04-09 17:30 | 44295.7292 | 0 | 15.1078 | 37.78
2021-04-09 18:00 | 44295.75 | 0 | 15.1604 | 37.78
2021-04-09 18:30 | 44295.7708 | 0 | 15.2286 | 37.78
2021-04-09 19:00 | 44295.7917 | 0 | 14.8046 | 37.78
2021-04-09 19:30 | 44295.8125 | 0 | 14.5025 | 37.78
2021-04-09 20:00 | 44295.8333 | 0 | 14.1024 | 37.78
2021-04-09 20:30 | 44295.8542 | 0 | 13.7174 | 37.78
2021-04-09 21:00 | 44295.875 | 0 | 13.2121 | 37.78
2021-04-09 21:30 | 44295.8958 | 0 | 12.7451 | 37.78
2021-04-09 22:00 | 44295.9167 | 0 | 12.3325 | 37.78
2021-04-09 22:30 | 44295.9375 | 0 | 11.4245 | 37.78
2021-04-09 23:00 | 44295.9583 | 0 | 10.7233 | 37.78
2021-04-09 23:30 | 44295.9792 | 0 | 10.3609 | 37.78
2021-04-10 | 44296 | 0 | 9.6772 | 37.78
2021-04-10 00:30 | 44296.0208 | 0 | 9.22 | 37.78
2021-04-10 01:00 | 44296.0417 | 0 | 8.7227 | 37.78
2021-04-10 01:30 | 44296.0625 | 0 | 8.5252 | 37.78
2021-04-10 02:00 | 44296.0833 | 0 | 8.4383 | 37.78
2021-04-10 02:30 | 44296.1042 | 0 | 8.2542 | 37.78
2021-04-10 03:00 | 44296.125 | 0 | 8.1087 | 37.78
2021-04-10 03:30 | 44296.1458 | 0 | 8.3059 | 37.78
2021-04-10 04:00 | 44296.1667 | 0 | 8.2364 | 37.78
2021-04-10 04:30 | 44296.1875 | 0 | 8.2482 | 37.78
2021-04-10 05:00 | 44296.2083 | 0 | 8.3994 | 37.78
2021-04-10 05:30 | 44296.2292 | 0 | 8.5958 | 37.78
2021-04-10 06:00 | 44296.25 | 0 | 8.5399 | 37.78
2021-04-10 06:30 | 44296.2708 | 0 | 8.8884 | 37.78
2021-04-10 07:00 | 44296.2917 | 0 | 8.846 | 37.78
2021-04-10 07:30 | 44296.3125 | 0 | 8.7626 | 37.78
2021-04-10 08:00 | 44296.3333 | 0 | 8.7767 | 37.78
2021-04-10 08:30 | 44296.3542 | 0 | 8.7246 | 37.78
2021-04-10 09:00 | 44296.375 | 0 | 8.8272 | 37.78
2021-04-10 09:30 | 44296.3958 | 0 | 8.9496 | 37.78
2021-04-10 10:00 | 44296.4167 | 0 | 8.9331 | 37.78
2021-04-10 10:30 | 44296.4375 | 0 | 8.8088 | 37.78
2021-04-10 11:00 | 44296.4583 | 0 | 8.96 | 37.78
2021-04-10 11:30 | 44296.4792 | 0 | 9.1564 | 37.78
2021-04-10 12:00 | 44296.5 | 0 | 9.3055 | 37.78
2021-04-10 12:30 | 44296.5208 | 0 | 9.7576 | 37.78
2021-04-10 13:00 | 44296.5417 | 0 | 10.1887 | 37.78
2021-04-10 13:30 | 44296.5625 | 0 | 10.8309 | 37.78
2021-04-10 14:00 | 44296.5833 | 0 | 11.5273 | 37.78
2021-04-10 14:30 | 44296.6042 | 0 | 12.1543 | 37.78
2021-04-10 15:00 | 44296.625 | 0 | 13.0904 | 37.78
2021-04-10 15:30 | 44296.6458 | 0 | 13.1381 | 37.78
2021-04-10 16:00 | 44296.6667 | 0 | 13.6931 | 37.78
2021-04-10 16:30 | 44296.6875 | 0 | 13.9747 | 37.78
2021-04-10 17:00 | 44296.7083 | 0 | 14.0069 | 37.78
2021-04-10 17:30 | 44296.7292 | 0 | 13.9908 | 37.78
2021-04-10 18:00 | 44296.75 | 0 | 14.0081 | 37.78
2021-04-10 18:30 | 44296.7708 | 0 | 13.9659 | 37.78
2021-04-10 19:00 | 44296.7917 | 0 | 13.3971 | 37.78
2021-04-10 19:30 | 44296.8125 | 0 | 12.8758 | 37.78
2021-04-10 20:00 | 44296.8333 | 0 | 12.4331 | 37.78
2021-04-10 20:30 | 44296.8542 | 0 | 11.847 | 37.78
2021-04-10 21:00 | 44296.875 | 0 | 11.5369 | 37.78
2021-04-10 21:30 | 44296.8958 | 0 | 11.0947 | 37.78
2021-04-10 22:00 | 44296.9167 | 0 | 10.5461 | 37.78
2021-04-10 22:30 | 44296.9375 | 0 | 9.8362 | 37.78
2021-04-10 23:00 | 44296.9583 | 0 | 9.5283 | 37.78
2021-04-10 23:30 | 44296.9792 | 0 | 9.1059 | 37.78
2021-04-11 | 44297 | 0 | 8.6084 | 37.78
2021-04-11 00:30 | 44297.0208 | 0 | 8.2007 | 37.78
2021-04-11 01:00 | 44297.0417 | 0 | 7.9269 | 37.78
2021-04-11 01:30 | 44297.0625 | 0 | 7.9069 | 37.78
2021-04-11 02:00 | 44297.0833 | 0 | 7.9481 | 37.78
2021-04-11 02:30 | 44297.1042 | 0 | 7.7397 | 37.78
2021-04-11 03:00 | 44297.125 | 0 | 7.6566 | 37.78
2021-04-11 03:30 | 44297.1458 | 0 | 7.5954 | 37.78
2021-04-11 04:00 | 44297.1667 | 0 | 7.6366 | 37.78
2021-04-11 04:30 | 44297.1875 | 0 | 7.6632 | 37.78
2021-04-11 05:00 | 44297.2083 | 0 | 7.7487 | 37.78
2021-04-11 05:30 | 44297.2292 | 0 | 7.7886 | 37.78
2021-04-11 06:00 | 44297.25 | 0 | 7.8646 | 37.78
2021-04-11 06:30 | 44297.2708 | 0 | 8.2289 | 37.78
2021-04-11 07:00 | 44297.2917 | 0 | 8.3759 | 37.78
2021-04-11 07:30 | 44297.3125 | 0 | 8.4271 | 37.78
2021-04-11 08:00 | 44297.3333 | 0 | 9.245 | 37.78
2021-04-11 08:30 | 44297.3542 | 0 | 9.6114 | 37.78
2021-04-11 09:00 | 44297.375 | 0 | 8.9755 | 37.78
2021-04-11 09:30 | 44297.3958 | 0 | 9.5681 | 37.78
2021-04-11 10:00 | 44297.4167 | 0 | 8.4531 | 37.78
2021-04-11 10:30 | 44297.4375 | 0 | 7.3807 | 37.78
2021-04-11 11:00 | 44297.4583 | 0 | 7.4931 | 37.78
2021-04-11 11:30 | 44297.4792 | 0 | 7.0752 | 37.78
2021-04-11 12:00 | 44297.5 | 0 | 6.4049 | 37.78
2021-04-11 12:30 | 44297.5208 | 0 | 7.0783 | 37.78
2021-04-11 13:00 | 44297.5417 | 0 | 7.3496 | 37.78
2021-04-11 13:30 | 44297.5625 | 0 | 7.7911 | 37.78
2021-04-11 14:00 | 44297.5833 | 0 | 8.1386 | 37.78
2021-04-11 14:30 | 44297.6042 | 0 | 8.9698 | 37.78
2021-04-11 15:00 | 44297.625 | 0 | 9.681 | 37.78
2021-04-11 15:30 | 44297.6458 | 0 | 10.3475 | 37.78
2021-04-11 16:00 | 44297.6667 | 0 | 10.9294 | 37.78
2021-04-11 16:30 | 44297.6875 | 0 | 11.6058 | 37.78
2021-04-11 17:00 | 44297.7083 | 0 | 12.0223 | 37.78
2021-04-11 17:30 | 44297.7292 | 0 | 12.0897 | 37.78
2021-04-11 18:00 | 44297.75 | 0 | 12.5634 | 37.78
2021-04-11 18:30 | 44297.7708 | 0 | 12.5691 | 37.78
2021-04-11 19:00 | 44297.7917 | 0 | 12.0764 | 37.78
2021-04-11 19:30 | 44297.8125 | 0 | 11.6318 | 37.78
2021-04-11 20:00 | 44297.8333 | 0 | 11.2623 | 37.78
2021-04-11 20:30 | 44297.8542 | 0 | 10.6487 | 37.78
2021-04-11 21:00 | 44297.875 | 0 | 10.3214 | 37.78
2021-04-11 21:30 | 44297.8958 | 0 | 9.8807 | 37.78
2021-04-11 22:00 | 44297.9167 | 0 | 9.6887 | 37.78
2021-04-11 22:30 | 44297.9375 | 0 | 8.8472 | 37.78
2021-04-11 23:00 | 44297.9583 | 0 | 8.3928 | 37.78
2021-04-11 23:30 | 44297.9792 | 0 | 8.0563 | 37.78
2021-04-12 | 44298 | 0 | 7.7804 | 37.78
2021-04-12 00:30 | 44298.0208 | 0 | 7.5662 | 37.78
2021-04-12 01:00 | 44298.0417 | 0 | 7.3933 | 37.78
2021-04-12 01:30 | 44298.0625 | 0 | 7.2401 | 37.78
2021-04-12 02:00 | 44298.0833 | 0 | 7.1284 | 37.78
2021-04-12 02:30 | 44298.1042 | 0 | 7.0548 | 37.78
2021-04-12 03:00 | 44298.125 | 0 | 7.0167 | 37.78
2021-04-12 03:30 | 44298.1458 | 0 | 7.2838 | 37.78
2021-04-12 04:00 | 44298.1667 | 0 | 7.5739 | 37.78
2021-04-12 04:30 | 44298.1875 | 0 | 7.9347 | 37.78
2021-04-12 05:00 | 44298.2083 | 0 | 8.5153 | 37.78
2021-04-12 05:30 | 44298.2292 | 0 | 9.0616 | 37.78
2021-04-12 06:00 | 44298.25 | 0 | 9.6685 | 37.78
2021-04-12 06:30 | 44298.2708 | 0 | 10.3894 | 37.78
2021-04-12 07:00 | 44298.2917 | 0 | 10.3634 | 37.78
2021-04-12 07:30 | 44298.3125 | 0 | 10.3186 | 37.78
2021-04-12 08:00 | 44298.3333 | 0 | 10.0409 | 37.78
2021-04-12 08:30 | 44298.3542 | 0 | 9.6349 | 37.78
2021-04-12 09:00 | 44298.375 | 0 | 9.3122 | 37.78
2021-04-12 09:30 | 44298.3958 | 0 | 8.9731 | 37.78
2021-04-12 10:00 | 44298.4167 | 0 | 8.7588 | 37.78
2021-04-12 10:30 | 44298.4375 | 0 | 8.7246 | 37.78
2021-04-12 11:00 | 44298.4583 | 0 | 8.4746 | 37.78
2021-04-12 11:30 | 44298.4792 | 0 | 8.8054 | 37.78
2021-04-12 12:00 | 44298.5 | 0 | 9.1303 | 37.78
2021-04-12 12:30 | 44298.5208 | 0 | 9.6558 | 37.78
2021-04-12 13:00 | 44298.5417 | 0 | 9.5308 | 37.78
2021-04-12 13:30 | 44298.5625 | 0 | 10.6072 | 37.78
2021-04-12 14:00 | 44298.5833 | 0 | 10.8837 | 37.78
2021-04-12 14:30 | 44298.6042 | 0 | 10.847 | 37.78
2021-04-12 15:00 | 44298.625 | 0 | 11.1279 | 37.78
2021-04-12 15:30 | 44298.6458 | 0 | 11.9034 | 37.78
2021-04-12 16:00 | 44298.6667 | 0 | 12.2165 | 37.78
2021-04-12 16:30 | 44298.6875 | 0 | 12.4195 | 37.78
2021-04-12 17:00 | 44298.7083 | 0 | 12.9199 | 37.78
2021-04-12 17:30 | 44298.7292 | 0 | 13.4201 | 37.78
2021-04-12 18:00 | 44298.75 | 0 | 12.5749 | 37.78
2021-04-12 18:30 | 44298.7708 | 0 | 12.7327 | 37.78
2021-04-12 19:00 | 44298.7917 | 0 | 13.1093 | 37.78
2021-04-12 19:30 | 44298.8125 | 0 | 12.7061 | 37.78
2021-04-12 20:00 | 44298.8333 | 0 | 12.4225 | 37.78
2021-04-12 20:30 | 44298.8542 | 0 | 12.0561 | 37.78
2021-04-12 21:00 | 44298.875 | 0 | 11.3465 | 37.78
2021-04-12 21:30 | 44298.8958 | 0 | 11.0069 | 37.78
2021-04-12 22:00 | 44298.9167 | 0 | 10.4765 | 37.78
2021-04-12 22:30 | 44298.9375 | 0 | 9.8543 | 37.78
2021-04-12 23:00 | 44298.9583 | 0 | 9.2914 | 37.78
2021-04-12 23:30 | 44298.9792 | 0 | 8.944 | 37.78
2021-04-13 | 44299 | 0 | 8.4955 | 37.78
2021-04-13 00:30 | 44299.0208 | 0 | 8.0621 | 37.78
2021-04-13 01:00 | 44299.0417 | 0 | 7.8639 | 37.78
2021-04-13 01:30 | 44299.0625 | 0 | 7.8164 | 37.78
2021-04-13 02:00 | 44299.0833 | 0 | 7.8599 | 37.78
2021-04-13 02:30 | 44299.1042 | 0 | 7.7114 | 37.78
2021-04-13 03:00 | 44299.125 | 0 | 7.6643 | 37.78
2021-04-13 03:30 | 44299.1458 | 0 | 7.8599 | 37.78
2021-04-13 04:00 | 44299.1667 | 0 | 8.0039 | 37.78
2021-04-13 04:30 | 44299.1875 | 0 | 8.4194 | 37.78
2021-04-13 05:00 | 44299.2083 | 0 | 8.6382 | 37.78
2021-04-13 05:30 | 44299.2292 | 0 | 9.4582 | 37.78
2021-04-13 06:00 | 44299.25 | 0 | 10.0548 | 37.78
2021-04-13 06:30 | 44299.2708 | 0 | 10.5846 | 37.78
2021-04-13 07:00 | 44299.2917 | 0 | 10.635 | 37.78
2021-04-13 07:30 | 44299.3125 | 0 | 10.4652 | 37.78
2021-04-13 08:00 | 44299.3333 | 0 | 10.1367 | 37.78
2021-04-13 08:30 | 44299.3542 | 0 | 9.8605 | 37.78
2021-04-13 09:00 | 44299.375 | 0 | 9.5338 | 37.78
2021-04-13 09:30 | 44299.3958 | 0 | 9.4018 | 37.78
2021-04-13 10:00 | 44299.4167 | 0 | 8.9899 | 37.78
2021-04-13 10:30 | 44299.4375 | 0 | 9.2718 | 37.78
2021-04-13 11:00 | 44299.4583 | 0 | 9.4797 | 37.78
2021-04-13 11:30 | 44299.4792 | 0 | 11.1515 | 37.78
2021-04-13 12:00 | 44299.5 | 0 | 9.0111 | 37.78
2021-04-13 12:30 | 44299.5208 | 0 | 9.4769 | 37.78
2021-04-13 13:00 | 44299.5417 | 0 | 9.8054 | 37.78
2021-04-13 13:30 | 44299.5625 | 0 | 10.4932 | 37.78
2021-04-13 14:00 | 44299.5833 | 0 | 11.331 | 37.78
2021-04-13 14:30 | 44299.6042 | 0 | 10.8805 | 37.78
2021-04-13 15:00 | 44299.625 | 0 | 11.628 | 37.78
2021-04-13 15:30 | 44299.6458 | 0 | 11.824 | 37.78
2021-04-13 16:00 | 44299.6667 | 0 | 12.2048 | 37.78
2021-04-13 16:30 | 44299.6875 | 0 | 12.8541 | 37.78
2021-04-13 17:00 | 44299.7083 | 0 | 12.7675 | 37.78
2021-04-13 17:30 | 44299.7292 | 0 | 13.0564 | 37.78
2021-04-13 18:00 | 44299.75 | 0 | 13.4591 | 37.78
2021-04-13 18:30 | 44299.7708 | 0 | 13.5524 | 37.78
2021-04-13 19:00 | 44299.7917 | 0 | 13.0869 | 37.78
2021-04-13 19:30 | 44299.8125 | 0 | 12.9092 | 37.78
2021-04-13 20:00 | 44299.8333 | 0 | 12.478 | 37.78
2021-04-13 20:30 | 44299.8542 | 0 | 12.0656 | 37.78
2021-04-13 21:00 | 44299.875 | 0 | 11.5022 | 37.78
2021-04-13 21:30 | 44299.8958 | 0 | 11.1422 | 37.78
2021-04-13 22:00 | 44299.9167 | 0 | 10.622 | 37.78
2021-04-13 22:30 | 44299.9375 | 0 | 9.8458 | 37.78
2021-04-13 23:00 | 44299.9583 | 0 | 9.0881 | 37.78
2021-04-13 23:30 | 44299.9792 | 0 | 8.706 | 37.78
2021-04-14 | 44300 | 0 | 8.1729 | 37.78
2021-04-14 00:30 | 44300.0208 | 0 | 8.0821 | 37.78
2021-04-14 01:00 | 44300.0417 | 0 | 7.9058 | 37.78
2021-04-14 01:30 | 44300.0625 | 0 | 7.7769 | 37.78
2021-04-14 02:00 | 44300.0833 | 0 | 7.7739 | 37.78
2021-04-14 02:30 | 44300.1042 | 0 | 7.5506 | 37.78
2021-04-14 03:00 | 44300.125 | 0 | 7.5943 | 37.78
2021-04-14 03:30 | 44300.1458 | 0 | 7.7016 | 37.78
2021-04-14 04:00 | 44300.1667 | 0 | 8.0717 | 37.78
2021-04-14 04:30 | 44300.1875 | 0 | 8.3817 | 37.78
2021-04-14 05:00 | 44300.2083 | 0 | 8.849 | 37.78
2021-04-14 05:30 | 44300.2292 | 0 | 9.5097 | 37.78
2021-04-14 06:00 | 44300.25 | 0 | 10.0008 | 37.78
2021-04-14 06:30 | 44300.2708 | 0 | 10.7224 | 37.78
2021-04-14 07:00 | 44300.2917 | 0 | 10.9504 | 37.78
2021-04-14 07:30 | 44300.3125 | 0 | 10.6269 | 37.78
2021-04-14 08:00 | 44300.3333 | 0 | 10.4212 | 37.78
2021-04-14 08:30 | 44300.3542 | 0 | 9.9208 | 37.78
2021-04-14 09:00 | 44300.375 | 0 | 9.5572 | 37.78
2021-04-14 09:30 | 44300.3958 | 0 | 9.3253 | 37.78
2021-04-14 10:00 | 44300.4167 | 0 | 9.1245 | 37.78
2021-04-14 10:30 | 44300.4375 | 0 | 9.401 | 37.78
2021-04-14 11:00 | 44300.4583 | 0 | 9.1609 | 37.78
2021-04-14 11:30 | 44300.4792 | 0 | 9.4272 | 37.78
2021-04-14 12:00 | 44300.5 | 0 | 9.6703 | 37.78
2021-04-14 12:30 | 44300.5208 | 0 | 10.0675 | 37.78
2021-04-14 13:00 | 44300.5417 | 0 | 9.8585 | 37.78
2021-04-14 13:30 | 44300.5625 | 0 | 10.0815 | 37.78
2021-04-14 14:00 | 44300.5833 | 0 | 10.8812 | 37.78
2021-04-14 14:30 | 44300.6042 | 0 | 11.5604 | 37.78
2021-04-14 15:00 | 44300.625 | 0 | 11.6553 | 37.78
2021-04-14 15:30 | 44300.6458 | 0 | 11.7696 | 37.78
2021-04-14 16:00 | 44300.6667 | 0 | 12.3134 | 37.78
2021-04-14 16:30 | 44300.6875 | 0 | 13.0019 | 37.78
2021-04-14 17:00 | 44300.7083 | 0 | 13.1986 | 37.78
2021-04-14 17:30 | 44300.7292 | 0 | 13.6276 | 37.78
2021-04-14 18:00 | 44300.75 | 0 | 13.8239 | 37.78
2021-04-14 18:30 | 44300.7708 | 0 | 13.9842 | 37.78
2021-04-14 19:00 | 44300.7917 | 0 | 13.7069 | 37.78
2021-04-14 19:30 | 44300.8125 | 0 | 13.3504 | 37.78
2021-04-14 20:00 | 44300.8333 | 0 | 12.8572 | 37.78
2021-04-14 20:30 | 44300.8542 | 0 | 12.2913 | 37.78
2021-04-14 21:00 | 44300.875 | 0 | 11.8194 | 37.78
2021-04-14 21:30 | 44300.8958 | 0 | 11.5895 | 37.78
2021-04-14 22:00 | 44300.9167 | 0 | 11.0363 | 37.78
2021-04-14 22:30 | 44300.9375 | 0 | 10.2034 | 37.78
2021-04-14 23:00 | 44300.9583 | 0 | 9.5784 | 37.78
2021-04-14 23:30 | 44300.9792 | 0 | 9.1631 | 37.78
2021-04-15 | 44301 | 0 | 8.7095 | 37.78
2021-04-15 00:30 | 44301.0208 | 0 | 8.2746 | 37.78
2021-04-15 01:00 | 44301.0417 | 0 | 8.0351 | 37.78
2021-04-15 01:30 | 44301.0625 | 0 | 7.8388 | 37.78
2021-04-15 02:00 | 44301.0833 | 0 | 7.9304 | 37.78
2021-04-15 02:30 | 44301.1042 | 0 | 7.9269 | 37.78
2021-04-15 03:00 | 44301.125 | 0 | 7.8634 | 37.78
2021-04-15 03:30 | 44301.1458 | 0 | 8.0652 | 37.78
2021-04-15 04:00 | 44301.1667 | 0 | 8.1909 | 37.78
2021-04-15 04:30 | 44301.1875 | 0 | 8.491 | 37.78
2021-04-15 05:00 | 44301.2083 | 0 | 8.986 | 37.78
2021-04-15 05:30 | 44301.2292 | 0 | 9.4853 | 37.78
2021-04-15 06:00 | 44301.25 | 0 | 10.2181 | 37.78
2021-04-15 06:30 | 44301.2708 | 0 | 10.7903 | 37.78
2021-04-15 07:00 | 44301.2917 | 0 | 10.8157 | 37.78
2021-04-15 07:30 | 44301.3125 | 0 | 10.7139 | 37.78
2021-04-15 08:00 | 44301.3333 | 0 | 10.4327 | 37.78
2021-04-15 08:30 | 44301.3542 | 0 | 10.3621 | 37.78
2021-04-15 09:00 | 44301.375 | 0 | 9.838 | 37.78
2021-04-15 09:30 | 44301.3958 | 0 | 9.7379 | 37.78
2021-04-15 10:00 | 44301.4167 | 0 | 9.4532 | 37.78
2021-04-15 10:30 | 44301.4375 | 0 | 9.9168 | 37.78
2021-04-15 11:00 | 44301.4583 | 0 | 9.7284 | 37.78
2021-04-15 11:30 | 44301.4792 | 0 | 10.0008 | 37.78
2021-04-15 12:00 | 44301.5 | 0 | 9.8048 | 37.78
2021-04-15 12:30 | 44301.5208 | 0 | 10.5571 | 37.78
2021-04-15 13:00 | 44301.5417 | 0 | 10.6679 | 37.78
2021-04-15 13:30 | 44301.5625 | 0 | 10.9069 | 37.78
2021-04-15 14:00 | 44301.5833 | 0 | 11.1619 | 37.78
2021-04-15 14:30 | 44301.6042 | 0 | 11.8154 | 37.78
2021-04-15 15:00 | 44301.625 | 0 | 12.2741 | 37.78
2021-04-15 15:30 | 44301.6458 | 0 | 12.7526 | 37.78
2021-04-15 16:00 | 44301.6667 | 0 | 13.3521 | 37.78
2021-04-15 16:30 | 44301.6875 | 0 | 13.7316 | 37.78
2021-04-15 17:00 | 44301.7083 | 0 | 13.8928 | 37.78
2021-04-15 17:30 | 44301.7292 | 0 | 14.2067 | 37.78
2021-04-15 18:00 | 44301.75 | 0 | 14.1812 | 37.78
2021-04-15 18:30 | 44301.7708 | 0 | 14.3364 | 37.78
2021-04-15 19:00 | 44301.7917 | 0 | 14.0853 | 37.78
2021-04-15 19:30 | 44301.8125 | 0 | 13.7099 | 37.78
2021-04-15 20:00 | 44301.8333 | 0 | 13.2628 | 37.78
2021-04-15 20:30 | 44301.8542 | 0 | 12.875 | 37.78
2021-04-15 21:00 | 44301.875 | 0 | 12.3721 | 37.78
2021-04-15 21:30 | 44301.8958 | 0 | 11.8459 | 37.78
2021-04-15 22:00 | 44301.9167 | 0 | 11.4402 | 37.78
2021-04-15 22:30 | 44301.9375 | 0 | 10.3815 | 37.78
2021-04-15 23:00 | 44301.9583 | 0 | 9.7662 | 37.78
2021-04-15 23:30 | 44301.9792 | 0 | 9.526 | 37.78
2021-04-16 | 44302 | 0 | 8.9626 | 37.78
2021-04-16 00:30 | 44302.0208 | 0 | 8.5806 | 37.78
2021-04-16 01:00 | 44302.0417 | 0 | 8.5334 | 37.78
2021-04-16 01:30 | 44302.0625 | 0 | 8.4152 | 37.78
2021-04-16 02:00 | 44302.0833 | 0 | 8.2959 | 37.78
2021-04-16 02:30 | 44302.1042 | 0 | 8.1856 | 37.78
2021-04-16 03:00 | 44302.125 | 0 | 8.1894 | 37.78
2021-04-16 03:30 | 44302.1458 | 0 | 8.2698 | 37.78
2021-04-16 04:00 | 44302.1667 | 0 | 8.3248 | 37.78
2021-04-16 04:30 | 44302.1875 | 0 | 8.8329 | 37.78
2021-04-16 05:00 | 44302.2083 | 0 | 9.3803 | 37.78
2021-04-16 05:30 | 44302.2292 | 0 | 9.6966 | 37.78
2021-04-16 06:00 | 44302.25 | 0 | 10.3112 | 37.78
2021-04-16 06:30 | 44302.2708 | 0 | 10.8181 | 37.78
2021-04-16 07:00 | 44302.2917 | 0 | 11.1486 | 37.78
2021-04-16 07:30 | 44302.3125 | 0 | 11.1405 | 37.78
2021-04-16 08:00 | 44302.3333 | 0 | 11.0547 | 37.78
2021-04-16 08:30 | 44302.3542 | 0 | 10.8216 | 37.78
2021-04-16 09:00 | 44302.375 | 0 | 10.7985 | 37.78
2021-04-16 09:30 | 44302.3958 | 0 | 10.513 | 37.78
2021-04-16 10:00 | 44302.4167 | 0 | 10.5175 | 37.78
2021-04-16 10:30 | 44302.4375 | 0 | 10.5187 | 37.78
2021-04-16 11:00 | 44302.4583 | 0 | 10.4505 | 37.78
2021-04-16 11:30 | 44302.4792 | 0 | 10.4975 | 37.78
2021-04-16 12:00 | 44302.5 | 0 | 10.5914 | 37.78
2021-04-16 12:30 | 44302.5208 | 0 | 11.0304 | 37.78
2021-04-16 13:00 | 44302.5417 | 0 | 11.0211 | 37.78
2021-04-16 13:30 | 44302.5625 | 0 | 11.7195 | 37.78
2021-04-16 14:00 | 44302.5833 | 0 | 12.4582 | 37.78
2021-04-16 14:30 | 44302.6042 | 0 | 14.2252 | 37.78
2021-04-16 15:00 | 44302.625 | 0 | 12.965 | 37.78
2021-04-16 15:30 | 44302.6458 | 0 | 14.2727 | 37.78
2021-04-16 16:00 | 44302.6667 | 0 | 14.2321 | 37.78
2021-04-16 16:30 | 44302.6875 | 0 | 14.1858 | 37.78
2021-04-16 17:00 | 44302.7083 | 0 | 14.1406 | 37.78
2021-04-16 17:30 | 44302.7292 | 0 | 14.294 | 37.78
2021-04-16 18:00 | 44302.75 | 0 | 14.3906 | 37.78
2021-04-16 18:30 | 44302.7708 | 0 | 14.0621 | 37.78
2021-04-16 19:00 | 44302.7917 | 0 | 13.8142 | 37.78
2021-04-16 19:30 | 44302.8125 | 0 | 13.5759 | 37.78
2021-04-16 20:00 | 44302.8333 | 0 | 13.3357 | 37.78
2021-04-16 20:30 | 44302.8542 | 0 | 12.8029 | 37.78
2021-04-16 21:00 | 44302.875 | 0 | 12.3113 | 37.78
2021-04-16 21:30 | 44302.8958 | 0 | 12.0577 | 37.78
2021-04-16 22:00 | 44302.9167 | 0 | 11.3776 | 37.78
2021-04-16 22:30 | 44302.9375 | 0 | 10.6333 | 37.78
2021-04-16 23:00 | 44302.9583 | 0 | 10.0674 | 37.78
2021-04-16 23:30 | 44302.9792 | 0 | 9.7664 | 37.78
2021-04-17 | 44303 | 0 | 9.2136 | 37.78
2021-04-17 00:30 | 44303.0208 | 0 | 8.8011 | 37.78
2021-04-17 01:00 | 44303.0417 | 0 | 8.3903 | 37.78
2021-04-17 01:30 | 44303.0625 | 0 | 8.2886 | 37.78
2021-04-17 02:00 | 44303.0833 | 0 | 8.2282 | 37.78
2021-04-17 02:30 | 44303.1042 | 0 | 8.1714 | 37.78
2021-04-17 03:00 | 44303.125 | 0 | 8.0163 | 37.78
2021-04-17 03:30 | 44303.1458 | 0 | 8.1005 | 37.78
2021-04-17 04:00 | 44303.1667 | 0 | 8.1291 | 37.78
2021-04-17 04:30 | 44303.1875 | 0 | 8.1939 | 37.78
2021-04-17 05:00 | 44303.2083 | 0 | 8.4417 | 37.78
2021-04-17 05:30 | 44303.2292 | 0 | 8.5345 | 37.78
2021-04-17 06:00 | 44303.25 | 0 | 8.6809 | 37.78
2021-04-17 06:30 | 44303.2708 | 0 | 9.1785 | 37.78
2021-04-17 07:00 | 44303.2917 | 0 | 9.6107 | 37.78
2021-04-17 07:30 | 44303.3125 | 0 | 10.018 | 37.78
2021-04-17 08:00 | 44303.3333 | 0 | 10.0508 | 37.78
2021-04-17 08:30 | 44303.3542 | 0 | 10.3351 | 37.78
2021-04-17 09:00 | 44303.375 | 0 | 10.8743 | 37.78
2021-04-17 09:30 | 44303.3958 | 0 | 10.7699 | 37.78
2021-04-17 10:00 | 44303.4167 | 0 | 10.8376 | 37.78
2021-04-17 10:30 | 44303.4375 | 0 | 10.0005 | 37.78
2021-04-17 11:00 | 44303.4583 | 0 | 9.5447 | 37.78
2021-04-17 11:30 | 44303.4792 | 0 | 10.7409 | 37.78
2021-04-17 12:00 | 44303.5 | 0 | 9.6158 | 37.78
2021-04-17 12:30 | 44303.5208 | 0 | 8.6132 | 37.78
2021-04-17 13:00 | 44303.5417 | 0 | 9.7346 | 37.78
2021-04-17 13:30 | 44303.5625 | 0 | 9.9208 | 37.78
2021-04-17 14:00 | 44303.5833 | 0 | 9.8515 | 37.78
2021-04-17 14:30 | 44303.6042 | 0 | 10.0674 | 37.78
2021-04-17 15:00 | 44303.625 | 0 | 9.9285 | 37.78
2021-04-17 15:30 | 44303.6458 | 0 | 10.27 | 37.78
2021-04-17 16:00 | 44303.6667 | 0 | 10.6428 | 37.78
2021-04-17 16:30 | 44303.6875 | 0 | 11.4144 | 37.78
2021-04-17 17:00 | 44303.7083 | 0 | 11.7882 | 37.78
2021-04-17 17:30 | 44303.7292 | 0 | 11.8566 | 37.78
2021-04-17 18:00 | 44303.75 | 0 | 11.9065 | 37.78
2021-04-17 18:30 | 44303.7708 | 0 | 11.8254 | 37.78
2021-04-17 19:00 | 44303.7917 | 0 | 11.4026 | 37.78
2021-04-17 19:30 | 44303.8125 | 0 | 11.3075 | 37.78
2021-04-17 20:00 | 44303.8333 | 0 | 10.9164 | 37.78
2021-04-17 20:30 | 44303.8542 | 0 | 10.431 | 37.78
2021-04-17 21:00 | 44303.875 | 0 | 9.9557 | 37.78
2021-04-17 21:30 | 44303.8958 | 0 | 9.8957 | 37.78
2021-04-17 22:00 | 44303.9167 | 0 | 9.6097 | 37.78
2021-04-17 22:30 | 44303.9375 | 0 | 8.9876 | 37.78
2021-04-17 23:00 | 44303.9583 | 0 | 8.5196 | 37.78
2021-04-17 23:30 | 44303.9792 | 0 | 8.1609 | 37.78
2021-04-18 | 44304 | 0 | 7.7714 | 37.78
2021-04-18 00:30 | 44304.0208 | 0 | 7.6246 | 37.78
2021-04-18 01:00 | 44304.0417 | 0 | 7.2581 | 37.78
2021-04-18 01:30 | 44304.0625 | 0 | 7.1848 | 37.78
2021-04-18 02:00 | 44304.0833 | 0 | 7.2781 | 37.78
2021-04-18 02:30 | 44304.1042 | 0 | 7.2041 | 37.78
2021-04-18 03:00 | 44304.125 | 0 | 7.1441 | 37.78
2021-04-18 03:30 | 44304.1458 | 0 | 7.0136 | 37.78
2021-04-18 04:00 | 44304.1667 | 0 | 7.0336 | 37.78
2021-04-18 04:30 | 44304.1875 | 0 | 7.0148 | 37.78
2021-04-18 05:00 | 44304.2083 | 0 | 7.1018 | 37.78
2021-04-18 05:30 | 44304.2292 | 0 | 7.2432 | 37.78
2021-04-18 06:00 | 44304.25 | 0 | 7.2721 | 37.78
2021-04-18 06:30 | 44304.2708 | 0 | 7.478 | 37.78
2021-04-18 07:00 | 44304.2917 | 0 | 7.1817 | 37.78
2021-04-18 07:30 | 44304.3125 | 0 | 6.9772 | 37.78
2021-04-18 08:00 | 44304.3333 | 0 | 7.1688 | 37.78
2021-04-18 08:30 | 44304.3542 | 0 | 6.962 | 37.78
2021-04-18 09:00 | 44304.375 | 0 | 6.6669 | 37.78
2021-04-18 09:30 | 44304.3958 | 0 | 6.3838 | 37.78
2021-04-18 10:00 | 44304.4167 | 0 | 6.1086 | 37.78
2021-04-18 10:30 | 44304.4375 | 0 | 6.0487 | 37.78
2021-04-18 11:00 | 44304.4583 | 0 | 5.8758 | 37.78
2021-04-18 11:30 | 44304.4792 | 0 | 6.0152 | 37.78
2021-04-18 12:00 | 44304.5 | 0 | 6.5821 | 37.78
2021-04-18 12:30 | 44304.5208 | 0 | 6.541 | 37.78
2021-04-18 13:00 | 44304.5417 | 0 | 6.4713 | 37.78
2021-04-18 13:30 | 44304.5625 | 0 | 7.5168 | 37.78
2021-04-18 14:00 | 44304.5833 | 0 | 7.4722 | 37.78
2021-04-18 14:30 | 44304.6042 | 0 | 8.4791 | 37.78
2021-04-18 15:00 | 44304.625 | 0 | 9.5347 | 37.78
2021-04-18 15:30 | 44304.6458 | 0 | 10.0621 | 37.78
2021-04-18 16:00 | 44304.6667 | 0 | 10.0266 | 37.78
2021-04-18 16:30 | 44304.6875 | 0 | 10.4248 | 37.78
2021-04-18 17:00 | 44304.7083 | 0 | 11.0783 | 37.78
2021-04-18 17:30 | 44304.7292 | 0 | 11.7385 | 37.78
2021-04-18 18:00 | 44304.75 | 0 | 12.2383 | 37.78
2021-04-18 18:30 | 44304.7708 | 0 | 12.2372 | 37.78
2021-04-18 19:00 | 44304.7917 | 0 | 11.6064 | 37.78
2021-04-18 19:30 | 44304.8125 | 0 | 11.2427 | 37.78
2021-04-18 20:00 | 44304.8333 | 0 | 10.9058 | 37.78
2021-04-18 20:30 | 44304.8542 | 0 | 10.5991 | 37.78
2021-04-18 21:00 | 44304.875 | 0 | 9.9414 | 37.78
2021-04-18 21:30 | 44304.8958 | 0 | 9.6712 | 37.78
2021-04-18 22:00 | 44304.9167 | 0 | 9.2944 | 37.78
2021-04-18 22:30 | 44304.9375 | 0 | 8.5418 | 37.78
2021-04-18 23:00 | 44304.9583 | 0 | 8.0786 | 37.78
2021-04-18 23:30 | 44304.9792 | 0 | 7.8588 | 37.78
2021-04-19 | 44305 | 0 | 7.6053 | 37.78
2021-04-19 00:30 | 44305.0208 | 0 | 7.3686 | 37.78
2021-04-19 01:00 | 44305.0417 | 0 | 7.1829 | 37.78
2021-04-19 01:30 | 44305.0625 | 0 | 7.2432 | 37.78
2021-04-19 02:00 | 44305.0833 | 0 | 7.2048 | 37.78
2021-04-19 02:30 | 44305.1042 | 0 | 7.1848 | 37.78
2021-04-19 03:00 | 44305.125 | 0 | 7.1484 | 37.78
2021-04-19 03:30 | 44305.1458 | 0 | 7.3274 | 37.78
2021-04-19 04:00 | 44305.1667 | 0 | 7.5315 | 37.78
2021-04-19 04:30 | 44305.1875 | 0 | 7.9042 | 37.78
2021-04-19 05:00 | 44305.2083 | 0 | 8.5375 | 37.78
2021-04-19 05:30 | 44305.2292 | 0 | 9.3298 | 37.78
2021-04-19 06:00 | 44305.25 | 0 | 10.082 | 37.78
2021-04-19 06:30 | 44305.2708 | 0 | 10.9096 | 37.78
2021-04-19 07:00 | 44305.2917 | 0 | 11.2121 | 37.78
2021-04-19 07:30 | 44305.3125 | 0 | 10.8832 | 37.78
2021-04-19 08:00 | 44305.3333 | 0 | 10.3969 | 37.78
2021-04-19 08:30 | 44305.3542 | 0 | 10.0686 | 37.78
2021-04-19 09:00 | 44305.375 | 0 | 9.7767 | 37.78
2021-04-19 09:30 | 44305.3958 | 0 | 9.5335 | 37.78
2021-04-19 10:00 | 44305.4167 | 0 | 9.3199 | 37.78
2021-04-19 10:30 | 44305.4375 | 0 | 9.0882 | 37.78
2021-04-19 11:00 | 44305.4583 | 0 | 9.1352 | 37.78
2021-04-19 11:30 | 44305.4792 | 0 | 9.1183 | 37.78
2021-04-19 12:00 | 44305.5 | 0 | 9.4474 | 37.78
2021-04-19 12:30 | 44305.5208 | 0 | 9.2662 | 37.78
2021-04-19 13:00 | 44305.5417 | 0 | 9.7677 | 37.78
2021-04-19 13:30 | 44305.5625 | 0 | 9.9108 | 37.78
2021-04-19 14:00 | 44305.5833 | 0 | 10.4847 | 37.78
2021-04-19 14:30 | 44305.6042 | 0 | 11.6851 | 37.78
2021-04-19 15:00 | 44305.625 | 0 | 12.4637 | 37.78
2021-04-19 15:30 | 44305.6458 | 0 | 12.2113 | 37.78
2021-04-19 16:00 | 44305.6667 | 0 | 12.2432 | 37.78
2021-04-19 16:30 | 44305.6875 | 0 | 13.1192 | 37.78
2021-04-19 17:00 | 44305.7083 | 0 | 13.2898 | 37.78
2021-04-19 17:30 | 44305.7292 | 0 | 13.8832 | 37.78
2021-04-19 18:00 | 44305.75 | 0 | 14.2001 | 37.78
2021-04-19 18:30 | 44305.7708 | 0 | 14.1375 | 37.78
2021-04-19 19:00 | 44305.7917 | 0 | 13.6008 | 37.78
2021-04-19 19:30 | 44305.8125 | 0 | 13.3962 | 37.78
2021-04-19 20:00 | 44305.8333 | 0 | 13.0208 | 37.78
2021-04-19 20:30 | 44305.8542 | 0 | 12.4558 | 37.78
2021-04-19 21:00 | 44305.875 | 0 | 11.8372 | 37.78
2021-04-19 21:30 | 44305.8958 | 0 | 11.5183 | 37.78
2021-04-19 22:00 | 44305.9167 | 0 | 10.9148 | 37.78
2021-04-19 22:30 | 44305.9375 | 0 | 10.0593 | 37.78
2021-04-19 23:00 | 44305.9583 | 0 | 9.3818 | 37.78
2021-04-19 23:30 | 44305.9792 | 0 | 9.2148 | 37.78
2021-04-20 | 44306 | 0 | 8.7427 | 37.78
2021-04-20 00:30 | 44306.0208 | 0 | 8.3491 | 37.78
2021-04-20 01:00 | 44306.0417 | 0 | 8.1686 | 37.78
2021-04-20 01:30 | 44306.0625 | 0 | 8.0351 | 37.78
2021-04-20 02:00 | 44306.0833 | 0 | 7.9493 | 37.78
2021-04-20 02:30 | 44306.1042 | 0 | 7.7402 | 37.78
2021-04-20 03:00 | 44306.125 | 0 | 7.6992 | 37.78
2021-04-20 03:30 | 44306.1458 | 0 | 7.9304 | 37.78
2021-04-20 04:00 | 44306.1667 | 0 | 8.2131 | 37.78
2021-04-20 04:30 | 44306.1875 | 0 | 8.5368 | 37.78
2021-04-20 05:00 | 44306.2083 | 0 | 9.0608 | 37.78
2021-04-20 05:30 | 44306.2292 | 0 | 9.76 | 37.78
2021-04-20 06:00 | 44306.25 | 0 | 10.6435 | 37.78
2021-04-20 06:30 | 44306.2708 | 0 | 11.195 | 37.78
2021-04-20 07:00 | 44306.2917 | 0 | 11.6165 | 37.78
2021-04-20 07:30 | 44306.3125 | 0 | 11.178 | 37.78
2021-04-20 08:00 | 44306.3333 | 0 | 10.7291 | 37.78
2021-04-20 08:30 | 44306.3542 | 0 | 10.2344 | 37.78
2021-04-20 09:00 | 44306.375 | 0 | 9.9065 | 37.78
2021-04-20 09:30 | 44306.3958 | 0 | 9.7915 | 37.78
2021-04-20 10:00 | 44306.4167 | 0 | 9.9231 | 37.78
2021-04-20 10:30 | 44306.4375 | 0 | 9.7838 | 37.78
2021-04-20 11:00 | 44306.4583 | 0 | 9.6649 | 37.78
2021-04-20 11:30 | 44306.4792 | 0 | 10.7233 | 37.78
2021-04-20 12:00 | 44306.5 | 0 | 11.8942 | 37.78
2021-04-20 12:30 | 44306.5208 | 0 | 11.0406 | 37.78
2021-04-20 13:00 | 44306.5417 | 0 | 10.5851 | 37.78
2021-04-20 13:30 | 44306.5625 | 0 | 10.3928 | 37.78
2021-04-20 14:00 | 44306.5833 | 0 | 10.8075 | 37.78
2021-04-20 14:30 | 44306.6042 | 0 | 11.3557 | 37.78
2021-04-20 15:00 | 44306.625 | 0 | 11.8451 | 37.78
2021-04-20 15:30 | 44306.6458 | 0 | 12.6578 | 37.78
2021-04-20 16:00 | 44306.6667 | 0 | 13.2185 | 37.78
2021-04-20 16:30 | 44306.6875 | 0 | 13.6306 | 37.78
2021-04-20 17:00 | 44306.7083 | 0 | 13.9516 | 37.78
2021-04-20 17:30 | 44306.7292 | 0 | 14.4101 | 37.78
2021-04-20 18:00 | 44306.75 | 0 | 14.6044 | 37.78
2021-04-20 18:30 | 44306.7708 | 0 | 14.5343 | 37.78
2021-04-20 19:00 | 44306.7917 | 0 | 14.1722 | 37.78
2021-04-20 19:30 | 44306.8125 | 0 | 13.8239 | 37.78
2021-04-20 20:00 | 44306.8333 | 0 | 13.4177 | 37.78
2021-04-20 20:30 | 44306.8542 | 0 | 12.8659 | 37.78
2021-04-20 21:00 | 44306.875 | 0 | 12.1394 | 37.78
2021-04-20 21:30 | 44306.8958 | 0 | 11.8435 | 37.78
2021-04-20 22:00 | 44306.9167 | 0 | 11.2318 | 37.78
2021-04-20 22:30 | 44306.9375 | 0 | 10.4579 | 37.78
2021-04-20 23:00 | 44306.9583 | 0 | 9.8367 | 37.78
2021-04-20 23:30 | 44306.9792 | 0 | 9.6389 | 37.78
2021-04-21 | 44307 | 0 | 8.9724 | 37.78
2021-04-21 00:30 | 44307.0208 | 0 | 8.4968 | 37.78
2021-04-21 01:00 | 44307.0417 | 0 | 8.3077 | 37.78
2021-04-21 01:30 | 44307.0625 | 0 | 8.1163 | 37.78
2021-04-21 02:00 | 44307.0833 | 0 | 8.0444 | 37.78
2021-04-21 02:30 | 44307.1042 | 0 | 8.0833 | 37.78
2021-04-21 03:00 | 44307.125 | 0 | 8.0609 | 37.78
2021-04-21 03:30 | 44307.1458 | 0 | 8.1768 | 37.78
2021-04-21 04:00 | 44307.1667 | 0 | 8.471 | 37.78
2021-04-21 04:30 | 44307.1875 | 0 | 8.6481 | 37.78
2021-04-21 05:00 | 44307.2083 | 0 | 9.2213 | 37.78
2021-04-21 05:30 | 44307.2292 | 0 | 9.8115 | 37.78
2021-04-21 06:00 | 44307.25 | 0 | 10.7743 | 37.78
2021-04-21 06:30 | 44307.2708 | 0 | 11.5353 | 37.78
2021-04-21 07:00 | 44307.2917 | 0 | 11.7847 | 37.78
2021-04-21 07:30 | 44307.3125 | 0 | 11.3932 | 37.78
2021-04-21 08:00 | 44307.3333 | 0 | 11.0752 | 37.78
2021-04-21 08:30 | 44307.3542 | 0 | 10.9187 | 37.78
2021-04-21 09:00 | 44307.375 | 0 | 10.6412 | 37.78
2021-04-21 09:30 | 44307.3958 | 0 | 10.6527 | 37.78
2021-04-21 10:00 | 44307.4167 | 0 | 10.6727 | 37.78
2021-04-21 10:30 | 44307.4375 | 0 | 10.3698 | 37.78
2021-04-21 11:00 | 44307.4583 | 0 | 10.3887 | 37.78
2021-04-21 11:30 | 44307.4792 | 0 | 10.5233 | 37.78
2021-04-21 12:00 | 44307.5 | 0 | 10.6724 | 37.78
2021-04-21 12:30 | 44307.5208 | 0 | 11.0123 | 37.78
2021-04-21 13:00 | 44307.5417 | 0 | 11.2547 | 37.78
2021-04-21 13:30 | 44307.5625 | 0 | 11.6788 | 37.78
2021-04-21 14:00 | 44307.5833 | 0 | 12.2613 | 37.78
2021-04-21 14:30 | 44307.6042 | 0 | 12.5344 | 37.78
2021-04-21 15:00 | 44307.625 | 0 | 12.934 | 37.78
2021-04-21 15:30 | 44307.6458 | 0 | 13.4517 | 37.78
2021-04-21 16:00 | 44307.6667 | 0 | 14.0119 | 37.78
2021-04-21 16:30 | 44307.6875 | 0 | 14.0519 | 37.78
2021-04-21 17:00 | 44307.7083 | 0 | 14.0738 | 37.78
2021-04-21 17:30 | 44307.7292 | 0 | 14.5178 | 37.78
2021-04-21 18:00 | 44307.75 | 0 | 14.7126 | 37.78
2021-04-21 18:30 | 44307.7708 | 0 | 14.6237 | 37.78
2021-04-21 19:00 | 44307.7917 | 0 | 14.092 | 37.78
2021-04-21 19:30 | 44307.8125 | 0 | 13.7735 | 37.78
2021-04-21 20:00 | 44307.8333 | 0 | 13.3574 | 37.78
2021-04-21 20:30 | 44307.8542 | 0 | 12.769 | 37.78
2021-04-21 21:00 | 44307.875 | 0 | 12.3005 | 37.78
2021-04-21 21:30 | 44307.8958 | 0 | 11.9019 | 37.78
2021-04-21 22:00 | 44307.9167 | 0 | 11.1894 | 37.78
2021-04-21 22:30 | 44307.9375 | 0 | 10.3789 | 37.78
2021-04-21 23:00 | 44307.9583 | 0 | 9.7465 | 37.78
2021-04-21 23:30 | 44307.9792 | 0 | 9.3511 | 37.78
2021-04-22 | 44308 | 0 | 8.7851 | 37.78
2021-04-22 00:30 | 44308.0208 | 0 | 8.4405 | 37.78
2021-04-22 01:00 | 44308.0417 | 0 | 8.2067 | 37.78
2021-04-22 01:30 | 44308.0625 | 0 | 8.0821 | 37.78
2021-04-22 02:00 | 44308.0833 | 0 | 8.0409 | 37.78
2021-04-22 02:30 | 44308.1042 | 0 | 7.9034 | 37.78
2021-04-22 03:00 | 44308.125 | 0 | 7.8001 | 37.78
2021-04-22 03:30 | 44308.1458 | 0 | 8.0409 | 37.78
2021-04-22 04:00 | 44308.1667 | 0 | 8.2161 | 37.78
2021-04-22 04:30 | 44308.1875 | 0 | 8.5176 | 37.78
2021-04-22 05:00 | 44308.2083 | 0 | 9.1202 | 37.78
2021-04-22 05:30 | 44308.2292 | 0 | 9.718 | 37.78
2021-04-22 06:00 | 44308.25 | 0 | 10.3425 | 37.78
2021-04-22 06:30 | 44308.2708 | 0 | 11.2414 | 37.78
2021-04-22 07:00 | 44308.2917 | 0 | 12.2072 | 37.78
2021-04-22 07:30 | 44308.3125 | 0 | 12.6826 | 37.78
2021-04-22 08:00 | 44308.3333 | 0 | 12.371 | 37.78
2021-04-22 08:30 | 44308.3542 | 0 | 12.1171 | 37.78
2021-04-22 09:00 | 44308.375 | 0 | 12.4291 | 37.78
2021-04-22 09:30 | 44308.3958 | 0 | 11.6409 | 37.78
2021-04-22 10:00 | 44308.4167 | 0 | 11.6744 | 37.78
2021-04-22 10:30 | 44308.4375 | 0 | 11.7156 | 37.78
2021-04-22 11:00 | 44308.4583 | 0 | 11.8106 | 37.78
2021-04-22 11:30 | 44308.4792 | 0 | 11.7355 | 37.78
2021-04-22 12:00 | 44308.5 | 0 | 11.1088 | 37.78
2021-04-22 12:30 | 44308.5208 | 0 | 11.5562 | 37.78
2021-04-22 13:00 | 44308.5417 | 0 | 12.4279 | 37.78
2021-04-22 13:30 | 44308.5625 | 0 | 11.8991 | 37.78
2021-04-22 14:00 | 44308.5833 | 0 | 11.8739 | 37.78
2021-04-22 14:30 | 44308.6042 | 0 | 12.5733 | 37.78
2021-04-22 15:00 | 44308.625 | 0 | 12.6414 | 37.78
2021-04-22 15:30 | 44308.6458 | 0 | 12.6014 | 37.78
2021-04-22 16:00 | 44308.6667 | 0 | 12.9507 | 37.78
2021-04-22 16:30 | 44308.6875 | 0 | 13.1863 | 37.78
2021-04-22 17:00 | 44308.7083 | 0 | 13.397 | 37.78
2021-04-22 17:30 | 44308.7292 | 0 | 13.3598 | 37.78
2021-04-22 18:00 | 44308.75 | 0 | 13.6452 | 37.78
2021-04-22 18:30 | 44308.7708 | 0 | 13.8558 | 37.78
2021-04-22 19:00 | 44308.7917 | 0 | 13.308 | 37.78
2021-04-22 19:30 | 44308.8125 | 0 | 13.194 | 37.78
2021-04-22 20:00 | 44308.8333 | 0 | 12.8412 | 37.78
2021-04-22 20:30 | 44308.8542 | 0 | 12.3806 | 37.78
2021-04-22 21:00 | 44308.875 | 0 | 11.8699 | 37.78
2021-04-22 21:30 | 44308.8958 | 0 | 11.4641 | 37.78
2021-04-22 22:00 | 44308.9167 | 0 | 10.8295 | 37.78
2021-04-22 22:30 | 44308.9375 | 0 | 9.9413 | 37.78
2021-04-22 23:00 | 44308.9583 | 0 | 9.2947 | 37.78
2021-04-22 23:30 | 44308.9792 | 0 | 8.9465 | 37.78
2021-04-23 | 44309 | 0 | 8.3716 | 37.78
2021-04-23 00:30 | 44309.0208 | 0 | 8.2686 | 37.78
2021-04-23 01:00 | 44309.0417 | 0 | 7.9458 | 37.78
2021-04-23 01:30 | 44309.0625 | 0 | 7.7869 | 37.78
2021-04-23 02:00 | 44309.0833 | 0 | 7.8145 | 37.78
2021-04-23 02:30 | 44309.1042 | 0 | 7.6397 | 37.78
2021-04-23 03:00 | 44309.125 | 0 | 7.5868 | 37.78
2021-04-23 03:30 | 44309.1458 | 0 | 7.8187 | 37.78
2021-04-23 04:00 | 44309.1667 | 0 | 8.1437 | 37.78
2021-04-23 04:30 | 44309.1875 | 0 | 8.4506 | 37.78
2021-04-23 05:00 | 44309.2083 | 0 | 8.9774 | 37.78
2021-04-23 05:30 | 44309.2292 | 0 | 9.7049 | 37.78
2021-04-23 06:00 | 44309.25 | 0 | 10.667 | 37.78
2021-04-23 06:30 | 44309.2708 | 0 | 11.683 | 37.78
2021-04-23 07:00 | 44309.2917 | 0 | 11.9417 | 37.78
2021-04-23 07:30 | 44309.3125 | 0 | 11.5899 | 37.78
2021-04-23 08:00 | 44309.3333 | 0 | 10.9911 | 37.78
2021-04-23 08:30 | 44309.3542 | 0 | 10.4703 | 37.78
2021-04-23 09:00 | 44309.375 | 0 | 9.7617 | 37.78
2021-04-23 09:30 | 44309.3958 | 0 | 9.4546 | 37.78
2021-04-23 10:00 | 44309.4167 | 0 | 8.9331 | 37.78
2021-04-23 10:30 | 44309.4375 | 0 | 8.8689 | 37.78
2021-04-23 11:00 | 44309.4583 | 0 | 8.7674 | 37.78
2021-04-23 11:30 | 44309.4792 | 0 | 8.5877 | 37.78
2021-04-23 12:00 | 44309.5 | 0 | 8.5288 | 37.78
2021-04-23 12:30 | 44309.5208 | 0 | 8.6216 | 37.78
2021-04-23 13:00 | 44309.5417 | 0 | 8.7723 | 37.78
2021-04-23 13:30 | 44309.5625 | 0 | 9.0547 | 37.78
2021-04-23 14:00 | 44309.5833 | 0 | 9.7269 | 37.78
2021-04-23 14:30 | 44309.6042 | 0 | 10.1572 | 37.78
2021-04-23 15:00 | 44309.625 | 0 | 10.5435 | 37.78
2021-04-23 15:30 | 44309.6458 | 0 | 11.2504 | 37.78
2021-04-23 16:00 | 44309.6667 | 0 | 11.8427 | 37.78
2021-04-23 16:30 | 44309.6875 | 0 | 12.1746 | 37.78
2021-04-23 17:00 | 44309.7083 | 0 | 12.3809 | 37.78
2021-04-23 17:30 | 44309.7292 | 0 | 12.7385 | 37.78
2021-04-23 18:00 | 44309.75 | 0 | 13.0403 | 37.78
2021-04-23 18:30 | 44309.7708 | 0 | 13.0308 | 37.78
2021-04-23 19:00 | 44309.7917 | 0 | 12.5742 | 37.78
2021-04-23 19:30 | 44309.8125 | 0 | 12.2423 | 37.78
2021-04-23 20:00 | 44309.8333 | 0 | 12.1787 | 37.78
2021-04-23 20:30 | 44309.8542 | 0 | 11.686 | 37.78
2021-04-23 21:00 | 44309.875 | 0 | 11.31 | 37.78
2021-04-23 21:30 | 44309.8958 | 0 | 11.0947 | 37.78
2021-04-23 22:00 | 44309.9167 | 0 | 10.5408 | 37.78
2021-04-23 22:30 | 44309.9375 | 0 | 9.8651 | 37.78
2021-04-23 23:00 | 44309.9583 | 0 | 9.3531 | 37.78
2021-04-23 23:30 | 44309.9792 | 0 | 8.9379 | 37.78
2021-04-24 | 44310 | 0 | 8.4163 | 37.78
2021-04-24 00:30 | 44310.0208 | 0 | 8.1233 | 37.78
2021-04-24 01:00 | 44310.0417 | 0 | 7.7557 | 37.78
2021-04-24 01:30 | 44310.0625 | 0 | 7.6219 | 37.78
2021-04-24 02:00 | 44310.0833 | 0 | 7.6343 | 37.78
2021-04-24 02:30 | 44310.1042 | 0 | 7.3686 | 37.78
2021-04-24 03:00 | 44310.125 | 0 | 7.3149 | 37.78
2021-04-24 03:30 | 44310.1458 | 0 | 7.5261 | 37.78
2021-04-24 04:00 | 44310.1667 | 0 | 7.5727 | 37.78
2021-04-24 04:30 | 44310.1875 | 0 | 7.8421 | 37.78
2021-04-24 05:00 | 44310.2083 | 0 | 7.9504 | 37.78
2021-04-24 05:30 | 44310.2292 | 0 | 8.0869 | 37.78
2021-04-24 06:00 | 44310.25 | 0 | 8.4687 | 37.78
2021-04-24 06:30 | 44310.2708 | 0 | 8.7407 | 37.78
2021-04-24 07:00 | 44310.2917 | 0 | 8.6874 | 37.78
2021-04-24 07:30 | 44310.3125 | 0 | 8.5064 | 37.78
2021-04-24 08:00 | 44310.3333 | 0 | 8.4787 | 37.78
2021-04-24 08:30 | 44310.3542 | 0 | 7.9882 | 37.78
2021-04-24 09:00 | 44310.375 | 0 | 7.6675 | 37.78
2021-04-24 09:30 | 44310.3958 | 0 | 7.3651 | 37.78
2021-04-24 10:00 | 44310.4167 | 0 | 6.9655 | 37.78
2021-04-24 10:30 | 44310.4375 | 0 | 6.7116 | 37.78
2021-04-24 11:00 | 44310.4583 | 0 | 6.3368 | 37.78
2021-04-24 11:30 | 44310.4792 | 0 | 6.786 | 37.78
2021-04-24 12:00 | 44310.5 | 0 | 7.2032 | 37.78
2021-04-24 12:30 | 44310.5208 | 0 | 7.5338 | 37.78
2021-04-24 13:00 | 44310.5417 | 0 | 6.55 | 37.78
2021-04-24 13:30 | 44310.5625 | 0 | 6.913 | 37.78
2021-04-24 14:00 | 44310.5833 | 0 | 7.7345 | 37.78
2021-04-24 14:30 | 44310.6042 | 0 | 8.0341 | 37.78
2021-04-24 15:00 | 44310.625 | 0 | 8.8395 | 37.78
2021-04-24 15:30 | 44310.6458 | 0 | 9.065 | 37.78
2021-04-24 16:00 | 44310.6667 | 0 | 9.6533 | 37.78
2021-04-24 16:30 | 44310.6875 | 0 | 10.3576 | 37.78
2021-04-24 17:00 | 44310.7083 | 0 | 10.722 | 37.78
2021-04-24 17:30 | 44310.7292 | 0 | 11.0956 | 37.78
2021-04-24 18:00 | 44310.75 | 0 | 11.2663 | 37.78
2021-04-24 18:30 | 44310.7708 | 0 | 11.2734 | 37.78
2021-04-24 19:00 | 44310.7917 | 0 | 10.925 | 37.78
2021-04-24 19:30 | 44310.8125 | 0 | 10.6505 | 37.78
2021-04-24 20:00 | 44310.8333 | 0 | 10.4706 | 37.78
2021-04-24 20:30 | 44310.8542 | 0 | 10.0815 | 37.78
2021-04-24 21:00 | 44310.875 | 0 | 9.8366 | 37.78
2021-04-24 21:30 | 44310.8958 | 0 | 9.4914 | 37.78
2021-04-24 22:00 | 44310.9167 | 0 | 9.166 | 37.78
2021-04-24 22:30 | 44310.9375 | 0 | 8.6423 | 37.78
2021-04-24 23:00 | 44310.9583 | 0 | 8.2228 | 37.78
2021-04-24 23:30 | 44310.9792 | 0 | 7.9266 | 37.78
2021-04-25 | 44311 | 0 | 7.6108 | 37.78
2021-04-25 00:30 | 44311.0208 | 0 | 7.324 | 37.78
2021-04-25 01:00 | 44311.0417 | 0 | 7.286 | 37.78
2021-04-25 01:30 | 44311.0625 | 0 | 6.9914 | 37.78
2021-04-25 02:00 | 44311.0833 | 0 | 7.0125 | 37.78
2021-04-25 02:30 | 44311.1042 | 0 | 6.9643 | 37.78
2021-04-25 03:00 | 44311.125 | 0 | 6.8607 | 37.78
2021-04-25 03:30 | 44311.1458 | 0 | 6.9431 | 37.78
2021-04-25 04:00 | 44311.1667 | 0 | 6.8973 | 37.78
2021-04-25 04:30 | 44311.1875 | 0 | 6.7914 | 37.78
2021-04-25 05:00 | 44311.2083 | 0 | 6.9042 | 37.78
2021-04-25 05:30 | 44311.2292 | 0 | 7.1644 | 37.78
2021-04-25 06:00 | 44311.25 | 0 | 7.3497 | 37.78
2021-04-25 06:30 | 44311.2708 | 0 | 7.2837 | 37.78
2021-04-25 07:00 | 44311.2917 | 0 | 7.3735 | 37.78
2021-04-25 07:30 | 44311.3125 | 0 | 6.9402 | 37.78
2021-04-25 08:00 | 44311.3333 | 0 | 6.5223 | 37.78
2021-04-25 08:30 | 44311.3542 | 0 | 6.4742 | 37.78
2021-04-25 09:00 | 44311.375 | 0 | 6.255 | 37.78
2021-04-25 09:30 | 44311.3958 | 0 | 6.0052 | 37.78
2021-04-25 10:00 | 44311.4167 | 0 | 5.6742 | 37.78
2021-04-25 10:30 | 44311.4375 | 0 | 5.5692 | 37.78
2021-04-25 11:00 | 44311.4583 | 0 | 5.3375 | 37.78
2021-04-25 11:30 | 44311.4792 | 0 | 5.3152 | 37.78
2021-04-25 12:00 | 44311.5 | 0 | 5.3398 | 37.78
2021-04-25 12:30 | 44311.5208 | 0 | 5.6055 | 37.78
2021-04-25 13:00 | 44311.5417 | 0 | 5.663 | 37.78
2021-04-25 13:30 | 44311.5625 | 0 | 5.9874 | 37.78
2021-04-25 14:00 | 44311.5833 | 0 | 6.3725 | 37.78
2021-04-25 14:30 | 44311.6042 | 0 | 7.6782 | 37.78
2021-04-25 15:00 | 44311.625 | 0 | 8.2698 | 37.78
2021-04-25 15:30 | 44311.6458 | 0 | 8.3099 | 37.78
2021-04-25 16:00 | 44311.6667 | 0 | 9.0464 | 37.78
2021-04-25 16:30 | 44311.6875 | 0 | 9.6192 | 37.78
2021-04-25 17:00 | 44311.7083 | 0 | 10.2413 | 37.78
2021-04-25 17:30 | 44311.7292 | 0 | 10.593 | 37.78
2021-04-25 18:00 | 44311.75 | 0 | 10.7962 | 37.78
2021-04-25 18:30 | 44311.7708 | 0 | 10.6876 | 37.78
2021-04-25 19:00 | 44311.7917 | 0 | 10.3993 | 37.78
2021-04-25 19:30 | 44311.8125 | 0 | 10.1562 | 37.78
2021-04-25 20:00 | 44311.8333 | 0 | 9.919 | 37.78
2021-04-25 20:30 | 44311.8542 | 0 | 9.6854 | 37.78
2021-04-25 21:00 | 44311.875 | 0 | 9.2906 | 37.78
2021-04-25 21:30 | 44311.8958 | 0 | 9.0459 | 37.78
2021-04-25 22:00 | 44311.9167 | 0 | 8.7887 | 37.78
2021-04-25 22:30 | 44311.9375 | 0 | 8.1747 | 37.78
2021-04-25 23:00 | 44311.9583 | 0 | 7.8256 | 37.78
2021-04-25 23:30 | 44311.9792 | 0 | 7.6038 | 37.78
2021-04-26 | 44312 | 0 | 7.4098 | 37.78
2021-04-26 00:30 | 44312.0208 | 0 | 7.1094 | 37.78
2021-04-26 01:00 | 44312.0417 | 0 | 6.9901 | 37.78
2021-04-26 01:30 | 44312.0625 | 0 | 6.8996 | 37.78
2021-04-26 02:00 | 44312.0833 | 0 | 6.8103 | 37.78
2021-04-26 02:30 | 44312.1042 | 0 | 6.8147 | 37.78
2021-04-26 03:00 | 44312.125 | 0 | 6.7103 | 37.78
2021-04-26 03:30 | 44312.1458 | 0 | 6.7284 | 37.78
2021-04-26 04:00 | 44312.1667 | 0 | 6.7703 | 37.78
2021-04-26 04:30 | 44312.1875 | 0 | 6.9913 | 37.78
2021-04-26 05:00 | 44312.2083 | 0 | 7.0986 | 37.78
2021-04-26 05:30 | 44312.2292 | 0 | 7.2828 | 37.78
2021-04-26 06:00 | 44312.25 | 0 | 7.6502 | 37.78
2021-04-26 06:30 | 44312.2708 | 0 | 7.7048 | 37.78
2021-04-26 07:00 | 44312.2917 | 0 | 7.662 | 37.78
2021-04-26 07:30 | 44312.3125 | 0 | 7.6284 | 37.78
2021-04-26 08:00 | 44312.3333 | 0 | 7.5685 | 37.78
2021-04-26 08:30 | 44312.3542 | 0 | 7.5003 | 37.78
2021-04-26 09:00 | 44312.375 | 0 | 7.306 | 37.78
2021-04-26 09:30 | 44312.3958 | 0 | 7.116 | 37.78
2021-04-26 10:00 | 44312.4167 | 0 | 6.9285 | 37.78
2021-04-26 10:30 | 44312.4375 | 0 | 8.0017 | 37.78
2021-04-26 11:00 | 44312.4583 | 0 | 7.0903 | 37.78
2021-04-26 11:30 | 44312.4792 | 0 | 8.7874 | 37.78
2021-04-26 12:00 | 44312.5 | 0 | 7.8971 | 37.78
2021-04-26 12:30 | 44312.5208 | 0 | 7.905 | 37.78
2021-04-26 13:00 | 44312.5417 | 0 | 8.6531 | 37.78
2021-04-26 13:30 | 44312.5625 | 0 | 8.0592 | 37.78
2021-04-26 14:00 | 44312.5833 | 0 | 8.2359 | 37.78
2021-04-26 14:30 | 44312.6042 | 0 | 9.4676 | 37.78
2021-04-26 15:00 | 44312.625 | 0 | 8.9628 | 37.78
2021-04-26 15:30 | 44312.6458 | 0 | 9.2826 | 37.78
2021-04-26 16:00 | 44312.6667 | 0 | 10.3675 | 37.78
2021-04-26 16:30 | 44312.6875 | 0 | 10.808 | 37.78
2021-04-26 17:00 | 44312.7083 | 0 | 11.5953 | 37.78
2021-04-26 17:30 | 44312.7292 | 0 | 12.1599 | 37.78
2021-04-26 18:00 | 44312.75 | 0 | 12.3955 | 37.78
2021-04-26 18:30 | 44312.7708 | 0 | 12.1061 | 37.78
2021-04-26 19:00 | 44312.7917 | 0 | 11.7177 | 37.78
2021-04-26 19:30 | 44312.8125 | 0 | 11.3898 | 37.78
2021-04-26 20:00 | 44312.8333 | 0 | 11.2029 | 37.78
2021-04-26 20:30 | 44312.8542 | 0 | 10.57 | 37.78
2021-04-26 21:00 | 44312.875 | 0 | 10.1158 | 37.78
2021-04-26 21:30 | 44312.8958 | 0 | 9.7261 | 37.78
2021-04-26 22:00 | 44312.9167 | 0 | 9.246 | 37.78
2021-04-26 22:30 | 44312.9375 | 0 | 8.5985 | 37.78
2021-04-26 23:00 | 44312.9583 | 0 | 8.1621 | 37.78
2021-04-26 23:30 | 44312.9792 | 0 | 7.8743 | 37.78
2021-04-27 | 44313 | 0 | 7.5026 | 37.78
2021-04-27 00:30 | 44313.0208 | 0 | 7.4325 | 37.78
2021-04-27 01:00 | 44313.0417 | 0 | 7.2303 | 37.78
2021-04-27 01:30 | 44313.0625 | 0 | 7.2209 | 37.78
2021-04-27 02:00 | 44313.0833 | 0 | 7.3263 | 37.78
2021-04-27 02:30 | 44313.1042 | 0 | 7.2241 | 37.78
2021-04-27 03:00 | 44313.125 | 0 | 7.1072 | 37.78
2021-04-27 03:30 | 44313.1458 | 0 | 7.3497 | 37.78
2021-04-27 04:00 | 44313.1667 | 0 | 7.6627 | 37.78
2021-04-27 04:30 | 44313.1875 | 0 | 8.2042 | 37.78
2021-04-27 05:00 | 44313.2083 | 0 | 8.4487 | 37.78
2021-04-27 05:30 | 44313.2292 | 0 | 9.2136 | 37.78
2021-04-27 06:00 | 44313.25 | 0 | 10.2365 | 37.78
2021-04-27 06:30 | 44313.2708 | 0 | 11.0971 | 37.78
2021-04-27 07:00 | 44313.2917 | 0 | 11.6448 | 37.78
2021-04-27 07:30 | 44313.3125 | 0 | 11.2827 | 37.78
2021-04-27 08:00 | 44313.3333 | 0 | 11.0916 | 37.78
2021-04-27 08:30 | 44313.3542 | 0 | 10.4757 | 37.78
2021-04-27 09:00 | 44313.375 | 0 | 10.0489 | 37.78
2021-04-27 09:30 | 44313.3958 | 0 | 9.7025 | 37.78
2021-04-27 10:00 | 44313.4167 | 0 | 9.4691 | 37.78
2021-04-27 10:30 | 44313.4375 | 0 | 9.5913 | 37.78
2021-04-27 11:00 | 44313.4583 | 0 | 10.4809 | 37.78
2021-04-27 11:30 | 44313.4792 | 0 | 10.9782 | 37.78
2021-04-27 12:00 | 44313.5 | 0 | 11.1717 | 37.78
2021-04-27 12:30 | 44313.5208 | 0 | 10.5117 | 37.78
2021-04-27 13:00 | 44313.5417 | 0 | 10.664 | 37.78
2021-04-27 13:30 | 44313.5625 | 0 | 10.444 | 37.78
2021-04-27 14:00 | 44313.5833 | 0 | 12.16 | 37.78
2021-04-27 14:30 | 44313.6042 | 0 | 11.4047 | 37.78
2021-04-27 15:00 | 44313.625 | 0 | 12.3166 | 37.78
2021-04-27 15:30 | 44313.6458 | 0 | 12.1249 | 37.78
2021-04-27 16:00 | 44313.6667 | 0 | 12.6089 | 37.78
2021-04-27 16:30 | 44313.6875 | 0 | 13.2658 | 37.78
2021-04-27 17:00 | 44313.7083 | 0 | 13.4964 | 37.78
2021-04-27 17:30 | 44313.7292 | 0 | 13.8842 | 37.78
2021-04-27 18:00 | 44313.75 | 0 | 13.8993 | 37.78
2021-04-27 18:30 | 44313.7708 | 0 | 13.9682 | 37.78
2021-04-27 19:00 | 44313.7917 | 0 | 13.5978 | 37.78
2021-04-27 19:30 | 44313.8125 | 0 | 13.3561 | 37.78
2021-04-27 20:00 | 44313.8333 | 0 | 13.0512 | 37.78
2021-04-27 20:30 | 44313.8542 | 0 | 12.5238 | 37.78
2021-04-27 21:00 | 44313.875 | 0 | 11.8542 | 37.78
2021-04-27 21:30 | 44313.8958 | 0 | 11.5468 | 37.78
2021-04-27 22:00 | 44313.9167 | 0 | 11.0567 | 37.78
2021-04-27 22:30 | 44313.9375 | 0 | 10.1637 | 37.78
2021-04-27 23:00 | 44313.9583 | 0 | 9.5867 | 37.78
2021-04-27 23:30 | 44313.9792 | 0 | 9.1711 | 37.78
2021-04-28 | 44314 | 0 | 8.6128 | 37.78
2021-04-28 00:30 | 44314.0208 | 0 | 8.3133 | 37.78
2021-04-28 01:00 | 44314.0417 | 0 | 8.0598 | 37.78
2021-04-28 01:30 | 44314.0625 | 0 | 7.8453 | 37.78
2021-04-28 02:00 | 44314.0833 | 0 | 7.7338 | 37.78
2021-04-28 02:30 | 44314.1042 | 0 | 7.6824 | 37.78
2021-04-28 03:00 | 44314.125 | 0 | 7.7078 | 37.78
2021-04-28 03:30 | 44314.1458 | 0 | 7.9092 | 37.78
2021-04-28 04:00 | 44314.1667 | 0 | 8.2458 | 37.78
2021-04-28 04:30 | 44314.1875 | 0 | 8.5846 | 37.78
2021-04-28 05:00 | 44314.2083 | 0 | 9.2193 | 37.78
2021-04-28 05:30 | 44314.2292 | 0 | 9.8608 | 37.78
2021-04-28 06:00 | 44314.25 | 0 | 10.7923 | 37.78
2021-04-28 06:30 | 44314.2708 | 0 | 11.6329 | 37.78
2021-04-28 07:00 | 44314.2917 | 0 | 11.8277 | 37.78
2021-04-28 07:30 | 44314.3125 | 0 | 11.4812 | 37.78
2021-04-28 08:00 | 44314.3333 | 0 | 11.2029 | 37.78
2021-04-28 08:30 | 44314.3542 | 0 | 10.4648 | 37.78
2021-04-28 09:00 | 44314.375 | 0 | 9.9978 | 37.78
2021-04-28 09:30 | 44314.3958 | 0 | 9.8997 | 37.78
2021-04-28 10:00 | 44314.4167 | 0 | 10.6491 | 37.78
2021-04-28 10:30 | 44314.4375 | 0 | 11.1879 | 37.78
2021-04-28 11:00 | 44314.4583 | 0 | 11.9724 | 37.78
2021-04-28 11:30 | 44314.4792 | 0 | 11.2141 | 37.78
2021-04-28 12:00 | 44314.5 | 0 | 11.068 | 37.78
2021-04-28 12:30 | 44314.5208 | 0 | 10.3429 | 37.78
2021-04-28 13:00 | 44314.5417 | 0 | 11.5882 | 37.78
2021-04-28 13:30 | 44314.5625 | 0 | 12.1006 | 37.78
2021-04-28 14:00 | 44314.5833 | 0 | 12.5567 | 37.78
2021-04-28 14:30 | 44314.6042 | 0 | 12.6878 | 37.78
2021-04-28 15:00 | 44314.625 | 0 | 12.591 | 37.78
2021-04-28 15:30 | 44314.6458 | 0 | 12.4809 | 37.78
2021-04-28 16:00 | 44314.6667 | 0 | 12.5233 | 37.78
2021-04-28 16:30 | 44314.6875 | 0 | 13.012 | 37.78
2021-04-28 17:00 | 44314.7083 | 0 | 13.345 | 37.78
2021-04-28 17:30 | 44314.7292 | 0 | 14.0296 | 37.78
2021-04-28 18:00 | 44314.75 | 0 | 13.9281 | 37.78
2021-04-28 18:30 | 44314.7708 | 0 | 13.9565 | 37.78
2021-04-28 19:00 | 44314.7917 | 0 | 13.4963 | 37.78
2021-04-28 19:30 | 44314.8125 | 0 | 13.3314 | 37.78
2021-04-28 20:00 | 44314.8333 | 0 | 13.1462 | 37.78
2021-04-28 20:30 | 44314.8542 | 0 | 12.5122 | 37.78
2021-04-28 21:00 | 44314.875 | 0 | 11.945 | 37.78
2021-04-28 21:30 | 44314.8958 | 0 | 11.4995 | 37.78
2021-04-28 22:00 | 44314.9167 | 0 | 11.1682 | 37.78
2021-04-28 22:30 | 44314.9375 | 0 | 10.1736 | 37.78
2021-04-28 23:00 | 44314.9583 | 0 | 9.6314 | 37.78
2021-04-28 23:30 | 44314.9792 | 0 | 9.142 | 37.78
2021-04-29 | 44315 | 0 | 8.7216 | 37.78
2021-04-29 00:30 | 44315.0208 | 0 | 8.33 | 37.78
2021-04-29 01:00 | 44315.0417 | 0 | 8.1033 | 37.78
2021-04-29 01:30 | 44315.0625 | 0 | 7.9544 | 37.78
2021-04-29 02:00 | 44315.0833 | 0 | 7.7964 | 37.78
2021-04-29 02:30 | 44315.1042 | 0 | 7.8376 | 37.78
2021-04-29 03:00 | 44315.125 | 0 | 7.7592 | 37.78
2021-04-29 03:30 | 44315.1458 | 0 | 7.9951 | 37.78
2021-04-29 04:00 | 44315.1667 | 0 | 8.232 | 37.78
2021-04-29 04:30 | 44315.1875 | 0 | 8.6788 | 37.78
2021-04-29 05:00 | 44315.2083 | 0 | 9.2683 | 37.78
2021-04-29 05:30 | 44315.2292 | 0 | 9.8488 | 37.78
2021-04-29 06:00 | 44315.25 | 0 | 10.9618 | 37.78
2021-04-29 06:30 | 44315.2708 | 0 | 11.9074 | 37.78
2021-04-29 07:00 | 44315.2917 | 0 | 12.4198 | 37.78
2021-04-29 07:30 | 44315.3125 | 0 | 11.6111 | 37.78
2021-04-29 08:00 | 44315.3333 | 0 | 11.3167 | 37.78
2021-04-29 08:30 | 44315.3542 | 0 | 11.7083 | 37.78
2021-04-29 09:00 | 44315.375 | 0 | 11.148 | 37.78
2021-04-29 09:30 | 44315.3958 | 0 | 10.0904 | 37.78
2021-04-29 10:00 | 44315.4167 | 0 | 10.3956 | 37.78
2021-04-29 10:30 | 44315.4375 | 0 | 11.1546 | 37.78
2021-04-29 11:00 | 44315.4583 | 0 | 11.56 | 37.78
2021-04-29 11:30 | 44315.4792 | 0 | 9.9529 | 37.78
2021-04-29 12:00 | 44315.5 | 0 | 10.1435 | 37.78
2021-04-29 12:30 | 44315.5208 | 0 | 10.1941 | 37.78
2021-04-29 13:00 | 44315.5417 | 0 | 9.9384 | 37.78
2021-04-29 13:30 | 44315.5625 | 0 | 11.3393 | 37.78
2021-04-29 14:00 | 44315.5833 | 0 | 11.9225 | 37.78
2021-04-29 14:30 | 44315.6042 | 0 | 11.1156 | 37.78
2021-04-29 15:00 | 44315.625 | 0 | 12.4517 | 37.78
2021-04-29 15:30 | 44315.6458 | 0 | 11.9909 | 37.78
2021-04-29 16:00 | 44315.6667 | 0 | 12.8003 | 37.78
2021-04-29 16:30 | 44315.6875 | 0 | 13.2021 | 37.78
2021-04-29 17:00 | 44315.7083 | 0 | 13.4872 | 37.78
2021-04-29 17:30 | 44315.7292 | 0 | 14.053 | 37.78
2021-04-29 18:00 | 44315.75 | 0 | 14.0544 | 37.78
2021-04-29 18:30 | 44315.7708 | 0 | 14.0277 | 37.78
2021-04-29 19:00 | 44315.7917 | 0 | 13.6138 | 37.78
2021-04-29 19:30 | 44315.8125 | 0 | 13.5206 | 37.78
2021-04-29 20:00 | 44315.8333 | 0 | 13.294 | 37.78
2021-04-29 20:30 | 44315.8542 | 0 | 12.6232 | 37.78
2021-04-29 21:00 | 44315.875 | 0 | 12.2539 | 37.78
2021-04-29 21:30 | 44315.8958 | 0 | 11.8681 | 37.78
2021-04-29 22:00 | 44315.9167 | 0 | 11.2354 | 37.78
2021-04-29 22:30 | 44315.9375 | 0 | 10.5602 | 37.78
2021-04-29 23:00 | 44315.9583 | 0 | 9.8875 | 37.78
2021-04-29 23:30 | 44315.9792 | 0 | 9.6154 | 37.78
2021-04-30 | 44316 | 0 | 8.9545 | 37.78
2021-04-30 00:30 | 44316.0208 | 0 | 8.6053 | 37.78
2021-04-30 01:00 | 44316.0417 | 0 | 8.3208 | 37.78
2021-04-30 01:30 | 44316.0625 | 0 | 8.1621 | 37.78
2021-04-30 02:00 | 44316.0833 | 0 | 8.0867 | 37.78
2021-04-30 02:30 | 44316.1042 | 0 | 8.1726 | 37.78
2021-04-30 03:00 | 44316.125 | 0 | 8.0632 | 37.78
2021-04-30 03:30 | 44316.1458 | 0 | 8.1757 | 37.78
2021-04-30 04:00 | 44316.1667 | 0 | 8.4052 | 37.78
2021-04-30 04:30 | 44316.1875 | 0 | 8.7679 | 37.78
2021-04-30 05:00 | 44316.2083 | 0 | 9.3186 | 37.78
2021-04-30 05:30 | 44316.2292 | 0 | 10.0294 | 37.78
2021-04-30 06:00 | 44316.25 | 0 | 10.6986 | 37.78
2021-04-30 06:30 | 44316.2708 | 0 | 11.5522 | 37.78
2021-04-30 07:00 | 44316.2917 | 0 | 12.3906 | 37.78
2021-04-30 07:30 | 44316.3125 | 0 | 12.1773 | 37.78
2021-04-30 08:00 | 44316.3333 | 0 | 12.0255 | 37.78
2021-04-30 08:30 | 44316.3542 | 0 | 11.4962 | 37.78
2021-04-30 09:00 | 44316.375 | 0 | 11.8035 | 37.78
2021-04-30 09:30 | 44316.3958 | 0 | 11.7031 | 37.78
2021-04-30 10:00 | 44316.4167 | 0 | 11.6277 | 37.78
2021-04-30 10:30 | 44316.4375 | 0 | 13.1115 | 37.78
2021-04-30 11:00 | 44316.4583 | 0 | 11.6255 | 37.78
2021-04-30 11:30 | 44316.4792 | 0 | 9.6382 | 37.78
2021-04-30 12:00 | 44316.5 | 0 | 10.5467 | 37.78
2021-04-30 12:30 | 44316.5208 | 0 | 11.7233 | 37.78
2021-04-30 13:00 | 44316.5417 | 0 | 12.5183 | 37.78
2021-04-30 13:30 | 44316.5625 | 0 | 12.6526 | 37.78
2021-04-30 14:00 | 44316.5833 | 0 | 12.3084 | 37.78
2021-04-30 14:30 | 44316.6042 | 0 | 12.7033 | 37.78
2021-04-30 15:00 | 44316.625 | 0 | 12.5083 | 37.78
2021-04-30 15:30 | 44316.6458 | 0 | 12.4721 | 37.78
2021-04-30 16:00 | 44316.6667 | 0 | 12.7138 | 37.78
2021-04-30 16:30 | 44316.6875 | 0 | 13.0646 | 37.78
2021-04-30 17:00 | 44316.7083 | 0 | 13.1671 | 37.78
2021-04-30 17:30 | 44316.7292 | 0 | 13.688 | 37.78
2021-04-30 18:00 | 44316.75 | 0 | 13.6719 | 37.78
2021-04-30 18:30 | 44316.7708 | 0 | 13.4016 | 37.78
2021-04-30 19:00 | 44316.7917 | 0 | 13.1281 | 37.78
2021-04-30 19:30 | 44316.8125 | 0 | 12.935 | 37.78
2021-04-30 20:00 | 44316.8333 | 0 | 12.5059 | 37.78
2021-04-30 20:30 | 44316.8542 | 0 | 11.891 | 37.78
2021-04-30 21:00 | 44316.875 | 0 | 11.5411 | 37.78
2021-04-30 21:30 | 44316.8958 | 0 | 11.1606 | 37.78
2021-04-30 22:00 | 44316.9167 | 0 | 10.7766 | 37.78
2021-04-30 22:30 | 44316.9375 | 0 | 10.0537 | 37.78
2021-04-30 23:00 | 44316.9583 | 0 | 9.6337 | 37.78
2021-04-30 23:30 | 44316.9792 | 0 | 9.3003 | 37.78
2021-05-01 | 44317 | 0 | 8.6973 | 39.95
2021-05-01 00:30 | 44317.0208 | 0 | 8.262 | 39.95
2021-05-01 01:00 | 44317.0417 | 0 | 8.0374 | 39.95
2021-05-01 01:30 | 44317.0625 | 0 | 7.8172 | 39.95
2021-05-01 02:00 | 44317.0833 | 0 | 7.8133 | 39.95
2021-05-01 02:30 | 44317.1042 | 0 | 7.5226 | 39.95
2021-05-01 03:00 | 44317.125 | 0 | 7.3721 | 39.95
2021-05-01 03:30 | 44317.1458 | 0 | 7.6538 | 39.95
2021-05-01 04:00 | 44317.1667 | 0 | 7.6589 | 39.95
2021-05-01 04:30 | 44317.1875 | 0 | 7.6701 | 39.95
2021-05-01 05:00 | 44317.2083 | 0 | 7.9928 | 39.95
2021-05-01 05:30 | 44317.2292 | 0 | 8.1377 | 39.95
2021-05-01 06:00 | 44317.25 | 0 | 8.3429 | 39.95
2021-05-01 06:30 | 44317.2708 | 0 | 8.7963 | 39.95
2021-05-01 07:00 | 44317.2917 | 0 | 9.4751 | 39.95
2021-05-01 07:30 | 44317.3125 | 0 | 9.9054 | 39.95
2021-05-01 08:00 | 44317.3333 | 0 | 10.1891 | 39.95
2021-05-01 08:30 | 44317.3542 | 0 | 10.4196 | 39.95
2021-05-01 09:00 | 44317.375 | 0 | 10.0397 | 39.95
2021-05-01 09:30 | 44317.3958 | 0 | 9.655 | 39.95
2021-05-01 10:00 | 44317.4167 | 0 | 10.1239 | 39.95
2021-05-01 10:30 | 44317.4375 | 0 | 10.7818 | 39.95
2021-05-01 11:00 | 44317.4583 | 0 | 10.7892 | 39.95
2021-05-01 11:30 | 44317.4792 | 0 | 9.9888 | 39.95
2021-05-01 12:00 | 44317.5 | 0 | 10.0382 | 39.95
2021-05-01 12:30 | 44317.5208 | 0 | 10.4761 | 39.95
2021-05-01 13:00 | 44317.5417 | 0 | 10.3233 | 39.95
2021-05-01 13:30 | 44317.5625 | 0 | 10.5505 | 39.95
2021-05-01 14:00 | 44317.5833 | 0 | 9.6935 | 39.95
2021-05-01 14:30 | 44317.6042 | 0 | 9.6442 | 39.95
2021-05-01 15:00 | 44317.625 | 0 | 9.5618 | 39.95
2021-05-01 15:30 | 44317.6458 | 0 | 9.7934 | 39.95
2021-05-01 16:00 | 44317.6667 | 0 | 10.2349 | 39.95
2021-05-01 16:30 | 44317.6875 | 0 | 10.6827 | 39.95
2021-05-01 17:00 | 44317.7083 | 0 | 10.8923 | 39.95
2021-05-01 17:30 | 44317.7292 | 0 | 11.3653 | 39.95
2021-05-01 18:00 | 44317.75 | 0 | 11.3556 | 39.95
2021-05-01 18:30 | 44317.7708 | 0 | 11.2671 | 39.95
2021-05-01 19:00 | 44317.7917 | 0 | 11.0289 | 39.95
2021-05-01 19:30 | 44317.8125 | 0 | 10.8592 | 39.95
2021-05-01 20:00 | 44317.8333 | 0 | 10.5795 | 39.95
2021-05-01 20:30 | 44317.8542 | 0 | 10.0366 | 39.95
2021-05-01 21:00 | 44317.875 | 0 | 9.6984 | 39.95
2021-05-01 21:30 | 44317.8958 | 0 | 9.4456 | 39.95
2021-05-01 22:00 | 44317.9167 | 0 | 9.1684 | 39.95
2021-05-01 22:30 | 44317.9375 | 0 | 8.7354 | 39.95
2021-05-01 23:00 | 44317.9583 | 0 | 8.3493 | 39.95
2021-05-01 23:30 | 44317.9792 | 0 | 8.0506 | 39.95
2021-05-02 | 44318 | 0 | 7.6589 | 39.95
2021-05-02 00:30 | 44318.0208 | 0 | 7.4968 | 39.95
2021-05-02 01:00 | 44318.0417 | 0 | 7.2816 | 39.95
2021-05-02 01:30 | 44318.0625 | 0 | 7.2264 | 39.95
2021-05-02 02:00 | 44318.0833 | 0 | 7.1825 | 39.95
2021-05-02 02:30 | 44318.1042 | 0 | 7.0722 | 39.95
2021-05-02 03:00 | 44318.125 | 0 | 6.9901 | 39.95
2021-05-02 03:30 | 44318.1458 | 0 | 6.9901 | 39.95
2021-05-02 04:00 | 44318.1667 | 0 | 7.0336 | 39.95
2021-05-02 04:30 | 44318.1875 | 0 | 6.9689 | 39.95
2021-05-02 05:00 | 44318.2083 | 0 | 7.1052 | 39.95
2021-05-02 05:30 | 44318.2292 | 0 | 7.2898 | 39.95
2021-05-02 06:00 | 44318.25 | 0 | 7.4406 | 39.95
2021-05-02 06:30 | 44318.2708 | 0 | 7.4414 | 39.95
2021-05-02 07:00 | 44318.2917 | 0 | 7.5484 | 39.95
2021-05-02 07:30 | 44318.3125 | 0 | 7.3975 | 39.95
2021-05-02 08:00 | 44318.3333 | 0 | 7.9138 | 39.95
2021-05-02 08:30 | 44318.3542 | 0 | 7.0072 | 39.95
2021-05-02 09:00 | 44318.375 | 0 | 7.7998 | 39.95
2021-05-02 09:30 | 44318.3958 | 0 | 8.1723 | 39.95
2021-05-02 10:00 | 44318.4167 | 0 | 7.8749 | 39.95
2021-05-02 10:30 | 44318.4375 | 0 | 8.3975 | 39.95
2021-05-02 11:00 | 44318.4583 | 0 | 9.0587 | 39.95
2021-05-02 11:30 | 44318.4792 | 0 | 9.5314 | 39.95
2021-05-02 12:00 | 44318.5 | 0 | 9.2618 | 39.95
2021-05-02 12:30 | 44318.5208 | 0 | 9.4187 | 39.95
2021-05-02 13:00 | 44318.5417 | 0 | 8.7884 | 39.95
2021-05-02 13:30 | 44318.5625 | 0 | 8.9254 | 39.95
2021-05-02 14:00 | 44318.5833 | 0 | 8.4853 | 39.95
2021-05-02 14:30 | 44318.6042 | 0 | 9.1506 | 39.95
2021-05-02 15:00 | 44318.625 | 0 | 9.0813 | 39.95
2021-05-02 15:30 | 44318.6458 | 0 | 9.6875 | 39.95
2021-05-02 16:00 | 44318.6667 | 0 | 9.9308 | 39.95
2021-05-02 16:30 | 44318.6875 | 0 | 10.4651 | 39.95
2021-05-02 17:00 | 44318.7083 | 0 | 10.9218 | 39.95
2021-05-02 17:30 | 44318.7292 | 0 | 11.249 | 39.95
2021-05-02 18:00 | 44318.75 | 0 | 11.2121 | 39.95
2021-05-02 18:30 | 44318.7708 | 0 | 11.2934 | 39.95
2021-05-02 19:00 | 44318.7917 | 0 | 10.872 | 39.95
2021-05-02 19:30 | 44318.8125 | 0 | 10.6022 | 39.95
2021-05-02 20:00 | 44318.8333 | 0 | 10.3432 | 39.95
2021-05-02 20:30 | 44318.8542 | 0 | 9.9194 | 39.95
2021-05-02 21:00 | 44318.875 | 0 | 9.6208 | 39.95
2021-05-02 21:30 | 44318.8958 | 0 | 9.4244 | 39.95
2021-05-02 22:00 | 44318.9167 | 0 | 9.1438 | 39.95
2021-05-02 22:30 | 44318.9375 | 0 | 8.5184 | 39.95
2021-05-02 23:00 | 44318.9583 | 0 | 8.1268 | 39.95
2021-05-02 23:30 | 44318.9792 | 0 | 7.8801 | 39.95
2021-05-03 | 44319 | 0 | 7.5427 | 39.95
2021-05-03 00:30 | 44319.0208 | 0 | 7.3443 | 39.95
2021-05-03 01:00 | 44319.0417 | 0 | 7.2008 | 39.95
2021-05-03 01:30 | 44319.0625 | 0 | 6.9901 | 39.95
2021-05-03 02:00 | 44319.0833 | 0 | 6.9443 | 39.95
2021-05-03 02:30 | 44319.1042 | 0 | 6.8338 | 39.95
2021-05-03 03:00 | 44319.125 | 0 | 6.9254 | 39.95
2021-05-03 03:30 | 44319.1458 | 0 | 6.9878 | 39.95
2021-05-03 04:00 | 44319.1667 | 0 | 6.9701 | 39.95
2021-05-03 04:30 | 44319.1875 | 0 | 7.0837 | 39.95
2021-05-03 05:00 | 44319.2083 | 0 | 7.2816 | 39.95
2021-05-03 05:30 | 44319.2292 | 0 | 7.4883 | 39.95
2021-05-03 06:00 | 44319.25 | 0 | 7.7857 | 39.95
2021-05-03 06:30 | 44319.2708 | 0 | 7.947 | 39.95
2021-05-03 07:00 | 44319.2917 | 0 | 7.9058 | 39.95
2021-05-03 07:30 | 44319.3125 | 0 | 7.8239 | 39.95
2021-05-03 08:00 | 44319.3333 | 0 | 7.8038 | 39.95
2021-05-03 08:30 | 44319.3542 | 0 | 7.7973 | 39.95
2021-05-03 09:00 | 44319.375 | 0 | 7.5919 | 39.95
2021-05-03 09:30 | 44319.3958 | 0 | 7.4834 | 39.95
2021-05-03 10:00 | 44319.4167 | 0 | 7.6498 | 39.95
2021-05-03 10:30 | 44319.4375 | 0 | 7.5089 | 39.95
2021-05-03 11:00 | 44319.4583 | 0 | 7.1656 | 39.95
2021-05-03 11:30 | 44319.4792 | 0 | 7.9979 | 39.95
2021-05-03 12:00 | 44319.5 | 0 | 9.3059 | 39.95
2021-05-03 12:30 | 44319.5208 | 0 | 8.6804 | 39.95
2021-05-03 13:00 | 44319.5417 | 0 | 9.39 | 39.95
2021-05-03 13:30 | 44319.5625 | 0 | 8.1763 | 39.95
2021-05-03 14:00 | 44319.5833 | 0 | 9.4318 | 39.95
2021-05-03 14:30 | 44319.6042 | 0 | 9.5781 | 39.95
2021-05-03 15:00 | 44319.625 | 0 | 9.4907 | 39.95
2021-05-03 15:30 | 44319.6458 | 0 | 10.4695 | 39.95
2021-05-03 16:00 | 44319.6667 | 0 | 10.9651 | 39.95
2021-05-03 16:30 | 44319.6875 | 0 | 11.6677 | 39.95
2021-05-03 17:00 | 44319.7083 | 0 | 11.9419 | 39.95
2021-05-03 17:30 | 44319.7292 | 0 | 12.6764 | 39.95
2021-05-03 18:00 | 44319.75 | 0 | 12.5879 | 39.95
2021-05-03 18:30 | 44319.7708 | 0 | 12.3809 | 39.95
2021-05-03 19:00 | 44319.7917 | 0 | 11.883 | 39.95
2021-05-03 19:30 | 44319.8125 | 0 | 11.5285 | 39.95
2021-05-03 20:00 | 44319.8333 | 0 | 11.0936 | 39.95
2021-05-03 20:30 | 44319.8542 | 0 | 10.6554 | 39.95
2021-05-03 21:00 | 44319.875 | 0 | 10.1836 | 39.95
2021-05-03 21:30 | 44319.8958 | 0 | 9.7924 | 39.95
2021-05-03 22:00 | 44319.9167 | 0 | 9.3167 | 39.95
2021-05-03 22:30 | 44319.9375 | 0 | 8.6984 | 39.95
2021-05-03 23:00 | 44319.9583 | 0 | 8.2703 | 39.95
2021-05-03 23:30 | 44319.9792 | 0 | 7.941 | 39.95
2021-05-04 | 44320 | 0 | 7.6566 | 39.95
2021-05-04 00:30 | 44320.0208 | 0 | 7.4591 | 39.95
2021-05-04 01:00 | 44320.0417 | 0 | 7.3886 | 39.95
2021-05-04 01:30 | 44320.0625 | 0 | 7.0838 | 39.95
2021-05-04 02:00 | 44320.0833 | 0 | 6.9231 | 39.95
2021-05-04 02:30 | 44320.1042 | 0 | 6.8796 | 39.95
2021-05-04 03:00 | 44320.125 | 0 | 6.9443 | 39.95
2021-05-04 03:30 | 44320.1458 | 0 | 7.0159 | 39.95
2021-05-04 04:00 | 44320.1667 | 0 | 7.4276 | 39.95
2021-05-04 04:30 | 44320.1875 | 0 | 7.8102 | 39.95
2021-05-04 05:00 | 44320.2083 | 0 | 8.4163 | 39.95
2021-05-04 05:30 | 44320.2292 | 0 | 9.0907 | 39.95
2021-05-04 06:00 | 44320.25 | 0 | 10.3282 | 39.95
2021-05-04 06:30 | 44320.2708 | 0 | 11.2103 | 39.95
2021-05-04 07:00 | 44320.2917 | 0 | 11.5353 | 39.95
2021-05-04 07:30 | 44320.3125 | 0 | 11.4375 | 39.95
2021-05-04 08:00 | 44320.3333 | 0 | 11.2442 | 39.95
2021-05-04 08:30 | 44320.3542 | 0 | 10.2184 | 39.95
2021-05-04 09:00 | 44320.375 | 0 | 9.6165 | 39.95
2021-05-04 09:30 | 44320.3958 | 0 | 9.2862 | 39.95
2021-05-04 10:00 | 44320.4167 | 0 | 9.1955 | 39.95
2021-05-04 10:30 | 44320.4375 | 0 | 9.1075 | 39.95
2021-05-04 11:00 | 44320.4583 | 0 | 9.0212 | 39.95
2021-05-04 11:30 | 44320.4792 | 0 | 9.1301 | 39.95
2021-05-04 12:00 | 44320.5 | 0 | 9.3947 | 39.95
2021-05-04 12:30 | 44320.5208 | 0 | 10.3383 | 39.95
2021-05-04 13:00 | 44320.5417 | 0 | 10.4374 | 39.95
2021-05-04 13:30 | 44320.5625 | 0 | 10.4222 | 39.95
2021-05-04 14:00 | 44320.5833 | 0 | 11.0618 | 39.95
2021-05-04 14:30 | 44320.6042 | 0 | 11.6579 | 39.95
2021-05-04 15:00 | 44320.625 | 0 | 11.7112 | 39.95
2021-05-04 15:30 | 44320.6458 | 0 | 12.4565 | 39.95
2021-05-04 16:00 | 44320.6667 | 0 | 13.0262 | 39.95
2021-05-04 16:30 | 44320.6875 | 0 | 13.1863 | 39.95
2021-05-04 17:00 | 44320.7083 | 0 | 13.799 | 39.95
2021-05-04 17:30 | 44320.7292 | 0 | 14.2731 | 39.95
2021-05-04 18:00 | 44320.75 | 0 | 14.6183 | 39.95
2021-05-04 18:30 | 44320.7708 | 0 | 14.3594 | 39.95
2021-05-04 19:00 | 44320.7917 | 0 | 13.9858 | 39.95
2021-05-04 19:30 | 44320.8125 | 0 | 13.9917 | 39.95
2021-05-04 20:00 | 44320.8333 | 0 | 13.5349 | 39.95
2021-05-04 20:30 | 44320.8542 | 0 | 12.8441 | 39.95
2021-05-04 21:00 | 44320.875 | 0 | 11.971 | 39.95
2021-05-04 21:30 | 44320.8958 | 0 | 11.7447 | 39.95
2021-05-04 22:00 | 44320.9167 | 0 | 11.4424 | 39.95
2021-05-04 22:30 | 44320.9375 | 0 | 10.6525 | 39.95
2021-05-04 23:00 | 44320.9583 | 0 | 10.1357 | 39.95
2021-05-04 23:30 | 44320.9792 | 0 | 9.2795 | 39.95
2021-05-05 | 44321 | 0 | 8.5702 | 39.95
2021-05-05 00:30 | 44321.0208 | 0 | 8.0963 | 39.95
2021-05-05 01:00 | 44321.0417 | 0 | 8.081 | 39.95
2021-05-05 01:30 | 44321.0625 | 0 | 7.9985 | 39.95
2021-05-05 02:00 | 44321.0833 | 0 | 7.9154 | 39.95
2021-05-05 02:30 | 44321.1042 | 0 | 7.9069 | 39.95
2021-05-05 03:00 | 44321.125 | 0 | 7.955 | 39.95
2021-05-05 03:30 | 44321.1458 | 0 | 8.2157 | 39.95
2021-05-05 04:00 | 44321.1667 | 0 | 8.2751 | 39.95
2021-05-05 04:30 | 44321.1875 | 0 | 8.7484 | 39.95
2021-05-05 05:00 | 44321.2083 | 0 | 9.3513 | 39.95
2021-05-05 05:30 | 44321.2292 | 0 | 10.0048 | 39.95
2021-05-05 06:00 | 44321.25 | 0 | 10.87 | 39.95
2021-05-05 06:30 | 44321.2708 | 0 | 11.7087 | 39.95
2021-05-05 07:00 | 44321.2917 | 0 | 11.7173 | 39.95
2021-05-05 07:30 | 44321.3125 | 0 | 12.3494 | 39.95
2021-05-05 08:00 | 44321.3333 | 0 | 11.4748 | 39.95
2021-05-05 08:30 | 44321.3542 | 0 | 13.1827 | 39.95
2021-05-05 09:00 | 44321.375 | 0 | 13.5997 | 39.95
2021-05-05 09:30 | 44321.3958 | 0 | 13.8039 | 39.95
2021-05-05 10:00 | 44321.4167 | 0 | 13.4675 | 39.95
2021-05-05 10:30 | 44321.4375 | 0 | 13.3933 | 39.95
2021-05-05 11:00 | 44321.4583 | 0 | 13.3028 | 39.95
2021-05-05 11:30 | 44321.4792 | 0 | 12.9492 | 39.95
2021-05-05 12:00 | 44321.5 | 0 | 12.699 | 39.95
2021-05-05 12:30 | 44321.5208 | 0 | 13.039 | 39.95
2021-05-05 13:00 | 44321.5417 | 0 | 12.8713 | 39.95
2021-05-05 13:30 | 44321.5625 | 0 | 12.9075 | 39.95
2021-05-05 14:00 | 44321.5833 | 0 | 13.1087 | 39.95
2021-05-05 14:30 | 44321.6042 | 0 | 11.9217 | 39.95
2021-05-05 15:00 | 44321.625 | 0 | 11.5738 | 39.95
2021-05-05 15:30 | 44321.6458 | 0 | 12.3297 | 39.95
2021-05-05 16:00 | 44321.6667 | 0 | 12.1874 | 39.95
2021-05-05 16:30 | 44321.6875 | 0 | 13.0471 | 39.95
2021-05-05 17:00 | 44321.7083 | 0 | 13.7173 | 39.95
2021-05-05 17:30 | 44321.7292 | 0 | 14.4777 | 39.95
2021-05-05 18:00 | 44321.75 | 0 | 14.7395 | 39.95
2021-05-05 18:30 | 44321.7708 | 0 | 14.8603 | 39.95
2021-05-05 19:00 | 44321.7917 | 0 | 14.3866 | 39.95
2021-05-05 19:30 | 44321.8125 | 0 | 14.0954 | 39.95
2021-05-05 20:00 | 44321.8333 | 0 | 13.7483 | 39.95
2021-05-05 20:30 | 44321.8542 | 0 | 13.2178 | 39.95
2021-05-05 21:00 | 44321.875 | 0 | 12.5423 | 39.95
2021-05-05 21:30 | 44321.8958 | 0 | 11.9709 | 39.95
2021-05-05 22:00 | 44321.9167 | 0 | 11.506 | 39.95
2021-05-05 22:30 | 44321.9375 | 0 | 10.555 | 39.95
2021-05-05 23:00 | 44321.9583 | 0 | 9.849 | 39.95
2021-05-05 23:30 | 44321.9792 | 0 | 9.3936 | 39.95
2021-05-06 | 44322 | 0 | 8.7908 | 39.95
2021-05-06 00:30 | 44322.0208 | 0 | 8.3963 | 39.95
2021-05-06 01:00 | 44322.0417 | 0 | 8.2259 | 39.95
2021-05-06 01:30 | 44322.0625 | 0 | 8.1186 | 39.95
2021-05-06 02:00 | 44322.0833 | 0 | 8.0163 | 39.95
2021-05-06 02:30 | 44322.1042 | 0 | 7.9504 | 39.95
2021-05-06 03:00 | 44322.125 | 0 | 7.9585 | 39.95
2021-05-06 03:30 | 44322.1458 | 0 | 7.9593 | 39.95
2021-05-06 04:00 | 44322.1667 | 0 | 8.3996 | 39.95
2021-05-06 04:30 | 44322.1875 | 0 | 8.7546 | 39.95
2021-05-06 05:00 | 44322.2083 | 0 | 9.3322 | 39.95
2021-05-06 05:30 | 44322.2292 | 0 | 10.27 | 39.95
2021-05-06 06:00 | 44322.25 | 0 | 11.4021 | 39.95
2021-05-06 06:30 | 44322.2708 | 0 | 12.2703 | 39.95
2021-05-06 07:00 | 44322.2917 | 0 | 12.6403 | 39.95
2021-05-06 07:30 | 44322.3125 | 0 | 12.1738 | 39.95
2021-05-06 08:00 | 44322.3333 | 0 | 11.563 | 39.95
2021-05-06 08:30 | 44322.3542 | 0 | 10.4535 | 39.95
2021-05-06 09:00 | 44322.375 | 0 | 9.7908 | 39.95
2021-05-06 09:30 | 44322.3958 | 0 | 9.4367 | 39.95
2021-05-06 10:00 | 44322.4167 | 0 | 8.9273 | 39.95
2021-05-06 10:30 | 44322.4375 | 0 | 8.9342 | 39.95
2021-05-06 11:00 | 44322.4583 | 0 | 8.6048 | 39.95
2021-05-06 11:30 | 44322.4792 | 0 | 8.7239 | 39.95
2021-05-06 12:00 | 44322.5 | 0 | 8.6749 | 39.95
2021-05-06 12:30 | 44322.5208 | 0 | 8.9508 | 39.95
2021-05-06 13:00 | 44322.5417 | 0 | 9.2185 | 39.95
2021-05-06 13:30 | 44322.5625 | 0 | 9.7816 | 39.95
2021-05-06 14:00 | 44322.5833 | 0 | 10.1577 | 39.95
2021-05-06 14:30 | 44322.6042 | 0 | 10.5029 | 39.95
2021-05-06 15:00 | 44322.625 | 0 | 11.08 | 39.95
2021-05-06 15:30 | 44322.6458 | 0 | 11.7223 | 39.95
2021-05-06 16:00 | 44322.6667 | 0 | 12.2542 | 39.95
2021-05-06 16:30 | 44322.6875 | 0 | 12.8627 | 39.95
2021-05-06 17:00 | 44322.7083 | 0 | 13.3859 | 39.95
2021-05-06 17:30 | 44322.7292 | 0 | 13.8381 | 39.95
2021-05-06 18:00 | 44322.75 | 0 | 14.0058 | 39.95
2021-05-06 18:30 | 44322.7708 | 0 | 13.9888 | 39.95
2021-05-06 19:00 | 44322.7917 | 0 | 13.8341 | 39.95
2021-05-06 19:30 | 44322.8125 | 0 | 13.7052 | 39.95
2021-05-06 20:00 | 44322.8333 | 0 | 13.3429 | 39.95
2021-05-06 20:30 | 44322.8542 | 0 | 12.7592 | 39.95
2021-05-06 21:00 | 44322.875 | 0 | 12.3446 | 39.95
2021-05-06 21:30 | 44322.8958 | 0 | 11.7682 | 39.95
2021-05-06 22:00 | 44322.9167 | 0 | 11.4376 | 39.95
2021-05-06 22:30 | 44322.9375 | 0 | 10.4595 | 39.95
2021-05-06 23:00 | 44322.9583 | 0 | 9.7488 | 39.95
2021-05-06 23:30 | 44322.9792 | 0 | 9.3738 | 39.95
2021-05-07 | 44323 | 0 | 8.5897 | 39.95
2021-05-07 00:30 | 44323.0208 | 0 | 8.3152 | 39.95
2021-05-07 01:00 | 44323.0417 | 0 | 8.0833 | 39.95
2021-05-07 01:30 | 44323.0625 | 0 | 7.9902 | 39.95
2021-05-07 02:00 | 44323.0833 | 0 | 7.9539 | 39.95
2021-05-07 02:30 | 44323.1042 | 0 | 7.8811 | 39.95
2021-05-07 03:00 | 44323.125 | 0 | 7.8399 | 39.95
2021-05-07 03:30 | 44323.1458 | 0 | 7.955 | 39.95
2021-05-07 04:00 | 44323.1667 | 0 | 8.2926 | 39.95
2021-05-07 04:30 | 44323.1875 | 0 | 8.4275 | 39.95
2021-05-07 05:00 | 44323.2083 | 0 | 9.0075 | 39.95
2021-05-07 05:30 | 44323.2292 | 0 | 9.9159 | 39.95
2021-05-07 06:00 | 44323.25 | 0 | 10.7887 | 39.95
2021-05-07 06:30 | 44323.2708 | 0 | 11.6081 | 39.95
2021-05-07 07:00 | 44323.2917 | 0 | 11.826 | 39.95
2021-05-07 07:30 | 44323.3125 | 0 | 11.4686 | 39.95
2021-05-07 08:00 | 44323.3333 | 0 | 11.0495 | 39.95
2021-05-07 08:30 | 44323.3542 | 0 | 10.4106 | 39.95
2021-05-07 09:00 | 44323.375 | 0 | 9.7743 | 39.95
2021-05-07 09:30 | 44323.3958 | 0 | 9.3879 | 39.95
2021-05-07 10:00 | 44323.4167 | 0 | 9.3308 | 39.95
2021-05-07 10:30 | 44323.4375 | 0 | 9.0671 | 39.95
2021-05-07 11:00 | 44323.4583 | 0 | 9.2383 | 39.95
2021-05-07 11:30 | 44323.4792 | 0 | 9.2413 | 39.95
2021-05-07 12:00 | 44323.5 | 0 | 9.4001 | 39.95
2021-05-07 12:30 | 44323.5208 | 0 | 9.3444 | 39.95
2021-05-07 13:00 | 44323.5417 | 0 | 10.733 | 39.95
2021-05-07 13:30 | 44323.5625 | 0 | 11.8471 | 39.95
2021-05-07 14:00 | 44323.5833 | 0 | 10.6418 | 39.95
2021-05-07 14:30 | 44323.6042 | 0 | 11.686 | 39.95
2021-05-07 15:00 | 44323.625 | 0 | 12.7308 | 39.95
2021-05-07 15:30 | 44323.6458 | 0 | 12.8625 | 39.95
2021-05-07 16:00 | 44323.6667 | 0 | 12.8157 | 39.95
2021-05-07 16:30 | 44323.6875 | 0 | 13.2049 | 39.95
2021-05-07 17:00 | 44323.7083 | 0 | 13.5605 | 39.95
2021-05-07 17:30 | 44323.7292 | 0 | 13.8624 | 39.95
2021-05-07 18:00 | 44323.75 | 0 | 13.578 | 39.95
2021-05-07 18:30 | 44323.7708 | 0 | 13.5198 | 39.95
2021-05-07 19:00 | 44323.7917 | 0 | 13.3468 | 39.95
2021-05-07 19:30 | 44323.8125 | 0 | 13.0415 | 39.95
2021-05-07 20:00 | 44323.8333 | 0 | 12.8112 | 39.95
2021-05-07 20:30 | 44323.8542 | 0 | 12.3743 | 39.95
2021-05-07 21:00 | 44323.875 | 0 | 12.0768 | 39.95
2021-05-07 21:30 | 44323.8958 | 0 | 11.7189 | 39.95
2021-05-07 22:00 | 44323.9167 | 0 | 11.238 | 39.95
2021-05-07 22:30 | 44323.9375 | 0 | 10.3654 | 39.95
2021-05-07 23:00 | 44323.9583 | 0 | 9.7083 | 39.95
2021-05-07 23:30 | 44323.9792 | 0 | 9.2899 | 39.95
2021-05-08 | 44324 | 0 | 8.8286 | 39.95
2021-05-08 00:30 | 44324.0208 | 0 | 8.4532 | 39.95
2021-05-08 01:00 | 44324.0417 | 0 | 8.3129 | 39.95
2021-05-08 01:30 | 44324.0625 | 0 | 8.0962 | 39.95
2021-05-08 02:00 | 44324.0833 | 0 | 8.0332 | 39.95
2021-05-08 02:30 | 44324.1042 | 0 | 7.8846 | 39.95
2021-05-08 03:00 | 44324.125 | 0 | 7.8176 | 39.95
2021-05-08 03:30 | 44324.1458 | 0 | 8.0197 | 39.95
2021-05-08 04:00 | 44324.1667 | 0 | 8.0421 | 39.95
2021-05-08 04:30 | 44324.1875 | 0 | 8.1885 | 39.95
2021-05-08 05:00 | 44324.2083 | 0 | 8.5299 | 39.95
2021-05-08 05:30 | 44324.2292 | 0 | 8.6665 | 39.95
2021-05-08 06:00 | 44324.25 | 0 | 8.9642 | 39.95
2021-05-08 06:30 | 44324.2708 | 0 | 9.3307 | 39.95
2021-05-08 07:00 | 44324.2917 | 0 | 9.4009 | 39.95
2021-05-08 07:30 | 44324.3125 | 0 | 9.2736 | 39.95
2021-05-08 08:00 | 44324.3333 | 0 | 9.2176 | 39.95
2021-05-08 08:30 | 44324.3542 | 0 | 8.8439 | 39.95
2021-05-08 09:00 | 44324.375 | 0 | 8.6153 | 39.95
2021-05-08 09:30 | 44324.3958 | 0 | 8.434 | 39.95
2021-05-08 10:00 | 44324.4167 | 0 | 8.031 | 39.95
2021-05-08 10:30 | 44324.4375 | 0 | 7.7899 | 39.95
2021-05-08 11:00 | 44324.4583 | 0 | 7.5696 | 39.95
2021-05-08 11:30 | 44324.4792 | 0 | 7.5315 | 39.95
2021-05-08 12:00 | 44324.5 | 0 | 7.5226 | 39.95
2021-05-08 12:30 | 44324.5208 | 0 | 8.131 | 39.95
2021-05-08 13:00 | 44324.5417 | 0 | 8.0792 | 39.95
2021-05-08 13:30 | 44324.5625 | 0 | 9.4447 | 39.95
2021-05-08 14:00 | 44324.5833 | 0 | 9.92 | 39.95
2021-05-08 14:30 | 44324.6042 | 0 | 10.1017 | 39.95
2021-05-08 15:00 | 44324.625 | 0 | 9.8998 | 39.95
2021-05-08 15:30 | 44324.6458 | 0 | 10.4505 | 39.95
2021-05-08 16:00 | 44324.6667 | 0 | 10.2702 | 39.95
2021-05-08 16:30 | 44324.6875 | 0 | 11.0515 | 39.95
2021-05-08 17:00 | 44324.7083 | 0 | 11.4824 | 39.95
2021-05-08 17:30 | 44324.7292 | 0 | 11.8498 | 39.95
2021-05-08 18:00 | 44324.75 | 0 | 11.8223 | 39.95
2021-05-08 18:30 | 44324.7708 | 0 | 11.7149 | 39.95
2021-05-08 19:00 | 44324.7917 | 0 | 11.3855 | 39.95
2021-05-08 19:30 | 44324.8125 | 0 | 11.2471 | 39.95
2021-05-08 20:00 | 44324.8333 | 0 | 10.9427 | 39.95
2021-05-08 20:30 | 44324.8542 | 0 | 10.6032 | 39.95
2021-05-08 21:00 | 44324.875 | 0 | 10.4428 | 39.95
2021-05-08 21:30 | 44324.8958 | 0 | 9.9579 | 39.95
2021-05-08 22:00 | 44324.9167 | 0 | 9.6514 | 39.95
2021-05-08 22:30 | 44324.9375 | 0 | 9.133 | 39.95
2021-05-08 23:00 | 44324.9583 | 0 | 8.6757 | 39.95
2021-05-08 23:30 | 44324.9792 | 0 | 8.3725 | 39.95
2021-05-09 | 44325 | 0 | 8.0087 | 39.95
2021-05-09 00:30 | 44325.0208 | 0 | 7.692 | 39.95
2021-05-09 01:00 | 44325.0417 | 0 | 7.4803 | 39.95
2021-05-09 01:30 | 44325.0625 | 0 | 7.344 | 39.95
2021-05-09 02:00 | 44325.0833 | 0 | 7.2369 | 39.95
2021-05-09 02:30 | 44325.1042 | 0 | 7.1987 | 39.95
2021-05-09 03:00 | 44325.125 | 0 | 7.1018 | 39.95
2021-05-09 03:30 | 44325.1458 | 0 | 7.1695 | 39.95
2021-05-09 04:00 | 44325.1667 | 0 | 7.1371 | 39.95
2021-05-09 04:30 | 44325.1875 | 0 | 7.1037 | 39.95
2021-05-09 05:00 | 44325.2083 | 0 | 7.3039 | 39.95
2021-05-09 05:30 | 44325.2292 | 0 | 7.4675 | 39.95
2021-05-09 06:00 | 44325.25 | 0 | 7.8611 | 39.95
2021-05-09 06:30 | 44325.2708 | 0 | 7.9115 | 39.95
2021-05-09 07:00 | 44325.2917 | 0 | 8.4774 | 39.95
2021-05-09 07:30 | 44325.3125 | 0 | 7.9891 | 39.95
2021-05-09 08:00 | 44325.3333 | 0 | 8.8271 | 39.95
2021-05-09 08:30 | 44325.3542 | 0 | 8.6055 | 39.95
2021-05-09 09:00 | 44325.375 | 0 | 8.35 | 39.95
2021-05-09 09:30 | 44325.3958 | 0 | 10.0183 | 39.95
2021-05-09 10:00 | 44325.4167 | 0 | 9.9259 | 39.95
2021-05-09 10:30 | 44325.4375 | 0 | 7.9679 | 39.95
2021-05-09 11:00 | 44325.4583 | 0 | 7.8915 | 39.95
2021-05-09 11:30 | 44325.4792 | 0 | 6.6609 | 39.95
2021-05-09 12:00 | 44325.5 | 0 | 6.9032 | 39.95
2021-05-09 12:30 | 44325.5208 | 0 | 7.6781 | 39.95
2021-05-09 13:00 | 44325.5417 | 0 | 8.3505 | 39.95
2021-05-09 13:30 | 44325.5625 | 0 | 8.0861 | 39.95
2021-05-09 14:00 | 44325.5833 | 0 | 7.6827 | 39.95
2021-05-09 14:30 | 44325.6042 | 0 | 8.6941 | 39.95
2021-05-09 15:00 | 44325.625 | 0 | 9.0994 | 39.95
2021-05-09 15:30 | 44325.6458 | 0 | 9.8905 | 39.95
2021-05-09 16:00 | 44325.6667 | 0 | 10.5433 | 39.95
2021-05-09 16:30 | 44325.6875 | 0 | 10.9977 | 39.95
2021-05-09 17:00 | 44325.7083 | 0 | 11.3452 | 39.95
2021-05-09 17:30 | 44325.7292 | 0 | 12.0101 | 39.95
2021-05-09 18:00 | 44325.75 | 0 | 12.0124 | 39.95
2021-05-09 18:30 | 44325.7708 | 0 | 11.8289 | 39.95
2021-05-09 19:00 | 44325.7917 | 0 | 11.5883 | 39.95
2021-05-09 19:30 | 44325.8125 | 0 | 11.4669 | 39.95
2021-05-09 20:00 | 44325.8333 | 0 | 11.1363 | 39.95
2021-05-09 20:30 | 44325.8542 | 0 | 10.5754 | 39.95
2021-05-09 21:00 | 44325.875 | 0 | 10.1338 | 39.95
2021-05-09 21:30 | 44325.8958 | 0 | 9.7732 | 39.95
2021-05-09 22:00 | 44325.9167 | 0 | 9.385 | 39.95
2021-05-09 22:30 | 44325.9375 | 0 | 8.7907 | 39.95
2021-05-09 23:00 | 44325.9583 | 0 | 8.3493 | 39.95
2021-05-09 23:30 | 44325.9792 | 0 | 8.0374 | 39.95
2021-05-10 | 44326 | 0 | 7.8825 | 39.95
2021-05-10 00:30 | 44326.0208 | 0 | 7.5461 | 39.95
2021-05-10 01:00 | 44326.0417 | 0 | 7.4803 | 39.95
2021-05-10 01:30 | 44326.0625 | 0 | 7.3209 | 39.95
2021-05-10 02:00 | 44326.0833 | 0 | 7.2068 | 39.95
2021-05-10 02:30 | 44326.1042 | 0 | 7.2432 | 39.95
2021-05-10 03:00 | 44326.125 | 0 | 7.2072 | 39.95
2021-05-10 03:30 | 44326.1458 | 0 | 7.4614 | 39.95
2021-05-10 04:00 | 44326.1667 | 0 | 7.6357 | 39.95
2021-05-10 04:30 | 44326.1875 | 0 | 8.0256 | 39.95
2021-05-10 05:00 | 44326.2083 | 0 | 8.8262 | 39.95
2021-05-10 05:30 | 44326.2292 | 0 | 9.5234 | 39.95
2021-05-10 06:00 | 44326.25 | 0 | 10.4729 | 39.95
2021-05-10 06:30 | 44326.2708 | 0 | 11.3518 | 39.95
2021-05-10 07:00 | 44326.2917 | 0 | 11.4029 | 39.95
2021-05-10 07:30 | 44326.3125 | 0 | 11.7388 | 39.95
2021-05-10 08:00 | 44326.3333 | 0 | 12.0808 | 39.95
2021-05-10 08:30 | 44326.3542 | 0 | 11.6876 | 39.95
2021-05-10 09:00 | 44326.375 | 0 | 11.3187 | 39.95
2021-05-10 09:30 | 44326.3958 | 0 | 10.2269 | 39.95
2021-05-10 10:00 | 44326.4167 | 0 | 9.9815 | 39.95
2021-05-10 10:30 | 44326.4375 | 0 | 9.985 | 39.95
2021-05-10 11:00 | 44326.4583 | 0 | 10.0251 | 39.95
2021-05-10 11:30 | 44326.4792 | 0 | 10.1998 | 39.95
2021-05-10 12:00 | 44326.5 | 0 | 10.541 | 39.95
2021-05-10 12:30 | 44326.5208 | 0 | 10.9638 | 39.95
2021-05-10 13:00 | 44326.5417 | 0 | 11.8371 | 39.95
2021-05-10 13:30 | 44326.5625 | 0 | 11.6072 | 39.95
2021-05-10 14:00 | 44326.5833 | 0 | 12.7244 | 39.95
2021-05-10 14:30 | 44326.6042 | 0 | 12.5694 | 39.95
2021-05-10 15:00 | 44326.625 | 0 | 12.5229 | 39.95
2021-05-10 15:30 | 44326.6458 | 0 | 13.8563 | 39.95
2021-05-10 16:00 | 44326.6667 | 0 | 13.651 | 39.95
2021-05-10 16:30 | 44326.6875 | 0 | 13.9005 | 39.95
2021-05-10 17:00 | 44326.7083 | 0 | 13.973 | 39.95
2021-05-10 17:30 | 44326.7292 | 0 | 14.7002 | 39.95
2021-05-10 18:00 | 44326.75 | 0 | 14.6926 | 39.95
2021-05-10 18:30 | 44326.7708 | 0 | 14.7552 | 39.95
2021-05-10 19:00 | 44326.7917 | 0 | 14.1229 | 39.95
2021-05-10 19:30 | 44326.8125 | 0 | 14.0488 | 39.95
2021-05-10 20:00 | 44326.8333 | 0 | 13.4968 | 39.95
2021-05-10 20:30 | 44326.8542 | 0 | 12.8973 | 39.95
2021-05-10 21:00 | 44326.875 | 0 | 12.2918 | 39.95
2021-05-10 21:30 | 44326.8958 | 0 | 11.9338 | 39.95
2021-05-10 22:00 | 44326.9167 | 0 | 11.453 | 39.95
2021-05-10 22:30 | 44326.9375 | 0 | 10.555 | 39.95
2021-05-10 23:00 | 44326.9583 | 0 | 9.9102 | 39.95
2021-05-10 23:30 | 44326.9792 | 0 | 9.6643 | 39.95
2021-05-11 | 44327 | 0 | 9.1267 | 39.95
2021-05-11 00:30 | 44327.0208 | 0 | 8.496 | 39.95
2021-05-11 01:00 | 44327.0417 | 0 | 8.4406 | 39.95
2021-05-11 01:30 | 44327.0625 | 0 | 8.3533 | 39.95
2021-05-11 02:00 | 44327.0833 | 0 | 8.1514 | 39.95
2021-05-11 02:30 | 44327.1042 | 0 | 8.0609 | 39.95
2021-05-11 03:00 | 44327.125 | 0 | 7.9751 | 39.95
2021-05-11 03:30 | 44327.1458 | 0 | 8.1302 | 39.95
2021-05-11 04:00 | 44327.1667 | 0 | 8.2398 | 39.95
2021-05-11 04:30 | 44327.1875 | 0 | 8.79 | 39.95
2021-05-11 05:00 | 44327.2083 | 0 | 9.3948 | 39.95
2021-05-11 05:30 | 44327.2292 | 0 | 9.8327 | 39.95
2021-05-11 06:00 | 44327.25 | 0 | 10.7982 | 39.95
2021-05-11 06:30 | 44327.2708 | 0 | 11.5731 | 39.95
2021-05-11 07:00 | 44327.2917 | 0 | 11.8724 | 39.95
2021-05-11 07:30 | 44327.3125 | 0 | 11.7042 | 39.95
2021-05-11 08:00 | 44327.3333 | 0 | 11.7911 | 39.95
2021-05-11 08:30 | 44327.3542 | 0 | 10.8629 | 39.95
2021-05-11 09:00 | 44327.375 | 0 | 10.525 | 39.95
2021-05-11 09:30 | 44327.3958 | 0 | 10.3326 | 39.95
2021-05-11 10:00 | 44327.4167 | 0 | 10.0886 | 39.95
2021-05-11 10:30 | 44327.4375 | 0 | 9.9616 | 39.95
2021-05-11 11:00 | 44327.4583 | 0 | 9.8531 | 39.95
2021-05-11 11:30 | 44327.4792 | 0 | 9.8192 | 39.95
2021-05-11 12:00 | 44327.5 | 0 | 10.0909 | 39.95
2021-05-11 12:30 | 44327.5208 | 0 | 10.0897 | 39.95
2021-05-11 13:00 | 44327.5417 | 0 | 10.568 | 39.95
2021-05-11 13:30 | 44327.5625 | 0 | 11.0231 | 39.95
2021-05-11 14:00 | 44327.5833 | 0 | 11.7202 | 39.95
2021-05-11 14:30 | 44327.6042 | 0 | 12.2916 | 39.95
2021-05-11 15:00 | 44327.625 | 0 | 12.9209 | 39.95
2021-05-11 15:30 | 44327.6458 | 0 | 13.1318 | 39.95
2021-05-11 16:00 | 44327.6667 | 0 | 13.5817 | 39.95
2021-05-11 16:30 | 44327.6875 | 0 | 13.9472 | 39.95
2021-05-11 17:00 | 44327.7083 | 0 | 14.1889 | 39.95
2021-05-11 17:30 | 44327.7292 | 0 | 14.79 | 39.95
2021-05-11 18:00 | 44327.75 | 0 | 14.7561 | 39.95
2021-05-11 18:30 | 44327.7708 | 0 | 14.6534 | 39.95
2021-05-11 19:00 | 44327.7917 | 0 | 14.0608 | 39.95
2021-05-11 19:30 | 44327.8125 | 0 | 14.09 | 39.95
2021-05-11 20:00 | 44327.8333 | 0 | 13.8405 | 39.95
2021-05-11 20:30 | 44327.8542 | 0 | 13.3073 | 39.95
2021-05-11 21:00 | 44327.875 | 0 | 12.6334 | 39.95
2021-05-11 21:30 | 44327.8958 | 0 | 12.2255 | 39.95
2021-05-11 22:00 | 44327.9167 | 0 | 11.9188 | 39.95
2021-05-11 22:30 | 44327.9375 | 0 | 11.0995 | 39.95
2021-05-11 23:00 | 44327.9583 | 0 | 10.4474 | 39.95
2021-05-11 23:30 | 44327.9792 | 0 | 9.9909 | 39.95
2021-05-12 | 44328 | 0 | 9.3552 | 39.95
2021-05-12 00:30 | 44328.0208 | 0 | 8.8407 | 39.95
2021-05-12 01:00 | 44328.0417 | 0 | 8.747 | 39.95
2021-05-12 01:30 | 44328.0625 | 0 | 8.6098 | 39.95
2021-05-12 02:00 | 44328.0833 | 0 | 8.4196 | 39.95
2021-05-12 02:30 | 44328.1042 | 0 | 8.4171 | 39.95
2021-05-12 03:00 | 44328.125 | 0 | 8.2517 | 39.95
2021-05-12 03:30 | 44328.1458 | 0 | 8.4629 | 39.95
2021-05-12 04:00 | 44328.1667 | 0 | 8.6069 | 39.95
2021-05-12 04:30 | 44328.1875 | 0 | 9.0793 | 39.95
2021-05-12 05:00 | 44328.2083 | 0 | 9.4413 | 39.95
2021-05-12 05:30 | 44328.2292 | 0 | 10.1509 | 39.95
2021-05-12 06:00 | 44328.25 | 0 | 11.0497 | 39.95
2021-05-12 06:30 | 44328.2708 | 0 | 12.0478 | 39.95
2021-05-12 07:00 | 44328.2917 | 0 | 12.1513 | 39.95
2021-05-12 07:30 | 44328.3125 | 0 | 12.0743 | 39.95
2021-05-12 08:00 | 44328.3333 | 0 | 11.7035 | 39.95
2021-05-12 08:30 | 44328.3542 | 0 | 11.576 | 39.95
2021-05-12 09:00 | 44328.375 | 0 | 11.9429 | 39.95
2021-05-12 09:30 | 44328.3958 | 0 | 11.9822 | 39.95
2021-05-12 10:00 | 44328.4167 | 0 | 11.1817 | 39.95
2021-05-12 10:30 | 44328.4375 | 0 | 12.6758 | 39.95
2021-05-12 11:00 | 44328.4583 | 0 | 13.1347 | 39.95
2021-05-12 11:30 | 44328.4792 | 0 | 12.0337 | 39.95
2021-05-12 12:00 | 44328.5 | 0 | 12.4337 | 39.95
2021-05-12 12:30 | 44328.5208 | 0 | 13.2708 | 39.95
2021-05-12 13:00 | 44328.5417 | 0 | 12.2037 | 39.95
2021-05-12 13:30 | 44328.5625 | 0 | 12.4669 | 39.95
2021-05-12 14:00 | 44328.5833 | 0 | 13.3221 | 39.95
2021-05-12 14:30 | 44328.6042 | 0 | 12.4686 | 39.95
2021-05-12 15:00 | 44328.625 | 0 | 13.4426 | 39.95
2021-05-12 15:30 | 44328.6458 | 0 | 13.8855 | 39.95
2021-05-12 16:00 | 44328.6667 | 0 | 14.1082 | 39.95
2021-05-12 16:30 | 44328.6875 | 0 | 14.704 | 39.95
2021-05-12 17:00 | 44328.7083 | 0 | 14.015 | 39.95
2021-05-12 17:30 | 44328.7292 | 0 | 14.3242 | 39.95
2021-05-12 18:00 | 44328.75 | 0 | 14.0058 | 39.95
2021-05-12 18:30 | 44328.7708 | 0 | 13.6674 | 39.95
2021-05-12 19:00 | 44328.7917 | 0 | 13.5098 | 39.95
2021-05-12 19:30 | 44328.8125 | 0 | 13.407 | 39.95
2021-05-12 20:00 | 44328.8333 | 0 | 13.1056 | 39.95
2021-05-12 20:30 | 44328.8542 | 0 | 12.805 | 39.95
2021-05-12 21:00 | 44328.875 | 0 | 12.2118 | 39.95
2021-05-12 21:30 | 44328.8958 | 0 | 11.7035 | 39.95
2021-05-12 22:00 | 44328.9167 | 0 | 11.292 | 39.95
2021-05-12 22:30 | 44328.9375 | 0 | 10.3471 | 39.95
2021-05-12 23:00 | 44328.9583 | 0 | 9.7677 | 39.95
2021-05-12 23:30 | 44328.9792 | 0 | 9.3882 | 39.95
2021-05-13 | 44329 | 0 | 8.9297 | 39.95
2021-05-13 00:30 | 44329.0208 | 0 | 8.438 | 39.95
2021-05-13 01:00 | 44329.0417 | 0 | 8.3278 | 39.95
2021-05-13 01:30 | 44329.0625 | 0 | 8.1886 | 39.95
2021-05-13 02:00 | 44329.0833 | 0 | 8.209 | 39.95
2021-05-13 02:30 | 44329.1042 | 0 | 8.101 | 39.95
2021-05-13 03:00 | 44329.125 | 0 | 8.1068 | 39.95
2021-05-13 03:30 | 44329.1458 | 0 | 8.2771 | 39.95
2021-05-13 04:00 | 44329.1667 | 0 | 8.6531 | 39.95
2021-05-13 04:30 | 44329.1875 | 0 | 8.8283 | 39.95
2021-05-13 05:00 | 44329.2083 | 0 | 9.3893 | 39.95
2021-05-13 05:30 | 44329.2292 | 0 | 10.0301 | 39.95
2021-05-13 06:00 | 44329.25 | 0 | 11.1478 | 39.95
2021-05-13 06:30 | 44329.2708 | 0 | 11.9736 | 39.95
2021-05-13 07:00 | 44329.2917 | 0 | 12.3701 | 39.95
2021-05-13 07:30 | 44329.3125 | 0 | 11.881 | 39.95
2021-05-13 08:00 | 44329.3333 | 0 | 11.5825 | 39.95
2021-05-13 08:30 | 44329.3542 | 0 | 10.9147 | 39.95
2021-05-13 09:00 | 44329.375 | 0 | 10.5834 | 39.95
2021-05-13 09:30 | 44329.3958 | 0 | 10.267 | 39.95
2021-05-13 10:00 | 44329.4167 | 0 | 9.871 | 39.95
2021-05-13 10:30 | 44329.4375 | 0 | 9.8891 | 39.95
2021-05-13 11:00 | 44329.4583 | 0 | 9.5626 | 39.95
2021-05-13 11:30 | 44329.4792 | 0 | 9.3327 | 39.95
2021-05-13 12:00 | 44329.5 | 0 | 9.2331 | 39.95
2021-05-13 12:30 | 44329.5208 | 0 | 9.3832 | 39.95
2021-05-13 13:00 | 44329.5417 | 0 | 9.6053 | 39.95
2021-05-13 13:30 | 44329.5625 | 0 | 9.8543 | 39.95
2021-05-13 14:00 | 44329.5833 | 0 | 10.2097 | 39.95
2021-05-13 14:30 | 44329.6042 | 0 | 10.7943 | 39.95
2021-05-13 15:00 | 44329.625 | 0 | 11.3464 | 39.95
2021-05-13 15:30 | 44329.6458 | 0 | 11.9391 | 39.95
2021-05-13 16:00 | 44329.6667 | 0 | 12.2872 | 39.95
2021-05-13 16:30 | 44329.6875 | 0 | 12.7678 | 39.95
2021-05-13 17:00 | 44329.7083 | 0 | 13.2546 | 39.95
2021-05-13 17:30 | 44329.7292 | 0 | 13.6827 | 39.95
2021-05-13 18:00 | 44329.75 | 0 | 13.73 | 39.95
2021-05-13 18:30 | 44329.7708 | 0 | 13.726 | 39.95
2021-05-13 19:00 | 44329.7917 | 0 | 13.491 | 39.95
2021-05-13 19:30 | 44329.8125 | 0 | 13.1469 | 39.95
2021-05-13 20:00 | 44329.8333 | 0 | 12.9126 | 39.95
2021-05-13 20:30 | 44329.8542 | 0 | 12.6122 | 39.95
2021-05-13 21:00 | 44329.875 | 0 | 12.1226 | 39.95
2021-05-13 21:30 | 44329.8958 | 0 | 11.7383 | 39.95
2021-05-13 22:00 | 44329.9167 | 0 | 11.149 | 39.95
2021-05-13 22:30 | 44329.9375 | 0 | 10.2341 | 39.95
2021-05-13 23:00 | 44329.9583 | 0 | 9.6145 | 39.95
2021-05-13 23:30 | 44329.9792 | 0 | 9.3291 | 39.95
2021-05-14 | 44330 | 0 | 8.6049 | 39.95
2021-05-14 00:30 | 44330.0208 | 0 | 8.1753 | 39.95
2021-05-14 01:00 | 44330.0417 | 0 | 7.8376 | 39.95
2021-05-14 01:30 | 44330.0625 | 0 | 7.8153 | 39.95
2021-05-14 02:00 | 44330.0833 | 0 | 7.7717 | 39.95
2021-05-14 02:30 | 44330.1042 | 0 | 7.8164 | 39.95
2021-05-14 03:00 | 44330.125 | 0 | 7.7781 | 39.95
2021-05-14 03:30 | 44330.1458 | 0 | 7.868 | 39.95
2021-05-14 04:00 | 44330.1667 | 0 | 8.2513 | 39.95
2021-05-14 04:30 | 44330.1875 | 0 | 8.4975 | 39.95
2021-05-14 05:00 | 44330.2083 | 0 | 9.0956 | 39.95
2021-05-14 05:30 | 44330.2292 | 0 | 9.7962 | 39.95
2021-05-14 06:00 | 44330.25 | 0 | 10.7301 | 39.95
2021-05-14 06:30 | 44330.2708 | 0 | 11.7237 | 39.95
2021-05-14 07:00 | 44330.2917 | 0 | 12.0086 | 39.95
2021-05-14 07:30 | 44330.3125 | 0 | 11.661 | 39.95
2021-05-14 08:00 | 44330.3333 | 0 | 11.1545 | 39.95
2021-05-14 08:30 | 44330.3542 | 0 | 10.2959 | 39.95
2021-05-14 09:00 | 44330.375 | 0 | 9.6654 | 39.95
2021-05-14 09:30 | 44330.3958 | 0 | 9.4442 | 39.95
2021-05-14 10:00 | 44330.4167 | 0 | 9.0224 | 39.95
2021-05-14 10:30 | 44330.4375 | 0 | 8.81 | 39.95
2021-05-14 11:00 | 44330.4583 | 0 | 8.8065 | 39.95
2021-05-14 11:30 | 44330.4792 | 0 | 8.6234 | 39.95
2021-05-14 12:00 | 44330.5 | 0 | 8.2971 | 39.95
2021-05-14 12:30 | 44330.5208 | 0 | 8.5769 | 39.95
2021-05-14 13:00 | 44330.5417 | 0 | 8.6876 | 39.95
2021-05-14 13:30 | 44330.5625 | 0 | 9.0898 | 39.95
2021-05-14 14:00 | 44330.5833 | 0 | 9.6291 | 39.95
2021-05-14 14:30 | 44330.6042 | 0 | 10.2141 | 39.95
2021-05-14 15:00 | 44330.625 | 0 | 10.8014 | 39.95
2021-05-14 15:30 | 44330.6458 | 0 | 11.5767 | 39.95
2021-05-14 16:00 | 44330.6667 | 0 | 12.2886 | 39.95
2021-05-14 16:30 | 44330.6875 | 0 | 12.7436 | 39.95
2021-05-14 17:00 | 44330.7083 | 0 | 12.8997 | 39.95
2021-05-14 17:30 | 44330.7292 | 0 | 13.1609 | 39.95
2021-05-14 18:00 | 44330.75 | 0 | 13.1897 | 39.95
2021-05-14 18:30 | 44330.7708 | 0 | 13.0686 | 39.95
2021-05-14 19:00 | 44330.7917 | 0 | 12.6148 | 39.95
2021-05-14 19:30 | 44330.8125 | 0 | 12.7061 | 39.95
2021-05-14 20:00 | 44330.8333 | 0 | 12.3967 | 39.95
2021-05-14 20:30 | 44330.8542 | 0 | 11.9989 | 39.95
2021-05-14 21:00 | 44330.875 | 0 | 11.6672 | 39.95
2021-05-14 21:30 | 44330.8958 | 0 | 11.2757 | 39.95
2021-05-14 22:00 | 44330.9167 | 0 | 10.8653 | 39.95
2021-05-14 22:30 | 44330.9375 | 0 | 10.0408 | 39.95
2021-05-14 23:00 | 44330.9583 | 0 | 9.4324 | 39.95
2021-05-14 23:30 | 44330.9792 | 0 | 9.0518 | 39.95
2021-05-15 | 44331 | 0 | 8.5575 | 39.95
2021-05-15 00:30 | 44331.0208 | 0 | 8.1539 | 39.95
2021-05-15 01:00 | 44331.0417 | 0 | 7.9458 | 39.95
2021-05-15 01:30 | 44331.0625 | 0 | 7.7864 | 39.95
2021-05-15 02:00 | 44331.0833 | 0 | 7.6573 | 39.95
2021-05-15 02:30 | 44331.1042 | 0 | 7.6343 | 39.95
2021-05-15 03:00 | 44331.125 | 0 | 7.4979 | 39.95
2021-05-15 03:30 | 44331.1458 | 0 | 7.6126 | 39.95
2021-05-15 04:00 | 44331.1667 | 0 | 7.6527 | 39.95
2021-05-15 04:30 | 44331.1875 | 0 | 7.7611 | 39.95
2021-05-15 05:00 | 44331.2083 | 0 | 8.0024 | 39.95
2021-05-15 05:30 | 44331.2292 | 0 | 8.328 | 39.95
2021-05-15 06:00 | 44331.25 | 0 | 8.7584 | 39.95
2021-05-15 06:30 | 44331.2708 | 0 | 9.0483 | 39.95
2021-05-15 07:00 | 44331.2917 | 0 | 9.0447 | 39.95
2021-05-15 07:30 | 44331.3125 | 0 | 9.0259 | 39.95
2021-05-15 08:00 | 44331.3333 | 0 | 9.2994 | 39.95
2021-05-15 08:30 | 44331.3542 | 0 | 8.6913 | 39.95
2021-05-15 09:00 | 44331.375 | 0 | 8.3081 | 39.95
2021-05-15 09:30 | 44331.3958 | 0 | 7.8992 | 39.95
2021-05-15 10:00 | 44331.4167 | 0 | 7.3169 | 39.95
2021-05-15 10:30 | 44331.4375 | 0 | 7.0302 | 39.95
2021-05-15 11:00 | 44331.4583 | 0 | 6.7573 | 39.95
2021-05-15 11:30 | 44331.4792 | 0 | 6.4788 | 39.95
2021-05-15 12:00 | 44331.5 | 0 | 6.5677 | 39.95
2021-05-15 12:30 | 44331.5208 | 0 | 6.7402 | 39.95
2021-05-15 13:00 | 44331.5417 | 0 | 6.6766 | 39.95
2021-05-15 13:30 | 44331.5625 | 0 | 6.9042 | 39.95
2021-05-15 14:00 | 44331.5833 | 0 | 7.4189 | 39.95
2021-05-15 14:30 | 44331.6042 | 0 | 7.9093 | 39.95
2021-05-15 15:00 | 44331.625 | 0 | 8.4078 | 39.95
2021-05-15 15:30 | 44331.6458 | 0 | 9.0816 | 39.95
2021-05-15 16:00 | 44331.6667 | 0 | 9.8478 | 39.95
2021-05-15 16:30 | 44331.6875 | 0 | 10.563 | 39.95
2021-05-15 17:00 | 44331.7083 | 0 | 11.0781 | 39.95
2021-05-15 17:30 | 44331.7292 | 0 | 11.3459 | 39.95
2021-05-15 18:00 | 44331.75 | 0 | 11.3769 | 39.95
2021-05-15 18:30 | 44331.7708 | 0 | 11.3047 | 39.95
2021-05-15 19:00 | 44331.7917 | 0 | 11.1675 | 39.95
2021-05-15 19:30 | 44331.8125 | 0 | 10.9634 | 39.95
2021-05-15 20:00 | 44331.8333 | 0 | 10.6904 | 39.95
2021-05-15 20:30 | 44331.8542 | 0 | 10.3039 | 39.95
2021-05-15 21:00 | 44331.875 | 0 | 9.9178 | 39.95
2021-05-15 21:30 | 44331.8958 | 0 | 9.7307 | 39.95
2021-05-15 22:00 | 44331.9167 | 0 | 9.3887 | 39.95
2021-05-15 22:30 | 44331.9375 | 0 | 8.9711 | 39.95
2021-05-15 23:00 | 44331.9583 | 0 | 8.4171 | 39.95
2021-05-15 23:30 | 44331.9792 | 0 | 8.1159 | 39.95
2021-05-16 | 44332 | 0 | 7.7143 | 39.95
2021-05-16 00:30 | 44332.0208 | 0 | 7.3586 | 39.95
2021-05-16 01:00 | 44332.0417 | 0 | 7.2249 | 39.95
2021-05-16 01:30 | 44332.0625 | 0 | 7.1136 | 39.95
2021-05-16 02:00 | 44332.0833 | 0 | 7.0571 | 39.95
2021-05-16 02:30 | 44332.1042 | 0 | 6.9408 | 39.95
2021-05-16 03:00 | 44332.125 | 0 | 6.8619 | 39.95
2021-05-16 03:30 | 44332.1458 | 0 | 7.0078 | 39.95
2021-05-16 04:00 | 44332.1667 | 0 | 6.8808 | 39.95
2021-05-16 04:30 | 44332.1875 | 0 | 6.9478 | 39.95
2021-05-16 05:00 | 44332.2083 | 0 | 7.1006 | 39.95
2021-05-16 05:30 | 44332.2292 | 0 | 7.2498 | 39.95
2021-05-16 06:00 | 44332.25 | 0 | 7.5307 | 39.95
2021-05-16 06:30 | 44332.2708 | 0 | 7.6832 | 39.95
2021-05-16 07:00 | 44332.2917 | 0 | 7.9581 | 39.95
2021-05-16 07:30 | 44332.3125 | 0 | 7.8334 | 39.95
2021-05-16 08:00 | 44332.3333 | 0 | 7.8004 | 39.95
2021-05-16 08:30 | 44332.3542 | 0 | 7.4949 | 39.95
2021-05-16 09:00 | 44332.375 | 0 | 7.1548 | 39.95
2021-05-16 09:30 | 44332.3958 | 0 | 6.7094 | 39.95
2021-05-16 10:00 | 44332.4167 | 0 | 6.3825 | 39.95
2021-05-16 10:30 | 44332.4375 | 0 | 6.1696 | 39.95
2021-05-16 11:00 | 44332.4583 | 0 | 6.0298 | 39.95
2021-05-16 11:30 | 44332.4792 | 0 | 5.937 | 39.95
2021-05-16 12:00 | 44332.5 | 0 | 5.85 | 39.95
2021-05-16 12:30 | 44332.5208 | 0 | 5.9004 | 39.95
2021-05-16 13:00 | 44332.5417 | 0 | 6.0545 | 39.95
2021-05-16 13:30 | 44332.5625 | 0 | 6.301 | 39.95
2021-05-16 14:00 | 44332.5833 | 0 | 6.8959 | 39.95
2021-05-16 14:30 | 44332.6042 | 0 | 7.3999 | 39.95
2021-05-16 15:00 | 44332.625 | 0 | 8.0519 | 39.95
2021-05-16 15:30 | 44332.6458 | 0 | 8.8471 | 39.95
2021-05-16 16:00 | 44332.6667 | 0 | 9.6873 | 39.95
2021-05-16 16:30 | 44332.6875 | 0 | 10.7356 | 39.95
2021-05-16 17:00 | 44332.7083 | 0 | 11.3478 | 39.95
2021-05-16 17:30 | 44332.7292 | 0 | 12.1558 | 39.95
2021-05-16 18:00 | 44332.75 | 0 | 12.2995 | 39.95
2021-05-16 18:30 | 44332.7708 | 0 | 12.1946 | 39.95
2021-05-16 19:00 | 44332.7917 | 0 | 11.9562 | 39.95
2021-05-16 19:30 | 44332.8125 | 0 | 11.5637 | 39.95
2021-05-16 20:00 | 44332.8333 | 0 | 11.2569 | 39.95
2021-05-16 20:30 | 44332.8542 | 0 | 10.9616 | 39.95
2021-05-16 21:00 | 44332.875 | 0 | 10.2989 | 39.95
2021-05-16 21:30 | 44332.8958 | 0 | 9.8926 | 39.95
2021-05-16 22:00 | 44332.9167 | 0 | 9.5104 | 39.95
2021-05-16 22:30 | 44332.9375 | 0 | 8.8041 | 39.95
2021-05-16 23:00 | 44332.9583 | 0 | 8.2525 | 39.95
2021-05-16 23:30 | 44332.9792 | 0 | 7.9227 | 39.95
2021-05-17 | 44333 | 0 | 7.6853 | 39.95
2021-05-17 00:30 | 44333.0208 | 0 | 7.5261 | 39.95
2021-05-17 01:00 | 44333.0417 | 0 | 7.2837 | 39.95
2021-05-17 01:30 | 44333.0625 | 0 | 7.1037 | 39.95
2021-05-17 02:00 | 44333.0833 | 0 | 7.2804 | 39.95
2021-05-17 02:30 | 44333.1042 | 0 | 7.2413 | 39.95
2021-05-17 03:00 | 44333.125 | 0 | 7.2663 | 39.95
2021-05-17 03:30 | 44333.1458 | 0 | 7.4649 | 39.95
2021-05-17 04:00 | 44333.1667 | 0 | 7.7869 | 39.95
2021-05-17 04:30 | 44333.1875 | 0 | 8.2175 | 39.95
2021-05-17 05:00 | 44333.2083 | 0 | 8.8789 | 39.95
2021-05-17 05:30 | 44333.2292 | 0 | 9.9918 | 39.95
2021-05-17 06:00 | 44333.25 | 0 | 11.4186 | 39.95
2021-05-17 06:30 | 44333.2708 | 0 | 12.7956 | 39.95
2021-05-17 07:00 | 44333.2917 | 0 | 13.308 | 39.95
2021-05-17 07:30 | 44333.3125 | 0 | 12.7572 | 39.95
2021-05-17 08:00 | 44333.3333 | 0 | 12.0097 | 39.95
2021-05-17 08:30 | 44333.3542 | 0 | 11.3002 | 39.95
2021-05-17 09:00 | 44333.375 | 0 | 10.4331 | 39.95
2021-05-17 09:30 | 44333.3958 | 0 | 9.7595 | 39.95
2021-05-17 10:00 | 44333.4167 | 0 | 9.1654 | 39.95
2021-05-17 10:30 | 44333.4375 | 0 | 9.0201 | 39.95
2021-05-17 11:00 | 44333.4583 | 0 | 8.6499 | 39.95
2021-05-17 11:30 | 44333.4792 | 0 | 8.5299 | 39.95
2021-05-17 12:00 | 44333.5 | 0 | 8.3536 | 39.95
2021-05-17 12:30 | 44333.5208 | 0 | 8.5534 | 39.95
2021-05-17 13:00 | 44333.5417 | 0 | 8.6157 | 39.95
2021-05-17 13:30 | 44333.5625 | 0 | 9.6701 | 39.95
2021-05-17 14:00 | 44333.5833 | 0 | 10.8274 | 39.95
2021-05-17 14:30 | 44333.6042 | 0 | 9.8263 | 39.95
2021-05-17 15:00 | 44333.625 | 0 | 10.3074 | 39.95
2021-05-17 15:30 | 44333.6458 | 0 | 10.961 | 39.95
2021-05-17 16:00 | 44333.6667 | 0 | 11.6176 | 39.95
2021-05-17 16:30 | 44333.6875 | 0 | 12.5002 | 39.95
2021-05-17 17:00 | 44333.7083 | 0 | 13.5177 | 39.95
2021-05-17 17:30 | 44333.7292 | 0 | 14.377 | 39.95
2021-05-17 18:00 | 44333.75 | 0 | 14.7584 | 39.95
2021-05-17 18:30 | 44333.7708 | 0 | 14.6111 | 39.95
2021-05-17 19:00 | 44333.7917 | 0 | 14.4606 | 39.95
2021-05-17 19:30 | 44333.8125 | 0 | 14.185 | 39.95
2021-05-17 20:00 | 44333.8333 | 0 | 13.9811 | 39.95
2021-05-17 20:30 | 44333.8542 | 0 | 13.2113 | 39.95
2021-05-17 21:00 | 44333.875 | 0 | 12.7233 | 39.95
2021-05-17 21:30 | 44333.8958 | 0 | 12.2155 | 39.95
2021-05-17 22:00 | 44333.9167 | 0 | 11.3151 | 39.95
2021-05-17 22:30 | 44333.9375 | 0 | 10.4539 | 39.95
2021-05-17 23:00 | 44333.9583 | 0 | 9.7541 | 39.95
2021-05-17 23:30 | 44333.9792 | 0 | 9.4017 | 39.95
2021-05-18 | 44334 | 0 | 8.7778 | 39.95
2021-05-18 00:30 | 44334.0208 | 0 | 8.3787 | 39.95
2021-05-18 01:00 | 44334.0417 | 0 | 8.244 | 39.95
2021-05-18 01:30 | 44334.0625 | 0 | 8.148 | 39.95
2021-05-18 02:00 | 44334.0833 | 0 | 7.9716 | 39.95
2021-05-18 02:30 | 44334.1042 | 0 | 7.8823 | 39.95
2021-05-18 03:00 | 44334.125 | 0 | 7.9304 | 39.95
2021-05-18 03:30 | 44334.1458 | 0 | 8.1016 | 39.95
2021-05-18 04:00 | 44334.1667 | 0 | 8.2759 | 39.95
2021-05-18 04:30 | 44334.1875 | 0 | 8.8864 | 39.95
2021-05-18 05:00 | 44334.2083 | 0 | 9.5808 | 39.95
2021-05-18 05:30 | 44334.2292 | 0 | 10.692 | 39.95
2021-05-18 06:00 | 44334.25 | 0 | 11.8493 | 39.95
2021-05-18 06:30 | 44334.2708 | 0 | 13.1305 | 39.95
2021-05-18 07:00 | 44334.2917 | 0 | 13.4475 | 39.95
2021-05-18 07:30 | 44334.3125 | 0 | 13.0451 | 39.95
2021-05-18 08:00 | 44334.3333 | 0 | 12.2285 | 39.95
2021-05-18 08:30 | 44334.3542 | 0 | 11.2452 | 39.95
2021-05-18 09:00 | 44334.375 | 0 | 10.3572 | 39.95
2021-05-18 09:30 | 44334.3958 | 0 | 9.8477 | 39.95
2021-05-18 10:00 | 44334.4167 | 0 | 9.3007 | 39.95
2021-05-18 10:30 | 44334.4375 | 0 | 9.1144 | 39.95
2021-05-18 11:00 | 44334.4583 | 0 | 8.8317 | 39.95
2021-05-18 11:30 | 44334.4792 | 0 | 9.187 | 39.95
2021-05-18 12:00 | 44334.5 | 0 | 10.0736 | 39.95
2021-05-18 12:30 | 44334.5208 | 0 | 9.4188 | 39.95
2021-05-18 13:00 | 44334.5417 | 0 | 9.8443 | 39.95
2021-05-18 13:30 | 44334.5625 | 0 | 9.7581 | 39.95
2021-05-18 14:00 | 44334.5833 | 0 | 10.206 | 39.95
2021-05-18 14:30 | 44334.6042 | 0 | 10.4472 | 39.95
2021-05-18 15:00 | 44334.625 | 0 | 10.9265 | 39.95
2021-05-18 15:30 | 44334.6458 | 0 | 11.5337 | 39.95
2021-05-18 16:00 | 44334.6667 | 0 | 12.2026 | 39.95
2021-05-18 16:30 | 44334.6875 | 0 | 12.9163 | 39.95
2021-05-18 17:00 | 44334.7083 | 0 | 13.6552 | 39.95
2021-05-18 17:30 | 44334.7292 | 0 | 14.4855 | 39.95
2021-05-18 18:00 | 44334.75 | 0 | 14.4369 | 39.95
2021-05-18 18:30 | 44334.7708 | 0 | 14.4372 | 39.95
2021-05-18 19:00 | 44334.7917 | 0 | 14.1112 | 39.95
2021-05-18 19:30 | 44334.8125 | 0 | 13.9705 | 39.95
2021-05-18 20:00 | 44334.8333 | 0 | 13.6695 | 39.95
2021-05-18 20:30 | 44334.8542 | 0 | 13.2046 | 39.95
2021-05-18 21:00 | 44334.875 | 0 | 12.5664 | 39.95
2021-05-18 21:30 | 44334.8958 | 0 | 11.9463 | 39.95
2021-05-18 22:00 | 44334.9167 | 0 | 11.3551 | 39.95
2021-05-18 22:30 | 44334.9375 | 0 | 10.5723 | 39.95
2021-05-18 23:00 | 44334.9583 | 0 | 9.8277 | 39.95
2021-05-18 23:30 | 44334.9792 | 0 | 9.3139 | 39.95
2021-05-19 | 44335 | 0 | 8.97 | 39.95
2021-05-19 00:30 | 44335.0208 | 0 | 8.4369 | 39.95
2021-05-19 01:00 | 44335.0417 | 0 | 8.3058 | 39.95
2021-05-19 01:30 | 44335.0625 | 0 | 8.0197 | 39.95
2021-05-19 02:00 | 44335.0833 | 0 | 7.9493 | 39.95
2021-05-19 02:30 | 44335.1042 | 0 | 7.8846 | 39.95
2021-05-19 03:00 | 44335.125 | 0 | 7.8857 | 39.95
2021-05-19 03:30 | 44335.1458 | 0 | 8.1897 | 39.95
2021-05-19 04:00 | 44335.1667 | 0 | 8.3194 | 39.95
2021-05-19 04:30 | 44335.1875 | 0 | 8.6207 | 39.95
2021-05-19 05:00 | 44335.2083 | 0 | 9.4321 | 39.95
2021-05-19 05:30 | 44335.2292 | 0 | 10.2334 | 39.95
2021-05-19 06:00 | 44335.25 | 0 | 11.4128 | 39.95
2021-05-19 06:30 | 44335.2708 | 0 | 12.4606 | 39.95
2021-05-19 07:00 | 44335.2917 | 0 | 12.6357 | 39.95
2021-05-19 07:30 | 44335.3125 | 0 | 12.7331 | 39.95
2021-05-19 08:00 | 44335.3333 | 0 | 12.7743 | 39.95
2021-05-19 08:30 | 44335.3542 | 0 | 12.7743 | 39.95
2021-05-19 09:00 | 44335.375 | 0 | 12.7743 | 39.95
2021-05-19 09:30 | 44335.3958 | 0 | 12.7743 | 39.95
2021-05-19 10:00 | 44335.4167 | 0 | 12.7743 | 39.95
2021-05-19 10:30 | 44335.4375 | 0 | 12.7743 | 39.95
2021-05-19 11:00 | 44335.4583 | 0 | 12.7743 | 39.95
2021-05-19 11:30 | 44335.4792 | 0 | 12.7743 | 39.95
2021-05-19 12:00 | 44335.5 | 0 | 11.3586 | 39.95
2021-05-19 12:30 | 44335.5208 | 0 | 10.5622 | 39.95
2021-05-19 13:00 | 44335.5417 | 0 | 11.3345 | 39.95
2021-05-19 13:30 | 44335.5625 | 0 | 11.0933 | 39.95
2021-05-19 14:00 | 44335.5833 | 0 | 12.1435 | 39.95
2021-05-19 14:30 | 44335.6042 | 0 | 12.0897 | 39.95
2021-05-19 15:00 | 44335.625 | 0 | 11.6793 | 39.95
2021-05-19 15:30 | 44335.6458 | 0 | 12.0609 | 39.95
2021-05-19 16:00 | 44335.6667 | 0 | 12.5089 | 39.95
2021-05-19 16:30 | 44335.6875 | 0 | 12.9229 | 39.95
2021-05-19 17:00 | 44335.7083 | 0 | 13.7151 | 39.95
2021-05-19 17:30 | 44335.7292 | 0 | 14.3254 | 39.95
2021-05-19 18:00 | 44335.75 | 0 | 14.2757 | 39.95
2021-05-19 18:30 | 44335.7708 | 0 | 14.422 | 39.95
2021-05-19 19:00 | 44335.7917 | 0 | 14.0081 | 39.95
2021-05-19 19:30 | 44335.8125 | 0 | 13.9429 | 39.95
2021-05-19 20:00 | 44335.8333 | 0 | 13.6947 | 39.95
2021-05-19 20:30 | 44335.8542 | 0 | 13.1681 | 39.95
2021-05-19 21:00 | 44335.875 | 0 | 12.6674 | 39.95
2021-05-19 21:30 | 44335.8958 | 0 | 11.8676 | 39.95
2021-05-19 22:00 | 44335.9167 | 0 | 11.3682 | 39.95
2021-05-19 22:30 | 44335.9375 | 0 | 10.3925 | 39.95
2021-05-19 23:00 | 44335.9583 | 0 | 9.7345 | 39.95
2021-05-19 23:30 | 44335.9792 | 0 | 9.2829 | 39.95
2021-05-20 | 44336 | 0 | 8.7628 | 39.95
2021-05-20 00:30 | 44336.0208 | 0 | 8.3231 | 39.95
2021-05-20 01:00 | 44336.0417 | 0 | 8.1575 | 39.95
2021-05-20 01:30 | 44336.0625 | 0 | 8.0749 | 39.95
2021-05-20 02:00 | 44336.0833 | 0 | 7.99 | 39.95
2021-05-20 02:30 | 44336.1042 | 0 | 7.886 | 39.95
2021-05-20 03:00 | 44336.125 | 0 | 7.886 | 39.95
2021-05-20 03:30 | 44336.1458 | 0 | 8.0518 | 39.95
2021-05-20 04:00 | 44336.1667 | 0 | 8.2016 | 39.95
2021-05-20 04:30 | 44336.1875 | 0 | 8.6741 | 39.95
2021-05-20 05:00 | 44336.2083 | 0 | 9.3726 | 39.95
2021-05-20 05:30 | 44336.2292 | 0 | 10.2445 | 39.95
2021-05-20 06:00 | 44336.25 | 0 | 11.2706 | 39.95
2021-05-20 06:30 | 44336.2708 | 0 | 12.3318 | 39.95
2021-05-20 07:00 | 44336.2917 | 0 | 12.8425 | 39.95
2021-05-20 07:30 | 44336.3125 | 0 | 12.4969 | 39.95
2021-05-20 08:00 | 44336.3333 | 0 | 11.9636 | 39.95
2021-05-20 08:30 | 44336.3542 | 0 | 11.1966 | 39.95
2021-05-20 09:00 | 44336.375 | 0 | 10.4234 | 39.95
2021-05-20 09:30 | 44336.3958 | 0 | 9.9319 | 39.95
2021-05-20 10:00 | 44336.4167 | 0 | 9.337 | 39.95
2021-05-20 10:30 | 44336.4375 | 0 | 9.1315 | 39.95
2021-05-20 11:00 | 44336.4583 | 0 | 9.3303 | 39.95
2021-05-20 11:30 | 44336.4792 | 0 | 11.0135 | 39.95
2021-05-20 12:00 | 44336.5 | 0 | 10.4659 | 39.95
2021-05-20 12:30 | 44336.5208 | 0 | 10.2759 | 39.95
2021-05-20 13:00 | 44336.5417 | 0 | 9.3426 | 39.95
2021-05-20 13:30 | 44336.5625 | 0 | 10.3706 | 39.95
2021-05-20 14:00 | 44336.5833 | 0 | 10.2132 | 39.95
2021-05-20 14:30 | 44336.6042 | 0 | 10.8172 | 39.95
2021-05-20 15:00 | 44336.625 | 0 | 11.4002 | 39.95
2021-05-20 15:30 | 44336.6458 | 0 | 11.7325 | 39.95
2021-05-20 16:00 | 44336.6667 | 0 | 12.2463 | 39.95
2021-05-20 16:30 | 44336.6875 | 0 | 12.8119 | 39.95
2021-05-20 17:00 | 44336.7083 | 0 | 13.5262 | 39.95
2021-05-20 17:30 | 44336.7292 | 0 | 13.8128 | 39.95
2021-05-20 18:00 | 44336.75 | 0 | 13.7372 | 39.95
2021-05-20 18:30 | 44336.7708 | 0 | 14.2893 | 39.95
2021-05-20 19:00 | 44336.7917 | 0 | 13.7818 | 39.95
2021-05-20 19:30 | 44336.8125 | 0 | 13.6427 | 39.95
2021-05-20 20:00 | 44336.8333 | 0 | 13.3068 | 39.95
2021-05-20 20:30 | 44336.8542 | 0 | 12.7691 | 39.95
2021-05-20 21:00 | 44336.875 | 0 | 12.2858 | 39.95
2021-05-20 21:30 | 44336.8958 | 0 | 11.7738 | 39.95
2021-05-20 22:00 | 44336.9167 | 0 | 11.2886 | 39.95
2021-05-20 22:30 | 44336.9375 | 0 | 10.367 | 39.95
2021-05-20 23:00 | 44336.9583 | 0 | 9.7107 | 39.95
2021-05-20 23:30 | 44336.9792 | 0 | 9.2631 | 39.95
2021-05-21 | 44337 | 0 | 8.7558 | 39.95
2021-05-21 00:30 | 44337.0208 | 0 | 8.4269 | 39.95
2021-05-21 01:00 | 44337.0417 | 0 | 8.1838 | 39.95
2021-05-21 01:30 | 44337.0625 | 0 | 8.0398 | 39.95
2021-05-21 02:00 | 44337.0833 | 0 | 8.0226 | 39.95
2021-05-21 02:30 | 44337.1042 | 0 | 7.9083 | 39.95
2021-05-21 03:00 | 44337.125 | 0 | 7.9058 | 39.95
2021-05-21 03:30 | 44337.1458 | 0 | 8.0492 | 39.95
2021-05-21 04:00 | 44337.1667 | 0 | 8.3255 | 39.95
2021-05-21 04:30 | 44337.1875 | 0 | 8.6906 | 39.95
2021-05-21 05:00 | 44337.2083 | 0 | 9.4004 | 39.95
2021-05-21 05:30 | 44337.2292 | 0 | 10.0883 | 39.95
2021-05-21 06:00 | 44337.25 | 0 | 11.3068 | 39.95
2021-05-21 06:30 | 44337.2708 | 0 | 12.2983 | 39.95
2021-05-21 07:00 | 44337.2917 | 0 | 12.7615 | 39.95
2021-05-21 07:30 | 44337.3125 | 0 | 12.691 | 39.95
2021-05-21 08:00 | 44337.3333 | 0 | 11.7837 | 39.95
2021-05-21 08:30 | 44337.3542 | 0 | 11.0457 | 39.95
2021-05-21 09:00 | 44337.375 | 0 | 10.422 | 39.95
2021-05-21 09:30 | 44337.3958 | 0 | 10.0496 | 39.95
2021-05-21 10:00 | 44337.4167 | 0 | 9.6371 | 39.95
2021-05-21 10:30 | 44337.4375 | 0 | 9.4914 | 39.95
2021-05-21 11:00 | 44337.4583 | 0 | 9.8329 | 39.95
2021-05-21 11:30 | 44337.4792 | 0 | 10.1961 | 39.95
2021-05-21 12:00 | 44337.5 | 0 | 9.8231 | 39.95
2021-05-21 12:30 | 44337.5208 | 0 | 9.6158 | 39.95
2021-05-21 13:00 | 44337.5417 | 0 | 9.3199 | 39.95
2021-05-21 13:30 | 44337.5625 | 0 | 9.2557 | 39.95
2021-05-21 14:00 | 44337.5833 | 0 | 9.6944 | 39.95
2021-05-21 14:30 | 44337.6042 | 0 | 10.1654 | 39.95
2021-05-21 15:00 | 44337.625 | 0 | 10.6407 | 39.95
2021-05-21 15:30 | 44337.6458 | 0 | 11.3011 | 39.95
2021-05-21 16:00 | 44337.6667 | 0 | 12.0075 | 39.95
2021-05-21 16:30 | 44337.6875 | 0 | 12.5869 | 39.95
2021-05-21 17:00 | 44337.7083 | 0 | 13.1883 | 39.95
2021-05-21 17:30 | 44337.7292 | 0 | 13.6005 | 39.95
2021-05-21 18:00 | 44337.75 | 0 | 13.5092 | 39.95
2021-05-21 18:30 | 44337.7708 | 0 | 13.5806 | 39.95
2021-05-21 19:00 | 44337.7917 | 0 | 13.237 | 39.95
2021-05-21 19:30 | 44337.8125 | 0 | 12.8853 | 39.95
2021-05-21 20:00 | 44337.8333 | 0 | 12.6729 | 39.95
2021-05-21 20:30 | 44337.8542 | 0 | 12.2666 | 39.95
2021-05-21 21:00 | 44337.875 | 0 | 11.8328 | 39.95
2021-05-21 21:30 | 44337.8958 | 0 | 11.5262 | 39.95
2021-05-21 22:00 | 44337.9167 | 0 | 11.1567 | 39.95
2021-05-21 22:30 | 44337.9375 | 0 | 10.4339 | 39.95
2021-05-21 23:00 | 44337.9583 | 0 | 9.8363 | 39.95
2021-05-21 23:30 | 44337.9792 | 0 | 9.3355 | 39.95
2021-05-22 | 44338 | 0 | 8.7676 | 39.95
2021-05-22 00:30 | 44338.0208 | 0 | 8.4075 | 39.95
2021-05-22 01:00 | 44338.0417 | 0 | 7.9977 | 39.95
2021-05-22 01:30 | 44338.0625 | 0 | 7.8439 | 39.95
2021-05-22 02:00 | 44338.0833 | 0 | 7.7835 | 39.95
2021-05-22 02:30 | 44338.1042 | 0 | 7.5785 | 39.95
2021-05-22 03:00 | 44338.125 | 0 | 7.6129 | 39.95
2021-05-22 03:30 | 44338.1458 | 0 | 7.6905 | 39.95
2021-05-22 04:00 | 44338.1667 | 0 | 7.7543 | 39.95
2021-05-22 04:30 | 44338.1875 | 0 | 7.9032 | 39.95
2021-05-22 05:00 | 44338.2083 | 0 | 8.2135 | 39.95
2021-05-22 05:30 | 44338.2292 | 0 | 8.4615 | 39.95
2021-05-22 06:00 | 44338.25 | 0 | 8.9262 | 39.95
2021-05-22 06:30 | 44338.2708 | 0 | 9.2088 | 39.95
2021-05-22 07:00 | 44338.2917 | 0 | 9.5928 | 39.95
2021-05-22 07:30 | 44338.3125 | 0 | 9.3373 | 39.95
2021-05-22 08:00 | 44338.3333 | 0 | 9.2583 | 39.95
2021-05-22 08:30 | 44338.3542 | 0 | 8.7988 | 39.95
2021-05-22 09:00 | 44338.375 | 0 | 8.3944 | 39.95
2021-05-22 09:30 | 44338.3958 | 0 | 8.0557 | 39.95
2021-05-22 10:00 | 44338.4167 | 0 | 7.472 | 39.95
2021-05-22 10:30 | 44338.4375 | 0 | 7.3651 | 39.95
2021-05-22 11:00 | 44338.4583 | 0 | 7.3811 | 39.95
2021-05-22 11:30 | 44338.4792 | 0 | 7.3634 | 39.95
2021-05-22 12:00 | 44338.5 | 0 | 7.3535 | 39.95
2021-05-22 12:30 | 44338.5208 | 0 | 6.5899 | 39.95
2021-05-22 13:00 | 44338.5417 | 0 | 7.1126 | 39.95
2021-05-22 13:30 | 44338.5625 | 0 | 6.9643 | 39.95
2021-05-22 14:00 | 44338.5833 | 0 | 7.4933 | 39.95
2021-05-22 14:30 | 44338.6042 | 0 | 8.5445 | 39.95
2021-05-22 15:00 | 44338.625 | 0 | 9.7501 | 39.95
2021-05-22 15:30 | 44338.6458 | 0 | 9.2804 | 39.95
2021-05-22 16:00 | 44338.6667 | 0 | 9.947 | 39.95
2021-05-22 16:30 | 44338.6875 | 0 | 10.7031 | 39.95
2021-05-22 17:00 | 44338.7083 | 0 | 11.1707 | 39.95
2021-05-22 17:30 | 44338.7292 | 0 | 11.5912 | 39.95
2021-05-22 18:00 | 44338.75 | 0 | 11.4644 | 39.95
2021-05-22 18:30 | 44338.7708 | 0 | 11.4263 | 39.95
2021-05-22 19:00 | 44338.7917 | 0 | 11.0766 | 39.95
2021-05-22 19:30 | 44338.8125 | 0 | 11.0169 | 39.95
2021-05-22 20:00 | 44338.8333 | 0 | 10.8808 | 39.95
2021-05-22 20:30 | 44338.8542 | 0 | 10.2965 | 39.95
2021-05-22 21:00 | 44338.875 | 0 | 9.9471 | 39.95
2021-05-22 21:30 | 44338.8958 | 0 | 9.5583 | 39.95
2021-05-22 22:00 | 44338.9167 | 0 | 9.3201 | 39.95
2021-05-22 22:30 | 44338.9375 | 0 | 8.6686 | 39.95
2021-05-22 23:00 | 44338.9583 | 0 | 8.306 | 39.95
2021-05-22 23:30 | 44338.9792 | 0 | 8.0002 | 39.95
2021-05-23 | 44339 | 0 | 7.7712 | 39.95
2021-05-23 00:30 | 44339.0208 | 0 | 7.4326 | 39.95
2021-05-23 01:00 | 44339.0417 | 0 | 7.1958 | 39.95
2021-05-23 01:30 | 44339.0625 | 0 | 6.9557 | 39.95
2021-05-23 02:00 | 44339.0833 | 0 | 6.9403 | 39.95
2021-05-23 02:30 | 44339.1042 | 0 | 6.8166 | 39.95
2021-05-23 03:00 | 44339.125 | 0 | 6.8536 | 39.95
2021-05-23 03:30 | 44339.1458 | 0 | 6.8982 | 39.95
2021-05-23 04:00 | 44339.1667 | 0 | 6.8364 | 39.95
2021-05-23 04:30 | 44339.1875 | 0 | 6.7496 | 39.95
2021-05-23 05:00 | 44339.2083 | 0 | 7.0219 | 39.95
2021-05-23 05:30 | 44339.2292 | 0 | 7.0966 | 39.95
2021-05-23 06:00 | 44339.25 | 0 | 7.4866 | 39.95
2021-05-23 06:30 | 44339.2708 | 0 | 7.8263 | 39.95
2021-05-23 07:00 | 44339.2917 | 0 | 7.9453 | 39.95
2021-05-23 07:30 | 44339.3125 | 0 | 7.878 | 39.95
2021-05-23 08:00 | 44339.3333 | 0 | 7.8147 | 39.95
2021-05-23 08:30 | 44339.3542 | 0 | 7.544 | 39.95
2021-05-23 09:00 | 44339.375 | 0 | 7.3277 | 39.95
2021-05-23 09:30 | 44339.3958 | 0 | 6.8737 | 39.95
2021-05-23 10:00 | 44339.4167 | 0 | 6.5709 | 39.95
2021-05-23 10:30 | 44339.4375 | 0 | 6.8592 | 39.95
2021-05-23 11:00 | 44339.4583 | 0 | 6.8306 | 39.95
2021-05-23 11:30 | 44339.4792 | 0 | 6.3496 | 39.95
2021-05-23 12:00 | 44339.5 | 0 | 7.2008 | 39.95
2021-05-23 12:30 | 44339.5208 | 0 | 6.4979 | 39.95
2021-05-23 13:00 | 44339.5417 | 0 | 6.4893 | 39.95
2021-05-23 13:30 | 44339.5625 | 0 | 7.993 | 39.95
2021-05-23 14:00 | 44339.5833 | 0 | 8.1845 | 39.95
2021-05-23 14:30 | 44339.6042 | 0 | 8.2407 | 39.95
2021-05-23 15:00 | 44339.625 | 0 | 8.6445 | 39.95
2021-05-23 15:30 | 44339.6458 | 0 | 9.7588 | 39.95
2021-05-23 16:00 | 44339.6667 | 0 | 10.1259 | 39.95
2021-05-23 16:30 | 44339.6875 | 0 | 10.8642 | 39.95
2021-05-23 17:00 | 44339.7083 | 0 | 11.586 | 39.95
2021-05-23 17:30 | 44339.7292 | 0 | 12.1085 | 39.95
2021-05-23 18:00 | 44339.75 | 0 | 12.1739 | 39.95
2021-05-23 18:30 | 44339.7708 | 0 | 12.1318 | 39.95
2021-05-23 19:00 | 44339.7917 | 0 | 11.8306 | 39.95
2021-05-23 19:30 | 44339.8125 | 0 | 11.4418 | 39.95
2021-05-23 20:00 | 44339.8333 | 0 | 11.0236 | 39.95
2021-05-23 20:30 | 44339.8542 | 0 | 10.4869 | 39.95
2021-05-23 21:00 | 44339.875 | 0 | 10.0169 | 39.95
2021-05-23 21:30 | 44339.8958 | 0 | 9.7117 | 39.95
2021-05-23 22:00 | 44339.9167 | 0 | 9.2701 | 39.95
2021-05-23 22:30 | 44339.9375 | 0 | 8.6058 | 39.95
2021-05-23 23:00 | 44339.9583 | 0 | 8.1905 | 39.95
2021-05-23 23:30 | 44339.9792 | 0 | 7.8582 | 39.95
2021-05-24 | 44340 | 0 | 7.3282 | 39.95
2021-05-24 00:30 | 44340.0208 | 0 | 7.2484 | 39.95
2021-05-24 01:00 | 44340.0417 | 0 | 7.1613 | 39.95
2021-05-24 01:30 | 44340.0625 | 0 | 6.948 | 39.95
2021-05-24 02:00 | 44340.0833 | 0 | 7.1668 | 39.95
2021-05-24 02:30 | 44340.1042 | 0 | 7.0863 | 39.95
2021-05-24 03:00 | 44340.125 | 0 | 7.1044 | 39.95
2021-05-24 03:30 | 44340.1458 | 0 | 7.2957 | 39.95
2021-05-24 04:00 | 44340.1667 | 0 | 7.6437 | 39.95
2021-05-24 04:30 | 44340.1875 | 0 | 8.1188 | 39.95
2021-05-24 05:00 | 44340.2083 | 0 | 8.8365 | 39.95
2021-05-24 05:30 | 44340.2292 | 0 | 9.7061 | 39.95
2021-05-24 06:00 | 44340.25 | 0 | 10.9759 | 39.95
2021-05-24 06:30 | 44340.2708 | 0 | 11.9486 | 39.95
2021-05-24 07:00 | 44340.2917 | 0 | 12.1988 | 39.95
2021-05-24 07:30 | 44340.3125 | 0 | 12.1764 | 39.95
2021-05-24 08:00 | 44340.3333 | 0 | 11.5878 | 39.95
2021-05-24 08:30 | 44340.3542 | 0 | 10.7809 | 39.95
2021-05-24 09:00 | 44340.375 | 0 | 10.318 | 39.95
2021-05-24 09:30 | 44340.3958 | 0 | 9.8309 | 39.95
2021-05-24 10:00 | 44340.4167 | 0 | 9.7062 | 39.95
2021-05-24 10:30 | 44340.4375 | 0 | 9.4767 | 39.95
2021-05-24 11:00 | 44340.4583 | 0 | 9.3941 | 39.95
2021-05-24 11:30 | 44340.4792 | 0 | 10.5927 | 39.95
2021-05-24 12:00 | 44340.5 | 0 | 11.4053 | 39.95
2021-05-24 12:30 | 44340.5208 | 0 | 10.9156 | 39.95
2021-05-24 13:00 | 44340.5417 | 0 | 10.1969 | 39.95
2021-05-24 13:30 | 44340.5625 | 0 | 11.1548 | 39.95
2021-05-24 14:00 | 44340.5833 | 0 | 10.3202 | 39.95
2021-05-24 14:30 | 44340.6042 | 0 | 11.1969 | 39.95
2021-05-24 15:00 | 44340.625 | 0 | 11.2006 | 39.95
2021-05-24 15:30 | 44340.6458 | 0 | 11.9456 | 39.95
2021-05-24 16:00 | 44340.6667 | 0 | 12.1768 | 39.95
2021-05-24 16:30 | 44340.6875 | 0 | 12.8189 | 39.95
2021-05-24 17:00 | 44340.7083 | 0 | 13.426 | 39.95
2021-05-24 17:30 | 44340.7292 | 0 | 14.2268 | 39.95
2021-05-24 18:00 | 44340.75 | 0 | 14.1666 | 39.95
2021-05-24 18:30 | 44340.7708 | 0 | 13.9989 | 39.95
2021-05-24 19:00 | 44340.7917 | 0 | 13.7941 | 39.95
2021-05-24 19:30 | 44340.8125 | 0 | 13.5585 | 39.95
2021-05-24 20:00 | 44340.8333 | 0 | 13.2752 | 39.95
2021-05-24 20:30 | 44340.8542 | 0 | 12.7021 | 39.95
2021-05-24 21:00 | 44340.875 | 0 | 12.0886 | 39.95
2021-05-24 21:30 | 44340.8958 | 0 | 11.6198 | 39.95
2021-05-24 22:00 | 44340.9167 | 0 | 10.8494 | 39.95
2021-05-24 22:30 | 44340.9375 | 0 | 9.9351 | 39.95
2021-05-24 23:00 | 44340.9583 | 0 | 9.4373 | 39.95
2021-05-24 23:30 | 44340.9792 | 0 | 9.136 | 39.95
2021-05-25 | 44341 | 0 | 8.7049 | 39.95
2021-05-25 00:30 | 44341.0208 | 0 | 8.3041 | 39.95
2021-05-25 01:00 | 44341.0417 | 0 | 8.1145 | 39.95
2021-05-25 01:30 | 44341.0625 | 0 | 7.821 | 39.95
2021-05-25 02:00 | 44341.0833 | 0 | 7.8147 | 39.95
2021-05-25 02:30 | 44341.1042 | 0 | 7.7345 | 39.95
2021-05-25 03:00 | 44341.125 | 0 | 7.7239 | 39.95
2021-05-25 03:30 | 44341.1458 | 0 | 7.9187 | 39.95
2021-05-25 04:00 | 44341.1667 | 0 | 7.9822 | 39.95
2021-05-25 04:30 | 44341.1875 | 0 | 8.5651 | 39.95
2021-05-25 05:00 | 44341.2083 | 0 | 9.1807 | 39.95
2021-05-25 05:30 | 44341.2292 | 0 | 10.1459 | 39.95
2021-05-25 06:00 | 44341.25 | 0 | 11.082 | 39.95
2021-05-25 06:30 | 44341.2708 | 0 | 12.1252 | 39.95
2021-05-25 07:00 | 44341.2917 | 0 | 12.7708 | 39.95
2021-05-25 07:30 | 44341.3125 | 0 | 12.2245 | 39.95
2021-05-25 08:00 | 44341.3333 | 0 | 11.5717 | 39.95
2021-05-25 08:30 | 44341.3542 | 0 | 10.7053 | 39.95
2021-05-25 09:00 | 44341.375 | 0 | 10.2083 | 39.95
2021-05-25 09:30 | 44341.3958 | 0 | 9.7118 | 39.95
2021-05-25 10:00 | 44341.4167 | 0 | 9.4295 | 39.95
2021-05-25 10:30 | 44341.4375 | 0 | 9.4716 | 39.95
2021-05-25 11:00 | 44341.4583 | 0 | 9.2477 | 39.95
2021-05-25 11:30 | 44341.4792 | 0 | 9.1959 | 39.95
2021-05-25 12:00 | 44341.5 | 0 | 9.5063 | 39.95
2021-05-25 12:30 | 44341.5208 | 0 | 9.6506 | 39.95
2021-05-25 13:00 | 44341.5417 | 0 | 10.2368 | 39.95
2021-05-25 13:30 | 44341.5625 | 0 | 9.9978 | 39.95
2021-05-25 14:00 | 44341.5833 | 0 | 11.3084 | 39.95
2021-05-25 14:30 | 44341.6042 | 0 | 11.8451 | 39.95
2021-05-25 15:00 | 44341.625 | 0 | 12.3477 | 39.95
2021-05-25 15:30 | 44341.6458 | 0 | 12.6102 | 39.95
2021-05-25 16:00 | 44341.6667 | 0 | 12.653 | 39.95
2021-05-25 16:30 | 44341.6875 | 0 | 13.0575 | 39.95
2021-05-25 17:00 | 44341.7083 | 0 | 13.5742 | 39.95
2021-05-25 17:30 | 44341.7292 | 0 | 14.0778 | 39.95
2021-05-25 18:00 | 44341.75 | 0 | 14.097 | 39.95
2021-05-25 18:30 | 44341.7708 | 0 | 13.9641 | 39.95
2021-05-25 19:00 | 44341.7917 | 0 | 13.553 | 39.95
2021-05-25 19:30 | 44341.8125 | 0 | 13.0205 | 39.95
2021-05-25 20:00 | 44341.8333 | 0 | 12.611 | 39.95
2021-05-25 20:30 | 44341.8542 | 0 | 12.2482 | 39.95
2021-05-25 21:00 | 44341.875 | 0 | 14.248 | 39.95
2021-05-25 21:30 | 44341.8958 | 0 | 12.9162 | 39.95
2021-05-25 22:00 | 44341.9167 | 0 | 11.5342 | 39.95
2021-05-25 22:30 | 44341.9375 | 0 | 10.3921 | 39.95
2021-05-25 23:00 | 44341.9583 | 0 | 9.6797 | 39.95
2021-05-25 23:30 | 44341.9792 | 0 | 9.1012 | 39.95
2021-05-26 | 44342 | 0 | 8.627 | 39.95
2021-05-26 00:30 | 44342.0208 | 0 | 8.31 | 39.95
2021-05-26 01:00 | 44342.0417 | 0 | 8.0921 | 39.95
2021-05-26 01:30 | 44342.0625 | 0 | 7.8501 | 39.95
2021-05-26 02:00 | 44342.0833 | 0 | 7.8817 | 39.95
2021-05-26 02:30 | 44342.1042 | 0 | 7.8336 | 39.95
2021-05-26 03:00 | 44342.125 | 0 | 7.9058 | 39.95
2021-05-26 03:30 | 44342.1458 | 0 | 8.0767 | 39.95
2021-05-26 04:00 | 44342.1667 | 0 | 8.2899 | 39.95
2021-05-26 04:30 | 44342.1875 | 0 | 8.7684 | 39.95
2021-05-26 05:00 | 44342.2083 | 0 | 9.4353 | 39.95
2021-05-26 05:30 | 44342.2292 | 0 | 10.0792 | 39.95
2021-05-26 06:00 | 44342.25 | 0 | 11.2852 | 39.95
2021-05-26 06:30 | 44342.2708 | 0 | 12.2833 | 39.95
2021-05-26 07:00 | 44342.2917 | 0 | 12.7442 | 39.95
2021-05-26 07:30 | 44342.3125 | 0 | 12.5987 | 39.95
2021-05-26 08:00 | 44342.3333 | 0 | 11.9109 | 39.95
2021-05-26 08:30 | 44342.3542 | 0 | 11.0349 | 39.95
2021-05-26 09:00 | 44342.375 | 0 | 10.3999 | 39.95
2021-05-26 09:30 | 44342.3958 | 0 | 9.8673 | 39.95
2021-05-26 10:00 | 44342.4167 | 0 | 9.5214 | 39.95
2021-05-26 10:30 | 44342.4375 | 0 | 9.3574 | 39.95
2021-05-26 11:00 | 44342.4583 | 0 | 9.3336 | 39.95
2021-05-26 11:30 | 44342.4792 | 0 | 9.2828 | 39.95
2021-05-26 12:00 | 44342.5 | 0 | 9.5137 | 39.95
2021-05-26 12:30 | 44342.5208 | 0 | 9.8063 | 39.95
2021-05-26 13:00 | 44342.5417 | 0 | 9.8733 | 39.95
2021-05-26 13:30 | 44342.5625 | 0 | 10.2449 | 39.95
2021-05-26 14:00 | 44342.5833 | 0 | 10.6699 | 39.95
2021-05-26 14:30 | 44342.6042 | 0 | 10.9301 | 39.95
2021-05-26 15:00 | 44342.625 | 0 | 11.4246 | 39.95
2021-05-26 15:30 | 44342.6458 | 0 | 12.0262 | 39.95
2021-05-26 16:00 | 44342.6667 | 0 | 12.4597 | 39.95
2021-05-26 16:30 | 44342.6875 | 0 | 12.6377 | 39.95
2021-05-26 17:00 | 44342.7083 | 0 | 13.3305 | 39.95
2021-05-26 17:30 | 44342.7292 | 0 | 14.0355 | 39.95
2021-05-26 18:00 | 44342.75 | 0 | 13.935 | 39.95
2021-05-26 18:30 | 44342.7708 | 0 | 13.977 | 39.95
2021-05-26 19:00 | 44342.7917 | 0 | 13.3171 | 39.95
2021-05-26 19:30 | 44342.8125 | 0 | 13.0325 | 39.95
2021-05-26 20:00 | 44342.8333 | 0 | 13.0837 | 39.95
2021-05-26 20:30 | 44342.8542 | 0 | 13.3768 | 39.95
2021-05-26 21:00 | 44342.875 | 0 | 12.3369 | 39.95
2021-05-26 21:30 | 44342.8958 | 0 | 11.9307 | 39.95
2021-05-26 22:00 | 44342.9167 | 0 | 11.1871 | 39.95
2021-05-26 22:30 | 44342.9375 | 0 | 10.323 | 39.95
2021-05-26 23:00 | 44342.9583 | 0 | 9.7267 | 39.95
2021-05-26 23:30 | 44342.9792 | 0 | 9.4238 | 39.95
2021-05-27 | 44343 | 0 | 8.8352 | 39.95
2021-05-27 00:30 | 44343.0208 | 0 | 8.5164 | 39.95
2021-05-27 01:00 | 44343.0417 | 0 | 8.1932 | 39.95
2021-05-27 01:30 | 44343.0625 | 0 | 8.1153 | 39.95
2021-05-27 02:00 | 44343.0833 | 0 | 8.0123 | 39.95
2021-05-27 02:30 | 44343.1042 | 0 | 7.9479 | 39.95
2021-05-27 03:00 | 44343.125 | 0 | 8.0123 | 39.95
2021-05-27 03:30 | 44343.1458 | 0 | 8.2811 | 39.95
2021-05-27 04:00 | 44343.1667 | 0 | 8.5031 | 39.95
2021-05-27 04:30 | 44343.1875 | 0 | 8.7301 | 39.95
2021-05-27 05:00 | 44343.2083 | 0 | 9.3947 | 39.95
2021-05-27 05:30 | 44343.2292 | 0 | 10.142 | 39.95
2021-05-27 06:00 | 44343.25 | 0 | 11.348 | 39.95
2021-05-27 06:30 | 44343.2708 | 0 | 13.006 | 39.95
2021-05-27 07:00 | 44343.2917 | 0 | 13.3459 | 39.95
2021-05-27 07:30 | 44343.3125 | 0 | 13.4568 | 39.95
2021-05-27 08:00 | 44343.3333 | 0 | 12.6064 | 39.95
2021-05-27 08:30 | 44343.3542 | 0 | 11.7298 | 39.95
2021-05-27 09:00 | 44343.375 | 0 | 11.7426 | 39.95
2021-05-27 09:30 | 44343.3958 | 0 | 11.4259 | 39.95
2021-05-27 10:00 | 44343.4167 | 0 | 11.3917 | 39.95
2021-05-27 10:30 | 44343.4375 | 0 | 10.9229 | 39.95
2021-05-27 11:00 | 44343.4583 | 0 | 10.3119 | 39.95
2021-05-27 11:30 | 44343.4792 | 0 | 9.7654 | 39.95
2021-05-27 12:00 | 44343.5 | 0 | 10.2183 | 39.95
2021-05-27 12:30 | 44343.5208 | 0 | 10.9616 | 39.95
2021-05-27 13:00 | 44343.5417 | 0 | 10.5446 | 39.95
2021-05-27 13:30 | 44343.5625 | 0 | 10.6815 | 39.95
2021-05-27 14:00 | 44343.5833 | 0 | 10.2779 | 39.95
2021-05-27 14:30 | 44343.6042 | 0 | 10.9875 | 39.95
2021-05-27 15:00 | 44343.625 | 0 | 11.4867 | 39.95
2021-05-27 15:30 | 44343.6458 | 0 | 12.3069 | 39.95
2021-05-27 16:00 | 44343.6667 | 0 | 12.7666 | 39.95
2021-05-27 16:30 | 44343.6875 | 0 | 13.0532 | 39.95
2021-05-27 17:00 | 44343.7083 | 0 | 13.5514 | 39.95
2021-05-27 17:30 | 44343.7292 | 0 | 13.9706 | 39.95
2021-05-27 18:00 | 44343.75 | 0 | 13.6349 | 39.95
2021-05-27 18:30 | 44343.7708 | 0 | 13.5487 | 39.95
2021-05-27 19:00 | 44343.7917 | 0 | 13.0127 | 39.95
2021-05-27 19:30 | 44343.8125 | 0 | 13.0514 | 39.95
2021-05-27 20:00 | 44343.8333 | 0 | 13.0231 | 39.95
2021-05-27 20:30 | 44343.8542 | 0 | 12.9944 | 39.95
2021-05-27 21:00 | 44343.875 | 0 | 12.2276 | 39.95
2021-05-27 21:30 | 44343.8958 | 0 | 12.1481 | 39.95
2021-05-27 22:00 | 44343.9167 | 0 | 11.0077 | 39.95
2021-05-27 22:30 | 44343.9375 | 0 | 10.1242 | 39.95
2021-05-27 23:00 | 44343.9583 | 0 | 9.5884 | 39.95
2021-05-27 23:30 | 44343.9792 | 0 | 9.3648 | 39.95
2021-05-28 | 44344 | 0 | 8.9099 | 39.95
2021-05-28 00:30 | 44344.0208 | 0 | 8.4723 | 39.95
2021-05-28 01:00 | 44344.0417 | 0 | 8.1955 | 39.95
2021-05-28 01:30 | 44344.0625 | 0 | 8.0054 | 39.95
2021-05-28 02:00 | 44344.0833 | 0 | 8.0848 | 39.95
2021-05-28 02:30 | 44344.1042 | 0 | 8.1359 | 39.95
2021-05-28 03:00 | 44344.125 | 0 | 7.9135 | 39.95
2021-05-28 03:30 | 44344.1458 | 0 | 8.0372 | 39.95
2021-05-28 04:00 | 44344.1667 | 0 | 8.3402 | 39.95
2021-05-28 04:30 | 44344.1875 | 0 | 8.6704 | 39.95
2021-05-28 05:00 | 44344.2083 | 0 | 9.436 | 39.95
2021-05-28 05:30 | 44344.2292 | 0 | 10.2446 | 39.95
2021-05-28 06:00 | 44344.25 | 0 | 11.4882 | 39.95
2021-05-28 06:30 | 44344.2708 | 0 | 12.4934 | 39.95
2021-05-28 07:00 | 44344.2917 | 0 | 13.0869 | 39.95
2021-05-28 07:30 | 44344.3125 | 0 | 12.7178 | 39.95
2021-05-28 08:00 | 44344.3333 | 0 | 12.335 | 39.95
2021-05-28 08:30 | 44344.3542 | 0 | 11.3863 | 39.95
2021-05-28 09:00 | 44344.375 | 0 | 10.5631 | 39.95
2021-05-28 09:30 | 44344.3958 | 0 | 9.9728 | 39.95
2021-05-28 10:00 | 44344.4167 | 0 | 9.4913 | 39.95
2021-05-28 10:30 | 44344.4375 | 0 | 9.3434 | 39.95
2021-05-28 11:00 | 44344.4583 | 0 | 8.958 | 39.95
2021-05-28 11:30 | 44344.4792 | 0 | 8.5852 | 39.95
2021-05-28 12:00 | 44344.5 | 0 | 8.6971 | 39.95
2021-05-28 12:30 | 44344.5208 | 0 | 8.5834 | 39.95
2021-05-28 13:00 | 44344.5417 | 0 | 8.613 | 39.95
2021-05-28 13:30 | 44344.5625 | 0 | 8.9804 | 39.95
2021-05-28 14:00 | 44344.5833 | 0 | 9.469 | 39.95
2021-05-28 14:30 | 44344.6042 | 0 | 9.9966 | 39.95
2021-05-28 15:00 | 44344.625 | 0 | 10.6462 | 39.95
2021-05-28 15:30 | 44344.6458 | 0 | 11.3809 | 39.95
2021-05-28 16:00 | 44344.6667 | 0 | 11.8988 | 39.95
2021-05-28 16:30 | 44344.6875 | 0 | 12.4279 | 39.95
2021-05-28 17:00 | 44344.7083 | 0 | 13.0897 | 39.95
2021-05-28 17:30 | 44344.7292 | 0 | 13.6741 | 39.95
2021-05-28 18:00 | 44344.75 | 0 | 13.5413 | 39.95
2021-05-28 18:30 | 44344.7708 | 0 | 13.5113 | 39.95
2021-05-28 19:00 | 44344.7917 | 0 | 13.4366 | 39.95
2021-05-28 19:30 | 44344.8125 | 0 | 13.2132 | 39.95
2021-05-28 20:00 | 44344.8333 | 0 | 13.1338 | 39.95
2021-05-28 20:30 | 44344.8542 | 0 | 12.6685 | 39.95
2021-05-28 21:00 | 44344.875 | 0 | 12.2005 | 39.95
2021-05-28 21:30 | 44344.8958 | 0 | 11.6877 | 39.95
2021-05-28 22:00 | 44344.9167 | 0 | 11.2579 | 39.95
2021-05-28 22:30 | 44344.9375 | 0 | 10.5106 | 39.95
2021-05-28 23:00 | 44344.9583 | 0 | 9.8184 | 39.95
2021-05-28 23:30 | 44344.9792 | 0 | 9.3797 | 39.95
2021-05-29 | 44345 | 0 | 8.8383 | 39.95
2021-05-29 00:30 | 44345.0208 | 0 | 8.3779 | 39.95
2021-05-29 01:00 | 44345.0417 | 0 | 8.2327 | 39.95
2021-05-29 01:30 | 44345.0625 | 0 | 8.0028 | 39.95
2021-05-29 02:00 | 44345.0833 | 0 | 7.8556 | 39.95
2021-05-29 02:30 | 44345.1042 | 0 | 7.7569 | 39.95
2021-05-29 03:00 | 44345.125 | 0 | 7.7477 | 39.95
2021-05-29 03:30 | 44345.1458 | 0 | 7.7661 | 39.95
2021-05-29 04:00 | 44345.1667 | 0 | 7.8293 | 39.95
2021-05-29 04:30 | 44345.1875 | 0 | 8.0123 | 39.95
2021-05-29 05:00 | 44345.2083 | 0 | 8.276 | 39.95
2021-05-29 05:30 | 44345.2292 | 0 | 8.5878 | 39.95
2021-05-29 06:00 | 44345.25 | 0 | 9.0005 | 39.95
2021-05-29 06:30 | 44345.2708 | 0 | 9.635 | 39.95
2021-05-29 07:00 | 44345.2917 | 0 | 10.4013 | 39.95
2021-05-29 07:30 | 44345.3125 | 0 | 10.6647 | 39.95
2021-05-29 08:00 | 44345.3333 | 0 | 10.1985 | 39.95
2021-05-29 08:30 | 44345.3542 | 0 | 10.1136 | 39.95
2021-05-29 09:00 | 44345.375 | 0 | 10.111 | 39.95
2021-05-29 09:30 | 44345.3958 | 0 | 8.9199 | 39.95
2021-05-29 10:00 | 44345.4167 | 0 | 8.5442 | 39.95
2021-05-29 10:30 | 44345.4375 | 0 | 7.7986 | 39.95
2021-05-29 11:00 | 44345.4583 | 0 | 7.0211 | 39.95
2021-05-29 11:30 | 44345.4792 | 0 | 6.7139 | 39.95
2021-05-29 12:00 | 44345.5 | 0 | 6.4988 | 39.95
2021-05-29 12:30 | 44345.5208 | 0 | 6.4885 | 39.95
2021-05-29 13:00 | 44345.5417 | 0 | 6.6666 | 39.95
2021-05-29 13:30 | 44345.5625 | 0 | 8.1085 | 39.95
2021-05-29 14:00 | 44345.5833 | 0 | 8.4325 | 39.95
2021-05-29 14:30 | 44345.6042 | 0 | 8.7986 | 39.95
2021-05-29 15:00 | 44345.625 | 0 | 9.387 | 39.95
2021-05-29 15:30 | 44345.6458 | 0 | 9.6005 | 39.95
2021-05-29 16:00 | 44345.6667 | 0 | 10.1878 | 39.95
2021-05-29 16:30 | 44345.6875 | 0 | 10.862 | 39.95
2021-05-29 17:00 | 44345.7083 | 0 | 11.6365 | 39.95
2021-05-29 17:30 | 44345.7292 | 0 | 12.0823 | 39.95
2021-05-29 18:00 | 44345.75 | 0 | 12.1069 | 39.95
2021-05-29 18:30 | 44345.7708 | 0 | 12.1318 | 39.95
2021-05-29 19:00 | 44345.7917 | 0 | 11.9486 | 39.95
2021-05-29 19:30 | 44345.8125 | 0 | 11.8927 | 39.95
2021-05-29 20:00 | 44345.8333 | 0 | 11.6152 | 39.95
2021-05-29 20:30 | 44345.8542 | 0 | 11.1049 | 39.95
2021-05-29 21:00 | 44345.875 | 0 | 10.7345 | 39.95
2021-05-29 21:30 | 44345.8958 | 0 | 10.444 | 39.95
2021-05-29 22:00 | 44345.9167 | 0 | 10.0652 | 39.95
2021-05-29 22:30 | 44345.9375 | 0 | 9.4317 | 39.95
2021-05-29 23:00 | 44345.9583 | 0 | 8.7594 | 39.95
2021-05-29 23:30 | 44345.9792 | 0 | 8.2516 | 39.95
2021-05-30 | 44346 | 0 | 7.9856 | 39.95
2021-05-30 00:30 | 44346.0208 | 0 | 7.5988 | 39.95
2021-05-30 01:00 | 44346.0417 | 0 | 7.3577 | 39.95
2021-05-30 01:30 | 44346.0625 | 0 | 7.2326 | 39.95
2021-05-30 02:00 | 44346.0833 | 0 | 7.1688 | 39.95
2021-05-30 02:30 | 44346.1042 | 0 | 7.015 | 39.95
2021-05-30 03:00 | 44346.125 | 0 | 7.0099 | 39.95
2021-05-30 03:30 | 44346.1458 | 0 | 7.1241 | 39.95
2021-05-30 04:00 | 44346.1667 | 0 | 7.082 | 39.95
2021-05-30 04:30 | 44346.1875 | 0 | 6.9927 | 39.95
2021-05-30 05:00 | 44346.2083 | 0 | 7.1983 | 39.95
2021-05-30 05:30 | 44346.2292 | 0 | 7.4866 | 39.95
2021-05-30 06:00 | 44346.25 | 0 | 7.9055 | 39.95
2021-05-30 06:30 | 44346.2708 | 0 | 8.3502 | 39.95
2021-05-30 07:00 | 44346.2917 | 0 | 9.0382 | 39.95
2021-05-30 07:30 | 44346.3125 | 0 | 8.7992 | 39.95
2021-05-30 08:00 | 44346.3333 | 0 | 8.5757 | 39.95
2021-05-30 08:30 | 44346.3542 | 0 | 8.3963 | 39.95
2021-05-30 09:00 | 44346.375 | 0 | 8.0793 | 39.95
2021-05-30 09:30 | 44346.3958 | 0 | 8.012 | 39.95
2021-05-30 10:00 | 44346.4167 | 0 | 7.3824 | 39.95
2021-05-30 10:30 | 44346.4375 | 0 | 6.7425 | 39.95
2021-05-30 11:00 | 44346.4583 | 0 | 6.6633 | 39.95
2021-05-30 11:30 | 44346.4792 | 0 | 6.7972 | 39.95
2021-05-30 12:00 | 44346.5 | 0 | 6.5773 | 39.95
2021-05-30 12:30 | 44346.5208 | 0 | 8.1969 | 39.95
2021-05-30 13:00 | 44346.5417 | 0 | 7.9648 | 39.95
2021-05-30 13:30 | 44346.5625 | 0 | 7.7696 | 39.95
2021-05-30 14:00 | 44346.5833 | 0 | 7.9559 | 39.95
2021-05-30 14:30 | 44346.6042 | 0 | 9.0494 | 39.95
2021-05-30 15:00 | 44346.625 | 0 | 8.4535 | 39.95
2021-05-30 15:30 | 44346.6458 | 0 | 9.9563 | 39.95
2021-05-30 16:00 | 44346.6667 | 0 | 10.4002 | 39.95
2021-05-30 16:30 | 44346.6875 | 0 | 10.9348 | 39.95
2021-05-30 17:00 | 44346.7083 | 0 | 12.1088 | 39.95
2021-05-30 17:30 | 44346.7292 | 0 | 12.5963 | 39.95
2021-05-30 18:00 | 44346.75 | 0 | 12.6033 | 39.95
2021-05-30 18:30 | 44346.7708 | 0 | 12.3447 | 39.95
2021-05-30 19:00 | 44346.7917 | 0 | 11.9727 | 39.95
2021-05-30 19:30 | 44346.8125 | 0 | 12.055 | 39.95
2021-05-30 20:00 | 44346.8333 | 0 | 12.1167 | 39.95
2021-05-30 20:30 | 44346.8542 | 0 | 11.7721 | 39.95
2021-05-30 21:00 | 44346.875 | 0 | 11.2292 | 39.95
2021-05-30 21:30 | 44346.8958 | 0 | 10.7142 | 39.95
2021-05-30 22:00 | 44346.9167 | 0 | 10.1816 | 39.95
2021-05-30 22:30 | 44346.9375 | 0 | 9.3547 | 39.95
2021-05-30 23:00 | 44346.9583 | 0 | 8.8062 | 39.95
2021-05-30 23:30 | 44346.9792 | 0 | 8.405 | 39.95
2021-05-31 | 44347 | 0 | 8.1491 | 39.95
2021-05-31 00:30 | 44347.0208 | 0 | 7.916 | 39.95
2021-05-31 01:00 | 44347.0417 | 0 | 7.7699 | 39.95
2021-05-31 01:30 | 44347.0625 | 0 | 7.6721 | 39.95
2021-05-31 02:00 | 44347.0833 | 0 | 7.7145 | 39.95
2021-05-31 02:30 | 44347.1042 | 0 | 7.5759 | 39.95
2021-05-31 03:00 | 44347.125 | 0 | 7.6103 | 39.95
2021-05-31 03:30 | 44347.1458 | 0 | 8.0647 | 39.95
2021-05-31 04:00 | 44347.1667 | 0 | 8.268 | 39.95
2021-05-31 04:30 | 44347.1875 | 0 | 8.7959 | 39.95
2021-05-31 05:00 | 44347.2083 | 0 | 9.5847 | 39.95
2021-05-31 05:30 | 44347.2292 | 0 | 10.078 | 39.95
2021-05-31 06:00 | 44347.25 | 0 | 11.4497 | 39.95
2021-05-31 06:30 | 44347.2708 | 0 | 12.5252 | 39.95
2021-05-31 07:00 | 44347.2917 | 0 | 12.9957 | 39.95
2021-05-31 07:30 | 44347.3125 | 0 | 13.1711 | 39.95
2021-05-31 08:00 | 44347.3333 | 0 | 13.092 | 39.95
2021-05-31 08:30 | 44347.3542 | 0 | 12.1559 | 39.95
2021-05-31 09:00 | 44347.375 | 0 | 11.3066 | 39.95
2021-05-31 09:30 | 44347.3958 | 0 | 10.5727 | 39.95
2021-05-31 10:00 | 44347.4167 | 0 | 9.8246 | 39.95
2021-05-31 10:30 | 44347.4375 | 0 | 9.7245 | 39.95
2021-05-31 11:00 | 44347.4583 | 0 | 9.447 | 39.95
2021-05-31 11:30 | 44347.4792 | 0 | 9.8239 | 39.95
2021-05-31 12:00 | 44347.5 | 0 | 10.9873 | 39.95
2021-05-31 12:30 | 44347.5208 | 0 | 11.5625 | 39.95
2021-05-31 13:00 | 44347.5417 | 0 | 11.344 | 39.95
2021-05-31 13:30 | 44347.5625 | 0 | 10.4495 | 39.95
2021-05-31 14:00 | 44347.5833 | 0 | 11.7771 | 39.95
2021-05-31 14:30 | 44347.6042 | 0 | 11.3912 | 39.95
2021-05-31 15:00 | 44347.625 | 0 | 11.834 | 39.95
2021-05-31 15:30 | 44347.6458 | 0 | 11.46 | 39.95
2021-05-31 16:00 | 44347.6667 | 0 | 12.1109 | 39.95
2021-05-31 16:30 | 44347.6875 | 0 | 12.7997 | 39.95
2021-05-31 17:00 | 44347.7083 | 0 | 13.7535 | 39.95
2021-05-31 17:30 | 44347.7292 | 0 | 14.7588 | 39.95
2021-05-31 18:00 | 44347.75 | 0 | 14.7275 | 39.95
2021-05-31 18:30 | 44347.7708 | 0 | 14.7 | 39.95
2021-05-31 19:00 | 44347.7917 | 0 | 14.4486 | 39.95
2021-05-31 19:30 | 44347.8125 | 0 | 14.2173 | 39.95
2021-05-31 20:00 | 44347.8333 | 0 | 14.0194 | 39.95
2021-05-31 20:30 | 44347.8542 | 0 | 13.29 | 39.95
2021-05-31 21:00 | 44347.875 | 0 | 12.7843 | 39.95
2021-05-31 21:30 | 44347.8958 | 0 | 12.1288 | 39.95
2021-05-31 22:00 | 44347.9167 | 0 | 11.4328 | 39.95
2021-05-31 22:30 | 44347.9375 | 0 | 10.5246 | 39.95
2021-05-31 23:00 | 44347.9583 | 0 | 9.8825 | 39.95
2021-05-31 23:30 | 44347.9792 | 0 | 9.3668 | 39.95
2021-06-01 | 44348 | 0 | 8.7987 | 39.95
2021-06-01 00:30 | 44348.0208 | 0 | 8.4022 | 39.95
2021-06-01 01:00 | 44348.0417 | 0 | 8.1268 | 39.95
2021-06-01 01:30 | 44348.0625 | 0 | 8.0329 | 39.95
2021-06-01 02:00 | 44348.0833 | 0 | 7.9908 | 39.95
2021-06-01 02:30 | 44348.1042 | 0 | 7.8611 | 39.95
2021-06-01 03:00 | 44348.125 | 0 | 7.8164 | 39.95
2021-06-01 03:30 | 44348.1458 | 0 | 7.9848 | 39.95
2021-06-01 04:00 | 44348.1667 | 0 | 8.3714 | 39.95
2021-06-01 04:30 | 44348.1875 | 0 | 8.8855 | 39.95
2021-06-01 05:00 | 44348.2083 | 0 | 9.6597 | 39.95
2021-06-01 05:30 | 44348.2292 | 0 | 10.432 | 39.95
2021-06-01 06:00 | 44348.25 | 0 | 11.8278 | 39.95
2021-06-01 06:30 | 44348.2708 | 0 | 13.2425 | 39.95
2021-06-01 07:00 | 44348.2917 | 0 | 14.189 | 39.95
2021-06-01 07:30 | 44348.3125 | 0 | 13.9759 | 39.95
2021-06-01 08:00 | 44348.3333 | 0 | 13.7518 | 39.95
2021-06-01 08:30 | 44348.3542 | 0 | 11.7795 | 39.95
2021-06-01 09:00 | 44348.375 | 0 | 10.926 | 39.95
2021-06-01 09:30 | 44348.3958 | 0 | 10.1192 | 39.95
2021-06-01 10:00 | 44348.4167 | 0 | 9.7324 | 39.95
2021-06-01 10:30 | 44348.4375 | 0 | 9.8279 | 39.95
2021-06-01 11:00 | 44348.4583 | 0 | 9.2506 | 39.95
2021-06-01 11:30 | 44348.4792 | 0 | 9.025 | 39.95
2021-06-01 12:00 | 44348.5 | 0 | 8.9554 | 39.95
2021-06-01 12:30 | 44348.5208 | 0 | 9.1821 | 39.95
2021-06-01 13:00 | 44348.5417 | 0 | 9.1395 | 39.95
2021-06-01 13:30 | 44348.5625 | 0 | 9.6171 | 39.95
2021-06-01 14:00 | 44348.5833 | 0 | 10.4133 | 39.95
2021-06-01 14:30 | 44348.6042 | 0 | 10.7612 | 39.95
2021-06-01 15:00 | 44348.625 | 0 | 11.8389 | 39.95
2021-06-01 15:30 | 44348.6458 | 0 | 11.9535 | 39.95
2021-06-01 16:00 | 44348.6667 | 0 | 12.7083 | 39.95
2021-06-01 16:30 | 44348.6875 | 0 | 13.0104 | 39.95
2021-06-01 17:00 | 44348.7083 | 0 | 13.9488 | 39.95
2021-06-01 17:30 | 44348.7292 | 0 | 14.3648 | 39.95
2021-06-01 18:00 | 44348.75 | 0 | 14.5686 | 39.95
2021-06-01 18:30 | 44348.7708 | 0 | 14.546 | 39.95
2021-06-01 19:00 | 44348.7917 | 0 | 14.3255 | 39.95
2021-06-01 19:30 | 44348.8125 | 0 | 14.2629 | 39.95
2021-06-01 20:00 | 44348.8333 | 0 | 13.6823 | 39.95
2021-06-01 20:30 | 44348.8542 | 0 | 13.1444 | 39.95
2021-06-01 21:00 | 44348.875 | 0 | 12.6699 | 39.95
2021-06-01 21:30 | 44348.8958 | 0 | 12.1342 | 39.95
2021-06-01 22:00 | 44348.9167 | 0 | 11.4263 | 39.95
2021-06-01 22:30 | 44348.9375 | 0 | 10.4241 | 39.95
2021-06-01 23:00 | 44348.9583 | 0 | 9.8148 | 39.95
2021-06-01 23:30 | 44348.9792 | 0 | 9.2918 | 39.95
2021-06-02 | 44349 | 0 | 8.7301 | 39.95
2021-06-02 00:30 | 44349.0208 | 0 | 8.3048 | 39.95
2021-06-02 01:00 | 44349.0417 | 0 | 8.1465 | 39.95
2021-06-02 01:30 | 44349.0625 | 0 | 8.02 | 39.95
2021-06-02 02:00 | 44349.0833 | 0 | 7.9676 | 39.95
2021-06-02 02:30 | 44349.1042 | 0 | 7.7924 | 39.95
2021-06-02 03:00 | 44349.125 | 0 | 7.9032 | 39.95
2021-06-02 03:30 | 44349.1458 | 0 | 8.1045 | 39.95
2021-06-02 04:00 | 44349.1667 | 0 | 8.3207 | 39.95
2021-06-02 04:30 | 44349.1875 | 0 | 8.7532 | 39.95
2021-06-02 05:00 | 44349.2083 | 0 | 9.3452 | 39.95
2021-06-02 05:30 | 44349.2292 | 0 | 10.2381 | 39.95
2021-06-02 06:00 | 44349.25 | 0 | 11.6614 | 39.95
2021-06-02 06:30 | 44349.2708 | 0 | 12.7477 | 39.95
2021-06-02 07:00 | 44349.2917 | 0 | 13.345 | 39.95
2021-06-02 07:30 | 44349.3125 | 0 | 13.5479 | 39.95
2021-06-02 08:00 | 44349.3333 | 0 | 12.4397 | 39.95
2021-06-02 08:30 | 44349.3542 | 0 | 11.4266 | 39.95
2021-06-02 09:00 | 44349.375 | 0 | 10.9209 | 39.95
2021-06-02 09:30 | 44349.3958 | 0 | 10.1684 | 39.95
2021-06-02 10:00 | 44349.4167 | 0 | 9.7178 | 39.95
2021-06-02 10:30 | 44349.4375 | 0 | 10.1263 | 39.95
2021-06-02 11:00 | 44349.4583 | 0 | 9.9836 | 39.95
2021-06-02 11:30 | 44349.4792 | 0 | 10.6904 | 39.95
2021-06-02 12:00 | 44349.5 | 0 | 10.4412 | 39.95
2021-06-02 12:30 | 44349.5208 | 0 | 10.9411 | 39.95
2021-06-02 13:00 | 44349.5417 | 0 | 10.9607 | 39.95
2021-06-02 13:30 | 44349.5625 | 0 | 11.3955 | 39.95
2021-06-02 14:00 | 44349.5833 | 0 | 11.8734 | 39.95
2021-06-02 14:30 | 44349.6042 | 0 | 11.8512 | 39.95
2021-06-02 15:00 | 44349.625 | 0 | 11.8718 | 39.95
2021-06-02 15:30 | 44349.6458 | 0 | 12.1957 | 39.95
2021-06-02 16:00 | 44349.6667 | 0 | 12.1696 | 39.95
2021-06-02 16:30 | 44349.6875 | 0 | 12.7998 | 39.95
2021-06-02 17:00 | 44349.7083 | 0 | 13.7981 | 39.95
2021-06-02 17:30 | 44349.7292 | 0 | 14.3416 | 39.95
2021-06-02 18:00 | 44349.75 | 0 | 14.4841 | 39.95
2021-06-02 18:30 | 44349.7708 | 0 | 14.6726 | 39.95
2021-06-02 19:00 | 44349.7917 | 0 | 14.1813 | 39.95
2021-06-02 19:30 | 44349.8125 | 0 | 13.9825 | 39.95
2021-06-02 20:00 | 44349.8333 | 0 | 13.7319 | 39.95
2021-06-02 20:30 | 44349.8542 | 0 | 12.9837 | 39.95
2021-06-02 21:00 | 44349.875 | 0 | 12.4266 | 39.95
2021-06-02 21:30 | 44349.8958 | 0 | 11.9951 | 39.95
2021-06-02 22:00 | 44349.9167 | 0 | 11.3612 | 39.95
2021-06-02 22:30 | 44349.9375 | 0 | 10.4862 | 39.95
2021-06-02 23:00 | 44349.9583 | 0 | 9.7099 | 39.95
2021-06-02 23:30 | 44349.9792 | 0 | 9.342 | 39.95
2021-06-03 | 44350 | 0 | 8.8259 | 39.95
2021-06-03 00:30 | 44350.0208 | 0 | 8.4435 | 39.95
2021-06-03 01:00 | 44350.0417 | 0 | 8.0715 | 39.95
2021-06-03 01:30 | 44350.0625 | 0 | 7.9779 | 39.95
2021-06-03 02:00 | 44350.0833 | 0 | 7.886 | 39.95
2021-06-03 02:30 | 44350.1042 | 0 | 7.8087 | 39.95
2021-06-03 03:00 | 44350.125 | 0 | 7.8388 | 39.95
2021-06-03 03:30 | 44350.1458 | 0 | 7.8955 | 39.95
2021-06-03 04:00 | 44350.1667 | 0 | 8.2587 | 39.95
2021-06-03 04:30 | 44350.1875 | 0 | 8.5873 | 39.95
2021-06-03 05:00 | 44350.2083 | 0 | 9.2699 | 39.95
2021-06-03 05:30 | 44350.2292 | 0 | 10.1263 | 39.95
2021-06-03 06:00 | 44350.25 | 0 | 11.2064 | 39.95
2021-06-03 06:30 | 44350.2708 | 0 | 12.3353 | 39.95
2021-06-03 07:00 | 44350.2917 | 0 | 13.2045 | 39.95
2021-06-03 07:30 | 44350.3125 | 0 | 13.0892 | 39.95
2021-06-03 08:00 | 44350.3333 | 0 | 12.9257 | 39.95
2021-06-03 08:30 | 44350.3542 | 0 | 11.5395 | 39.95
2021-06-03 09:00 | 44350.375 | 0 | 11.8945 | 39.95
2021-06-03 09:30 | 44350.3958 | 0 | 10.5607 | 39.95
2021-06-03 10:00 | 44350.4167 | 0 | 9.92 | 39.95
2021-06-03 10:30 | 44350.4375 | 0 | 11.3944 | 39.95
2021-06-03 11:00 | 44350.4583 | 0 | 12.2298 | 39.95
2021-06-03 11:30 | 44350.4792 | 0 | 12.5655 | 39.95
2021-06-03 12:00 | 44350.5 | 0 | 12.4965 | 39.95
2021-06-03 12:30 | 44350.5208 | 0 | 12.481 | 39.95
2021-06-03 13:00 | 44350.5417 | 0 | 12.6334 | 39.95
2021-06-03 13:30 | 44350.5625 | 0 | 12.5312 | 39.95
2021-06-03 14:00 | 44350.5833 | 0 | 12.6051 | 39.95
2021-06-03 14:30 | 44350.6042 | 0 | 12.7548 | 39.95
2021-06-03 15:00 | 44350.625 | 0 | 12.5733 | 39.95
2021-06-03 15:30 | 44350.6458 | 0 | 12.7442 | 39.95
2021-06-03 16:00 | 44350.6667 | 0 | 13.2842 | 39.95
2021-06-03 16:30 | 44350.6875 | 0 | 13.7948 | 39.95
2021-06-03 17:00 | 44350.7083 | 0 | 14.3365 | 39.95
2021-06-03 17:30 | 44350.7292 | 0 | 14.9558 | 39.95
2021-06-03 18:00 | 44350.75 | 0 | 14.8832 | 39.95
2021-06-03 18:30 | 44350.7708 | 0 | 14.6777 | 39.95
2021-06-03 19:00 | 44350.7917 | 0 | 14.2779 | 39.95
2021-06-03 19:30 | 44350.8125 | 0 | 14.3926 | 39.95
2021-06-03 20:00 | 44350.8333 | 0 | 13.9368 | 39.95
2021-06-03 20:30 | 44350.8542 | 0 | 13.1247 | 39.95
2021-06-03 21:00 | 44350.875 | 0 | 12.7688 | 39.95
2021-06-03 21:30 | 44350.8958 | 0 | 12.1565 | 39.95
2021-06-03 22:00 | 44350.9167 | 0 | 11.6281 | 39.95
2021-06-03 22:30 | 44350.9375 | 0 | 10.5958 | 39.95
2021-06-03 23:00 | 44350.9583 | 0 | 9.7921 | 39.95
2021-06-03 23:30 | 44350.9792 | 0 | 9.3907 | 39.95
2021-06-04 | 44351 | 0 | 8.913 | 39.95
2021-06-04 00:30 | 44351.0208 | 0 | 8.4216 | 39.95
2021-06-04 01:00 | 44351.0417 | 0 | 8.1068 | 39.95
2021-06-04 01:30 | 44351.0625 | 0 | 8.017 | 39.95
2021-06-04 02:00 | 44351.0833 | 0 | 7.9187 | 39.95
2021-06-04 02:30 | 44351.1042 | 0 | 7.8439 | 39.95
2021-06-04 03:00 | 44351.125 | 0 | 7.8139 | 39.95
2021-06-04 03:30 | 44351.1458 | 0 | 7.9874 | 39.95
2021-06-04 04:00 | 44351.1667 | 0 | 8.2472 | 39.95
2021-06-04 04:30 | 44351.1875 | 0 | 8.7389 | 39.95
2021-06-04 05:00 | 44351.2083 | 0 | 9.4346 | 39.95
2021-06-04 05:30 | 44351.2292 | 0 | 10.3691 | 39.95
2021-06-04 06:00 | 44351.25 | 0 | 11.4701 | 39.95
2021-06-04 06:30 | 44351.2708 | 0 | 12.5904 | 39.95
2021-06-04 07:00 | 44351.2917 | 0 | 13.3711 | 39.95
2021-06-04 07:30 | 44351.3125 | 0 | 13.065 | 39.95
2021-06-04 08:00 | 44351.3333 | 0 | 12.3986 | 39.95
2021-06-04 08:30 | 44351.3542 | 0 | 11.4466 | 39.95
2021-06-04 09:00 | 44351.375 | 0 | 10.8693 | 39.95
2021-06-04 09:30 | 44351.3958 | 0 | 10.3023 | 39.95
2021-06-04 10:00 | 44351.4167 | 0 | 9.7711 | 39.95
2021-06-04 10:30 | 44351.4375 | 0 | 9.3748 | 39.95
2021-06-04 11:00 | 44351.4583 | 0 | 9.1072 | 39.95
2021-06-04 11:30 | 44351.4792 | 0 | 8.8032 | 39.95
2021-06-04 12:00 | 44351.5 | 0 | 9.2368 | 39.95
2021-06-04 12:30 | 44351.5208 | 0 | 9.3056 | 39.95
2021-06-04 13:00 | 44351.5417 | 0 | 9.2501 | 39.95
2021-06-04 13:30 | 44351.5625 | 0 | 9.104 | 39.95
2021-06-04 14:00 | 44351.5833 | 0 | 9.6013 | 39.95
2021-06-04 14:30 | 44351.6042 | 0 | 10.0853 | 39.95
2021-06-04 15:00 | 44351.625 | 0 | 10.5824 | 39.95
2021-06-04 15:30 | 44351.6458 | 0 | 11.376 | 39.95
2021-06-04 16:00 | 44351.6667 | 0 | 12.0096 | 39.95
2021-06-04 16:30 | 44351.6875 | 0 | 12.578 | 39.95
2021-06-04 17:00 | 44351.7083 | 0 | 13.5093 | 39.95
2021-06-04 17:30 | 44351.7292 | 0 | 13.9336 | 39.95
2021-06-04 18:00 | 44351.75 | 0 | 13.7517 | 39.95
2021-06-04 18:30 | 44351.7708 | 0 | 13.7993 | 39.95
2021-06-04 19:00 | 44351.7917 | 0 | 13.6586 | 39.95
2021-06-04 19:30 | 44351.8125 | 0 | 13.4695 | 39.95
2021-06-04 20:00 | 44351.8333 | 0 | 13.3895 | 39.95
2021-06-04 20:30 | 44351.8542 | 0 | 12.7654 | 39.95
2021-06-04 21:00 | 44351.875 | 0 | 12.412 | 39.95
2021-06-04 21:30 | 44351.8958 | 0 | 11.9637 | 39.95
2021-06-04 22:00 | 44351.9167 | 0 | 11.3363 | 39.95
2021-06-04 22:30 | 44351.9375 | 0 | 10.5002 | 39.95
2021-06-04 23:00 | 44351.9583 | 0 | 9.7254 | 39.95
2021-06-04 23:30 | 44351.9792 | 0 | 9.2802 | 39.95
2021-06-05 | 44352 | 0 | 8.7394 | 39.95
2021-06-05 00:30 | 44352.0208 | 0 | 8.3855 | 39.95
2021-06-05 01:00 | 44352.0417 | 0 | 8.1093 | 39.95
2021-06-05 01:30 | 44352.0625 | 0 | 7.8608 | 39.95
2021-06-05 02:00 | 44352.0833 | 0 | 7.8505 | 39.95
2021-06-05 02:30 | 44352.1042 | 0 | 7.6627 | 39.95
2021-06-05 03:00 | 44352.125 | 0 | 7.6329 | 39.95
2021-06-05 03:30 | 44352.1458 | 0 | 7.6131 | 39.95
2021-06-05 04:00 | 44352.1667 | 0 | 7.7472 | 39.95
2021-06-05 04:30 | 44352.1875 | 0 | 7.7992 | 39.95
2021-06-05 05:00 | 44352.2083 | 0 | 8.1284 | 39.95
2021-06-05 05:30 | 44352.2292 | 0 | 8.413 | 39.95
2021-06-05 06:00 | 44352.25 | 0 | 8.9497 | 39.95
2021-06-05 06:30 | 44352.2708 | 0 | 9.6497 | 39.95
2021-06-05 07:00 | 44352.2917 | 0 | 10.0274 | 39.95
2021-06-05 07:30 | 44352.3125 | 0 | 10.0325 | 39.95
2021-06-05 08:00 | 44352.3333 | 0 | 10.005 | 39.95
2021-06-05 08:30 | 44352.3542 | 0 | 9.4999 | 39.95
2021-06-05 09:00 | 44352.375 | 0 | 8.9104 | 39.95
2021-06-05 09:30 | 44352.3958 | 0 | 8.3203 | 39.95
2021-06-05 10:00 | 44352.4167 | 0 | 7.748 | 39.95
2021-06-05 10:30 | 44352.4375 | 0 | 7.349 | 39.95
2021-06-05 11:00 | 44352.4583 | 0 | 6.9136 | 39.95
2021-06-05 11:30 | 44352.4792 | 0 | 6.6173 | 39.95
2021-06-05 12:00 | 44352.5 | 0 | 6.4988 | 39.95
2021-06-05 12:30 | 44352.5208 | 0 | 6.6002 | 39.95
2021-06-05 13:00 | 44352.5417 | 0 | 6.6978 | 39.95
2021-06-05 13:30 | 44352.5625 | 0 | 6.985 | 39.95
2021-06-05 14:00 | 44352.5833 | 0 | 7.4318 | 39.95
2021-06-05 14:30 | 44352.6042 | 0 | 8.0017 | 39.95
2021-06-05 15:00 | 44352.625 | 0 | 8.5984 | 39.95
2021-06-05 15:30 | 44352.6458 | 0 | 9.2032 | 39.95
2021-06-05 16:00 | 44352.6667 | 0 | 9.9984 | 39.95
2021-06-05 16:30 | 44352.6875 | 0 | 10.8752 | 39.95
2021-06-05 17:00 | 44352.7083 | 0 | 11.8138 | 39.95
2021-06-05 17:30 | 44352.7292 | 0 | 12.2581 | 39.95
2021-06-05 18:00 | 44352.75 | 0 | 12.5118 | 39.95
2021-06-05 18:30 | 44352.7708 | 0 | 12.5062 | 39.95
2021-06-05 19:00 | 44352.7917 | 0 | 12.216 | 39.95
2021-06-05 19:30 | 44352.8125 | 0 | 11.858 | 39.95
2021-06-05 20:00 | 44352.8333 | 0 | 11.5071 | 39.95
2021-06-05 20:30 | 44352.8542 | 0 | 11.1362 | 39.95
2021-06-05 21:00 | 44352.875 | 0 | 10.7499 | 39.95
2021-06-05 21:30 | 44352.8958 | 0 | 10.5608 | 39.95
2021-06-05 22:00 | 44352.9167 | 0 | 10.1034 | 39.95
2021-06-05 22:30 | 44352.9375 | 0 | 9.4048 | 39.95
2021-06-05 23:00 | 44352.9583 | 0 | 8.9709 | 39.95
2021-06-05 23:30 | 44352.9792 | 0 | 8.6046 | 39.95
2021-06-06 | 44353 | 0 | 8.1809 | 39.95
2021-06-06 00:30 | 44353.0208 | 0 | 7.6814 | 39.95
2021-06-06 01:00 | 44353.0417 | 0 | 7.5312 | 39.95
2021-06-06 01:30 | 44353.0625 | 0 | 7.4196 | 39.95
2021-06-06 02:00 | 44353.0833 | 0 | 7.4119 | 39.95
2021-06-06 02:30 | 44353.1042 | 0 | 7.2128 | 39.95
2021-06-06 03:00 | 44353.125 | 0 | 7.2209 | 39.95
2021-06-06 03:30 | 44353.1458 | 0 | 7.1837 | 39.95
2021-06-06 04:00 | 44353.1667 | 0 | 7.2538 | 39.95
2021-06-06 04:30 | 44353.1875 | 0 | 7.2607 | 39.95
2021-06-06 05:00 | 44353.2083 | 0 | 7.4463 | 39.95
2021-06-06 05:30 | 44353.2292 | 0 | 7.6805 | 39.95
2021-06-06 06:00 | 44353.25 | 0 | 8.1632 | 39.95
2021-06-06 06:30 | 44353.2708 | 0 | 8.6628 | 39.95
2021-06-06 07:00 | 44353.2917 | 0 | 9.1335 | 39.95
2021-06-06 07:30 | 44353.3125 | 0 | 9.3202 | 39.95
2021-06-06 08:00 | 44353.3333 | 0 | 9.2383 | 39.95
2021-06-06 08:30 | 44353.3542 | 0 | 8.9287 | 39.95
2021-06-06 09:00 | 44353.375 | 0 | 8.5652 | 39.95
2021-06-06 09:30 | 44353.3958 | 0 | 7.9731 | 39.95
2021-06-06 10:00 | 44353.4167 | 0 | 7.38 | 39.95
2021-06-06 10:30 | 44353.4375 | 0 | 6.8862 | 39.95
2021-06-06 11:00 | 44353.4583 | 0 | 6.4972 | 39.95
2021-06-06 11:30 | 44353.4792 | 0 | 6.2978 | 39.95
2021-06-06 12:00 | 44353.5 | 0 | 6.1483 | 39.95
2021-06-06 12:30 | 44353.5208 | 0 | 6.1744 | 39.95
2021-06-06 13:00 | 44353.5417 | 0 | 6.3645 | 39.95
2021-06-06 13:30 | 44353.5625 | 0 | 6.6341 | 39.95
2021-06-06 14:00 | 44353.5833 | 0 | 7.1296 | 39.95
2021-06-06 14:30 | 44353.6042 | 0 | 7.653 | 39.95
2021-06-06 15:00 | 44353.625 | 0 | 8.2793 | 39.95
2021-06-06 15:30 | 44353.6458 | 0 | 9.1948 | 39.95
2021-06-06 16:00 | 44353.6667 | 0 | 9.943 | 39.95
2021-06-06 16:30 | 44353.6875 | 0 | 10.9995 | 39.95
2021-06-06 17:00 | 44353.7083 | 0 | 12.1529 | 39.95
2021-06-06 17:30 | 44353.7292 | 0 | 13.0273 | 39.95
2021-06-06 18:00 | 44353.75 | 0 | 13.0551 | 39.95
2021-06-06 18:30 | 44353.7708 | 0 | 12.8679 | 39.95
2021-06-06 19:00 | 44353.7917 | 0 | 12.8336 | 39.95
2021-06-06 19:30 | 44353.8125 | 0 | 12.6205 | 39.95
2021-06-06 20:00 | 44353.8333 | 0 | 12.3173 | 39.95
2021-06-06 20:30 | 44353.8542 | 0 | 11.7627 | 39.95
2021-06-06 21:00 | 44353.875 | 0 | 11.0898 | 39.95
2021-06-06 21:30 | 44353.8958 | 0 | 10.5139 | 39.95
2021-06-06 22:00 | 44353.9167 | 0 | 9.9671 | 39.95
2021-06-06 22:30 | 44353.9375 | 0 | 9.2097 | 39.95
2021-06-06 23:00 | 44353.9583 | 0 | 8.5674 | 39.95
2021-06-06 23:30 | 44353.9792 | 0 | 8.2255 | 39.95
2021-06-07 | 44354 | 0 | 7.8374 | 39.95
2021-06-07 00:30 | 44354.0208 | 0 | 7.6578 | 39.95
2021-06-07 01:00 | 44354.0417 | 0 | 7.4642 | 39.95
2021-06-07 01:30 | 44354.0625 | 0 | 7.3972 | 39.95
2021-06-07 02:00 | 44354.0833 | 0 | 7.3672 | 39.95
2021-06-07 02:30 | 44354.1042 | 0 | 7.4368 | 39.95
2021-06-07 03:00 | 44354.125 | 0 | 7.3251 | 39.95
2021-06-07 03:30 | 44354.1458 | 0 | 7.6026 | 39.95
2021-06-07 04:00 | 44354.1667 | 0 | 7.8368 | 39.95
2021-06-07 04:30 | 44354.1875 | 0 | 8.3471 | 39.95
2021-06-07 05:00 | 44354.2083 | 0 | 9.2182 | 39.95
2021-06-07 05:30 | 44354.2292 | 0 | 10.1047 | 39.95
2021-06-07 06:00 | 44354.25 | 0 | 11.9227 | 39.95
2021-06-07 06:30 | 44354.2708 | 0 | 13.5391 | 39.95
2021-06-07 07:00 | 44354.2917 | 0 | 14.5287 | 39.95
2021-06-07 07:30 | 44354.3125 | 0 | 14.1673 | 39.95
2021-06-07 08:00 | 44354.3333 | 0 | 13.1391 | 39.95
2021-06-07 08:30 | 44354.3542 | 0 | 12.4819 | 39.95
2021-06-07 09:00 | 44354.375 | 0 | 11.692 | 39.95
2021-06-07 09:30 | 44354.3958 | 0 | 10.7483 | 39.95
2021-06-07 10:00 | 44354.4167 | 0 | 9.9435 | 39.95
2021-06-07 10:30 | 44354.4375 | 0 | 9.5257 | 39.95
2021-06-07 11:00 | 44354.4583 | 0 | 9.3651 | 39.95
2021-06-07 11:30 | 44354.4792 | 0 | 9.3082 | 39.95
2021-06-07 12:00 | 44354.5 | 0 | 9.1263 | 39.95
2021-06-07 12:30 | 44354.5208 | 0 | 9.2331 | 39.95
2021-06-07 13:00 | 44354.5417 | 0 | 9.9072 | 39.95
2021-06-07 13:30 | 44354.5625 | 0 | 10.6822 | 39.95
2021-06-07 14:00 | 44354.5833 | 0 | 11.3556 | 39.95
2021-06-07 14:30 | 44354.6042 | 0 | 11.052 | 39.95
2021-06-07 15:00 | 44354.625 | 0 | 10.771 | 39.95
2021-06-07 15:30 | 44354.6458 | 0 | 11.6079 | 39.95
2021-06-07 16:00 | 44354.6667 | 0 | 12.1413 | 39.95
2021-06-07 16:30 | 44354.6875 | 0 | 12.9805 | 39.95
2021-06-07 17:00 | 44354.7083 | 0 | 13.9804 | 39.95
2021-06-07 17:30 | 44354.7292 | 0 | 14.8046 | 39.95
2021-06-07 18:00 | 44354.75 | 0 | 15.1415 | 39.95
2021-06-07 18:30 | 44354.7708 | 0 | 15.4003 | 39.95
2021-06-07 19:00 | 44354.7917 | 0 | 15.0199 | 39.95
2021-06-07 19:30 | 44354.8125 | 0 | 14.7524 | 39.95
2021-06-07 20:00 | 44354.8333 | 0 | 14.295 | 39.95
2021-06-07 20:30 | 44354.8542 | 0 | 13.6659 | 39.95
2021-06-07 21:00 | 44354.875 | 0 | 13.1244 | 39.95
2021-06-07 21:30 | 44354.8958 | 0 | 12.4707 | 39.95
2021-06-07 22:00 | 44354.9167 | 0 | 11.5365 | 39.95
2021-06-07 22:30 | 44354.9375 | 0 | 10.5902 | 39.95
2021-06-07 23:00 | 44354.9583 | 0 | 10.0929 | 39.95
2021-06-07 23:30 | 44354.9792 | 0 | 9.562 | 39.95
2021-06-08 | 44355 | 0 | 9 | 39.95
2021-06-08 00:30 | 44355.0208 | 0 | 8.4695 | 39.95
2021-06-08 01:00 | 44355.0417 | 0 | 8.2774 | 39.95
2021-06-08 01:30 | 44355.0625 | 0 | 8.1145 | 39.95
2021-06-08 02:00 | 44355.0833 | 0 | 8.0288 | 39.95
2021-06-08 02:30 | 44355.1042 | 0 | 7.8413 | 39.95
2021-06-08 03:00 | 44355.125 | 0 | 7.8929 | 39.95
2021-06-08 03:30 | 44355.1458 | 0 | 8.0372 | 39.95
2021-06-08 04:00 | 44355.1667 | 0 | 8.3903 | 39.95
2021-06-08 04:30 | 44355.1875 | 0 | 8.9031 | 39.95
2021-06-08 05:00 | 44355.2083 | 0 | 9.725 | 39.95
2021-06-08 05:30 | 44355.2292 | 0 | 10.8471 | 39.95
2021-06-08 06:00 | 44355.25 | 0 | 12.2576 | 39.95
2021-06-08 06:30 | 44355.2708 | 0 | 13.4438 | 39.95
2021-06-08 07:00 | 44355.2917 | 0 | 14.5631 | 39.95
2021-06-08 07:30 | 44355.3125 | 0 | 14.1005 | 39.95
2021-06-08 08:00 | 44355.3333 | 0 | 13.1276 | 39.95
2021-06-08 08:30 | 44355.3542 | 0 | 12.1096 | 39.95
2021-06-08 09:00 | 44355.375 | 0 | 10.8581 | 39.95
2021-06-08 09:30 | 44355.3958 | 0 | 10.2184 | 39.95
2021-06-08 10:00 | 44355.4167 | 0 | 10.5358 | 39.95
2021-06-08 10:30 | 44355.4375 | 0 | 10.8728 | 39.95
2021-06-08 11:00 | 44355.4583 | 0 | 12.0122 | 39.95
2021-06-08 11:30 | 44355.4792 | 0 | 11.98 | 39.95
2021-06-08 12:00 | 44355.5 | 0 | 11.9554 | 39.95
2021-06-08 12:30 | 44355.5208 | 0 | 11.1874 | 39.95
2021-06-08 13:00 | 44355.5417 | 0 | 11.278 | 39.95
2021-06-08 13:30 | 44355.5625 | 0 | 11.2991 | 39.95
2021-06-08 14:00 | 44355.5833 | 0 | 11.4813 | 39.95
2021-06-08 14:30 | 44355.6042 | 0 | 12.1451 | 39.95
2021-06-08 15:00 | 44355.625 | 0 | 12.0963 | 39.95
2021-06-08 15:30 | 44355.6458 | 0 | 12.415 | 39.95
2021-06-08 16:00 | 44355.6667 | 0 | 12.8244 | 39.95
2021-06-08 16:30 | 44355.6875 | 0 | 13.7648 | 39.95
2021-06-08 17:00 | 44355.7083 | 0 | 14.6432 | 39.95
2021-06-08 17:30 | 44355.7292 | 0 | 15.3675 | 39.95
2021-06-08 18:00 | 44355.75 | 0 | 15.427 | 39.95
2021-06-08 18:30 | 44355.7708 | 0 | 15.3922 | 39.95
2021-06-08 19:00 | 44355.7917 | 0 | 15.039 | 39.95
2021-06-08 19:30 | 44355.8125 | 0 | 14.8735 | 39.95
2021-06-08 20:00 | 44355.8333 | 0 | 14.3861 | 39.95
2021-06-08 20:30 | 44355.8542 | 0 | 13.9661 | 39.95
2021-06-08 21:00 | 44355.875 | 0 | 13.0873 | 39.95
2021-06-08 21:30 | 44355.8958 | 0 | 12.481 | 39.95
2021-06-08 22:00 | 44355.9167 | 0 | 11.9378 | 39.95
2021-06-08 22:30 | 44355.9375 | 0 | 10.8542 | 39.95
2021-06-08 23:00 | 44355.9583 | 0 | 9.9907 | 39.95
2021-06-08 23:30 | 44355.9792 | 0 | 9.604 | 39.95
2021-06-09 | 44356 | 0 | 8.8811 | 39.95
2021-06-09 00:30 | 44356.0208 | 0 | 8.452 | 39.95
2021-06-09 01:00 | 44356.0417 | 0 | 8.1981 | 39.95
2021-06-09 01:30 | 44356.0625 | 0 | 8.1898 | 39.95
2021-06-09 02:00 | 44356.0833 | 0 | 8.1317 | 39.95
2021-06-09 02:30 | 44356.1042 | 0 | 7.9753 | 39.95
2021-06-09 03:00 | 44356.125 | 0 | 8.0346 | 39.95
2021-06-09 03:30 | 44356.1458 | 0 | 8.1941 | 39.95
2021-06-09 04:00 | 44356.1667 | 0 | 8.485 | 39.95
2021-06-09 04:30 | 44356.1875 | 0 | 8.8976 | 39.95
2021-06-09 05:00 | 44356.2083 | 0 | 9.684 | 39.95
2021-06-09 05:30 | 44356.2292 | 0 | 10.5178 | 39.95
2021-06-09 06:00 | 44356.25 | 0 | 11.7831 | 39.95
2021-06-09 06:30 | 44356.2708 | 0 | 13.1995 | 39.95
2021-06-09 07:00 | 44356.2917 | 0 | 13.9879 | 39.95
2021-06-09 07:30 | 44356.3125 | 0 | 14.2929 | 39.95
2021-06-09 08:00 | 44356.3333 | 0 | 14.6185 | 39.95
2021-06-09 08:30 | 44356.3542 | 0 | 14.2035 | 39.95
2021-06-09 09:00 | 44356.375 | 0 | 12.4226 | 39.95
2021-06-09 09:30 | 44356.3958 | 0 | 12.8451 | 39.95
2021-06-09 10:00 | 44356.4167 | 0 | 13.2966 | 39.95
2021-06-09 10:30 | 44356.4375 | 0 | 11.9784 | 39.95
2021-06-09 11:00 | 44356.4583 | 0 | 11.3464 | 39.95
2021-06-09 11:30 | 44356.4792 | 0 | 9.938 | 39.95
2021-06-09 12:00 | 44356.5 | 0 | 11.5304 | 39.95
2021-06-09 12:30 | 44356.5208 | 0 | 12.1074 | 39.95
2021-06-09 13:00 | 44356.5417 | 0 | 10.3907 | 39.95
2021-06-09 13:30 | 44356.5625 | 0 | 9.8681 | 39.95
2021-06-09 14:00 | 44356.5833 | 0 | 10.4416 | 39.95
2021-06-09 14:30 | 44356.6042 | 0 | 11.1673 | 39.95
2021-06-09 15:00 | 44356.625 | 0 | 11.2457 | 39.95
2021-06-09 15:30 | 44356.6458 | 0 | 12.2602 | 39.95
2021-06-09 16:00 | 44356.6667 | 0 | 13.1467 | 39.95
2021-06-09 16:30 | 44356.6875 | 0 | 13.9463 | 39.95
2021-06-09 17:00 | 44356.7083 | 0 | 15.3813 | 39.95
2021-06-09 17:30 | 44356.7292 | 0 | 16.7103 | 39.95
2021-06-09 18:00 | 44356.75 | 0 | 17.2752 | 39.95
2021-06-09 18:30 | 44356.7708 | 0 | 17.7461 | 39.95
2021-06-09 19:00 | 44356.7917 | 0 | 17.3843 | 39.95
2021-06-09 19:30 | 44356.8125 | 0 | 17.1271 | 39.95
2021-06-09 20:00 | 44356.8333 | 0 | 16.6138 | 39.95
2021-06-09 20:30 | 44356.8542 | 0 | 15.5214 | 39.95
2021-06-09 21:00 | 44356.875 | 0 | 14.9825 | 39.95
2021-06-09 21:30 | 44356.8958 | 0 | 14.3799 | 39.95
2021-06-09 22:00 | 44356.9167 | 0 | 13.3558 | 39.95
2021-06-09 22:30 | 44356.9375 | 0 | 12.0319 | 39.95
2021-06-09 23:00 | 44356.9583 | 0 | 11.2639 | 39.95
2021-06-09 23:30 | 44356.9792 | 0 | 10.3145 | 39.95
2021-06-10 | 44357 | 0 | 9.5654 | 39.95
2021-06-10 00:30 | 44357.0208 | 0 | 9.1412 | 39.95
2021-06-10 01:00 | 44357.0417 | 0 | 8.9777 | 39.95
2021-06-10 01:30 | 44357.0625 | 0 | 8.7007 | 39.95
2021-06-10 02:00 | 44357.0833 | 0 | 8.6972 | 39.95
2021-06-10 02:30 | 44357.1042 | 0 | 8.5362 | 39.95
2021-06-10 03:00 | 44357.125 | 0 | 8.4443 | 39.95
2021-06-10 03:30 | 44357.1458 | 0 | 8.6877 | 39.95
2021-06-10 04:00 | 44357.1667 | 0 | 8.8409 | 39.95
2021-06-10 04:30 | 44357.1875 | 0 | 9.4432 | 39.95
2021-06-10 05:00 | 44357.2083 | 0 | 10.4805 | 39.95
2021-06-10 05:30 | 44357.2292 | 0 | 11.6492 | 39.95
2021-06-10 06:00 | 44357.25 | 0 | 13.4357 | 39.95
2021-06-10 06:30 | 44357.2708 | 0 | 15.1143 | 39.95
2021-06-10 07:00 | 44357.2917 | 0 | 16.0528 | 39.95
2021-06-10 07:30 | 44357.3125 | 0 | 15.4872 | 39.95
2021-06-10 08:00 | 44357.3333 | 0 | 14.312 | 39.95
2021-06-10 08:30 | 44357.3542 | 0 | 12.985 | 39.95
2021-06-10 09:00 | 44357.375 | 0 | 12.008 | 39.95
2021-06-10 09:30 | 44357.3958 | 0 | 11.3027 | 39.95
2021-06-10 10:00 | 44357.4167 | 0 | 10.5499 | 39.95
2021-06-10 10:30 | 44357.4375 | 0 | 9.9337 | 39.95
2021-06-10 11:00 | 44357.4583 | 0 | 9.4077 | 39.95
2021-06-10 11:30 | 44357.4792 | 0 | 9.1761 | 39.95
2021-06-10 12:00 | 44357.5 | 0 | 9.025 | 39.95
2021-06-10 12:30 | 44357.5208 | 0 | 9.0619 | 39.95
2021-06-10 13:00 | 44357.5417 | 0 | 9.3451 | 39.95
2021-06-10 13:30 | 44357.5625 | 0 | 9.727 | 39.95
2021-06-10 14:00 | 44357.5833 | 0 | 10.1598 | 39.95
2021-06-10 14:30 | 44357.6042 | 0 | 10.7669 | 39.95
2021-06-10 15:00 | 44357.625 | 0 | 11.4321 | 39.95
2021-06-10 15:30 | 44357.6458 | 0 | 12.4074 | 39.95
2021-06-10 16:00 | 44357.6667 | 0 | 13.2453 | 39.95
2021-06-10 16:30 | 44357.6875 | 0 | 14.4391 | 39.95
2021-06-10 17:00 | 44357.7083 | 0 | 15.6366 | 39.95
2021-06-10 17:30 | 44357.7292 | 0 | 16.8353 | 39.95
2021-06-10 18:00 | 44357.75 | 0 | 16.9654 | 39.95
2021-06-10 18:30 | 44357.7708 | 0 | 17.2554 | 39.95
2021-06-10 19:00 | 44357.7917 | 0 | 17.1368 | 39.95
2021-06-10 19:30 | 44357.8125 | 0 | 17.0893 | 39.95
2021-06-10 20:00 | 44357.8333 | 0 | 16.8289 | 39.95
2021-06-10 20:30 | 44357.8542 | 0 | 16.1377 | 39.95
2021-06-10 21:00 | 44357.875 | 0 | 15.2165 | 39.95
2021-06-10 21:30 | 44357.8958 | 0 | 14.4298 | 39.95
2021-06-10 22:00 | 44357.9167 | 0 | 13.3794 | 39.95
2021-06-10 22:30 | 44357.9375 | 0 | 12.2319 | 39.95
2021-06-10 23:00 | 44357.9583 | 0 | 11.2673 | 39.95
2021-06-10 23:30 | 44357.9792 | 0 | 10.4924 | 39.95
2021-06-11 | 44358 | 0 | 9.7269 | 39.95
2021-06-11 00:30 | 44358.0208 | 0 | 9.2501 | 39.95
2021-06-11 01:00 | 44358.0417 | 0 | 9.0026 | 39.95
2021-06-11 01:30 | 44358.0625 | 0 | 8.7745 | 39.95
2021-06-11 02:00 | 44358.0833 | 0 | 8.7891 | 39.95
2021-06-11 02:30 | 44358.1042 | 0 | 8.6453 | 39.95
2021-06-11 03:00 | 44358.125 | 0 | 8.5585 | 39.95
2021-06-11 03:30 | 44358.1458 | 0 | 8.7547 | 39.95
2021-06-11 04:00 | 44358.1667 | 0 | 9.0417 | 39.95
2021-06-11 04:30 | 44358.1875 | 0 | 9.53 | 39.95
2021-06-11 05:00 | 44358.2083 | 0 | 10.5157 | 39.95
2021-06-11 05:30 | 44358.2292 | 0 | 11.5888 | 39.95
2021-06-11 06:00 | 44358.25 | 0 | 13.3314 | 39.95
2021-06-11 06:30 | 44358.2708 | 0 | 15.1104 | 39.95
2021-06-11 07:00 | 44358.2917 | 0 | 16.2501 | 39.95
2021-06-11 07:30 | 44358.3125 | 0 | 15.587 | 39.95
2021-06-11 08:00 | 44358.3333 | 0 | 14.5318 | 39.95
2021-06-11 08:30 | 44358.3542 | 0 | 14.3144 | 39.95
2021-06-11 09:00 | 44358.375 | 0 | 12.3724 | 39.95
2021-06-11 09:30 | 44358.3958 | 0 | 12.1771 | 39.95
2021-06-11 10:00 | 44358.4167 | 0 | 11.0279 | 39.95
2021-06-11 10:30 | 44358.4375 | 0 | 10.7757 | 39.95
2021-06-11 11:00 | 44358.4583 | 0 | 10.6425 | 39.95
2021-06-11 11:30 | 44358.4792 | 0 | 9.8506 | 39.95
2021-06-11 12:00 | 44358.5 | 0 | 9.5058 | 39.95
2021-06-11 12:30 | 44358.5208 | 0 | 9.5717 | 39.95
2021-06-11 13:00 | 44358.5417 | 0 | 9.8626 | 39.95
2021-06-11 13:30 | 44358.5625 | 0 | 9.6161 | 39.95
2021-06-11 14:00 | 44358.5833 | 0 | 10.8671 | 39.95
2021-06-11 14:30 | 44358.6042 | 0 | 10.9589 | 39.95
2021-06-11 15:00 | 44358.625 | 0 | 11.5075 | 39.95
2021-06-11 15:30 | 44358.6458 | 0 | 12.3795 | 39.95
2021-06-11 16:00 | 44358.6667 | 0 | 12.4799 | 39.95
2021-06-11 16:30 | 44358.6875 | 0 | 13.7258 | 39.95
2021-06-11 17:00 | 44358.7083 | 0 | 15.0093 | 39.95
2021-06-11 17:30 | 44358.7292 | 0 | 15.7395 | 39.95
2021-06-11 18:00 | 44358.75 | 0 | 16.0008 | 39.95
2021-06-11 18:30 | 44358.7708 | 0 | 16.2716 | 39.95
2021-06-11 19:00 | 44358.7917 | 0 | 16.1254 | 39.95
2021-06-11 19:30 | 44358.8125 | 0 | 15.8089 | 39.95
2021-06-11 20:00 | 44358.8333 | 0 | 15.4664 | 39.95
2021-06-11 20:30 | 44358.8542 | 0 | 14.9721 | 39.95
2021-06-11 21:00 | 44358.875 | 0 | 14.495 | 39.95
2021-06-11 21:30 | 44358.8958 | 0 | 13.8273 | 39.95
2021-06-11 22:00 | 44358.9167 | 0 | 13.1453 | 39.95
2021-06-11 22:30 | 44358.9375 | 0 | 11.9988 | 39.95
2021-06-11 23:00 | 44358.9583 | 0 | 11.0846 | 39.95
2021-06-11 23:30 | 44358.9792 | 0 | 10.5043 | 39.95
2021-06-12 | 44359 | 0 | 9.7399 | 39.95
2021-06-12 00:30 | 44359.0208 | 0 | 9.26 | 39.95
2021-06-12 01:00 | 44359.0417 | 0 | 8.9353 | 39.95
2021-06-12 01:30 | 44359.0625 | 0 | 8.6221 | 39.95
2021-06-12 02:00 | 44359.0833 | 0 | 8.5955 | 39.95
2021-06-12 02:30 | 44359.1042 | 0 | 8.4718 | 39.95
2021-06-12 03:00 | 44359.125 | 0 | 8.4219 | 39.95
2021-06-12 03:30 | 44359.1458 | 0 | 8.5655 | 39.95
2021-06-12 04:00 | 44359.1667 | 0 | 8.5757 | 39.95
2021-06-12 04:30 | 44359.1875 | 0 | 8.6823 | 39.95
2021-06-12 05:00 | 44359.2083 | 0 | 9.2558 | 39.95
2021-06-12 05:30 | 44359.2292 | 0 | 9.629 | 39.95
2021-06-12 06:00 | 44359.25 | 0 | 10.5796 | 39.95
2021-06-12 06:30 | 44359.2708 | 0 | 11.3552 | 39.95
2021-06-12 07:00 | 44359.2917 | 0 | 12.0941 | 39.95
2021-06-12 07:30 | 44359.3125 | 0 | 12.2186 | 39.95
2021-06-12 08:00 | 44359.3333 | 0 | 12.0791 | 39.95
2021-06-12 08:30 | 44359.3542 | 0 | 11.3662 | 39.95
2021-06-12 09:00 | 44359.375 | 0 | 10.583 | 39.95
2021-06-12 09:30 | 44359.3958 | 0 | 9.7727 | 39.95
2021-06-12 10:00 | 44359.4167 | 0 | 8.8365 | 39.95
2021-06-12 10:30 | 44359.4375 | 0 | 8.2499 | 39.95
2021-06-12 11:00 | 44359.4583 | 0 | 7.5678 | 39.95
2021-06-12 11:30 | 44359.4792 | 0 | 7.2724 | 39.95
2021-06-12 12:00 | 44359.5 | 0 | 6.9456 | 39.95
2021-06-12 12:30 | 44359.5208 | 0 | 6.9308 | 39.95
2021-06-12 13:00 | 44359.5417 | 0 | 6.8957 | 39.95
2021-06-12 13:30 | 44359.5625 | 0 | 7.2335 | 39.95
2021-06-12 14:00 | 44359.5833 | 0 | 7.7791 | 39.95
2021-06-12 14:30 | 44359.6042 | 0 | 8.1184 | 39.95
2021-06-12 15:00 | 44359.625 | 0 | 8.8983 | 39.95
2021-06-12 15:30 | 44359.6458 | 0 | 9.6938 | 39.95
2021-06-12 16:00 | 44359.6667 | 0 | 10.2974 | 39.95
2021-06-12 16:30 | 44359.6875 | 0 | 11.171 | 39.95
2021-06-12 17:00 | 44359.7083 | 0 | 12.3021 | 39.95
2021-06-12 17:30 | 44359.7292 | 0 | 12.83 | 39.95
2021-06-12 18:00 | 44359.75 | 0 | 13.08 | 39.95
2021-06-12 18:30 | 44359.7708 | 0 | 13.0225 | 39.95
2021-06-12 19:00 | 44359.7917 | 0 | 12.9451 | 39.95
2021-06-12 19:30 | 44359.8125 | 0 | 12.7743 | 39.95
2021-06-12 20:00 | 44359.8333 | 0 | 12.4117 | 39.95
2021-06-12 20:30 | 44359.8542 | 0 | 12.0619 | 39.95
2021-06-12 21:00 | 44359.875 | 0 | 11.5073 | 39.95
2021-06-12 21:30 | 44359.8958 | 0 | 11.1964 | 39.95
2021-06-12 22:00 | 44359.9167 | 0 | 10.6403 | 39.95
2021-06-12 22:30 | 44359.9375 | 0 | 9.8905 | 39.95
2021-06-12 23:00 | 44359.9583 | 0 | 9.4059 | 39.95
2021-06-12 23:30 | 44359.9792 | 0 | 8.9115 | 39.95
2021-06-13 | 44360 | 0 | 8.4589 | 39.95
2021-06-13 00:30 | 44360.0208 | 0 | 8.0977 | 39.95
2021-06-13 01:00 | 44360.0417 | 0 | 7.9135 | 39.95
2021-06-13 01:30 | 44360.0625 | 0 | 7.6397 | 39.95
2021-06-13 02:00 | 44360.0833 | 0 | 7.5484 | 39.95
2021-06-13 02:30 | 44360.1042 | 0 | 7.5261 | 39.95
2021-06-13 03:00 | 44360.125 | 0 | 7.5063 | 39.95
2021-06-13 03:30 | 44360.1458 | 0 | 7.4368 | 39.95
2021-06-13 04:00 | 44360.1667 | 0 | 7.4617 | 39.95
2021-06-13 04:30 | 44360.1875 | 0 | 7.4368 | 39.95
2021-06-13 05:00 | 44360.2083 | 0 | 7.7449 | 39.95
2021-06-13 05:30 | 44360.2292 | 0 | 8.0913 | 39.95
2021-06-13 06:00 | 44360.25 | 0 | 8.5832 | 39.95
2021-06-13 06:30 | 44360.2708 | 0 | 9.1881 | 39.95
2021-06-13 07:00 | 44360.2917 | 0 | 9.8007 | 39.95
2021-06-13 07:30 | 44360.3125 | 0 | 9.9904 | 39.95
2021-06-13 08:00 | 44360.3333 | 0 | 10.0171 | 39.95
2021-06-13 08:30 | 44360.3542 | 0 | 9.6233 | 39.95
2021-06-13 09:00 | 44360.375 | 0 | 9.6849 | 39.95
2021-06-13 09:30 | 44360.3958 | 0 | 8.9109 | 39.95
2021-06-13 10:00 | 44360.4167 | 0 | 8.0357 | 39.95
2021-06-13 10:30 | 44360.4375 | 0 | 7.8074 | 39.95
2021-06-13 11:00 | 44360.4583 | 0 | 7.0866 | 39.95
2021-06-13 11:30 | 44360.4792 | 0 | 6.7189 | 39.95
2021-06-13 12:00 | 44360.5 | 0 | 6.3699 | 39.95
2021-06-13 12:30 | 44360.5208 | 0 | 6.2557 | 39.95
2021-06-13 13:00 | 44360.5417 | 0 | 6.4387 | 39.95
2021-06-13 13:30 | 44360.5625 | 0 | 6.6408 | 39.95
2021-06-13 14:00 | 44360.5833 | 0 | 7.271 | 39.95
2021-06-13 14:30 | 44360.6042 | 0 | 7.7846 | 39.95
2021-06-13 15:00 | 44360.625 | 0 | 8.4245 | 39.95
2021-06-13 15:30 | 44360.6458 | 0 | 9.2939 | 39.95
2021-06-13 16:00 | 44360.6667 | 0 | 10.2818 | 39.95
2021-06-13 16:30 | 44360.6875 | 0 | 11.2854 | 39.95
2021-06-13 17:00 | 44360.7083 | 0 | 12.4415 | 39.95
2021-06-13 17:30 | 44360.7292 | 0 | 13.2284 | 39.95
2021-06-13 18:00 | 44360.75 | 0 | 13.4792 | 39.95
2021-06-13 18:30 | 44360.7708 | 0 | 13.5533 | 39.95
2021-06-13 19:00 | 44360.7917 | 0 | 13.1786 | 39.95
2021-06-13 19:30 | 44360.8125 | 0 | 12.9412 | 39.95
2021-06-13 20:00 | 44360.8333 | 0 | 12.7295 | 39.95
2021-06-13 20:30 | 44360.8542 | 0 | 12.1398 | 39.95
2021-06-13 21:00 | 44360.875 | 0 | 11.6559 | 39.95
2021-06-13 21:30 | 44360.8958 | 0 | 11.0825 | 39.95
2021-06-13 22:00 | 44360.9167 | 0 | 10.5143 | 39.95
2021-06-13 22:30 | 44360.9375 | 0 | 9.6417 | 39.95
2021-06-13 23:00 | 44360.9583 | 0 | 8.8305 | 39.95
2021-06-13 23:30 | 44360.9792 | 0 | 8.4572 | 39.95
2021-06-14 | 44361 | 0 | 8.1036 | 39.95
2021-06-14 00:30 | 44361.0208 | 0 | 7.9109 | 39.95
2021-06-14 01:00 | 44361.0417 | 0 | 7.6669 | 39.95
2021-06-14 01:30 | 44361.0625 | 0 | 7.5063 | 39.95
2021-06-14 02:00 | 44361.0833 | 0 | 7.6154 | 39.95
2021-06-14 02:30 | 44361.1042 | 0 | 7.4668 | 39.95
2021-06-14 03:00 | 44361.125 | 0 | 7.4565 | 39.95
2021-06-14 03:30 | 44361.1458 | 0 | 7.8214 | 39.95
2021-06-14 04:00 | 44361.1667 | 0 | 8.0793 | 39.95
2021-06-14 04:30 | 44361.1875 | 0 | 8.6428 | 39.95
2021-06-14 05:00 | 44361.2083 | 0 | 9.5348 | 39.95
2021-06-14 05:30 | 44361.2292 | 0 | 10.7069 | 39.95
2021-06-14 06:00 | 44361.25 | 0 | 12.718 | 39.95
2021-06-14 06:30 | 44361.2708 | 0 | 14.2438 | 39.95
2021-06-14 07:00 | 44361.2917 | 0 | 15.5918 | 39.95
2021-06-14 07:30 | 44361.3125 | 0 | 15.72 | 39.95
2021-06-14 08:00 | 44361.3333 | 0 | 15.2319 | 39.95
2021-06-14 08:30 | 44361.3542 | 0 | 13.7674 | 39.95
2021-06-14 09:00 | 44361.375 | 0 | 12.7446 | 39.95
2021-06-14 09:30 | 44361.3958 | 0 | 11.6473 | 39.95
2021-06-14 10:00 | 44361.4167 | 0 | 10.7313 | 39.95
2021-06-14 10:30 | 44361.4375 | 0 | 10.2361 | 39.95
2021-06-14 11:00 | 44361.4583 | 0 | 9.7069 | 39.95
2021-06-14 11:30 | 44361.4792 | 0 | 9.5635 | 39.95
2021-06-14 12:00 | 44361.5 | 0 | 9.4318 | 39.95
2021-06-14 12:30 | 44361.5208 | 0 | 9.4441 | 39.95
2021-06-14 13:00 | 44361.5417 | 0 | 9.5309 | 39.95
2021-06-14 13:30 | 44361.5625 | 0 | 9.7087 | 39.95
2021-06-14 14:00 | 44361.5833 | 0 | 10.109 | 39.95
2021-06-14 14:30 | 44361.6042 | 0 | 10.3643 | 39.95
2021-06-14 15:00 | 44361.625 | 0 | 10.7449 | 39.95
2021-06-14 15:30 | 44361.6458 | 0 | 11.4905 | 39.95
2021-06-14 16:00 | 44361.6667 | 0 | 12.1745 | 39.95
2021-06-14 16:30 | 44361.6875 | 0 | 13.0185 | 39.95
2021-06-14 17:00 | 44361.7083 | 0 | 14.317 | 39.95
2021-06-14 17:30 | 44361.7292 | 0 | 15.2891 | 39.95
2021-06-14 18:00 | 44361.75 | 0 | 15.5959 | 39.95
2021-06-14 18:30 | 44361.7708 | 0 | 15.784 | 39.95
2021-06-14 19:00 | 44361.7917 | 0 | 15.3571 | 39.95
2021-06-14 19:30 | 44361.8125 | 0 | 15.3132 | 39.95
2021-06-14 20:00 | 44361.8333 | 0 | 14.7366 | 39.95
2021-06-14 20:30 | 44361.8542 | 0 | 14.14 | 39.95
2021-06-14 21:00 | 44361.875 | 0 | 13.5283 | 39.95
2021-06-14 21:30 | 44361.8958 | 0 | 12.814 | 39.95
2021-06-14 22:00 | 44361.9167 | 0 | 11.9494 | 39.95
2021-06-14 22:30 | 44361.9375 | 0 | 10.9023 | 39.95
2021-06-14 23:00 | 44361.9583 | 0 | 10.3105 | 39.95
2021-06-14 23:30 | 44361.9792 | 0 | 9.8535 | 39.95
2021-06-15 | 44362 | 0 | 9.2349 | 39.95
2021-06-15 00:30 | 44362.0208 | 0 | 8.6408 | 39.95
2021-06-15 01:00 | 44362.0417 | 0 | 8.4718 | 39.95
2021-06-15 01:30 | 44362.0625 | 0 | 8.3195 | 39.95
2021-06-15 02:00 | 44362.0833 | 0 | 8.1737 | 39.95
2021-06-15 02:30 | 44362.1042 | 0 | 8.153 | 39.95
2021-06-15 03:00 | 44362.125 | 0 | 8.1239 | 39.95
2021-06-15 03:30 | 44362.1458 | 0 | 8.2216 | 39.95
2021-06-15 04:00 | 44362.1667 | 0 | 8.4877 | 39.95
2021-06-15 04:30 | 44362.1875 | 0 | 9.0769 | 39.95
2021-06-15 05:00 | 44362.2083 | 0 | 9.9519 | 39.95
2021-06-15 05:30 | 44362.2292 | 0 | 10.9818 | 39.95
2021-06-15 06:00 | 44362.25 | 0 | 12.3919 | 39.95
2021-06-15 06:30 | 44362.2708 | 0 | 13.9571 | 39.95
2021-06-15 07:00 | 44362.2917 | 0 | 15.0561 | 39.95
2021-06-15 07:30 | 44362.3125 | 0 | 14.4751 | 39.95
2021-06-15 08:00 | 44362.3333 | 0 | 13.3978 | 39.95
2021-06-15 08:30 | 44362.3542 | 0 | 13.0394 | 39.95
2021-06-15 09:00 | 44362.375 | 0 | 14.0261 | 39.95
2021-06-15 09:30 | 44362.3958 | 0 | 15.3601 | 39.95
2021-06-15 10:00 | 44362.4167 | 0 | 15.2004 | 39.95
2021-06-15 10:30 | 44362.4375 | 0 | 14.1729 | 39.95
2021-06-15 11:00 | 44362.4583 | 0 | 12.143 | 39.95
2021-06-15 11:30 | 44362.4792 | 0 | 9.9285 | 39.95
2021-06-15 12:00 | 44362.5 | 0 | 9.5945 | 39.95
2021-06-15 12:30 | 44362.5208 | 0 | 9.3797 | 39.95
2021-06-15 13:00 | 44362.5417 | 0 | 9.4613 | 39.95
2021-06-15 13:30 | 44362.5625 | 0 | 9.8573 | 39.95
2021-06-15 14:00 | 44362.5833 | 0 | 11.1871 | 39.95
2021-06-15 14:30 | 44362.6042 | 0 | 11.096 | 39.95
2021-06-15 15:00 | 44362.625 | 0 | 11.5319 | 39.95
2021-06-15 15:30 | 44362.6458 | 0 | 12.4221 | 39.95
2021-06-15 16:00 | 44362.6667 | 0 | 12.83 | 39.95
2021-06-15 16:30 | 44362.6875 | 0 | 13.1774 | 39.95
2021-06-15 17:00 | 44362.7083 | 0 | 14.2676 | 39.95
2021-06-15 17:30 | 44362.7292 | 0 | 15.0727 | 39.95
2021-06-15 18:00 | 44362.75 | 0 | 15.2583 | 39.95
2021-06-15 18:30 | 44362.7708 | 0 | 15.5949 | 39.95
2021-06-15 19:00 | 44362.7917 | 0 | 15.2588 | 39.95
2021-06-15 19:30 | 44362.8125 | 0 | 15.0994 | 39.95
2021-06-15 20:00 | 44362.8333 | 0 | 14.9502 | 39.95
2021-06-15 20:30 | 44362.8542 | 0 | 14.4006 | 39.95
2021-06-15 21:00 | 44362.875 | 0 | 13.6856 | 39.95
2021-06-15 21:30 | 44362.8958 | 0 | 12.9778 | 39.95
2021-06-15 22:00 | 44362.9167 | 0 | 12.2326 | 39.95
2021-06-15 22:30 | 44362.9375 | 0 | 11.1991 | 39.95
2021-06-15 23:00 | 44362.9583 | 0 | 10.4869 | 39.95
2021-06-15 23:30 | 44362.9792 | 0 | 9.8229 | 39.95
2021-06-16 | 44363 | 0 | 9.2752 | 39.95
2021-06-16 00:30 | 44363.0208 | 0 | 8.707 | 39.95
2021-06-16 01:00 | 44363.0417 | 0 | 8.5336 | 39.95
2021-06-16 01:30 | 44363.0625 | 0 | 8.4048 | 39.95
2021-06-16 02:00 | 44363.0833 | 0 | 8.2274 | 39.95
2021-06-16 02:30 | 44363.1042 | 0 | 8.1886 | 39.95
2021-06-16 03:00 | 44363.125 | 0 | 8.1119 | 39.95
2021-06-16 03:30 | 44363.1458 | 0 | 8.2958 | 39.95
2021-06-16 04:00 | 44363.1667 | 0 | 8.5779 | 39.95
2021-06-16 04:30 | 44363.1875 | 0 | 9.0549 | 39.95
2021-06-16 05:00 | 44363.2083 | 0 | 9.9073 | 39.95
2021-06-16 05:30 | 44363.2292 | 0 | 11.0271 | 39.95
2021-06-16 06:00 | 44363.25 | 0 | 12.4394 | 39.95
2021-06-16 06:30 | 44363.2708 | 0 | 14.0549 | 39.95
2021-06-16 07:00 | 44363.2917 | 0 | 14.8291 | 39.95
2021-06-16 07:30 | 44363.3125 | 0 | 14.8895 | 39.95
2021-06-16 08:00 | 44363.3333 | 0 | 14.4641 | 39.95
2021-06-16 08:30 | 44363.3542 | 0 | 13.8081 | 39.95
2021-06-16 09:00 | 44363.375 | 0 | 12.1361 | 39.95
2021-06-16 09:30 | 44363.3958 | 0 | 11.0574 | 39.95
2021-06-16 10:00 | 44363.4167 | 0 | 10.5035 | 39.95
2021-06-16 10:30 | 44363.4375 | 0 | 10.0772 | 39.95
2021-06-16 11:00 | 44363.4583 | 0 | 9.6566 | 39.95
2021-06-16 11:30 | 44363.4792 | 0 | 9.5584 | 39.95
2021-06-16 12:00 | 44363.5 | 0 | 9.3926 | 39.95
2021-06-16 12:30 | 44363.5208 | 0 | 9.2755 | 39.95
2021-06-16 13:00 | 44363.5417 | 0 | 9.4785 | 39.95
2021-06-16 13:30 | 44363.5625 | 0 | 10.0991 | 39.95
2021-06-16 14:00 | 44363.5833 | 0 | 10.5114 | 39.95
2021-06-16 14:30 | 44363.6042 | 0 | 11.0367 | 39.95
2021-06-16 15:00 | 44363.625 | 0 | 11.144 | 39.95
2021-06-16 15:30 | 44363.6458 | 0 | 12.0317 | 39.95
2021-06-16 16:00 | 44363.6667 | 0 | 12.4352 | 39.95
2021-06-16 16:30 | 44363.6875 | 0 | 13.3142 | 39.95
2021-06-16 17:00 | 44363.7083 | 0 | 14.1492 | 39.95
2021-06-16 17:30 | 44363.7292 | 0 | 14.5907 | 39.95
2021-06-16 18:00 | 44363.75 | 0 | 14.7421 | 39.95
2021-06-16 18:30 | 44363.7708 | 0 | 15.116 | 39.95
2021-06-16 19:00 | 44363.7917 | 0 | 14.8661 | 39.95
2021-06-16 19:30 | 44363.8125 | 0 | 14.741 | 39.95
2021-06-16 20:00 | 44363.8333 | 0 | 14.4291 | 39.95
2021-06-16 20:30 | 44363.8542 | 0 | 13.8836 | 39.95
2021-06-16 21:00 | 44363.875 | 0 | 13.2723 | 39.95
2021-06-16 21:30 | 44363.8958 | 0 | 12.5888 | 39.95
2021-06-16 22:00 | 44363.9167 | 0 | 11.8627 | 39.95
2021-06-16 22:30 | 44363.9375 | 0 | 10.9669 | 39.95
2021-06-16 23:00 | 44363.9583 | 0 | 10.1912 | 39.95
2021-06-16 23:30 | 44363.9792 | 0 | 9.7851 | 39.95
2021-06-17 | 44364 | 0 | 9.0535 | 39.95
2021-06-17 00:30 | 44364.0208 | 0 | 8.7859 | 39.95
2021-06-17 01:00 | 44364.0417 | 0 | 8.5637 | 39.95
2021-06-17 01:30 | 44364.0625 | 0 | 8.3629 | 39.95
2021-06-17 02:00 | 44364.0833 | 0 | 8.2376 | 39.95
2021-06-17 02:30 | 44364.1042 | 0 | 8.05 | 39.95
2021-06-17 03:00 | 44364.125 | 0 | 8.0595 | 39.95
2021-06-17 03:30 | 44364.1458 | 0 | 8.2187 | 39.95
2021-06-17 04:00 | 44364.1667 | 0 | 8.4117 | 39.95
2021-06-17 04:30 | 44364.1875 | 0 | 8.9162 | 39.95
2021-06-17 05:00 | 44364.2083 | 0 | 9.5986 | 39.95
2021-06-17 05:30 | 44364.2292 | 0 | 10.4977 | 39.95
2021-06-17 06:00 | 44364.25 | 0 | 11.736 | 39.95
2021-06-17 06:30 | 44364.2708 | 0 | 12.8912 | 39.95
2021-06-17 07:00 | 44364.2917 | 0 | 13.417 | 39.95
2021-06-17 07:30 | 44364.3125 | 0 | 13.2708 | 39.95
2021-06-17 08:00 | 44364.3333 | 0 | 12.6618 | 39.95
2021-06-17 08:30 | 44364.3542 | 0 | 11.6767 | 39.95
2021-06-17 09:00 | 44364.375 | 0 | 10.9178 | 39.95
2021-06-17 09:30 | 44364.3958 | 0 | 10.3521 | 39.95
2021-06-17 10:00 | 44364.4167 | 0 | 9.8013 | 39.95
2021-06-17 10:30 | 44364.4375 | 0 | 9.5163 | 39.95
2021-06-17 11:00 | 44364.4583 | 0 | 9.1905 | 39.95
2021-06-17 11:30 | 44364.4792 | 0 | 9.1736 | 39.95
2021-06-17 12:00 | 44364.5 | 0 | 8.8291 | 39.95
2021-06-17 12:30 | 44364.5208 | 0 | 9.0594 | 39.95
2021-06-17 13:00 | 44364.5417 | 0 | 9.2142 | 39.95
2021-06-17 13:30 | 44364.5625 | 0 | 9.4716 | 39.95
2021-06-17 14:00 | 44364.5833 | 0 | 9.7176 | 39.95
2021-06-17 14:30 | 44364.6042 | 0 | 10.35 | 39.95
2021-06-17 15:00 | 44364.625 | 0 | 10.843 | 39.95
2021-06-17 15:30 | 44364.6458 | 0 | 11.6171 | 39.95
2021-06-17 16:00 | 44364.6667 | 0 | 12.2496 | 39.95
2021-06-17 16:30 | 44364.6875 | 0 | 12.8054 | 39.95
2021-06-17 17:00 | 44364.7083 | 0 | 13.5933 | 39.95
2021-06-17 17:30 | 44364.7292 | 0 | 14.2912 | 39.95
2021-06-17 18:00 | 44364.75 | 0 | 14.2602 | 39.95
2021-06-17 18:30 | 44364.7708 | 0 | 14.5011 | 39.95
2021-06-17 19:00 | 44364.7917 | 0 | 13.975 | 39.95
2021-06-17 19:30 | 44364.8125 | 0 | 14.1263 | 39.95
2021-06-17 20:00 | 44364.8333 | 0 | 13.9206 | 39.95
2021-06-17 20:30 | 44364.8542 | 0 | 13.3784 | 39.95
2021-06-17 21:00 | 44364.875 | 0 | 12.9273 | 39.95
2021-06-17 21:30 | 44364.8958 | 0 | 12.394 | 39.95
2021-06-17 22:00 | 44364.9167 | 0 | 11.7316 | 39.95
2021-06-17 22:30 | 44364.9375 | 0 | 10.7994 | 39.95
2021-06-17 23:00 | 44364.9583 | 0 | 10.1882 | 39.95
2021-06-17 23:30 | 44364.9792 | 0 | 9.6892 | 39.95
2021-06-18 | 44365 | 0 | 9.0318 | 39.95
2021-06-18 00:30 | 44365.0208 | 0 | 8.7538 | 39.95
2021-06-18 01:00 | 44365.0417 | 0 | 8.3819 | 39.95
2021-06-18 01:30 | 44365.0625 | 0 | 8.2161 | 39.95
2021-06-18 02:00 | 44365.0833 | 0 | 8.2282 | 39.95
2021-06-18 02:30 | 44365.1042 | 0 | 8.0475 | 39.95
2021-06-18 03:00 | 44365.125 | 0 | 8.0398 | 39.95
2021-06-18 03:30 | 44365.1458 | 0 | 8.2016 | 39.95
2021-06-18 04:00 | 44365.1667 | 0 | 8.471 | 39.95
2021-06-18 04:30 | 44365.1875 | 0 | 8.9362 | 39.95
2021-06-18 05:00 | 44365.2083 | 0 | 9.6881 | 39.95
2021-06-18 05:30 | 44365.2292 | 0 | 10.6615 | 39.95
2021-06-18 06:00 | 44365.25 | 0 | 11.9997 | 39.95
2021-06-18 06:30 | 44365.2708 | 0 | 13.3629 | 39.95
2021-06-18 07:00 | 44365.2917 | 0 | 14.4104 | 39.95
2021-06-18 07:30 | 44365.3125 | 0 | 14.3627 | 39.95
2021-06-18 08:00 | 44365.3333 | 0 | 13.0814 | 39.95
2021-06-18 08:30 | 44365.3542 | 0 | 11.9939 | 39.95
2021-06-18 09:00 | 44365.375 | 0 | 11.2648 | 39.95
2021-06-18 09:30 | 44365.3958 | 0 | 10.6025 | 39.95
2021-06-18 10:00 | 44365.4167 | 0 | 9.7662 | 39.95
2021-06-18 10:30 | 44365.4375 | 0 | 9.6554 | 39.95
2021-06-18 11:00 | 44365.4583 | 0 | 9.1324 | 39.95
2021-06-18 11:30 | 44365.4792 | 0 | 8.891 | 39.95
2021-06-18 12:00 | 44365.5 | 0 | 8.7117 | 39.95
2021-06-18 12:30 | 44365.5208 | 0 | 8.5809 | 39.95
2021-06-18 13:00 | 44365.5417 | 0 | 9.043 | 39.95
2021-06-18 13:30 | 44365.5625 | 0 | 9.1238 | 39.95
2021-06-18 14:00 | 44365.5833 | 0 | 9.6433 | 39.95
2021-06-18 14:30 | 44365.6042 | 0 | 10.1079 | 39.95
2021-06-18 15:00 | 44365.625 | 0 | 10.8994 | 39.95
2021-06-18 15:30 | 44365.6458 | 0 | 11.5151 | 39.95
2021-06-18 16:00 | 44365.6667 | 0 | 12.1649 | 39.95
2021-06-18 16:30 | 44365.6875 | 0 | 12.8614 | 39.95
2021-06-18 17:00 | 44365.7083 | 0 | 13.7712 | 39.95
2021-06-18 17:30 | 44365.7292 | 0 | 14.305 | 39.95
2021-06-18 18:00 | 44365.75 | 0 | 14.3625 | 39.95
2021-06-18 18:30 | 44365.7708 | 0 | 14.5892 | 39.95
2021-06-18 19:00 | 44365.7917 | 0 | 14.347 | 39.95
2021-06-18 19:30 | 44365.8125 | 0 | 14.3548 | 39.95
2021-06-18 20:00 | 44365.8333 | 0 | 14.0805 | 39.95
2021-06-18 20:30 | 44365.8542 | 0 | 13.5547 | 39.95
2021-06-18 21:00 | 44365.875 | 0 | 13.0599 | 39.95
2021-06-18 21:30 | 44365.8958 | 0 | 12.3843 | 39.95
2021-06-18 22:00 | 44365.9167 | 0 | 11.9553 | 39.95
2021-06-18 22:30 | 44365.9375 | 0 | 11.0452 | 39.95
2021-06-18 23:00 | 44365.9583 | 0 | 10.4071 | 39.95
2021-06-18 23:30 | 44365.9792 | 0 | 9.8862 | 39.95
2021-06-19 | 44366 | 0 | 9.14 | 39.95
2021-06-19 00:30 | 44366.0208 | 0 | 8.6722 | 39.95
2021-06-19 01:00 | 44366.0417 | 0 | 8.469 | 39.95
2021-06-19 01:30 | 44366.0625 | 0 | 8.2284 | 39.95
2021-06-19 02:00 | 44366.0833 | 0 | 8.1585 | 39.95
2021-06-19 02:30 | 44366.1042 | 0 | 8.0793 | 39.95
2021-06-19 03:00 | 44366.125 | 0 | 8.02 | 39.95
2021-06-19 03:30 | 44366.1458 | 0 | 8.1915 | 39.95
2021-06-19 04:00 | 44366.1667 | 0 | 8.178 | 39.95
2021-06-19 04:30 | 44366.1875 | 0 | 8.2705 | 39.95
2021-06-19 05:00 | 44366.2083 | 0 | 8.6516 | 39.95
2021-06-19 05:30 | 44366.2292 | 0 | 9.0422 | 39.95
2021-06-19 06:00 | 44366.25 | 0 | 9.6334 | 39.95
2021-06-19 06:30 | 44366.2708 | 0 | 10.3016 | 39.95
2021-06-19 07:00 | 44366.2917 | 0 | 11.032 | 39.95
2021-06-19 07:30 | 44366.3125 | 0 | 10.9203 | 39.95
2021-06-19 08:00 | 44366.3333 | 0 | 10.6919 | 39.95
2021-06-19 08:30 | 44366.3542 | 0 | 10.167 | 39.95
2021-06-19 09:00 | 44366.375 | 0 | 9.4515 | 39.95
2021-06-19 09:30 | 44366.3958 | 0 | 8.9527 | 39.95
2021-06-19 10:00 | 44366.4167 | 0 | 8.2963 | 39.95
2021-06-19 10:30 | 44366.4375 | 0 | 7.7531 | 39.95
2021-06-19 11:00 | 44366.4583 | 0 | 7.4943 | 39.95
2021-06-19 11:30 | 44366.4792 | 0 | 7.0461 | 39.95
2021-06-19 12:00 | 44366.5 | 0 | 6.9206 | 39.95
2021-06-19 12:30 | 44366.5208 | 0 | 6.9008 | 39.95
2021-06-19 13:00 | 44366.5417 | 0 | 7.1021 | 39.95
2021-06-19 13:30 | 44366.5625 | 0 | 7.2383 | 39.95
2021-06-19 14:00 | 44366.5833 | 0 | 7.6311 | 39.95
2021-06-19 14:30 | 44366.6042 | 0 | 8.0113 | 39.95
2021-06-19 15:00 | 44366.625 | 0 | 8.6654 | 39.95
2021-06-19 15:30 | 44366.6458 | 0 | 9.4712 | 39.95
2021-06-19 16:00 | 44366.6667 | 0 | 10.3744 | 39.95
2021-06-19 16:30 | 44366.6875 | 0 | 11.6194 | 39.95
2021-06-19 17:00 | 44366.7083 | 0 | 12.6924 | 39.95
2021-06-19 17:30 | 44366.7292 | 0 | 13.2604 | 39.95
2021-06-19 18:00 | 44366.75 | 0 | 13.6126 | 39.95
2021-06-19 18:30 | 44366.7708 | 0 | 13.9713 | 39.95
2021-06-19 19:00 | 44366.7917 | 0 | 13.7466 | 39.95
2021-06-19 19:30 | 44366.8125 | 0 | 13.5234 | 39.95
2021-06-19 20:00 | 44366.8333 | 0 | 13.1513 | 39.95
2021-06-19 20:30 | 44366.8542 | 0 | 12.6232 | 39.95
2021-06-19 21:00 | 44366.875 | 0 | 12.0858 | 39.95
2021-06-19 21:30 | 44366.8958 | 0 | 11.6671 | 39.95
2021-06-19 22:00 | 44366.9167 | 0 | 11.0491 | 39.95
2021-06-19 22:30 | 44366.9375 | 0 | 10.1835 | 39.95
2021-06-19 23:00 | 44366.9583 | 0 | 9.6127 | 39.95
2021-06-19 23:30 | 44366.9792 | 0 | 9.0449 | 39.95
2021-06-20 | 44367 | 0 | 8.583 | 39.95
2021-06-20 00:30 | 44367.0208 | 0 | 8.186 | 39.95
2021-06-20 01:00 | 44367.0417 | 0 | 7.7454 | 39.95
2021-06-20 01:30 | 44367.0625 | 0 | 7.6801 | 39.95
2021-06-20 02:00 | 44367.0833 | 0 | 7.6106 | 39.95
2021-06-20 02:30 | 44367.1042 | 0 | 7.3972 | 39.95
2021-06-20 03:00 | 44367.125 | 0 | 7.4093 | 39.95
2021-06-20 03:30 | 44367.1458 | 0 | 7.4445 | 39.95
2021-06-20 04:00 | 44367.1667 | 0 | 7.4712 | 39.95
2021-06-20 04:30 | 44367.1875 | 0 | 7.4445 | 39.95
2021-06-20 05:00 | 44367.2083 | 0 | 7.6275 | 39.95
2021-06-20 05:30 | 44367.2292 | 0 | 7.921 | 39.95
2021-06-20 06:00 | 44367.25 | 0 | 8.4636 | 39.95
2021-06-20 06:30 | 44367.2708 | 0 | 8.853 | 39.95
2021-06-20 07:00 | 44367.2917 | 0 | 9.3649 | 39.95
2021-06-20 07:30 | 44367.3125 | 0 | 9.6292 | 39.95
2021-06-20 08:00 | 44367.3333 | 0 | 9.4215 | 39.95
2021-06-20 08:30 | 44367.3542 | 0 | 9.0327 | 39.95
2021-06-20 09:00 | 44367.375 | 0 | 8.3971 | 39.95
2021-06-20 09:30 | 44367.3958 | 0 | 7.9856 | 39.95
2021-06-20 10:00 | 44367.4167 | 0 | 7.4788 | 39.95
2021-06-20 10:30 | 44367.4375 | 0 | 6.9406 | 39.95
2021-06-20 11:00 | 44367.4583 | 0 | 6.4242 | 39.95
2021-06-20 11:30 | 44367.4792 | 0 | 6.4937 | 39.95
2021-06-20 12:00 | 44367.5 | 0 | 6.4395 | 39.95
2021-06-20 12:30 | 44367.5208 | 0 | 6.345 | 39.95
2021-06-20 13:00 | 44367.5417 | 0 | 6.3794 | 39.95
2021-06-20 13:30 | 44367.5625 | 0 | 6.671 | 39.95
2021-06-20 14:00 | 44367.5833 | 0 | 7.06 | 39.95
2021-06-20 14:30 | 44367.6042 | 0 | 7.7425 | 39.95
2021-06-20 15:00 | 44367.625 | 0 | 8.5236 | 39.95
2021-06-20 15:30 | 44367.6458 | 0 | 9.0761 | 39.95
2021-06-20 16:00 | 44367.6667 | 0 | 9.5958 | 39.95
2021-06-20 16:30 | 44367.6875 | 0 | 10.822 | 39.95
2021-06-20 17:00 | 44367.7083 | 0 | 11.9287 | 39.95
2021-06-20 17:30 | 44367.7292 | 0 | 12.3659 | 39.95
2021-06-20 18:00 | 44367.75 | 0 | 12.5403 | 39.95
2021-06-20 18:30 | 44367.7708 | 0 | 12.4673 | 39.95
2021-06-20 19:00 | 44367.7917 | 0 | 12.203 | 39.95
2021-06-20 19:30 | 44367.8125 | 0 | 12.0854 | 39.95
2021-06-20 20:00 | 44367.8333 | 0 | 12.0121 | 39.95
2021-06-20 20:30 | 44367.8542 | 0 | 11.6129 | 39.95
2021-06-20 21:00 | 44367.875 | 0 | 11.0595 | 39.95
2021-06-20 21:30 | 44367.8958 | 0 | 10.6038 | 39.95
2021-06-20 22:00 | 44367.9167 | 0 | 10.0499 | 39.95
2021-06-20 22:30 | 44367.9375 | 0 | 9.1861 | 39.95
2021-06-20 23:00 | 44367.9583 | 0 | 8.6006 | 39.95
2021-06-20 23:30 | 44367.9792 | 0 | 8.1611 | 39.95
2021-06-21 | 44368 | 0 | 7.8348 | 39.95
2021-06-21 00:30 | 44368.0208 | 0 | 7.7265 | 39.95
2021-06-21 01:00 | 44368.0417 | 0 | 7.4049 | 39.95
2021-06-21 01:30 | 44368.0625 | 0 | 7.2501 | 39.95
2021-06-21 02:00 | 44368.0833 | 0 | 7.2934 | 39.95
2021-06-21 02:30 | 44368.1042 | 0 | 7.2303 | 39.95
2021-06-21 03:00 | 44368.125 | 0 | 7.2389 | 39.95
2021-06-21 03:30 | 44368.1458 | 0 | 7.5213 | 39.95
2021-06-21 04:00 | 44368.1667 | 0 | 7.8334 | 39.95
2021-06-21 04:30 | 44368.1875 | 0 | 8.3445 | 39.95
2021-06-21 05:00 | 44368.2083 | 0 | 9.2523 | 39.95
2021-06-21 05:30 | 44368.2292 | 0 | 10.2262 | 39.95
2021-06-21 06:00 | 44368.25 | 0 | 11.8662 | 39.95
2021-06-21 06:30 | 44368.2708 | 0 | 13.379 | 39.95
2021-06-21 07:00 | 44368.2917 | 0 | 14.1888 | 39.95
2021-06-21 07:30 | 44368.3125 | 0 | 14.2336 | 39.95
2021-06-21 08:00 | 44368.3333 | 0 | 13.5208 | 39.95
2021-06-21 08:30 | 44368.3542 | 0 | 12.3042 | 39.95
2021-06-21 09:00 | 44368.375 | 0 | 11.2979 | 39.95
2021-06-21 09:30 | 44368.3958 | 0 | 10.6744 | 39.95
2021-06-21 10:00 | 44368.4167 | 0 | 9.9907 | 39.95
2021-06-21 10:30 | 44368.4375 | 0 | 9.5927 | 39.95
2021-06-21 11:00 | 44368.4583 | 0 | 9.245 | 39.95
2021-06-21 11:30 | 44368.4792 | 0 | 9.1592 | 39.95
2021-06-21 12:00 | 44368.5 | 0 | 8.9829 | 39.95
2021-06-21 12:30 | 44368.5208 | 0 | 9.0742 | 39.95
2021-06-21 13:00 | 44368.5417 | 0 | 9.1395 | 39.95
2021-06-21 13:30 | 44368.5625 | 0 | 9.5518 | 39.95
2021-06-21 14:00 | 44368.5833 | 0 | 10.1494 | 39.95
2021-06-21 14:30 | 44368.6042 | 0 | 10.3007 | 39.95
2021-06-21 15:00 | 44368.625 | 0 | 10.6453 | 39.95
2021-06-21 15:30 | 44368.6458 | 0 | 11.3401 | 39.95
2021-06-21 16:00 | 44368.6667 | 0 | 11.8503 | 39.95
2021-06-21 16:30 | 44368.6875 | 0 | 12.7489 | 39.95
2021-06-21 17:00 | 44368.7083 | 0 | 13.6639 | 39.95
2021-06-21 17:30 | 44368.7292 | 0 | 14.6165 | 39.95
2021-06-21 18:00 | 44368.75 | 0 | 14.9236 | 39.95
2021-06-21 18:30 | 44368.7708 | 0 | 14.7791 | 39.95
2021-06-21 19:00 | 44368.7917 | 0 | 14.576 | 39.95
2021-06-21 19:30 | 44368.8125 | 0 | 14.4691 | 39.95
2021-06-21 20:00 | 44368.8333 | 0 | 14.0945 | 39.95
2021-06-21 20:30 | 44368.8542 | 0 | 13.4428 | 39.95
2021-06-21 21:00 | 44368.875 | 0 | 12.8466 | 39.95
2021-06-21 21:30 | 44368.8958 | 0 | 12.3768 | 39.95
2021-06-21 22:00 | 44368.9167 | 0 | 11.6378 | 39.95
2021-06-21 22:30 | 44368.9375 | 0 | 10.8086 | 39.95
2021-06-21 23:00 | 44368.9583 | 0 | 10.0196 | 39.95
2021-06-21 23:30 | 44368.9792 | 0 | 9.554 | 39.95
2021-06-22 | 44369 | 0 | 8.9999 | 39.95
2021-06-22 00:30 | 44369.0208 | 0 | 8.5853 | 39.95
2021-06-22 01:00 | 44369.0417 | 0 | 8.288 | 39.95
2021-06-22 01:30 | 44369.0625 | 0 | 8.0767 | 39.95
2021-06-22 02:00 | 44369.0833 | 0 | 8.0149 | 39.95
2021-06-22 02:30 | 44369.1042 | 0 | 7.886 | 39.95
2021-06-22 03:00 | 44369.125 | 0 | 8.0097 | 39.95
2021-06-22 03:30 | 44369.1458 | 0 | 8.1093 | 39.95
2021-06-22 04:00 | 44369.1667 | 0 | 8.3825 | 39.95
2021-06-22 04:30 | 44369.1875 | 0 | 8.8993 | 39.95
2021-06-22 05:00 | 44369.2083 | 0 | 9.6976 | 39.95
2021-06-22 05:30 | 44369.2292 | 0 | 10.6116 | 39.95
2021-06-22 06:00 | 44369.25 | 0 | 12.0478 | 39.95
2021-06-22 06:30 | 44369.2708 | 0 | 13.4553 | 39.95
2021-06-22 07:00 | 44369.2917 | 0 | 14.2577 | 39.95
2021-06-22 07:30 | 44369.3125 | 0 | 13.9061 | 39.95
2021-06-22 08:00 | 44369.3333 | 0 | 13.0493 | 39.95
2021-06-22 08:30 | 44369.3542 | 0 | 11.9477 | 39.95
2021-06-22 09:00 | 44369.375 | 0 | 11.0044 | 39.95
2021-06-22 09:30 | 44369.3958 | 0 | 10.2984 | 39.95
2021-06-22 10:00 | 44369.4167 | 0 | 9.7668 | 39.95
2021-06-22 10:30 | 44369.4375 | 0 | 9.3488 | 39.95
2021-06-22 11:00 | 44369.4583 | 0 | 8.9558 | 39.95
2021-06-22 11:30 | 44369.4792 | 0 | 9.4992 | 39.95
2021-06-22 12:00 | 44369.5 | 0 | 10.2112 | 39.95
2021-06-22 12:30 | 44369.5208 | 0 | 9.7269 | 39.95
2021-06-22 13:00 | 44369.5417 | 0 | 9.6392 | 39.95
2021-06-22 13:30 | 44369.5625 | 0 | 11.1422 | 39.95
2021-06-22 14:00 | 44369.5833 | 0 | 10.5825 | 39.95
2021-06-22 14:30 | 44369.6042 | 0 | 11.0744 | 39.95
2021-06-22 15:00 | 44369.625 | 0 | 11.6179 | 39.95
2021-06-22 15:30 | 44369.6458 | 0 | 12.1311 | 39.95
2021-06-22 16:00 | 44369.6667 | 0 | 12.6876 | 39.95
2021-06-22 16:30 | 44369.6875 | 0 | 13.1435 | 39.95
2021-06-22 17:00 | 44369.7083 | 0 | 14.1033 | 39.95
2021-06-22 17:30 | 44369.7292 | 0 | 14.9658 | 39.95
2021-06-22 18:00 | 44369.75 | 0 | 15.1939 | 39.95
2021-06-22 18:30 | 44369.7708 | 0 | 15.3944 | 39.95
2021-06-22 19:00 | 44369.7917 | 0 | 15.1965 | 39.95
2021-06-22 19:30 | 44369.8125 | 0 | 14.9922 | 39.95
2021-06-22 20:00 | 44369.8333 | 0 | 14.5752 | 39.95
2021-06-22 20:30 | 44369.8542 | 0 | 13.9348 | 39.95
2021-06-22 21:00 | 44369.875 | 0 | 13.1857 | 39.95
2021-06-22 21:30 | 44369.8958 | 0 | 12.4665 | 39.95
2021-06-22 22:00 | 44369.9167 | 0 | 11.9217 | 39.95
2021-06-22 22:30 | 44369.9375 | 0 | 10.9203 | 39.95
2021-06-22 23:00 | 44369.9583 | 0 | 10.1504 | 39.95
2021-06-22 23:30 | 44369.9792 | 0 | 9.6333 | 39.95
2021-06-23 | 44370 | 0 | 8.9076 | 39.95
2021-06-23 00:30 | 44370.0208 | 0 | 8.643 | 39.95
2021-06-23 01:00 | 44370.0417 | 0 | 8.3831 | 39.95
2021-06-23 01:30 | 44370.0625 | 0 | 8.1411 | 39.95
2021-06-23 02:00 | 44370.0833 | 0 | 8.1712 | 39.95
2021-06-23 02:30 | 44370.1042 | 0 | 8.0423 | 39.95
2021-06-23 03:00 | 44370.125 | 0 | 7.9805 | 39.95
2021-06-23 03:30 | 44370.1458 | 0 | 8.156 | 39.95
2021-06-23 04:00 | 44370.1667 | 0 | 8.489 | 39.95
2021-06-23 04:30 | 44370.1875 | 0 | 8.9449 | 39.95
2021-06-23 05:00 | 44370.2083 | 0 | 9.6281 | 39.95
2021-06-23 05:30 | 44370.2292 | 0 | 10.4121 | 39.95
2021-06-23 06:00 | 44370.25 | 0 | 11.946 | 39.95
2021-06-23 06:30 | 44370.2708 | 0 | 13.1518 | 39.95
2021-06-23 07:00 | 44370.2917 | 0 | 13.8863 | 39.95
2021-06-23 07:30 | 44370.3125 | 0 | 13.5562 | 39.95
2021-06-23 08:00 | 44370.3333 | 0 | 12.721 | 39.95
2021-06-23 08:30 | 44370.3542 | 0 | 11.9926 | 39.95
2021-06-23 09:00 | 44370.375 | 0 | 12.4893 | 39.95
2021-06-23 09:30 | 44370.3958 | 0 | 11.6124 | 39.95
2021-06-23 10:00 | 44370.4167 | 0 | 10.8013 | 39.95
2021-06-23 10:30 | 44370.4375 | 0 | 10.4734 | 39.95
2021-06-23 11:00 | 44370.4583 | 0 | 9.6813 | 39.95
2021-06-23 11:30 | 44370.4792 | 0 | 9.2851 | 39.95
2021-06-23 12:00 | 44370.5 | 0 | 9.11 | 39.95
2021-06-23 12:30 | 44370.5208 | 0 | 9.9756 | 39.95
2021-06-23 13:00 | 44370.5417 | 0 | 9.4648 | 39.95
2021-06-23 13:30 | 44370.5625 | 0 | 11.1389 | 39.95
2021-06-23 14:00 | 44370.5833 | 0 | 11.4916 | 39.95
2021-06-23 14:30 | 44370.6042 | 0 | 11.6103 | 39.95
2021-06-23 15:00 | 44370.625 | 0 | 11.5852 | 39.95
2021-06-23 15:30 | 44370.6458 | 0 | 12.0053 | 39.95
2021-06-23 16:00 | 44370.6667 | 0 | 12.435 | 39.95
2021-06-23 16:30 | 44370.6875 | 0 | 13.0462 | 39.95
2021-06-23 17:00 | 44370.7083 | 0 | 14.0759 | 39.95
2021-06-23 17:30 | 44370.7292 | 0 | 14.6371 | 39.95
2021-06-23 18:00 | 44370.75 | 0 | 14.7146 | 39.95
2021-06-23 18:30 | 44370.7708 | 0 | 14.8091 | 39.95
2021-06-23 19:00 | 44370.7917 | 0 | 14.5832 | 39.95
2021-06-23 19:30 | 44370.8125 | 0 | 14.31 | 39.95
2021-06-23 20:00 | 44370.8333 | 0 | 14.1407 | 39.95
2021-06-23 20:30 | 44370.8542 | 0 | 13.534 | 39.95
2021-06-23 21:00 | 44370.875 | 0 | 12.9279 | 39.95
2021-06-23 21:30 | 44370.8958 | 0 | 12.2952 | 39.95
2021-06-23 22:00 | 44370.9167 | 0 | 11.7655 | 39.95
2021-06-23 22:30 | 44370.9375 | 0 | 10.7426 | 39.95
2021-06-23 23:00 | 44370.9583 | 0 | 9.9967 | 39.95
2021-06-23 23:30 | 44370.9792 | 0 | 9.5738 | 39.95
2021-06-24 | 44371 | 0 | 9.0762 | 39.95
2021-06-24 00:30 | 44371.0208 | 0 | 8.5944 | 39.95
2021-06-24 01:00 | 44371.0417 | 0 | 8.3996 | 39.95
2021-06-24 01:30 | 44371.0625 | 0 | 8.099 | 39.95
2021-06-24 02:00 | 44371.0833 | 0 | 8.166 | 39.95
2021-06-24 02:30 | 44371.1042 | 0 | 8.0028 | 39.95
2021-06-24 03:00 | 44371.125 | 0 | 7.8662 | 39.95
2021-06-24 03:30 | 44371.1458 | 0 | 8.1887 | 39.95
2021-06-24 04:00 | 44371.1667 | 0 | 8.434 | 39.95
2021-06-24 04:30 | 44371.1875 | 0 | 8.906 | 39.95
2021-06-24 05:00 | 44371.2083 | 0 | 9.6037 | 39.95
2021-06-24 05:30 | 44371.2292 | 0 | 10.2749 | 39.95
2021-06-24 06:00 | 44371.25 | 0 | 11.4277 | 39.95
2021-06-24 06:30 | 44371.2708 | 0 | 12.5323 | 39.95
2021-06-24 07:00 | 44371.2917 | 0 | 13.4462 | 39.95
2021-06-24 07:30 | 44371.3125 | 0 | 13.3841 | 39.95
2021-06-24 08:00 | 44371.3333 | 0 | 12.7035 | 39.95
2021-06-24 08:30 | 44371.3542 | 0 | 12.651 | 39.95
2021-06-24 09:00 | 44371.375 | 0 | 12.8762 | 39.95
2021-06-24 09:30 | 44371.3958 | 0 | 12.1208 | 39.95
2021-06-24 10:00 | 44371.4167 | 0 | 11.3317 | 39.95
2021-06-24 10:30 | 44371.4375 | 0 | 10.6087 | 39.95
2021-06-24 11:00 | 44371.4583 | 0 | 10.053 | 39.95
2021-06-24 11:30 | 44371.4792 | 0 | 9.4216 | 39.95
2021-06-24 12:00 | 44371.5 | 0 | 10.1469 | 39.95
2021-06-24 12:30 | 44371.5208 | 0 | 9.887 | 39.95
2021-06-24 13:00 | 44371.5417 | 0 | 9.5886 | 39.95
2021-06-24 13:30 | 44371.5625 | 0 | 11.3319 | 39.95
2021-06-24 14:00 | 44371.5833 | 0 | 12.0372 | 39.95
2021-06-24 14:30 | 44371.6042 | 0 | 12.7322 | 39.95
2021-06-24 15:00 | 44371.625 | 0 | 12.5189 | 39.95
2021-06-24 15:30 | 44371.6458 | 0 | 12.7863 | 39.95
2021-06-24 16:00 | 44371.6667 | 0 | 12.9647 | 39.95
2021-06-24 16:30 | 44371.6875 | 0 | 13.3578 | 39.95
2021-06-24 17:00 | 44371.7083 | 0 | 14.0225 | 39.95
2021-06-24 17:30 | 44371.7292 | 0 | 14.3725 | 39.95
2021-06-24 18:00 | 44371.75 | 0 | 14.3024 | 39.95
2021-06-24 18:30 | 44371.7708 | 0 | 14.467 | 39.95
2021-06-24 19:00 | 44371.7917 | 0 | 14.2412 | 39.95
2021-06-24 19:30 | 44371.8125 | 0 | 14.0349 | 39.95
2021-06-24 20:00 | 44371.8333 | 0 | 13.655 | 39.95
2021-06-24 20:30 | 44371.8542 | 0 | 13.1814 | 39.95
2021-06-24 21:00 | 44371.875 | 0 | 12.6782 | 39.95
2021-06-24 21:30 | 44371.8958 | 0 | 12.1051 | 39.95
2021-06-24 22:00 | 44371.9167 | 0 | 11.5751 | 39.95
2021-06-24 22:30 | 44371.9375 | 0 | 10.7244 | 39.95
2021-06-24 23:00 | 44371.9583 | 0 | 10.1043 | 39.95
2021-06-24 23:30 | 44371.9792 | 0 | 9.6308 | 39.95
2021-06-25 | 44372 | 0 | 9.0855 | 39.95
2021-06-25 00:30 | 44372.0208 | 0 | 8.6233 | 39.95
2021-06-25 01:00 | 44372.0417 | 0 | 8.3575 | 39.95
2021-06-25 01:30 | 44372.0625 | 0 | 8.2722 | 39.95
2021-06-25 02:00 | 44372.0833 | 0 | 8.2135 | 39.95
2021-06-25 02:30 | 44372.1042 | 0 | 8.1844 | 39.95
2021-06-25 03:00 | 44372.125 | 0 | 8.235 | 39.95
2021-06-25 03:30 | 44372.1458 | 0 | 8.2514 | 39.95
2021-06-25 04:00 | 44372.1667 | 0 | 8.4117 | 39.95
2021-06-25 04:30 | 44372.1875 | 0 | 8.8718 | 39.95
2021-06-25 05:00 | 44372.2083 | 0 | 9.484 | 39.95
2021-06-25 05:30 | 44372.2292 | 0 | 9.9618 | 39.95
2021-06-25 06:00 | 44372.25 | 0 | 11.0649 | 39.95
2021-06-25 06:30 | 44372.2708 | 0 | 12.3729 | 39.95
2021-06-25 07:00 | 44372.2917 | 0 | 13.3693 | 39.95
2021-06-25 07:30 | 44372.3125 | 0 | 13.9353 | 39.95
2021-06-25 08:00 | 44372.3333 | 0 | 13.7151 | 39.95
2021-06-25 08:30 | 44372.3542 | 0 | 13.2656 | 39.95
2021-06-25 09:00 | 44372.375 | 0 | 13.2738 | 39.95
2021-06-25 09:30 | 44372.3958 | 0 | 13.2012 | 39.95
2021-06-25 10:00 | 44372.4167 | 0 | 12.8486 | 39.95
2021-06-25 10:30 | 44372.4375 | 0 | 13.4793 | 39.95
2021-06-25 11:00 | 44372.4583 | 0 | 13.5378 | 39.95
2021-06-25 11:30 | 44372.4792 | 0 | 13.0791 | 39.95
2021-06-25 12:00 | 44372.5 | 0 | 12.7717 | 39.95
2021-06-25 12:30 | 44372.5208 | 0 | 12.6849 | 39.95
2021-06-25 13:00 | 44372.5417 | 0 | 12.7995 | 39.95
2021-06-25 13:30 | 44372.5625 | 0 | 12.7863 | 39.95
2021-06-25 14:00 | 44372.5833 | 0 | 12.7969 | 39.95
2021-06-25 14:30 | 44372.6042 | 0 | 12.9976 | 39.95
2021-06-25 15:00 | 44372.625 | 0 | 13.1036 | 39.95
2021-06-25 15:30 | 44372.6458 | 0 | 13.3197 | 39.95
2021-06-25 16:00 | 44372.6667 | 0 | 13.4216 | 39.95
2021-06-25 16:30 | 44372.6875 | 0 | 14.1863 | 39.95
2021-06-25 17:00 | 44372.7083 | 0 | 14.2973 | 39.95
2021-06-25 17:30 | 44372.7292 | 0 | 14.5311 | 39.95
2021-06-25 18:00 | 44372.75 | 0 | 14.2456 | 39.95
2021-06-25 18:30 | 44372.7708 | 0 | 14.1915 | 39.95
2021-06-25 19:00 | 44372.7917 | 0 | 13.8534 | 39.95
2021-06-25 19:30 | 44372.8125 | 0 | 13.7071 | 39.95
2021-06-25 20:00 | 44372.8333 | 0 | 13.4966 | 39.95
2021-06-25 20:30 | 44372.8542 | 0 | 13.3904 | 39.95
2021-06-25 21:00 | 44372.875 | 0 | 12.6087 | 39.95
2021-06-25 21:30 | 44372.8958 | 0 | 12.1675 | 39.95
2021-06-25 22:00 | 44372.9167 | 0 | 11.6144 | 39.95
2021-06-25 22:30 | 44372.9375 | 0 | 10.6071 | 39.95
2021-06-25 23:00 | 44372.9583 | 0 | 10.0467 | 39.95
2021-06-25 23:30 | 44372.9792 | 0 | 9.5953 | 39.95
2021-06-26 | 44373 | 0 | 8.9522 | 39.95
2021-06-26 00:30 | 44373.0208 | 0 | 8.5456 | 39.95
2021-06-26 01:00 | 44373.0417 | 0 | 8.2402 | 39.95
2021-06-26 01:30 | 44373.0625 | 0 | 8.0054 | 39.95
2021-06-26 02:00 | 44373.0833 | 0 | 7.953 | 39.95
2021-06-26 02:30 | 44373.1042 | 0 | 7.7472 | 39.95
2021-06-26 03:00 | 44373.125 | 0 | 7.7197 | 39.95
2021-06-26 03:30 | 44373.1458 | 0 | 7.5999 | 39.95
2021-06-26 04:00 | 44373.1667 | 0 | 7.6773 | 39.95
2021-06-26 04:30 | 44373.1875 | 0 | 7.6973 | 39.95
2021-06-26 05:00 | 44373.2083 | 0 | 8.0699 | 39.95
2021-06-26 05:30 | 44373.2292 | 0 | 8.2009 | 39.95
2021-06-26 06:00 | 44373.25 | 0 | 8.6156 | 39.95
2021-06-26 06:30 | 44373.2708 | 0 | 9.0589 | 39.95
2021-06-26 07:00 | 44373.2917 | 0 | 9.6378 | 39.95
2021-06-26 07:30 | 44373.3125 | 0 | 10.149 | 39.95
2021-06-26 08:00 | 44373.3333 | 0 | 10.797 | 39.95
2021-06-26 08:30 | 44373.3542 | 0 | 11.6528 | 39.95
2021-06-26 09:00 | 44373.375 | 0 | 11.7696 | 39.95
2021-06-26 09:30 | 44373.3958 | 0 | 11.8292 | 39.95
2021-06-26 10:00 | 44373.4167 | 0 | 11.9803 | 39.95
2021-06-26 10:30 | 44373.4375 | 0 | 11.858 | 39.95
2021-06-26 11:00 | 44373.4583 | 0 | 12.0027 | 39.95
2021-06-26 11:30 | 44373.4792 | 0 | 11.8065 | 39.95
2021-06-26 12:00 | 44373.5 | 0 | 11.6551 | 39.95
2021-06-26 12:30 | 44373.5208 | 0 | 11.2657 | 39.95
2021-06-26 13:00 | 44373.5417 | 0 | 10.5489 | 39.95
2021-06-26 13:30 | 44373.5625 | 0 | 11.0728 | 39.95
2021-06-26 14:00 | 44373.5833 | 0 | 11.1688 | 39.95
2021-06-26 14:30 | 44373.6042 | 0 | 11.4118 | 39.95
2021-06-26 15:00 | 44373.625 | 0 | 11.7917 | 39.95
2021-06-26 15:30 | 44373.6458 | 0 | 12.2031 | 39.95
2021-06-26 16:00 | 44373.6667 | 0 | 12.3053 | 39.95
2021-06-26 16:30 | 44373.6875 | 0 | 12.7723 | 39.95
2021-06-26 17:00 | 44373.7083 | 0 | 13.2656 | 39.95
2021-06-26 17:30 | 44373.7292 | 0 | 13.3945 | 39.95
2021-06-26 18:00 | 44373.75 | 0 | 13.4277 | 39.95
2021-06-26 18:30 | 44373.7708 | 0 | 13.2973 | 39.95
2021-06-26 19:00 | 44373.7917 | 0 | 12.8769 | 39.95
2021-06-26 19:30 | 44373.8125 | 0 | 12.66 | 39.95
2021-06-26 20:00 | 44373.8333 | 0 | 12.4862 | 39.95
2021-06-26 20:30 | 44373.8542 | 0 | 11.8784 | 39.95
2021-06-26 21:00 | 44373.875 | 0 | 11.3427 | 39.95
2021-06-26 21:30 | 44373.8958 | 0 | 10.9456 | 39.95
2021-06-26 22:00 | 44373.9167 | 0 | 10.5346 | 39.95
2021-06-26 22:30 | 44373.9375 | 0 | 9.8763 | 39.95
2021-06-26 23:00 | 44373.9583 | 0 | 9.2755 | 39.95
2021-06-26 23:30 | 44373.9792 | 0 | 8.8434 | 39.95
2021-06-27 | 44374 | 0 | 8.2694 | 39.95
2021-06-27 00:30 | 44374.0208 | 0 | 7.9228 | 39.95
2021-06-27 01:00 | 44374.0417 | 0 | 7.618 | 39.95
2021-06-27 01:30 | 44374.0625 | 0 | 7.4247 | 39.95
2021-06-27 02:00 | 44374.0833 | 0 | 7.4737 | 39.95
2021-06-27 02:30 | 44374.1042 | 0 | 7.417 | 39.95
2021-06-27 03:00 | 44374.125 | 0 | 7.283 | 39.95
2021-06-27 03:30 | 44374.1458 | 0 | 7.2804 | 39.95
2021-06-27 04:00 | 44374.1667 | 0 | 7.3053 | 39.95
2021-06-27 04:30 | 44374.1875 | 0 | 7.3449 | 39.95
2021-06-27 05:00 | 44374.2083 | 0 | 7.5631 | 39.95
2021-06-27 05:30 | 44374.2292 | 0 | 7.8663 | 39.95
2021-06-27 06:00 | 44374.25 | 0 | 8.2959 | 39.95
2021-06-27 06:30 | 44374.2708 | 0 | 8.624 | 39.95
2021-06-27 07:00 | 44374.2917 | 0 | 9.1821 | 39.95
2021-06-27 07:30 | 44374.3125 | 0 | 9.8293 | 39.95
2021-06-27 08:00 | 44374.3333 | 0 | 10.5642 | 39.95
2021-06-27 08:30 | 44374.3542 | 0 | 10.852 | 39.95
2021-06-27 09:00 | 44374.375 | 0 | 10.2796 | 39.95
2021-06-27 09:30 | 44374.3958 | 0 | 8.5289 | 39.95
2021-06-27 10:00 | 44374.4167 | 0 | 7.7699 | 39.95
2021-06-27 10:30 | 44374.4375 | 0 | 7.2412 | 39.95
2021-06-27 11:00 | 44374.4583 | 0 | 6.8887 | 39.95
2021-06-27 11:30 | 44374.4792 | 0 | 6.5325 | 39.95
2021-06-27 12:00 | 44374.5 | 0 | 6.4653 | 39.95
2021-06-27 12:30 | 44374.5208 | 0 | 6.2408 | 39.95
2021-06-27 13:00 | 44374.5417 | 0 | 6.2531 | 39.95
2021-06-27 13:30 | 44374.5625 | 0 | 6.8898 | 39.95
2021-06-27 14:00 | 44374.5833 | 0 | 7.2683 | 39.95
2021-06-27 14:30 | 44374.6042 | 0 | 7.8986 | 39.95
2021-06-27 15:00 | 44374.625 | 0 | 8.2223 | 39.95
2021-06-27 15:30 | 44374.6458 | 0 | 9.0733 | 39.95
2021-06-27 16:00 | 44374.6667 | 0 | 10.0451 | 39.95
2021-06-27 16:30 | 44374.6875 | 0 | 10.9845 | 39.95
2021-06-27 17:00 | 44374.7083 | 0 | 12.14 | 39.95
2021-06-27 17:30 | 44374.7292 | 0 | 13.1182 | 39.95
2021-06-27 18:00 | 44374.75 | 0 | 13.3475 | 39.95
2021-06-27 18:30 | 44374.7708 | 0 | 13.3569 | 39.95
2021-06-27 19:00 | 44374.7917 | 0 | 12.9489 | 39.95
2021-06-27 19:30 | 44374.8125 | 0 | 13.5113 | 39.95
2021-06-27 20:00 | 44374.8333 | 0 | 13.0922 | 39.95
2021-06-27 20:30 | 44374.8542 | 0 | 12.7743 | 39.95
2021-06-27 21:00 | 44374.875 | 0 | 12.5057 | 39.95
2021-06-27 21:30 | 44374.8958 | 0 | 11.5933 | 39.95
2021-06-27 22:00 | 44374.9167 | 0 | 10.8016 | 39.95
2021-06-27 22:30 | 44374.9375 | 0 | 10.1095 | 39.95
2021-06-27 23:00 | 44374.9583 | 0 | 9.4901 | 39.95
2021-06-27 23:30 | 44374.9792 | 0 | 9.0369 | 39.95
2021-06-28 | 44375 | 0 | 8.6716 | 39.95
2021-06-28 00:30 | 44375.0208 | 0 | 8.3452 | 39.95
2021-06-28 01:00 | 44375.0417 | 0 | 8.1136 | 39.95
2021-06-28 01:30 | 44375.0625 | 0 | 7.961 | 39.95
2021-06-28 02:00 | 44375.0833 | 0 | 7.916 | 39.95
2021-06-28 02:30 | 44375.1042 | 0 | 7.923 | 39.95
2021-06-28 03:00 | 44375.125 | 0 | 7.8637 | 39.95
2021-06-28 03:30 | 44375.1458 | 0 | 8.2201 | 39.95
2021-06-28 04:00 | 44375.1667 | 0 | 8.3996 | 39.95
2021-06-28 04:30 | 44375.1875 | 0 | 8.7418 | 39.95
2021-06-28 05:00 | 44375.2083 | 0 | 9.3123 | 39.95
2021-06-28 05:30 | 44375.2292 | 0 | 10.0752 | 39.95
2021-06-28 06:00 | 44375.25 | 0 | 11.6896 | 39.95
2021-06-28 06:30 | 44375.2708 | 0 | 13.1062 | 39.95
2021-06-28 07:00 | 44375.2917 | 0 | 14.2635 | 39.95
2021-06-28 07:30 | 44375.3125 | 0 | 13.9941 | 39.95
2021-06-28 08:00 | 44375.3333 | 0 | 13.486 | 39.95
2021-06-28 08:30 | 44375.3542 | 0 | 12.7663 | 39.95
2021-06-28 09:00 | 44375.375 | 0 | 11.7613 | 39.95
2021-06-28 09:30 | 44375.3958 | 0 | 10.8937 | 39.95
2021-06-28 10:00 | 44375.4167 | 0 | 10.2881 | 39.95
2021-06-28 10:30 | 44375.4375 | 0 | 9.806 | 39.95
2021-06-28 11:00 | 44375.4583 | 0 | 9.3803 | 39.95
2021-06-28 11:30 | 44375.4792 | 0 | 8.8125 | 39.95
2021-06-28 12:00 | 44375.5 | 0 | 9.1457 | 39.95
2021-06-28 12:30 | 44375.5208 | 0 | 8.7795 | 39.95
2021-06-28 13:00 | 44375.5417 | 0 | 10.1407 | 39.95
2021-06-28 13:30 | 44375.5625 | 0 | 9.6351 | 39.95
2021-06-28 14:00 | 44375.5833 | 0 | 10.0646 | 39.95
2021-06-28 14:30 | 44375.6042 | 0 | 10.4204 | 39.95
2021-06-28 15:00 | 44375.625 | 0 | 10.8983 | 39.95
2021-06-28 15:30 | 44375.6458 | 0 | 12.0753 | 39.95
2021-06-28 16:00 | 44375.6667 | 0 | 12.5814 | 39.95
2021-06-28 16:30 | 44375.6875 | 0 | 13.0927 | 39.95
2021-06-28 17:00 | 44375.7083 | 0 | 13.984 | 39.95
2021-06-28 17:30 | 44375.7292 | 0 | 15.375 | 39.95
2021-06-28 18:00 | 44375.75 | 0 | 15.7222 | 39.95
2021-06-28 18:30 | 44375.7708 | 0 | 15.918 | 39.95
2021-06-28 19:00 | 44375.7917 | 0 | 15.6483 | 39.95
2021-06-28 19:30 | 44375.8125 | 0 | 15.2506 | 39.95
2021-06-28 20:00 | 44375.8333 | 0 | 14.8387 | 39.95
2021-06-28 20:30 | 44375.8542 | 0 | 13.9495 | 39.95
2021-06-28 21:00 | 44375.875 | 0 | 13.4437 | 39.95
2021-06-28 21:30 | 44375.8958 | 0 | 12.8404 | 39.95
2021-06-28 22:00 | 44375.9167 | 0 | 11.9295 | 39.95
2021-06-28 22:30 | 44375.9375 | 0 | 10.931 | 39.95
2021-06-28 23:00 | 44375.9583 | 0 | 10.1477 | 39.95
2021-06-28 23:30 | 44375.9792 | 0 | 9.5888 | 39.95
2021-06-29 | 44376 | 0 | 9.0799 | 39.95
2021-06-29 00:30 | 44376.0208 | 0 | 8.6026 | 39.95
2021-06-29 01:00 | 44376.0417 | 0 | 8.4194 | 39.95
2021-06-29 01:30 | 44376.0625 | 0 | 8.2708 | 39.95
2021-06-29 02:00 | 44376.0833 | 0 | 8.2854 | 39.95
2021-06-29 02:30 | 44376.1042 | 0 | 8.1955 | 39.95
2021-06-29 03:00 | 44376.125 | 0 | 8.0925 | 39.95
2021-06-29 03:30 | 44376.1458 | 0 | 8.2525 | 39.95
2021-06-29 04:00 | 44376.1667 | 0 | 8.5311 | 39.95
2021-06-29 04:30 | 44376.1875 | 0 | 8.8862 | 39.95
2021-06-29 05:00 | 44376.2083 | 0 | 9.6545 | 39.95
2021-06-29 05:30 | 44376.2292 | 0 | 10.5148 | 39.95
2021-06-29 06:00 | 44376.25 | 0 | 11.7385 | 39.95
2021-06-29 06:30 | 44376.2708 | 0 | 13.0391 | 39.95
2021-06-29 07:00 | 44376.2917 | 0 | 13.6256 | 39.95
2021-06-29 07:30 | 44376.3125 | 0 | 13.3239 | 39.95
2021-06-29 08:00 | 44376.3333 | 0 | 12.6677 | 39.95
2021-06-29 08:30 | 44376.3542 | 0 | 12.2202 | 39.95
2021-06-29 09:00 | 44376.375 | 0 | 11.426 | 39.95
2021-06-29 09:30 | 44376.3958 | 0 | 10.6776 | 39.95
2021-06-29 10:00 | 44376.4167 | 0 | 9.9539 | 39.95
2021-06-29 10:30 | 44376.4375 | 0 | 9.5497 | 39.95
2021-06-29 11:00 | 44376.4583 | 0 | 9.8289 | 39.95
2021-06-29 11:30 | 44376.4792 | 0 | 10.0665 | 39.95
2021-06-29 12:00 | 44376.5 | 0 | 9.9851 | 39.95
2021-06-29 12:30 | 44376.5208 | 0 | 8.8525 | 39.95
2021-06-29 13:00 | 44376.5417 | 0 | 10.0195 | 39.95
2021-06-29 13:30 | 44376.5625 | 0 | 10.7864 | 39.95
2021-06-29 14:00 | 44376.5833 | 0 | 10.0073 | 39.95
2021-06-29 14:30 | 44376.6042 | 0 | 10.7307 | 39.95
2021-06-29 15:00 | 44376.625 | 0 | 11.4151 | 39.95
2021-06-29 15:30 | 44376.6458 | 0 | 11.5946 | 39.95
2021-06-29 16:00 | 44376.6667 | 0 | 12.3844 | 39.95
2021-06-29 16:30 | 44376.6875 | 0 | 12.9707 | 39.95
2021-06-29 17:00 | 44376.7083 | 0 | 13.7662 | 39.95
2021-06-29 17:30 | 44376.7292 | 0 | 14.7288 | 39.95
2021-06-29 18:00 | 44376.75 | 0 | 14.8804 | 39.95
2021-06-29 18:30 | 44376.7708 | 0 | 15.1398 | 39.95
2021-06-29 19:00 | 44376.7917 | 0 | 14.4707 | 39.95
2021-06-29 19:30 | 44376.8125 | 0 | 14.0773 | 39.95
2021-06-29 20:00 | 44376.8333 | 0 | 13.9576 | 39.95
2021-06-29 20:30 | 44376.8542 | 0 | 13.1179 | 39.95
2021-06-29 21:00 | 44376.875 | 0 | 12.8218 | 39.95
2021-06-29 21:30 | 44376.8958 | 0 | 12.069 | 39.95
2021-06-29 22:00 | 44376.9167 | 0 | 11.2856 | 39.95
2021-06-29 22:30 | 44376.9375 | 0 | 10.5847 | 39.95
2021-06-29 23:00 | 44376.9583 | 0 | 9.9862 | 39.95
2021-06-29 23:30 | 44376.9792 | 0 | 9.4227 | 39.95
2021-06-30 | 44377 | 0 | 8.8442 | 39.95
2021-06-30 00:30 | 44377.0208 | 0 | 8.5757 | 39.95
2021-06-30 01:00 | 44377.0417 | 0 | 8.3203 | 39.95
2021-06-30 01:30 | 44377.0625 | 0 | 8.1611 | 39.95
2021-06-30 02:00 | 44377.0833 | 0 | 8.1265 | 39.95
2021-06-30 02:30 | 44377.1042 | 0 | 7.9395 | 39.95
2021-06-30 03:00 | 44377.125 | 0 | 7.9281 | 39.95
2021-06-30 03:30 | 44377.1458 | 0 | 8.1294 | 39.95
2021-06-30 04:00 | 44377.1667 | 0 | 8.4743 | 39.95
2021-06-30 04:30 | 44377.1875 | 0 | 8.77 | 39.95
2021-06-30 05:00 | 44377.2083 | 0 | 9.5316 | 39.95
2021-06-30 05:30 | 44377.2292 | 0 | 10.0896 | 39.95
2021-06-30 06:00 | 44377.25 | 0 | 11.0247 | 39.95
2021-06-30 06:30 | 44377.2708 | 0 | 11.7944 | 39.95
2021-06-30 07:00 | 44377.2917 | 0 | 12.6686 | 39.95
2021-06-30 07:30 | 44377.3125 | 0 | 13.2274 | 39.95
2021-06-30 08:00 | 44377.3333 | 0 | 13.5385 | 39.95
2021-06-30 08:30 | 44377.3542 | 0 | 13.8856 | 39.95
2021-06-30 09:00 | 44377.375 | 0 | 12.9196 | 39.95
2021-06-30 09:30 | 44377.3958 | 0 | 10.8413 | 39.95
2021-06-30 10:00 | 44377.4167 | 0 | 10.2684 | 39.95
2021-06-30 10:30 | 44377.4375 | 0 | 10.0209 | 39.95
2021-06-30 11:00 | 44377.4583 | 0 | 10.5902 | 39.95
2021-06-30 11:30 | 44377.4792 | 0 | 13.1718 | 39.95
2021-06-30 12:00 | 44377.5 | 0 | 11.3965 | 39.95
2021-06-30 12:30 | 44377.5208 | 0 | 10.7307 | 39.95
2021-06-30 13:00 | 44377.5417 | 0 | 11.5553 | 39.95
2021-06-30 13:30 | 44377.5625 | 0 | 12.4885 | 39.95
2021-06-30 14:00 | 44377.5833 | 0 | 11.9352 | 39.95
2021-06-30 14:30 | 44377.6042 | 0 | 11.2972 | 39.95
2021-06-30 15:00 | 44377.625 | 0 | 11.3333 | 39.95
2021-06-30 15:30 | 44377.6458 | 0 | 12.1317 | 39.95
2021-07-01 | 44378 | 0 | 8.9777 | 39.95
2021-07-01 00:30 | 44378.0208 | 0 | 8.5575 | 39.95
2021-07-01 01:00 | 44378.0417 | 0 | 8.2161 | 39.95
2021-07-01 01:30 | 44378.0625 | 0 | 8.1359 | 39.95
2021-07-01 02:00 | 44378.0833 | 0 | 8.1663 | 39.95
2021-07-01 02:30 | 44378.1042 | 0 | 8.0328 | 39.95
2021-07-01 03:00 | 44378.125 | 0 | 7.9977 | 39.95
2021-07-01 03:30 | 44378.1458 | 0 | 8.1715 | 39.95
2021-07-01 04:00 | 44378.1667 | 0 | 8.5202 | 39.95
2021-07-01 04:30 | 44378.1875 | 0 | 8.7799 | 39.95
2021-07-01 05:00 | 44378.2083 | 0 | 9.3026 | 39.95
2021-07-01 05:30 | 44378.2292 | 0 | 10.1203 | 39.95
2021-07-01 06:00 | 44378.25 | 0 | 11.1738 | 39.95
2021-07-01 06:30 | 44378.2708 | 0 | 11.9019 | 39.95
2021-07-01 07:00 | 44378.2917 | 0 | 12.7754 | 39.95
2021-07-01 07:30 | 44378.3125 | 0 | 13.4127 | 39.95
2021-07-01 08:00 | 44378.3333 | 0 | 12.8716 | 39.95
2021-07-01 08:30 | 44378.3542 | 0 | 12.8536 | 39.95
2021-07-01 09:00 | 44378.375 | 0 | 11.601 | 39.95
2021-07-01 09:30 | 44378.3958 | 0 | 10.8078 | 39.95
2021-07-01 10:00 | 44378.4167 | 0 | 11.1969 | 39.95
2021-07-01 10:30 | 44378.4375 | 0 | 12.2001 | 39.95
2021-07-01 11:00 | 44378.4583 | 0 | 10.546 | 39.95
2021-07-01 11:30 | 44378.4792 | 0 | 12.1108 | 39.95
2021-07-01 12:00 | 44378.5 | 0 | 12.161 | 39.95
2021-07-01 12:30 | 44378.5208 | 0 | 13.0662 | 39.95
2021-07-01 13:00 | 44378.5417 | 0 | 13.0958 | 39.95
2021-07-01 13:30 | 44378.5625 | 0 | 12.8905 | 39.95
2021-07-01 14:00 | 44378.5833 | 0 | 12.8059 | 39.95
2021-07-01 14:30 | 44378.6042 | 0 | 11.7394 | 39.95
2021-07-01 15:00 | 44378.625 | 0 | 13.3613 | 39.95
2021-07-01 15:30 | 44378.6458 | 0 | 13.4046 | 39.95
2021-07-01 16:00 | 44378.6667 | 0 | 13.7752 | 39.95
2021-07-01 16:30 | 44378.6875 | 0 | 14.4547 | 39.95
2021-07-01 17:00 | 44378.7083 | 0 | 15.0471 | 39.95
2021-07-01 17:30 | 44378.7292 | 0 | 15.6876 | 39.95
2021-07-01 18:00 | 44378.75 | 0 | 15.705 | 39.95
2021-07-01 18:30 | 44378.7708 | 0 | 15.3993 | 39.95
2021-07-01 19:00 | 44378.7917 | 0 | 14.8855 | 39.95
2021-07-01 19:30 | 44378.8125 | 0 | 14.6176 | 39.95
2021-07-01 20:00 | 44378.8333 | 0 | 14.1239 | 39.95
2021-07-01 20:30 | 44378.8542 | 0 | 13.2429 | 39.95
2021-07-01 21:00 | 44378.875 | 0 | 12.8037 | 39.95
2021-07-01 21:30 | 44378.8958 | 0 | 12.2942 | 39.95
2021-07-01 22:00 | 44378.9167 | 0 | 11.5745 | 39.95
2021-07-01 22:30 | 44378.9375 | 0 | 10.6348 | 39.95
2021-07-01 23:00 | 44378.9583 | 0 | 10.1189 | 39.95
2021-07-01 23:30 | 44378.9792 | 0 | 9.7321 | 39.95
2021-07-02 | 44379 | 0 | 9.1314 | 39.95
2021-07-02 00:30 | 44379.0208 | 0 | 8.6663 | 39.95
2021-07-02 01:00 | 44379.0417 | 0 | 8.3824 | 39.95
2021-07-02 01:30 | 44379.0625 | 0 | 8.2012 | 39.95
2021-07-02 02:00 | 44379.0833 | 0 | 8.1463 | 39.95
2021-07-02 02:30 | 44379.1042 | 0 | 8.1317 | 39.95
2021-07-02 03:00 | 44379.125 | 0 | 8.1068 | 39.95
2021-07-02 03:30 | 44379.1458 | 0 | 8.1463 | 39.95
2021-07-02 04:00 | 44379.1667 | 0 | 8.5433 | 39.95
2021-07-02 04:30 | 44379.1875 | 0 | 8.6702 | 39.95
2021-07-02 05:00 | 44379.2083 | 0 | 9.2757 | 39.95
2021-07-02 05:30 | 44379.2292 | 0 | 10.1043 | 39.95
2021-07-02 06:00 | 44379.25 | 0 | 10.7945 | 39.95
2021-07-02 06:30 | 44379.2708 | 0 | 11.6525 | 39.95
2021-07-02 07:00 | 44379.2917 | 0 | 12.4735 | 39.95
2021-07-02 07:30 | 44379.3125 | 0 | 13.0667 | 39.95
2021-07-02 08:00 | 44379.3333 | 0 | 13.6845 | 39.95
2021-07-02 08:30 | 44379.3542 | 0 | 12.9961 | 39.95
2021-07-02 09:00 | 44379.375 | 0 | 12.592 | 39.95
2021-07-02 09:30 | 44379.3958 | 0 | 12.1206 | 39.95
2021-07-02 10:00 | 44379.4167 | 0 | 11.22 | 39.95
2021-07-02 10:30 | 44379.4375 | 0 | 12.9856 | 39.95
2021-07-02 11:00 | 44379.4583 | 0 | 11.4817 | 39.95
2021-07-02 11:30 | 44379.4792 | 0 | 10.738 | 39.95
2021-07-02 12:00 | 44379.5 | 0 | 11.0443 | 39.95
2021-07-02 12:30 | 44379.5208 | 0 | 12.8972 | 39.95
2021-07-02 13:00 | 44379.5417 | 0 | 13.5831 | 39.95
2021-07-02 13:30 | 44379.5625 | 0 | 11.9097 | 39.95
2021-07-02 14:00 | 44379.5833 | 0 | 12.2889 | 39.95
2021-07-02 14:30 | 44379.6042 | 0 | 12.6511 | 39.95
2021-07-02 15:00 | 44379.625 | 0 | 12.5489 | 39.95
2021-07-02 15:30 | 44379.6458 | 0 | 12.5535 | 39.95
2021-07-02 16:00 | 44379.6667 | 0 | 12.382 | 39.95
2021-07-02 16:30 | 44379.6875 | 0 | 13.1742 | 39.95
2021-07-02 17:00 | 44379.7083 | 0 | 13.874 | 39.95
2021-07-02 17:30 | 44379.7292 | 0 | 14.6514 | 39.95
2021-07-02 18:00 | 44379.75 | 0 | 14.8788 | 39.95
2021-07-02 18:30 | 44379.7708 | 0 | 14.7172 | 39.95
2021-07-02 19:00 | 44379.7917 | 0 | 14.2605 | 39.95
2021-07-02 19:30 | 44379.8125 | 0 | 13.9055 | 39.95
2021-07-02 20:00 | 44379.8333 | 0 | 13.2523 | 39.95
2021-07-02 20:30 | 44379.8542 | 0 | 12.826 | 39.95
2021-07-02 21:00 | 44379.875 | 0 | 12.3556 | 39.95
2021-07-02 21:30 | 44379.8958 | 0 | 11.7905 | 39.95
2021-07-02 22:00 | 44379.9167 | 0 | 11.1152 | 39.95
2021-07-02 22:30 | 44379.9375 | 0 | 10.3645 | 39.95
2021-07-02 23:00 | 44379.9583 | 0 | 9.7839 | 39.95
2021-07-02 23:30 | 44379.9792 | 0 | 9.4687 | 39.95
2021-07-03 | 44380 | 0 | 8.9066 | 39.95
2021-07-03 00:30 | 44380.0208 | 0 | 8.3481 | 39.95
2021-07-03 01:00 | 44380.0417 | 0 | 8.0475 | 39.95
2021-07-03 01:30 | 44380.0625 | 0 | 8.0595 | 39.95
2021-07-03 02:00 | 44380.0833 | 0 | 7.9805 | 39.95
2021-07-03 02:30 | 44380.1042 | 0 | 7.7265 | 39.95
2021-07-03 03:00 | 44380.125 | 0 | 7.7397 | 39.95
2021-07-03 03:30 | 44380.1458 | 0 | 7.8714 | 39.95
2021-07-03 04:00 | 44380.1667 | 0 | 7.8783 | 39.95
2021-07-03 04:30 | 44380.1875 | 0 | 7.9977 | 39.95
2021-07-03 05:00 | 44380.2083 | 0 | 8.3104 | 39.95
2021-07-03 05:30 | 44380.2292 | 0 | 8.3126 | 39.95
2021-07-03 06:00 | 44380.25 | 0 | 8.6204 | 39.95
2021-07-03 06:30 | 44380.2708 | 0 | 8.8279 | 39.95
2021-07-03 07:00 | 44380.2917 | 0 | 9.5723 | 39.95
2021-07-03 07:30 | 44380.3125 | 0 | 10.2428 | 39.95
2021-07-03 08:00 | 44380.3333 | 0 | 11.003 | 39.95
2021-07-03 08:30 | 44380.3542 | 0 | 11.3743 | 39.95
2021-07-03 09:00 | 44380.375 | 0 | 11.7642 | 39.95
2021-07-03 09:30 | 44380.3958 | 0 | 12.4525 | 39.95
2021-07-03 10:00 | 44380.4167 | 0 | 12.3593 | 39.95
2021-07-03 10:30 | 44380.4375 | 0 | 12.7618 | 39.95
2021-07-03 11:00 | 44380.4583 | 0 | 12.9474 | 39.95
2021-07-03 11:30 | 44380.4792 | 0 | 12.9733 | 39.95
2021-07-03 12:00 | 44380.5 | 0 | 12.4918 | 39.95
2021-07-03 12:30 | 44380.5208 | 0 | 12.2505 | 39.95
2021-07-03 13:00 | 44380.5417 | 0 | 12.5404 | 39.95
2021-07-03 13:30 | 44380.5625 | 0 | 11.9732 | 39.95
2021-07-03 14:00 | 44380.5833 | 0 | 12.1509 | 39.95
2021-07-03 14:30 | 44380.6042 | 0 | 12.0743 | 39.95
2021-07-03 15:00 | 44380.625 | 0 | 11.845 | 39.95
2021-07-03 15:30 | 44380.6458 | 0 | 12.2297 | 39.95
2021-07-03 16:00 | 44380.6667 | 0 | 12.0699 | 39.95
2021-07-03 16:30 | 44380.6875 | 0 | 12.4468 | 39.95
2021-07-03 17:00 | 44380.7083 | 0 | 13.1566 | 39.95
2021-07-03 17:30 | 44380.7292 | 0 | 13.4818 | 39.95
2021-07-03 18:00 | 44380.75 | 0 | 13.2855 | 39.95
2021-07-03 18:30 | 44380.7708 | 0 | 13.1711 | 39.95
2021-07-03 19:00 | 44380.7917 | 0 | 12.793 | 39.95
2021-07-03 19:30 | 44380.8125 | 0 | 12.6111 | 39.95
2021-07-03 20:00 | 44380.8333 | 0 | 12.2779 | 39.95
2021-07-03 20:30 | 44380.8542 | 0 | 11.8455 | 39.95
2021-07-03 21:00 | 44380.875 | 0 | 11.2623 | 39.95
2021-07-03 21:30 | 44380.8958 | 0 | 10.8365 | 39.95
2021-07-03 22:00 | 44380.9167 | 0 | 10.4181 | 39.95
2021-07-03 22:30 | 44380.9375 | 0 | 9.7941 | 39.95
2021-07-03 23:00 | 44380.9583 | 0 | 9.1474 | 39.95
2021-07-03 23:30 | 44380.9792 | 0 | 8.7489 | 39.95
2021-07-04 | 44381 | 0 | 8.3217 | 39.95
2021-07-04 00:30 | 44381.0208 | 0 | 7.9014 | 39.95
2021-07-04 01:00 | 44381.0417 | 0 | 7.5871 | 39.95
2021-07-04 01:30 | 44381.0625 | 0 | 7.3749 | 39.95
2021-07-04 02:00 | 44381.0833 | 0 | 7.3302 | 39.95
2021-07-04 02:30 | 44381.1042 | 0 | 7.2779 | 39.95
2021-07-04 03:00 | 44381.125 | 0 | 7.2252 | 39.95
2021-07-04 03:30 | 44381.1458 | 0 | 7.3208 | 39.95
2021-07-04 04:00 | 44381.1667 | 0 | 7.2235 | 39.95
2021-07-04 04:30 | 44381.1875 | 0 | 7.2578 | 39.95
2021-07-04 05:00 | 44381.2083 | 0 | 7.3128 | 39.95
2021-07-04 05:30 | 44381.2292 | 0 | 7.4565 | 39.95
2021-07-04 06:00 | 44381.25 | 0 | 7.8781 | 39.95
2021-07-04 06:30 | 44381.2708 | 0 | 8.2239 | 39.95
2021-07-04 07:00 | 44381.2917 | 0 | 8.611 | 39.95
2021-07-04 07:30 | 44381.3125 | 0 | 8.6127 | 39.95
2021-07-04 08:00 | 44381.3333 | 0 | 8.4915 | 39.95
2021-07-04 08:30 | 44381.3542 | 0 | 8.294 | 39.95
2021-07-04 09:00 | 44381.375 | 0 | 8.0915 | 39.95
2021-07-04 09:30 | 44381.3958 | 0 | 7.886 | 39.95
2021-07-04 10:00 | 44381.4167 | 0 | 7.4667 | 39.95
2021-07-04 10:30 | 44381.4375 | 0 | 7.2326 | 39.95
2021-07-04 11:00 | 44381.4583 | 0 | 6.6208 | 39.95
2021-07-04 11:30 | 44381.4792 | 0 | 6.5264 | 39.95
2021-07-04 12:00 | 44381.5 | 0 | 6.0868 | 39.95
2021-07-04 12:30 | 44381.5208 | 0 | 6.5816 | 39.95
2021-07-04 13:00 | 44381.5417 | 0 | 7.3021 | 39.95
2021-07-04 13:30 | 44381.5625 | 0 | 8.3988 | 39.95
2021-07-04 14:00 | 44381.5833 | 0 | 8.2575 | 39.95
2021-07-04 14:30 | 44381.6042 | 0 | 7.9595 | 39.95
2021-07-04 15:00 | 44381.625 | 0 | 8.8134 | 39.95
2021-07-04 15:30 | 44381.6458 | 0 | 9.4581 | 39.95
2021-07-04 16:00 | 44381.6667 | 0 | 9.7994 | 39.95
2021-07-04 16:30 | 44381.6875 | 0 | 10.486 | 39.95
2021-07-04 17:00 | 44381.7083 | 0 | 11.2683 | 39.95
2021-07-04 17:30 | 44381.7292 | 0 | 12.1843 | 39.95
2021-07-04 18:00 | 44381.75 | 0 | 12.3674 | 39.95
2021-07-04 18:30 | 44381.7708 | 0 | 12.303 | 39.95
2021-07-04 19:00 | 44381.7917 | 0 | 12.1073 | 39.95
2021-07-04 19:30 | 44381.8125 | 0 | 11.8263 | 39.95
2021-07-04 20:00 | 44381.8333 | 0 | 11.635 | 39.95
2021-07-04 20:30 | 44381.8542 | 0 | 10.9831 | 39.95
2021-07-04 21:00 | 44381.875 | 0 | 10.4335 | 39.95
2021-07-04 21:30 | 44381.8958 | 0 | 10.1484 | 39.95
2021-07-04 22:00 | 44381.9167 | 0 | 9.6713 | 39.95
2021-07-04 22:30 | 44381.9375 | 0 | 9.0637 | 39.95
2021-07-04 23:00 | 44381.9583 | 0 | 8.568 | 39.95
2021-07-04 23:30 | 44381.9792 | 0 | 8.1795 | 39.95
2021-07-05 | 44382 | 0 | 7.851 | 39.95
2021-07-05 00:30 | 44382.0208 | 0 | 7.5454 | 39.95
2021-07-05 01:00 | 44382.0417 | 0 | 7.3328 | 39.95
2021-07-05 01:30 | 44382.0625 | 0 | 7.2501 | 39.95
2021-07-05 02:00 | 44382.0833 | 0 | 7.2389 | 39.95
2021-07-05 02:30 | 44382.1042 | 0 | 7.1508 | 39.95
2021-07-05 03:00 | 44382.125 | 0 | 7.2017 | 39.95
2021-07-05 03:30 | 44382.1458 | 0 | 7.5528 | 39.95
2021-07-05 04:00 | 44382.1667 | 0 | 7.8351 | 39.95
2021-07-05 04:30 | 44382.1875 | 0 | 8.1414 | 39.95
2021-07-05 05:00 | 44382.2083 | 0 | 8.8379 | 39.95
2021-07-05 05:30 | 44382.2292 | 0 | 9.775 | 39.95
2021-07-05 06:00 | 44382.25 | 0 | 10.9031 | 39.95
2021-07-05 06:30 | 44382.2708 | 0 | 12.2477 | 39.95
2021-07-05 07:00 | 44382.2917 | 0 | 13.2883 | 39.95
2021-07-05 07:30 | 44382.3125 | 0 | 13.7008 | 39.95
2021-07-05 08:00 | 44382.3333 | 0 | 13.4414 | 39.95
2021-07-05 08:30 | 44382.3542 | 0 | 13.194 | 39.95
2021-07-05 09:00 | 44382.375 | 0 | 12.0203 | 39.95
2021-07-05 09:30 | 44382.3958 | 0 | 11.7097 | 39.95
2021-07-05 10:00 | 44382.4167 | 0 | 10.2988 | 39.95
2021-07-05 10:30 | 44382.4375 | 0 | 9.5685 | 39.95
2021-07-05 11:00 | 44382.4583 | 0 | 9.2966 | 39.95
2021-07-05 11:30 | 44382.4792 | 0 | 9.6092 | 39.95
2021-07-05 12:00 | 44382.5 | 0 | 9.3557 | 39.95
2021-07-05 12:30 | 44382.5208 | 0 | 9.117 | 39.95
2021-07-05 13:00 | 44382.5417 | 0 | 8.5783 | 39.95
2021-07-05 13:30 | 44382.5625 | 0 | 9.517 | 39.95
2021-07-05 14:00 | 44382.5833 | 0 | 9.6322 | 39.95
2021-07-05 14:30 | 44382.6042 | 0 | 10.2834 | 39.95
2021-07-05 15:00 | 44382.625 | 0 | 11.3971 | 39.95
2021-07-05 15:30 | 44382.6458 | 0 | 1.6264 | 39.95
2021-07-05 16:00 | 44382.6667 | 0 | 0.81522 | 39.95
2021-07-05 16:30 | 44382.6875 | 0 | 13.1272 | 39.95
2021-07-05 17:00 | 44382.7083 | 0 | 14.4289 | 39.95
2021-07-05 17:30 | 44382.7292 | 0 | 15.5761 | 39.95
2021-07-05 18:00 | 44382.75 | 0 | 15.8974 | 39.95
2021-07-05 18:30 | 44382.7708 | 0 | 16.3575 | 39.95
2021-07-05 19:00 | 44382.7917 | 0 | 16.1858 | 39.95
2021-07-05 19:30 | 44382.8125 | 0 | 16.1121 | 39.95
2021-07-05 20:00 | 44382.8333 | 0 | 15.66 | 39.95
2021-07-05 20:30 | 44382.8542 | 0 | 14.8947 | 39.95
2021-07-05 21:00 | 44382.875 | 0 | 14.1484 | 39.95
2021-07-05 21:30 | 44382.8958 | 0 | 13.5439 | 39.95
2021-07-05 22:00 | 44382.9167 | 0 | 12.6075 | 39.95
2021-07-05 22:30 | 44382.9375 | 0 | 11.478 | 39.95
2021-07-05 23:00 | 44382.9583 | 0 | 10.7279 | 39.95
2021-07-05 23:30 | 44382.9792 | 0 | 9.9847 | 39.95
2021-07-06 | 44383 | 0 | 9.1444 | 39.95
2021-07-06 00:30 | 44383.0208 | 0 | 8.6498 | 39.95
2021-07-06 01:00 | 44383.0417 | 0 | 8.3425 | 39.95
2021-07-06 01:30 | 44383.0625 | 0 | 8.3023 | 39.95
2021-07-06 02:00 | 44383.0833 | 0 | 8.2259 | 39.95
2021-07-06 02:30 | 44383.1042 | 0 | 8.1093 | 39.95
2021-07-06 03:00 | 44383.125 | 0 | 8.1068 | 39.95
2021-07-06 03:30 | 44383.1458 | 0 | 8.3204 | 39.95
2021-07-06 04:00 | 44383.1667 | 0 | 8.7383 | 39.95
2021-07-06 04:30 | 44383.1875 | 0 | 9.0095 | 39.95
2021-07-06 05:00 | 44383.2083 | 0 | 9.8444 | 39.95
2021-07-06 05:30 | 44383.2292 | 0 | 10.8211 | 39.95
2021-07-06 06:00 | 44383.25 | 0 | 11.9977 | 39.95
2021-07-06 06:30 | 44383.2708 | 0 | 13.3816 | 39.95
2021-07-06 07:00 | 44383.2917 | 0 | 14.6364 | 39.95
2021-07-06 07:30 | 44383.3125 | 0 | 15.1995 | 39.95
2021-07-06 08:00 | 44383.3333 | 0 | 15.4557 | 39.95
2021-07-06 08:30 | 44383.3542 | 0 | 15.2344 | 39.95
2021-07-06 09:00 | 44383.375 | 0 | 14.6379 | 39.95
2021-07-06 09:30 | 44383.3958 | 0 | 13.69 | 39.95
2021-07-06 10:00 | 44383.4167 | 0 | 12.3596 | 39.95
2021-07-06 10:30 | 44383.4375 | 0 | 11.1565 | 39.95
2021-07-06 11:00 | 44383.4583 | 0 | 11.5286 | 39.95
2021-07-06 11:30 | 44383.4792 | 0 | 9.7029 | 39.95
2021-07-06 12:00 | 44383.5 | 0 | 10.554 | 39.95
2021-07-06 12:30 | 44383.5208 | 0 | 10.1762 | 39.95
2021-07-06 13:00 | 44383.5417 | 0 | 9.8246 | 39.95
2021-07-06 13:30 | 44383.5625 | 0 | 9.9063 | 39.95
2021-07-06 14:00 | 44383.5833 | 0 | 10.3167 | 39.95
2021-07-06 14:30 | 44383.6042 | 0 | 10.9601 | 39.95
2021-07-06 15:00 | 44383.625 | 0 | 10.8041 | 39.95
2021-07-06 15:30 | 44383.6458 | 0 | 11.6863 | 39.95
2021-07-06 16:00 | 44383.6667 | 0 | 12.535 | 39.95
2021-07-06 16:30 | 44383.6875 | 0 | 13.2932 | 39.95
2021-07-06 17:00 | 44383.7083 | 0 | 14.4468 | 39.95
2021-07-06 17:30 | 44383.7292 | 0 | 15.8465 | 39.95
2021-07-06 18:00 | 44383.75 | 0 | 16.2831 | 39.95
2021-07-06 18:30 | 44383.7708 | 0 | 16.8233 | 39.95
2021-07-06 19:00 | 44383.7917 | 0 | 16.4659 | 39.95
2021-07-06 19:30 | 44383.8125 | 0 | 16.6939 | 39.95
2021-07-06 20:00 | 44383.8333 | 0 | 16.1653 | 39.95
2021-07-06 20:30 | 44383.8542 | 0 | 15.4115 | 39.95
2021-07-06 21:00 | 44383.875 | 0 | 14.755 | 39.95
2021-07-06 21:30 | 44383.8958 | 0 | 14.1827 | 39.95
2021-07-06 22:00 | 44383.9167 | 0 | 13.2717 | 39.95
2021-07-06 22:30 | 44383.9375 | 0 | 11.9943 | 39.95
2021-07-06 23:00 | 44383.9583 | 0 | 11.1374 | 39.95
2021-07-06 23:30 | 44383.9792 | 0 | 10.524 | 39.95
2021-07-07 | 44384 | 0 | 9.8253 | 39.95
2021-07-07 00:30 | 44384.0208 | 0 | 9.3321 | 39.95
2021-07-07 01:00 | 44384.0417 | 0 | 9.0971 | 39.95
2021-07-07 01:30 | 44384.0625 | 0 | 8.9184 | 39.95
2021-07-07 02:00 | 44384.0833 | 0 | 8.8661 | 39.95
2021-07-07 02:30 | 44384.1042 | 0 | 8.8039 | 39.95
2021-07-07 03:00 | 44384.125 | 0 | 8.6242 | 39.95
2021-07-07 03:30 | 44384.1458 | 0 | 8.7971 | 39.95
2021-07-07 04:00 | 44384.1667 | 0 | 9.3036 | 39.95
2021-07-07 04:30 | 44384.1875 | 0 | 9.6668 | 39.95
2021-07-07 05:00 | 44384.2083 | 0 | 10.6352 | 39.95
2021-07-07 05:30 | 44384.2292 | 0 | 11.7879 | 39.95
2021-07-07 06:00 | 44384.25 | 0 | 13.1594 | 39.95
2021-07-07 06:30 | 44384.2708 | 0 | 14.5071 | 39.95
2021-07-07 07:00 | 44384.2917 | 0 | 15.7035 | 39.95
2021-07-07 07:30 | 44384.3125 | 0 | 15.7797 | 39.95
2021-07-07 08:00 | 44384.3333 | 0 | 15.0502 | 39.95
2021-07-07 08:30 | 44384.3542 | 0 | 14.1263 | 39.95
2021-07-07 09:00 | 44384.375 | 0 | 13.1129 | 39.95
2021-07-07 09:30 | 44384.3958 | 0 | 12.0556 | 39.95
2021-07-07 10:00 | 44384.4167 | 0 | 11.2404 | 39.95
2021-07-07 10:30 | 44384.4375 | 0 | 10.6452 | 39.95
2021-07-07 11:00 | 44384.4583 | 0 | 9.8892 | 39.95
2021-07-07 11:30 | 44384.4792 | 0 | 9.7768 | 39.95
2021-07-07 12:00 | 44384.5 | 0 | 9.3829 | 39.95
2021-07-07 12:30 | 44384.5208 | 0 | 9.7497 | 39.95
2021-07-07 13:00 | 44384.5417 | 0 | 9.423 | 39.95
2021-07-07 13:30 | 44384.5625 | 0 | 9.4012 | 39.95
2021-07-07 14:00 | 44384.5833 | 0 | 10.0918 | 39.95
2021-07-07 14:30 | 44384.6042 | 0 | 10.6533 | 39.95
2021-07-07 15:00 | 44384.625 | 0 | 10.8977 | 39.95
2021-07-07 15:30 | 44384.6458 | 0 | 11.4564 | 39.95
2021-07-07 16:00 | 44384.6667 | 0 | 12.0495 | 39.95
2021-07-07 16:30 | 44384.6875 | 0 | 12.9688 | 39.95
2021-07-07 17:00 | 44384.7083 | 0 | 14.0848 | 39.95
2021-07-07 17:30 | 44384.7292 | 0 | 15.0594 | 39.95
2021-07-07 18:00 | 44384.75 | 0 | 15.3896 | 39.95
2021-07-07 18:30 | 44384.7708 | 0 | 15.6801 | 39.95
2021-07-07 19:00 | 44384.7917 | 0 | 15.6973 | 39.95
2021-07-07 19:30 | 44384.8125 | 0 | 15.5782 | 39.95
2021-07-07 20:00 | 44384.8333 | 0 | 15.3496 | 39.95
2021-07-07 20:30 | 44384.8542 | 0 | 14.807 | 39.95
2021-07-07 21:00 | 44384.875 | 0 | 14.1271 | 39.95
2021-07-07 21:30 | 44384.8958 | 0 | 13.6435 | 39.95
2021-07-07 22:00 | 44384.9167 | 0 | 12.8296 | 39.95
2021-07-07 22:30 | 44384.9375 | 0 | 11.507 | 39.95
2021-07-07 23:00 | 44384.9583 | 0 | 10.613 | 39.95
2021-07-07 23:30 | 44384.9792 | 0 | 10.0376 | 39.95
2021-07-08 | 44385 | 0 | 9.3468 | 39.95
2021-07-08 00:30 | 44385.0208 | 0 | 8.9588 | 39.95
2021-07-08 01:00 | 44385.0417 | 0 | 8.6255 | 39.95
2021-07-08 01:30 | 44385.0625 | 0 | 8.5087 | 39.95
2021-07-08 02:00 | 44385.0833 | 0 | 8.3601 | 39.95
2021-07-08 02:30 | 44385.1042 | 0 | 8.2153 | 39.95
2021-07-08 03:00 | 44385.125 | 0 | 8.1291 | 39.95
2021-07-08 03:30 | 44385.1458 | 0 | 8.4743 | 39.95
2021-07-08 04:00 | 44385.1667 | 0 | 8.6705 | 39.95
2021-07-08 04:30 | 44385.1875 | 0 | 9.1062 | 39.95
2021-07-08 05:00 | 44385.2083 | 0 | 10.0885 | 39.95
2021-07-08 05:30 | 44385.2292 | 0 | 10.9301 | 39.95
2021-07-08 06:00 | 44385.25 | 0 | 12.4267 | 39.95
2021-07-08 06:30 | 44385.2708 | 0 | 13.3719 | 39.95
2021-07-08 07:00 | 44385.2917 | 0 | 14.2125 | 39.95
2021-07-08 07:30 | 44385.3125 | 0 | 14.03 | 39.95
2021-07-08 08:00 | 44385.3333 | 0 | 14.0526 | 39.95
2021-07-08 08:30 | 44385.3542 | 0 | 13.8983 | 39.95
2021-07-08 09:00 | 44385.375 | 0 | 14.0814 | 39.95
2021-07-08 09:30 | 44385.3958 | 0 | 13.753 | 39.95
2021-07-08 10:00 | 44385.4167 | 0 | 12.8221 | 39.95
2021-07-08 10:30 | 44385.4375 | 0 | 12.5687 | 39.95
2021-07-08 11:00 | 44385.4583 | 0 | 11.5725 | 39.95
2021-07-08 11:30 | 44385.4792 | 0 | 11.0374 | 39.95
2021-07-08 12:00 | 44385.5 | 0 | 9.8887 | 39.95
2021-07-08 12:30 | 44385.5208 | 0 | 11.3789 | 39.95
2021-07-08 13:00 | 44385.5417 | 0 | 11.266 | 39.95
2021-07-08 13:30 | 44385.5625 | 0 | 11.4442 | 39.95
2021-07-08 14:00 | 44385.5833 | 0 | 11.8284 | 39.95
2021-07-08 14:30 | 44385.6042 | 0 | 12.275 | 39.95
2021-07-08 15:00 | 44385.625 | 0 | 12.165 | 39.95
2021-07-08 15:30 | 44385.6458 | 0 | 12.0095 | 39.95
2021-07-08 16:00 | 44385.6667 | 0 | 12.7625 | 39.95
2021-07-08 16:30 | 44385.6875 | 0 | 13.3188 | 39.95
2021-07-08 17:00 | 44385.7083 | 0 | 14.1439 | 39.95
2021-07-08 17:30 | 44385.7292 | 0 | 14.811 | 39.95
2021-07-08 18:00 | 44385.75 | 0 | 15.303 | 39.95
2021-07-08 18:30 | 44385.7708 | 0 | 15.5355 | 39.95
2021-07-08 19:00 | 44385.7917 | 0 | 15.303 | 39.95
2021-07-08 19:30 | 44385.8125 | 0 | 15.5218 | 39.95
2021-07-08 20:00 | 44385.8333 | 0 | 15.1746 | 39.95
2021-07-08 20:30 | 44385.8542 | 0 | 14.5569 | 39.95
2021-07-08 21:00 | 44385.875 | 0 | 13.8718 | 39.95
2021-07-08 21:30 | 44385.8958 | 0 | 13.2106 | 39.95
2021-07-08 22:00 | 44385.9167 | 0 | 12.5385 | 39.95
2021-07-08 22:30 | 44385.9375 | 0 | 11.2947 | 39.95
2021-07-08 23:00 | 44385.9583 | 0 | 10.5546 | 39.95
2021-07-08 23:30 | 44385.9792 | 0 | 9.8905 | 39.95
2021-07-09 | 44386 | 0 | 9.2251 | 39.95
2021-07-09 00:30 | 44386.0208 | 0 | 8.7225 | 39.95
2021-07-09 01:00 | 44386.0417 | 0 | 8.4692 | 39.95
2021-07-09 01:30 | 44386.0625 | 0 | 8.3718 | 39.95
2021-07-09 02:00 | 44386.0833 | 0 | 8.3083 | 39.95
2021-07-09 02:30 | 44386.1042 | 0 | 8.2004 | 39.95
2021-07-09 03:00 | 44386.125 | 0 | 8.1119 | 39.95
2021-07-09 03:30 | 44386.1458 | 0 | 8.3207 | 39.95
2021-07-09 04:00 | 44386.1667 | 0 | 8.4736 | 39.95
2021-07-09 04:30 | 44386.1875 | 0 | 9.0016 | 39.95
2021-07-09 05:00 | 44386.2083 | 0 | 9.476 | 39.95
2021-07-09 05:30 | 44386.2292 | 0 | 10.4431 | 39.95
2021-07-09 06:00 | 44386.25 | 0 | 11.3415 | 39.95
2021-07-09 06:30 | 44386.2708 | 0 | 12.3296 | 39.95
2021-07-09 07:00 | 44386.2917 | 0 | 13.1801 | 39.95
2021-07-09 07:30 | 44386.3125 | 0 | 13.8887 | 39.95
2021-07-09 08:00 | 44386.3333 | 0 | 14.2477 | 39.95
2021-07-09 08:30 | 44386.3542 | 0 | 14.4747 | 39.95
2021-07-09 09:00 | 44386.375 | 0 | 14.5924 | 39.95
2021-07-09 09:30 | 44386.3958 | 0 | 14.2694 | 39.95
2021-07-09 10:00 | 44386.4167 | 0 | 13.1161 | 39.95
2021-07-09 10:30 | 44386.4375 | 0 | 13.711 | 39.95
2021-07-09 11:00 | 44386.4583 | 0 | 13.7175 | 39.95
2021-07-09 11:30 | 44386.4792 | 0 | 13.486 | 39.95
2021-07-09 12:00 | 44386.5 | 0 | 12.8704 | 39.95
2021-07-09 12:30 | 44386.5208 | 0 | 11.6671 | 39.95
2021-07-09 13:00 | 44386.5417 | 0 | 9.8025 | 39.95
2021-07-09 13:30 | 44386.5625 | 0 | 10.1621 | 39.95
2021-07-09 14:00 | 44386.5833 | 0 | 10.5107 | 39.95
2021-07-09 14:30 | 44386.6042 | 0 | 11.2151 | 39.95
2021-07-09 15:00 | 44386.625 | 0 | 12.7183 | 39.95
2021-07-09 15:30 | 44386.6458 | 0 | 12.1187 | 39.95
2021-07-09 16:00 | 44386.6667 | 0 | 12.1834 | 39.95
2021-07-09 16:30 | 44386.6875 | 0 | 13.0034 | 39.95
2021-07-09 17:00 | 44386.7083 | 0 | 13.5836 | 39.95
2021-07-09 17:30 | 44386.7292 | 0 | 14.1316 | 39.95
2021-07-09 18:00 | 44386.75 | 0 | 14.3195 | 39.95
2021-07-09 18:30 | 44386.7708 | 0 | 14.4194 | 39.95
2021-07-09 19:00 | 44386.7917 | 0 | 14.2834 | 39.95
2021-07-09 19:30 | 44386.8125 | 0 | 14.1735 | 39.95
2021-07-09 20:00 | 44386.8333 | 0 | 13.7173 | 39.95
2021-07-09 20:30 | 44386.8542 | 0 | 13.1999 | 39.95
2021-07-09 21:00 | 44386.875 | 0 | 12.7419 | 39.95
2021-07-09 21:30 | 44386.8958 | 0 | 12.24 | 39.95
2021-07-09 22:00 | 44386.9167 | 0 | 11.7565 | 39.95
2021-07-09 22:30 | 44386.9375 | 0 | 10.8342 | 39.95
2021-07-09 23:00 | 44386.9583 | 0 | 10.2314 | 39.95
2021-07-09 23:30 | 44386.9792 | 0 | 9.7313 | 39.95
2021-07-10 | 44387 | 0 | 9.264 | 39.95
2021-07-10 00:30 | 44387.0208 | 0 | 8.6258 | 39.95
2021-07-10 01:00 | 44387.0417 | 0 | 8.422 | 39.95
2021-07-10 01:30 | 44387.0625 | 0 | 8.2999 | 39.95
2021-07-10 02:00 | 44387.0833 | 0 | 8.1239 | 39.95
2021-07-10 02:30 | 44387.1042 | 0 | 8.1342 | 39.95
2021-07-10 03:00 | 44387.125 | 0 | 7.9977 | 39.95
2021-07-10 03:30 | 44387.1458 | 0 | 8.099 | 39.95
2021-07-10 04:00 | 44387.1667 | 0 | 8.1737 | 39.95
2021-07-10 04:30 | 44387.1875 | 0 | 8.162 | 39.95
2021-07-10 05:00 | 44387.2083 | 0 | 8.6714 | 39.95
2021-07-10 05:30 | 44387.2292 | 0 | 8.8343 | 39.95
2021-07-10 06:00 | 44387.25 | 0 | 9.2979 | 39.95
2021-07-10 06:30 | 44387.2708 | 0 | 9.7978 | 39.95
2021-07-10 07:00 | 44387.2917 | 0 | 10.1786 | 39.95
2021-07-10 07:30 | 44387.3125 | 0 | 10.2681 | 39.95
2021-07-10 08:00 | 44387.3333 | 0 | 10.2481 | 39.95
2021-07-10 08:30 | 44387.3542 | 0 | 9.9231 | 39.95
2021-07-10 09:00 | 44387.375 | 0 | 9.5927 | 39.95
2021-07-10 09:30 | 44387.3958 | 0 | 8.9074 | 39.95
2021-07-10 10:00 | 44387.4167 | 0 | 8.1317 | 39.95
2021-07-10 10:30 | 44387.4375 | 0 | 7.6251 | 39.95
2021-07-10 11:00 | 44387.4583 | 0 | 7.3996 | 39.95
2021-07-10 11:30 | 44387.4792 | 0 | 7.1559 | 39.95
2021-07-10 12:00 | 44387.5 | 0 | 6.6988 | 39.95
2021-07-10 12:30 | 44387.5208 | 0 | 6.4765 | 39.95
2021-07-10 13:00 | 44387.5417 | 0 | 6.7531 | 39.95
2021-07-10 13:30 | 44387.5625 | 0 | 7.1571 | 39.95
2021-07-10 14:00 | 44387.5833 | 0 | 7.6717 | 39.95
2021-07-10 14:30 | 44387.6042 | 0 | 8.1238 | 39.95
2021-07-10 15:00 | 44387.625 | 0 | 8.5629 | 39.95
2021-07-10 15:30 | 44387.6458 | 0 | 9.4889 | 39.95
2021-07-10 16:00 | 44387.6667 | 0 | 10.3457 | 39.95
2021-07-10 16:30 | 44387.6875 | 0 | 11.5332 | 39.95
2021-07-10 17:00 | 44387.7083 | 0 | 12.6387 | 39.95
2021-07-10 17:30 | 44387.7292 | 0 | 13.2787 | 39.95
2021-07-10 18:00 | 44387.75 | 0 | 13.6426 | 39.95
2021-07-10 18:30 | 44387.7708 | 0 | 13.4834 | 39.95
2021-07-10 19:00 | 44387.7917 | 0 | 13.0406 | 39.95
2021-07-10 19:30 | 44387.8125 | 0 | 13.0549 | 39.95
2021-07-10 20:00 | 44387.8333 | 0 | 12.8984 | 39.95
2021-07-10 20:30 | 44387.8542 | 0 | 12.2667 | 39.95
2021-07-10 21:00 | 44387.875 | 0 | 11.9107 | 39.95
2021-07-10 21:30 | 44387.8958 | 0 | 11.5452 | 39.95
2021-07-10 22:00 | 44387.9167 | 0 | 11.0505 | 39.95
2021-07-10 22:30 | 44387.9375 | 0 | 10.4737 | 39.95
2021-07-10 23:00 | 44387.9583 | 0 | 9.9077 | 39.95
2021-07-10 23:30 | 44387.9792 | 0 | 9.3272 | 39.95
2021-07-11 | 44388 | 0 | 8.79 | 39.95
2021-07-11 00:30 | 44388.0208 | 0 | 8.3229 | 39.95
2021-07-11 01:00 | 44388.0417 | 0 | 8.1757 | 39.95
2021-07-11 01:30 | 44388.0625 | 0 | 7.8378 | 39.95
2021-07-11 02:00 | 44388.0833 | 0 | 7.5536 | 39.95
2021-07-11 02:30 | 44388.1042 | 0 | 7.5287 | 39.95
2021-07-11 03:00 | 44388.125 | 0 | 7.4814 | 39.95
2021-07-11 03:30 | 44388.1458 | 0 | 7.4565 | 39.95
2021-07-11 04:00 | 44388.1667 | 0 | 7.3551 | 39.95
2021-07-11 04:30 | 44388.1875 | 0 | 7.387 | 39.95
2021-07-11 05:00 | 44388.2083 | 0 | 7.6432 | 39.95
2021-07-11 05:30 | 44388.2292 | 0 | 7.8483 | 39.95
2021-07-11 06:00 | 44388.25 | 0 | 8.3179 | 39.95
2021-07-11 06:30 | 44388.2708 | 0 | 8.668 | 39.95
2021-07-11 07:00 | 44388.2917 | 0 | 9.2701 | 39.95
2021-07-11 07:30 | 44388.3125 | 0 | 9.3519 | 39.95
2021-07-11 08:00 | 44388.3333 | 0 | 9.2234 | 39.95
2021-07-11 08:30 | 44388.3542 | 0 | 8.9906 | 39.95
2021-07-11 09:00 | 44388.375 | 0 | 8.6608 | 39.95
2021-07-11 09:30 | 44388.3958 | 0 | 8.2144 | 39.95
2021-07-11 10:00 | 44388.4167 | 0 | 7.6595 | 39.95
2021-07-11 10:30 | 44388.4375 | 0 | 7.2571 | 39.95
2021-07-11 11:00 | 44388.4583 | 0 | 6.8384 | 39.95
2021-07-11 11:30 | 44388.4792 | 0 | 6.4292 | 39.95
2021-07-11 12:00 | 44388.5 | 0 | 6.3029 | 39.95
2021-07-11 12:30 | 44388.5208 | 0 | 6.2211 | 39.95
2021-07-11 13:00 | 44388.5417 | 0 | 6.9468 | 39.95
2021-07-11 13:30 | 44388.5625 | 0 | 7.501 | 39.95
2021-07-11 14:00 | 44388.5833 | 0 | 8.4609 | 39.95
2021-07-11 14:30 | 44388.6042 | 0 | 7.732 | 39.95
2021-07-11 15:00 | 44388.625 | 0 | 8.9799 | 39.95
2021-07-11 15:30 | 44388.6458 | 0 | 10.0368 | 39.95
2021-07-11 16:00 | 44388.6667 | 0 | 10.4895 | 39.95
2021-07-11 16:30 | 44388.6875 | 0 | 11.2356 | 39.95
2021-07-11 17:00 | 44388.7083 | 0 | 12.0675 | 39.95
2021-07-11 17:30 | 44388.7292 | 0 | 12.8934 | 39.95
2021-07-11 18:00 | 44388.75 | 0 | 13.196 | 39.95
2021-07-11 18:30 | 44388.7708 | 0 | 13.2269 | 39.95
2021-07-11 19:00 | 44388.7917 | 0 | 13.0483 | 39.95
2021-07-11 19:30 | 44388.8125 | 0 | 12.7494 | 39.95
2021-07-11 20:00 | 44388.8333 | 0 | 12.4639 | 39.95
2021-07-11 20:30 | 44388.8542 | 0 | 11.9552 | 39.95
2021-07-11 21:00 | 44388.875 | 0 | 11.3817 | 39.95
2021-07-11 21:30 | 44388.8958 | 0 | 10.8882 | 39.95
2021-07-11 22:00 | 44388.9167 | 0 | 10.4266 | 39.95
2021-07-11 22:30 | 44388.9375 | 0 | 9.3798 | 39.95
2021-07-11 23:00 | 44388.9583 | 0 | 8.8217 | 39.95
2021-07-11 23:30 | 44388.9792 | 0 | 8.4271 | 39.95
2021-07-12 | 44389 | 0 | 8.0042 | 39.95
2021-07-12 00:30 | 44389.0208 | 0 | 7.811 | 39.95
2021-07-12 01:00 | 44389.0417 | 0 | 7.5536 | 39.95
2021-07-12 01:30 | 44389.0625 | 0 | 7.5089 | 39.95
2021-07-12 02:00 | 44389.0833 | 0 | 7.4814 | 39.95
2021-07-12 02:30 | 44389.1042 | 0 | 7.3895 | 39.95
2021-07-12 03:00 | 44389.125 | 0 | 7.4119 | 39.95
2021-07-12 03:30 | 44389.1458 | 0 | 7.7621 | 39.95
2021-07-12 04:00 | 44389.1667 | 0 | 8.0518 | 39.95
2021-07-12 04:30 | 44389.1875 | 0 | 8.5779 | 39.95
2021-07-12 05:00 | 44389.2083 | 0 | 9.5233 | 39.95
2021-07-12 05:30 | 44389.2292 | 0 | 10.5757 | 39.95
2021-07-12 06:00 | 44389.25 | 0 | 12.0713 | 39.95
2021-07-12 06:30 | 44389.2708 | 0 | 13.654 | 39.95
2021-07-12 07:00 | 44389.2917 | 0 | 14.4444 | 39.95
2021-07-12 07:30 | 44389.3125 | 0 | 14.5298 | 39.95
2021-07-12 08:00 | 44389.3333 | 0 | 13.6325 | 39.95
2021-07-12 08:30 | 44389.3542 | 0 | 12.442 | 39.95
2021-07-12 09:00 | 44389.375 | 0 | 11.6179 | 39.95
2021-07-12 09:30 | 44389.3958 | 0 | 10.851 | 39.95
2021-07-12 10:00 | 44389.4167 | 0 | 9.8879 | 39.95
2021-07-12 10:30 | 44389.4375 | 0 | 9.3528 | 39.95
2021-07-12 11:00 | 44389.4583 | 0 | 9.4433 | 39.95
2021-07-12 11:30 | 44389.4792 | 0 | 11.7373 | 39.95
2021-07-12 12:00 | 44389.5 | 0 | 9.2792 | 39.95
2021-07-12 12:30 | 44389.5208 | 0 | 10.8713 | 39.95
2021-07-12 13:00 | 44389.5417 | 0 | 11.2798 | 39.95
2021-07-12 13:30 | 44389.5625 | 0 | 10.9712 | 39.95
2021-07-12 14:00 | 44389.5833 | 0 | 11.4373 | 39.95
2021-07-12 14:30 | 44389.6042 | 0 | 11.8314 | 39.95
2021-07-12 15:00 | 44389.625 | 0 | 11.9777 | 39.95
2021-07-12 15:30 | 44389.6458 | 0 | 11.9709 | 39.95
2021-07-12 16:00 | 44389.6667 | 0 | 12.8066 | 39.95
2021-07-12 16:30 | 44389.6875 | 0 | 13.4982 | 39.95
2021-07-12 17:00 | 44389.7083 | 0 | 14.3407 | 39.95
2021-07-12 17:30 | 44389.7292 | 0 | 15.492 | 39.95
2021-07-12 18:00 | 44389.75 | 0 | 16.0879 | 39.95
2021-07-12 18:30 | 44389.7708 | 0 | 16.0821 | 39.95
2021-07-12 19:00 | 44389.7917 | 0 | 15.8465 | 39.95
2021-07-12 19:30 | 44389.8125 | 0 | 15.6054 | 39.95
2021-07-12 20:00 | 44389.8333 | 0 | 15.335 | 39.95
2021-07-12 20:30 | 44389.8542 | 0 | 14.6823 | 39.95
2021-07-12 21:00 | 44389.875 | 0 | 13.9181 | 39.95
2021-07-12 21:30 | 44389.8958 | 0 | 13.1441 | 39.95
2021-07-12 22:00 | 44389.9167 | 0 | 12.3467 | 39.95
2021-07-12 22:30 | 44389.9375 | 0 | 11.2281 | 39.95
2021-07-12 23:00 | 44389.9583 | 0 | 10.4018 | 39.95
2021-07-12 23:30 | 44389.9792 | 0 | 9.5968 | 39.95
2021-07-13 | 44390 | 0 | 8.9539 | 39.95
2021-07-13 00:30 | 44390.0208 | 0 | 8.5087 | 39.95
2021-07-13 01:00 | 44390.0417 | 0 | 8.5113 | 39.95
2021-07-13 01:30 | 44390.0625 | 0 | 8.2651 | 39.95
2021-07-13 02:00 | 44390.0833 | 0 | 8.2508 | 39.95
2021-07-13 02:30 | 44390.1042 | 0 | 8.1291 | 39.95
2021-07-13 03:00 | 44390.125 | 0 | 8.0567 | 39.95
2021-07-13 03:30 | 44390.1458 | 0 | 8.2454 | 39.95
2021-07-13 04:00 | 44390.1667 | 0 | 8.6376 | 39.95
2021-07-13 04:30 | 44390.1875 | 0 | 9.023 | 39.95
2021-07-13 05:00 | 44390.2083 | 0 | 9.8077 | 39.95
2021-07-13 05:30 | 44390.2292 | 0 | 10.9781 | 39.95
2021-07-13 06:00 | 44390.25 | 0 | 12.3138 | 39.95
2021-07-13 06:30 | 44390.2708 | 0 | 13.8992 | 39.95
2021-07-13 07:00 | 44390.2917 | 0 | 14.7942 | 39.95
2021-07-13 07:30 | 44390.3125 | 0 | 13.8925 | 39.95
2021-07-13 08:00 | 44390.3333 | 0 | 12.7519 | 39.95
2021-07-13 08:30 | 44390.3542 | 0 | 12.2228 | 39.95
2021-07-13 09:00 | 44390.375 | 0 | 11.4714 | 39.95
2021-07-13 09:30 | 44390.3958 | 0 | 10.637 | 39.95
2021-07-13 10:00 | 44390.4167 | 0 | 9.9468 | 39.95
2021-07-13 10:30 | 44390.4375 | 0 | 9.6597 | 39.95
2021-07-13 11:00 | 44390.4583 | 0 | 9.1766 | 39.95
2021-07-13 11:30 | 44390.4792 | 0 | 8.9854 | 39.95
2021-07-13 12:00 | 44390.5 | 0 | 8.771 | 39.95
2021-07-13 12:30 | 44390.5208 | 0 | 8.8592 | 39.95
2021-07-13 13:00 | 44390.5417 | 0 | 9.8759 | 39.95
2021-07-13 13:30 | 44390.5625 | 0 | 9.9512 | 39.95
2021-07-13 14:00 | 44390.5833 | 0 | 11.7208 | 39.95
2021-07-13 14:30 | 44390.6042 | 0 | 12.1172 | 39.95
2021-07-13 15:00 | 44390.625 | 0 | 11.8778 | 39.95
2021-07-13 15:30 | 44390.6458 | 0 | 11.5473 | 39.95
2021-07-13 16:00 | 44390.6667 | 0 | 12.0459 | 39.95
2021-07-13 16:30 | 44390.6875 | 0 | 12.9048 | 39.95
2021-07-13 17:00 | 44390.7083 | 0 | 13.8361 | 39.95
2021-07-13 17:30 | 44390.7292 | 0 | 14.6416 | 39.95
2021-07-13 18:00 | 44390.75 | 0 | 15.0759 | 39.95
2021-07-13 18:30 | 44390.7708 | 0 | 15.4716 | 39.95
2021-07-13 19:00 | 44390.7917 | 0 | 15.1716 | 39.95
2021-07-13 19:30 | 44390.8125 | 0 | 15.1192 | 39.95
2021-07-13 20:00 | 44390.8333 | 0 | 14.8752 | 39.95
2021-07-13 20:30 | 44390.8542 | 0 | 14.3436 | 39.95
2021-07-13 21:00 | 44390.875 | 0 | 13.6141 | 39.95
2021-07-13 21:30 | 44390.8958 | 0 | 12.8867 | 39.95
2021-07-13 22:00 | 44390.9167 | 0 | 12.0165 | 39.95
2021-07-13 22:30 | 44390.9375 | 0 | 11.0191 | 39.95
2021-07-13 23:00 | 44390.9583 | 0 | 10.2438 | 39.95
2021-07-13 23:30 | 44390.9792 | 0 | 9.6374 | 39.95
2021-07-14 | 44391 | 0 | 9.0803 | 39.95
2021-07-14 00:30 | 44391.0208 | 0 | 8.4747 | 39.95
2021-07-14 01:00 | 44391.0417 | 0 | 8.2599 | 39.95
2021-07-14 01:30 | 44391.0625 | 0 | 8.2184 | 39.95
2021-07-14 02:00 | 44391.0833 | 0 | 8.1342 | 39.95
2021-07-14 02:30 | 44391.1042 | 0 | 8.0647 | 39.95
2021-07-14 03:00 | 44391.125 | 0 | 8.1463 | 39.95
2021-07-14 03:30 | 44391.1458 | 0 | 8.2067 | 39.95
2021-07-14 04:00 | 44391.1667 | 0 | 8.4512 | 39.95
2021-07-14 04:30 | 44391.1875 | 0 | 8.968 | 39.95
2021-07-14 05:00 | 44391.2083 | 0 | 9.6199 | 39.95
2021-07-14 05:30 | 44391.2292 | 0 | 10.7246 | 39.95
2021-07-14 06:00 | 44391.25 | 0 | 11.8802 | 39.95
2021-07-14 06:30 | 44391.2708 | 0 | 13.4866 | 39.95
2021-07-14 07:00 | 44391.2917 | 0 | 14.3028 | 39.95
2021-07-14 07:30 | 44391.3125 | 0 | 14.7842 | 39.95
2021-07-14 08:00 | 44391.3333 | 0 | 14.4085 | 39.95
2021-07-14 08:30 | 44391.3542 | 0 | 13.4218 | 39.95
2021-07-14 09:00 | 44391.375 | 0 | 11.9284 | 39.95
2021-07-14 09:30 | 44391.3958 | 0 | 10.8174 | 39.95
2021-07-14 10:00 | 44391.4167 | 0 | 10.6737 | 39.95
2021-07-14 10:30 | 44391.4375 | 0 | 9.4407 | 39.95
2021-07-14 11:00 | 44391.4583 | 0 | 11.2518 | 39.95
2021-07-14 11:30 | 44391.4792 | 0 | 9.2634 | 39.95
2021-07-14 12:00 | 44391.5 | 0 | 10.4801 | 39.95
2021-07-14 12:30 | 44391.5208 | 0 | 9.4933 | 39.95
2021-07-14 13:00 | 44391.5417 | 0 | 9.9255 | 39.95
2021-07-14 13:30 | 44391.5625 | 0 | 11.1064 | 39.95
2021-07-14 14:00 | 44391.5833 | 0 | 11.692 | 39.95
2021-07-14 14:30 | 44391.6042 | 0 | 11.3803 | 39.95
2021-07-14 15:00 | 44391.625 | 0 | 11.1534 | 39.95
2021-07-14 15:30 | 44391.6458 | 0 | 11.2543 | 39.95
2021-07-14 16:00 | 44391.6667 | 0 | 12.0938 | 39.95
2021-07-14 16:30 | 44391.6875 | 0 | 12.718 | 39.95
2021-07-14 17:00 | 44391.7083 | 0 | 13.8275 | 39.95
2021-07-14 17:30 | 44391.7292 | 0 | 14.7453 | 39.95
2021-07-14 18:00 | 44391.75 | 0 | 14.9133 | 39.95
2021-07-14 18:30 | 44391.7708 | 0 | 15.2514 | 39.95
2021-07-14 19:00 | 44391.7917 | 0 | 14.8327 | 39.95
2021-07-14 19:30 | 44391.8125 | 0 | 14.7593 | 39.95
2021-07-14 20:00 | 44391.8333 | 0 | 14.291 | 39.95
2021-07-14 20:30 | 44391.8542 | 0 | 13.6034 | 39.95
2021-07-14 21:00 | 44391.875 | 0 | 12.9023 | 39.95
2021-07-14 21:30 | 44391.8958 | 0 | 12.3568 | 39.95
2021-07-14 22:00 | 44391.9167 | 0 | 11.6844 | 39.95
2021-07-14 22:30 | 44391.9375 | 0 | 10.8557 | 39.95
2021-07-14 23:00 | 44391.9583 | 0 | 10.072 | 39.95
2021-07-14 23:30 | 44391.9792 | 0 | 9.3995 | 39.95
2021-07-15 | 44392 | 0 | 8.9236 | 39.95
2021-07-15 00:30 | 44392.0208 | 0 | 8.4865 | 39.95
2021-07-15 01:00 | 44392.0417 | 0 | 8.2705 | 39.95
2021-07-15 01:30 | 44392.0625 | 0 | 8.1359 | 39.95
2021-07-15 02:00 | 44392.0833 | 0 | 8.2083 | 39.95
2021-07-15 02:30 | 44392.1042 | 0 | 8.0028 | 39.95
2021-07-15 03:00 | 44392.125 | 0 | 8.0174 | 39.95
2021-07-15 03:30 | 44392.1458 | 0 | 8.099 | 39.95
2021-07-15 04:00 | 44392.1667 | 0 | 8.4495 | 39.95
2021-07-15 04:30 | 44392.1875 | 0 | 8.8397 | 39.95
2021-07-15 05:00 | 44392.2083 | 0 | 9.5287 | 39.95
2021-07-15 05:30 | 44392.2292 | 0 | 10.2243 | 39.95
2021-07-15 06:00 | 44392.25 | 0 | 11.4874 | 39.95
2021-07-15 06:30 | 44392.2708 | 0 | 12.4717 | 39.95
2021-07-15 07:00 | 44392.2917 | 0 | 13.3596 | 39.95
2021-07-15 07:30 | 44392.3125 | 0 | 14.1017 | 39.95
2021-07-15 08:00 | 44392.3333 | 0 | 14.1787 | 39.95
2021-07-15 08:30 | 44392.3542 | 0 | 13.1705 | 39.95
2021-07-15 09:00 | 44392.375 | 0 | 13.0973 | 39.95
2021-07-15 09:30 | 44392.3958 | 0 | 12.8011 | 39.95
2021-07-15 10:00 | 44392.4167 | 0 | 11.7905 | 39.95
2021-07-15 10:30 | 44392.4375 | 0 | 11.503 | 39.95
2021-07-15 11:00 | 44392.4583 | 0 | 11.4872 | 39.95
2021-07-15 11:30 | 44392.4792 | 0 | 11.0074 | 39.95
2021-07-15 12:00 | 44392.5 | 0 | 10.072 | 39.95
2021-07-15 12:30 | 44392.5208 | 0 | 11.4675 | 39.95
2021-07-15 13:00 | 44392.5417 | 0 | 10.6341 | 39.95
2021-07-15 13:30 | 44392.5625 | 0 | 11.3002 | 39.95
2021-07-15 14:00 | 44392.5833 | 0 | 10.8924 | 39.95
2021-07-15 14:30 | 44392.6042 | 0 | 11.6017 | 39.95
2021-07-15 15:00 | 44392.625 | 0 | 11.9599 | 39.95
2021-07-15 15:30 | 44392.6458 | 0 | 11.7095 | 39.95
2021-07-15 16:00 | 44392.6667 | 0 | 12.5732 | 39.95
2021-07-15 16:30 | 44392.6875 | 0 | 13.2293 | 39.95
2021-07-15 17:00 | 44392.7083 | 0 | 13.6573 | 39.95
2021-07-15 17:30 | 44392.7292 | 0 | 14.278 | 39.95
2021-07-15 18:00 | 44392.75 | 0 | 14.2104 | 39.95
2021-07-15 18:30 | 44392.7708 | 0 | 14.5576 | 39.95
2021-07-15 19:00 | 44392.7917 | 0 | 14.3531 | 39.95
2021-07-15 19:30 | 44392.8125 | 0 | 14.3024 | 39.95
2021-07-15 20:00 | 44392.8333 | 0 | 13.973 | 39.95
2021-07-15 20:30 | 44392.8542 | 0 | 13.2647 | 39.95
2021-07-15 21:00 | 44392.875 | 0 | 12.586 | 39.95
2021-07-15 21:30 | 44392.8958 | 0 | 12.2881 | 39.95
2021-07-15 22:00 | 44392.9167 | 0 | 11.6837 | 39.95
2021-07-15 22:30 | 44392.9375 | 0 | 10.8651 | 39.95
2021-07-15 23:00 | 44392.9583 | 0 | 10.0745 | 39.95
2021-07-15 23:30 | 44392.9792 | 0 | 9.5136 | 39.95
2021-07-16 | 44393 | 0 | 8.9649 | 39.95
2021-07-16 00:30 | 44393.0208 | 0 | 8.5169 | 39.95
2021-07-16 01:00 | 44393.0417 | 0 | 8.2748 | 39.95
2021-07-16 01:30 | 44393.0625 | 0 | 8.1714 | 39.95
2021-07-16 02:00 | 44393.0833 | 0 | 8.144 | 39.95
2021-07-16 02:30 | 44393.1042 | 0 | 7.9779 | 39.95
2021-07-16 03:00 | 44393.125 | 0 | 7.9728 | 39.95
2021-07-16 03:30 | 44393.1458 | 0 | 8.2585 | 39.95
2021-07-16 04:00 | 44393.1667 | 0 | 8.4263 | 39.95
2021-07-16 04:30 | 44393.1875 | 0 | 8.7555 | 39.95
2021-07-16 05:00 | 44393.2083 | 0 | 9.4275 | 39.95
2021-07-16 05:30 | 44393.2292 | 0 | 10.353 | 39.95
2021-07-16 06:00 | 44393.25 | 0 | 11.177 | 39.95
2021-07-16 06:30 | 44393.2708 | 0 | 12.0835 | 39.95
2021-07-16 07:00 | 44393.2917 | 0 | 13.1198 | 39.95
2021-07-16 07:30 | 44393.3125 | 0 | 12.8327 | 39.95
2021-07-16 08:00 | 44393.3333 | 0 | 12.487 | 39.95
2021-07-16 08:30 | 44393.3542 | 0 | 12.2295 | 39.95
2021-07-16 09:00 | 44393.375 | 0 | 12.9533 | 39.95
2021-07-16 09:30 | 44393.3958 | 0 | 12.9495 | 39.95
2021-07-16 10:00 | 44393.4167 | 0 | 11.9087 | 39.95
2021-07-16 10:30 | 44393.4375 | 0 | 11.0715 | 39.95
2021-07-16 11:00 | 44393.4583 | 0 | 9.8593 | 39.95
2021-07-16 11:30 | 44393.4792 | 0 | 10.9626 | 39.95
2021-07-16 12:00 | 44393.5 | 0 | 11.9669 | 39.95
2021-07-16 12:30 | 44393.5208 | 0 | 12.2051 | 39.95
2021-07-16 13:00 | 44393.5417 | 0 | 12.5809 | 39.95
2021-07-16 13:30 | 44393.5625 | 0 | 11.8974 | 39.95
2021-07-16 14:00 | 44393.5833 | 0 | 12.3293 | 39.95
2021-07-16 14:30 | 44393.6042 | 0 | 11.9289 | 39.95
2021-07-16 15:00 | 44393.625 | 0 | 11.913 | 39.95
2021-07-16 15:30 | 44393.6458 | 0 | 12.9169 | 39.95
2021-07-16 16:00 | 44393.6667 | 0 | 12.5815 | 39.95
2021-07-16 16:30 | 44393.6875 | 0 | 13.0841 | 39.95
2021-07-16 17:00 | 44393.7083 | 0 | 13.8983 | 39.95
2021-07-16 17:30 | 44393.7292 | 0 | 14.2056 | 39.95
2021-07-16 18:00 | 44393.75 | 0 | 14.2362 | 39.95
2021-07-16 18:30 | 44393.7708 | 0 | 14.2431 | 39.95
2021-07-16 19:00 | 44393.7917 | 0 | 14.1692 | 39.95
2021-07-16 19:30 | 44393.8125 | 0 | 14.1142 | 39.95
2021-07-16 20:00 | 44393.8333 | 0 | 13.7882 | 39.95
2021-07-16 20:30 | 44393.8542 | 0 | 13.2699 | 39.95
2021-07-16 21:00 | 44393.875 | 0 | 12.8114 | 39.95
2021-07-16 21:30 | 44393.8958 | 0 | 12.3948 | 39.95
2021-07-16 22:00 | 44393.9167 | 0 | 11.8757 | 39.95
2021-07-16 22:30 | 44393.9375 | 0 | 10.998 | 39.95
2021-07-16 23:00 | 44393.9583 | 0 | 10.1404 | 39.95
2021-07-16 23:30 | 44393.9792 | 0 | 9.7219 | 39.95
2021-07-17 | 44394 | 0 | 9.0897 | 39.95
2021-07-17 00:30 | 44394.0208 | 0 | 8.5585 | 39.95
2021-07-17 01:00 | 44394.0417 | 0 | 8.2165 | 39.95
2021-07-17 01:30 | 44394.0625 | 0 | 8.278 | 39.95
2021-07-17 02:00 | 44394.0833 | 0 | 8.0277 | 39.95
2021-07-17 02:30 | 44394.1042 | 0 | 7.9281 | 39.95
2021-07-17 03:00 | 44394.125 | 0 | 7.9083 | 39.95
2021-07-17 03:30 | 44394.1458 | 0 | 7.8637 | 39.95
2021-07-17 04:00 | 44394.1667 | 0 | 7.8139 | 39.95
2021-07-17 04:30 | 44394.1875 | 0 | 7.9427 | 39.95
2021-07-17 05:00 | 44394.2083 | 0 | 8.2041 | 39.95
2021-07-17 05:30 | 44394.2292 | 0 | 8.6509 | 39.95
2021-07-17 06:00 | 44394.25 | 0 | 9.1648 | 39.95
2021-07-17 06:30 | 44394.2708 | 0 | 9.7674 | 39.95
2021-07-17 07:00 | 44394.2917 | 0 | 10.2985 | 39.95
2021-07-17 07:30 | 44394.3125 | 0 | 10.1312 | 39.95
2021-07-17 08:00 | 44394.3333 | 0 | 9.8632 | 39.95
2021-07-17 08:30 | 44394.3542 | 0 | 9.3768 | 39.95
2021-07-17 09:00 | 44394.375 | 0 | 8.9116 | 39.95
2021-07-17 09:30 | 44394.3958 | 0 | 8.4013 | 39.95
2021-07-17 10:00 | 44394.4167 | 0 | 7.7358 | 39.95
2021-07-17 10:30 | 44394.4375 | 0 | 7.2775 | 39.95
2021-07-17 11:00 | 44394.4583 | 0 | 6.8155 | 39.95
2021-07-17 11:30 | 44394.4792 | 0 | 6.5477 | 39.95
2021-07-17 12:00 | 44394.5 | 0 | 6.3974 | 39.95
2021-07-17 12:30 | 44394.5208 | 0 | 6.3794 | 39.95
2021-07-17 13:00 | 44394.5417 | 0 | 6.5632 | 39.95
2021-07-17 13:30 | 44394.5625 | 0 | 6.8046 | 39.95
2021-07-17 14:00 | 44394.5833 | 0 | 7.1875 | 39.95
2021-07-17 14:30 | 44394.6042 | 0 | 7.6463 | 39.95
2021-07-17 15:00 | 44394.625 | 0 | 8.3787 | 39.95
2021-07-17 15:30 | 44394.6458 | 0 | 8.9952 | 39.95
2021-07-17 16:00 | 44394.6667 | 0 | 9.8138 | 39.95
2021-07-17 16:30 | 44394.6875 | 0 | 10.6719 | 39.95
2021-07-17 17:00 | 44394.7083 | 0 | 11.6711 | 39.95
2021-07-17 17:30 | 44394.7292 | 0 | 12.2555 | 39.95
2021-07-17 18:00 | 44394.75 | 0 | 12.3872 | 39.95
2021-07-17 18:30 | 44394.7708 | 0 | 12.6824 | 39.95
2021-07-17 19:00 | 44394.7917 | 0 | 12.2858 | 39.95
2021-07-17 19:30 | 44394.8125 | 0 | 12.0396 | 39.95
2021-07-17 20:00 | 44394.8333 | 0 | 11.7594 | 39.95
2021-07-17 20:30 | 44394.8542 | 0 | 11.4466 | 39.95
2021-07-17 21:00 | 44394.875 | 0 | 11.0695 | 39.95
2021-07-17 21:30 | 44394.8958 | 0 | 10.8164 | 39.95
2021-07-17 22:00 | 44394.9167 | 0 | 10.492 | 39.95
2021-07-17 22:30 | 44394.9375 | 0 | 9.8343 | 39.95
2021-07-17 23:00 | 44394.9583 | 0 | 9.2503 | 39.95
2021-07-17 23:30 | 44394.9792 | 0 | 8.8815 | 39.95
2021-07-18 | 44395 | 0 | 8.353 | 39.95
2021-07-18 00:30 | 44395.0208 | 0 | 7.8344 | 39.95
2021-07-18 01:00 | 44395.0417 | 0 | 7.6223 | 39.95
2021-07-18 01:30 | 44395.0625 | 0 | 7.4891 | 39.95
2021-07-18 02:00 | 44395.0833 | 0 | 7.3947 | 39.95
2021-07-18 02:30 | 44395.1042 | 0 | 7.2235 | 39.95
2021-07-18 03:00 | 44395.125 | 0 | 7.2976 | 39.95
2021-07-18 03:30 | 44395.1458 | 0 | 7.3921 | 39.95
2021-07-18 04:00 | 44395.1667 | 0 | 7.3251 | 39.95
2021-07-18 04:30 | 44395.1875 | 0 | 7.2656 | 39.95
2021-07-18 05:00 | 44395.2083 | 0 | 7.4514 | 39.95
2021-07-18 05:30 | 44395.2292 | 0 | 7.6699 | 39.95
2021-07-18 06:00 | 44395.25 | 0 | 8.1098 | 39.95
2021-07-18 06:30 | 44395.2708 | 0 | 8.3453 | 39.95
2021-07-18 07:00 | 44395.2917 | 0 | 8.5378 | 39.95
2021-07-18 07:30 | 44395.3125 | 0 | 8.7438 | 39.95
2021-07-18 08:00 | 44395.3333 | 0 | 8.6453 | 39.95
2021-07-18 08:30 | 44395.3542 | 0 | 8.4447 | 39.95
2021-07-18 09:00 | 44395.375 | 0 | 8.0226 | 39.95
2021-07-18 09:30 | 44395.3958 | 0 | 7.6397 | 39.95
2021-07-18 10:00 | 44395.4167 | 0 | 7.1733 | 39.95
2021-07-18 10:30 | 44395.4375 | 0 | 6.8192 | 39.95
2021-07-18 11:00 | 44395.4583 | 0 | 6.4044 | 39.95
2021-07-18 11:30 | 44395.4792 | 0 | 6.1129 | 39.95
2021-07-18 12:00 | 44395.5 | 0 | 6.0101 | 39.95
2021-07-18 12:30 | 44395.5208 | 0 | 5.9233 | 39.95
2021-07-18 13:00 | 44395.5417 | 0 | 5.8288 | 39.95
2021-07-18 13:30 | 44395.5625 | 0 | 6.0971 | 39.95
2021-07-18 14:00 | 44395.5833 | 0 | 6.5617 | 39.95
2021-07-18 14:30 | 44395.6042 | 0 | 7.267 | 39.95
2021-07-18 15:00 | 44395.625 | 0 | 7.954 | 39.95
2021-07-18 15:30 | 44395.6458 | 0 | 8.7609 | 39.95
2021-07-18 16:00 | 44395.6667 | 0 | 9.7753 | 39.95
2021-07-18 16:30 | 44395.6875 | 0 | 10.9981 | 39.95
2021-07-18 17:00 | 44395.7083 | 0 | 12.0063 | 39.95
2021-07-18 17:30 | 44395.7292 | 0 | 12.9019 | 39.95
2021-07-18 18:00 | 44395.75 | 0 | 13.3996 | 39.95
2021-07-18 18:30 | 44395.7708 | 0 | 13.4145 | 39.95
2021-07-18 19:00 | 44395.7917 | 0 | 13.1642 | 39.95
2021-07-18 19:30 | 44395.8125 | 0 | 12.9778 | 39.95
2021-07-18 20:00 | 44395.8333 | 0 | 12.6492 | 39.95
2021-07-18 20:30 | 44395.8542 | 0 | 12.2262 | 39.95
2021-07-18 21:00 | 44395.875 | 0 | 11.5791 | 39.95
2021-07-18 21:30 | 44395.8958 | 0 | 10.9845 | 39.95
2021-07-18 22:00 | 44395.9167 | 0 | 10.3326 | 39.95
2021-07-18 22:30 | 44395.9375 | 0 | 9.3933 | 39.95
2021-07-18 23:00 | 44395.9583 | 0 | 8.7206 | 39.95
2021-07-18 23:30 | 44395.9792 | 0 | 8.3572 | 39.95
2021-07-19 | 44396 | 0 | 7.983 | 39.95
2021-07-19 00:30 | 44396.0208 | 0 | 7.7042 | 39.95
2021-07-19 01:00 | 44396.0417 | 0 | 7.5207 | 39.95
2021-07-19 01:30 | 44396.0625 | 0 | 7.4368 | 39.95
2021-07-19 02:00 | 44396.0833 | 0 | 7.417 | 39.95
2021-07-19 02:30 | 44396.1042 | 0 | 7.3723 | 39.95
2021-07-19 03:00 | 44396.125 | 0 | 7.32 | 39.95
2021-07-19 03:30 | 44396.1458 | 0 | 7.6728 | 39.95
2021-07-19 04:00 | 44396.1667 | 0 | 8.0037 | 39.95
2021-07-19 04:30 | 44396.1875 | 0 | 8.3516 | 39.95
2021-07-19 05:00 | 44396.2083 | 0 | 9.2492 | 39.95
2021-07-19 05:30 | 44396.2292 | 0 | 10.2775 | 39.95
2021-07-19 06:00 | 44396.25 | 0 | 12.0087 | 39.95
2021-07-19 06:30 | 44396.2708 | 0 | 13.6617 | 39.95
2021-07-19 07:00 | 44396.2917 | 0 | 14.8626 | 39.95
2021-07-19 07:30 | 44396.3125 | 0 | 15.4193 | 39.95
2021-07-19 08:00 | 44396.3333 | 0 | 13.795 | 39.95
2021-07-19 08:30 | 44396.3542 | 0 | 13.3416 | 39.95
2021-07-19 09:00 | 44396.375 | 0 | 12.1625 | 39.95
2021-07-19 09:30 | 44396.3958 | 0 | 10.7839 | 39.95
2021-07-19 10:00 | 44396.4167 | 0 | 9.901 | 39.95
2021-07-19 10:30 | 44396.4375 | 0 | 9.4767 | 39.95
2021-07-19 11:00 | 44396.4583 | 0 | 8.8383 | 39.95
2021-07-19 11:30 | 44396.4792 | 0 | 8.6496 | 39.95
2021-07-19 12:00 | 44396.5 | 0 | 8.4743 | 39.95
2021-07-19 12:30 | 44396.5208 | 0 | 8.2679 | 39.95
2021-07-19 13:00 | 44396.5417 | 0 | 8.4635 | 39.95
2021-07-19 13:30 | 44396.5625 | 0 | 8.7344 | 39.95
2021-07-19 14:00 | 44396.5833 | 0 | 9.4195 | 39.95
2021-07-19 14:30 | 44396.6042 | 0 | 10.3923 | 39.95
2021-07-19 15:00 | 44396.625 | 0 | 10.462 | 39.95
2021-07-19 15:30 | 44396.6458 | 0 | 11.3104 | 39.95
2021-07-19 16:00 | 44396.6667 | 0 | 11.7104 | 39.95
2021-07-19 16:30 | 44396.6875 | 0 | 12.5567 | 39.95
2021-07-19 17:00 | 44396.7083 | 0 | 13.634 | 39.95
2021-07-19 17:30 | 44396.7292 | 0 | 14.8534 | 39.95
2021-07-19 18:00 | 44396.75 | 0 | 15.3033 | 39.95
2021-07-19 18:30 | 44396.7708 | 0 | 15.782 | 39.95
2021-07-19 19:00 | 44396.7917 | 0 | 15.3575 | 39.95
2021-07-19 19:30 | 44396.8125 | 0 | 15.1467 | 39.95
2021-07-19 20:00 | 44396.8333 | 0 | 14.781 | 39.95
2021-07-19 20:30 | 44396.8542 | 0 | 14.0432 | 39.95
2021-07-19 21:00 | 44396.875 | 0 | 13.4419 | 39.95
2021-07-19 21:30 | 44396.8958 | 0 | 12.8286 | 39.95
2021-07-19 22:00 | 44396.9167 | 0 | 11.9947 | 39.95
2021-07-19 22:30 | 44396.9375 | 0 | 10.9297 | 39.95
2021-07-19 23:00 | 44396.9583 | 0 | 10.2298 | 39.95
2021-07-19 23:30 | 44396.9792 | 0 | 9.6371 | 39.95
2021-07-20 | 44397 | 0 | 9.0508 | 39.95
2021-07-20 00:30 | 44397.0208 | 0 | 8.6722 | 39.95
2021-07-20 01:00 | 44397.0417 | 0 | 8.6006 | 39.95
2021-07-20 01:30 | 44397.0625 | 0 | 8.3379 | 39.95
2021-07-20 02:00 | 44397.0833 | 0 | 8.278 | 39.95
2021-07-20 02:30 | 44397.1042 | 0 | 8.1145 | 39.95
2021-07-20 03:00 | 44397.125 | 0 | 8.1637 | 39.95
2021-07-20 03:30 | 44397.1458 | 0 | 8.3032 | 39.95
2021-07-20 04:00 | 44397.1667 | 0 | 8.6139 | 39.95
2021-07-20 04:30 | 44397.1875 | 0 | 9.0709 | 39.95
2021-07-20 05:00 | 44397.2083 | 0 | 10.087 | 39.95
2021-07-20 05:30 | 44397.2292 | 0 | 11.3893 | 39.95
2021-07-20 06:00 | 44397.25 | 0 | 13.217 | 39.95
2021-07-20 06:30 | 44397.2708 | 0 | 15.1033 | 39.95
2021-07-20 07:00 | 44397.2917 | 0 | 16.1024 | 39.95
2021-07-20 07:30 | 44397.3125 | 0 | 15.7026 | 39.95
2021-07-20 08:00 | 44397.3333 | 0 | 14.0685 | 39.95
2021-07-20 08:30 | 44397.3542 | 0 | 12.6744 | 39.95
2021-07-20 09:00 | 44397.375 | 0 | 11.5441 | 39.95
2021-07-20 09:30 | 44397.3958 | 0 | 10.6751 | 39.95
2021-07-20 10:00 | 44397.4167 | 0 | 10.0268 | 39.95
2021-07-20 10:30 | 44397.4375 | 0 | 9.5661 | 39.95
2021-07-20 11:00 | 44397.4583 | 0 | 9.1239 | 39.95
2021-07-20 11:30 | 44397.4792 | 0 | 8.7842 | 39.95
2021-07-20 12:00 | 44397.5 | 0 | 8.6075 | 39.95
2021-07-20 12:30 | 44397.5208 | 0 | 8.8143 | 39.95
2021-07-20 13:00 | 44397.5417 | 0 | 8.7415 | 39.95
2021-07-20 13:30 | 44397.5625 | 0 | 8.9855 | 39.95
2021-07-20 14:00 | 44397.5833 | 0 | 9.3148 | 39.95
2021-07-20 14:30 | 44397.6042 | 0 | 10.1487 | 39.95
2021-07-20 15:00 | 44397.625 | 0 | 10.6435 | 39.95
2021-07-20 15:30 | 44397.6458 | 0 | 11.1214 | 39.95
2021-07-20 16:00 | 44397.6667 | 0 | 12.1249 | 39.95
2021-07-20 16:30 | 44397.6875 | 0 | 13.0481 | 39.95
2021-07-20 17:00 | 44397.7083 | 0 | 14.2516 | 39.95
2021-07-20 17:30 | 44397.7292 | 0 | 15.5425 | 39.95
2021-07-20 18:00 | 44397.75 | 0 | 16.0008 | 39.95
2021-07-20 18:30 | 44397.7708 | 0 | 16.4593 | 39.95
2021-07-20 19:00 | 44397.7917 | 0 | 16.3475 | 39.95
2021-07-20 19:30 | 44397.8125 | 0 | 16.0097 | 39.95
2021-07-20 20:00 | 44397.8333 | 0 | 15.6683 | 39.95
2021-07-20 20:30 | 44397.8542 | 0 | 14.8387 | 39.95
2021-07-20 21:00 | 44397.875 | 0 | 14.2929 | 39.95
2021-07-20 21:30 | 44397.8958 | 0 | 13.3995 | 39.95
2021-07-20 22:00 | 44397.9167 | 0 | 12.6263 | 39.95
2021-07-20 22:30 | 44397.9375 | 0 | 11.3718 | 39.95
2021-07-20 23:00 | 44397.9583 | 0 | 10.5855 | 39.95
2021-07-20 23:30 | 44397.9792 | 0 | 9.9509 | 39.95
2021-07-21 | 44398 | 0 | 9.2356 | 39.95
2021-07-21 00:30 | 44398.0208 | 0 | 8.9349 | 39.95
2021-07-21 01:00 | 44398.0417 | 0 | 8.7538 | 39.95
2021-07-21 01:30 | 44398.0625 | 0 | 8.5465 | 39.95
2021-07-21 02:00 | 44398.0833 | 0 | 8.4813 | 39.95
2021-07-21 02:30 | 44398.1042 | 0 | 8.3129 | 39.95
2021-07-21 03:00 | 44398.125 | 0 | 8.4168 | 39.95
2021-07-21 03:30 | 44398.1458 | 0 | 8.4366 | 39.95
2021-07-21 04:00 | 44398.1667 | 0 | 8.635 | 39.95
2021-07-21 04:30 | 44398.1875 | 0 | 9.241 | 39.95
2021-07-21 05:00 | 44398.2083 | 0 | 10.0039 | 39.95
2021-07-21 05:30 | 44398.2292 | 0 | 11.4041 | 39.95
2021-07-21 06:00 | 44398.25 | 0 | 12.9819 | 39.95
2021-07-21 06:30 | 44398.2708 | 0 | 14.4127 | 39.95
2021-07-21 07:00 | 44398.2917 | 0 | 15.7071 | 39.95
2021-07-21 07:30 | 44398.3125 | 0 | 15.4417 | 39.95
2021-07-21 08:00 | 44398.3333 | 0 | 14.4414 | 39.95
2021-07-21 08:30 | 44398.3542 | 0 | 12.7953 | 39.95
2021-07-21 09:00 | 44398.375 | 0 | 11.7555 | 39.95
2021-07-21 09:30 | 44398.3958 | 0 | 11.1786 | 39.95
2021-07-21 10:00 | 44398.4167 | 0 | 10.6693 | 39.95
2021-07-21 10:30 | 44398.4375 | 0 | 10.3695 | 39.95
2021-07-21 11:00 | 44398.4583 | 0 | 9.8348 | 39.95
2021-07-21 11:30 | 44398.4792 | 0 | 9.6082 | 39.95
2021-07-21 12:00 | 44398.5 | 0 | 9.5383 | 39.95
2021-07-21 12:30 | 44398.5208 | 0 | 9.4743 | 39.95
2021-07-21 13:00 | 44398.5417 | 0 | 9.5881 | 39.95
2021-07-21 13:30 | 44398.5625 | 0 | 10.3712 | 39.95
2021-07-21 14:00 | 44398.5833 | 0 | 10.3268 | 39.95
2021-07-21 14:30 | 44398.6042 | 0 | 10.6352 | 39.95
2021-07-21 15:00 | 44398.625 | 0 | 11.177 | 39.95
2021-07-21 15:30 | 44398.6458 | 0 | 11.9051 | 39.95
2021-07-21 16:00 | 44398.6667 | 0 | 12.4881 | 39.95
2021-07-21 16:30 | 44398.6875 | 0 | 13.8539 | 39.95
2021-07-21 17:00 | 44398.7083 | 0 | 15.3892 | 39.95
2021-07-21 17:30 | 44398.7292 | 0 | 16.8462 | 39.95
2021-07-21 18:00 | 44398.75 | 0 | 17.5616 | 39.95
2021-07-21 18:30 | 44398.7708 | 0 | 18.0633 | 39.95
2021-07-21 19:00 | 44398.7917 | 0 | 17.6923 | 39.95
2021-07-21 19:30 | 44398.8125 | 0 | 17.7671 | 39.95
2021-07-21 20:00 | 44398.8333 | 0 | 17.4278 | 39.95
2021-07-21 20:30 | 44398.8542 | 0 | 16.7206 | 39.95
2021-07-21 21:00 | 44398.875 | 0 | 15.7085 | 39.95
2021-07-21 21:30 | 44398.8958 | 0 | 14.8431 | 39.95
2021-07-21 22:00 | 44398.9167 | 0 | 13.8461 | 39.95
2021-07-21 22:30 | 44398.9375 | 0 | 12.5281 | 39.95
2021-07-21 23:00 | 44398.9583 | 0 | 11.3907 | 39.95
2021-07-21 23:30 | 44398.9792 | 0 | 10.5842 | 39.95
2021-07-22 | 44399 | 0 | 9.9179 | 39.95
2021-07-22 00:30 | 44399.0208 | 0 | 9.4048 | 39.95
2021-07-22 01:00 | 44399.0417 | 0 | 9.1807 | 39.95
2021-07-22 01:30 | 44399.0625 | 0 | 8.8638 | 39.95
2021-07-22 02:00 | 44399.0833 | 0 | 8.8039 | 39.95
2021-07-22 02:30 | 44399.1042 | 0 | 8.7538 | 39.95
2021-07-22 03:00 | 44399.125 | 0 | 8.7948 | 39.95
2021-07-22 03:30 | 44399.1458 | 0 | 8.8884 | 39.95
2021-07-22 04:00 | 44399.1667 | 0 | 9.2662 | 39.95
2021-07-22 04:30 | 44399.1875 | 0 | 9.7779 | 39.95
2021-07-22 05:00 | 44399.2083 | 0 | 11.0469 | 39.95
2021-07-22 05:30 | 44399.2292 | 0 | 12.2792 | 39.95
2021-07-22 06:00 | 44399.25 | 0 | 14.3186 | 39.95
2021-07-22 06:30 | 44399.2708 | 0 | 16.0478 | 39.95
2021-07-22 07:00 | 44399.2917 | 0 | 17.2379 | 39.95
2021-07-22 07:30 | 44399.3125 | 0 | 16.7862 | 39.95
2021-07-22 08:00 | 44399.3333 | 0 | 15.6295 | 39.95
2021-07-22 08:30 | 44399.3542 | 0 | 1.0041 | 39.95
2021-07-22 09:00 | 44399.375 | 0 | 0.37966 | 39.95
2021-07-22 09:30 | 44399.3958 | 0 | 0.37966 | 39.95
2021-07-22 10:00 | 44399.4167 | 0 | 0.37966 | 39.95
2021-07-22 10:30 | 44399.4375 | 0 | 0.37966 | 39.95
2021-07-22 11:00 | 44399.4583 | 0 | 0.37966 | 39.95
2021-07-22 11:30 | 44399.4792 | 0 | 0.37966 | 39.95
2021-07-22 12:00 | 44399.5 | 0 | 0.37966 | 39.95
2021-07-22 12:30 | 44399.5208 | 0 | 0.37966 | 39.95
2021-07-22 13:00 | 44399.5417 | 0 | 0.37966 | 39.95
2021-07-22 13:30 | 44399.5625 | 0 | 0.37966 | 39.95
2021-07-22 14:00 | 44399.5833 | 0 | 9.6738 | 39.95
2021-07-22 14:30 | 44399.6042 | 0 | 10.3145 | 39.95
2021-07-22 15:00 | 44399.625 | 0 | 10.7762 | 39.95
2021-07-22 15:30 | 44399.6458 | 0 | 11.4189 | 39.95
2021-07-22 16:00 | 44399.6667 | 0 | 12.3824 | 39.95
2021-07-22 16:30 | 44399.6875 | 0 | 13.4149 | 39.95
2021-07-22 17:00 | 44399.7083 | 0 | 14.6532 | 39.95
2021-07-22 17:30 | 44399.7292 | 0 | 15.8125 | 39.95
2021-07-22 18:00 | 44399.75 | 0 | 16.4493 | 39.95
2021-07-22 18:30 | 44399.7708 | 0 | 16.8431 | 39.95
2021-07-22 19:00 | 44399.7917 | 0 | 16.929 | 39.95
2021-07-22 19:30 | 44399.8125 | 0 | 16.8435 | 39.95
2021-07-22 20:00 | 44399.8333 | 0 | 16.6223 | 39.95
2021-07-22 20:30 | 44399.8542 | 0 | 15.7967 | 39.95
2021-07-22 21:00 | 44399.875 | 0 | 14.907 | 39.95
2021-07-22 21:30 | 44399.8958 | 0 | 14.1675 | 39.95
2021-07-22 22:00 | 44399.9167 | 0 | 13.3 | 39.95
2021-07-22 22:30 | 44399.9375 | 0 | 11.9877 | 39.95
2021-07-22 23:00 | 44399.9583 | 0 | 11.0294 | 39.95
2021-07-22 23:30 | 44399.9792 | 0 | 10.3595 | 39.95
2021-07-23 | 44400 | 0 | 9.6674 | 39.95
2021-07-23 00:30 | 44400.0208 | 0 | 9.16 | 39.95
2021-07-23 01:00 | 44400.0417 | 0 | 8.8909 | 39.95
2021-07-23 01:30 | 44400.0625 | 0 | 8.638 | 39.95
2021-07-23 02:00 | 44400.0833 | 0 | 8.6733 | 39.95
2021-07-23 02:30 | 44400.1042 | 0 | 8.5405 | 39.95
2021-07-23 03:00 | 44400.125 | 0 | 8.5804 | 39.95
2021-07-23 03:30 | 44400.1458 | 0 | 8.7572 | 39.95
2021-07-23 04:00 | 44400.1667 | 0 | 8.8378 | 39.95
2021-07-23 04:30 | 44400.1875 | 0 | 9.5136 | 39.95
2021-07-23 05:00 | 44400.2083 | 0 | 10.3212 | 39.95
2021-07-23 05:30 | 44400.2292 | 0 | 11.4382 | 39.95
2021-07-23 06:00 | 44400.25 | 0 | 12.9162 | 39.95
2021-07-23 06:30 | 44400.2708 | 0 | 14.7814 | 39.95
2021-07-23 07:00 | 44400.2917 | 0 | 15.8637 | 39.95
2021-07-23 07:30 | 44400.3125 | 0 | 16.0436 | 39.95
2021-07-23 08:00 | 44400.3333 | 0 | 15.8358 | 39.95
2021-07-23 08:30 | 44400.3542 | 0 | 14.8326 | 39.95
2021-07-23 09:00 | 44400.375 | 0 | 14.446 | 39.95
2021-07-23 09:30 | 44400.3958 | 0 | 14.7172 | 39.95
2021-07-23 10:00 | 44400.4167 | 0 | 13.7802 | 39.95
2021-07-23 10:30 | 44400.4375 | 0 | 12.6272 | 39.95
2021-07-23 11:00 | 44400.4583 | 0 | 12.1739 | 39.95
2021-07-23 11:30 | 44400.4792 | 0 | 10.7718 | 39.95
2021-07-23 12:00 | 44400.5 | 0 | 11.0915 | 39.95
2021-07-23 12:30 | 44400.5208 | 0 | 12.1746 | 39.95
2021-07-23 13:00 | 44400.5417 | 0 | 12.77 | 39.95
2021-07-23 13:30 | 44400.5625 | 0 | 12.5489 | 39.95
2021-07-23 14:00 | 44400.5833 | 0 | 12.8831 | 39.95
2021-07-23 14:30 | 44400.6042 | 0 | 12.9081 | 39.95
2021-07-23 15:00 | 44400.625 | 0 | 13.5431 | 39.95
2021-07-23 15:30 | 44400.6458 | 0 | 13.4814 | 39.95
2021-07-23 16:00 | 44400.6667 | 0 | 14.1236 | 39.95
2021-07-23 16:30 | 44400.6875 | 0 | 14.7755 | 39.95
2021-07-23 17:00 | 44400.7083 | 0 | 15.2722 | 39.95
2021-07-23 17:30 | 44400.7292 | 0 | 15.7909 | 39.95
2021-07-23 18:00 | 44400.75 | 0 | 15.8785 | 39.95
2021-07-23 18:30 | 44400.7708 | 0 | 16.0823 | 39.95
2021-07-23 19:00 | 44400.7917 | 0 | 15.7485 | 39.95
2021-07-23 19:30 | 44400.8125 | 0 | 15.449 | 39.95
2021-07-23 20:00 | 44400.8333 | 0 | 15.4104 | 39.95
2021-07-23 20:30 | 44400.8542 | 0 | 14.7137 | 39.95
2021-07-23 21:00 | 44400.875 | 0 | 14.0062 | 39.95
2021-07-23 21:30 | 44400.8958 | 0 | 13.4299 | 39.95
2021-07-23 22:00 | 44400.9167 | 0 | 12.6121 | 39.95
2021-07-23 22:30 | 44400.9375 | 0 | 11.7775 | 39.95
2021-07-23 23:00 | 44400.9583 | 0 | 10.8969 | 39.95
2021-07-23 23:30 | 44400.9792 | 0 | 10.172 | 39.95
2021-07-24 | 44401 | 0 | 9.4572 | 39.95
2021-07-24 00:30 | 44401.0208 | 0 | 8.9633 | 39.95
2021-07-24 01:00 | 44401.0417 | 0 | 8.5887 | 39.95
2021-07-24 01:30 | 44401.0625 | 0 | 8.3852 | 39.95
2021-07-24 02:00 | 44401.0833 | 0 | 8.3223 | 39.95
2021-07-24 02:30 | 44401.1042 | 0 | 8.1514 | 39.95
2021-07-24 03:00 | 44401.125 | 0 | 8.1561 | 39.95
2021-07-24 03:30 | 44401.1458 | 0 | 8.2239 | 39.95
2021-07-24 04:00 | 44401.1667 | 0 | 8.0938 | 39.95
2021-07-24 04:30 | 44401.1875 | 0 | 8.1769 | 39.95
2021-07-24 05:00 | 44401.2083 | 0 | 8.4872 | 39.95
2021-07-24 05:30 | 44401.2292 | 0 | 8.7982 | 39.95
2021-07-24 06:00 | 44401.25 | 0 | 9.2517 | 39.95
2021-07-24 06:30 | 44401.2708 | 0 | 9.8951 | 39.95
2021-07-24 07:00 | 44401.2917 | 0 | 10.6808 | 39.95
2021-07-24 07:30 | 44401.3125 | 0 | 10.8911 | 39.95
2021-07-24 08:00 | 44401.3333 | 0 | 10.8484 | 39.95
2021-07-24 08:30 | 44401.3542 | 0 | 9.7909 | 39.95
2021-07-24 09:00 | 44401.375 | 0 | 9.047 | 39.95
2021-07-24 09:30 | 44401.3958 | 0 | 8.4528 | 39.95
2021-07-24 10:00 | 44401.4167 | 0 | 7.7711 | 39.95
2021-07-24 10:30 | 44401.4375 | 0 | 7.4281 | 39.95
2021-07-24 11:00 | 44401.4583 | 0 | 6.8939 | 39.95
2021-07-24 11:30 | 44401.4792 | 0 | 7.4675 | 39.95
2021-07-24 12:00 | 44401.5 | 0 | 6.3465 | 39.95
2021-07-24 12:30 | 44401.5208 | 0 | 6.2331 | 39.95
2021-07-24 13:00 | 44401.5417 | 0 | 6.4506 | 39.95
2021-07-24 13:30 | 44401.5625 | 0 | 6.7482 | 39.95
2021-07-24 14:00 | 44401.5833 | 0 | 7.2455 | 39.95
2021-07-24 14:30 | 44401.6042 | 0 | 7.5666 | 39.95
2021-07-24 15:00 | 44401.625 | 0 | 8.3066 | 39.95
2021-07-24 15:30 | 44401.6458 | 0 | 9.0744 | 39.95
2021-07-24 16:00 | 44401.6667 | 0 | 9.7567 | 39.95
2021-07-24 16:30 | 44401.6875 | 0 | 10.6269 | 39.95
2021-07-24 17:00 | 44401.7083 | 0 | 11.4055 | 39.95
2021-07-24 17:30 | 44401.7292 | 0 | 12.1328 | 39.95
2021-07-24 18:00 | 44401.75 | 0 | 12.3006 | 39.95
2021-07-24 18:30 | 44401.7708 | 0 | 12.5137 | 39.95
2021-07-24 19:00 | 44401.7917 | 0 | 12.3238 | 39.95
2021-07-24 19:30 | 44401.8125 | 0 | 12.1583 | 39.95
2021-07-24 20:00 | 44401.8333 | 0 | 12.0229 | 39.95
2021-07-24 20:30 | 44401.8542 | 0 | 11.5417 | 39.95
2021-07-24 21:00 | 44401.875 | 0 | 11.1849 | 39.95
2021-07-24 21:30 | 44401.8958 | 0 | 11.0104 | 39.95
2021-07-24 22:00 | 44401.9167 | 0 | 10.5197 | 39.95
2021-07-24 22:30 | 44401.9375 | 0 | 9.9754 | 39.95
2021-07-24 23:00 | 44401.9583 | 0 | 9.2842 | 39.95
2021-07-24 23:30 | 44401.9792 | 0 | 8.7783 | 39.95
2021-07-25 | 44402 | 0 | 8.245 | 39.95
2021-07-25 00:30 | 44402.0208 | 0 | 7.9187 | 39.95
2021-07-25 01:00 | 44402.0417 | 0 | 7.7698 | 39.95
2021-07-25 01:30 | 44402.0625 | 0 | 7.5476 | 39.95
2021-07-25 02:00 | 44402.0833 | 0 | 7.4191 | 39.95
2021-07-25 02:30 | 44402.1042 | 0 | 7.4051 | 39.95
2021-07-25 03:00 | 44402.125 | 0 | 7.2749 | 39.95
2021-07-25 03:30 | 44402.1458 | 0 | 7.4051 | 39.95
2021-07-25 04:00 | 44402.1667 | 0 | 7.3345 | 39.95
2021-07-25 04:30 | 44402.1875 | 0 | 7.4144 | 39.95
2021-07-25 05:00 | 44402.2083 | 0 | 7.4955 | 39.95
2021-07-25 05:30 | 44402.2292 | 0 | 7.7611 | 39.95
2021-07-25 06:00 | 44402.25 | 0 | 8.1121 | 39.95
2021-07-25 06:30 | 44402.2708 | 0 | 8.512 | 39.95
2021-07-25 07:00 | 44402.2917 | 0 | 9.0764 | 39.95
2021-07-25 07:30 | 44402.3125 | 0 | 8.919 | 39.95
2021-07-25 08:00 | 44402.3333 | 0 | 8.8136 | 39.95
2021-07-25 08:30 | 44402.3542 | 0 | 8.53 | 39.95
2021-07-25 09:00 | 44402.375 | 0 | 8.1571 | 39.95
2021-07-25 09:30 | 44402.3958 | 0 | 7.6995 | 39.95
2021-07-25 10:00 | 44402.4167 | 0 | 7.2296 | 39.95
2021-07-25 10:30 | 44402.4375 | 0 | 6.85 | 39.95
2021-07-25 11:00 | 44402.4583 | 0 | 6.3684 | 39.95
2021-07-25 11:30 | 44402.4792 | 0 | 6.1216 | 39.95
2021-07-25 12:00 | 44402.5 | 0 | 6.1238 | 39.95
2021-07-25 12:30 | 44402.5208 | 0 | 6.0157 | 39.95
2021-07-25 13:00 | 44402.5417 | 0 | 6.0494 | 39.95
2021-07-25 13:30 | 44402.5625 | 0 | 6.286 | 39.95
2021-07-25 14:00 | 44402.5833 | 0 | 6.8278 | 39.95
2021-07-25 14:30 | 44402.6042 | 0 | 7.3729 | 39.95
2021-07-25 15:00 | 44402.625 | 0 | 8.0961 | 39.95
2021-07-25 15:30 | 44402.6458 | 0 | 8.7908 | 39.95
2021-07-25 16:00 | 44402.6667 | 0 | 9.9028 | 39.95
2021-07-25 16:30 | 44402.6875 | 0 | 10.9806 | 39.95
2021-07-25 17:00 | 44402.7083 | 0 | 12.1397 | 39.95
2021-07-25 17:30 | 44402.7292 | 0 | 13.0876 | 39.95
2021-07-25 18:00 | 44402.75 | 0 | 13.6552 | 39.95
2021-07-25 18:30 | 44402.7708 | 0 | 13.7848 | 39.95
2021-07-25 19:00 | 44402.7917 | 0 | 13.4745 | 39.95
2021-07-25 19:30 | 44402.8125 | 0 | 13.2589 | 39.95
2021-07-25 20:00 | 44402.8333 | 0 | 13.0243 | 39.95
2021-07-25 20:30 | 44402.8542 | 0 | 12.6153 | 39.95
2021-07-25 21:00 | 44402.875 | 0 | 11.8179 | 39.95
2021-07-25 21:30 | 44402.8958 | 0 | 11.3946 | 39.95
2021-07-25 22:00 | 44402.9167 | 0 | 10.5852 | 39.95
2021-07-25 22:30 | 44402.9375 | 0 | 9.7462 | 39.95
2021-07-25 23:00 | 44402.9583 | 0 | 9.0732 | 39.95
2021-07-25 23:30 | 44402.9792 | 0 | 8.5431 | 39.95
2021-07-26 | 44403 | 0 | 8.1141 | 39.95
2021-07-26 00:30 | 44403.0208 | 0 | 7.8964 | 39.95
2021-07-26 01:00 | 44403.0417 | 0 | 7.6848 | 39.95
2021-07-26 01:30 | 44403.0625 | 0 | 7.6154 | 39.95
2021-07-26 02:00 | 44403.0833 | 0 | 7.6331 | 39.95
2021-07-26 02:30 | 44403.1042 | 0 | 7.6425 | 39.95
2021-07-26 03:00 | 44403.125 | 0 | 7.6597 | 39.95
2021-07-26 03:30 | 44403.1458 | 0 | 7.9281 | 39.95
2021-07-26 04:00 | 44403.1667 | 0 | 8.1063 | 39.95
2021-07-26 04:30 | 44403.1875 | 0 | 8.5475 | 39.95
2021-07-26 05:00 | 44403.2083 | 0 | 9.5704 | 39.95
2021-07-26 05:30 | 44403.2292 | 0 | 10.6973 | 39.95
2021-07-26 06:00 | 44403.25 | 0 | 12.3551 | 39.95
2021-07-26 06:30 | 44403.2708 | 0 | 14.4857 | 39.95
2021-07-26 07:00 | 44403.2917 | 0 | 15.6247 | 39.95
2021-07-26 07:30 | 44403.3125 | 0 | 14.9676 | 39.95
2021-07-26 08:00 | 44403.3333 | 0 | 13.4823 | 39.95
2021-07-26 08:30 | 44403.3542 | 0 | 12.3129 | 39.95
2021-07-26 09:00 | 44403.375 | 0 | 11.094 | 39.95
2021-07-26 09:30 | 44403.3958 | 0 | 10.4934 | 39.95
2021-07-26 10:00 | 44403.4167 | 0 | 9.8068 | 39.95
2021-07-26 10:30 | 44403.4375 | 0 | 9.5048 | 39.95
2021-07-26 11:00 | 44403.4583 | 0 | 9.065 | 39.95
2021-07-26 11:30 | 44403.4792 | 0 | 8.7912 | 39.95
2021-07-26 12:00 | 44403.5 | 0 | 8.6111 | 39.95
2021-07-26 12:30 | 44403.5208 | 0 | 9.7389 | 39.95
2021-07-26 13:00 | 44403.5417 | 0 | 10.8718 | 39.95
2021-07-26 13:30 | 44403.5625 | 0 | 9.1507 | 39.95
2021-07-26 14:00 | 44403.5833 | 0 | 9.822 | 39.95
2021-07-26 14:30 | 44403.6042 | 0 | 9.5231 | 39.95
2021-07-26 15:00 | 44403.625 | 0 | 9.9961 | 39.95
2021-07-26 15:30 | 44403.6458 | 0 | 10.914 | 39.95
2021-07-26 16:00 | 44403.6667 | 0 | 11.4308 | 39.95
2021-07-26 16:30 | 44403.6875 | 0 | 12.7154 | 39.95
2021-07-26 17:00 | 44403.7083 | 0 | 13.6871 | 39.95
2021-07-26 17:30 | 44403.7292 | 0 | 14.8408 | 39.95
2021-07-26 18:00 | 44403.75 | 0 | 15.3151 | 39.95
2021-07-26 18:30 | 44403.7708 | 0 | 15.7164 | 39.95
2021-07-26 19:00 | 44403.7917 | 0 | 15.3875 | 39.95
2021-07-26 19:30 | 44403.8125 | 0 | 15.2932 | 39.95
2021-07-26 20:00 | 44403.8333 | 0 | 15.0284 | 39.95
2021-07-26 20:30 | 44403.8542 | 0 | 14.3172 | 39.95
2021-07-26 21:00 | 44403.875 | 0 | 13.4654 | 39.95
2021-07-26 21:30 | 44403.8958 | 0 | 12.9878 | 39.95
2021-07-26 22:00 | 44403.9167 | 0 | 12.2081 | 39.95
2021-07-26 22:30 | 44403.9375 | 0 | 11.1852 | 39.95
2021-07-26 23:00 | 44403.9583 | 0 | 10.3307 | 39.95
2021-07-26 23:30 | 44403.9792 | 0 | 9.814 | 39.95
2021-07-27 | 44404 | 0 | 9.1554 | 39.95
2021-07-27 00:30 | 44404.0208 | 0 | 8.7882 | 39.95
2021-07-27 01:00 | 44404.0417 | 0 | 8.5134 | 39.95
2021-07-27 01:30 | 44404.0625 | 0 | 8.383 | 39.95
2021-07-27 02:00 | 44404.0833 | 0 | 8.3105 | 39.95
2021-07-27 02:30 | 44404.1042 | 0 | 8.2317 | 39.95
2021-07-27 03:00 | 44404.125 | 0 | 8.253 | 39.95
2021-07-27 03:30 | 44404.1458 | 0 | 8.5476 | 39.95
2021-07-27 04:00 | 44404.1667 | 0 | 8.7884 | 39.95
2021-07-27 04:30 | 44404.1875 | 0 | 9.2733 | 39.95
2021-07-27 05:00 | 44404.2083 | 0 | 10.2866 | 39.95
2021-07-27 05:30 | 44404.2292 | 0 | 11.4455 | 39.95
2021-07-27 06:00 | 44404.25 | 0 | 13.0542 | 39.95
2021-07-27 06:30 | 44404.2708 | 0 | 15.2228 | 39.95
2021-07-27 07:00 | 44404.2917 | 0 | 16.087 | 39.95
2021-07-27 07:30 | 44404.3125 | 0 | 15.4683 | 39.95
2021-07-27 08:00 | 44404.3333 | 0 | 14.3154 | 39.95
2021-07-27 08:30 | 44404.3542 | 0 | 12.8306 | 39.95
2021-07-27 09:00 | 44404.375 | 0 | 11.7204 | 39.95
2021-07-27 09:30 | 44404.3958 | 0 | 10.9942 | 39.95
2021-07-27 10:00 | 44404.4167 | 0 | 10.0685 | 39.95
2021-07-27 10:30 | 44404.4375 | 0 | 9.6223 | 39.95
2021-07-27 11:00 | 44404.4583 | 0 | 9.1905 | 39.95
2021-07-27 11:30 | 44404.4792 | 0 | 8.7893 | 39.95
2021-07-27 12:00 | 44404.5 | 0 | 8.6576 | 39.95
2021-07-27 12:30 | 44404.5208 | 0 | 8.6651 | 39.95
2021-07-27 13:00 | 44404.5417 | 0 | 8.6329 | 39.95
2021-07-27 13:30 | 44404.5625 | 0 | 8.8178 | 39.95
2021-07-27 14:00 | 44404.5833 | 0 | 9.3025 | 39.95
2021-07-27 14:30 | 44404.6042 | 0 | 9.9532 | 39.95
2021-07-27 15:00 | 44404.625 | 0 | 10.332 | 39.95
2021-07-27 15:30 | 44404.6458 | 0 | 11.0475 | 39.95
2021-07-27 16:00 | 44404.6667 | 0 | 11.8293 | 39.95
2021-07-27 16:30 | 44404.6875 | 0 | 12.6468 | 39.95
2021-07-27 17:00 | 44404.7083 | 0 | 13.5061 | 39.95
2021-07-27 17:30 | 44404.7292 | 0 | 14.4246 | 39.95
2021-07-27 18:00 | 44404.75 | 0 | 14.7619 | 39.95
2021-07-27 18:30 | 44404.7708 | 0 | 15.2827 | 39.95
2021-07-27 19:00 | 44404.7917 | 0 | 15.0425 | 39.95
2021-07-27 19:30 | 44404.8125 | 0 | 14.7078 | 39.95
2021-07-27 20:00 | 44404.8333 | 0 | 14.3505 | 39.95
2021-07-27 20:30 | 44404.8542 | 0 | 13.9936 | 39.95
2021-07-27 21:00 | 44404.875 | 0 | 13.3078 | 39.95
2021-07-27 21:30 | 44404.8958 | 0 | 12.7296 | 39.95
2021-07-27 22:00 | 44404.9167 | 0 | 11.9943 | 39.95
2021-07-27 22:30 | 44404.9375 | 0 | 11.0423 | 39.95
2021-07-27 23:00 | 44404.9583 | 0 | 10.2066 | 39.95
2021-07-27 23:30 | 44404.9792 | 0 | 9.7283 | 39.95
2021-07-28 | 44405 | 0 | 9.1774 | 39.95
2021-07-28 00:30 | 44405.0208 | 0 | 8.8293 | 39.95
2021-07-28 01:00 | 44405.0417 | 0 | 8.5217 | 39.95
2021-07-28 01:30 | 44405.0625 | 0 | 8.4053 | 39.95
2021-07-28 02:00 | 44405.0833 | 0 | 8.2324 | 39.95
2021-07-28 02:30 | 44405.1042 | 0 | 8.2286 | 39.95
2021-07-28 03:00 | 44405.125 | 0 | 8.2431 | 39.95
2021-07-28 03:30 | 44405.1458 | 0 | 8.3971 | 39.95
2021-07-28 04:00 | 44405.1667 | 0 | 8.5855 | 39.95
2021-07-28 04:30 | 44405.1875 | 0 | 9.0177 | 39.95
2021-07-28 05:00 | 44405.2083 | 0 | 9.8651 | 39.95
2021-07-28 05:30 | 44405.2292 | 0 | 10.9842 | 39.95
2021-07-28 06:00 | 44405.25 | 0 | 12.578 | 39.95
2021-07-28 06:30 | 44405.2708 | 0 | 14.0271 | 39.95
2021-07-28 07:00 | 44405.2917 | 0 | 14.9963 | 39.95
2021-07-28 07:30 | 44405.3125 | 0 | 14.1692 | 39.95
2021-07-28 08:00 | 44405.3333 | 0 | 13.7279 | 39.95
2021-07-28 08:30 | 44405.3542 | 0 | 12.2603 | 39.95
2021-07-28 09:00 | 44405.375 | 0 | 11.2426 | 39.95
2021-07-28 09:30 | 44405.3958 | 0 | 10.2866 | 39.95
2021-07-28 10:00 | 44405.4167 | 0 | 9.6738 | 39.95
2021-07-28 10:30 | 44405.4375 | 0 | 9.2583 | 39.95
2021-07-28 11:00 | 44405.4583 | 0 | 8.7654 | 39.95
2021-07-28 11:30 | 44405.4792 | 0 | 8.5304 | 39.95
2021-07-28 12:00 | 44405.5 | 0 | 8.9889 | 39.95
2021-07-28 12:30 | 44405.5208 | 0 | 9.266 | 39.95
2021-07-28 13:00 | 44405.5417 | 0 | 8.947 | 39.95
2021-07-28 13:30 | 44405.5625 | 0 | 9.2438 | 39.95
2021-07-28 14:00 | 44405.5833 | 0 | 9.7375 | 39.95
2021-07-28 14:30 | 44405.6042 | 0 | 10.2224 | 39.95
2021-07-28 15:00 | 44405.625 | 0 | 10.669 | 39.95
2021-07-28 15:30 | 44405.6458 | 0 | 11.3158 | 39.95
2021-07-28 16:00 | 44405.6667 | 0 | 11.8597 | 39.95
2021-07-28 16:30 | 44405.6875 | 0 | 12.6102 | 39.95
2021-07-28 17:00 | 44405.7083 | 0 | 13.2365 | 39.95
2021-07-28 17:30 | 44405.7292 | 0 | 14.1712 | 39.95
2021-07-28 18:00 | 44405.75 | 0 | 14.419 | 39.95
2021-07-28 18:30 | 44405.7708 | 0 | 14.743 | 39.95
2021-07-28 19:00 | 44405.7917 | 0 | 14.4041 | 39.95
2021-07-28 19:30 | 44405.8125 | 0 | 14.2205 | 39.95
2021-07-28 20:00 | 44405.8333 | 0 | 13.8617 | 39.95
2021-07-28 20:30 | 44405.8542 | 0 | 13.3663 | 39.95
2021-07-28 21:00 | 44405.875 | 0 | 12.8701 | 39.95
2021-07-28 21:30 | 44405.8958 | 0 | 12.3397 | 39.95
2021-07-28 22:00 | 44405.9167 | 0 | 11.4822 | 39.95
2021-07-28 22:30 | 44405.9375 | 0 | 10.6951 | 39.95
2021-07-28 23:00 | 44405.9583 | 0 | 9.9359 | 39.95
2021-07-28 23:30 | 44405.9792 | 0 | 9.4443 | 39.95
2021-07-29 | 44406 | 0 | 8.8499 | 39.95
2021-07-29 00:30 | 44406.0208 | 0 | 8.5371 | 39.95
2021-07-29 01:00 | 44406.0417 | 0 | 8.3775 | 39.95
2021-07-29 01:30 | 44406.0625 | 0 | 8.1518 | 39.95
2021-07-29 02:00 | 44406.0833 | 0 | 8.1013 | 39.95
2021-07-29 02:30 | 44406.1042 | 0 | 8.0337 | 39.95
2021-07-29 03:00 | 44406.125 | 0 | 8.0844 | 39.95
2021-07-29 03:30 | 44406.1458 | 0 | 8.1554 | 39.95
2021-07-29 04:00 | 44406.1667 | 0 | 8.3291 | 39.95
2021-07-29 04:30 | 44406.1875 | 0 | 8.7762 | 39.95
2021-07-29 05:00 | 44406.2083 | 0 | 9.4981 | 39.95
2021-07-29 05:30 | 44406.2292 | 0 | 10.5352 | 39.95
2021-07-29 06:00 | 44406.25 | 0 | 11.5712 | 39.95
2021-07-29 06:30 | 44406.2708 | 0 | 12.5693 | 39.95
2021-07-29 07:00 | 44406.2917 | 0 | 13.4685 | 39.95
2021-07-29 07:30 | 44406.3125 | 0 | 13.7008 | 39.95
2021-07-29 08:00 | 44406.3333 | 0 | 12.8213 | 39.95
2021-07-29 08:30 | 44406.3542 | 0 | 12.1649 | 39.95
2021-07-29 09:00 | 44406.375 | 0 | 11.1664 | 39.95
2021-07-29 09:30 | 44406.3958 | 0 | 10.0601 | 39.95
2021-07-29 10:00 | 44406.4167 | 0 | 9.5584 | 39.95
2021-07-29 10:30 | 44406.4375 | 0 | 9.3262 | 39.95
2021-07-29 11:00 | 44406.4583 | 0 | 9.0363 | 39.95
2021-07-29 11:30 | 44406.4792 | 0 | 8.9747 | 39.95
2021-07-29 12:00 | 44406.5 | 0 | 8.6965 | 39.95
2021-07-29 12:30 | 44406.5208 | 0 | 8.7673 | 39.95
2021-07-29 13:00 | 44406.5417 | 0 | 8.994 | 39.95
2021-07-29 13:30 | 44406.5625 | 0 | 9.6517 | 39.95
2021-07-29 14:00 | 44406.5833 | 0 | 10.2308 | 39.95
2021-07-29 14:30 | 44406.6042 | 0 | 10.7233 | 39.95
2021-07-29 15:00 | 44406.625 | 0 | 10.6392 | 39.95
2021-07-29 15:30 | 44406.6458 | 0 | 11.1946 | 39.95
2021-07-29 16:00 | 44406.6667 | 0 | 11.6661 | 39.95
2021-07-29 16:30 | 44406.6875 | 0 | 12.3873 | 39.95
2021-07-29 17:00 | 44406.7083 | 0 | 12.9285 | 39.95
2021-07-29 17:30 | 44406.7292 | 0 | 13.6736 | 39.95
2021-07-29 18:00 | 44406.75 | 0 | 13.9563 | 39.95
2021-07-29 18:30 | 44406.7708 | 0 | 14.309 | 39.95
2021-07-29 19:00 | 44406.7917 | 0 | 13.8895 | 39.95
2021-07-29 19:30 | 44406.8125 | 0 | 13.7792 | 39.95
2021-07-29 20:00 | 44406.8333 | 0 | 13.545 | 39.95
2021-07-29 20:30 | 44406.8542 | 0 | 12.9948 | 39.95
2021-07-29 21:00 | 44406.875 | 0 | 12.5848 | 39.95
2021-07-29 21:30 | 44406.8958 | 0 | 12.1828 | 39.95
2021-07-29 22:00 | 44406.9167 | 0 | 11.5612 | 39.95
2021-07-29 22:30 | 44406.9375 | 0 | 10.6986 | 39.95
2021-07-29 23:00 | 44406.9583 | 0 | 10.0394 | 39.95
2021-07-29 23:30 | 44406.9792 | 0 | 9.5762 | 39.95
2021-07-30 | 44407 | 0 | 9.0452 | 39.95
2021-07-30 00:30 | 44407.0208 | 0 | 8.5818 | 39.95
2021-07-30 01:00 | 44407.0417 | 0 | 8.353 | 39.95
2021-07-30 01:30 | 44407.0625 | 0 | 8.2101 | 39.95
2021-07-30 02:00 | 44407.0833 | 0 | 8.1122 | 39.95
2021-07-30 02:30 | 44407.1042 | 0 | 8.0343 | 39.95
2021-07-30 03:00 | 44407.125 | 0 | 7.9951 | 39.95
2021-07-30 03:30 | 44407.1458 | 0 | 8.2218 | 39.95
2021-07-30 04:00 | 44407.1667 | 0 | 8.3405 | 39.95
2021-07-30 04:30 | 44407.1875 | 0 | 8.8217 | 39.95
2021-07-30 05:00 | 44407.2083 | 0 | 9.659 | 39.95
2021-07-30 05:30 | 44407.2292 | 0 | 10.8189 | 39.95
2021-07-30 06:00 | 44407.25 | 0 | 12.1352 | 39.95
2021-07-30 06:30 | 44407.2708 | 0 | 13.6416 | 39.95
2021-07-30 07:00 | 44407.2917 | 0 | 14.1468 | 39.95
2021-07-30 07:30 | 44407.3125 | 0 | 14.0697 | 39.95
2021-07-30 08:00 | 44407.3333 | 0 | 13.0657 | 39.95
2021-07-30 08:30 | 44407.3542 | 0 | 11.9716 | 39.95
2021-07-30 09:00 | 44407.375 | 0 | 10.9871 | 39.95
2021-07-30 09:30 | 44407.3958 | 0 | 10.3533 | 39.95
2021-07-30 10:00 | 44407.4167 | 0 | 9.5249 | 39.95
2021-07-30 10:30 | 44407.4375 | 0 | 9.1811 | 39.95
2021-07-30 11:00 | 44407.4583 | 0 | 8.9955 | 39.95
2021-07-30 11:30 | 44407.4792 | 0 | 8.6879 | 39.95
2021-07-30 12:00 | 44407.5 | 0 | 8.3291 | 39.95
2021-07-30 12:30 | 44407.5208 | 0 | 8.1494 | 39.95
2021-07-30 13:00 | 44407.5417 | 0 | 8.3257 | 39.95
2021-07-30 13:30 | 44407.5625 | 0 | 8.4417 | 39.95
2021-07-30 14:00 | 44407.5833 | 0 | 9.0338 | 39.95
2021-07-30 14:30 | 44407.6042 | 0 | 9.3405 | 39.95
2021-07-30 15:00 | 44407.625 | 0 | 9.9491 | 39.95
2021-07-30 15:30 | 44407.6458 | 0 | 10.7696 | 39.95
2021-07-30 16:00 | 44407.6667 | 0 | 11.744 | 39.95
2021-07-30 16:30 | 44407.6875 | 0 | 12.5504 | 39.95
2021-07-30 17:00 | 44407.7083 | 0 | 12.9087 | 39.95
2021-07-30 17:30 | 44407.7292 | 0 | 13.5129 | 39.95
2021-07-30 18:00 | 44407.75 | 0 | 13.7352 | 39.95
2021-07-30 18:30 | 44407.7708 | 0 | 13.8829 | 39.95
2021-07-30 19:00 | 44407.7917 | 0 | 13.7947 | 39.95
2021-07-30 19:30 | 44407.8125 | 0 | 13.8159 | 39.95
2021-07-30 20:00 | 44407.8333 | 0 | 13.6929 | 39.95
2021-07-30 20:30 | 44407.8542 | 0 | 13.2471 | 39.95
2021-07-30 21:00 | 44407.875 | 0 | 12.7496 | 39.95
2021-07-30 21:30 | 44407.8958 | 0 | 12.4268 | 39.95
2021-07-30 22:00 | 44407.9167 | 0 | 11.8755 | 39.95
2021-07-30 22:30 | 44407.9375 | 0 | 10.9059 | 39.95
2021-07-30 23:00 | 44407.9583 | 0 | 10.1177 | 39.95
2021-07-30 23:30 | 44407.9792 | 0 | 9.6508 | 39.95
2021-07-31 | 44408 | 0 | 9.1493 | 39.95
2021-07-31 00:30 | 44408.0208 | 0 | 8.523 | 39.95
2021-07-31 01:00 | 44408.0417 | 0 | 8.414 | 39.95
2021-07-31 01:30 | 44408.0625 | 0 | 8.2134 | 39.95
2021-07-31 02:00 | 44408.0833 | 0 | 8.012 | 39.95
2021-07-31 02:30 | 44408.1042 | 0 | 7.8726 | 39.95
2021-07-31 03:00 | 44408.125 | 0 | 7.8557 | 39.95
2021-07-31 03:30 | 44408.1458 | 0 | 7.9667 | 39.95
2021-07-31 04:00 | 44408.1667 | 0 | 7.9396 | 39.95
2021-07-31 04:30 | 44408.1875 | 0 | 8.0705 | 39.95
2021-07-31 05:00 | 44408.2083 | 0 | 8.4665 | 39.95
2021-07-31 05:30 | 44408.2292 | 0 | 8.9406 | 39.95
2021-07-31 06:00 | 44408.25 | 0 | 9.3834 | 39.95
2021-07-31 06:30 | 44408.2708 | 0 | 9.9237 | 39.95
2021-07-31 07:00 | 44408.2917 | 0 | 10.5012 | 39.95
2021-07-31 07:30 | 44408.3125 | 0 | 10.6181 | 39.95
2021-07-31 08:00 | 44408.3333 | 0 | 10.404 | 39.95
2021-07-31 08:30 | 44408.3542 | 0 | 9.5529 | 39.95
2021-07-31 09:00 | 44408.375 | 0 | 8.9768 | 39.95
2021-07-31 09:30 | 44408.3958 | 0 | 8.2715 | 39.95
2021-07-31 10:00 | 44408.4167 | 0 | 7.5135 | 39.95
2021-07-31 10:30 | 44408.4375 | 0 | 6.864 | 39.95
2021-07-31 11:00 | 44408.4583 | 0 | 6.6507 | 39.95
2021-07-31 11:30 | 44408.4792 | 0 | 6.334 | 39.95
2021-07-31 12:00 | 44408.5 | 0 | 6.1026 | 39.95
2021-07-31 12:30 | 44408.5208 | 0 | 6.1564 | 39.95
2021-07-31 13:00 | 44408.5417 | 0 | 6.1823 | 39.95
2021-07-31 13:30 | 44408.5625 | 0 | 6.3195 | 39.95
2021-07-31 14:00 | 44408.5833 | 0 | 6.8931 | 39.95
2021-07-31 14:30 | 44408.6042 | 0 | 7.3503 | 39.95
2021-07-31 15:00 | 44408.625 | 0 | 8.0497 | 39.95
2021-07-31 15:30 | 44408.6458 | 0 | 8.8089 | 39.95
2021-07-31 16:00 | 44408.6667 | 0 | 9.6193 | 39.95
2021-07-31 16:30 | 44408.6875 | 0 | 10.5077 | 39.95
2021-07-31 17:00 | 44408.7083 | 0 | 11.2844 | 39.95
2021-07-31 17:30 | 44408.7292 | 0 | 12.035 | 39.95
2021-07-31 18:00 | 44408.75 | 0 | 12.3872 | 39.95
2021-07-31 18:30 | 44408.7708 | 0 | 12.5534 | 39.95
2021-07-31 19:00 | 44408.7917 | 0 | 12.2775 | 39.95
2021-07-31 19:30 | 44408.8125 | 0 | 12.0094 | 39.95
2021-07-31 20:00 | 44408.8333 | 0 | 11.751 | 39.95
2021-07-31 20:30 | 44408.8542 | 0 | 11.2067 | 39.95
2021-07-31 21:00 | 44408.875 | 0 | 10.7565 | 39.95
2021-07-31 21:30 | 44408.8958 | 0 | 10.48 | 39.95
2021-07-31 22:00 | 44408.9167 | 0 | 10.0577 | 39.95
2021-07-31 22:30 | 44408.9375 | 0 | 9.3962 | 39.95
2021-07-31 23:00 | 44408.9583 | 0 | 8.7588 | 39.95
2021-07-31 23:30 | 44408.9792 | 0 | 8.3508 | 39.95
2021-08-01 | 44409 | 0 | 7.9679 | 39.95
2021-08-01 00:30 | 44409.0208 | 0 | 7.6384 | 39.95
2021-08-01 01:00 | 44409.0417 | 0 | 7.4537 | 39.95
2021-08-01 01:30 | 44409.0625 | 0 | 7.1806 | 39.95
2021-08-01 02:00 | 44409.0833 | 0 | 7.1018 | 39.95
2021-08-01 02:30 | 44409.1042 | 0 | 7.1275 | 39.95
2021-08-01 03:00 | 44409.125 | 0 | 7.1501 | 39.95
2021-08-01 03:30 | 44409.1458 | 0 | 7.1969 | 39.95
2021-08-01 04:00 | 44409.1667 | 0 | 7.1132 | 39.95
2021-08-01 04:30 | 44409.1875 | 0 | 7.1072 | 39.95
2021-08-01 05:00 | 44409.2083 | 0 | 7.1535 | 39.95
2021-08-01 05:30 | 44409.2292 | 0 | 7.3915 | 39.95
2021-08-01 06:00 | 44409.25 | 0 | 7.6794 | 39.95
2021-08-01 06:30 | 44409.2708 | 0 | 8.0842 | 39.95
2021-08-01 07:00 | 44409.2917 | 0 | 8.1683 | 39.95
2021-08-01 07:30 | 44409.3125 | 0 | 8.2001 | 39.95
2021-08-01 08:00 | 44409.3333 | 0 | 8.0011 | 39.95
2021-08-01 08:30 | 44409.3542 | 0 | 7.7941 | 39.95
2021-08-01 09:00 | 44409.375 | 0 | 7.6851 | 39.95
2021-08-01 09:30 | 44409.3958 | 0 | 7.4096 | 39.95
2021-08-01 10:00 | 44409.4167 | 0 | 6.9849 | 39.95
2021-08-01 10:30 | 44409.4375 | 0 | 6.7597 | 39.95
2021-08-01 11:00 | 44409.4583 | 0 | 6.5718 | 39.95
2021-08-01 11:30 | 44409.4792 | 0 | 6.4433 | 39.95
2021-08-01 12:00 | 44409.5 | 0 | 6.337 | 39.95
2021-08-01 12:30 | 44409.5208 | 0 | 6.2972 | 39.95
2021-08-01 13:00 | 44409.5417 | 0 | 6.6308 | 39.95
2021-08-01 13:30 | 44409.5625 | 0 | 6.7103 | 39.95
2021-08-01 14:00 | 44409.5833 | 0 | 7.2675 | 39.95
2021-08-01 14:30 | 44409.6042 | 0 | 7.6104 | 39.95
2021-08-01 15:00 | 44409.625 | 0 | 8.2663 | 39.95
2021-08-01 15:30 | 44409.6458 | 0 | 8.9582 | 39.95
2021-08-01 16:00 | 44409.6667 | 0 | 9.8383 | 39.95
2021-08-01 16:30 | 44409.6875 | 0 | 10.5474 | 39.95
2021-08-01 17:00 | 44409.7083 | 0 | 11.5049 | 39.95
2021-08-01 17:30 | 44409.7292 | 0 | 12.1738 | 39.95
2021-08-01 18:00 | 44409.75 | 0 | 12.4914 | 39.95
2021-08-01 18:30 | 44409.7708 | 0 | 12.5648 | 39.95
2021-08-01 19:00 | 44409.7917 | 0 | 11.992 | 39.95
2021-08-01 19:30 | 44409.8125 | 0 | 11.4482 | 39.95
2021-08-01 20:00 | 44409.8333 | 0 | 11.1299 | 39.95
2021-08-01 20:30 | 44409.8542 | 0 | 10.5198 | 39.95
2021-08-01 21:00 | 44409.875 | 0 | 10.2293 | 39.95
2021-08-01 21:30 | 44409.8958 | 0 | 9.9096 | 39.95
2021-08-01 22:00 | 44409.9167 | 0 | 9.4695 | 39.95
2021-08-01 22:30 | 44409.9375 | 0 | 8.796 | 39.95
2021-08-01 23:00 | 44409.9583 | 0 | 8.2762 | 39.95
2021-08-01 23:30 | 44409.9792 | 0 | 7.884 | 39.95
2021-08-02 | 44410 | 0 | 7.6378 | 39.95
2021-08-02 00:30 | 44410.0208 | 0 | 7.4482 | 39.95
2021-08-02 01:00 | 44410.0417 | 0 | 7.1692 | 39.95
2021-08-02 01:30 | 44410.0625 | 0 | 7.1519 | 39.95
2021-08-02 02:00 | 44410.0833 | 0 | 7.1356 | 39.95
2021-08-02 02:30 | 44410.1042 | 0 | 7.0794 | 39.95
2021-08-02 03:00 | 44410.125 | 0 | 7.0849 | 39.95
2021-08-02 03:30 | 44410.1458 | 0 | 7.4303 | 39.95
2021-08-02 04:00 | 44410.1667 | 0 | 7.6442 | 39.95
2021-08-02 04:30 | 44410.1875 | 0 | 8.0935 | 39.95
2021-08-02 05:00 | 44410.2083 | 0 | 8.4892 | 39.95
2021-08-02 05:30 | 44410.2292 | 0 | 9.1649 | 39.95
2021-08-02 06:00 | 44410.25 | 0 | 10.0185 | 39.95
2021-08-02 06:30 | 44410.2708 | 0 | 10.7903 | 39.95
2021-08-02 07:00 | 44410.2917 | 0 | 11.2204 | 39.95
2021-08-02 07:30 | 44410.3125 | 0 | 10.9282 | 39.95
2021-08-02 08:00 | 44410.3333 | 0 | 11.6183 | 39.95
2021-08-02 08:30 | 44410.3542 | 0 | 10.6881 | 39.95
2021-08-02 09:00 | 44410.375 | 0 | 10.3023 | 39.95
2021-08-02 09:30 | 44410.3958 | 0 | 10.2551 | 39.95
2021-08-02 10:00 | 44410.4167 | 0 | 10.2942 | 39.95
2021-08-02 10:30 | 44410.4375 | 0 | 9.239 | 39.95
2021-08-02 11:00 | 44410.4583 | 0 | 9.5051 | 39.95
2021-08-02 11:30 | 44410.4792 | 0 | 10.2882 | 39.95
2021-08-02 12:00 | 44410.5 | 0 | 9.7779 | 39.95
2021-08-02 12:30 | 44410.5208 | 0 | 11.2997 | 39.95
2021-08-02 13:00 | 44410.5417 | 0 | 9.9606 | 39.95
2021-08-02 13:30 | 44410.5625 | 0 | 10.3565 | 39.95
2021-08-02 14:00 | 44410.5833 | 0 | 11.0473 | 39.95
2021-08-02 14:30 | 44410.6042 | 0 | 11.5425 | 39.95
2021-08-02 15:00 | 44410.625 | 0 | 11.5959 | 39.95
2021-08-02 15:30 | 44410.6458 | 0 | 11.7237 | 39.95
2021-08-02 16:00 | 44410.6667 | 0 | 12.1524 | 39.95
2021-08-02 16:30 | 44410.6875 | 0 | 12.5182 | 39.95
2021-08-02 17:00 | 44410.7083 | 0 | 13.1757 | 39.95
2021-08-02 17:30 | 44410.7292 | 0 | 13.761 | 39.95
2021-08-02 18:00 | 44410.75 | 0 | 14.0249 | 39.95
2021-08-02 18:30 | 44410.7708 | 0 | 14.0462 | 39.95
2021-08-02 19:00 | 44410.7917 | 0 | 13.637 | 39.95
2021-08-02 19:30 | 44410.8125 | 0 | 13.3111 | 39.95
2021-08-02 20:00 | 44410.8333 | 0 | 12.887 | 39.95
2021-08-02 20:30 | 44410.8542 | 0 | 12.3672 | 39.95
2021-08-02 21:00 | 44410.875 | 0 | 11.8376 | 39.95
2021-08-02 21:30 | 44410.8958 | 0 | 11.3995 | 39.95
2021-08-02 22:00 | 44410.9167 | 0 | 10.9333 | 39.95
2021-08-02 22:30 | 44410.9375 | 0 | 10.1807 | 39.95
2021-08-02 23:00 | 44410.9583 | 0 | 9.5275 | 39.95
2021-08-02 23:30 | 44410.9792 | 0 | 9.0373 | 39.95
2021-08-03 | 44411 | 0 | 8.6978 | 39.95
2021-08-03 00:30 | 44411.0208 | 0 | 8.2405 | 39.95
2021-08-03 01:00 | 44411.0417 | 0 | 7.9619 | 39.95
2021-08-03 01:30 | 44411.0625 | 0 | 7.9058 | 39.95
2021-08-03 02:00 | 44411.0833 | 0 | 7.8726 | 39.95
2021-08-03 02:30 | 44411.1042 | 0 | 7.7681 | 39.95
2021-08-03 03:00 | 44411.125 | 0 | 7.7991 | 39.95
2021-08-03 03:30 | 44411.1458 | 0 | 7.939 | 39.95
2021-08-03 04:00 | 44411.1667 | 0 | 8.1267 | 39.95
2021-08-03 04:30 | 44411.1875 | 0 | 8.4695 | 39.95
2021-08-03 05:00 | 44411.2083 | 0 | 8.9006 | 39.95
2021-08-03 05:30 | 44411.2292 | 0 | 9.5453 | 39.95
2021-08-03 06:00 | 44411.25 | 0 | 10.109 | 39.95
2021-08-03 06:30 | 44411.2708 | 0 | 10.8038 | 39.95
2021-08-03 07:00 | 44411.2917 | 0 | 11.7584 | 39.95
2021-08-03 07:30 | 44411.3125 | 0 | 12.1925 | 39.95
2021-08-03 08:00 | 44411.3333 | 0 | 12.908 | 39.95
2021-08-03 08:30 | 44411.3542 | 0 | 13.134 | 39.95
2021-08-03 09:00 | 44411.375 | 0 | 12.2371 | 39.95
2021-08-03 09:30 | 44411.3958 | 0 | 11.3274 | 39.95
2021-08-03 10:00 | 44411.4167 | 0 | 9.8555 | 39.95
2021-08-03 10:30 | 44411.4375 | 0 | 9.8386 | 39.95
2021-08-03 11:00 | 44411.4583 | 0 | 8.5547 | 39.95
2021-08-03 11:30 | 44411.4792 | 0 | 9.2246 | 39.95
2021-08-03 12:00 | 44411.5 | 0 | 10.8393 | 39.95
2021-08-03 12:30 | 44411.5208 | 0 | 11.7784 | 39.95
2021-08-03 13:00 | 44411.5417 | 0 | 11.0616 | 39.95
2021-08-03 13:30 | 44411.5625 | 0 | 11.6182 | 39.95
2021-08-03 14:00 | 44411.5833 | 0 | 12.1112 | 39.95
2021-08-03 14:30 | 44411.6042 | 0 | 11.7922 | 39.95
2021-08-03 15:00 | 44411.625 | 0 | 11.9538 | 39.95
2021-08-03 15:30 | 44411.6458 | 0 | 12.4894 | 39.95
2021-08-03 16:00 | 44411.6667 | 0 | 12.5841 | 39.95
2021-08-03 16:30 | 44411.6875 | 0 | 12.8592 | 39.95
2021-08-03 17:00 | 44411.7083 | 0 | 13.1992 | 39.95
2021-08-03 17:30 | 44411.7292 | 0 | 13.9608 | 39.95
2021-08-03 18:00 | 44411.75 | 0 | 14.1257 | 39.95
2021-08-03 18:30 | 44411.7708 | 0 | 14.1559 | 39.95
2021-08-03 19:00 | 44411.7917 | 0 | 13.792 | 39.95
2021-08-03 19:30 | 44411.8125 | 0 | 13.4115 | 39.95
2021-08-03 20:00 | 44411.8333 | 0 | 13.0909 | 39.95
2021-08-03 20:30 | 44411.8542 | 0 | 12.4383 | 39.95
2021-08-03 21:00 | 44411.875 | 0 | 11.8313 | 39.95
2021-08-03 21:30 | 44411.8958 | 0 | 11.3426 | 39.95
2021-08-03 22:00 | 44411.9167 | 0 | 10.8103 | 39.95
2021-08-03 22:30 | 44411.9375 | 0 | 10.0353 | 39.95
2021-08-03 23:00 | 44411.9583 | 0 | 9.5759 | 39.95
2021-08-03 23:30 | 44411.9792 | 0 | 9.1772 | 39.95
2021-08-04 | 44412 | 0 | 8.681 | 39.95
2021-08-04 00:30 | 44412.0208 | 0 | 8.3176 | 39.95
2021-08-04 01:00 | 44412.0417 | 0 | 8.0681 | 39.95
2021-08-04 01:30 | 44412.0625 | 0 | 7.9118 | 39.95
2021-08-04 02:00 | 44412.0833 | 0 | 7.7772 | 39.95
2021-08-04 02:30 | 44412.1042 | 0 | 7.7571 | 39.95
2021-08-04 03:00 | 44412.125 | 0 | 7.7734 | 39.95
2021-08-04 03:30 | 44412.1458 | 0 | 7.8889 | 39.95
2021-08-04 04:00 | 44412.1667 | 0 | 8.0554 | 39.95
2021-08-04 04:30 | 44412.1875 | 0 | 8.3301 | 39.95
2021-08-04 05:00 | 44412.2083 | 0 | 8.8434 | 39.95
2021-08-04 05:30 | 44412.2292 | 0 | 9.659 | 39.95
2021-08-04 06:00 | 44412.25 | 0 | 10.2894 | 39.95
2021-08-04 06:30 | 44412.2708 | 0 | 10.949 | 39.95
2021-08-04 07:00 | 44412.2917 | 0 | 11.7514 | 39.95
2021-08-04 07:30 | 44412.3125 | 0 | 11.6021 | 39.95
2021-08-04 08:00 | 44412.3333 | 0 | 11.3551 | 39.95
2021-08-04 08:30 | 44412.3542 | 0 | 10.8873 | 39.95
2021-08-04 09:00 | 44412.375 | 0 | 9.9825 | 39.95
2021-08-04 09:30 | 44412.3958 | 0 | 9.5553 | 39.95
2021-08-04 10:00 | 44412.4167 | 0 | 8.797 | 39.95
2021-08-04 10:30 | 44412.4375 | 0 | 8.3548 | 39.95
2021-08-04 11:00 | 44412.4583 | 0 | 8.1182 | 39.95
2021-08-04 11:30 | 44412.4792 | 0 | 7.9655 | 39.95
2021-08-04 12:00 | 44412.5 | 0 | 7.7064 | 39.95
2021-08-04 12:30 | 44412.5208 | 0 | 7.8219 | 39.95
2021-08-04 13:00 | 44412.5417 | 0 | 8.0397 | 39.95
2021-08-04 13:30 | 44412.5625 | 0 | 8.2701 | 39.95
2021-08-04 14:00 | 44412.5833 | 0 | 8.6065 | 39.95
2021-08-04 14:30 | 44412.6042 | 0 | 9.1555 | 39.95
2021-08-04 15:00 | 44412.625 | 0 | 9.7343 | 39.95
2021-08-04 15:30 | 44412.6458 | 0 | 10.4051 | 39.95
2021-08-04 16:00 | 44412.6667 | 0 | 11.362 | 39.95
2021-08-04 16:30 | 44412.6875 | 0 | 12.4719 | 39.95
2021-08-04 17:00 | 44412.7083 | 0 | 13.1807 | 39.95
2021-08-04 17:30 | 44412.7292 | 0 | 14.4477 | 39.95
2021-08-04 18:00 | 44412.75 | 0 | 15.295 | 39.95
2021-08-04 18:30 | 44412.7708 | 0 | 15.6244 | 39.95
2021-08-04 19:00 | 44412.7917 | 0 | 15.2224 | 39.95
2021-08-04 19:30 | 44412.8125 | 0 | 14.835 | 39.95
2021-08-04 20:00 | 44412.8333 | 0 | 14.4909 | 39.95
2021-08-04 20:30 | 44412.8542 | 0 | 13.94 | 39.95
2021-08-04 21:00 | 44412.875 | 0 | 13.2541 | 39.95
2021-08-04 21:30 | 44412.8958 | 0 | 12.6031 | 39.95
2021-08-04 22:00 | 44412.9167 | 0 | 11.8807 | 39.95
2021-08-04 22:30 | 44412.9375 | 0 | 11.0417 | 39.95
2021-08-04 23:00 | 44412.9583 | 0 | 10.2388 | 39.95
2021-08-04 23:30 | 44412.9792 | 0 | 9.7463 | 39.95
2021-08-05 | 44413 | 0 | 9.2042 | 39.95
2021-08-05 00:30 | 44413.0208 | 0 | 8.6507 | 39.95
2021-08-05 01:00 | 44413.0417 | 0 | 8.4592 | 39.95
2021-08-05 01:30 | 44413.0625 | 0 | 8.2168 | 39.95
2021-08-05 02:00 | 44413.0833 | 0 | 8.1663 | 39.95
2021-08-05 02:30 | 44413.1042 | 0 | 8.1122 | 39.95
2021-08-05 03:00 | 44413.125 | 0 | 8.1683 | 39.95
2021-08-05 03:30 | 44413.1458 | 0 | 8.281 | 39.95
2021-08-05 04:00 | 44413.1667 | 0 | 8.5474 | 39.95
2021-08-05 04:30 | 44413.1875 | 0 | 8.8937 | 39.95
2021-08-05 05:00 | 44413.2083 | 0 | 9.5524 | 39.95
2021-08-05 05:30 | 44413.2292 | 0 | 10.2827 | 39.95
2021-08-05 06:00 | 44413.25 | 0 | 11.2862 | 39.95
2021-08-05 06:30 | 44413.2708 | 0 | 12.5165 | 39.95
2021-08-05 07:00 | 44413.2917 | 0 | 13.4284 | 39.95
2021-08-05 07:30 | 44413.3125 | 0 | 13.7812 | 39.95
2021-08-05 08:00 | 44413.3333 | 0 | 13.1156 | 39.95
2021-08-05 08:30 | 44413.3542 | 0 | 12.2595 | 39.95
2021-08-05 09:00 | 44413.375 | 0 | 11.2357 | 39.95
2021-08-05 09:30 | 44413.3958 | 0 | 10.5894 | 39.95
2021-08-05 10:00 | 44413.4167 | 0 | 9.9 | 39.95
2021-08-05 10:30 | 44413.4375 | 0 | 9.5252 | 39.95
2021-08-05 11:00 | 44413.4583 | 0 | 9.2006 | 39.95
2021-08-05 11:30 | 44413.4792 | 0 | 9.0562 | 39.95
2021-08-05 12:00 | 44413.5 | 0 | 8.8184 | 39.95
2021-08-05 12:30 | 44413.5208 | 0 | 8.6765 | 39.95
2021-08-05 13:00 | 44413.5417 | 0 | 8.7649 | 39.95
2021-08-05 13:30 | 44413.5625 | 0 | 8.8397 | 39.95
2021-08-05 14:00 | 44413.5833 | 0 | 9.0924 | 39.95
2021-08-05 14:30 | 44413.6042 | 0 | 9.5593 | 39.95
2021-08-05 15:00 | 44413.625 | 0 | 10.2051 | 39.95
2021-08-05 15:30 | 44413.6458 | 0 | 10.8546 | 39.95
2021-08-05 16:00 | 44413.6667 | 0 | 11.5787 | 39.95
2021-08-05 16:30 | 44413.6875 | 0 | 12.6131 | 39.95
2021-08-05 17:00 | 44413.7083 | 0 | 13.2623 | 39.95
2021-08-05 17:30 | 44413.7292 | 0 | 14.4367 | 39.95
2021-08-05 18:00 | 44413.75 | 0 | 15.1596 | 39.95
2021-08-05 18:30 | 44413.7708 | 0 | 15.3435 | 39.95
2021-08-05 19:00 | 44413.7917 | 0 | 14.8858 | 39.95
2021-08-05 19:30 | 44413.8125 | 0 | 14.678 | 39.95
2021-08-05 20:00 | 44413.8333 | 0 | 14.3494 | 39.95
2021-08-05 20:30 | 44413.8542 | 0 | 13.6929 | 39.95
2021-08-05 21:00 | 44413.875 | 0 | 13.0191 | 39.95
2021-08-05 21:30 | 44413.8958 | 0 | 12.466 | 39.95
2021-08-05 22:00 | 44413.9167 | 0 | 11.8719 | 39.95
2021-08-05 22:30 | 44413.9375 | 0 | 11.064 | 39.95
2021-08-05 23:00 | 44413.9583 | 0 | 10.2405 | 39.95
2021-08-05 23:30 | 44413.9792 | 0 | 9.669 | 39.95
2021-08-06 | 44414 | 0 | 9.1147 | 39.95
2021-08-06 00:30 | 44414.0208 | 0 | 8.798 | 39.95
2021-08-06 01:00 | 44414.0417 | 0 | 8.3873 | 39.95
2021-08-06 01:30 | 44414.0625 | 0 | 8.2391 | 39.95
2021-08-06 02:00 | 44414.0833 | 0 | 8.144 | 39.95
2021-08-06 02:30 | 44414.1042 | 0 | 8.1236 | 39.95
2021-08-06 03:00 | 44414.125 | 0 | 8.0844 | 39.95
2021-08-06 03:30 | 44414.1458 | 0 | 8.2904 | 39.95
2021-08-06 04:00 | 44414.1667 | 0 | 8.5896 | 39.95
2021-08-06 04:30 | 44414.1875 | 0 | 8.9955 | 39.95
2021-08-06 05:00 | 44414.2083 | 0 | 9.6755 | 39.95
2021-08-06 05:30 | 44414.2292 | 0 | 10.3323 | 39.95
2021-08-06 06:00 | 44414.25 | 0 | 11.1308 | 39.95
2021-08-06 06:30 | 44414.2708 | 0 | 12.3383 | 39.95
2021-08-06 07:00 | 44414.2917 | 0 | 13.2832 | 39.95
2021-08-06 07:30 | 44414.3125 | 0 | 13.3054 | 39.95
2021-08-06 08:00 | 44414.3333 | 0 | 12.8784 | 39.95
2021-08-06 08:30 | 44414.3542 | 0 | 12.2118 | 39.95
2021-08-06 09:00 | 44414.375 | 0 | 11.3245 | 39.95
2021-08-06 09:30 | 44414.3958 | 0 | 10.5392 | 39.95
2021-08-06 10:00 | 44414.4167 | 0 | 9.7125 | 39.95
2021-08-06 10:30 | 44414.4375 | 0 | 9.3823 | 39.95
2021-08-06 11:00 | 44414.4583 | 0 | 9.0176 | 39.95
2021-08-06 11:30 | 44414.4792 | 0 | 8.7196 | 39.95
2021-08-06 12:00 | 44414.5 | 0 | 8.3449 | 39.95
2021-08-06 12:30 | 44414.5208 | 0 | 8.2824 | 39.95
2021-08-06 13:00 | 44414.5417 | 0 | 8.2675 | 39.95
2021-08-06 13:30 | 44414.5625 | 0 | 8.6407 | 39.95
2021-08-06 14:00 | 44414.5833 | 0 | 8.7991 | 39.95
2021-08-06 14:30 | 44414.6042 | 0 | 9.1252 | 39.95
2021-08-06 15:00 | 44414.625 | 0 | 9.9395 | 39.95
2021-08-06 15:30 | 44414.6458 | 0 | 10.6273 | 39.95
2021-08-06 16:00 | 44414.6667 | 0 | 11.2421 | 39.95
2021-08-06 16:30 | 44414.6875 | 0 | 12.1246 | 39.95
2021-08-06 17:00 | 44414.7083 | 0 | 12.8394 | 39.95
2021-08-06 17:30 | 44414.7292 | 0 | 13.6895 | 39.95
2021-08-06 18:00 | 44414.75 | 0 | 14.147 | 39.95
2021-08-06 18:30 | 44414.7708 | 0 | 14.5354 | 39.95
2021-08-06 19:00 | 44414.7917 | 0 | 14.2096 | 39.95
2021-08-06 19:30 | 44414.8125 | 0 | 14.0492 | 39.95
2021-08-06 20:00 | 44414.8333 | 0 | 13.772 | 39.95
2021-08-06 20:30 | 44414.8542 | 0 | 13.0954 | 39.95
2021-08-06 21:00 | 44414.875 | 0 | 12.4441 | 39.95
2021-08-06 21:30 | 44414.8958 | 0 | 11.9743 | 39.95
2021-08-06 22:00 | 44414.9167 | 0 | 11.4192 | 39.95
2021-08-06 22:30 | 44414.9375 | 0 | 10.6694 | 39.95
2021-08-06 23:00 | 44414.9583 | 0 | 10.1678 | 39.95
2021-08-06 23:30 | 44414.9792 | 0 | 9.7548 | 39.95
2021-08-07 | 44415 | 0 | 8.994 | 39.95
2021-08-07 00:30 | 44415.0208 | 0 | 8.6261 | 39.95
2021-08-07 01:00 | 44415.0417 | 0 | 8.2973 | 39.95
2021-08-07 01:30 | 44415.0625 | 0 | 8.1351 | 39.95
2021-08-07 02:00 | 44415.0833 | 0 | 7.9673 | 39.95
2021-08-07 02:30 | 44415.1042 | 0 | 7.8631 | 39.95
2021-08-07 03:00 | 44415.125 | 0 | 7.9003 | 39.95
2021-08-07 03:30 | 44415.1458 | 0 | 7.8997 | 39.95
2021-08-07 04:00 | 44415.1667 | 0 | 7.7261 | 39.95
2021-08-07 04:30 | 44415.1875 | 0 | 7.8502 | 39.95
2021-08-07 05:00 | 44415.2083 | 0 | 7.9329 | 39.95
2021-08-07 05:30 | 44415.2292 | 0 | 8.2905 | 39.95
2021-08-07 06:00 | 44415.25 | 0 | 8.7013 | 39.95
2021-08-07 06:30 | 44415.2708 | 0 | 9.1703 | 39.95
2021-08-07 07:00 | 44415.2917 | 0 | 9.7773 | 39.95
2021-08-07 07:30 | 44415.3125 | 0 | 10.2663 | 39.95
2021-08-07 08:00 | 44415.3333 | 0 | 10.7491 | 39.95
2021-08-07 08:30 | 44415.3542 | 0 | 10.8907 | 39.95
2021-08-07 09:00 | 44415.375 | 0 | 8.7953 | 39.95
2021-08-07 09:30 | 44415.3958 | 0 | 9.0793 | 39.95
2021-08-07 10:00 | 44415.4167 | 0 | 8.6457 | 39.95
2021-08-07 10:30 | 44415.4375 | 0 | 8.1809 | 39.95
2021-08-07 11:00 | 44415.4583 | 0 | 7.1002 | 39.95
2021-08-07 11:30 | 44415.4792 | 0 | 7.0419 | 39.95
2021-08-07 12:00 | 44415.5 | 0 | 6.7205 | 39.95
2021-08-07 12:30 | 44415.5208 | 0 | 6.5827 | 39.95
2021-08-07 13:00 | 44415.5417 | 0 | 6.6229 | 39.95
2021-08-07 13:30 | 44415.5625 | 0 | 6.8332 | 39.95
2021-08-07 14:00 | 44415.5833 | 0 | 7.2795 | 39.95
2021-08-07 14:30 | 44415.6042 | 0 | 7.6052 | 39.95
2021-08-07 15:00 | 44415.625 | 0 | 8.105 | 39.95
2021-08-07 15:30 | 44415.6458 | 0 | 8.884 | 39.95
2021-08-07 16:00 | 44415.6667 | 0 | 9.6084 | 39.95
2021-08-07 16:30 | 44415.6875 | 0 | 10.5266 | 39.95
2021-08-07 17:00 | 44415.7083 | 0 | 11.3887 | 39.95
2021-08-07 17:30 | 44415.7292 | 0 | 12.4059 | 39.95
2021-08-07 18:00 | 44415.75 | 0 | 12.9787 | 39.95
2021-08-07 18:30 | 44415.7708 | 0 | 13.1417 | 39.95
2021-08-07 19:00 | 44415.7917 | 0 | 12.7628 | 39.95
2021-08-07 19:30 | 44415.8125 | 0 | 12.6463 | 39.95
2021-08-07 20:00 | 44415.8333 | 0 | 12.4105 | 39.95
2021-08-07 20:30 | 44415.8542 | 0 | 11.8045 | 39.95
2021-08-07 21:00 | 44415.875 | 0 | 11.2368 | 39.95
2021-08-07 21:30 | 44415.8958 | 0 | 11.0329 | 39.95
2021-08-07 22:00 | 44415.9167 | 0 | 10.4498 | 39.95
2021-08-07 22:30 | 44415.9375 | 0 | 9.845 | 39.95
2021-08-07 23:00 | 44415.9583 | 0 | 9.2514 | 39.95
2021-08-07 23:30 | 44415.9792 | 0 | 8.6812 | 39.95
2021-08-08 | 44416 | 0 | 8.3067 | 39.95
2021-08-08 00:30 | 44416.0208 | 0 | 7.951 | 39.95
2021-08-08 01:00 | 44416.0417 | 0 | 7.6885 | 39.95
2021-08-08 01:30 | 44416.0625 | 0 | 7.4881 | 39.95
2021-08-08 02:00 | 44416.0833 | 0 | 7.2967 | 39.95
2021-08-08 02:30 | 44416.1042 | 0 | 7.294 | 39.95
2021-08-08 03:00 | 44416.125 | 0 | 7.3136 | 39.95
2021-08-08 03:30 | 44416.1458 | 0 | 7.3366 | 39.95
2021-08-08 04:00 | 44416.1667 | 0 | 7.269 | 39.95
2021-08-08 04:30 | 44416.1875 | 0 | 7.3806 | 39.95
2021-08-08 05:00 | 44416.2083 | 0 | 7.5653 | 39.95
2021-08-08 05:30 | 44416.2292 | 0 | 7.5941 | 39.95
2021-08-08 06:00 | 44416.25 | 0 | 7.9722 | 39.95
2021-08-08 06:30 | 44416.2708 | 0 | 8.2125 | 39.95
2021-08-08 07:00 | 44416.2917 | 0 | 8.6999 | 39.95
2021-08-08 07:30 | 44416.3125 | 0 | 8.6769 | 39.95
2021-08-08 08:00 | 44416.3333 | 0 | 8.5256 | 39.95
2021-08-08 08:30 | 44416.3542 | 0 | 8.2452 | 39.95
2021-08-08 09:00 | 44416.375 | 0 | 7.8864 | 39.95
2021-08-08 09:30 | 44416.3958 | 0 | 7.4675 | 39.95
2021-08-08 10:00 | 44416.4167 | 0 | 6.7869 | 39.95
2021-08-08 10:30 | 44416.4375 | 0 | 6.4036 | 39.95
2021-08-08 11:00 | 44416.4583 | 0 | 6.19 | 39.95
2021-08-08 11:30 | 44416.4792 | 0 | 6.0413 | 39.95
2021-08-08 12:00 | 44416.5 | 0 | 6.3584 | 39.95
2021-08-08 12:30 | 44416.5208 | 0 | 7.2454 | 39.95
2021-08-08 13:00 | 44416.5417 | 0 | 7.8828 | 39.95
2021-08-08 13:30 | 44416.5625 | 0 | 8.4506 | 39.95
2021-08-08 14:00 | 44416.5833 | 0 | 7.2268 | 39.95
2021-08-08 14:30 | 44416.6042 | 0 | 7.3883 | 39.95
2021-08-08 15:00 | 44416.625 | 0 | 8.3906 | 39.95
2021-08-08 15:30 | 44416.6458 | 0 | 9.6379 | 39.95
2021-08-08 16:00 | 44416.6667 | 0 | 10.207 | 39.95
2021-08-08 16:30 | 44416.6875 | 0 | 10.3514 | 39.95
2021-08-08 17:00 | 44416.7083 | 0 | 11.2527 | 39.95
2021-08-08 17:30 | 44416.7292 | 0 | 12.0085 | 39.95
2021-08-08 18:00 | 44416.75 | 0 | 12.4871 | 39.95
2021-08-08 18:30 | 44416.7708 | 0 | 12.5642 | 39.95
2021-08-08 19:00 | 44416.7917 | 0 | 12.1778 | 39.95
2021-08-08 19:30 | 44416.8125 | 0 | 12.0113 | 39.95
2021-08-08 20:00 | 44416.8333 | 0 | 11.7977 | 39.95
2021-08-08 20:30 | 44416.8542 | 0 | 11.2874 | 39.95
2021-08-08 21:00 | 44416.875 | 0 | 10.8878 | 39.95
2021-08-08 21:30 | 44416.8958 | 0 | 10.4114 | 39.95
2021-08-08 22:00 | 44416.9167 | 0 | 9.8499 | 39.95
2021-08-08 22:30 | 44416.9375 | 0 | 9.1202 | 39.95
2021-08-08 23:00 | 44416.9583 | 0 | 8.5498 | 39.95
2021-08-08 23:30 | 44416.9792 | 0 | 8.2228 | 39.95
2021-08-09 | 44417 | 0 | 7.7912 | 39.95
2021-08-09 00:30 | 44417.0208 | 0 | 7.5768 | 39.95
2021-08-09 01:00 | 44417.0417 | 0 | 7.3589 | 39.95
2021-08-09 01:30 | 44417.0625 | 0 | 7.2601 | 39.95
2021-08-09 02:00 | 44417.0833 | 0 | 7.2768 | 39.95
2021-08-09 02:30 | 44417.1042 | 0 | 7.1464 | 39.95
2021-08-09 03:00 | 44417.125 | 0 | 7.2432 | 39.95
2021-08-09 03:30 | 44417.1458 | 0 | 7.3971 | 39.95
2021-08-09 04:00 | 44417.1667 | 0 | 7.6124 | 39.95
2021-08-09 04:30 | 44417.1875 | 0 | 8.1053 | 39.95
2021-08-09 05:00 | 44417.2083 | 0 | 8.7946 | 39.95
2021-08-09 05:30 | 44417.2292 | 0 | 9.6079 | 39.95
2021-08-09 06:00 | 44417.25 | 0 | 10.6887 | 39.95
2021-08-09 06:30 | 44417.2708 | 0 | 12.2182 | 39.95
2021-08-09 07:00 | 44417.2917 | 0 | 13.2917 | 39.95
2021-08-09 07:30 | 44417.3125 | 0 | 13.9198 | 39.95
2021-08-09 08:00 | 44417.3333 | 0 | 13.8116 | 39.95
2021-08-09 08:30 | 44417.3542 | 0 | 13.3241 | 39.95
2021-08-09 09:00 | 44417.375 | 0 | 12.8568 | 39.95
2021-08-09 09:30 | 44417.3958 | 0 | 11.75 | 39.95
2021-08-09 10:00 | 44417.4167 | 0 | 12.2669 | 39.95
2021-08-09 10:30 | 44417.4375 | 0 | 12.1778 | 39.95
2021-08-09 11:00 | 44417.4583 | 0 | 11.1575 | 39.95
2021-08-09 11:30 | 44417.4792 | 0 | 11.6853 | 39.95
2021-08-09 12:00 | 44417.5 | 0 | 11.1565 | 39.95
2021-08-09 12:30 | 44417.5208 | 0 | 9.5026 | 39.95
2021-08-09 13:00 | 44417.5417 | 0 | 8.9734 | 39.95
2021-08-09 13:30 | 44417.5625 | 0 | 10.0873 | 39.95
2021-08-09 14:00 | 44417.5833 | 0 | 11.4438 | 39.95
2021-08-09 14:30 | 44417.6042 | 0 | 11.0607 | 39.95
2021-08-09 15:00 | 44417.625 | 0 | 11.0438 | 39.95
2021-08-09 15:30 | 44417.6458 | 0 | 11.4557 | 39.95
2021-08-09 16:00 | 44417.6667 | 0 | 12.1681 | 39.95
2021-08-09 16:30 | 44417.6875 | 0 | 12.8651 | 39.95
2021-08-09 17:00 | 44417.7083 | 0 | 13.7693 | 39.95
2021-08-09 17:30 | 44417.7292 | 0 | 14.6067 | 39.95
2021-08-09 18:00 | 44417.75 | 0 | 15.0631 | 39.95
2021-08-09 18:30 | 44417.7708 | 0 | 15.3529 | 39.95
2021-08-09 19:00 | 44417.7917 | 0 | 14.7009 | 39.95
2021-08-09 19:30 | 44417.8125 | 0 | 14.7251 | 39.95
2021-08-09 20:00 | 44417.8333 | 0 | 14.0562 | 39.95
2021-08-09 20:30 | 44417.8542 | 0 | 13.6049 | 39.95
2021-08-09 21:00 | 44417.875 | 0 | 12.7468 | 39.95
2021-08-09 21:30 | 44417.8958 | 0 | 12.3383 | 39.95
2021-08-09 22:00 | 44417.9167 | 0 | 11.4347 | 39.95
2021-08-09 22:30 | 44417.9375 | 0 | 10.6241 | 39.95
2021-08-09 23:00 | 44417.9583 | 0 | 9.9411 | 39.95
2021-08-09 23:30 | 44417.9792 | 0 | 9.3578 | 39.95
2021-08-10 | 44418 | 0 | 8.9049 | 39.95
2021-08-10 00:30 | 44418.0208 | 0 | 8.371 | 39.95
2021-08-10 01:00 | 44418.0417 | 0 | 8.2337 | 39.95
2021-08-10 01:30 | 44418.0625 | 0 | 8.0681 | 39.95
2021-08-10 02:00 | 44418.0833 | 0 | 8.0283 | 39.95
2021-08-10 02:30 | 44418.1042 | 0 | 8.0567 | 39.95
2021-08-10 03:00 | 44418.125 | 0 | 8.0005 | 39.95
2021-08-10 03:30 | 44418.1458 | 0 | 8.0512 | 39.95
2021-08-10 04:00 | 44418.1667 | 0 | 8.1971 | 39.95
2021-08-10 04:30 | 44418.1875 | 0 | 8.6445 | 39.95
2021-08-10 05:00 | 44418.2083 | 0 | 9.3818 | 39.95
2021-08-10 05:30 | 44418.2292 | 0 | 10.1865 | 39.95
2021-08-10 06:00 | 44418.25 | 0 | 11.2981 | 39.95
2021-08-10 06:30 | 44418.2708 | 0 | 12.6557 | 39.95
2021-08-10 07:00 | 44418.2917 | 0 | 14.016 | 39.95
2021-08-10 07:30 | 44418.3125 | 0 | 14.0641 | 39.95
2021-08-10 08:00 | 44418.3333 | 0 | 13.9515 | 39.95
2021-08-10 08:30 | 44418.3542 | 0 | 13.3962 | 39.95
2021-08-10 09:00 | 44418.375 | 0 | 12.0523 | 39.95
2021-08-10 09:30 | 44418.3958 | 0 | 11.0568 | 39.95
2021-08-10 10:00 | 44418.4167 | 0 | 10.1983 | 39.95
2021-08-10 10:30 | 44418.4375 | 0 | 10.2254 | 39.95
2021-08-10 11:00 | 44418.4583 | 0 | 9.3568 | 39.95
2021-08-10 11:30 | 44418.4792 | 0 | 10.7297 | 39.95
2021-08-10 12:00 | 44418.5 | 0 | 11.6745 | 39.95
2021-08-10 12:30 | 44418.5208 | 0 | 11.4556 | 39.95
2021-08-10 13:00 | 44418.5417 | 0 | 11.2726 | 39.95
2021-08-10 13:30 | 44418.5625 | 0 | 11.3416 | 39.95
2021-08-10 14:00 | 44418.5833 | 0 | 10.8351 | 39.95
2021-08-10 14:30 | 44418.6042 | 0 | 10.1842 | 39.95
2021-08-10 15:00 | 44418.625 | 0 | 9.7344 | 39.95
2021-08-10 15:30 | 44418.6458 | 0 | 11.0267 | 39.95
2021-08-10 16:00 | 44418.6667 | 0 | 11.4895 | 39.95
2021-08-10 16:30 | 44418.6875 | 0 | 12.1334 | 39.95
2021-08-10 17:00 | 44418.7083 | 0 | 12.9273 | 39.95
2021-08-10 17:30 | 44418.7292 | 0 | 13.9425 | 39.95
2021-08-10 18:00 | 44418.75 | 0 | 14.5939 | 39.95
2021-08-10 18:30 | 44418.7708 | 0 | 14.4737 | 39.95
2021-08-10 19:00 | 44418.7917 | 0 | 14.2144 | 39.95
2021-08-10 19:30 | 44418.8125 | 0 | 14.3152 | 39.95
2021-08-10 20:00 | 44418.8333 | 0 | 14.1227 | 39.95
2021-08-10 20:30 | 44418.8542 | 0 | 13.5653 | 39.95
2021-08-10 21:00 | 44418.875 | 0 | 12.9686 | 39.95
2021-08-10 21:30 | 44418.8958 | 0 | 12.3915 | 39.95
2021-08-10 22:00 | 44418.9167 | 0 | 11.6742 | 39.95
2021-08-10 22:30 | 44418.9375 | 0 | 10.8521 | 39.95
2021-08-10 23:00 | 44418.9583 | 0 | 10.0259 | 39.95
2021-08-10 23:30 | 44418.9792 | 0 | 9.4248 | 39.95
2021-08-11 | 44419 | 0 | 8.8145 | 39.95
2021-08-11 00:30 | 44419.0208 | 0 | 8.4031 | 39.95
2021-08-11 01:00 | 44419.0417 | 0 | 8.2297 | 39.95
2021-08-11 01:30 | 44419.0625 | 0 | 8.1128 | 39.95
2021-08-11 02:00 | 44419.0833 | 0 | 8.0953 | 39.95
2021-08-11 02:30 | 44419.1042 | 0 | 7.9912 | 39.95
2021-08-11 03:00 | 44419.125 | 0 | 7.872 | 39.95
2021-08-11 03:30 | 44419.1458 | 0 | 8.0953 | 39.95
2021-08-11 04:00 | 44419.1667 | 0 | 8.4052 | 39.95
2021-08-11 04:30 | 44419.1875 | 0 | 8.8914 | 39.95
2021-08-11 05:00 | 44419.2083 | 0 | 9.5069 | 39.95
2021-08-11 05:30 | 44419.2292 | 0 | 10.3823 | 39.95
2021-08-11 06:00 | 44419.25 | 0 | 11.5437 | 39.95
2021-08-11 06:30 | 44419.2708 | 0 | 11.7735 | 39.95
2021-08-11 07:00 | 44419.2917 | 0 | 12.3187 | 39.95
2021-08-11 07:30 | 44419.3125 | 0 | 12.0284 | 39.95
2021-08-11 08:00 | 44419.3333 | 0 | 12.5209 | 39.95
2021-08-11 08:30 | 44419.3542 | 0 | 12.2824 | 39.95
2021-08-11 09:00 | 44419.375 | 0 | 12.3926 | 39.95
2021-08-11 09:30 | 44419.3958 | 0 | 11.1464 | 39.95
2021-08-11 10:00 | 44419.4167 | 0 | 9.6933 | 39.95
2021-08-11 10:30 | 44419.4375 | 0 | 8.9429 | 39.95
2021-08-11 11:00 | 44419.4583 | 0 | 10.1786 | 39.95
2021-08-11 11:30 | 44419.4792 | 0 | 9.0948 | 39.95
2021-08-11 12:00 | 44419.5 | 0 | 10.1092 | 39.95
2021-08-11 12:30 | 44419.5208 | 0 | 8.9135 | 39.95
2021-08-11 13:00 | 44419.5417 | 0 | 8.4924 | 39.95
2021-08-11 13:30 | 44419.5625 | 0 | 8.9221 | 39.95
2021-08-11 14:00 | 44419.5833 | 0 | 8.8842 | 39.95
2021-08-11 14:30 | 44419.6042 | 0 | 9.4123 | 39.95
2021-08-11 15:00 | 44419.625 | 0 | 10.1621 | 39.95
2021-08-11 15:30 | 44419.6458 | 0 | 10.7795 | 39.95
2021-08-11 16:00 | 44419.6667 | 0 | 11.3152 | 39.95
2021-08-11 16:30 | 44419.6875 | 0 | 11.5416 | 39.95
2021-08-11 17:00 | 44419.7083 | 0 | 12.1244 | 39.95
2021-08-11 17:30 | 44419.7292 | 0 | 12.9945 | 39.95
2021-08-11 18:00 | 44419.75 | 0 | 13.3789 | 39.95
2021-08-11 18:30 | 44419.7708 | 0 | 13.6139 | 39.95
2021-08-11 19:00 | 44419.7917 | 0 | 13.2336 | 39.95
2021-08-11 19:30 | 44419.8125 | 0 | 12.8863 | 39.95
2021-08-11 20:00 | 44419.8333 | 0 | 12.5163 | 39.95
2021-08-11 20:30 | 44419.8542 | 0 | 12.1465 | 39.95
2021-08-11 21:00 | 44419.875 | 0 | 11.5765 | 39.95
2021-08-11 21:30 | 44419.8958 | 0 | 11.279 | 39.95
2021-08-11 22:00 | 44419.9167 | 0 | 10.6782 | 39.95
2021-08-11 22:30 | 44419.9375 | 0 | 9.8624 | 39.95
2021-08-11 23:00 | 44419.9583 | 0 | 9.1888 | 39.95
2021-08-11 23:30 | 44419.9792 | 0 | 8.7549 | 39.95
2021-08-12 | 44420 | 0 | 8.2889 | 39.95
2021-08-12 00:30 | 44420.0208 | 0 | 7.9172 | 39.95
2021-08-12 01:00 | 44420.0417 | 0 | 7.7832 | 39.95
2021-08-12 01:30 | 44420.0625 | 0 | 7.6883 | 39.95
2021-08-12 02:00 | 44420.0833 | 0 | 7.5991 | 39.95
2021-08-12 02:30 | 44420.1042 | 0 | 7.4051 | 39.95
2021-08-12 03:00 | 44420.125 | 0 | 7.5146 | 39.95
2021-08-12 03:30 | 44420.1458 | 0 | 7.5653 | 39.95
2021-08-12 04:00 | 44420.1667 | 0 | 7.7729 | 39.95
2021-08-12 04:30 | 44420.1875 | 0 | 8.4354 | 39.95
2021-08-12 05:00 | 44420.2083 | 0 | 8.8496 | 39.95
2021-08-12 05:30 | 44420.2292 | 0 | 9.7011 | 39.95
2021-08-12 06:00 | 44420.25 | 0 | 10.5851 | 39.95
2021-08-12 06:30 | 44420.2708 | 0 | 11.7291 | 39.95
2021-08-12 07:00 | 44420.2917 | 0 | 12.1429 | 39.95
2021-08-12 07:30 | 44420.3125 | 0 | 11.9177 | 39.95
2021-08-12 08:00 | 44420.3333 | 0 | 11.3878 | 39.95
2021-08-12 08:30 | 44420.3542 | 0 | 10.5927 | 39.95
2021-08-12 09:00 | 44420.375 | 0 | 10.0344 | 39.95
2021-08-12 09:30 | 44420.3958 | 0 | 9.4523 | 39.95
2021-08-12 10:00 | 44420.4167 | 0 | 8.8823 | 39.95
2021-08-12 10:30 | 44420.4375 | 0 | 8.4985 | 39.95
2021-08-12 11:00 | 44420.4583 | 0 | 8.1828 | 39.95
2021-08-12 11:30 | 44420.4792 | 0 | 8.012 | 39.95
2021-08-12 12:00 | 44420.5 | 0 | 7.8496 | 39.95
2021-08-12 12:30 | 44420.5208 | 0 | 8.1291 | 39.95
2021-08-12 13:00 | 44420.5417 | 0 | 8.1638 | 39.95
2021-08-12 13:30 | 44420.5625 | 0 | 8.4515 | 39.95
2021-08-12 14:00 | 44420.5833 | 0 | 8.9828 | 39.95
2021-08-12 14:30 | 44420.6042 | 0 | 9.165 | 39.95
2021-08-12 15:00 | 44420.625 | 0 | 9.838 | 39.95
2021-08-12 15:30 | 44420.6458 | 0 | 10.2721 | 39.95
2021-08-12 16:00 | 44420.6667 | 0 | 10.8993 | 39.95
2021-08-12 16:30 | 44420.6875 | 0 | 11.483 | 39.95
2021-08-12 17:00 | 44420.7083 | 0 | 12.1575 | 39.95
2021-08-12 17:30 | 44420.7292 | 0 | 12.695 | 39.95
2021-08-12 18:00 | 44420.75 | 0 | 13.005 | 39.95
2021-08-12 18:30 | 44420.7708 | 0 | 13.285 | 39.95
2021-08-12 19:00 | 44420.7917 | 0 | 12.736 | 39.95
2021-08-12 19:30 | 44420.8125 | 0 | 12.3689 | 39.95
2021-08-12 20:00 | 44420.8333 | 0 | 12.1296 | 39.95
2021-08-12 20:30 | 44420.8542 | 0 | 11.7838 | 39.95
2021-08-12 21:00 | 44420.875 | 0 | 11.346 | 39.95
2021-08-12 21:30 | 44420.8958 | 0 | 11.4499 | 39.95
2021-08-12 22:00 | 44420.9167 | 0 | 11.0374 | 39.95
2021-08-12 22:30 | 44420.9375 | 0 | 10.2764 | 39.95
2021-08-12 23:00 | 44420.9583 | 0 | 9.6246 | 39.95
2021-08-12 23:30 | 44420.9792 | 0 | 9.2402 | 39.95
2021-08-13 | 44421 | 0 | 8.6314 | 39.95
2021-08-13 00:30 | 44421.0208 | 0 | 8.2242 | 39.95
2021-08-13 01:00 | 44421.0417 | 0 | 8.0965 | 39.95
2021-08-13 01:30 | 44421.0625 | 0 | 7.7941 | 39.95
2021-08-13 02:00 | 44421.0833 | 0 | 7.7681 | 39.95
2021-08-13 02:30 | 44421.1042 | 0 | 7.5525 | 39.95
2021-08-13 03:00 | 44421.125 | 0 | 7.5768 | 39.95
2021-08-13 03:30 | 44421.1458 | 0 | 7.604 | 39.95
2021-08-13 04:00 | 44421.1667 | 0 | 7.7877 | 39.95
2021-08-13 04:30 | 44421.1875 | 0 | 8.2208 | 39.95
2021-08-13 05:00 | 44421.2083 | 0 | 8.8219 | 39.95
2021-08-13 05:30 | 44421.2292 | 0 | 9.4377 | 39.95
2021-08-13 06:00 | 44421.25 | 0 | 10.2279 | 39.95
2021-08-13 06:30 | 44421.2708 | 0 | 11.0286 | 39.95
2021-08-13 07:00 | 44421.2917 | 0 | 11.8512 | 39.95
2021-08-13 07:30 | 44421.3125 | 0 | 11.384 | 39.95
2021-08-13 08:00 | 44421.3333 | 0 | 10.9629 | 39.95
2021-08-13 08:30 | 44421.3542 | 0 | 10.2765 | 39.95
2021-08-13 09:00 | 44421.375 | 0 | 9.6337 | 39.95
2021-08-13 09:30 | 44421.3958 | 0 | 8.9339 | 39.95
2021-08-13 10:00 | 44421.4167 | 0 | 8.582 | 39.95
2021-08-13 10:30 | 44421.4375 | 0 | 8.3003 | 39.95
2021-08-13 11:00 | 44421.4583 | 0 | 8.2424 | 39.95
2021-08-13 11:30 | 44421.4792 | 0 | 8.0029 | 39.95
2021-08-13 12:00 | 44421.5 | 0 | 8.1387 | 39.95
2021-08-13 12:30 | 44421.5208 | 0 | 8.3404 | 39.95
2021-08-13 13:00 | 44421.5417 | 0 | 9.3445 | 39.95
2021-08-13 13:30 | 44421.5625 | 0 | 9.7909 | 39.95
2021-08-13 14:00 | 44421.5833 | 0 | 9.5664 | 39.95
2021-08-13 14:30 | 44421.6042 | 0 | 9.1483 | 39.95
2021-08-13 15:00 | 44421.625 | 0 | 9.5469 | 39.95
2021-08-13 15:30 | 44421.6458 | 0 | 10.478 | 39.95
2021-08-13 16:00 | 44421.6667 | 0 | 11.5356 | 39.95
2021-08-13 16:30 | 44421.6875 | 0 | 12.0085 | 39.95
2021-08-13 17:00 | 44421.7083 | 0 | 12.3915 | 39.95
2021-08-13 17:30 | 44421.7292 | 0 | 12.5118 | 39.95
2021-08-13 18:00 | 44421.75 | 0 | 12.5107 | 39.95
2021-08-13 18:30 | 44421.7708 | 0 | 12.4095 | 39.95
2021-08-13 19:00 | 44421.7917 | 0 | 12.2389 | 39.95
2021-08-13 19:30 | 44421.8125 | 0 | 11.9445 | 39.95
2021-08-13 20:00 | 44421.8333 | 0 | 11.6136 | 39.95
2021-08-13 20:30 | 44421.8542 | 0 | 11.1165 | 39.95
2021-08-13 21:00 | 44421.875 | 0 | 10.7971 | 39.95
2021-08-13 21:30 | 44421.8958 | 0 | 10.4806 | 39.95
2021-08-13 22:00 | 44421.9167 | 0 | 10.086 | 39.95
2021-08-13 22:30 | 44421.9375 | 0 | 9.565 | 39.95
2021-08-13 23:00 | 44421.9583 | 0 | 8.9898 | 39.95
2021-08-13 23:30 | 44421.9792 | 0 | 8.5111 | 39.95
2021-08-14 | 44422 | 0 | 8.0407 | 39.95
2021-08-14 00:30 | 44422.0208 | 0 | 7.7701 | 39.95
2021-08-14 01:00 | 44422.0417 | 0 | 7.5328 | 39.95
2021-08-14 01:30 | 44422.0625 | 0 | 7.3867 | 39.95
2021-08-14 02:00 | 44422.0833 | 0 | 7.3142 | 39.95
2021-08-14 02:30 | 44422.1042 | 0 | 7.1672 | 39.95
2021-08-14 03:00 | 44422.125 | 0 | 7.2354 | 39.95
2021-08-14 03:30 | 44422.1458 | 0 | 7.2973 | 39.95
2021-08-14 04:00 | 44422.1667 | 0 | 7.3245 | 39.95
2021-08-14 04:30 | 44422.1875 | 0 | 7.5484 | 39.95
2021-08-14 05:00 | 44422.2083 | 0 | 7.7152 | 39.95
2021-08-14 05:30 | 44422.2292 | 0 | 8.0214 | 39.95
2021-08-14 06:00 | 44422.25 | 0 | 8.3404 | 39.95
2021-08-14 06:30 | 44422.2708 | 0 | 8.8089 | 39.95
2021-08-14 07:00 | 44422.2917 | 0 | 9.0894 | 39.95
2021-08-14 07:30 | 44422.3125 | 0 | 9.3031 | 39.95
2021-08-14 08:00 | 44422.3333 | 0 | 9.5608 | 39.95
2021-08-14 08:30 | 44422.3542 | 0 | 9.187 | 39.95
2021-08-14 09:00 | 44422.375 | 0 | 9.2363 | 39.95
2021-08-14 09:30 | 44422.3958 | 0 | 8.4949 | 39.95
2021-08-14 10:00 | 44422.4167 | 0 | 7.8778 | 39.95
2021-08-14 10:30 | 44422.4375 | 0 | 7.3752 | 39.95
2021-08-14 11:00 | 44422.4583 | 0 | 7.0182 | 39.95
2021-08-14 11:30 | 44422.4792 | 0 | 7.0185 | 39.95
2021-08-14 12:00 | 44422.5 | 0 | 6.7171 | 39.95
2021-08-14 12:30 | 44422.5208 | 0 | 6.5904 | 39.95
2021-08-14 13:00 | 44422.5417 | 0 | 6.7795 | 39.95
2021-08-14 13:30 | 44422.5625 | 0 | 6.5885 | 39.95
2021-08-14 14:00 | 44422.5833 | 0 | 6.8268 | 39.95
2021-08-14 14:30 | 44422.6042 | 0 | 7.389 | 39.95
2021-08-14 15:00 | 44422.625 | 0 | 7.9175 | 39.95
2021-08-14 15:30 | 44422.6458 | 0 | 8.5505 | 39.95
2021-08-14 16:00 | 44422.6667 | 0 | 9.3056 | 39.95
2021-08-14 16:30 | 44422.6875 | 0 | 10.0652 | 39.95
2021-08-14 17:00 | 44422.7083 | 0 | 10.5525 | 39.95
2021-08-14 17:30 | 44422.7292 | 0 | 10.9268 | 39.95
2021-08-14 18:00 | 44422.75 | 0 | 11.3067 | 39.95
2021-08-14 18:30 | 44422.7708 | 0 | 11.2198 | 39.95
2021-08-14 19:00 | 44422.7917 | 0 | 11.1301 | 39.95
2021-08-14 19:30 | 44422.8125 | 0 | 10.9987 | 39.95
2021-08-14 20:00 | 44422.8333 | 0 | 10.6977 | 39.95
2021-08-14 20:30 | 44422.8542 | 0 | 10.2998 | 39.95
2021-08-14 21:00 | 44422.875 | 0 | 9.9851 | 39.95
2021-08-14 21:30 | 44422.8958 | 0 | 9.7399 | 39.95
2021-08-14 22:00 | 44422.9167 | 0 | 9.3455 | 39.95
2021-08-14 22:30 | 44422.9375 | 0 | 8.9333 | 39.95
2021-08-14 23:00 | 44422.9583 | 0 | 8.5055 | 39.95
2021-08-14 23:30 | 44422.9792 | 0 | 8.1794 | 39.95
2021-08-15 | 44423 | 0 | 7.5913 | 39.95
2021-08-15 00:30 | 44423.0208 | 0 | 7.3704 | 39.95
2021-08-15 01:00 | 44423.0417 | 0 | 7.2625 | 39.95
2021-08-15 01:30 | 44423.0625 | 0 | 6.9459 | 39.95
2021-08-15 02:00 | 44423.0833 | 0 | 6.9901 | 39.95
2021-08-15 02:30 | 44423.1042 | 0 | 6.9678 | 39.95
2021-08-15 03:00 | 44423.125 | 0 | 6.802 | 39.95
2021-08-15 03:30 | 44423.1458 | 0 | 6.8676 | 39.95
2021-08-15 04:00 | 44423.1667 | 0 | 6.8338 | 39.95
2021-08-15 04:30 | 44423.1875 | 0 | 6.8223 | 39.95
2021-08-15 05:00 | 44423.2083 | 0 | 6.9624 | 39.95
2021-08-15 05:30 | 44423.2292 | 0 | 7.0605 | 39.95
2021-08-15 06:00 | 44423.25 | 0 | 7.2655 | 39.95
2021-08-15 06:30 | 44423.2708 | 0 | 7.537 | 39.95
2021-08-15 07:00 | 44423.2917 | 0 | 7.4313 | 39.95
2021-08-15 07:30 | 44423.3125 | 0 | 7.4537 | 39.95
2021-08-15 08:00 | 44423.3333 | 0 | 7.2716 | 39.95
2021-08-15 08:30 | 44423.3542 | 0 | 7.0472 | 39.95
2021-08-15 09:00 | 44423.375 | 0 | 6.7171 | 39.95
2021-08-15 09:30 | 44423.3958 | 0 | 6.4166 | 39.95
2021-08-15 10:00 | 44423.4167 | 0 | 6.1191 | 39.95
2021-08-15 10:30 | 44423.4375 | 0 | 6.334 | 39.95
2021-08-15 11:00 | 44423.4583 | 0 | 5.5572 | 39.95
2021-08-15 11:30 | 44423.4792 | 0 | 5.7193 | 39.95
2021-08-15 12:00 | 44423.5 | 0 | 6.2745 | 39.95
2021-08-15 12:30 | 44423.5208 | 0 | 5.6792 | 39.95
2021-08-15 13:00 | 44423.5417 | 0 | 5.48 | 39.95
2021-08-15 13:30 | 44423.5625 | 0 | 5.92 | 39.95
2021-08-15 14:00 | 44423.5833 | 0 | 8.1219 | 39.95
2021-08-15 14:30 | 44423.6042 | 0 | 9.6061 | 39.95
2021-08-15 15:00 | 44423.625 | 0 | 9.6596 | 39.95
2021-08-15 15:30 | 44423.6458 | 0 | 9.088 | 39.95
2021-08-15 16:00 | 44423.6667 | 0 | 8.6805 | 39.95
2021-08-15 16:30 | 44423.6875 | 0 | 9.8425 | 39.95
2021-08-15 17:00 | 44423.7083 | 0 | 10.6165 | 39.95
2021-08-15 17:30 | 44423.7292 | 0 | 11.3766 | 39.95
2021-08-15 18:00 | 44423.75 | 0 | 11.8536 | 39.95
2021-08-15 18:30 | 44423.7708 | 0 | 11.8437 | 39.95
2021-08-15 19:00 | 44423.7917 | 0 | 11.5598 | 39.95
2021-08-15 19:30 | 44423.8125 | 0 | 11.1815 | 39.95
2021-08-15 20:00 | 44423.8333 | 0 | 10.9792 | 39.95
2021-08-15 20:30 | 44423.8542 | 0 | 10.4849 | 39.95
2021-08-15 21:00 | 44423.875 | 0 | 10.0218 | 39.95
2021-08-15 21:30 | 44423.8958 | 0 | 9.6869 | 39.95
2021-08-15 22:00 | 44423.9167 | 0 | 9.1429 | 39.95
2021-08-15 22:30 | 44423.9375 | 0 | 8.5792 | 39.95
2021-08-15 23:00 | 44423.9583 | 0 | 7.9124 | 39.95
2021-08-15 23:30 | 44423.9792 | 0 | 7.6418 | 39.95
2021-08-16 | 44424 | 0 | 7.3832 | 39.95
2021-08-16 00:30 | 44424.0208 | 0 | 7.1915 | 39.95
2021-08-16 01:00 | 44424.0417 | 0 | 6.9149 | 39.95
2021-08-16 01:30 | 44424.0625 | 0 | 6.7831 | 39.95
2021-08-16 02:00 | 44424.0833 | 0 | 6.8899 | 39.95
2021-08-16 02:30 | 44424.1042 | 0 | 6.8392 | 39.95
2021-08-16 03:00 | 44424.125 | 0 | 6.7966 | 39.95
2021-08-16 03:30 | 44424.1458 | 0 | 6.9449 | 39.95
2021-08-16 04:00 | 44424.1667 | 0 | 7.3265 | 39.95
2021-08-16 04:30 | 44424.1875 | 0 | 7.7221 | 39.95
2021-08-16 05:00 | 44424.2083 | 0 | 8.4228 | 39.95
2021-08-16 05:30 | 44424.2292 | 0 | 9.2516 | 39.95
2021-08-16 06:00 | 44424.25 | 0 | 10.0081 | 39.95
2021-08-16 06:30 | 44424.2708 | 0 | 11.1803 | 39.95
2021-08-16 07:00 | 44424.2917 | 0 | 11.7023 | 39.95
2021-08-16 07:30 | 44424.3125 | 0 | 11.5558 | 39.95
2021-08-16 08:00 | 44424.3333 | 0 | 11.0458 | 39.95
2021-08-16 08:30 | 44424.3542 | 0 | 10.3749 | 39.95
2021-08-16 09:00 | 44424.375 | 0 | 9.7826 | 39.95
2021-08-16 09:30 | 44424.3958 | 0 | 9.4159 | 39.95
2021-08-16 10:00 | 44424.4167 | 0 | 8.9888 | 39.95
2021-08-16 10:30 | 44424.4375 | 0 | 8.8884 | 39.95
2021-08-16 11:00 | 44424.4583 | 0 | 8.7162 | 39.95
2021-08-16 11:30 | 44424.4792 | 0 | 8.5599 | 39.95
2021-08-16 12:00 | 44424.5 | 0 | 8.3977 | 39.95
2021-08-16 12:30 | 44424.5208 | 0 | 8.6206 | 39.95
2021-08-16 13:00 | 44424.5417 | 0 | 9.7133 | 39.95
2021-08-16 13:30 | 44424.5625 | 0 | 11.1891 | 39.95
2021-08-16 14:00 | 44424.5833 | 0 | 9.6511 | 39.95
2021-08-16 14:30 | 44424.6042 | 0 | 10.7803 | 39.95
2021-08-16 15:00 | 44424.625 | 0 | 11.2886 | 39.95
2021-08-16 15:30 | 44424.6458 | 0 | 11.5749 | 39.95
2021-08-16 16:00 | 44424.6667 | 0 | 11.9138 | 39.95
2021-08-16 16:30 | 44424.6875 | 0 | 12.3807 | 39.95
2021-08-16 17:00 | 44424.7083 | 0 | 12.9653 | 39.95
2021-08-16 17:30 | 44424.7292 | 0 | 13.5559 | 39.95
2021-08-16 18:00 | 44424.75 | 0 | 13.9231 | 39.95
2021-08-16 18:30 | 44424.7708 | 0 | 13.8303 | 39.95
2021-08-16 19:00 | 44424.7917 | 0 | 13.2346 | 39.95
2021-08-16 19:30 | 44424.8125 | 0 | 12.9773 | 39.95
2021-08-16 20:00 | 44424.8333 | 0 | 12.5125 | 39.95
2021-08-16 20:30 | 44424.8542 | 0 | 12.161 | 39.95
2021-08-16 21:00 | 44424.875 | 0 | 11.6861 | 39.95
2021-08-16 21:30 | 44424.8958 | 0 | 11.1461 | 39.95
2021-08-16 22:00 | 44424.9167 | 0 | 10.5998 | 39.95
2021-08-16 22:30 | 44424.9375 | 0 | 9.8642 | 39.95
2021-08-16 23:00 | 44424.9583 | 0 | 9.1318 | 39.95
2021-08-16 23:30 | 44424.9792 | 0 | 8.7419 | 39.95
2021-08-17 | 44425 | 0 | 8.3254 | 39.95
2021-08-17 00:30 | 44425.0208 | 0 | 7.9673 | 39.95
2021-08-17 01:00 | 44425.0417 | 0 | 7.9118 | 39.95
2021-08-17 01:30 | 44425.0625 | 0 | 7.6973 | 39.95
2021-08-17 02:00 | 44425.0833 | 0 | 7.6788 | 39.95
2021-08-17 02:30 | 44425.1042 | 0 | 7.5261 | 39.95
2021-08-17 03:00 | 44425.125 | 0 | 7.5424 | 39.95
2021-08-17 03:30 | 44425.1458 | 0 | 7.7233 | 39.95
2021-08-17 04:00 | 44425.1667 | 0 | 7.8605 | 39.95
2021-08-17 04:30 | 44425.1875 | 0 | 8.2342 | 39.95
2021-08-17 05:00 | 44425.2083 | 0 | 9.0579 | 39.95
2021-08-17 05:30 | 44425.2292 | 0 | 9.5621 | 39.95
2021-08-17 06:00 | 44425.25 | 0 | 10.6678 | 39.95
2021-08-17 06:30 | 44425.2708 | 0 | 11.6528 | 39.95
2021-08-17 07:00 | 44425.2917 | 0 | 12.0635 | 39.95
2021-08-17 07:30 | 44425.3125 | 0 | 11.7645 | 39.95
2021-08-17 08:00 | 44425.3333 | 0 | 11.1462 | 39.95
2021-08-17 08:30 | 44425.3542 | 0 | 10.1147 | 39.95
2021-08-17 09:00 | 44425.375 | 0 | 9.38 | 39.95
2021-08-17 09:30 | 44425.3958 | 0 | 8.8407 | 39.95
2021-08-17 10:00 | 44425.4167 | 0 | 8.4512 | 39.95
2021-08-17 10:30 | 44425.4375 | 0 | 8.2601 | 39.95
2021-08-17 11:00 | 44425.4583 | 0 | 7.9619 | 39.95
2021-08-17 11:30 | 44425.4792 | 0 | 7.8327 | 39.95
2021-08-17 12:00 | 44425.5 | 0 | 7.951 | 39.95
2021-08-17 12:30 | 44425.5208 | 0 | 8.0174 | 39.95
2021-08-17 13:00 | 44425.5417 | 0 | 8.1206 | 39.95
2021-08-17 13:30 | 44425.5625 | 0 | 8.4723 | 39.95
2021-08-17 14:00 | 44425.5833 | 0 | 9.0134 | 39.95
2021-08-17 14:30 | 44425.6042 | 0 | 9.5961 | 39.95
2021-08-17 15:00 | 44425.625 | 0 | 9.9853 | 39.95
2021-08-17 15:30 | 44425.6458 | 0 | 10.7046 | 39.95
2021-08-17 16:00 | 44425.6667 | 0 | 11.4619 | 39.95
2021-08-17 16:30 | 44425.6875 | 0 | 12.109 | 39.95
2021-08-17 17:00 | 44425.7083 | 0 | 12.6282 | 39.95
2021-08-17 17:30 | 44425.7292 | 0 | 13.4308 | 39.95
2021-08-17 18:00 | 44425.75 | 0 | 13.807 | 39.95
2021-08-17 18:30 | 44425.7708 | 0 | 13.8617 | 39.95
2021-08-17 19:00 | 44425.7917 | 0 | 13.4278 | 39.95
2021-08-17 19:30 | 44425.8125 | 0 | 13.2378 | 39.95
2021-08-17 20:00 | 44425.8333 | 0 | 12.8244 | 39.95
2021-08-17 20:30 | 44425.8542 | 0 | 12.3226 | 39.95
2021-08-17 21:00 | 44425.875 | 0 | 11.7432 | 39.95
2021-08-17 21:30 | 44425.8958 | 0 | 11.3148 | 39.95
2021-08-17 22:00 | 44425.9167 | 0 | 10.7184 | 39.95
2021-08-17 22:30 | 44425.9375 | 0 | 10.0756 | 39.95
2021-08-17 23:00 | 44425.9583 | 0 | 9.4403 | 39.95
2021-08-17 23:30 | 44425.9792 | 0 | 8.8614 | 39.95
2021-08-18 | 44426 | 0 | 8.3909 | 39.95
2021-08-18 00:30 | 44426.0208 | 0 | 8.1236 | 39.95
2021-08-18 01:00 | 44426.0417 | 0 | 7.9287 | 39.95
2021-08-18 01:30 | 44426.0625 | 0 | 7.7121 | 39.95
2021-08-18 02:00 | 44426.0833 | 0 | 7.7474 | 39.95
2021-08-18 02:30 | 44426.1042 | 0 | 7.677 | 39.95
2021-08-18 03:00 | 44426.125 | 0 | 7.7213 | 39.95
2021-08-18 03:30 | 44426.1458 | 0 | 7.8327 | 39.95
2021-08-18 04:00 | 44426.1667 | 0 | 8.0942 | 39.95
2021-08-18 04:30 | 44426.1875 | 0 | 8.4779 | 39.95
2021-08-18 05:00 | 44426.2083 | 0 | 9.1395 | 39.95
2021-08-18 05:30 | 44426.2292 | 0 | 10.029 | 39.95
2021-08-18 06:00 | 44426.25 | 0 | 10.7792 | 39.95
2021-08-18 06:30 | 44426.2708 | 0 | 11.8091 | 39.95
2021-08-18 07:00 | 44426.2917 | 0 | 12.2457 | 39.95
2021-08-18 07:30 | 44426.3125 | 0 | 11.8516 | 39.95
2021-08-18 08:00 | 44426.3333 | 0 | 12.9417 | 39.95
2021-08-18 08:30 | 44426.3542 | 0 | 13.7594 | 39.95
2021-08-18 09:00 | 44426.375 | 0 | 13.7291 | 39.95
2021-08-18 09:30 | 44426.3958 | 0 | 13.2493 | 39.95
2021-08-18 10:00 | 44426.4167 | 0 | 12.6185 | 39.95
2021-08-18 10:30 | 44426.4375 | 0 | 12.6294 | 39.95
2021-08-18 11:00 | 44426.4583 | 0 | 11.8399 | 39.95
2021-08-18 11:30 | 44426.4792 | 0 | 11.298 | 39.95
2021-08-18 12:00 | 44426.5 | 0 | 11.4784 | 39.95
2021-08-18 12:30 | 44426.5208 | 0 | 12.9401 | 39.95
2021-08-18 13:00 | 44426.5417 | 0 | 12.2751 | 39.95
2021-08-18 13:30 | 44426.5625 | 0 | 12.1495 | 39.95
2021-08-18 14:00 | 44426.5833 | 0 | 12.4129 | 39.95
2021-08-18 14:30 | 44426.6042 | 0 | 12.4017 | 39.95
2021-08-18 15:00 | 44426.625 | 0 | 12.5712 | 39.95
2021-08-18 15:30 | 44426.6458 | 0 | 13.1376 | 39.95
2021-08-18 16:00 | 44426.6667 | 0 | 12.9682 | 39.95
2021-08-18 16:30 | 44426.6875 | 0 | 13.022 | 39.95
2021-08-18 17:00 | 44426.7083 | 0 | 13.7437 | 39.95
2021-08-18 17:30 | 44426.7292 | 0 | 14.4471 | 39.95
2021-08-18 18:00 | 44426.75 | 0 | 15.015 | 39.95
2021-08-18 18:30 | 44426.7708 | 0 | 15.2572 | 39.95
2021-08-18 19:00 | 44426.7917 | 0 | 14.7975 | 39.95
2021-08-18 19:30 | 44426.8125 | 0 | 14.5748 | 39.95
2021-08-18 20:00 | 44426.8333 | 0 | 13.9151 | 39.95
2021-08-18 20:30 | 44426.8542 | 0 | 13.342 | 39.95
2021-08-18 21:00 | 44426.875 | 0 | 12.7393 | 39.95
2021-08-18 21:30 | 44426.8958 | 0 | 12.1963 | 39.95
2021-08-18 22:00 | 44426.9167 | 0 | 11.4116 | 39.95
2021-08-18 22:30 | 44426.9375 | 0 | 10.435 | 39.95
2021-08-18 23:00 | 44426.9583 | 0 | 9.7298 | 39.95
2021-08-18 23:30 | 44426.9792 | 0 | 9.1865 | 39.95
2021-08-19 | 44427 | 0 | 8.7107 | 39.95
2021-08-19 00:30 | 44427.0208 | 0 | 8.2956 | 39.95
2021-08-19 01:00 | 44427.0417 | 0 | 8.1351 | 39.95
2021-08-19 01:30 | 44427.0625 | 0 | 7.9673 | 39.95
2021-08-19 02:00 | 44427.0833 | 0 | 7.9782 | 39.95
2021-08-19 02:30 | 44427.1042 | 0 | 7.8949 | 39.95
2021-08-19 03:00 | 44427.125 | 0 | 7.8611 | 39.95
2021-08-19 03:30 | 44427.1458 | 0 | 8.0446 | 39.95
2021-08-19 04:00 | 44427.1667 | 0 | 8.2641 | 39.95
2021-08-19 04:30 | 44427.1875 | 0 | 8.7989 | 39.95
2021-08-19 05:00 | 44427.2083 | 0 | 9.4533 | 39.95
2021-08-19 05:30 | 44427.2292 | 0 | 10.306 | 39.95
2021-08-19 06:00 | 44427.25 | 0 | 11.3762 | 39.95
2021-08-19 06:30 | 44427.2708 | 0 | 12.5703 | 39.95
2021-08-19 07:00 | 44427.2917 | 0 | 13.115 | 39.95
2021-08-19 07:30 | 44427.3125 | 0 | 12.5962 | 39.95
2021-08-19 08:00 | 44427.3333 | 0 | 11.8882 | 39.95
2021-08-19 08:30 | 44427.3542 | 0 | 10.8377 | 39.95
2021-08-19 09:00 | 44427.375 | 0 | 10.0035 | 39.95
2021-08-19 09:30 | 44427.3958 | 0 | 9.4534 | 39.95
2021-08-19 10:00 | 44427.4167 | 0 | 9.3659 | 39.95
2021-08-19 10:30 | 44427.4375 | 0 | 9.9877 | 39.95
2021-08-19 11:00 | 44427.4583 | 0 | 8.9668 | 39.95
2021-08-19 11:30 | 44427.4792 | 0 | 8.1407 | 39.95
2021-08-19 12:00 | 44427.5 | 0 | 8.4605 | 39.95
2021-08-19 12:30 | 44427.5208 | 0 | 9.5701 | 39.95
2021-08-19 13:00 | 44427.5417 | 0 | 11.7314 | 39.95
2021-08-19 13:30 | 44427.5625 | 0 | 9.6898 | 39.95
2021-08-19 14:00 | 44427.5833 | 0 | 10.4657 | 39.95
2021-08-19 14:30 | 44427.6042 | 0 | 9.3226 | 39.95
2021-08-19 15:00 | 44427.625 | 0 | 10.551 | 39.95
2021-08-19 15:30 | 44427.6458 | 0 | 11.4952 | 39.95
2021-08-19 16:00 | 44427.6667 | 0 | 11.9506 | 39.95
2021-08-19 16:30 | 44427.6875 | 0 | 11.9896 | 39.95
2021-08-19 17:00 | 44427.7083 | 0 | 12.7737 | 39.95
2021-08-19 17:30 | 44427.7292 | 0 | 13.6448 | 39.95
2021-08-19 18:00 | 44427.75 | 0 | 14.2259 | 39.95
2021-08-19 18:30 | 44427.7708 | 0 | 14.547 | 39.95
2021-08-19 19:00 | 44427.7917 | 0 | 14.0353 | 39.95
2021-08-19 19:30 | 44427.8125 | 0 | 13.6624 | 39.95
2021-08-19 20:00 | 44427.8333 | 0 | 13.5265 | 39.95
2021-08-19 20:30 | 44427.8542 | 0 | 13.2777 | 39.95
2021-08-19 21:00 | 44427.875 | 0 | 12.6597 | 39.95
2021-08-19 21:30 | 44427.8958 | 0 | 11.9077 | 39.95
2021-08-19 22:00 | 44427.9167 | 0 | 11.2743 | 39.95
2021-08-19 22:30 | 44427.9375 | 0 | 10.5004 | 39.95
2021-08-19 23:00 | 44427.9583 | 0 | 9.8613 | 39.95
2021-08-19 23:30 | 44427.9792 | 0 | 9.3408 | 39.95
2021-08-20 | 44428 | 0 | 8.9526 | 39.95
2021-08-20 00:30 | 44428.0208 | 0 | 8.3916 | 39.95
2021-08-20 01:00 | 44428.0417 | 0 | 8.3156 | 39.95
2021-08-20 01:30 | 44428.0625 | 0 | 8.0458 | 39.95
2021-08-20 02:00 | 44428.0833 | 0 | 7.9384 | 39.95
2021-08-20 02:30 | 44428.1042 | 0 | 7.9504 | 39.95
2021-08-20 03:00 | 44428.125 | 0 | 7.8949 | 39.95
2021-08-20 03:30 | 44428.1458 | 0 | 8.0005 | 39.95
2021-08-20 04:00 | 44428.1667 | 0 | 8.2101 | 39.95
2021-08-20 04:30 | 44428.1875 | 0 | 8.612 | 39.95
2021-08-20 05:00 | 44428.2083 | 0 | 9.4113 | 39.95
2021-08-20 05:30 | 44428.2292 | 0 | 10.2136 | 39.95
2021-08-20 06:00 | 44428.25 | 0 | 11.0151 | 39.95
2021-08-20 06:30 | 44428.2708 | 0 | 12.0482 | 39.95
2021-08-20 07:00 | 44428.2917 | 0 | 12.4768 | 39.95
2021-08-20 07:30 | 44428.3125 | 0 | 12.057 | 39.95
2021-08-20 08:00 | 44428.3333 | 0 | 11.4881 | 39.95
2021-08-20 08:30 | 44428.3542 | 0 | 10.5624 | 39.95
2021-08-20 09:00 | 44428.375 | 0 | 9.9296 | 39.95
2021-08-20 09:30 | 44428.3958 | 0 | 9.4154 | 39.95
2021-08-20 10:00 | 44428.4167 | 0 | 8.9228 | 39.95
2021-08-20 10:30 | 44428.4375 | 0 | 8.648 | 39.95
2021-08-20 11:00 | 44428.4583 | 0 | 8.5649 | 39.95
2021-08-20 11:30 | 44428.4792 | 0 | 8.8496 | 39.95
2021-08-20 12:00 | 44428.5 | 0 | 8.5633 | 39.95
2021-08-20 12:30 | 44428.5208 | 0 | 8.6482 | 39.95
2021-08-20 13:00 | 44428.5417 | 0 | 9.9306 | 39.95
2021-08-20 13:30 | 44428.5625 | 0 | 9.2396 | 39.95
2021-08-20 14:00 | 44428.5833 | 0 | 9.211 | 39.95
2021-08-20 14:30 | 44428.6042 | 0 | 9.6482 | 39.95
2021-08-20 15:00 | 44428.625 | 0 | 10.3162 | 39.95
2021-08-20 15:30 | 44428.6458 | 0 | 10.8015 | 39.95
2021-08-20 16:00 | 44428.6667 | 0 | 11.4691 | 39.95
2021-08-20 16:30 | 44428.6875 | 0 | 12.3346 | 39.95
2021-08-20 17:00 | 44428.7083 | 0 | 12.4522 | 39.95
2021-08-20 17:30 | 44428.7292 | 0 | 13.0373 | 39.95
2021-08-20 18:00 | 44428.75 | 0 | 13.1713 | 39.95
2021-08-20 18:30 | 44428.7708 | 0 | 13.2064 | 39.95
2021-08-20 19:00 | 44428.7917 | 0 | 12.9729 | 39.95
2021-08-20 19:30 | 44428.8125 | 0 | 12.9043 | 39.95
2021-08-20 20:00 | 44428.8333 | 0 | 12.691 | 39.95
2021-08-20 20:30 | 44428.8542 | 0 | 12.196 | 39.95
2021-08-20 21:00 | 44428.875 | 0 | 11.7371 | 39.95
2021-08-20 21:30 | 44428.8958 | 0 | 11.3324 | 39.95
2021-08-20 22:00 | 44428.9167 | 0 | 10.8145 | 39.95
2021-08-20 22:30 | 44428.9375 | 0 | 10.2686 | 39.95
2021-08-20 23:00 | 44428.9583 | 0 | 9.7493 | 39.95
2021-08-20 23:30 | 44428.9792 | 0 | 9.228 | 39.95
2021-08-21 | 44429 | 0 | 8.7021 | 39.95
2021-08-21 00:30 | 44429.0208 | 0 | 8.2729 | 39.95
2021-08-21 01:00 | 44429.0417 | 0 | 8.0403 | 39.95
2021-08-21 01:30 | 44429.0625 | 0 | 7.7931 | 39.95
2021-08-21 02:00 | 44429.0833 | 0 | 7.7762 | 39.95
2021-08-21 02:30 | 44429.1042 | 0 | 7.5207 | 39.95
2021-08-21 03:00 | 44429.125 | 0 | 7.5038 | 39.95
2021-08-21 03:30 | 44429.1458 | 0 | 7.5708 | 39.95
2021-08-21 04:00 | 44429.1667 | 0 | 7.5539 | 39.95
2021-08-21 04:30 | 44429.1875 | 0 | 7.7281 | 39.95
2021-08-21 05:00 | 44429.2083 | 0 | 8.0005 | 39.95
2021-08-21 05:30 | 44429.2292 | 0 | 8.1812 | 39.95
2021-08-21 06:00 | 44429.25 | 0 | 8.5461 | 39.95
2021-08-21 06:30 | 44429.2708 | 0 | 8.9391 | 39.95
2021-08-21 07:00 | 44429.2917 | 0 | 8.8908 | 39.95
2021-08-21 07:30 | 44429.3125 | 0 | 8.5935 | 39.95
2021-08-21 08:00 | 44429.3333 | 0 | 8.528 | 39.95
2021-08-21 08:30 | 44429.3542 | 0 | 8.0403 | 39.95
2021-08-21 09:00 | 44429.375 | 0 | 7.765 | 39.95
2021-08-21 09:30 | 44429.3958 | 0 | 7.2848 | 39.95
2021-08-21 10:00 | 44429.4167 | 0 | 6.8036 | 39.95
2021-08-21 10:30 | 44429.4375 | 0 | 6.4378 | 39.95
2021-08-21 11:00 | 44429.4583 | 0 | 6.1628 | 39.95
2021-08-21 11:30 | 44429.4792 | 0 | 5.9683 | 39.95
2021-08-21 12:00 | 44429.5 | 0 | 6.0189 | 39.95
2021-08-21 12:30 | 44429.5208 | 0 | 5.9121 | 39.95
2021-08-21 13:00 | 44429.5417 | 0 | 6.156 | 39.95
2021-08-21 13:30 | 44429.5625 | 0 | 6.3419 | 39.95
2021-08-21 14:00 | 44429.5833 | 0 | 6.8246 | 39.95
2021-08-21 14:30 | 44429.6042 | 0 | 7.2937 | 39.95
2021-08-21 15:00 | 44429.625 | 0 | 8.0037 | 39.95
2021-08-21 15:30 | 44429.6458 | 0 | 8.6342 | 39.95
2021-08-21 16:00 | 44429.6667 | 0 | 9.1852 | 39.95
2021-08-21 16:30 | 44429.6875 | 0 | 10.0633 | 39.95
2021-08-21 17:00 | 44429.7083 | 0 | 10.3901 | 39.95
2021-08-21 17:30 | 44429.7292 | 0 | 10.8298 | 39.95
2021-08-21 18:00 | 44429.75 | 0 | 11.1941 | 39.95
2021-08-21 18:30 | 44429.7708 | 0 | 11.3937 | 39.95
2021-08-21 19:00 | 44429.7917 | 0 | 11.0553 | 39.95
2021-08-21 19:30 | 44429.8125 | 0 | 10.9236 | 39.95
2021-08-21 20:00 | 44429.8333 | 0 | 10.6567 | 39.95
2021-08-21 20:30 | 44429.8542 | 0 | 10.342 | 39.95
2021-08-21 21:00 | 44429.875 | 0 | 10.023 | 39.95
2021-08-21 21:30 | 44429.8958 | 0 | 9.7594 | 39.95
2021-08-21 22:00 | 44429.9167 | 0 | 9.4961 | 39.95
2021-08-21 22:30 | 44429.9375 | 0 | 8.9952 | 39.95
2021-08-21 23:00 | 44429.9583 | 0 | 8.4997 | 39.95
2021-08-21 23:30 | 44429.9792 | 0 | 8.0963 | 39.95
2021-08-22 | 44430 | 0 | 7.7032 | 39.95
2021-08-22 00:30 | 44430.0208 | 0 | 7.5436 | 39.95
2021-08-22 01:00 | 44430.0417 | 0 | 7.1927 | 39.95
2021-08-22 01:30 | 44430.0625 | 0 | 7.1583 | 39.95
2021-08-22 02:00 | 44430.0833 | 0 | 7.0293 | 39.95
2021-08-22 02:30 | 44430.1042 | 0 | 6.9509 | 39.95
2021-08-22 03:00 | 44430.125 | 0 | 6.9956 | 39.95
2021-08-22 03:30 | 44430.1458 | 0 | 6.94 | 39.95
2021-08-22 04:00 | 44430.1667 | 0 | 6.9346 | 39.95
2021-08-22 04:30 | 44430.1875 | 0 | 6.9503 | 39.95
2021-08-22 05:00 | 44430.2083 | 0 | 7.1674 | 39.95
2021-08-22 05:30 | 44430.2292 | 0 | 7.1475 | 39.95
2021-08-22 06:00 | 44430.25 | 0 | 7.4362 | 39.95
2021-08-22 06:30 | 44430.2708 | 0 | 7.6324 | 39.95
2021-08-22 07:00 | 44430.2917 | 0 | 7.5877 | 39.95
2021-08-22 07:30 | 44430.3125 | 0 | 7.4989 | 39.95
2021-08-22 08:00 | 44430.3333 | 0 | 7.2804 | 39.95
2021-08-22 08:30 | 44430.3542 | 0 | 7.0105 | 39.95
2021-08-22 09:00 | 44430.375 | 0 | 6.7807 | 39.95
2021-08-22 09:30 | 44430.3958 | 0 | 6.3292 | 39.95
2021-08-22 10:00 | 44430.4167 | 0 | 6.1028 | 39.95
2021-08-22 10:30 | 44430.4375 | 0 | 5.8626 | 39.95
2021-08-22 11:00 | 44430.4583 | 0 | 5.5134 | 39.95
2021-08-22 11:30 | 44430.4792 | 0 | 5.3598 | 39.95
2021-08-22 12:00 | 44430.5 | 0 | 5.3152 | 39.95
2021-08-22 12:30 | 44430.5208 | 0 | 5.3484 | 39.95
2021-08-22 13:00 | 44430.5417 | 0 | 5.6085 | 39.95
2021-08-22 13:30 | 44430.5625 | 0 | 5.8633 | 39.95
2021-08-22 14:00 | 44430.5833 | 0 | 6.4089 | 39.95
2021-08-22 14:30 | 44430.6042 | 0 | 6.8349 | 39.95
2021-08-22 15:00 | 44430.625 | 0 | 7.5113 | 39.95
2021-08-22 15:30 | 44430.6458 | 0 | 8.3347 | 39.95
2021-08-22 16:00 | 44430.6667 | 0 | 9.1529 | 39.95
2021-08-22 16:30 | 44430.6875 | 0 | 9.9713 | 39.95
2021-08-22 17:00 | 44430.7083 | 0 | 10.7058 | 39.95
2021-08-22 17:30 | 44430.7292 | 0 | 11.3016 | 39.95
2021-08-22 18:00 | 44430.75 | 0 | 11.9434 | 39.95
2021-08-22 18:30 | 44430.7708 | 0 | 12.0898 | 39.95
2021-08-22 19:00 | 44430.7917 | 0 | 11.7256 | 39.95
2021-08-22 19:30 | 44430.8125 | 0 | 11.9519 | 39.95
2021-08-22 20:00 | 44430.8333 | 0 | 11.8507 | 39.95
2021-08-22 20:30 | 44430.8542 | 0 | 11.3216 | 39.95
2021-08-22 21:00 | 44430.875 | 0 | 10.8715 | 39.95
2021-08-22 21:30 | 44430.8958 | 0 | 10.5325 | 39.95
2021-08-22 22:00 | 44430.9167 | 0 | 9.8877 | 39.95
2021-08-22 22:30 | 44430.9375 | 0 | 9.214 | 39.95
2021-08-22 23:00 | 44430.9583 | 0 | 8.6463 | 39.95
2021-08-22 23:30 | 44430.9792 | 0 | 8.3345 | 39.95
2021-08-23 | 44431 | 0 | 7.9683 | 39.95
2021-08-23 00:30 | 44431.0208 | 0 | 7.7569 | 39.95
2021-08-23 01:00 | 44431.0417 | 0 | 7.6327 | 39.95
2021-08-23 01:30 | 44431.0625 | 0 | 7.543 | 39.95
2021-08-23 02:00 | 44431.0833 | 0 | 7.543 | 39.95
2021-08-23 02:30 | 44431.1042 | 0 | 7.4084 | 39.95
2021-08-23 03:00 | 44431.125 | 0 | 7.5877 | 39.95
2021-08-23 03:30 | 44431.1458 | 0 | 7.7321 | 39.95
2021-08-23 04:00 | 44431.1667 | 0 | 7.9553 | 39.95
2021-08-23 04:30 | 44431.1875 | 0 | 8.501 | 39.95
2021-08-23 05:00 | 44431.2083 | 0 | 8.8065 | 39.95
2021-08-23 05:30 | 44431.2292 | 0 | 9.4359 | 39.95
2021-08-23 06:00 | 44431.25 | 0 | 10.4139 | 39.95
2021-08-23 06:30 | 44431.2708 | 0 | 11.369 | 39.95
2021-08-23 07:00 | 44431.2917 | 0 | 11.8315 | 39.95
2021-08-23 07:30 | 44431.3125 | 0 | 11.6048 | 39.95
2021-08-23 08:00 | 44431.3333 | 0 | 11.0821 | 39.95
2021-08-23 08:30 | 44431.3542 | 0 | 10.4844 | 39.95
2021-08-23 09:00 | 44431.375 | 0 | 9.2888 | 39.95
2021-08-23 09:30 | 44431.3958 | 0 | 9.4039 | 39.95
2021-08-23 10:00 | 44431.4167 | 0 | 9.7402 | 39.95
2021-08-23 10:30 | 44431.4375 | 0 | 9.5543 | 39.95
2021-08-23 11:00 | 44431.4583 | 0 | 8.8846 | 39.95
2021-08-23 11:30 | 44431.4792 | 0 | 8.5142 | 39.95
2021-08-23 12:00 | 44431.5 | 0 | 8.3361 | 39.95
2021-08-23 12:30 | 44431.5208 | 0 | 8.3007 | 39.95
2021-08-23 13:00 | 44431.5417 | 0 | 8.1822 | 39.95
2021-08-23 13:30 | 44431.5625 | 0 | 8.5395 | 39.95
2021-08-23 14:00 | 44431.5833 | 0 | 9.1007 | 39.95
2021-08-23 14:30 | 44431.6042 | 0 | 9.4515 | 39.95
2021-08-23 15:00 | 44431.625 | 0 | 9.8964 | 39.95
2021-08-23 15:30 | 44431.6458 | 0 | 10.7731 | 39.95
2021-08-23 16:00 | 44431.6667 | 0 | 11.4202 | 39.95
2021-08-23 16:30 | 44431.6875 | 0 | 12.1275 | 39.95
2021-08-23 17:00 | 44431.7083 | 0 | 12.5303 | 39.95
2021-08-23 17:30 | 44431.7292 | 0 | 13.3345 | 39.95
2021-08-23 18:00 | 44431.75 | 0 | 14.047 | 39.95
2021-08-23 18:30 | 44431.7708 | 0 | 14.1758 | 39.95
2021-08-23 19:00 | 44431.7917 | 0 | 13.8385 | 39.95
2021-08-23 19:30 | 44431.8125 | 0 | 13.5137 | 39.95
2021-08-23 20:00 | 44431.8333 | 0 | 13.0528 | 39.95
2021-08-23 20:30 | 44431.8542 | 0 | 12.6825 | 39.95
2021-08-23 21:00 | 44431.875 | 0 | 12.0033 | 39.95
2021-08-23 21:30 | 44431.8958 | 0 | 11.4112 | 39.95
2021-08-23 22:00 | 44431.9167 | 0 | 10.9054 | 39.95
2021-08-23 22:30 | 44431.9375 | 0 | 10.0383 | 39.95
2021-08-23 23:00 | 44431.9583 | 0 | 9.3563 | 39.95
2021-08-23 23:30 | 44431.9792 | 0 | 8.9783 | 39.95
2021-08-24 | 44432 | 0 | 8.4672 | 39.95
2021-08-24 00:30 | 44432.0208 | 0 | 8.2357 | 39.95
2021-08-24 01:00 | 44432.0417 | 0 | 7.9124 | 39.95
2021-08-24 01:30 | 44432.0625 | 0 | 7.8219 | 39.95
2021-08-24 02:00 | 44432.0833 | 0 | 7.7907 | 39.95
2021-08-24 02:30 | 44432.1042 | 0 | 7.7309 | 39.95
2021-08-24 03:00 | 44432.125 | 0 | 7.7714 | 39.95
2021-08-24 03:30 | 44432.1458 | 0 | 7.9613 | 39.95
2021-08-24 04:00 | 44432.1667 | 0 | 8.1084 | 39.95
2021-08-24 04:30 | 44432.1875 | 0 | 8.6898 | 39.95
2021-08-24 05:00 | 44432.2083 | 0 | 9.3819 | 39.95
2021-08-24 05:30 | 44432.2292 | 0 | 10.0102 | 39.95
2021-08-24 06:00 | 44432.25 | 0 | 10.8796 | 39.95
2021-08-24 06:30 | 44432.2708 | 0 | 11.7585 | 39.95
2021-08-24 07:00 | 44432.2917 | 0 | 11.9971 | 39.95
2021-08-24 07:30 | 44432.3125 | 0 | 11.9201 | 39.95
2021-08-24 08:00 | 44432.3333 | 0 | 12.6438 | 39.95
2021-08-24 08:30 | 44432.3542 | 0 | 13.5352 | 39.95
2021-08-24 09:00 | 44432.375 | 0 | 13.2924 | 39.95
2021-08-24 09:30 | 44432.3958 | 0 | 11.1935 | 39.95
2021-08-24 10:00 | 44432.4167 | 0 | 11.2333 | 39.95
2021-08-24 10:30 | 44432.4375 | 0 | 10.8269 | 39.95
2021-08-24 11:00 | 44432.4583 | 0 | 10.3847 | 39.95
2021-08-24 11:30 | 44432.4792 | 0 | 10.3847 | 39.95
2021-08-24 12:00 | 44432.5 | 0 | 10.3847 | 39.95
2021-08-24 12:30 | 44432.5208 | 0 | 8.878 | 39.95
2021-08-24 13:00 | 44432.5417 | 0 | 7.687 | 39.95
2021-08-24 13:30 | 44432.5625 | 0 | 7.8997 | 39.95
2021-08-24 14:00 | 44432.5833 | 0 | 8.3548 | 39.95
2021-08-24 14:30 | 44432.6042 | 0 | 8.918 | 39.95
2021-08-24 15:00 | 44432.625 | 0 | 9.7563 | 39.95
2021-08-24 15:30 | 44432.6458 | 0 | 10.5398 | 39.95
2021-08-24 16:00 | 44432.6667 | 0 | 11.2912 | 39.95
2021-08-24 16:30 | 44432.6875 | 0 | 12.157 | 39.95
2021-08-24 17:00 | 44432.7083 | 0 | 12.8641 | 39.95
2021-08-24 17:30 | 44432.7292 | 0 | 13.9507 | 39.95
2021-08-24 18:00 | 44432.75 | 0 | 14.6164 | 39.95
2021-08-24 18:30 | 44432.7708 | 0 | 15.0828 | 39.95
2021-08-24 19:00 | 44432.7917 | 0 | 14.9411 | 39.95
2021-08-24 19:30 | 44432.8125 | 0 | 14.8492 | 39.95
2021-08-24 20:00 | 44432.8333 | 0 | 14.5953 | 39.95
2021-08-24 20:30 | 44432.8542 | 0 | 14.067 | 39.95
2021-08-24 21:00 | 44432.875 | 0 | 13.0052 | 39.95
2021-08-24 21:30 | 44432.8958 | 0 | 12.4856 | 39.95
2021-08-24 22:00 | 44432.9167 | 0 | 11.7822 | 39.95
2021-08-24 22:30 | 44432.9375 | 0 | 10.6539 | 39.95
2021-08-24 23:00 | 44432.9583 | 0 | 9.9634 | 39.95
2021-08-24 23:30 | 44432.9792 | 0 | 9.5292 | 39.95
2021-08-25 | 44433 | 0 | 9.1899 | 39.95
2021-08-25 00:30 | 44433.0208 | 0 | 8.616 | 39.95
2021-08-25 01:00 | 44433.0417 | 0 | 8.2914 | 39.95
2021-08-25 01:30 | 44433.0625 | 0 | 8.0735 | 39.95
2021-08-25 02:00 | 44433.0833 | 0 | 8.0675 | 39.95
2021-08-25 02:30 | 44433.1042 | 0 | 7.9674 | 39.95
2021-08-25 03:00 | 44433.125 | 0 | 8.0229 | 39.95
2021-08-25 03:30 | 44433.1458 | 0 | 8.1862 | 39.95
2021-08-25 04:00 | 44433.1667 | 0 | 8.4411 | 39.95
2021-08-25 04:30 | 44433.1875 | 0 | 8.8551 | 39.95
2021-08-25 05:00 | 44433.2083 | 0 | 9.8174 | 39.95
2021-08-25 05:30 | 44433.2292 | 0 | 10.7692 | 39.95
2021-08-25 06:00 | 44433.25 | 0 | 12.0639 | 39.95
2021-08-25 06:30 | 44433.2708 | 0 | 13.3531 | 39.95
2021-08-25 07:00 | 44433.2917 | 0 | 13.7877 | 39.95
2021-08-25 07:30 | 44433.3125 | 0 | 12.8032 | 39.95
2021-08-25 08:00 | 44433.3333 | 0 | 12.0201 | 39.95
2021-08-25 08:30 | 44433.3542 | 0 | 11.0884 | 39.95
2021-08-25 09:00 | 44433.375 | 0 | 9.9526 | 39.95
2021-08-25 09:30 | 44433.3958 | 0 | 9.2158 | 39.95
2021-08-25 10:00 | 44433.4167 | 0 | 8.8204 | 39.95
2021-08-25 10:30 | 44433.4375 | 0 | 8.2301 | 39.95
2021-08-25 11:00 | 44433.4583 | 0 | 7.9341 | 39.95
2021-08-25 11:30 | 44433.4792 | 0 | 7.8243 | 39.95
2021-08-25 12:00 | 44433.5 | 0 | 7.675 | 39.95
2021-08-25 12:30 | 44433.5208 | 0 | 7.6692 | 39.95
2021-08-25 13:00 | 44433.5417 | 0 | 7.7231 | 39.95
2021-08-25 13:30 | 44433.5625 | 0 | 8.1186 | 39.95
2021-08-25 14:00 | 44433.5833 | 0 | 8.5637 | 39.95
2021-08-25 14:30 | 44433.6042 | 0 | 8.9142 | 39.95
2021-08-25 15:00 | 44433.625 | 0 | 9.6169 | 39.95
2021-08-25 15:30 | 44433.6458 | 0 | 10.4131 | 39.95
2021-08-25 16:00 | 44433.6667 | 0 | 11.1096 | 39.95
2021-08-25 16:30 | 44433.6875 | 0 | 11.948 | 39.95
2021-08-25 17:00 | 44433.7083 | 0 | 12.6038 | 39.95
2021-08-25 17:30 | 44433.7292 | 0 | 13.6074 | 39.95
2021-08-25 18:00 | 44433.75 | 0 | 14.4087 | 39.95
2021-08-25 18:30 | 44433.7708 | 0 | 14.8831 | 39.95
2021-08-25 19:00 | 44433.7917 | 0 | 15.0262 | 39.95
2021-08-25 19:30 | 44433.8125 | 0 | 14.8234 | 39.95
2021-08-25 20:00 | 44433.8333 | 0 | 14.4983 | 39.95
2021-08-25 20:30 | 44433.8542 | 0 | 13.9002 | 39.95
2021-08-25 21:00 | 44433.875 | 0 | 13.1308 | 39.95
2021-08-25 21:30 | 44433.8958 | 0 | 12.6827 | 39.95
2021-08-25 22:00 | 44433.9167 | 0 | 12.0622 | 39.95
2021-08-25 22:30 | 44433.9375 | 0 | 11.0952 | 39.95
2021-08-25 23:00 | 44433.9583 | 0 | 10.2774 | 39.95
2021-08-25 23:30 | 44433.9792 | 0 | 9.6854 | 39.95
2021-08-26 | 44434 | 0 | 9.0879 | 39.95
2021-08-26 00:30 | 44434.0208 | 0 | 8.5748 | 39.95
2021-08-26 01:00 | 44434.0417 | 0 | 8.2874 | 39.95
2021-08-26 01:30 | 44434.0625 | 0 | 8.2222 | 39.95
2021-08-26 02:00 | 44434.0833 | 0 | 8.0681 | 39.95
2021-08-26 02:30 | 44434.1042 | 0 | 8.006 | 39.95
2021-08-26 03:00 | 44434.125 | 0 | 8.1236 | 39.95
2021-08-26 03:30 | 44434.1458 | 0 | 8.1436 | 39.95
2021-08-26 04:00 | 44434.1667 | 0 | 8.4689 | 39.95
2021-08-26 04:30 | 44434.1875 | 0 | 8.9381 | 39.95
2021-08-26 05:00 | 44434.2083 | 0 | 9.7983 | 39.95
2021-08-26 05:30 | 44434.2292 | 0 | 10.6965 | 39.95
2021-08-26 06:00 | 44434.25 | 0 | 12.0962 | 39.95
2021-08-26 06:30 | 44434.2708 | 0 | 13.4487 | 39.95
2021-08-26 07:00 | 44434.2917 | 0 | 14.0168 | 39.95
2021-08-26 07:30 | 44434.3125 | 0 | 13.2745 | 39.95
2021-08-26 08:00 | 44434.3333 | 0 | 13.3331 | 39.95
2021-08-26 08:30 | 44434.3542 | 0 | 13.2209 | 39.95
2021-08-26 09:00 | 44434.375 | 0 | 13.2209 | 39.95
2021-08-26 09:30 | 44434.3958 | 0 | 13.2209 | 39.95
2021-08-26 10:00 | 44434.4167 | 0 | 13.2209 | 39.95
2021-08-26 10:30 | 44434.4375 | 0 | 8.9095 | 39.95
2021-08-26 11:00 | 44434.4583 | 0 | 8.3122 | 39.95
2021-08-26 11:30 | 44434.4792 | 0 | 7.9691 | 39.95
2021-08-26 12:00 | 44434.5 | 0 | 7.9842 | 39.95
2021-08-26 12:30 | 44434.5208 | 0 | 7.74 | 39.95
2021-08-26 13:00 | 44434.5417 | 0 | 7.8009 | 39.95
2021-08-26 13:30 | 44434.5625 | 0 | 8.1585 | 39.95
2021-08-26 14:00 | 44434.5833 | 0 | 8.5746 | 39.95
2021-08-26 14:30 | 44434.6042 | 0 | 9.0276 | 39.95
2021-08-26 15:00 | 44434.625 | 0 | 9.5535 | 39.95
2021-08-26 15:30 | 44434.6458 | 0 | 10.3877 | 39.95
2021-08-26 16:00 | 44434.6667 | 0 | 11.0995 | 39.95
2021-08-26 16:30 | 44434.6875 | 0 | 11.7991 | 39.95
2021-08-26 17:00 | 44434.7083 | 0 | 12.5781 | 39.95
2021-08-26 17:30 | 44434.7292 | 0 | 13.707 | 39.95
2021-08-26 18:00 | 44434.75 | 0 | 14.4766 | 39.95
2021-08-26 18:30 | 44434.7708 | 0 | 14.8258 | 39.95
2021-08-26 19:00 | 44434.7917 | 0 | 14.5551 | 39.95
2021-08-26 19:30 | 44434.8125 | 0 | 14.5349 | 39.95
2021-08-26 20:00 | 44434.8333 | 0 | 14.2736 | 39.95
2021-08-26 20:30 | 44434.8542 | 0 | 13.7767 | 39.95
2021-08-26 21:00 | 44434.875 | 0 | 13.088 | 39.95
2021-08-26 21:30 | 44434.8958 | 0 | 12.5854 | 39.95
2021-08-26 22:00 | 44434.9167 | 0 | 11.893 | 39.95
2021-08-26 22:30 | 44434.9375 | 0 | 10.9527 | 39.95
2021-08-26 23:00 | 44434.9583 | 0 | 10.2427 | 39.95
2021-08-26 23:30 | 44434.9792 | 0 | 9.5919 | 39.95
2021-08-27 | 44435 | 0 | 9.0735 | 39.95
2021-08-27 00:30 | 44435.0208 | 0 | 8.6847 | 39.95
2021-08-27 01:00 | 44435.0417 | 0 | 8.4816 | 39.95
2021-08-27 01:30 | 44435.0625 | 0 | 8.2482 | 39.95
2021-08-27 02:00 | 44435.0833 | 0 | 8.1581 | 39.95
2021-08-27 02:30 | 44435.1042 | 0 | 8.1013 | 39.95
2021-08-27 03:00 | 44435.125 | 0 | 8.006 | 39.95
2021-08-27 03:30 | 44435.1458 | 0 | 8.2572 | 39.95
2021-08-27 04:00 | 44435.1667 | 0 | 8.575 | 39.95
2021-08-27 04:30 | 44435.1875 | 0 | 8.9802 | 39.95
2021-08-27 05:00 | 44435.2083 | 0 | 9.8811 | 39.95
2021-08-27 05:30 | 44435.2292 | 0 | 10.8046 | 39.95
2021-08-27 06:00 | 44435.25 | 0 | 12.1553 | 39.95
2021-08-27 06:30 | 44435.2708 | 0 | 13.4618 | 39.95
2021-08-27 07:00 | 44435.2917 | 0 | 13.8358 | 39.95
2021-08-27 07:30 | 44435.3125 | 0 | 13.0567 | 39.95
2021-08-27 08:00 | 44435.3333 | 0 | 12.7356 | 39.95
2021-08-27 08:30 | 44435.3542 | 0 | 20.577 | 39.95
2021-08-27 09:00 | 44435.375 | 0 | 18.8385 | 39.95
2021-08-27 09:30 | 44435.3958 | 0 | 17.7963 | 39.95
2021-08-27 10:00 | 44435.4167 | 0 | 16.5962 | 39.95
2021-08-27 10:30 | 44435.4375 | 0 | 15.8199 | 39.95
2021-08-27 11:00 | 44435.4583 | 0 | 15.1331 | 39.95
2021-08-27 11:30 | 44435.4792 | 0 | 14.6034 | 39.95
2021-08-27 12:00 | 44435.5 | 0 | 12.9687 | 39.95
2021-08-27 12:30 | 44435.5208 | 0 | 7.537 | 39.95
2021-08-27 13:00 | 44435.5417 | 0 | 7.68 | 39.95
2021-08-27 13:30 | 44435.5625 | 0 | 8.0214 | 39.95
2021-08-27 14:00 | 44435.5833 | 0 | 8.1856 | 39.95
2021-08-27 14:30 | 44435.6042 | 0 | 8.8823 | 39.95
2021-08-27 15:00 | 44435.625 | 0 | 9.3125 | 39.95
2021-08-27 15:30 | 44435.6458 | 0 | 10.1141 | 39.95
2021-08-27 16:00 | 44435.6667 | 0 | 10.8988 | 39.95
2021-08-27 16:30 | 44435.6875 | 0 | 11.77 | 39.95
2021-08-27 17:00 | 44435.7083 | 0 | 12.3683 | 39.95
2021-08-27 17:30 | 44435.7292 | 0 | 13.0451 | 39.95
2021-08-27 18:00 | 44435.75 | 0 | 13.5447 | 39.95
2021-08-27 18:30 | 44435.7708 | 0 | 13.7643 | 39.95
2021-08-27 19:00 | 44435.7917 | 0 | 13.5217 | 39.95
2021-08-27 19:30 | 44435.8125 | 0 | 13.3756 | 39.95
2021-08-27 20:00 | 44435.8333 | 0 | 13.2553 | 39.95
2021-08-27 20:30 | 44435.8542 | 0 | 12.6969 | 39.95
2021-08-27 21:00 | 44435.875 | 0 | 12.2273 | 39.95
2021-08-27 21:30 | 44435.8958 | 0 | 11.815 | 39.95
2021-08-27 22:00 | 44435.9167 | 0 | 11.279 | 39.95
2021-08-27 22:30 | 44435.9375 | 0 | 10.564 | 39.95
2021-08-27 23:00 | 44435.9583 | 0 | 10.0412 | 39.95
2021-08-27 23:30 | 44435.9792 | 0 | 9.4071 | 39.95
2021-08-28 | 44436 | 0 | 8.8816 | 39.95
2021-08-28 00:30 | 44436.0208 | 0 | 8.4105 | 39.95
2021-08-28 01:00 | 44436.0417 | 0 | 8.1965 | 39.95
2021-08-28 01:30 | 44436.0625 | 0 | 7.9396 | 39.95
2021-08-28 02:00 | 44436.0833 | 0 | 7.8188 | 39.95
2021-08-28 02:30 | 44436.1042 | 0 | 7.6802 | 39.95
2021-08-28 03:00 | 44436.125 | 0 | 7.7793 | 39.95
2021-08-28 03:30 | 44436.1458 | 0 | 7.7792 | 39.95
2021-08-28 04:00 | 44436.1667 | 0 | 7.8164 | 39.95
2021-08-28 04:30 | 44436.1875 | 0 | 7.9585 | 39.95
2021-08-28 05:00 | 44436.2083 | 0 | 8.4526 | 39.95
2021-08-28 05:30 | 44436.2292 | 0 | 8.8496 | 39.95
2021-08-28 06:00 | 44436.25 | 0 | 9.4431 | 39.95
2021-08-28 06:30 | 44436.2708 | 0 | 9.7807 | 39.95
2021-08-28 07:00 | 44436.2917 | 0 | 9.9887 | 39.95
2021-08-28 07:30 | 44436.3125 | 0 | 9.665 | 39.95
2021-08-28 08:00 | 44436.3333 | 0 | 9.2073 | 39.95
2021-08-28 08:30 | 44436.3542 | 0 | 8.594 | 39.95
2021-08-28 09:00 | 44436.375 | 0 | 7.8541 | 39.95
2021-08-28 09:30 | 44436.3958 | 0 | 7.4488 | 39.95
2021-08-28 10:00 | 44436.4167 | 0 | 6.6825 | 39.95
2021-08-28 10:30 | 44436.4375 | 0 | 6.2449 | 39.95
2021-08-28 11:00 | 44436.4583 | 0 | 5.766 | 39.95
2021-08-28 11:30 | 44436.4792 | 0 | 5.5162 | 39.95
2021-08-28 12:00 | 44436.5 | 0 | 5.5053 | 39.95
2021-08-28 12:30 | 44436.5208 | 0 | 5.5101 | 39.95
2021-08-28 13:00 | 44436.5417 | 0 | 5.6333 | 39.95
2021-08-28 13:30 | 44436.5625 | 0 | 5.7936 | 39.95
2021-08-28 14:00 | 44436.5833 | 0 | 6.2765 | 39.95
2021-08-28 14:30 | 44436.6042 | 0 | 6.8383 | 39.95
2021-08-28 15:00 | 44436.625 | 0 | 7.4961 | 39.95
2021-08-28 15:30 | 44436.6458 | 0 | 8.2378 | 39.95
2021-08-28 16:00 | 44436.6667 | 0 | 8.937 | 39.95
2021-08-28 16:30 | 44436.6875 | 0 | 9.836 | 39.95
2021-08-28 17:00 | 44436.7083 | 0 | 10.6551 | 39.95
2021-08-28 17:30 | 44436.7292 | 0 | 11.2117 | 39.95
2021-08-28 18:00 | 44436.75 | 0 | 11.7518 | 39.95
2021-08-28 18:30 | 44436.7708 | 0 | 11.812 | 39.95
2021-08-28 19:00 | 44436.7917 | 0 | 11.6032 | 39.95
2021-08-28 19:30 | 44436.8125 | 0 | 11.3406 | 39.95
2021-08-28 20:00 | 44436.8333 | 0 | 11.2458 | 39.95
2021-08-28 20:30 | 44436.8542 | 0 | 10.6923 | 39.95
2021-08-28 21:00 | 44436.875 | 0 | 10.3278 | 39.95
2021-08-28 21:30 | 44436.8958 | 0 | 10.139 | 39.95
2021-08-28 22:00 | 44436.9167 | 0 | 9.6912 | 39.95
2021-08-28 22:30 | 44436.9375 | 0 | 9.1248 | 39.95
2021-08-28 23:00 | 44436.9583 | 0 | 8.7811 | 39.95
2021-08-28 23:30 | 44436.9792 | 0 | 8.2861 | 39.95
2021-08-29 | 44437 | 0 | 7.8404 | 39.95
2021-08-29 00:30 | 44437.0208 | 0 | 7.5659 | 39.95
2021-08-29 01:00 | 44437.0417 | 0 | 7.3529 | 39.95
2021-08-29 01:30 | 44437.0625 | 0 | 7.2233 | 39.95
2021-08-29 02:00 | 44437.0833 | 0 | 7.2006 | 39.95
2021-08-29 02:30 | 44437.1042 | 0 | 6.9998 | 39.95
2021-08-29 03:00 | 44437.125 | 0 | 7.0626 | 39.95
2021-08-29 03:30 | 44437.1458 | 0 | 7.0686 | 39.95
2021-08-29 04:00 | 44437.1667 | 0 | 6.9847 | 39.95
2021-08-29 04:30 | 44437.1875 | 0 | 7.0511 | 39.95
2021-08-29 05:00 | 44437.2083 | 0 | 7.1555 | 39.95
2021-08-29 05:30 | 44437.2292 | 0 | 7.3734 | 39.95
2021-08-29 06:00 | 44437.25 | 0 | 7.672 | 39.95
2021-08-29 06:30 | 44437.2708 | 0 | 7.9335 | 39.95
2021-08-29 07:00 | 44437.2917 | 0 | 8.1158 | 39.95
2021-08-29 07:30 | 44437.3125 | 0 | 7.6791 | 39.95
2021-08-29 08:00 | 44437.3333 | 0 | 8.6616 | 39.95
2021-08-29 08:30 | 44437.3542 | 0 | 9.5401 | 39.95
2021-08-29 09:00 | 44437.375 | 0 | 9.2372 | 39.95
2021-08-29 09:30 | 44437.3958 | 0 | 8.2934 | 39.95
2021-08-29 10:00 | 44437.4167 | 0 | 7.5322 | 39.95
2021-08-29 10:30 | 44437.4375 | 0 | 6.3799 | 39.95
2021-08-29 11:00 | 44437.4583 | 0 | 5.7931 | 39.95
2021-08-29 11:30 | 44437.4792 | 0 | 5.2089 | 39.95
2021-08-29 12:00 | 44437.5 | 0 | 5.1741 | 39.95
2021-08-29 12:30 | 44437.5208 | 0 | 5.3317 | 39.95
2021-08-29 13:00 | 44437.5417 | 0 | 5.061 | 39.95
2021-08-29 13:30 | 44437.5625 | 0 | 5.9456 | 39.95
2021-08-29 14:00 | 44437.5833 | 0 | 5.9351 | 39.95
2021-08-29 14:30 | 44437.6042 | 0 | 6.4637 | 39.95
2021-08-29 15:00 | 44437.625 | 0 | 7.2649 | 39.95
2021-08-29 15:30 | 44437.6458 | 0 | 8.1274 | 39.95
2021-08-29 16:00 | 44437.6667 | 0 | 8.9104 | 39.95
2021-08-29 16:30 | 44437.6875 | 0 | 9.9245 | 39.95
2021-08-29 17:00 | 44437.7083 | 0 | 10.6818 | 39.95
2021-08-29 17:30 | 44437.7292 | 0 | 11.343 | 39.95
2021-08-29 18:00 | 44437.75 | 0 | 12.1429 | 39.95
2021-08-29 18:30 | 44437.7708 | 0 | 12.1892 | 39.95
2021-08-29 19:00 | 44437.7917 | 0 | 11.7308 | 39.95
2021-08-29 19:30 | 44437.8125 | 0 | 11.5092 | 39.95
2021-08-29 20:00 | 44437.8333 | 0 | 11.2038 | 39.95
2021-08-29 20:30 | 44437.8542 | 0 | 10.7937 | 39.95
2021-08-29 21:00 | 44437.875 | 0 | 10.2684 | 39.95
2021-08-29 21:30 | 44437.8958 | 0 | 9.9103 | 39.95
2021-08-29 22:00 | 44437.9167 | 0 | 9.4351 | 39.95
2021-08-29 22:30 | 44437.9375 | 0 | 8.7415 | 39.95
2021-08-29 23:00 | 44437.9583 | 0 | 8.27 | 39.95
2021-08-29 23:30 | 44437.9792 | 0 | 7.9456 | 39.95
2021-08-30 | 44438 | 0 | 7.5091 | 39.95
2021-08-30 00:30 | 44438.0208 | 0 | 7.3197 | 39.95
2021-08-30 01:00 | 44438.0417 | 0 | 7.1841 | 39.95
2021-08-30 01:30 | 44438.0625 | 0 | 7.0571 | 39.95
2021-08-30 02:00 | 44438.0833 | 0 | 7.1127 | 39.95
2021-08-30 02:30 | 44438.1042 | 0 | 7.1078 | 39.95
2021-08-30 03:00 | 44438.125 | 0 | 7.068 | 39.95
2021-08-30 03:30 | 44438.1458 | 0 | 7.3241 | 39.95
2021-08-30 04:00 | 44438.1667 | 0 | 7.6949 | 39.95
2021-08-30 04:30 | 44438.1875 | 0 | 8.2063 | 39.95
2021-08-30 05:00 | 44438.2083 | 0 | 8.7693 | 39.95
2021-08-30 05:30 | 44438.2292 | 0 | 9.5613 | 39.95
2021-08-30 06:00 | 44438.25 | 0 | 10.5725 | 39.95
2021-08-30 06:30 | 44438.2708 | 0 | 11.4667 | 39.95
2021-08-30 07:00 | 44438.2917 | 0 | 11.6769 | 39.95
2021-08-30 07:30 | 44438.3125 | 0 | 11.2132 | 39.95
2021-08-30 08:00 | 44438.3333 | 0 | 11.6622 | 39.95
2021-08-30 08:30 | 44438.3542 | 0 | 10.1181 | 39.95
2021-08-30 09:00 | 44438.375 | 0 | 8.7463 | 39.95
2021-08-30 09:30 | 44438.3958 | 0 | 7.7827 | 39.95
2021-08-30 10:00 | 44438.4167 | 0 | 8.3067 | 39.95
2021-08-30 10:30 | 44438.4375 | 0 | 8.0141 | 39.95
2021-08-30 11:00 | 44438.4583 | 0 | 7.9504 | 39.95
2021-08-30 11:30 | 44438.4792 | 0 | 7.7677 | 39.95
2021-08-30 12:00 | 44438.5 | 0 | 7.942 | 39.95
2021-08-30 12:30 | 44438.5208 | 0 | 7.8816 | 39.95
2021-08-30 13:00 | 44438.5417 | 0 | 8.1345 | 39.95
2021-08-30 13:30 | 44438.5625 | 0 | 8.469 | 39.95
2021-08-30 14:00 | 44438.5833 | 0 | 8.8553 | 39.95
2021-08-30 14:30 | 44438.6042 | 0 | 9.2461 | 39.95
2021-08-30 15:00 | 44438.625 | 0 | 9.9372 | 39.95
2021-08-30 15:30 | 44438.6458 | 0 | 10.9665 | 39.95
2021-08-30 16:00 | 44438.6667 | 0 | 11.519 | 39.95
2021-08-30 16:30 | 44438.6875 | 0 | 12.012 | 39.95
2021-08-30 17:00 | 44438.7083 | 0 | 12.4722 | 39.95
2021-08-30 17:30 | 44438.7292 | 0 | 13.5293 | 39.95
2021-08-30 18:00 | 44438.75 | 0 | 13.9739 | 39.95
2021-08-30 18:30 | 44438.7708 | 0 | 14.2902 | 39.95
2021-08-30 19:00 | 44438.7917 | 0 | 13.9025 | 39.95
2021-08-30 19:30 | 44438.8125 | 0 | 13.5414 | 39.95
2021-08-30 20:00 | 44438.8333 | 0 | 13.0979 | 39.95
2021-08-30 20:30 | 44438.8542 | 0 | 12.6213 | 39.95
2021-08-30 21:00 | 44438.875 | 0 | 11.8974 | 39.95
2021-08-30 21:30 | 44438.8958 | 0 | 11.5232 | 39.95
2021-08-30 22:00 | 44438.9167 | 0 | 11.0184 | 39.95
2021-08-30 22:30 | 44438.9375 | 0 | 10.1281 | 39.95
2021-08-30 23:00 | 44438.9583 | 0 | 9.4276 | 39.95
2021-08-30 23:30 | 44438.9792 | 0 | 9.0067 | 39.95
2021-08-31 | 44439 | 0 | 8.41 | 39.95
2021-08-31 00:30 | 44439.0208 | 0 | 8.1155 | 39.95
2021-08-31 01:00 | 44439.0417 | 0 | 7.8279 | 39.95
2021-08-31 01:30 | 44439.0625 | 0 | 7.7424 | 39.95
2021-08-31 02:00 | 44439.0833 | 0 | 7.6378 | 39.95
2021-08-31 02:30 | 44439.1042 | 0 | 7.6022 | 39.95
2021-08-31 03:00 | 44439.125 | 0 | 7.6044 | 39.95
2021-08-31 03:30 | 44439.1458 | 0 | 7.7788 | 39.95
2021-08-31 04:00 | 44439.1667 | 0 | 7.9498 | 39.95
2021-08-31 04:30 | 44439.1875 | 0 | 8.4265 | 39.95
2021-08-31 05:00 | 44439.2083 | 0 | 9.0542 | 39.95
2021-08-31 05:30 | 44439.2292 | 0 | 9.7259 | 39.95
2021-08-31 06:00 | 44439.25 | 0 | 10.8288 | 39.95
2021-08-31 06:30 | 44439.2708 | 0 | 11.6917 | 39.95
2021-08-31 07:00 | 44439.2917 | 0 | 12.3726 | 39.95
2021-08-31 07:30 | 44439.3125 | 0 | 11.5321 | 39.95
2021-08-31 08:00 | 44439.3333 | 0 | 11.9441 | 39.95
2021-08-31 08:30 | 44439.3542 | 0 | 11.732 | 39.95
2021-08-31 09:00 | 44439.375 | 0 | 12.0258 | 39.95
2021-08-31 09:30 | 44439.3958 | 0 | 10.7972 | 39.95
2021-08-31 10:00 | 44439.4167 | 0 | 11.2957 | 39.95
2021-08-31 10:30 | 44439.4375 | 0 | 11.6011 | 39.95
2021-08-31 11:00 | 44439.4583 | 0 | 10.9644 | 39.95
2021-08-31 11:30 | 44439.4792 | 0 | 10.4223 | 39.95
2021-08-31 12:00 | 44439.5 | 0 | 9.495 | 39.95
2021-08-31 12:30 | 44439.5208 | 0 | 8.2852 | 39.95
2021-08-31 13:00 | 44439.5417 | 0 | 8.4134 | 39.95
2021-08-31 13:30 | 44439.5625 | 0 | 8.9909 | 39.95
2021-08-31 14:00 | 44439.5833 | 0 | 9.6564 | 39.95
2021-08-31 14:30 | 44439.6042 | 0 | 10.1546 | 39.95
2021-08-31 15:00 | 44439.625 | 0 | 10.5893 | 39.95
2021-08-31 15:30 | 44439.6458 | 0 | 11.2332 | 39.95
2021-08-31 16:00 | 44439.6667 | 0 | 12.0736 | 39.95
2021-08-31 16:30 | 44439.6875 | 0 | 12.9727 | 39.95
2021-08-31 17:00 | 44439.7083 | 0 | 13.3789 | 39.95
2021-08-31 17:30 | 44439.7292 | 0 | 14.062 | 39.95
2021-08-31 18:00 | 44439.75 | 0 | 14.2706 | 39.95
2021-08-31 18:30 | 44439.7708 | 0 | 14.5733 | 39.95
2021-08-31 19:00 | 44439.7917 | 0 | 14.0517 | 39.95
2021-08-31 19:30 | 44439.8125 | 0 | 13.7475 | 39.95
2021-08-31 20:00 | 44439.8333 | 0 | 13.5187 | 39.95
2021-08-31 20:30 | 44439.8542 | 0 | 12.9882 | 39.95
2021-08-31 21:00 | 44439.875 | 0 | 12.3626 | 39.95
2021-08-31 21:30 | 44439.8958 | 0 | 11.9246 | 39.95
2021-08-31 22:00 | 44439.9167 | 0 | 11.415 | 39.95
2021-08-31 22:30 | 44439.9375 | 0 | 10.6812 | 39.95
2021-08-31 23:00 | 44439.9583 | 0 | 9.8252 | 39.95
2021-08-31 23:30 | 44439.9792 | 0 | 9.2458 | 39.95
2021-09-01 | 44440 | 0 | 8.6653 | 39.95
2021-09-01 00:30 | 44440.0208 | 0 | 8.347 | 39.95
2021-09-01 01:00 | 44440.0417 | 0 | 8.2228 | 39.95
2021-09-01 01:30 | 44440.0625 | 0 | 8.0228 | 39.95
2021-09-01 02:00 | 44440.0833 | 0 | 8.014 | 39.95
2021-09-01 02:30 | 44440.1042 | 0 | 7.8273 | 39.95
2021-09-01 03:00 | 44440.125 | 0 | 7.8834 | 39.95
2021-09-01 03:30 | 44440.1458 | 0 | 8.0784 | 39.95
2021-09-01 04:00 | 44440.1667 | 0 | 8.3487 | 39.95
2021-09-01 04:30 | 44440.1875 | 0 | 8.8008 | 39.95
2021-09-01 05:00 | 44440.2083 | 0 | 9.4893 | 39.95
2021-09-01 05:30 | 44440.2292 | 0 | 9.9797 | 39.95
2021-09-01 06:00 | 44440.25 | 0 | 11.0154 | 39.95
2021-09-01 06:30 | 44440.2708 | 0 | 11.9279 | 39.95
2021-09-01 07:00 | 44440.2917 | 0 | 12.5048 | 39.95
2021-09-01 07:30 | 44440.3125 | 0 | 12.7568 | 39.95
2021-09-01 08:00 | 44440.3333 | 0 | 12.697 | 39.95
2021-09-01 08:30 | 44440.3542 | 0 | 10.9987 | 39.95
2021-09-01 09:00 | 44440.375 | 0 | 9.8314 | 39.95
2021-09-01 09:30 | 44440.3958 | 0 | 9.3836 | 39.95
2021-09-01 10:00 | 44440.4167 | 0 | 9.227 | 39.95
2021-09-01 10:30 | 44440.4375 | 0 | 9.2847 | 39.95
2021-09-01 11:00 | 44440.4583 | 0 | 9.1733 | 39.95
2021-09-01 11:30 | 44440.4792 | 0 | 9.3123 | 39.95
2021-09-01 12:00 | 44440.5 | 0 | 9.3206 | 39.95
2021-09-01 12:30 | 44440.5208 | 0 | 9.3292 | 39.95
2021-09-01 13:00 | 44440.5417 | 0 | 9.4069 | 39.95
2021-09-01 13:30 | 44440.5625 | 0 | 9.8154 | 39.95
2021-09-01 14:00 | 44440.5833 | 0 | 10.4175 | 39.95
2021-09-01 14:30 | 44440.6042 | 0 | 10.8408 | 39.95
2021-09-01 15:00 | 44440.625 | 0 | 11.2973 | 39.95
2021-09-01 15:30 | 44440.6458 | 0 | 11.9754 | 39.95
2021-09-01 16:00 | 44440.6667 | 0 | 12.6 | 39.95
2021-09-01 16:30 | 44440.6875 | 0 | 13.1167 | 39.95
2021-09-01 17:00 | 44440.7083 | 0 | 13.4338 | 39.95
2021-09-01 17:30 | 44440.7292 | 0 | 14.2355 | 39.95
2021-09-01 18:00 | 44440.75 | 0 | 14.6269 | 39.95
2021-09-01 18:30 | 44440.7708 | 0 | 14.6894 | 39.95
2021-09-01 19:00 | 44440.7917 | 0 | 14.3641 | 39.95
2021-09-01 19:30 | 44440.8125 | 0 | 14.2543 | 39.95
2021-09-01 20:00 | 44440.8333 | 0 | 13.7083 | 39.95
2021-09-01 20:30 | 44440.8542 | 0 | 13.1491 | 39.95
2021-09-01 21:00 | 44440.875 | 0 | 12.7192 | 39.95
2021-09-01 21:30 | 44440.8958 | 0 | 12.399 | 39.95
2021-09-01 22:00 | 44440.9167 | 0 | 11.6239 | 39.95
2021-09-01 22:30 | 44440.9375 | 0 | 10.7337 | 39.95
2021-09-01 23:00 | 44440.9583 | 0 | 10.0736 | 39.95
2021-09-01 23:30 | 44440.9792 | 0 | 9.5969 | 39.95
2021-09-02 | 44441 | 0 | 8.9956 | 39.95
2021-09-02 00:30 | 44441.0208 | 0 | 8.5575 | 39.95
2021-09-02 01:00 | 44441.0417 | 0 | 8.3494 | 39.95
2021-09-02 01:30 | 44441.0625 | 0 | 8.1941 | 39.95
2021-09-02 02:00 | 44441.0833 | 0 | 8.1683 | 39.95
2021-09-02 02:30 | 44441.1042 | 0 | 8.0567 | 39.95
2021-09-02 03:00 | 44441.125 | 0 | 8.1345 | 39.95
2021-09-02 03:30 | 44441.1458 | 0 | 8.2051 | 39.95
2021-09-02 04:00 | 44441.1667 | 0 | 8.3627 | 39.95
2021-09-02 04:30 | 44441.1875 | 0 | 8.9344 | 39.95
2021-09-02 05:00 | 44441.2083 | 0 | 9.5317 | 39.95
2021-09-02 05:30 | 44441.2292 | 0 | 10.2734 | 39.95
2021-09-02 06:00 | 44441.25 | 0 | 10.863 | 39.95
2021-09-02 06:30 | 44441.2708 | 0 | 11.7236 | 39.95
2021-09-02 07:00 | 44441.2917 | 0 | 11.8765 | 39.95
2021-09-02 07:30 | 44441.3125 | 0 | 11.6364 | 39.95
2021-09-02 08:00 | 44441.3333 | 0 | 11.8512 | 39.95
2021-09-02 08:30 | 44441.3542 | 0 | 11.0362 | 39.95
2021-09-02 09:00 | 44441.375 | 0 | 11.1232 | 39.95
2021-09-02 09:30 | 44441.3958 | 0 | 10.2197 | 39.95
2021-09-02 10:00 | 44441.4167 | 0 | 10.1419 | 39.95
2021-09-02 10:30 | 44441.4375 | 0 | 10.5166 | 39.95
2021-09-02 11:00 | 44441.4583 | 0 | 10.284 | 39.95
2021-09-02 11:30 | 44441.4792 | 0 | 10.6088 | 39.95
2021-09-02 12:00 | 44441.5 | 0 | 10.3176 | 39.95
2021-09-02 12:30 | 44441.5208 | 0 | 9.9733 | 39.95
2021-09-02 13:00 | 44441.5417 | 0 | 9.6221 | 39.95
2021-09-02 13:30 | 44441.5625 | 0 | 9.8683 | 39.95
2021-09-02 14:00 | 44441.5833 | 0 | 9.8392 | 39.95
2021-09-02 14:30 | 44441.6042 | 0 | 10.5549 | 39.95
2021-09-02 15:00 | 44441.625 | 0 | 10.8245 | 39.95
2021-09-02 15:30 | 44441.6458 | 0 | 11.4317 | 39.95
2021-09-02 16:00 | 44441.6667 | 0 | 12.1914 | 39.95
2021-09-02 16:30 | 44441.6875 | 0 | 12.5571 | 39.95
2021-09-02 17:00 | 44441.7083 | 0 | 12.822 | 39.95
2021-09-02 17:30 | 44441.7292 | 0 | 13.4045 | 39.95
2021-09-02 18:00 | 44441.75 | 0 | 13.813 | 39.95
2021-09-02 18:30 | 44441.7708 | 0 | 14.0468 | 39.95
2021-09-02 19:00 | 44441.7917 | 0 | 13.7163 | 39.95
2021-09-02 19:30 | 44441.8125 | 0 | 13.6253 | 39.95
2021-09-02 20:00 | 44441.8333 | 0 | 13.2195 | 39.95
2021-09-02 20:30 | 44441.8542 | 0 | 12.7868 | 39.95
2021-09-02 21:00 | 44441.875 | 0 | 12.3188 | 39.95
2021-09-02 21:30 | 44441.8958 | 0 | 11.656 | 39.95
2021-09-02 22:00 | 44441.9167 | 0 | 11.1329 | 39.95
2021-09-02 22:30 | 44441.9375 | 0 | 10.1255 | 39.95
2021-09-02 23:00 | 44441.9583 | 0 | 9.6374 | 39.95
2021-09-02 23:30 | 44441.9792 | 0 | 9.1988 | 39.95
2021-09-03 | 44442 | 0 | 8.5808 | 39.95
2021-09-03 00:30 | 44442.0208 | 0 | 8.1409 | 39.95
2021-09-03 01:00 | 44442.0417 | 0 | 7.9177 | 39.95
2021-09-03 01:30 | 44442.0625 | 0 | 7.7514 | 39.95
2021-09-03 02:00 | 44442.0833 | 0 | 7.807 | 39.95
2021-09-03 02:30 | 44442.1042 | 0 | 7.8164 | 39.95
2021-09-03 03:00 | 44442.125 | 0 | 7.8333 | 39.95
2021-09-03 03:30 | 44442.1458 | 0 | 7.9329 | 39.95
2021-09-03 04:00 | 44442.1667 | 0 | 8.1291 | 39.95
2021-09-03 04:30 | 44442.1875 | 0 | 8.6844 | 39.95
2021-09-03 05:00 | 44442.2083 | 0 | 9.4489 | 39.95
2021-09-03 05:30 | 44442.2292 | 0 | 9.9604 | 39.95
2021-09-03 06:00 | 44442.25 | 0 | 10.5981 | 39.95
2021-09-03 06:30 | 44442.2708 | 0 | 11.4762 | 39.95
2021-09-03 07:00 | 44442.2917 | 0 | 12.5645 | 39.95
2021-09-03 07:30 | 44442.3125 | 0 | 11.7915 | 39.95
2021-09-03 08:00 | 44442.3333 | 0 | 11.6067 | 39.95
2021-09-03 08:30 | 44442.3542 | 0 | 12.7723 | 39.95
2021-09-03 09:00 | 44442.375 | 0 | 11.0995 | 39.95
2021-09-03 09:30 | 44442.3958 | 0 | 9.889 | 39.95
2021-09-03 10:00 | 44442.4167 | 0 | 9.3909 | 39.95
2021-09-03 10:30 | 44442.4375 | 0 | 8.7806 | 39.95
2021-09-03 11:00 | 44442.4583 | 0 | 8.417 | 39.95
2021-09-03 11:30 | 44442.4792 | 0 | 8.285 | 39.95
2021-09-03 12:00 | 44442.5 | 0 | 7.9426 | 39.95
2021-09-03 12:30 | 44442.5208 | 0 | 8.0066 | 39.95
2021-09-03 13:00 | 44442.5417 | 0 | 8.0114 | 39.95
2021-09-03 13:30 | 44442.5625 | 0 | 8.6485 | 39.95
2021-09-03 14:00 | 44442.5833 | 0 | 9.6396 | 39.95
2021-09-03 14:30 | 44442.6042 | 0 | 9.8194 | 39.95
2021-09-03 15:00 | 44442.625 | 0 | 10.3381 | 39.95
2021-09-03 15:30 | 44442.6458 | 0 | 11.5661 | 39.95
2021-09-03 16:00 | 44442.6667 | 0 | 11.9578 | 39.95
2021-09-03 16:30 | 44442.6875 | 0 | 12.5563 | 39.95
2021-09-03 17:00 | 44442.7083 | 0 | 12.5868 | 39.95
2021-09-03 17:30 | 44442.7292 | 0 | 13.3298 | 39.95
2021-09-03 18:00 | 44442.75 | 0 | 13.403 | 39.95
2021-09-03 18:30 | 44442.7708 | 0 | 13.3109 | 39.95
2021-09-03 19:00 | 44442.7917 | 0 | 12.969 | 39.95
2021-09-03 19:30 | 44442.8125 | 0 | 12.9431 | 39.95
2021-09-03 20:00 | 44442.8333 | 0 | 12.7107 | 39.95
2021-09-03 20:30 | 44442.8542 | 0 | 12.1283 | 39.95
2021-09-03 21:00 | 44442.875 | 0 | 11.6169 | 39.95
2021-09-03 21:30 | 44442.8958 | 0 | 11.3172 | 39.95
2021-09-03 22:00 | 44442.9167 | 0 | 10.8448 | 39.95
2021-09-03 22:30 | 44442.9375 | 0 | 10.2003 | 39.95
2021-09-03 23:00 | 44442.9583 | 0 | 9.7103 | 39.95
2021-09-03 23:30 | 44442.9792 | 0 | 9.2503 | 39.95
2021-09-04 | 44443 | 0 | 8.7761 | 39.95
2021-09-04 00:30 | 44443.0208 | 0 | 8.2789 | 39.95
2021-09-04 01:00 | 44443.0417 | 0 | 7.9003 | 39.95
2021-09-04 01:30 | 44443.0625 | 0 | 7.7961 | 39.95
2021-09-04 02:00 | 44443.0833 | 0 | 7.811 | 39.95
2021-09-04 02:30 | 44443.1042 | 0 | 7.6923 | 39.95
2021-09-04 03:00 | 44443.125 | 0 | 7.5816 | 39.95
2021-09-04 03:30 | 44443.1458 | 0 | 7.677 | 39.95
2021-09-04 04:00 | 44443.1667 | 0 | 7.5986 | 39.95
2021-09-04 04:30 | 44443.1875 | 0 | 7.7545 | 39.95
2021-09-04 05:00 | 44443.2083 | 0 | 8.0482 | 39.95
2021-09-04 05:30 | 44443.2292 | 0 | 8.2813 | 39.95
2021-09-04 06:00 | 44443.25 | 0 | 8.5958 | 39.95
2021-09-04 06:30 | 44443.2708 | 0 | 9.0725 | 39.95
2021-09-04 07:00 | 44443.2917 | 0 | 8.6891 | 39.95
2021-09-04 07:30 | 44443.3125 | 0 | 8.1659 | 39.95
2021-09-04 08:00 | 44443.3333 | 0 | 8.0742 | 39.95
2021-09-04 08:30 | 44443.3542 | 0 | 7.7454 | 39.95
2021-09-04 09:00 | 44443.375 | 0 | 8.0404 | 39.95
2021-09-04 09:30 | 44443.3958 | 0 | 7.0245 | 39.95
2021-09-04 10:00 | 44443.4167 | 0 | 7.0189 | 39.95
2021-09-04 10:30 | 44443.4375 | 0 | 7.6842 | 39.95
2021-09-04 11:00 | 44443.4583 | 0 | 6.9988 | 39.95
2021-09-04 11:30 | 44443.4792 | 0 | 7.5114 | 39.95
2021-09-04 12:00 | 44443.5 | 0 | 7.6616 | 39.95
2021-09-04 12:30 | 44443.5208 | 0 | 7.378 | 39.95
2021-09-04 13:00 | 44443.5417 | 0 | 6.9312 | 39.95
2021-09-04 13:30 | 44443.5625 | 0 | 6.6389 | 39.95
2021-09-04 14:00 | 44443.5833 | 0 | 6.8969 | 39.95
2021-09-04 14:30 | 44443.6042 | 0 | 7.3802 | 39.95
2021-09-04 15:00 | 44443.625 | 0 | 7.8854 | 39.95
2021-09-04 15:30 | 44443.6458 | 0 | 8.5782 | 39.95
2021-09-04 16:00 | 44443.6667 | 0 | 9.3055 | 39.95
2021-09-04 16:30 | 44443.6875 | 0 | 10.0857 | 39.95
2021-09-04 17:00 | 44443.7083 | 0 | 10.5593 | 39.95
2021-09-04 17:30 | 44443.7292 | 0 | 11.0633 | 39.95
2021-09-04 18:00 | 44443.75 | 0 | 11.2388 | 39.95
2021-09-04 18:30 | 44443.7708 | 0 | 11.5033 | 39.95
2021-09-04 19:00 | 44443.7917 | 0 | 11.2657 | 39.95
2021-09-04 19:30 | 44443.8125 | 0 | 11.1048 | 39.95
2021-09-04 20:00 | 44443.8333 | 0 | 10.7611 | 39.95
2021-09-04 20:30 | 44443.8542 | 0 | 10.4354 | 39.95
2021-09-04 21:00 | 44443.875 | 0 | 10.0631 | 39.95
2021-09-04 21:30 | 44443.8958 | 0 | 9.8036 | 39.95
2021-09-04 22:00 | 44443.9167 | 0 | 9.4601 | 39.95
2021-09-04 22:30 | 44443.9375 | 0 | 9.0569 | 39.95
2021-09-04 23:00 | 44443.9583 | 0 | 8.6099 | 39.95
2021-09-04 23:30 | 44443.9792 | 0 | 8.0058 | 39.95
2021-09-05 | 44444 | 0 | 7.7167 | 39.95
2021-09-05 00:30 | 44444.0208 | 0 | 7.4597 | 39.95
2021-09-05 01:00 | 44444.0417 | 0 | 7.3251 | 39.95
2021-09-05 01:30 | 44444.0625 | 0 | 7.1484 | 39.95
2021-09-05 02:00 | 44444.0833 | 0 | 7.1132 | 39.95
2021-09-05 02:30 | 44444.1042 | 0 | 7.0016 | 39.95
2021-09-05 03:00 | 44444.125 | 0 | 6.9624 | 39.95
2021-09-05 03:30 | 44444.1458 | 0 | 6.9286 | 39.95
2021-09-05 04:00 | 44444.1667 | 0 | 6.8954 | 39.95
2021-09-05 04:30 | 44444.1875 | 0 | 6.9449 | 39.95
2021-09-05 05:00 | 44444.2083 | 0 | 6.7491 | 39.95
2021-09-05 05:30 | 44444.2292 | 0 | 6.8 | 39.95
2021-09-05 06:00 | 44444.25 | 0 | 6.9394 | 39.95
2021-09-05 06:30 | 44444.2708 | 0 | 7.1127 | 39.95
2021-09-05 07:00 | 44444.2917 | 0 | 6.9569 | 39.95
2021-09-05 07:30 | 44444.3125 | 0 | 7.6588 | 39.95
2021-09-05 08:00 | 44444.3333 | 0 | 8.2393 | 39.95
2021-09-05 08:30 | 44444.3542 | 0 | 8.0377 | 39.95
2021-09-05 09:00 | 44444.375 | 0 | 8.133 | 39.95
2021-09-05 09:30 | 44444.3958 | 0 | 7.6891 | 39.95
2021-09-05 10:00 | 44444.4167 | 0 | 6.4958 | 39.95
2021-09-05 10:30 | 44444.4375 | 0 | 5.3686 | 39.95
2021-09-05 11:00 | 44444.4583 | 0 | 6.3196 | 39.95
2021-09-05 11:30 | 44444.4792 | 0 | 7.1368 | 39.95
2021-09-05 12:00 | 44444.5 | 0 | 9.0235 | 39.95
2021-09-05 12:30 | 44444.5208 | 0 | 9.8491 | 39.95
2021-09-05 13:00 | 44444.5417 | 0 | 9.1298 | 39.95
2021-09-05 13:30 | 44444.5625 | 0 | 9.8781 | 39.95
2021-09-05 14:00 | 44444.5833 | 0 | 9.9714 | 39.95
2021-09-05 14:30 | 44444.6042 | 0 | 10.0823 | 39.95
2021-09-05 15:00 | 44444.625 | 0 | 10.3208 | 39.95
2021-09-05 15:30 | 44444.6458 | 0 | 10.6724 | 39.95
2021-09-05 16:00 | 44444.6667 | 0 | 10.7734 | 39.95
2021-09-05 16:30 | 44444.6875 | 0 | 11.1426 | 39.95
2021-09-05 17:00 | 44444.7083 | 0 | 11.4165 | 39.95
2021-09-05 17:30 | 44444.7292 | 0 | 11.6175 | 39.95
2021-09-05 18:00 | 44444.75 | 0 | 11.5822 | 39.95
2021-09-05 18:30 | 44444.7708 | 0 | 11.5336 | 39.95
2021-09-05 19:00 | 44444.7917 | 0 | 11.422 | 39.95
2021-09-05 19:30 | 44444.8125 | 0 | 11.2754 | 39.95
2021-09-05 20:00 | 44444.8333 | 0 | 11.2399 | 39.95
2021-09-05 20:30 | 44444.8542 | 0 | 10.6295 | 39.95
2021-09-05 21:00 | 44444.875 | 0 | 10.2016 | 39.95
2021-09-05 21:30 | 44444.8958 | 0 | 9.7913 | 39.95
2021-09-05 22:00 | 44444.9167 | 0 | 9.3502 | 39.95
2021-09-05 22:30 | 44444.9375 | 0 | 8.675 | 39.95
2021-09-05 23:00 | 44444.9583 | 0 | 8.2303 | 39.95
2021-09-05 23:30 | 44444.9792 | 0 | 7.9612 | 39.95
2021-09-06 | 44445 | 0 | 7.5098 | 39.95
2021-09-06 00:30 | 44445.0208 | 0 | 7.3221 | 39.95
2021-09-06 01:00 | 44445.0417 | 0 | 7.1241 | 39.95
2021-09-06 01:30 | 44445.0625 | 0 | 6.9999 | 39.95
2021-09-06 02:00 | 44445.0833 | 0 | 7.0855 | 39.95
2021-09-06 02:30 | 44445.1042 | 0 | 6.9286 | 39.95
2021-09-06 03:00 | 44445.125 | 0 | 7.0903 | 39.95
2021-09-06 03:30 | 44445.1458 | 0 | 7.2036 | 39.95
2021-09-06 04:00 | 44445.1667 | 0 | 7.6498 | 39.95
2021-09-06 04:30 | 44445.1875 | 0 | 8.1836 | 39.95
2021-09-06 05:00 | 44445.2083 | 0 | 8.7553 | 39.95
2021-09-06 05:30 | 44445.2292 | 0 | 9.6346 | 39.95
2021-09-06 06:00 | 44445.25 | 0 | 10.7414 | 39.95
2021-09-06 06:30 | 44445.2708 | 0 | 11.7029 | 39.95
2021-09-06 07:00 | 44445.2917 | 0 | 12.2753 | 39.95
2021-09-06 07:30 | 44445.3125 | 0 | 11.8659 | 39.95
2021-09-06 08:00 | 44445.3333 | 0 | 11.1002 | 39.95
2021-09-06 08:30 | 44445.3542 | 0 | 10.4161 | 39.95
2021-09-06 09:00 | 44445.375 | 0 | 9.6187 | 39.95
2021-09-06 09:30 | 44445.3958 | 0 | 8.7052 | 39.95
2021-09-06 10:00 | 44445.4167 | 0 | 8.4504 | 39.95
2021-09-06 10:30 | 44445.4375 | 0 | 8.3315 | 39.95
2021-09-06 11:00 | 44445.4583 | 0 | 8.6566 | 39.95
2021-09-06 11:30 | 44445.4792 | 0 | 7.6896 | 39.95
2021-09-06 12:00 | 44445.5 | 0 | 7.7052 | 39.95
2021-09-06 12:30 | 44445.5208 | 0 | 7.4398 | 39.95
2021-09-06 13:00 | 44445.5417 | 0 | 7.3746 | 39.95
2021-09-06 13:30 | 44445.5625 | 0 | 7.6949 | 39.95
2021-09-06 14:00 | 44445.5833 | 0 | 8.4423 | 39.95
2021-09-06 14:30 | 44445.6042 | 0 | 8.5126 | 39.95
2021-09-06 15:00 | 44445.625 | 0 | 9.4914 | 39.95
2021-09-06 15:30 | 44445.6458 | 0 | 10.0599 | 39.95
2021-09-06 16:00 | 44445.6667 | 0 | 10.757 | 39.95
2021-09-06 16:30 | 44445.6875 | 0 | 11.5823 | 39.95
2021-09-06 17:00 | 44445.7083 | 0 | 12.3086 | 39.95
2021-09-06 17:30 | 44445.7292 | 0 | 12.8401 | 39.95
2021-09-06 18:00 | 44445.75 | 0 | 13.6597 | 39.95
2021-09-06 18:30 | 44445.7708 | 0 | 14.084 | 39.95
2021-09-06 19:00 | 44445.7917 | 0 | 13.7177 | 39.95
2021-09-06 19:30 | 44445.8125 | 0 | 13.5162 | 39.95
2021-09-06 20:00 | 44445.8333 | 0 | 13.1714 | 39.95
2021-09-06 20:30 | 44445.8542 | 0 | 12.6019 | 39.95
2021-09-06 21:00 | 44445.875 | 0 | 12.1599 | 39.95
2021-09-06 21:30 | 44445.8958 | 0 | 11.8468 | 39.95
2021-09-06 22:00 | 44445.9167 | 0 | 11.0576 | 39.95
2021-09-06 22:30 | 44445.9375 | 0 | 10.3166 | 39.95
2021-09-06 23:00 | 44445.9583 | 0 | 9.6036 | 39.95
2021-09-06 23:30 | 44445.9792 | 0 | 9.0777 | 39.95
2021-09-07 | 44446 | 0 | 8.4345 | 39.95
2021-09-07 00:30 | 44446.0208 | 0 | 8.1297 | 39.95
2021-09-07 01:00 | 44446.0417 | 0 | 7.9062 | 39.95
2021-09-07 01:30 | 44446.0625 | 0 | 7.7772 | 39.95
2021-09-07 02:00 | 44446.0833 | 0 | 7.8019 | 39.95
2021-09-07 02:30 | 44446.1042 | 0 | 7.6468 | 39.95
2021-09-07 03:00 | 44446.125 | 0 | 7.7569 | 39.95
2021-09-07 03:30 | 44446.1458 | 0 | 7.8158 | 39.95
2021-09-07 04:00 | 44446.1667 | 0 | 8.1454 | 39.95
2021-09-07 04:30 | 44446.1875 | 0 | 8.5707 | 39.95
2021-09-07 05:00 | 44446.2083 | 0 | 9.3099 | 39.95
2021-09-07 05:30 | 44446.2292 | 0 | 10.0303 | 39.95
2021-09-07 06:00 | 44446.25 | 0 | 11.1486 | 39.95
2021-09-07 06:30 | 44446.2708 | 0 | 11.8989 | 39.95
2021-09-07 07:00 | 44446.2917 | 0 | 12.0844 | 39.95
2021-09-07 07:30 | 44446.3125 | 0 | 11.5061 | 39.95
2021-09-07 08:00 | 44446.3333 | 0 | 10.6704 | 39.95
2021-09-07 08:30 | 44446.3542 | 0 | 9.7037 | 39.95
2021-09-07 09:00 | 44446.375 | 0 | 8.9747 | 39.95
2021-09-07 09:30 | 44446.3958 | 0 | 8.3418 | 39.95
2021-09-07 10:00 | 44446.4167 | 0 | 7.887 | 39.95
2021-09-07 10:30 | 44446.4375 | 0 | 7.6865 | 39.95
2021-09-07 11:00 | 44446.4583 | 0 | 7.4537 | 39.95
2021-09-07 11:30 | 44446.4792 | 0 | 7.4036 | 39.95
2021-09-07 12:00 | 44446.5 | 0 | 7.2825 | 39.95
2021-09-07 12:30 | 44446.5208 | 0 | 7.3414 | 39.95
2021-09-07 13:00 | 44446.5417 | 0 | 7.546 | 39.95
2021-09-07 13:30 | 44446.5625 | 0 | 7.8705 | 39.95
2021-09-07 14:00 | 44446.5833 | 0 | 8.3572 | 39.95
2021-09-07 14:30 | 44446.6042 | 0 | 8.9317 | 39.95
2021-09-07 15:00 | 44446.625 | 0 | 9.5604 | 39.95
2021-09-07 15:30 | 44446.6458 | 0 | 10.3214 | 39.95
2021-09-07 16:00 | 44446.6667 | 0 | 11.0295 | 39.95
2021-09-07 16:30 | 44446.6875 | 0 | 11.8907 | 39.95
2021-09-07 17:00 | 44446.7083 | 0 | 12.4004 | 39.95
2021-09-07 17:30 | 44446.7292 | 0 | 13.2106 | 39.95
2021-09-07 18:00 | 44446.75 | 0 | 13.7668 | 39.95
2021-09-07 18:30 | 44446.7708 | 0 | 14.1252 | 39.95
2021-09-07 19:00 | 44446.7917 | 0 | 13.901 | 39.95
2021-09-07 19:30 | 44446.8125 | 0 | 13.6569 | 39.95
2021-09-07 20:00 | 44446.8333 | 0 | 13.4879 | 39.95
2021-09-07 20:30 | 44446.8542 | 0 | 13.0676 | 39.95
2021-09-07 21:00 | 44446.875 | 0 | 12.3444 | 39.95
2021-09-07 21:30 | 44446.8958 | 0 | 11.9276 | 39.95
2021-09-07 22:00 | 44446.9167 | 0 | 11.1219 | 39.95
2021-09-07 22:30 | 44446.9375 | 0 | 10.2536 | 39.95
2021-09-07 23:00 | 44446.9583 | 0 | 9.4517 | 39.95
2021-09-07 23:30 | 44446.9792 | 0 | 8.9152 | 39.95
2021-09-08 | 44447 | 0 | 8.4144 | 39.95
2021-09-08 00:30 | 44447.0208 | 0 | 8.1737 | 39.95
2021-09-08 01:00 | 44447.0417 | 0 | 8.0681 | 39.95
2021-09-08 01:30 | 44447.0625 | 0 | 7.8895 | 39.95
2021-09-08 02:00 | 44447.0833 | 0 | 7.8111 | 39.95
2021-09-08 02:30 | 44447.1042 | 0 | 7.6692 | 39.95
2021-09-08 03:00 | 44447.125 | 0 | 7.8219 | 39.95
2021-09-08 03:30 | 44447.1458 | 0 | 7.9058 | 39.95
2021-09-08 04:00 | 44447.1667 | 0 | 8.035 | 39.95
2021-09-08 04:30 | 44447.1875 | 0 | 8.6416 | 39.95
2021-09-08 05:00 | 44447.2083 | 0 | 9.4058 | 39.95
2021-09-08 05:30 | 44447.2292 | 0 | 10.1712 | 39.95
2021-09-08 06:00 | 44447.25 | 0 | 11.3791 | 39.95
2021-09-08 06:30 | 44447.2708 | 0 | 11.9717 | 39.95
2021-09-08 07:00 | 44447.2917 | 0 | 12.1327 | 39.95
2021-09-08 07:30 | 44447.3125 | 0 | 11.7306 | 39.95
2021-09-08 08:00 | 44447.3333 | 0 | 10.8344 | 39.95
2021-09-08 08:30 | 44447.3542 | 0 | 10.0312 | 39.95
2021-09-08 09:00 | 44447.375 | 0 | 9.0214 | 39.95
2021-09-08 09:30 | 44447.3958 | 0 | 8.6033 | 39.95
2021-09-08 10:00 | 44447.4167 | 0 | 8.3886 | 39.95
2021-09-08 10:30 | 44447.4375 | 0 | 8.0319 | 39.95
2021-09-08 11:00 | 44447.4583 | 0 | 9.0178 | 39.95
2021-09-08 11:30 | 44447.4792 | 0 | 9.9981 | 39.95
2021-09-08 12:00 | 44447.5 | 0 | 9.41 | 39.95
2021-09-08 12:30 | 44447.5208 | 0 | 9.4344 | 39.95
2021-09-08 13:00 | 44447.5417 | 0 | 8.3748 | 39.95
2021-09-08 13:30 | 44447.5625 | 0 | 8.9606 | 39.95
2021-09-08 14:00 | 44447.5833 | 0 | 10.3916 | 39.95
2021-09-08 14:30 | 44447.6042 | 0 | 10.0007 | 39.95
2021-09-08 15:00 | 44447.625 | 0 | 10.1299 | 39.95
2021-09-08 15:30 | 44447.6458 | 0 | 11.0217 | 39.95
2021-09-08 16:00 | 44447.6667 | 0 | 11.2973 | 39.95
2021-09-08 16:30 | 44447.6875 | 0 | 12.17 | 39.95
2021-09-08 17:00 | 44447.7083 | 0 | 12.7108 | 39.95
2021-09-08 17:30 | 44447.7292 | 0 | 13.5386 | 39.95
2021-09-08 18:00 | 44447.75 | 0 | 13.914 | 39.95
2021-09-08 18:30 | 44447.7708 | 0 | 14.4029 | 39.95
2021-09-08 19:00 | 44447.7917 | 0 | 14.2555 | 39.95
2021-09-08 19:30 | 44447.8125 | 0 | 13.7792 | 39.95
2021-09-08 20:00 | 44447.8333 | 0 | 13.4285 | 39.95
2021-09-08 20:30 | 44447.8542 | 0 | 12.8904 | 39.95
2021-09-08 21:00 | 44447.875 | 0 | 12.5065 | 39.95
2021-09-08 21:30 | 44447.8958 | 0 | 12.0976 | 39.95
2021-09-08 22:00 | 44447.9167 | 0 | 11.1842 | 39.95
2021-09-08 22:30 | 44447.9375 | 0 | 10.3455 | 39.95
2021-09-08 23:00 | 44447.9583 | 0 | 9.8144 | 39.95
2021-09-08 23:30 | 44447.9792 | 0 | 9.4552 | 39.95
2021-09-09 | 44448 | 0 | 8.5941 | 39.95
2021-09-09 00:30 | 44448.0208 | 0 | 8.1802 | 39.95
2021-09-09 01:00 | 44448.0417 | 0 | 7.9728 | 39.95
2021-09-09 01:30 | 44448.0625 | 0 | 7.878 | 39.95
2021-09-09 02:00 | 44448.0833 | 0 | 7.878 | 39.95
2021-09-09 02:30 | 44448.1042 | 0 | 7.6899 | 39.95
2021-09-09 03:00 | 44448.125 | 0 | 7.7233 | 39.95
2021-09-09 03:30 | 44448.1458 | 0 | 7.8828 | 39.95
2021-09-09 04:00 | 44448.1667 | 0 | 8.1729 | 39.95
2021-09-09 04:30 | 44448.1875 | 0 | 8.6715 | 39.95
2021-09-09 05:00 | 44448.2083 | 0 | 9.2113 | 39.95
2021-09-09 05:30 | 44448.2292 | 0 | 9.9755 | 39.95
2021-09-09 06:00 | 44448.25 | 0 | 10.7977 | 39.95
2021-09-09 06:30 | 44448.2708 | 0 | 11.7071 | 39.95
2021-09-09 07:00 | 44448.2917 | 0 | 11.6513 | 39.95
2021-09-09 07:30 | 44448.3125 | 0 | 11.1639 | 39.95
2021-09-09 08:00 | 44448.3333 | 0 | 10.3677 | 39.95
2021-09-09 08:30 | 44448.3542 | 0 | 9.7228 | 39.95
2021-09-09 09:00 | 44448.375 | 0 | 8.9524 | 39.95
2021-09-09 09:30 | 44448.3958 | 0 | 8.7445 | 39.95
2021-09-09 10:00 | 44448.4167 | 0 | 9.836 | 39.95
2021-09-09 10:30 | 44448.4375 | 0 | 10.1299 | 39.95
2021-09-09 11:00 | 44448.4583 | 0 | 9.6871 | 39.95
2021-09-09 11:30 | 44448.4792 | 0 | 8.33 | 39.95
2021-09-09 12:00 | 44448.5 | 0 | 7.9639 | 39.95
2021-09-09 12:30 | 44448.5208 | 0 | 7.9054 | 39.95
2021-09-09 13:00 | 44448.5417 | 0 | 8.0399 | 39.95
2021-09-09 13:30 | 44448.5625 | 0 | 8.3687 | 39.95
2021-09-09 14:00 | 44448.5833 | 0 | 8.7895 | 39.95
2021-09-09 14:30 | 44448.6042 | 0 | 9.311 | 39.95
2021-09-09 15:00 | 44448.625 | 0 | 9.9201 | 39.95
2021-09-09 15:30 | 44448.6458 | 0 | 10.5146 | 39.95
2021-09-09 16:00 | 44448.6667 | 0 | 11.1971 | 39.95
2021-09-09 16:30 | 44448.6875 | 0 | 11.9855 | 39.95
2021-09-09 17:00 | 44448.7083 | 0 | 12.4968 | 39.95
2021-09-09 17:30 | 44448.7292 | 0 | 13.1751 | 39.95
2021-09-09 18:00 | 44448.75 | 0 | 13.5608 | 39.95
2021-09-09 18:30 | 44448.7708 | 0 | 13.8905 | 39.95
2021-09-09 19:00 | 44448.7917 | 0 | 13.6136 | 39.95
2021-09-09 19:30 | 44448.8125 | 0 | 13.5891 | 39.95
2021-09-09 20:00 | 44448.8333 | 0 | 13.1942 | 39.95
2021-09-09 20:30 | 44448.8542 | 0 | 12.7965 | 39.95
2021-09-09 21:00 | 44448.875 | 0 | 12.2108 | 39.95
2021-09-09 21:30 | 44448.8958 | 0 | 11.686 | 39.95
2021-09-09 22:00 | 44448.9167 | 0 | 11.1012 | 39.95
2021-09-09 22:30 | 44448.9375 | 0 | 10.0772 | 39.95
2021-09-09 23:00 | 44448.9583 | 0 | 9.5392 | 39.95
2021-09-09 23:30 | 44448.9792 | 0 | 9.0846 | 39.95
2021-09-10 | 44449 | 0 | 8.3565 | 39.95
2021-09-10 00:30 | 44449.0208 | 0 | 8.0735 | 39.95
2021-09-10 01:00 | 44449.0417 | 0 | 7.8799 | 39.95
2021-09-10 01:30 | 44449.0625 | 0 | 7.6937 | 39.95
2021-09-10 02:00 | 44449.0833 | 0 | 7.6915 | 39.95
2021-09-10 02:30 | 44449.1042 | 0 | 7.6997 | 39.95
2021-09-10 03:00 | 44449.125 | 0 | 7.604 | 39.95
2021-09-10 03:30 | 44449.1458 | 0 | 7.6716 | 39.95
2021-09-10 04:00 | 44449.1667 | 0 | 7.7444 | 39.95
2021-09-10 04:30 | 44449.1875 | 0 | 8.5438 | 39.95
2021-09-10 05:00 | 44449.2083 | 0 | 9.1727 | 39.95
2021-09-10 05:30 | 44449.2292 | 0 | 9.7975 | 39.95
2021-09-10 06:00 | 44449.25 | 0 | 10.7113 | 39.95
2021-09-10 06:30 | 44449.2708 | 0 | 11.3832 | 39.95
2021-09-10 07:00 | 44449.2917 | 0 | 11.6237 | 39.95
2021-09-10 07:30 | 44449.3125 | 0 | 11.0635 | 39.95
2021-09-10 08:00 | 44449.3333 | 0 | 10.2906 | 39.95
2021-09-10 08:30 | 44449.3542 | 0 | 9.547 | 39.95
2021-09-10 09:00 | 44449.375 | 0 | 9.1443 | 39.95
2021-09-10 09:30 | 44449.3958 | 0 | 8.7358 | 39.95
2021-09-10 10:00 | 44449.4167 | 0 | 8.3808 | 39.95
2021-09-10 10:30 | 44449.4375 | 0 | 8.1941 | 39.95
2021-09-10 11:00 | 44449.4583 | 0 | 8.3023 | 39.95
2021-09-10 11:30 | 44449.4792 | 0 | 8.1941 | 39.95
2021-09-10 12:00 | 44449.5 | 0 | 8.3633 | 39.95
2021-09-10 12:30 | 44449.5208 | 0 | 8.4194 | 39.95
2021-09-10 13:00 | 44449.5417 | 0 | 8.6065 | 39.95
2021-09-10 13:30 | 44449.5625 | 0 | 9.0495 | 39.95
2021-09-10 14:00 | 44449.5833 | 0 | 9.6869 | 39.95
2021-09-10 14:30 | 44449.6042 | 0 | 10.2212 | 39.95
2021-09-10 15:00 | 44449.625 | 0 | 10.7058 | 39.95
2021-09-10 15:30 | 44449.6458 | 0 | 11.2954 | 39.95
2021-09-10 16:00 | 44449.6667 | 0 | 11.8653 | 39.95
2021-09-10 16:30 | 44449.6875 | 0 | 12.6483 | 39.95
2021-09-10 17:00 | 44449.7083 | 0 | 12.9127 | 39.95
2021-09-10 17:30 | 44449.7292 | 0 | 13.129 | 39.95
2021-09-10 18:00 | 44449.75 | 0 | 13.398 | 39.95
2021-09-10 18:30 | 44449.7708 | 0 | 13.6171 | 39.95
2021-09-10 19:00 | 44449.7917 | 0 | 13.401 | 39.95
2021-09-10 19:30 | 44449.8125 | 0 | 13.0173 | 39.95
2021-09-10 20:00 | 44449.8333 | 0 | 12.5147 | 39.95
2021-09-10 20:30 | 44449.8542 | 0 | 12.017 | 39.95
2021-09-10 21:00 | 44449.875 | 0 | 11.5912 | 39.95
2021-09-10 21:30 | 44449.8958 | 0 | 11.354 | 39.95
2021-09-10 22:00 | 44449.9167 | 0 | 10.8004 | 39.95
2021-09-10 22:30 | 44449.9375 | 0 | 9.9226 | 39.95
2021-09-10 23:00 | 44449.9583 | 0 | 9.4419 | 39.95
2021-09-10 23:30 | 44449.9792 | 0 | 8.9485 | 39.95
2021-09-11 | 44450 | 0 | 8.3664 | 39.95
2021-09-11 00:30 | 44450.0208 | 0 | 8.079 | 39.95
2021-09-11 01:00 | 44450.0417 | 0 | 7.9181 | 39.95
2021-09-11 01:30 | 44450.0625 | 0 | 7.7086 | 39.95
2021-09-11 02:00 | 44450.0833 | 0 | 7.5768 | 39.95
2021-09-11 02:30 | 44450.1042 | 0 | 7.4036 | 39.95
2021-09-11 03:00 | 44450.125 | 0 | 7.3752 | 39.95
2021-09-11 03:30 | 44450.1458 | 0 | 7.5315 | 39.95
2021-09-11 04:00 | 44450.1667 | 0 | 7.5092 | 39.95
2021-09-11 04:30 | 44450.1875 | 0 | 7.7018 | 39.95
2021-09-11 05:00 | 44450.2083 | 0 | 8.0506 | 39.95
2021-09-11 05:30 | 44450.2292 | 0 | 8.2209 | 39.95
2021-09-11 06:00 | 44450.25 | 0 | 8.5643 | 39.95
2021-09-11 06:30 | 44450.2708 | 0 | 8.4532 | 39.95
2021-09-11 07:00 | 44450.2917 | 0 | 8.3548 | 39.95
2021-09-11 07:30 | 44450.3125 | 0 | 8.013 | 39.95
2021-09-11 08:00 | 44450.3333 | 0 | 7.7593 | 39.95
2021-09-11 08:30 | 44450.3542 | 0 | 7.3776 | 39.95
2021-09-11 09:00 | 44450.375 | 0 | 7.0022 | 39.95
2021-09-11 09:30 | 44450.3958 | 0 | 6.6927 | 39.95
2021-09-11 10:00 | 44450.4167 | 0 | 6.1976 | 39.95
2021-09-11 10:30 | 44450.4375 | 0 | 6.1421 | 39.95
2021-09-11 11:00 | 44450.4583 | 0 | 5.8403 | 39.95
2021-09-11 11:30 | 44450.4792 | 0 | 5.6221 | 39.95
2021-09-11 12:00 | 44450.5 | 0 | 5.5331 | 39.95
2021-09-11 12:30 | 44450.5208 | 0 | 5.5379 | 39.95
2021-09-11 13:00 | 44450.5417 | 0 | 5.7445 | 39.95
2021-09-11 13:30 | 44450.5625 | 0 | 5.9649 | 39.95
2021-09-11 14:00 | 44450.5833 | 0 | 6.3564 | 39.95
2021-09-11 14:30 | 44450.6042 | 0 | 6.9508 | 39.95
2021-09-11 15:00 | 44450.625 | 0 | 7.6244 | 39.95
2021-09-11 15:30 | 44450.6458 | 0 | 8.3699 | 39.95
2021-09-11 16:00 | 44450.6667 | 0 | 9.1047 | 39.95
2021-09-11 16:30 | 44450.6875 | 0 | 10.0482 | 39.95
2021-09-11 17:00 | 44450.7083 | 0 | 10.6726 | 39.95
2021-09-11 17:30 | 44450.7292 | 0 | 11.0594 | 39.95
2021-09-11 18:00 | 44450.75 | 0 | 11.4675 | 39.95
2021-09-11 18:30 | 44450.7708 | 0 | 11.6797 | 39.95
2021-09-11 19:00 | 44450.7917 | 0 | 11.3212 | 39.95
2021-09-11 19:30 | 44450.8125 | 0 | 11.0046 | 39.95
2021-09-11 20:00 | 44450.8333 | 0 | 10.8585 | 39.95
2021-09-11 20:30 | 44450.8542 | 0 | 10.3817 | 39.95
2021-09-11 21:00 | 44450.875 | 0 | 10.1422 | 39.95
2021-09-11 21:30 | 44450.8958 | 0 | 9.8656 | 39.95
2021-09-11 22:00 | 44450.9167 | 0 | 9.5225 | 39.95
2021-09-11 22:30 | 44450.9375 | 0 | 9.0525 | 39.95
2021-09-11 23:00 | 44450.9583 | 0 | 8.4914 | 39.95
2021-09-11 23:30 | 44450.9792 | 0 | 8.1524 | 39.95
2021-09-12 | 44451 | 0 | 7.7233 | 39.95
2021-09-12 00:30 | 44451.0208 | 0 | 7.4482 | 39.95
2021-09-12 01:00 | 44451.0417 | 0 | 7.2193 | 39.95
2021-09-12 01:30 | 44451.0625 | 0 | 7.1118 | 39.95
2021-09-12 02:00 | 44451.0833 | 0 | 7.1132 | 39.95
2021-09-12 02:30 | 44451.1042 | 0 | 7.074 | 39.95
2021-09-12 03:00 | 44451.125 | 0 | 6.9678 | 39.95
2021-09-12 03:30 | 44451.1458 | 0 | 7.007 | 39.95
2021-09-12 04:00 | 44451.1667 | 0 | 6.8284 | 39.95
2021-09-12 04:30 | 44451.1875 | 0 | 6.9618 | 39.95
2021-09-12 05:00 | 44451.2083 | 0 | 7.0348 | 39.95
2021-09-12 05:30 | 44451.2292 | 0 | 7.1609 | 39.95
2021-09-12 06:00 | 44451.25 | 0 | 7.3161 | 39.95
2021-09-12 06:30 | 44451.2708 | 0 | 7.0517 | 39.95
2021-09-12 07:00 | 44451.2917 | 0 | 6.963 | 39.95
2021-09-12 07:30 | 44451.3125 | 0 | 6.6223 | 39.95
2021-09-12 08:00 | 44451.3333 | 0 | 6.2555 | 39.95
2021-09-12 08:30 | 44451.3542 | 0 | 6.131 | 39.95
2021-09-12 09:00 | 44451.375 | 0 | 5.7677 | 39.95
2021-09-12 09:30 | 44451.3958 | 0 | 5.4556 | 39.95
2021-09-12 10:00 | 44451.4167 | 0 | 5.2705 | 39.95
2021-09-12 10:30 | 44451.4375 | 0 | 5.1376 | 39.95
2021-09-12 11:00 | 44451.4583 | 0 | 4.9862 | 39.95
2021-09-12 11:30 | 44451.4792 | 0 | 4.9742 | 39.95
2021-09-12 12:00 | 44451.5 | 0 | 4.8305 | 39.95
2021-09-12 12:30 | 44451.5208 | 0 | 4.7985 | 39.95
2021-09-12 13:00 | 44451.5417 | 0 | 5.2421 | 39.95
2021-09-12 13:30 | 44451.5625 | 0 | 5.3937 | 39.95
2021-09-12 14:00 | 44451.5833 | 0 | 6.0567 | 39.95
2021-09-12 14:30 | 44451.6042 | 0 | 6.5811 | 39.95
2021-09-12 15:00 | 44451.625 | 0 | 7.1901 | 39.95
2021-09-12 15:30 | 44451.6458 | 0 | 7.9287 | 39.95
2021-09-12 16:00 | 44451.6667 | 0 | 8.8781 | 39.95
2021-09-12 16:30 | 44451.6875 | 0 | 9.9152 | 39.95
2021-09-12 17:00 | 44451.7083 | 0 | 10.6369 | 39.95
2021-09-12 17:30 | 44451.7292 | 0 | 11.2683 | 39.95
2021-09-12 18:00 | 44451.75 | 0 | 11.8289 | 39.95
2021-09-12 18:30 | 44451.7708 | 0 | 12.1435 | 39.95
2021-09-12 19:00 | 44451.7917 | 0 | 11.7982 | 39.95
2021-09-12 19:30 | 44451.8125 | 0 | 11.3599 | 39.95
2021-09-12 20:00 | 44451.8333 | 0 | 11.1023 | 39.95
2021-09-12 20:30 | 44451.8542 | 0 | 10.5127 | 39.95
2021-09-12 21:00 | 44451.875 | 0 | 10.0855 | 39.95
2021-09-12 21:30 | 44451.8958 | 0 | 9.8135 | 39.95
2021-09-12 22:00 | 44451.9167 | 0 | 9.3625 | 39.95
2021-09-12 22:30 | 44451.9375 | 0 | 8.8407 | 39.95
2021-09-12 23:00 | 44451.9583 | 0 | 8.4065 | 39.95
2021-09-12 23:30 | 44451.9792 | 0 | 8.0022 | 39.95
2021-09-13 | 44452 | 0 | 7.5599 | 39.95
2021-09-13 00:30 | 44452.0208 | 0 | 7.4482 | 39.95
2021-09-13 01:00 | 44452.0417 | 0 | 7.2903 | 39.95
2021-09-13 01:30 | 44452.0625 | 0 | 7.2299 | 39.95
2021-09-13 02:00 | 44452.0833 | 0 | 7.1468 | 39.95
2021-09-13 02:30 | 44452.1042 | 0 | 7.0293 | 39.95
2021-09-13 03:00 | 44452.125 | 0 | 7.1758 | 39.95
2021-09-13 03:30 | 44452.1458 | 0 | 7.3915 | 39.95
2021-09-13 04:00 | 44452.1667 | 0 | 7.5778 | 39.95
2021-09-13 04:30 | 44452.1875 | 0 | 7.9928 | 39.95
2021-09-13 05:00 | 44452.2083 | 0 | 8.7074 | 39.95
2021-09-13 05:30 | 44452.2292 | 0 | 9.2576 | 39.95
2021-09-13 06:00 | 44452.25 | 0 | 10.0651 | 39.95
2021-09-13 06:30 | 44452.2708 | 0 | 10.9351 | 39.95
2021-09-13 07:00 | 44452.2917 | 0 | 11.3605 | 39.95
2021-09-13 07:30 | 44452.3125 | 0 | 10.7354 | 39.95
2021-09-13 08:00 | 44452.3333 | 0 | 10.3613 | 39.95
2021-09-13 08:30 | 44452.3542 | 0 | 9.9334 | 39.95
2021-09-13 09:00 | 44452.375 | 0 | 9.6257 | 39.95
2021-09-13 09:30 | 44452.3958 | 0 | 9.3603 | 39.95
2021-09-13 10:00 | 44452.4167 | 0 | 9.0863 | 39.95
2021-09-13 10:30 | 44452.4375 | 0 | 9.1689 | 39.95
2021-09-13 11:00 | 44452.4583 | 0 | 9.4189 | 39.95
2021-09-13 11:30 | 44452.4792 | 0 | 9.3568 | 39.95
2021-09-13 12:00 | 44452.5 | 0 | 9.5016 | 39.95
2021-09-13 12:30 | 44452.5208 | 0 | 10.2152 | 39.95
2021-09-13 13:00 | 44452.5417 | 0 | 13.0984 | 39.95
2021-09-13 13:30 | 44452.5625 | 0 | 11.4928 | 39.95
2021-09-13 14:00 | 44452.5833 | 0 | 11.2201 | 39.95
2021-09-13 14:30 | 44452.6042 | 0 | 13.4209 | 39.95
2021-09-13 15:00 | 44452.625 | 0 | 12.4314 | 39.95
2021-09-13 15:30 | 44452.6458 | 0 | 12.0602 | 39.95
2021-09-13 16:00 | 44452.6667 | 0 | 12.0413 | 39.95
2021-09-13 16:30 | 44452.6875 | 0 | 12.9665 | 39.95
2021-09-13 17:00 | 44452.7083 | 0 | 13.2806 | 39.95
2021-09-13 17:30 | 44452.7292 | 0 | 13.8603 | 39.95
2021-09-13 18:00 | 44452.75 | 0 | 14.3629 | 39.95
2021-09-13 18:30 | 44452.7708 | 0 | 14.7138 | 39.95
2021-09-13 19:00 | 44452.7917 | 0 | 14.311 | 39.95
2021-09-13 19:30 | 44452.8125 | 0 | 13.8557 | 39.95
2021-09-13 20:00 | 44452.8333 | 0 | 13.4655 | 39.95
2021-09-13 20:30 | 44452.8542 | 0 | 12.691 | 39.95
2021-09-13 21:00 | 44452.875 | 0 | 12.2906 | 39.95
2021-09-13 21:30 | 44452.8958 | 0 | 11.9073 | 39.95
2021-09-13 22:00 | 44452.9167 | 0 | 11.0733 | 39.95
2021-09-13 22:30 | 44452.9375 | 0 | 10.1225 | 39.95
2021-09-13 23:00 | 44452.9583 | 0 | 9.3881 | 39.95
2021-09-13 23:30 | 44452.9792 | 0 | 8.9382 | 39.95
2021-09-14 | 44453 | 0 | 8.4242 | 39.95
2021-09-14 00:30 | 44453.0208 | 0 | 7.9754 | 39.95
2021-09-14 01:00 | 44453.0417 | 0 | 7.8973 | 39.95
2021-09-14 01:30 | 44453.0625 | 0 | 7.6601 | 39.95
2021-09-14 02:00 | 44453.0833 | 0 | 7.7142 | 39.95
2021-09-14 02:30 | 44453.1042 | 0 | 7.5877 | 39.95
2021-09-14 03:00 | 44453.125 | 0 | 7.604 | 39.95
2021-09-14 03:30 | 44453.1458 | 0 | 7.7142 | 39.95
2021-09-14 04:00 | 44453.1667 | 0 | 7.8547 | 39.95
2021-09-14 04:30 | 44453.1875 | 0 | 8.365 | 39.95
2021-09-14 05:00 | 44453.2083 | 0 | 8.9859 | 39.95
2021-09-14 05:30 | 44453.2292 | 0 | 9.6482 | 39.95
2021-09-14 06:00 | 44453.25 | 0 | 10.2317 | 39.95
2021-09-14 06:30 | 44453.2708 | 0 | 10.808 | 39.95
2021-09-14 07:00 | 44453.2917 | 0 | 11.0468 | 39.95
2021-09-14 07:30 | 44453.3125 | 0 | 10.4156 | 39.95
2021-09-14 08:00 | 44453.3333 | 0 | 9.6075 | 39.95
2021-09-14 08:30 | 44453.3542 | 0 | 8.9135 | 39.95
2021-09-14 09:00 | 44453.375 | 0 | 8.3013 | 39.95
2021-09-14 09:30 | 44453.3958 | 0 | 7.8441 | 39.95
2021-09-14 10:00 | 44453.4167 | 0 | 7.5211 | 39.95
2021-09-14 10:30 | 44453.4375 | 0 | 7.3311 | 39.95
2021-09-14 11:00 | 44453.4583 | 0 | 6.8586 | 39.95
2021-09-14 11:30 | 44453.4792 | 0 | 6.796 | 39.95
2021-09-14 12:00 | 44453.5 | 0 | 6.873 | 39.95
2021-09-14 12:30 | 44453.5208 | 0 | 6.8507 | 39.95
2021-09-14 13:00 | 44453.5417 | 0 | 7.0636 | 39.95
2021-09-14 13:30 | 44453.5625 | 0 | 7.2321 | 39.95
2021-09-14 14:00 | 44453.5833 | 0 | 7.9329 | 39.95
2021-09-14 14:30 | 44453.6042 | 0 | 8.5952 | 39.95
2021-09-14 15:00 | 44453.625 | 0 | 9.0814 | 39.95
2021-09-14 15:30 | 44453.6458 | 0 | 9.9577 | 39.95
2021-09-14 16:00 | 44453.6667 | 0 | 10.6314 | 39.95
2021-09-14 16:30 | 44453.6875 | 0 | 11.4383 | 39.95
2021-09-14 17:00 | 44453.7083 | 0 | 12.1423 | 39.95
2021-09-14 17:30 | 44453.7292 | 0 | 12.9692 | 39.95
2021-09-14 18:00 | 44453.75 | 0 | 13.5718 | 39.95
2021-09-14 18:30 | 44453.7708 | 0 | 13.9503 | 39.95
2021-09-14 19:00 | 44453.7917 | 0 | 13.7515 | 39.95
2021-09-14 19:30 | 44453.8125 | 0 | 13.4541 | 39.95
2021-09-14 20:00 | 44453.8333 | 0 | 13.1589 | 39.95
2021-09-14 20:30 | 44453.8542 | 0 | 12.4319 | 39.95
2021-09-14 21:00 | 44453.875 | 0 | 11.9503 | 39.95
2021-09-14 21:30 | 44453.8958 | 0 | 11.3454 | 39.95
2021-09-14 22:00 | 44453.9167 | 0 | 10.7278 | 39.95
2021-09-14 22:30 | 44453.9375 | 0 | 9.9093 | 39.95
2021-09-14 23:00 | 44453.9583 | 0 | 9.3311 | 39.95
2021-09-14 23:30 | 44453.9792 | 0 | 8.9337 | 39.95
2021-09-15 | 44454 | 0 | 8.4521 | 39.95
2021-09-15 00:30 | 44454.0208 | 0 | 8.2429 | 39.95
2021-09-15 01:00 | 44454.0417 | 0 | 7.9172 | 39.95
2021-09-15 01:30 | 44454.0625 | 0 | 7.8913 | 39.95
2021-09-15 02:00 | 44454.0833 | 0 | 7.8722 | 39.95
2021-09-15 02:30 | 44454.1042 | 0 | 7.7848 | 39.95
2021-09-15 03:00 | 44454.125 | 0 | 7.785 | 39.95
2021-09-15 03:30 | 44454.1458 | 0 | 7.8438 | 39.95
2021-09-15 04:00 | 44454.1667 | 0 | 8.0428 | 39.95
2021-09-15 04:30 | 44454.1875 | 0 | 8.7295 | 39.95
2021-09-15 05:00 | 44454.2083 | 0 | 9.227 | 39.95
2021-09-15 05:30 | 44454.2292 | 0 | 10.0709 | 39.95
2021-09-15 06:00 | 44454.25 | 0 | 11.1188 | 39.95
2021-09-15 06:30 | 44454.2708 | 0 | 11.4076 | 39.95
2021-09-15 07:00 | 44454.2917 | 0 | 11.5991 | 39.95
2021-09-15 07:30 | 44454.3125 | 0 | 10.998 | 39.95
2021-09-15 08:00 | 44454.3333 | 0 | 10.2411 | 39.95
2021-09-15 08:30 | 44454.3542 | 0 | 9.3041 | 39.95
2021-09-15 09:00 | 44454.375 | 0 | 8.668 | 39.95
2021-09-15 09:30 | 44454.3958 | 0 | 8.1283 | 39.95
2021-09-15 10:00 | 44454.4167 | 0 | 7.7287 | 39.95
2021-09-15 10:30 | 44454.4375 | 0 | 7.4714 | 39.95
2021-09-15 11:00 | 44454.4583 | 0 | 7.3354 | 39.95
2021-09-15 11:30 | 44454.4792 | 0 | 7.4651 | 39.95
2021-09-15 12:00 | 44454.5 | 0 | 7.3535 | 39.95
2021-09-15 12:30 | 44454.5208 | 0 | 7.3746 | 39.95
2021-09-15 13:00 | 44454.5417 | 0 | 7.8193 | 39.95
2021-09-15 13:30 | 44454.5625 | 0 | 8.1464 | 39.95
2021-09-15 14:00 | 44454.5833 | 0 | 8.6225 | 39.95
2021-09-15 14:30 | 44454.6042 | 0 | 9.2702 | 39.95
2021-09-15 15:00 | 44454.625 | 0 | 9.7677 | 39.95
2021-09-15 15:30 | 44454.6458 | 0 | 10.4098 | 39.95
2021-09-15 16:00 | 44454.6667 | 0 | 11.0789 | 39.95
2021-09-15 16:30 | 44454.6875 | 0 | 12.036 | 39.95
2021-09-15 17:00 | 44454.7083 | 0 | 12.5527 | 39.95
2021-09-15 17:30 | 44454.7292 | 0 | 13.2518 | 39.95
2021-09-15 18:00 | 44454.75 | 0 | 13.6676 | 39.95
2021-09-15 18:30 | 44454.7708 | 0 | 13.8774 | 39.95
2021-09-15 19:00 | 44454.7917 | 0 | 13.7098 | 39.95
2021-09-15 19:30 | 44454.8125 | 0 | 13.412 | 39.95
2021-09-15 20:00 | 44454.8333 | 0 | 13.1837 | 39.95
2021-09-15 20:30 | 44454.8542 | 0 | 12.517 | 39.95
2021-09-15 21:00 | 44454.875 | 0 | 12.0592 | 39.95
2021-09-15 21:30 | 44454.8958 | 0 | 11.602 | 39.95
2021-09-15 22:00 | 44454.9167 | 0 | 10.9613 | 39.95
2021-09-15 22:30 | 44454.9375 | 0 | 10.1184 | 39.95
2021-09-15 23:00 | 44454.9583 | 0 | 9.5645 | 39.95
2021-09-15 23:30 | 44454.9792 | 0 | 8.9199 | 39.95
2021-09-16 | 44455 | 0 | 8.4423 | 39.95
2021-09-16 00:30 | 44455.0208 | 0 | 8.1688 | 39.95
2021-09-16 01:00 | 44455.0417 | 0 | 7.9172 | 39.95
2021-09-16 01:30 | 44455.0625 | 0 | 7.8219 | 39.95
2021-09-16 02:00 | 44455.0833 | 0 | 7.7738 | 39.95
2021-09-16 02:30 | 44455.1042 | 0 | 7.8333 | 39.95
2021-09-16 03:00 | 44455.125 | 0 | 7.7458 | 39.95
2021-09-16 03:30 | 44455.1458 | 0 | 7.8492 | 39.95
2021-09-16 04:00 | 44455.1667 | 0 | 8.1653 | 39.95
2021-09-16 04:30 | 44455.1875 | 0 | 8.7355 | 39.95
2021-09-16 05:00 | 44455.2083 | 0 | 9.0486 | 39.95
2021-09-16 05:30 | 44455.2292 | 0 | 9.7742 | 39.95
2021-09-16 06:00 | 44455.25 | 0 | 10.7207 | 39.95
2021-09-16 06:30 | 44455.2708 | 0 | 11.3991 | 39.95
2021-09-16 07:00 | 44455.2917 | 0 | 11.3734 | 39.95
2021-09-16 07:30 | 44455.3125 | 0 | 10.6231 | 39.95
2021-09-16 08:00 | 44455.3333 | 0 | 9.9153 | 39.95
2021-09-16 08:30 | 44455.3542 | 0 | 9.2282 | 39.95
2021-09-16 09:00 | 44455.375 | 0 | 8.7393 | 39.95
2021-09-16 09:30 | 44455.3958 | 0 | 8.4651 | 39.95
2021-09-16 10:00 | 44455.4167 | 0 | 8.0229 | 39.95
2021-09-16 10:30 | 44455.4375 | 0 | 7.9842 | 39.95
2021-09-16 11:00 | 44455.4583 | 0 | 7.6273 | 39.95
2021-09-16 11:30 | 44455.4792 | 0 | 7.9871 | 39.95
2021-09-16 12:00 | 44455.5 | 0 | 8.2309 | 39.95
2021-09-16 12:30 | 44455.5208 | 0 | 8.3324 | 39.95
2021-09-16 13:00 | 44455.5417 | 0 | 8.8588 | 39.95
2021-09-16 13:30 | 44455.5625 | 0 | 8.5258 | 39.95
2021-09-16 14:00 | 44455.5833 | 0 | 9.0561 | 39.95
2021-09-16 14:30 | 44455.6042 | 0 | 9.4169 | 39.95
2021-09-16 15:00 | 44455.625 | 0 | 9.6865 | 39.95
2021-09-16 15:30 | 44455.6458 | 0 | 10.4244 | 39.95
2021-09-16 16:00 | 44455.6667 | 0 | 11.1312 | 39.95
2021-09-16 16:30 | 44455.6875 | 0 | 11.9911 | 39.95
2021-09-16 17:00 | 44455.7083 | 0 | 12.3739 | 39.95
2021-09-16 17:30 | 44455.7292 | 0 | 12.8976 | 39.95
2021-09-16 18:00 | 44455.75 | 0 | 13.5349 | 39.95
2021-09-16 18:30 | 44455.7708 | 0 | 13.7207 | 39.95
2021-09-16 19:00 | 44455.7917 | 0 | 13.4845 | 39.95
2021-09-16 19:30 | 44455.8125 | 0 | 13.4516 | 39.95
2021-09-16 20:00 | 44455.8333 | 0 | 13.0054 | 39.95
2021-09-16 20:30 | 44455.8542 | 0 | 12.4993 | 39.95
2021-09-16 21:00 | 44455.875 | 0 | 12.0056 | 39.95
2021-09-16 21:30 | 44455.8958 | 0 | 11.6824 | 39.95
2021-09-16 22:00 | 44455.9167 | 0 | 11.0164 | 39.95
2021-09-16 22:30 | 44455.9375 | 0 | 10.1916 | 39.95
2021-09-16 23:00 | 44455.9583 | 0 | 9.4941 | 39.95
2021-09-16 23:30 | 44455.9792 | 0 | 9.1087 | 39.95
2021-09-17 | 44456 | 0 | 8.6383 | 39.95
2021-09-17 00:30 | 44456.0208 | 0 | 8.1531 | 39.95
2021-09-17 01:00 | 44456.0417 | 0 | 8.018 | 39.95
2021-09-17 01:30 | 44456.0625 | 0 | 7.7772 | 39.95
2021-09-17 02:00 | 44456.0833 | 0 | 7.7718 | 39.95
2021-09-17 02:30 | 44456.1042 | 0 | 7.7663 | 39.95
2021-09-17 03:00 | 44456.125 | 0 | 7.6305 | 39.95
2021-09-17 03:30 | 44456.1458 | 0 | 7.5539 | 39.95
2021-09-17 04:00 | 44456.1667 | 0 | 7.9095 | 39.95
2021-09-17 04:30 | 44456.1875 | 0 | 8.4375 | 39.95
2021-09-17 05:00 | 44456.2083 | 0 | 8.9524 | 39.95
2021-09-17 05:30 | 44456.2292 | 0 | 9.6228 | 39.95
2021-09-17 06:00 | 44456.25 | 0 | 10.3259 | 39.95
2021-09-17 06:30 | 44456.2708 | 0 | 10.9032 | 39.95
2021-09-17 07:00 | 44456.2917 | 0 | 11.2343 | 39.95
2021-09-17 07:30 | 44456.3125 | 0 | 10.5993 | 39.95
2021-09-17 08:00 | 44456.3333 | 0 | 9.9694 | 39.95
2021-09-17 08:30 | 44456.3542 | 0 | 9.4403 | 39.95
2021-09-17 09:00 | 44456.375 | 0 | 8.8457 | 39.95
2021-09-17 09:30 | 44456.3958 | 0 | 8.5767 | 39.95
2021-09-17 10:00 | 44456.4167 | 0 | 8.3158 | 39.95
2021-09-17 10:30 | 44456.4375 | 0 | 8.561 | 39.95
2021-09-17 11:00 | 44456.4583 | 0 | 8.5347 | 39.95
2021-09-17 11:30 | 44456.4792 | 0 | 8.0685 | 39.95
2021-09-17 12:00 | 44456.5 | 0 | 8.0758 | 39.95
2021-09-17 12:30 | 44456.5208 | 0 | 7.7218 | 39.95
2021-09-17 13:00 | 44456.5417 | 0 | 7.7117 | 39.95
2021-09-17 13:30 | 44456.5625 | 0 | 8.6952 | 39.95
2021-09-17 14:00 | 44456.5833 | 0 | 9.0303 | 39.95
2021-09-17 14:30 | 44456.6042 | 0 | 8.8796 | 39.95
2021-09-17 15:00 | 44456.625 | 0 | 9.5429 | 39.95
2021-09-17 15:30 | 44456.6458 | 0 | 10.2006 | 39.95
2021-09-17 16:00 | 44456.6667 | 0 | 11.0529 | 39.95
2021-09-17 16:30 | 44456.6875 | 0 | 11.8035 | 39.95
2021-09-17 17:00 | 44456.7083 | 0 | 12.1468 | 39.95
2021-09-17 17:30 | 44456.7292 | 0 | 12.5385 | 39.95
2021-09-17 18:00 | 44456.75 | 0 | 12.9627 | 39.95
2021-09-17 18:30 | 44456.7708 | 0 | 13.2155 | 39.95
2021-09-17 19:00 | 44456.7917 | 0 | 12.9519 | 39.95
2021-09-17 19:30 | 44456.8125 | 0 | 12.7097 | 39.95
2021-09-17 20:00 | 44456.8333 | 0 | 12.2781 | 39.95
2021-09-17 20:30 | 44456.8542 | 0 | 11.7898 | 39.95
2021-09-17 21:00 | 44456.875 | 0 | 11.5178 | 39.95
2021-09-17 21:30 | 44456.8958 | 0 | 11.142 | 39.95
2021-09-17 22:00 | 44456.9167 | 0 | 10.6447 | 39.95
2021-09-17 22:30 | 44456.9375 | 0 | 9.9501 | 39.95
2021-09-17 23:00 | 44456.9583 | 0 | 9.5286 | 39.95
2021-09-17 23:30 | 44456.9792 | 0 | 8.9725 | 39.95
2021-09-18 | 44457 | 0 | 8.3321 | 39.95
2021-09-18 00:30 | 44457.0208 | 0 | 8.0174 | 39.95
2021-09-18 01:00 | 44457.0417 | 0 | 7.9196 | 39.95
2021-09-18 01:30 | 44457.0625 | 0 | 7.6581 | 39.95
2021-09-18 02:00 | 44457.0833 | 0 | 7.6824 | 39.95
2021-09-18 02:30 | 44457.1042 | 0 | 7.6547 | 39.95
2021-09-18 03:00 | 44457.125 | 0 | 7.6824 | 39.95
2021-09-18 03:30 | 44457.1458 | 0 | 7.6919 | 39.95
2021-09-18 04:00 | 44457.1667 | 0 | 7.7321 | 39.95
2021-09-18 04:30 | 44457.1875 | 0 | 7.8442 | 39.95
2021-09-18 05:00 | 44457.2083 | 0 | 7.9999 | 39.95
2021-09-18 05:30 | 44457.2292 | 0 | 8.2627 | 39.95
2021-09-18 06:00 | 44457.25 | 0 | 8.4049 | 39.95
2021-09-18 06:30 | 44457.2708 | 0 | 8.4685 | 39.95
2021-09-18 07:00 | 44457.2917 | 0 | 8.5039 | 39.95
2021-09-18 07:30 | 44457.3125 | 0 | 8.082 | 39.95
2021-09-18 08:00 | 44457.3333 | 0 | 7.2829 | 39.95
2021-09-18 08:30 | 44457.3542 | 0 | 6.9624 | 39.95
2021-09-18 09:00 | 44457.375 | 0 | 7.8653 | 39.95
2021-09-18 09:30 | 44457.3958 | 0 | 7.6995 | 39.95
2021-09-18 10:00 | 44457.4167 | 0 | 6.3797 | 39.95
2021-09-18 10:30 | 44457.4375 | 0 | 6.5248 | 39.95
2021-09-18 11:00 | 44457.4583 | 0 | 5.7273 | 39.95
2021-09-18 11:30 | 44457.4792 | 0 | 5.597 | 39.95
2021-09-18 12:00 | 44457.5 | 0 | 5.3128 | 39.95
2021-09-18 12:30 | 44457.5208 | 0 | 5.2323 | 39.95
2021-09-18 13:00 | 44457.5417 | 0 | 5.5666 | 39.95
2021-09-18 13:30 | 44457.5625 | 0 | 6.4717 | 39.95
2021-09-18 14:00 | 44457.5833 | 0 | 7.04 | 39.95
2021-09-18 14:30 | 44457.6042 | 0 | 6.9209 | 39.95
2021-09-18 15:00 | 44457.625 | 0 | 7.1644 | 39.95
2021-09-18 15:30 | 44457.6458 | 0 | 8.0095 | 39.95
2021-09-18 16:00 | 44457.6667 | 0 | 8.3915 | 39.95
2021-09-18 16:30 | 44457.6875 | 0 | 9.8956 | 39.95
2021-09-18 17:00 | 44457.7083 | 0 | 10.3914 | 39.95
2021-09-18 17:30 | 44457.7292 | 0 | 10.7147 | 39.95
2021-09-18 18:00 | 44457.75 | 0 | 11.0989 | 39.95
2021-09-18 18:30 | 44457.7708 | 0 | 11.1663 | 39.95
2021-09-18 19:00 | 44457.7917 | 0 | 10.8124 | 39.95
2021-09-18 19:30 | 44457.8125 | 0 | 10.7494 | 39.95
2021-09-18 20:00 | 44457.8333 | 0 | 10.4839 | 39.95
2021-09-18 20:30 | 44457.8542 | 0 | 10.0721 | 39.95
2021-09-18 21:00 | 44457.875 | 0 | 9.7048 | 39.95
2021-09-18 21:30 | 44457.8958 | 0 | 9.524 | 39.95
2021-09-18 22:00 | 44457.9167 | 0 | 9.3795 | 39.95
2021-09-18 22:30 | 44457.9375 | 0 | 8.9451 | 39.95
2021-09-18 23:00 | 44457.9583 | 0 | 8.6393 | 39.95
2021-09-18 23:30 | 44457.9792 | 0 | 8.2566 | 39.95
2021-09-19 | 44458 | 0 | 7.7064 | 39.95
2021-09-19 00:30 | 44458.0208 | 0 | 7.3704 | 39.95
2021-09-19 01:00 | 44458.0417 | 0 | 7.262 | 39.95
2021-09-19 01:30 | 44458.0625 | 0 | 7.1036 | 39.95
2021-09-19 02:00 | 44458.0833 | 0 | 7.0016 | 39.95
2021-09-19 02:30 | 44458.1042 | 0 | 6.94 | 39.95
2021-09-19 03:00 | 44458.125 | 0 | 6.9455 | 39.95
2021-09-19 03:30 | 44458.1458 | 0 | 6.9286 | 39.95
2021-09-19 04:00 | 44458.1667 | 0 | 6.9007 | 39.95
2021-09-19 04:30 | 44458.1875 | 0 | 6.9902 | 39.95
2021-09-19 05:00 | 44458.2083 | 0 | 7.0626 | 39.95
2021-09-19 05:30 | 44458.2292 | 0 | 7.1589 | 39.95
2021-09-19 06:00 | 44458.25 | 0 | 7.268 | 39.95
2021-09-19 06:30 | 44458.2708 | 0 | 7.074 | 39.95
2021-09-19 07:00 | 44458.2917 | 0 | 6.9901 | 39.95
2021-09-19 07:30 | 44458.3125 | 0 | 6.7619 | 39.95
2021-09-19 08:00 | 44458.3333 | 0 | 6.4149 | 39.95
2021-09-19 08:30 | 44458.3542 | 0 | 6.2129 | 39.95
2021-09-19 09:00 | 44458.375 | 0 | 6.0413 | 39.95
2021-09-19 09:30 | 44458.3958 | 0 | 6.0745 | 39.95
2021-09-19 10:00 | 44458.4167 | 0 | 5.7114 | 39.95
2021-09-19 10:30 | 44458.4375 | 0 | 5.589 | 39.95
2021-09-19 11:00 | 44458.4583 | 0 | 5.422 | 39.95
2021-09-19 11:30 | 44458.4792 | 0 | 5.2983 | 39.95
2021-09-19 12:00 | 44458.5 | 0 | 5.3598 | 39.95
2021-09-19 12:30 | 44458.5208 | 0 | 5.3653 | 39.95
2021-09-19 13:00 | 44458.5417 | 0 | 5.591 | 39.95
2021-09-19 13:30 | 44458.5625 | 0 | 6.0532 | 39.95
2021-09-19 14:00 | 44458.5833 | 0 | 6.5864 | 39.95
2021-09-19 14:30 | 44458.6042 | 0 | 7.0089 | 39.95
2021-09-19 15:00 | 44458.625 | 0 | 7.7976 | 39.95
2021-09-19 15:30 | 44458.6458 | 0 | 8.5722 | 39.95
2021-09-19 16:00 | 44458.6667 | 0 | 9.3938 | 39.95
2021-09-19 16:30 | 44458.6875 | 0 | 10.1537 | 39.95
2021-09-19 17:00 | 44458.7083 | 0 | 10.7118 | 39.95
2021-09-19 17:30 | 44458.7292 | 0 | 11.1367 | 39.95
2021-09-19 18:00 | 44458.75 | 0 | 11.5007 | 39.95
2021-09-19 18:30 | 44458.7708 | 0 | 11.7693 | 39.95
2021-09-19 19:00 | 44458.7917 | 0 | 11.4294 | 39.95
2021-09-19 19:30 | 44458.8125 | 0 | 11.0492 | 39.95
2021-09-19 20:00 | 44458.8333 | 0 | 10.7363 | 39.95
2021-09-19 20:30 | 44458.8542 | 0 | 10.3668 | 39.95
2021-09-19 21:00 | 44458.875 | 0 | 10.0065 | 39.95
2021-09-19 21:30 | 44458.8958 | 0 | 9.7079 | 39.95
2021-09-19 22:00 | 44458.9167 | 0 | 9.1973 | 39.95
2021-09-19 22:30 | 44458.9375 | 0 | 8.56 | 39.95
2021-09-19 23:00 | 44458.9583 | 0 | 8.1802 | 39.95
2021-09-19 23:30 | 44458.9792 | 0 | 7.9051 | 39.95
2021-09-20 | 44459 | 0 | 7.4621 | 39.95
2021-09-20 00:30 | 44459.0208 | 0 | 7.2349 | 39.95
2021-09-20 01:00 | 44459.0417 | 0 | 7.074 | 39.95
2021-09-20 01:30 | 44459.0625 | 0 | 6.9901 | 39.95
2021-09-20 02:00 | 44459.0833 | 0 | 7.0185 | 39.95
2021-09-20 02:30 | 44459.1042 | 0 | 6.867 | 39.95
2021-09-20 03:00 | 44459.125 | 0 | 7.068 | 39.95
2021-09-20 03:30 | 44459.1458 | 0 | 7.276 | 39.95
2021-09-20 04:00 | 44459.1667 | 0 | 7.519 | 39.95
2021-09-20 04:30 | 44459.1875 | 0 | 7.8154 | 39.95
2021-09-20 05:00 | 44459.2083 | 0 | 8.4326 | 39.95
2021-09-20 05:30 | 44459.2292 | 0 | 8.8996 | 39.95
2021-09-20 06:00 | 44459.25 | 0 | 9.6671 | 39.95
2021-09-20 06:30 | 44459.2708 | 0 | 10.4139 | 39.95
2021-09-20 07:00 | 44459.2917 | 0 | 9.9712 | 39.95
2021-09-20 07:30 | 44459.3125 | 0 | 10.1271 | 39.95
2021-09-20 08:00 | 44459.3333 | 0 | 10.093 | 39.95
2021-09-20 08:30 | 44459.3542 | 0 | 9.1381 | 39.95
2021-09-20 09:00 | 44459.375 | 0 | 8.727 | 39.95
2021-09-20 09:30 | 44459.3958 | 0 | 8.6806 | 39.95
2021-09-20 10:00 | 44459.4167 | 0 | 8.2001 | 39.95
2021-09-20 10:30 | 44459.4375 | 0 | 8.4238 | 39.95
2021-09-20 11:00 | 44459.4583 | 0 | 8.4759 | 39.95
2021-09-20 11:30 | 44459.4792 | 0 | 8.5202 | 39.95
2021-09-20 12:00 | 44459.5 | 0 | 8.391 | 39.95
2021-09-20 12:30 | 44459.5208 | 0 | 8.5812 | 39.95
2021-09-20 13:00 | 44459.5417 | 0 | 8.7053 | 39.95
2021-09-20 13:30 | 44459.5625 | 0 | 9.1465 | 39.95
2021-09-20 14:00 | 44459.5833 | 0 | 9.7068 | 39.95
2021-09-20 14:30 | 44459.6042 | 0 | 10.0574 | 39.95
2021-09-20 15:00 | 44459.625 | 0 | 11.1219 | 39.95
2021-09-20 15:30 | 44459.6458 | 0 | 11.6132 | 39.95
2021-09-20 16:00 | 44459.6667 | 0 | 11.8032 | 39.95
2021-09-20 16:30 | 44459.6875 | 0 | 12.5948 | 39.95
2021-09-20 17:00 | 44459.7083 | 0 | 12.8978 | 39.95
2021-09-20 17:30 | 44459.7292 | 0 | 13.5418 | 39.95
2021-09-20 18:00 | 44459.75 | 0 | 13.94 | 39.95
2021-09-20 18:30 | 44459.7708 | 0 | 13.9281 | 39.95
2021-09-20 19:00 | 44459.7917 | 0 | 13.612 | 39.95
2021-09-20 19:30 | 44459.8125 | 0 | 13.1708 | 39.95
2021-09-20 20:00 | 44459.8333 | 0 | 12.9226 | 39.95
2021-09-20 20:30 | 44459.8542 | 0 | 12.235 | 39.95
2021-09-20 21:00 | 44459.875 | 0 | 11.8998 | 39.95
2021-09-20 21:30 | 44459.8958 | 0 | 11.6305 | 39.95
2021-09-20 22:00 | 44459.9167 | 0 | 11.1 | 39.95
2021-09-20 22:30 | 44459.9375 | 0 | 10.3035 | 39.95
2021-09-20 23:00 | 44459.9583 | 0 | 9.6036 | 39.95
2021-09-20 23:30 | 44459.9792 | 0 | 9.1915 | 39.95
2021-09-21 | 44460 | 0 | 8.5991 | 39.95
2021-09-21 00:30 | 44460.0208 | 0 | 8.3674 | 39.95
2021-09-21 01:00 | 44460.0417 | 0 | 8.0725 | 39.95
2021-09-21 01:30 | 44460.0625 | 0 | 7.8128 | 39.95
2021-09-21 02:00 | 44460.0833 | 0 | 7.6738 | 39.95
2021-09-21 02:30 | 44460.1042 | 0 | 7.604 | 39.95
2021-09-21 03:00 | 44460.125 | 0 | 7.6439 | 39.95
2021-09-21 03:30 | 44460.1458 | 0 | 7.6838 | 39.95
2021-09-21 04:00 | 44460.1667 | 0 | 7.8661 | 39.95
2021-09-21 04:30 | 44460.1875 | 0 | 8.2725 | 39.95
2021-09-21 05:00 | 44460.2083 | 0 | 8.8616 | 39.95
2021-09-21 05:30 | 44460.2292 | 0 | 9.4858 | 39.95
2021-09-21 06:00 | 44460.25 | 0 | 10.1102 | 39.95
2021-09-21 06:30 | 44460.2708 | 0 | 10.5718 | 39.95
2021-09-21 07:00 | 44460.2917 | 0 | 10.4993 | 39.95
2021-09-21 07:30 | 44460.3125 | 0 | 10.3811 | 39.95
2021-09-21 08:00 | 44460.3333 | 0 | 10.0386 | 39.95
2021-09-21 08:30 | 44460.3542 | 0 | 9.7302 | 39.95
2021-09-21 09:00 | 44460.375 | 0 | 9.0708 | 39.95
2021-09-21 09:30 | 44460.3958 | 0 | 8.6437 | 39.95
2021-09-21 10:00 | 44460.4167 | 0 | 8.225 | 39.95
2021-09-21 10:30 | 44460.4375 | 0 | 8.1563 | 39.95
2021-09-21 11:00 | 44460.4583 | 0 | 7.7671 | 39.95
2021-09-21 11:30 | 44460.4792 | 0 | 7.6382 | 39.95
2021-09-21 12:00 | 44460.5 | 0 | 7.5176 | 39.95
2021-09-21 12:30 | 44460.5208 | 0 | 7.2855 | 39.95
2021-09-21 13:00 | 44460.5417 | 0 | 7.5961 | 39.95
2021-09-21 13:30 | 44460.5625 | 0 | 8.3234 | 39.95
2021-09-21 14:00 | 44460.5833 | 0 | 8.7687 | 39.95
2021-09-21 14:30 | 44460.6042 | 0 | 9.7081 | 39.95
2021-09-21 15:00 | 44460.625 | 0 | 9.653 | 39.95
2021-09-21 15:30 | 44460.6458 | 0 | 9.7324 | 39.95
2021-09-21 16:00 | 44460.6667 | 0 | 10.6952 | 39.95
2021-09-21 16:30 | 44460.6875 | 0 | 11.7847 | 39.95
2021-09-21 17:00 | 44460.7083 | 0 | 12.4914 | 39.95
2021-09-21 17:30 | 44460.7292 | 0 | 13.0898 | 39.95
2021-09-21 18:00 | 44460.75 | 0 | 13.7117 | 39.95
2021-09-21 18:30 | 44460.7708 | 0 | 14.1381 | 39.95
2021-09-21 19:00 | 44460.7917 | 0 | 13.8052 | 39.95
2021-09-21 19:30 | 44460.8125 | 0 | 13.4913 | 39.95
2021-09-21 20:00 | 44460.8333 | 0 | 13.2046 | 39.95
2021-09-21 20:30 | 44460.8542 | 0 | 12.6824 | 39.95
2021-09-21 21:00 | 44460.875 | 0 | 12.331 | 39.95
2021-09-21 21:30 | 44460.8958 | 0 | 11.8854 | 39.95
2021-09-21 22:00 | 44460.9167 | 0 | 11.1627 | 39.95
2021-09-21 22:30 | 44460.9375 | 0 | 10.291 | 39.95
2021-09-21 23:00 | 44460.9583 | 0 | 9.5366 | 39.95
2021-09-21 23:30 | 44460.9792 | 0 | 9.1797 | 39.95
2021-09-22 | 44461 | 0 | 8.7451 | 39.95
2021-09-22 00:30 | 44461.0208 | 0 | 8.3138 | 39.95
2021-09-22 01:00 | 44461.0417 | 0 | 8.1965 | 39.95
2021-09-22 01:30 | 44461.0625 | 0 | 8.0899 | 39.95
2021-09-22 02:00 | 44461.0833 | 0 | 8.0289 | 39.95
2021-09-22 02:30 | 44461.1042 | 0 | 7.8387 | 39.95
2021-09-22 03:00 | 44461.125 | 0 | 7.9003 | 39.95
2021-09-22 03:30 | 44461.1458 | 0 | 8.0446 | 39.95
2021-09-22 04:00 | 44461.1667 | 0 | 8.3202 | 39.95
2021-09-22 04:30 | 44461.1875 | 0 | 8.6735 | 39.95
2021-09-22 05:00 | 44461.2083 | 0 | 9.336 | 39.95
2021-09-22 05:30 | 44461.2292 | 0 | 10.0357 | 39.95
2021-09-22 06:00 | 44461.25 | 0 | 10.7817 | 39.95
2021-09-22 06:30 | 44461.2708 | 0 | 11.1732 | 39.95
2021-09-22 07:00 | 44461.2917 | 0 | 11.0607 | 39.95
2021-09-22 07:30 | 44461.3125 | 0 | 10.5336 | 39.95
2021-09-22 08:00 | 44461.3333 | 0 | 9.8903 | 39.95
2021-09-22 08:30 | 44461.3542 | 0 | 9.239 | 39.95
2021-09-22 09:00 | 44461.375 | 0 | 8.39 | 39.95
2021-09-22 09:30 | 44461.3958 | 0 | 8.2298 | 39.95
2021-09-22 10:00 | 44461.4167 | 0 | 7.5812 | 39.95
2021-09-22 10:30 | 44461.4375 | 0 | 7.4024 | 39.95
2021-09-22 11:00 | 44461.4583 | 0 | 7.1559 | 39.95
2021-09-22 11:30 | 44461.4792 | 0 | 7.2402 | 39.95
2021-09-22 12:00 | 44461.5 | 0 | 7.2662 | 39.95
2021-09-22 12:30 | 44461.5208 | 0 | 7.5432 | 39.95
2021-09-22 13:00 | 44461.5417 | 0 | 7.6461 | 39.95
2021-09-22 13:30 | 44461.5625 | 0 | 8.0714 | 39.95
2021-09-22 14:00 | 44461.5833 | 0 | 8.8509 | 39.95
2021-09-22 14:30 | 44461.6042 | 0 | 9.4722 | 39.95
2021-09-22 15:00 | 44461.625 | 0 | 9.7384 | 39.95
2021-09-22 15:30 | 44461.6458 | 0 | 10.1698 | 39.95
2021-09-22 16:00 | 44461.6667 | 0 | 10.9563 | 39.95
2021-09-22 16:30 | 44461.6875 | 0 | 11.7928 | 39.95
2021-09-22 17:00 | 44461.7083 | 0 | 12.2661 | 39.95
2021-09-22 17:30 | 44461.7292 | 0 | 12.8456 | 39.95
2021-09-22 18:00 | 44461.75 | 0 | 13.3471 | 39.95
2021-09-22 18:30 | 44461.7708 | 0 | 13.8331 | 39.95
2021-09-22 19:00 | 44461.7917 | 0 | 13.3867 | 39.95
2021-09-22 19:30 | 44461.8125 | 0 | 13.294 | 39.95
2021-09-22 20:00 | 44461.8333 | 0 | 13.0405 | 39.95
2021-09-22 20:30 | 44461.8542 | 0 | 12.6155 | 39.95
2021-09-22 21:00 | 44461.875 | 0 | 12.0784 | 39.95
2021-09-22 21:30 | 44461.8958 | 0 | 11.6382 | 39.95
2021-09-22 22:00 | 44461.9167 | 0 | 10.9044 | 39.95
2021-09-22 22:30 | 44461.9375 | 0 | 10.0641 | 39.95
2021-09-22 23:00 | 44461.9583 | 0 | 9.5594 | 39.95
2021-09-22 23:30 | 44461.9792 | 0 | 9.1969 | 39.95
2021-09-23 | 44462 | 0 | 8.6851 | 39.95
2021-09-23 00:30 | 44462.0208 | 0 | 8.191 | 39.95
2021-09-23 01:00 | 44462.0417 | 0 | 8.1291 | 39.95
2021-09-23 01:30 | 44462.0625 | 0 | 7.9782 | 39.95
2021-09-23 02:00 | 44462.0833 | 0 | 8.0418 | 39.95
2021-09-23 02:30 | 44462.1042 | 0 | 7.8128 | 39.95
2021-09-23 03:00 | 44462.125 | 0 | 7.7138 | 39.95
2021-09-23 03:30 | 44462.1458 | 0 | 7.8997 | 39.95
2021-09-23 04:00 | 44462.1667 | 0 | 8.2625 | 39.95
2021-09-23 04:30 | 44462.1875 | 0 | 8.6749 | 39.95
2021-09-23 05:00 | 44462.2083 | 0 | 9.3539 | 39.95
2021-09-23 05:30 | 44462.2292 | 0 | 9.9962 | 39.95
2021-09-23 06:00 | 44462.25 | 0 | 10.627 | 39.95
2021-09-23 06:30 | 44462.2708 | 0 | 10.8834 | 39.95
2021-09-23 07:00 | 44462.2917 | 0 | 10.8724 | 39.95
2021-09-23 07:30 | 44462.3125 | 0 | 10.4005 | 39.95
2021-09-23 08:00 | 44462.3333 | 0 | 9.8626 | 39.95
2021-09-23 08:30 | 44462.3542 | 0 | 9.2134 | 39.95
2021-09-23 09:00 | 44462.375 | 0 | 8.6236 | 39.95
2021-09-23 09:30 | 44462.3958 | 0 | 8.2511 | 39.95
2021-09-23 10:00 | 44462.4167 | 0 | 7.7845 | 39.95
2021-09-23 10:30 | 44462.4375 | 0 | 7.7707 | 39.95
2021-09-23 11:00 | 44462.4583 | 0 | 7.4645 | 39.95
2021-09-23 11:30 | 44462.4792 | 0 | 7.7118 | 39.95
2021-09-23 12:00 | 44462.5 | 0 | 7.7995 | 39.95
2021-09-23 12:30 | 44462.5208 | 0 | 7.8719 | 39.95
2021-09-23 13:00 | 44462.5417 | 0 | 8.0168 | 39.95
2021-09-23 13:30 | 44462.5625 | 0 | 8.3998 | 39.95
2021-09-23 14:00 | 44462.5833 | 0 | 8.9819 | 39.95
2021-09-23 14:30 | 44462.6042 | 0 | 9.5352 | 39.95
2021-09-23 15:00 | 44462.625 | 0 | 10.1153 | 39.95
2021-09-23 15:30 | 44462.6458 | 0 | 10.6029 | 39.95
2021-09-23 16:00 | 44462.6667 | 0 | 11.4462 | 39.95
2021-09-23 16:30 | 44462.6875 | 0 | 12.1562 | 39.95
2021-09-23 17:00 | 44462.7083 | 0 | 12.5673 | 39.95
2021-09-23 17:30 | 44462.7292 | 0 | 13.1684 | 39.95
2021-09-23 18:00 | 44462.75 | 0 | 13.3857 | 39.95
2021-09-23 18:30 | 44462.7708 | 0 | 13.8107 | 39.95
2021-09-23 19:00 | 44462.7917 | 0 | 13.5638 | 39.95
2021-09-23 19:30 | 44462.8125 | 0 | 13.149 | 39.95
2021-09-23 20:00 | 44462.8333 | 0 | 12.7823 | 39.95
2021-09-23 20:30 | 44462.8542 | 0 | 12.3827 | 39.95
2021-09-23 21:00 | 44462.875 | 0 | 11.8708 | 39.95
2021-09-23 21:30 | 44462.8958 | 0 | 11.4647 | 39.95
2021-09-23 22:00 | 44462.9167 | 0 | 10.9067 | 39.95
2021-09-23 22:30 | 44462.9375 | 0 | 10.0331 | 39.95
2021-09-23 23:00 | 44462.9583 | 0 | 9.4575 | 39.95
2021-09-23 23:30 | 44462.9792 | 0 | 9.0176 | 39.95
2021-09-24 | 44463 | 0 | 8.5624 | 39.95
2021-09-24 00:30 | 44463.0208 | 0 | 8.2506 | 39.95
2021-09-24 01:00 | 44463.0417 | 0 | 8.0398 | 39.95
2021-09-24 01:30 | 44463.0625 | 0 | 8.012 | 39.95
2021-09-24 02:00 | 44463.0833 | 0 | 7.8906 | 39.95
2021-09-24 02:30 | 44463.1042 | 0 | 7.8333 | 39.95
2021-09-24 03:00 | 44463.125 | 0 | 7.8015 | 39.95
2021-09-24 03:30 | 44463.1458 | 0 | 7.9722 | 39.95
2021-09-24 04:00 | 44463.1667 | 0 | 8.2754 | 39.95
2021-09-24 04:30 | 44463.1875 | 0 | 8.5619 | 39.95
2021-09-24 05:00 | 44463.2083 | 0 | 9.0967 | 39.95
2021-09-24 05:30 | 44463.2292 | 0 | 9.4428 | 39.95
2021-09-24 06:00 | 44463.25 | 0 | 10.1662 | 39.95
2021-09-24 06:30 | 44463.2708 | 0 | 10.4024 | 39.95
2021-09-24 07:00 | 44463.2917 | 0 | 10.5559 | 39.95
2021-09-24 07:30 | 44463.3125 | 0 | 10.1685 | 39.95
2021-09-24 08:00 | 44463.3333 | 0 | 9.8513 | 39.95
2021-09-24 08:30 | 44463.3542 | 0 | 9.4312 | 39.95
2021-09-24 09:00 | 44463.375 | 0 | 8.9729 | 39.95
2021-09-24 09:30 | 44463.3958 | 0 | 8.7521 | 39.95
2021-09-24 10:00 | 44463.4167 | 0 | 8.3713 | 39.95
2021-09-24 10:30 | 44463.4375 | 0 | 8.3639 | 39.95
2021-09-24 11:00 | 44463.4583 | 0 | 8.1494 | 39.95
2021-09-24 11:30 | 44463.4792 | 0 | 8.3132 | 39.95
2021-09-24 12:00 | 44463.5 | 0 | 8.2675 | 39.95
2021-09-24 12:30 | 44463.5208 | 0 | 8.1808 | 39.95
2021-09-24 13:00 | 44463.5417 | 0 | 8.3017 | 39.95
2021-09-24 13:30 | 44463.5625 | 0 | 8.5172 | 39.95
2021-09-24 14:00 | 44463.5833 | 0 | 9.0837 | 39.95
2021-09-24 14:30 | 44463.6042 | 0 | 9.6263 | 39.95
2021-09-24 15:00 | 44463.625 | 0 | 10.1005 | 39.95
2021-09-24 15:30 | 44463.6458 | 0 | 10.8374 | 39.95
2021-09-24 16:00 | 44463.6667 | 0 | 11.5466 | 39.95
2021-09-24 16:30 | 44463.6875 | 0 | 12.1842 | 39.95
2021-09-24 17:00 | 44463.7083 | 0 | 12.4974 | 39.95
2021-09-24 17:30 | 44463.7292 | 0 | 12.7916 | 39.95
2021-09-24 18:00 | 44463.75 | 0 | 13.1425 | 39.95
2021-09-24 18:30 | 44463.7708 | 0 | 13.3053 | 39.95
2021-09-24 19:00 | 44463.7917 | 0 | 12.9097 | 39.95
2021-09-24 19:30 | 44463.8125 | 0 | 12.7079 | 39.95
2021-09-24 20:00 | 44463.8333 | 0 | 12.246 | 39.95
2021-09-24 20:30 | 44463.8542 | 0 | 11.7763 | 39.95
2021-09-24 21:00 | 44463.875 | 0 | 11.3451 | 39.95
2021-09-24 21:30 | 44463.8958 | 0 | 11.0885 | 39.95
2021-09-24 22:00 | 44463.9167 | 0 | 10.7466 | 39.95
2021-09-24 22:30 | 44463.9375 | 0 | 10.0732 | 39.95
2021-09-24 23:00 | 44463.9583 | 0 | 9.4992 | 39.95
2021-09-24 23:30 | 44463.9792 | 0 | 9.0067 | 39.95
2021-09-25 | 44464 | 0 | 8.3765 | 39.95
2021-09-25 00:30 | 44464.0208 | 0 | 8.1554 | 39.95
2021-09-25 01:00 | 44464.0417 | 0 | 7.8869 | 39.95
2021-09-25 01:30 | 44464.0625 | 0 | 7.8388 | 39.95
2021-09-25 02:00 | 44464.0833 | 0 | 7.6714 | 39.95
2021-09-25 02:30 | 44464.1042 | 0 | 7.6547 | 39.95
2021-09-25 03:00 | 44464.125 | 0 | 7.6046 | 39.95
2021-09-25 03:30 | 44464.1458 | 0 | 7.5985 | 39.95
2021-09-25 04:00 | 44464.1667 | 0 | 7.7279 | 39.95
2021-09-25 04:30 | 44464.1875 | 0 | 7.9891 | 39.95
2021-09-25 05:00 | 44464.2083 | 0 | 8.0735 | 39.95
2021-09-25 05:30 | 44464.2292 | 0 | 8.0675 | 39.95
2021-09-25 06:00 | 44464.25 | 0 | 8.1385 | 39.95
2021-09-25 06:30 | 44464.2708 | 0 | 7.9788 | 39.95
2021-09-25 07:00 | 44464.2917 | 0 | 7.6303 | 39.95
2021-09-25 07:30 | 44464.3125 | 0 | 7.3259 | 39.95
2021-09-25 08:00 | 44464.3333 | 0 | 7.3496 | 39.95
2021-09-25 08:30 | 44464.3542 | 0 | 7.3567 | 39.95
2021-09-25 09:00 | 44464.375 | 0 | 7.493 | 39.95
2021-09-25 09:30 | 44464.3958 | 0 | 7.2109 | 39.95
2021-09-25 10:00 | 44464.4167 | 0 | 6.4233 | 39.95
2021-09-25 10:30 | 44464.4375 | 0 | 6.4489 | 39.95
2021-09-25 11:00 | 44464.4583 | 0 | 6.5094 | 39.95
2021-09-25 11:30 | 44464.4792 | 0 | 6.4214 | 39.95
2021-09-25 12:00 | 44464.5 | 0 | 7.3368 | 39.95
2021-09-25 12:30 | 44464.5208 | 0 | 8.6162 | 39.95
2021-09-25 13:00 | 44464.5417 | 0 | 8.7451 | 39.95
2021-09-25 13:30 | 44464.5625 | 0 | 8.6714 | 39.95
2021-09-25 14:00 | 44464.5833 | 0 | 6.8207 | 39.95
2021-09-25 14:30 | 44464.6042 | 0 | 8.1111 | 39.95
2021-09-25 15:00 | 44464.625 | 0 | 8.2015 | 39.95
2021-09-25 15:30 | 44464.6458 | 0 | 9.2909 | 39.95
2021-09-25 16:00 | 44464.6667 | 0 | 10.4801 | 39.95
2021-09-25 16:30 | 44464.6875 | 0 | 10.4567 | 39.95
2021-09-25 17:00 | 44464.7083 | 0 | 10.6412 | 39.95
2021-09-25 17:30 | 44464.7292 | 0 | 10.8781 | 39.95
2021-09-25 18:00 | 44464.75 | 0 | 11.1386 | 39.95
2021-09-25 18:30 | 44464.7708 | 0 | 11.141 | 39.95
2021-09-25 19:00 | 44464.7917 | 0 | 10.7738 | 39.95
2021-09-25 19:30 | 44464.8125 | 0 | 10.6839 | 39.95
2021-09-25 20:00 | 44464.8333 | 0 | 10.5748 | 39.95
2021-09-25 20:30 | 44464.8542 | 0 | 10.3464 | 39.95
2021-09-25 21:00 | 44464.875 | 0 | 10.0225 | 39.95
2021-09-25 21:30 | 44464.8958 | 0 | 9.9068 | 39.95
2021-09-25 22:00 | 44464.9167 | 0 | 9.6288 | 39.95
2021-09-25 22:30 | 44464.9375 | 0 | 9.0758 | 39.95
2021-09-25 23:00 | 44464.9583 | 0 | 8.6878 | 39.95
2021-09-25 23:30 | 44464.9792 | 0 | 8.3777 | 39.95
2021-09-26 | 44465 | 0 | 7.8955 | 39.95
2021-09-26 00:30 | 44465.0208 | 0 | 7.6383 | 39.95
2021-09-26 01:00 | 44465.0417 | 0 | 7.4205 | 39.95
2021-09-26 01:30 | 44465.0625 | 0 | 7.3474 | 39.95
2021-09-26 02:00 | 44465.0833 | 0 | 7.275 | 39.95
2021-09-26 02:30 | 44465.1042 | 0 | 7.2193 | 39.95
2021-09-26 03:00 | 44465.125 | 0 | 7.1187 | 39.95
2021-09-26 03:30 | 44465.1458 | 0 | 7.1782 | 39.95
2021-09-26 04:00 | 44465.1667 | 0 | 7.0736 | 39.95
2021-09-26 04:30 | 44465.1875 | 0 | 7.0794 | 39.95
2021-09-26 05:00 | 44465.2083 | 0 | 7.1519 | 39.95
2021-09-26 05:30 | 44465.2292 | 0 | 7.3059 | 39.95
2021-09-26 06:00 | 44465.25 | 0 | 7.8388 | 39.95
2021-09-26 06:30 | 44465.2708 | 0 | 7.8015 | 39.95
2021-09-26 07:00 | 44465.2917 | 0 | 7.2703 | 39.95
2021-09-26 07:30 | 44465.3125 | 0 | 7.0165 | 39.95
2021-09-26 08:00 | 44465.3333 | 0 | 6.7128 | 39.95
2021-09-26 08:30 | 44465.3542 | 0 | 7.2294 | 39.95
2021-09-26 09:00 | 44465.375 | 0 | 8.5711 | 39.95
2021-09-26 09:30 | 44465.3958 | 0 | 8.5824 | 39.95
2021-09-26 10:00 | 44465.4167 | 0 | 7.1843 | 39.95
2021-09-26 10:30 | 44465.4375 | 0 | 6.8501 | 39.95
2021-09-26 11:00 | 44465.4583 | 0 | 6.6692 | 39.95
2021-09-26 11:30 | 44465.4792 | 0 | 7.4043 | 39.95
2021-09-26 12:00 | 44465.5 | 0 | 7.5832 | 39.95
2021-09-26 12:30 | 44465.5208 | 0 | 7.985 | 39.95
2021-09-26 13:00 | 44465.5417 | 0 | 7.8268 | 39.95
2021-09-26 13:30 | 44465.5625 | 0 | 7.9806 | 39.95
2021-09-26 14:00 | 44465.5833 | 0 | 8.6279 | 39.95
2021-09-26 14:30 | 44465.6042 | 0 | 8.885 | 39.95
2021-09-26 15:00 | 44465.625 | 0 | 9.1007 | 39.95
2021-09-26 15:30 | 44465.6458 | 0 | 9.522 | 39.95
2021-09-26 16:00 | 44465.6667 | 0 | 10.0825 | 39.95
2021-09-26 16:30 | 44465.6875 | 0 | 10.3589 | 39.95
2021-09-26 17:00 | 44465.7083 | 0 | 10.9261 | 39.95
2021-09-26 17:30 | 44465.7292 | 0 | 11.2595 | 39.95
2021-09-26 18:00 | 44465.75 | 0 | 11.5236 | 39.95
2021-09-26 18:30 | 44465.7708 | 0 | 11.5876 | 39.95
2021-09-26 19:00 | 44465.7917 | 0 | 11.2015 | 39.95
2021-09-26 19:30 | 44465.8125 | 0 | 10.869 | 39.95
2021-09-26 20:00 | 44465.8333 | 0 | 10.6086 | 39.95
2021-09-26 20:30 | 44465.8542 | 0 | 10.121 | 39.95
2021-09-26 21:00 | 44465.875 | 0 | 9.8139 | 39.95
2021-09-26 21:30 | 44465.8958 | 0 | 9.5549 | 39.95
2021-09-26 22:00 | 44465.9167 | 0 | 9.0419 | 39.95
2021-09-26 22:30 | 44465.9375 | 0 | 8.6101 | 39.95
2021-09-26 23:00 | 44465.9583 | 0 | 8.1407 | 39.95
2021-09-26 23:30 | 44465.9792 | 0 | 7.7931 | 39.95
2021-09-27 | 44466 | 0 | 7.5283 | 39.95
2021-09-27 00:30 | 44466.0208 | 0 | 7.3311 | 39.95
2021-09-27 01:00 | 44466.0417 | 0 | 7.2436 | 39.95
2021-09-27 01:30 | 44466.0625 | 0 | 7.1018 | 39.95
2021-09-27 02:00 | 44466.0833 | 0 | 7.1668 | 39.95
2021-09-27 02:30 | 44466.1042 | 0 | 7.1724 | 39.95
2021-09-27 03:00 | 44466.125 | 0 | 7.1577 | 39.95
2021-09-27 03:30 | 44466.1458 | 0 | 7.3857 | 39.95
2021-09-27 04:00 | 44466.1667 | 0 | 7.6647 | 39.95
2021-09-27 04:30 | 44466.1875 | 0 | 8.0392 | 39.95
2021-09-27 05:00 | 44466.2083 | 0 | 8.4605 | 39.95
2021-09-27 05:30 | 44466.2292 | 0 | 9.0842 | 39.95
2021-09-27 06:00 | 44466.25 | 0 | 9.9113 | 39.95
2021-09-27 06:30 | 44466.2708 | 0 | 10.4356 | 39.95
2021-09-27 07:00 | 44466.2917 | 0 | 11.7682 | 39.95
2021-09-27 07:30 | 44466.3125 | 0 | 11.744 | 39.95
2021-09-27 08:00 | 44466.3333 | 0 | 11.4452 | 39.95
2021-09-27 08:30 | 44466.3542 | 0 | 11.1332 | 39.95
2021-09-27 09:00 | 44466.375 | 0 | 11.1595 | 39.95
2021-09-27 09:30 | 44466.3958 | 0 | 11.7506 | 39.95
2021-09-27 10:00 | 44466.4167 | 0 | 11.9688 | 39.95
2021-09-27 10:30 | 44466.4375 | 0 | 11.1953 | 39.95
2021-09-27 11:00 | 44466.4583 | 0 | 11.4164 | 39.95
2021-09-27 11:30 | 44466.4792 | 0 | 11.4691 | 39.95
2021-09-27 12:00 | 44466.5 | 0 | 11.4538 | 39.95
2021-09-27 12:30 | 44466.5208 | 0 | 11.4875 | 39.95
2021-09-27 13:00 | 44466.5417 | 0 | 11.5444 | 39.95
2021-09-27 13:30 | 44466.5625 | 0 | 11.7138 | 39.95
2021-09-27 14:00 | 44466.5833 | 0 | 11.6999 | 39.95
2021-09-27 14:30 | 44466.6042 | 0 | 11.7341 | 39.95
2021-09-27 15:00 | 44466.625 | 0 | 11.2667 | 39.95
2021-09-27 15:30 | 44466.6458 | 0 | 11.5635 | 39.95
2021-09-27 16:00 | 44466.6667 | 0 | 11.5599 | 39.95
2021-09-27 16:30 | 44466.6875 | 0 | 12.2142 | 39.95
2021-09-27 17:00 | 44466.7083 | 0 | 12.6403 | 39.95
2021-09-27 17:30 | 44466.7292 | 0 | 13.1514 | 39.95
2021-09-27 18:00 | 44466.75 | 0 | 13.6006 | 39.95
2021-09-27 18:30 | 44466.7708 | 0 | 13.7291 | 39.95
2021-09-27 19:00 | 44466.7917 | 0 | 13.2991 | 39.95
2021-09-27 19:30 | 44466.8125 | 0 | 12.8413 | 39.95
2021-09-27 20:00 | 44466.8333 | 0 | 12.8453 | 39.95
2021-09-27 20:30 | 44466.8542 | 0 | 12.0782 | 39.95
2021-09-27 21:00 | 44466.875 | 0 | 11.6046 | 39.95
2021-09-27 21:30 | 44466.8958 | 0 | 11.217 | 39.95
2021-09-27 22:00 | 44466.9167 | 0 | 10.5984 | 39.95
2021-09-27 22:30 | 44466.9375 | 0 | 9.75 | 39.95
2021-09-27 23:00 | 44466.9583 | 0 | 9.1447 | 39.95
2021-09-27 23:30 | 44466.9792 | 0 | 8.6359 | 39.95
2021-09-28 | 44467 | 0 | 8.1846 | 39.95
2021-09-28 00:30 | 44467.0208 | 0 | 7.945 | 39.95
2021-09-28 01:00 | 44467.0417 | 0 | 7.8188 | 39.95
2021-09-28 01:30 | 44467.0625 | 0 | 7.6824 | 39.95
2021-09-28 02:00 | 44467.0833 | 0 | 7.6547 | 39.95
2021-09-28 02:30 | 44467.1042 | 0 | 7.6046 | 39.95
2021-09-28 03:00 | 44467.125 | 0 | 7.5038 | 39.95
2021-09-28 03:30 | 44467.1458 | 0 | 7.6185 | 39.95
2021-09-28 04:00 | 44467.1667 | 0 | 7.8828 | 39.95
2021-09-28 04:30 | 44467.1875 | 0 | 8.407 | 39.95
2021-09-28 05:00 | 44467.2083 | 0 | 8.9506 | 39.95
2021-09-28 05:30 | 44467.2292 | 0 | 9.5373 | 39.95
2021-09-28 06:00 | 44467.25 | 0 | 10.0147 | 39.95
2021-09-28 06:30 | 44467.2708 | 0 | 10.8302 | 39.95
2021-09-28 07:00 | 44467.2917 | 0 | 11.7856 | 39.95
2021-09-28 07:30 | 44467.3125 | 0 | 11.5239 | 39.95
2021-09-28 08:00 | 44467.3333 | 0 | 11.0651 | 39.95
2021-09-28 08:30 | 44467.3542 | 0 | 11.7578 | 39.95
2021-09-28 09:00 | 44467.375 | 0 | 11.9013 | 39.95
2021-09-28 09:30 | 44467.3958 | 0 | 11.095 | 39.95
2021-09-28 10:00 | 44467.4167 | 0 | 10.3068 | 39.95
2021-09-28 10:30 | 44467.4375 | 0 | 11.2254 | 39.95
2021-09-28 11:00 | 44467.4583 | 0 | 10.68 | 39.95
2021-09-28 11:30 | 44467.4792 | 0 | 8.5178 | 39.95
2021-09-28 12:00 | 44467.5 | 0 | 9.8237 | 39.95
2021-09-28 12:30 | 44467.5208 | 0 | 9.7863 | 39.95
2021-09-28 13:00 | 44467.5417 | 0 | 10.5277 | 39.95
2021-09-28 13:30 | 44467.5625 | 0 | 10.86 | 39.95
2021-09-28 14:00 | 44467.5833 | 0 | 11.5976 | 39.95
2021-09-28 14:30 | 44467.6042 | 0 | 11.1709 | 39.95
2021-09-28 15:00 | 44467.625 | 0 | 10.6335 | 39.95
2021-09-28 15:30 | 44467.6458 | 0 | 10.6809 | 39.95
2021-09-28 16:00 | 44467.6667 | 0 | 11.0804 | 39.95
2021-09-28 16:30 | 44467.6875 | 0 | 11.6715 | 39.95
2021-09-28 17:00 | 44467.7083 | 0 | 12.1121 | 39.95
2021-09-28 17:30 | 44467.7292 | 0 | 12.8763 | 39.95
2021-09-28 18:00 | 44467.75 | 0 | 13.403 | 39.95
2021-09-28 18:30 | 44467.7708 | 0 | 13.6638 | 39.95
2021-09-28 19:00 | 44467.7917 | 0 | 13.1904 | 39.95
2021-09-28 19:30 | 44467.8125 | 0 | 12.9495 | 39.95
2021-09-28 20:00 | 44467.8333 | 0 | 12.6477 | 39.95
2021-09-28 20:30 | 44467.8542 | 0 | 12.2723 | 39.95
2021-09-28 21:00 | 44467.875 | 0 | 11.6884 | 39.95
2021-09-28 21:30 | 44467.8958 | 0 | 11.3314 | 39.95
2021-09-28 22:00 | 44467.9167 | 0 | 10.6727 | 39.95
2021-09-28 22:30 | 44467.9375 | 0 | 9.8202 | 39.95
2021-09-28 23:00 | 44467.9583 | 0 | 9.2574 | 39.95
2021-09-28 23:30 | 44467.9792 | 0 | 8.8427 | 39.95
2021-09-29 | 44468 | 0 | 8.3792 | 39.95
2021-09-29 00:30 | 44468.0208 | 0 | 8.0844 | 39.95
2021-09-29 01:00 | 44468.0417 | 0 | 7.7758 | 39.95
2021-09-29 01:30 | 44468.0625 | 0 | 7.7048 | 39.95
2021-09-29 02:00 | 44468.0833 | 0 | 7.6601 | 39.95
2021-09-29 02:30 | 44468.1042 | 0 | 7.7867 | 39.95
2021-09-29 03:00 | 44468.125 | 0 | 7.6269 | 39.95
2021-09-29 03:30 | 44468.1458 | 0 | 7.7227 | 39.95
2021-09-29 04:00 | 44468.1667 | 0 | 7.9553 | 39.95
2021-09-29 04:30 | 44468.1875 | 0 | 8.3763 | 39.95
2021-09-29 05:00 | 44468.2083 | 0 | 8.9971 | 39.95
2021-09-29 05:30 | 44468.2292 | 0 | 9.5614 | 39.95
2021-09-29 06:00 | 44468.25 | 0 | 10.085 | 39.95
2021-09-29 06:30 | 44468.2708 | 0 | 11.3013 | 39.95
2021-09-29 07:00 | 44468.2917 | 0 | 11.3995 | 39.95
2021-09-29 07:30 | 44468.3125 | 0 | 11.1603 | 39.95
2021-09-29 08:00 | 44468.3333 | 0 | 10.9319 | 39.95
2021-09-29 08:30 | 44468.3542 | 0 | 10.27 | 39.95
2021-09-29 09:00 | 44468.375 | 0 | 10.8557 | 39.95
2021-09-29 09:30 | 44468.3958 | 0 | 11.473 | 39.95
2021-09-29 10:00 | 44468.4167 | 0 | 11.4001 | 39.95
2021-09-29 10:30 | 44468.4375 | 0 | 10.8018 | 39.95
2021-09-29 11:00 | 44468.4583 | 0 | 9.1431 | 39.95
2021-09-29 11:30 | 44468.4792 | 0 | 7.6923 | 39.95
2021-09-29 12:00 | 44468.5 | 0 | 7.9425 | 39.95
2021-09-29 12:30 | 44468.5208 | 0 | 9.2369 | 39.95
2021-09-29 13:00 | 44468.5417 | 0 | 10.201 | 39.95
2021-09-29 13:30 | 44468.5625 | 0 | 9.864 | 39.95
2021-09-29 14:00 | 44468.5833 | 0 | 10.31 | 39.95
2021-09-29 14:30 | 44468.6042 | 0 | 9.8653 | 39.95
2021-09-29 15:00 | 44468.625 | 0 | 11.0137 | 39.95
2021-09-29 15:30 | 44468.6458 | 0 | 11.9222 | 39.95
2021-09-29 16:00 | 44468.6667 | 0 | 11.8705 | 39.95
2021-09-29 16:30 | 44468.6875 | 0 | 12.1381 | 39.95
2021-09-29 17:00 | 44468.7083 | 0 | 12.0705 | 39.95
2021-09-29 17:30 | 44468.7292 | 0 | 12.579 | 39.95
2021-09-29 18:00 | 44468.75 | 0 | 12.7302 | 39.95
2021-09-29 18:30 | 44468.7708 | 0 | 12.7628 | 39.95
2021-09-29 19:00 | 44468.7917 | 0 | 12.627 | 39.95
2021-09-29 19:30 | 44468.8125 | 0 | 12.0902 | 39.95
2021-09-29 20:00 | 44468.8333 | 0 | 11.7584 | 39.95
2021-09-29 20:30 | 44468.8542 | 0 | 11.3444 | 39.95
2021-09-29 21:00 | 44468.875 | 0 | 10.6995 | 39.95
2021-09-29 21:30 | 44468.8958 | 0 | 10.535 | 39.95
2021-09-29 22:00 | 44468.9167 | 0 | 10.2534 | 39.95
2021-09-29 22:30 | 44468.9375 | 0 | 9.539 | 39.95
2021-09-29 23:00 | 44468.9583 | 0 | 8.8775 | 39.95
2021-09-29 23:30 | 44468.9792 | 0 | 8.5667 | 39.95
2021-09-30 | 44469 | 0 | 8.0015 | 39.95
2021-09-30 00:30 | 44469.0208 | 0 | 7.8671 | 39.95
2021-09-30 01:00 | 44469.0417 | 0 | 7.6854 | 39.95
2021-09-30 01:30 | 44469.0625 | 0 | 7.5708 | 39.95
2021-09-30 02:00 | 44469.0833 | 0 | 7.5877 | 39.95
2021-09-30 02:30 | 44469.1042 | 0 | 7.4259 | 39.95
2021-09-30 03:00 | 44469.125 | 0 | 7.3366 | 39.95
2021-09-30 03:30 | 44469.1458 | 0 | 7.4476 | 39.95
2021-09-30 04:00 | 44469.1667 | 0 | 7.5623 | 39.95
2021-09-30 04:30 | 44469.1875 | 0 | 8.0769 | 39.95
2021-09-30 05:00 | 44469.2083 | 0 | 8.5463 | 39.95
2021-09-30 05:30 | 44469.2292 | 0 | 9.1057 | 39.95
2021-09-30 06:00 | 44469.25 | 0 | 9.424 | 39.95
2021-09-30 06:30 | 44469.2708 | 0 | 10.1927 | 39.95
2021-09-30 07:00 | 44469.2917 | 0 | 10.5432 | 39.95
2021-09-30 07:30 | 44469.3125 | 0 | 10.8243 | 39.95
2021-09-30 08:00 | 44469.3333 | 0 | 10.6726 | 39.95
2021-09-30 08:30 | 44469.3542 | 0 | 11.4526 | 39.95
2021-09-30 09:00 | 44469.375 | 0 | 11.0342 | 39.95
2021-09-30 09:30 | 44469.3958 | 0 | 9.1096 | 39.95
2021-09-30 10:00 | 44469.4167 | 0 | 9.4052 | 39.95
2021-09-30 10:30 | 44469.4375 | 0 | 9.2758 | 39.95
2021-09-30 11:00 | 44469.4583 | 0 | 8.9948 | 39.95
2021-09-30 11:30 | 44469.4792 | 0 | 10.154 | 39.95
2021-09-30 12:00 | 44469.5 | 0 | 8.6336 | 39.95
2021-09-30 12:30 | 44469.5208 | 0 | 10.4192 | 39.95
2021-09-30 13:00 | 44469.5417 | 0 | 10.1634 | 39.95
2021-09-30 13:30 | 44469.5625 | 0 | 9.4829 | 39.95
2021-09-30 14:00 | 44469.5833 | 0 | 11.7235 | 39.95
2021-09-30 14:30 | 44469.6042 | 0 | 11.6846 | 39.95
2021-09-30 15:00 | 44469.625 | 0 | 11.2186 | 39.95
2021-09-30 15:30 | 44469.6458 | 0 | 10.9407 | 39.95
2021-09-30 16:00 | 44469.6667 | 0 | 12.1927 | 39.95
2021-09-30 16:30 | 44469.6875 | 0 | 12.893 | 39.95
2021-09-30 17:00 | 44469.7083 | 0 | 12.7103 | 39.95
2021-09-30 17:30 | 44469.7292 | 0 | 12.6675 | 39.95
2021-09-30 18:00 | 44469.75 | 0 | 12.5793 | 39.95
2021-09-30 18:30 | 44469.7708 | 0 | 12.8338 | 39.95
2021-09-30 19:00 | 44469.7917 | 0 | 12.663 | 39.95
2021-09-30 19:30 | 44469.8125 | 0 | 12.3861 | 39.95
2021-09-30 20:00 | 44469.8333 | 0 | 11.9818 | 39.95
2021-09-30 20:30 | 44469.8542 | 0 | 11.3814 | 39.95
2021-09-30 21:00 | 44469.875 | 0 | 10.8927 | 39.95
2021-09-30 21:30 | 44469.8958 | 0 | 10.7961 | 39.95
2021-09-30 22:00 | 44469.9167 | 0 | 10.4513 | 39.95
2021-09-30 22:30 | 44469.9375 | 0 | 9.8754 | 39.95
2021-09-30 23:00 | 44469.9583 | 0 | 9.2842 | 39.95
2021-09-30 23:30 | 44469.9792 | 0 | 8.8656 | 39.95
2021-10-01 | 44470 | 0 | 8.3351 | 39.95
2021-10-01 00:30 | 44470.0208 | 0 | 7.9171 | 39.95
2021-10-01 01:00 | 44470.0417 | 0 | 7.8581 | 39.95
2021-10-01 01:30 | 44470.0625 | 0 | 7.5261 | 39.95
2021-10-01 02:00 | 44470.0833 | 0 | 7.5653 | 39.95
2021-10-01 02:30 | 44470.1042 | 0 | 7.409 | 39.95
2021-10-01 03:00 | 44470.125 | 0 | 7.324 | 39.95
2021-10-01 03:30 | 44470.1458 | 0 | 7.414 | 39.95
2021-10-01 04:00 | 44470.1667 | 0 | 7.4852 | 39.95
2021-10-01 04:30 | 44470.1875 | 0 | 7.9607 | 39.95
2021-10-01 05:00 | 44470.2083 | 0 | 8.5859 | 39.95
2021-10-01 05:30 | 44470.2292 | 0 | 8.7391 | 39.95
2021-10-01 06:00 | 44470.25 | 0 | 9.2454 | 39.95
2021-10-01 06:30 | 44470.2708 | 0 | 10.0859 | 39.95
2021-10-01 07:00 | 44470.2917 | 0 | 10.3447 | 39.95
2021-10-01 07:30 | 44470.3125 | 0 | 10.8341 | 39.95
2021-10-01 08:00 | 44470.3333 | 0 | 11.7764 | 39.95
2021-10-01 08:30 | 44470.3542 | 0 | 11.7283 | 39.95
2021-10-01 09:00 | 44470.375 | 0 | 11.0945 | 39.95
2021-10-01 09:30 | 44470.3958 | 0 | 10.1484 | 39.95
2021-10-01 10:00 | 44470.4167 | 0 | 10.9455 | 39.95
2021-10-01 10:30 | 44470.4375 | 0 | 11.0995 | 39.95
2021-10-01 11:00 | 44470.4583 | 0 | 10.9156 | 39.95
2021-10-01 11:30 | 44470.4792 | 0 | 10.9673 | 39.95
2021-10-01 12:00 | 44470.5 | 0 | 9.284 | 39.95
2021-10-01 12:30 | 44470.5208 | 0 | 7.7753 | 39.95
2021-10-01 13:00 | 44470.5417 | 0 | 8.5328 | 39.95
2021-10-01 13:30 | 44470.5625 | 0 | 9.4333 | 39.95
2021-10-01 14:00 | 44470.5833 | 0 | 8.5446 | 39.95
2021-10-01 14:30 | 44470.6042 | 0 | 9.0477 | 39.95
2021-10-01 15:00 | 44470.625 | 0 | 9.2769 | 39.95
2021-10-01 15:30 | 44470.6458 | 0 | 9.9193 | 39.95
2021-10-01 16:00 | 44470.6667 | 0 | 10.9074 | 39.95
2021-10-01 16:30 | 44470.6875 | 0 | 11.6331 | 39.95
2021-10-01 17:00 | 44470.7083 | 0 | 11.6299 | 39.95
2021-10-01 17:30 | 44470.7292 | 0 | 12.0519 | 39.95
2021-10-01 18:00 | 44470.75 | 0 | 12.2775 | 39.95
2021-10-01 18:30 | 44470.7708 | 0 | 12.2821 | 39.95
2021-10-01 19:00 | 44470.7917 | 0 | 11.7685 | 39.95
2021-10-01 19:30 | 44470.8125 | 0 | 11.6317 | 39.95
2021-10-01 20:00 | 44470.8333 | 0 | 11.2143 | 39.95
2021-10-01 20:30 | 44470.8542 | 0 | 10.7096 | 39.95
2021-10-01 21:00 | 44470.875 | 0 | 10.3275 | 39.95
2021-10-01 21:30 | 44470.8958 | 0 | 10.0386 | 39.95
2021-10-01 22:00 | 44470.9167 | 0 | 9.7867 | 39.95
2021-10-01 22:30 | 44470.9375 | 0 | 9.1393 | 39.95
2021-10-01 23:00 | 44470.9583 | 0 | 8.8282 | 39.95
2021-10-01 23:30 | 44470.9792 | 0 | 8.7614 | 39.95
2021-10-02 | 44471 | 0 | 8.2255 | 39.95
2021-10-02 00:30 | 44471.0208 | 0 | 7.7507 | 39.95
2021-10-02 01:00 | 44471.0417 | 0 | 7.6551 | 39.95
2021-10-02 01:30 | 44471.0625 | 0 | 7.5038 | 39.95
2021-10-02 02:00 | 44471.0833 | 0 | 7.3812 | 39.95
2021-10-02 02:30 | 44471.1042 | 0 | 7.3197 | 39.95
2021-10-02 03:00 | 44471.125 | 0 | 7.138 | 39.95
2021-10-02 03:30 | 44471.1458 | 0 | 7.1444 | 39.95
2021-10-02 04:00 | 44471.1667 | 0 | 7.074 | 39.95
2021-10-02 04:30 | 44471.1875 | 0 | 7.1275 | 39.95
2021-10-02 05:00 | 44471.2083 | 0 | 7.3247 | 39.95
2021-10-02 05:30 | 44471.2292 | 0 | 7.3529 | 39.95
2021-10-02 06:00 | 44471.25 | 0 | 7.486 | 39.95
2021-10-02 06:30 | 44471.2708 | 0 | 6.8957 | 39.95
2021-10-02 07:00 | 44471.2917 | 0 | 6.6541 | 39.95
2021-10-02 07:30 | 44471.3125 | 0 | 6.1975 | 39.95
2021-10-02 08:00 | 44471.3333 | 0 | 6.0139 | 39.95
2021-10-02 08:30 | 44471.3542 | 0 | 5.6631 | 39.95
2021-10-02 09:00 | 44471.375 | 0 | 5.3653 | 39.95
2021-10-02 09:30 | 44471.3958 | 0 | 5.4329 | 39.95
2021-10-02 10:00 | 44471.4167 | 0 | 5.0877 | 39.95
2021-10-02 10:30 | 44471.4375 | 0 | 5.087 | 39.95
2021-10-02 11:00 | 44471.4583 | 0 | 5.425 | 39.95
2021-10-02 11:30 | 44471.4792 | 0 | 5.2439 | 39.95
2021-10-02 12:00 | 44471.5 | 0 | 5.4988 | 39.95
2021-10-02 12:30 | 44471.5208 | 0 | 6.4013 | 39.95
2021-10-02 13:00 | 44471.5417 | 0 | 6.2456 | 39.95
2021-10-02 13:30 | 44471.5625 | 0 | 5.8915 | 39.95
2021-10-02 14:00 | 44471.5833 | 0 | 7.5622 | 39.95
2021-10-02 14:30 | 44471.6042 | 0 | 7.4468 | 39.95
2021-10-02 15:00 | 44471.625 | 0 | 7.7992 | 39.95
2021-10-02 15:30 | 44471.6458 | 0 | 8.2327 | 39.95
2021-10-02 16:00 | 44471.6667 | 0 | 8.8914 | 39.95
2021-10-02 16:30 | 44471.6875 | 0 | 9.8574 | 39.95
2021-10-02 17:00 | 44471.7083 | 0 | 10.1949 | 39.95
2021-10-02 17:30 | 44471.7292 | 0 | 10.5996 | 39.95
2021-10-02 18:00 | 44471.75 | 0 | 10.9877 | 39.95
2021-10-02 18:30 | 44471.7708 | 0 | 11.1386 | 39.95
2021-10-02 19:00 | 44471.7917 | 0 | 10.6936 | 39.95
2021-10-02 19:30 | 44471.8125 | 0 | 10.5694 | 39.95
2021-10-02 20:00 | 44471.8333 | 0 | 10.2382 | 39.95
2021-10-02 20:30 | 44471.8542 | 0 | 9.824 | 39.95
2021-10-02 21:00 | 44471.875 | 0 | 9.4437 | 39.95
2021-10-02 21:30 | 44471.8958 | 0 | 9.3292 | 39.95
2021-10-02 22:00 | 44471.9167 | 0 | 9.0651 | 39.95
2021-10-02 22:30 | 44471.9375 | 0 | 8.5644 | 39.95
2021-10-02 23:00 | 44471.9583 | 0 | 8.1741 | 39.95
2021-10-02 23:30 | 44471.9792 | 0 | 7.8816 | 39.95
2021-10-03 | 44472 | 0 | 7.3277 | 39.95
2021-10-03 00:30 | 44472.0208 | 0 | 7.1119 | 39.95
2021-10-03 01:00 | 44472.0417 | 0 | 6.9787 | 39.95
2021-10-03 01:30 | 44472.0625 | 0 | 6.9352 | 39.95
2021-10-03 02:00 | 44472.0833 | 0 | 6.7181 | 39.95
2021-10-03 02:30 | 44472.1042 | 0 | 6.8284 | 39.95
2021-10-03 03:00 | 44472.125 | 0 | 6.7499 | 39.95
2021-10-03 03:30 | 44472.1458 | 0 | 6.7523 | 39.95
2021-10-03 04:00 | 44472.1667 | 0 | 6.7519 | 39.95
2021-10-03 04:30 | 44472.1875 | 0 | 6.7296 | 39.95
2021-10-03 05:00 | 44472.2083 | 0 | 6.8056 | 39.95
2021-10-03 05:30 | 44472.2292 | 0 | 6.7614 | 39.95
2021-10-03 06:00 | 44472.25 | 0 | 6.4998 | 39.95
2021-10-03 06:30 | 44472.2708 | 0 | 6.3083 | 39.95
2021-10-03 07:00 | 44472.2917 | 0 | 6.1912 | 39.95
2021-10-03 07:30 | 44472.3125 | 0 | 5.6152 | 39.95
2021-10-03 08:00 | 44472.3333 | 0 | 5.5331 | 39.95
2021-10-03 08:30 | 44472.3542 | 0 | 5.3828 | 39.95
2021-10-03 09:00 | 44472.375 | 0 | 5.2258 | 39.95
2021-10-03 09:30 | 44472.3958 | 0 | 5.3097 | 39.95
2021-10-03 10:00 | 44472.4167 | 0 | 5.0953 | 39.95
2021-10-03 10:30 | 44472.4375 | 0 | 5.059 | 39.95
2021-10-03 11:00 | 44472.4583 | 0 | 4.8158 | 39.95
2021-10-03 11:30 | 44472.4792 | 0 | 4.8462 | 39.95
2021-10-03 12:00 | 44472.5 | 0 | 4.9069 | 39.95
2021-10-03 12:30 | 44472.5208 | 0 | 5.5839 | 39.95
2021-10-03 13:00 | 44472.5417 | 0 | 6.3252 | 39.95
2021-10-03 13:30 | 44472.5625 | 0 | 6.2967 | 39.95
2021-10-03 14:00 | 44472.5833 | 0 | 6.5513 | 39.95
2021-10-03 14:30 | 44472.6042 | 0 | 7.057 | 39.95
2021-10-03 15:00 | 44472.625 | 0 | 7.768 | 39.95
2021-10-03 15:30 | 44472.6458 | 0 | 8.6108 | 39.95
2021-10-03 16:00 | 44472.6667 | 0 | 9.2941 | 39.95
2021-10-03 16:30 | 44472.6875 | 0 | 10.0533 | 39.95
2021-10-03 17:00 | 44472.7083 | 0 | 10.3306 | 39.95
2021-10-03 17:30 | 44472.7292 | 0 | 10.6983 | 39.95
2021-10-03 18:00 | 44472.75 | 0 | 11.1971 | 39.95
2021-10-03 18:30 | 44472.7708 | 0 | 11.3273 | 39.95
2021-10-03 19:00 | 44472.7917 | 0 | 11.0873 | 39.95
2021-10-03 19:30 | 44472.8125 | 0 | 10.8394 | 39.95
2021-10-03 20:00 | 44472.8333 | 0 | 10.4806 | 39.95
2021-10-03 20:30 | 44472.8542 | 0 | 10.1282 | 39.95
2021-10-03 21:00 | 44472.875 | 0 | 9.9014 | 39.95
2021-10-03 21:30 | 44472.8958 | 0 | 9.7801 | 39.95
2021-10-03 22:00 | 44472.9167 | 0 | 9.3513 | 39.95
2021-10-03 22:30 | 44472.9375 | 0 | 8.8048 | 39.95
2021-10-03 23:00 | 44472.9583 | 0 | 8.3808 | 39.95
2021-10-03 23:30 | 44472.9792 | 0 | 8.1033 | 39.95
2021-10-04 | 44473 | 0 | 7.7369 | 39.95
2021-10-04 00:30 | 44473.0208 | 0 | 7.4027 | 39.95
2021-10-04 01:00 | 44473.0417 | 0 | 7.3142 | 39.95
2021-10-04 01:30 | 44473.0625 | 0 | 7.1692 | 39.95
2021-10-04 02:00 | 44473.0833 | 0 | 7.0348 | 39.95
2021-10-04 02:30 | 44473.1042 | 0 | 6.9515 | 39.95
2021-10-04 03:00 | 44473.125 | 0 | 6.8099 | 39.95
2021-10-04 03:30 | 44473.1458 | 0 | 7.0919 | 39.95
2021-10-04 04:00 | 44473.1667 | 0 | 7.0324 | 39.95
2021-10-04 04:30 | 44473.1875 | 0 | 7.336 | 39.95
2021-10-04 05:00 | 44473.2083 | 0 | 7.4253 | 39.95
2021-10-04 05:30 | 44473.2292 | 0 | 7.4645 | 39.95
2021-10-04 06:00 | 44473.25 | 0 | 7.4319 | 39.95
2021-10-04 06:30 | 44473.2708 | 0 | 7.1841 | 39.95
2021-10-04 07:00 | 44473.2917 | 0 | 7.2327 | 39.95
2021-10-04 07:30 | 44473.3125 | 0 | 6.9133 | 39.95
2021-10-04 08:00 | 44473.3333 | 0 | 7.1997 | 39.95
2021-10-04 08:30 | 44473.3542 | 0 | 6.5698 | 39.95
2021-10-04 09:00 | 44473.375 | 0 | 6.4541 | 39.95
2021-10-04 09:30 | 44473.3958 | 0 | 6.6308 | 39.95
2021-10-04 10:00 | 44473.4167 | 0 | 6.5972 | 39.95
2021-10-04 10:30 | 44473.4375 | 0 | 6.8115 | 39.95
2021-10-04 11:00 | 44473.4583 | 0 | 6.867 | 39.95
2021-10-04 11:30 | 44473.4792 | 0 | 7.1551 | 39.95
2021-10-04 12:00 | 44473.5 | 0 | 7.4229 | 39.95
2021-10-04 12:30 | 44473.5208 | 0 | 8.1503 | 39.95
2021-10-04 13:00 | 44473.5417 | 0 | 8.6839 | 39.95
2021-10-04 13:30 | 44473.5625 | 0 | 9.5619 | 39.95
2021-10-04 14:00 | 44473.5833 | 0 | 10.8707 | 39.95
2021-10-04 14:30 | 44473.6042 | 0 | 11.5911 | 39.95
2021-10-04 15:00 | 44473.625 | 0 | 12.5615 | 39.95
2021-10-04 15:30 | 44473.6458 | 0 | 13.4064 | 39.95
2021-10-04 16:00 | 44473.6667 | 0 | 14.1857 | 39.95
2021-10-04 16:30 | 44473.6875 | 0 | 15.2525 | 39.95
2021-10-04 17:00 | 44473.7083 | 0 | 15.5642 | 39.95
2021-10-04 17:30 | 44473.7292 | 0 | 15.5824 | 39.95
2021-10-04 18:00 | 44473.75 | 0 | 15.8532 | 39.95
2021-10-04 18:30 | 44473.7708 | 0 | 16.3093 | 39.95
2021-10-04 19:00 | 44473.7917 | 0 | 15.7985 | 39.95
2021-10-04 19:30 | 44473.8125 | 0 | 15.4419 | 39.95
2021-10-04 20:00 | 44473.8333 | 0 | 14.4969 | 39.95
2021-10-04 20:30 | 44473.8542 | 0 | 13.7883 | 39.95
2021-10-04 21:00 | 44473.875 | 0 | 12.7316 | 39.95
2021-10-04 21:30 | 44473.8958 | 0 | 12.0264 | 39.95
2021-10-04 22:00 | 44473.9167 | 0 | 11.1465 | 39.95
2021-10-04 22:30 | 44473.9375 | 0 | 10.2125 | 39.95
2021-10-04 23:00 | 44473.9583 | 0 | 9.4204 | 39.95
2021-10-04 23:30 | 44473.9792 | 0 | 9.1121 | 39.95
2021-10-05 | 44474 | 0 | 8.616 | 39.95
2021-10-05 00:30 | 44474.0208 | 0 | 8.3311 | 39.95
2021-10-05 01:00 | 44474.0417 | 0 | 8.1013 | 39.95
2021-10-05 01:30 | 44474.0625 | 0 | 7.9287 | 39.95
2021-10-05 02:00 | 44474.0833 | 0 | 7.7458 | 39.95
2021-10-05 02:30 | 44474.1042 | 0 | 7.6555 | 39.95
2021-10-05 03:00 | 44474.125 | 0 | 7.5038 | 39.95
2021-10-05 03:30 | 44474.1458 | 0 | 7.6541 | 39.95
2021-10-05 04:00 | 44474.1667 | 0 | 7.7848 | 39.95
2021-10-05 04:30 | 44474.1875 | 0 | 8.2895 | 39.95
2021-10-05 05:00 | 44474.2083 | 0 | 8.795 | 39.95
2021-10-05 05:30 | 44474.2292 | 0 | 9.2021 | 39.95
2021-10-05 06:00 | 44474.25 | 0 | 9.5443 | 39.95
2021-10-05 06:30 | 44474.2708 | 0 | 10.1132 | 39.95
2021-10-05 07:00 | 44474.2917 | 0 | 10.2432 | 39.95
2021-10-05 07:30 | 44474.3125 | 0 | 10.0449 | 39.95
2021-10-05 08:00 | 44474.3333 | 0 | 9.6101 | 39.95
2021-10-05 08:30 | 44474.3542 | 0 | 9.3483 | 39.95
2021-10-05 09:00 | 44474.375 | 0 | 9.1184 | 39.95
2021-10-05 09:30 | 44474.3958 | 0 | 9.1902 | 39.95
2021-10-05 10:00 | 44474.4167 | 0 | 9.0278 | 39.95
2021-10-05 10:30 | 44474.4375 | 0 | 9.1262 | 39.95
2021-10-05 11:00 | 44474.4583 | 0 | 9.1754 | 39.95
2021-10-05 11:30 | 44474.4792 | 0 | 9.6085 | 39.95
2021-10-05 12:00 | 44474.5 | 0 | 9.6477 | 39.95
2021-10-05 12:30 | 44474.5208 | 0 | 9.8199 | 39.95
2021-10-05 13:00 | 44474.5417 | 0 | 10.3261 | 39.95
2021-10-05 13:30 | 44474.5625 | 0 | 10.6363 | 39.95
2021-10-05 14:00 | 44474.5833 | 0 | 11.3136 | 39.95
2021-10-05 14:30 | 44474.6042 | 0 | 11.8929 | 39.95
2021-10-05 15:00 | 44474.625 | 0 | 12.3029 | 39.95
2021-10-05 15:30 | 44474.6458 | 0 | 12.8141 | 39.95
2021-10-05 16:00 | 44474.6667 | 0 | 13.7209 | 39.95
2021-10-05 16:30 | 44474.6875 | 0 | 14.556 | 39.95
2021-10-05 17:00 | 44474.7083 | 0 | 14.4478 | 39.95
2021-10-05 17:30 | 44474.7292 | 0 | 14.7444 | 39.95
2021-10-05 18:00 | 44474.75 | 0 | 14.9535 | 39.95
2021-10-05 18:30 | 44474.7708 | 0 | 15.1035 | 39.95
2021-10-05 19:00 | 44474.7917 | 0 | 14.5952 | 39.95
2021-10-05 19:30 | 44474.8125 | 0 | 14.4081 | 39.95
2021-10-05 20:00 | 44474.8333 | 0 | 13.6557 | 39.95
2021-10-05 20:30 | 44474.8542 | 0 | 13.0149 | 39.95
2021-10-05 21:00 | 44474.875 | 0 | 12.398 | 39.95
2021-10-05 21:30 | 44474.8958 | 0 | 11.8941 | 39.95
2021-10-05 22:00 | 44474.9167 | 0 | 11.2464 | 39.95
2021-10-05 22:30 | 44474.9375 | 0 | 10.5486 | 39.95
2021-10-05 23:00 | 44474.9583 | 0 | 9.8261 | 39.95
2021-10-05 23:30 | 44474.9792 | 0 | 9.332 | 39.95
2021-10-06 | 44475 | 0 | 8.7604 | 39.95
2021-10-06 00:30 | 44475.0208 | 0 | 8.3206 | 39.95
2021-10-06 01:00 | 44475.0417 | 0 | 8.1132 | 39.95
2021-10-06 01:30 | 44475.0625 | 0 | 7.9003 | 39.95
2021-10-06 02:00 | 44475.0833 | 0 | 7.8279 | 39.95
2021-10-06 02:30 | 44475.1042 | 0 | 7.6754 | 39.95
2021-10-06 03:00 | 44475.125 | 0 | 7.6119 | 39.95
2021-10-06 03:30 | 44475.1458 | 0 | 7.7653 | 39.95
2021-10-06 04:00 | 44475.1667 | 0 | 8.1504 | 39.95
2021-10-06 04:30 | 44475.1875 | 0 | 8.4015 | 39.95
2021-10-06 05:00 | 44475.2083 | 0 | 8.8511 | 39.95
2021-10-06 05:30 | 44475.2292 | 0 | 9.4292 | 39.95
2021-10-06 06:00 | 44475.25 | 0 | 9.6988 | 39.95
2021-10-06 06:30 | 44475.2708 | 0 | 9.9937 | 39.95
2021-10-06 07:00 | 44475.2917 | 0 | 10.1052 | 39.95
2021-10-06 07:30 | 44475.3125 | 0 | 9.7418 | 39.95
2021-10-06 08:00 | 44475.3333 | 0 | 9.1322 | 39.95
2021-10-06 08:30 | 44475.3542 | 0 | 8.7325 | 39.95
2021-10-06 09:00 | 44475.375 | 0 | 8.4271 | 39.95
2021-10-06 09:30 | 44475.3958 | 0 | 8.2685 | 39.95
2021-10-06 10:00 | 44475.4167 | 0 | 8.3355 | 39.95
2021-10-06 10:30 | 44475.4375 | 0 | 8.3971 | 39.95
2021-10-06 11:00 | 44475.4583 | 0 | 8.4695 | 39.95
2021-10-06 11:30 | 44475.4792 | 0 | 8.5852 | 39.95
2021-10-06 12:00 | 44475.5 | 0 | 8.5093 | 39.95
2021-10-06 12:30 | 44475.5208 | 0 | 8.6749 | 39.95
2021-10-06 13:00 | 44475.5417 | 0 | 8.9101 | 39.95
2021-10-06 13:30 | 44475.5625 | 0 | 9.2965 | 39.95
2021-10-06 14:00 | 44475.5833 | 0 | 9.85 | 39.95
2021-10-06 14:30 | 44475.6042 | 0 | 10.3092 | 39.95
2021-10-06 15:00 | 44475.625 | 0 | 10.7748 | 39.95
2021-10-06 15:30 | 44475.6458 | 0 | 11.4652 | 39.95
2021-10-06 16:00 | 44475.6667 | 0 | 12.1855 | 39.95
2021-10-06 16:30 | 44475.6875 | 0 | 13.1068 | 39.95
2021-10-06 17:00 | 44475.7083 | 0 | 13.3266 | 39.95
2021-10-06 17:30 | 44475.7292 | 0 | 13.6579 | 39.95
2021-10-06 18:00 | 44475.75 | 0 | 14.0023 | 39.95
2021-10-06 18:30 | 44475.7708 | 0 | 14.1875 | 39.95
2021-10-06 19:00 | 44475.7917 | 0 | 13.7982 | 39.95
2021-10-06 19:30 | 44475.8125 | 0 | 13.3912 | 39.95
2021-10-06 20:00 | 44475.8333 | 0 | 13.0523 | 39.95
2021-10-06 20:30 | 44475.8542 | 0 | 12.5135 | 39.95
2021-10-06 21:00 | 44475.875 | 0 | 11.9922 | 39.95
2021-10-06 21:30 | 44475.8958 | 0 | 11.7749 | 39.95
2021-10-06 22:00 | 44475.9167 | 0 | 11.0943 | 39.95
2021-10-06 22:30 | 44475.9375 | 0 | 10.4091 | 39.95
2021-10-06 23:00 | 44475.9583 | 0 | 9.7288 | 39.95
2021-10-06 23:30 | 44475.9792 | 0 | 9.4095 | 39.95
2021-10-07 | 44476 | 0 | 8.8131 | 39.95
2021-10-07 00:30 | 44476.0208 | 0 | 8.4006 | 39.95
2021-10-07 01:00 | 44476.0417 | 0 | 8.0967 | 39.95
2021-10-07 01:30 | 44476.0625 | 0 | 7.843 | 39.95
2021-10-07 02:00 | 44476.0833 | 0 | 7.7885 | 39.95
2021-10-07 02:30 | 44476.1042 | 0 | 7.7014 | 39.95
2021-10-07 03:00 | 44476.125 | 0 | 7.6634 | 39.95
2021-10-07 03:30 | 44476.1458 | 0 | 7.7766 | 39.95
2021-10-07 04:00 | 44476.1667 | 0 | 8.0051 | 39.95
2021-10-07 04:30 | 44476.1875 | 0 | 8.3651 | 39.95
2021-10-07 05:00 | 44476.2083 | 0 | 8.8604 | 39.95
2021-10-07 05:30 | 44476.2292 | 0 | 9.2106 | 39.95
2021-10-07 06:00 | 44476.25 | 0 | 9.714 | 39.95
2021-10-07 06:30 | 44476.2708 | 0 | 9.9471 | 39.95
2021-10-07 07:00 | 44476.2917 | 0 | 10.3177 | 39.95
2021-10-07 07:30 | 44476.3125 | 0 | 10.1986 | 39.95
2021-10-07 08:00 | 44476.3333 | 0 | 9.6129 | 39.95
2021-10-07 08:30 | 44476.3542 | 0 | 9.3682 | 39.95
2021-10-07 09:00 | 44476.375 | 0 | 9.0048 | 39.95
2021-10-07 09:30 | 44476.3958 | 0 | 8.8647 | 39.95
2021-10-07 10:00 | 44476.4167 | 0 | 8.9168 | 39.95
2021-10-07 10:30 | 44476.4375 | 0 | 9.0123 | 39.95
2021-10-07 11:00 | 44476.4583 | 0 | 8.9621 | 39.95
2021-10-07 11:30 | 44476.4792 | 0 | 9.038 | 39.95
2021-10-07 12:00 | 44476.5 | 0 | 9.0697 | 39.95
2021-10-07 12:30 | 44476.5208 | 0 | 9.0695 | 39.95
2021-10-07 13:00 | 44476.5417 | 0 | 9.6577 | 39.95
2021-10-07 13:30 | 44476.5625 | 0 | 10.5414 | 39.95
2021-10-07 14:00 | 44476.5833 | 0 | 12.466 | 39.95
2021-10-07 14:30 | 44476.6042 | 0 | 12.5817 | 39.95
2021-10-07 15:00 | 44476.625 | 0 | 12.678 | 39.95
2021-10-07 15:30 | 44476.6458 | 0 | 12.1713 | 39.95
2021-10-07 16:00 | 44476.6667 | 0 | 12.3358 | 39.95
2021-10-07 16:30 | 44476.6875 | 0 | 12.5866 | 39.95
2021-10-07 17:00 | 44476.7083 | 0 | 12.9604 | 39.95
2021-10-07 17:30 | 44476.7292 | 0 | 13.4117 | 39.95
2021-10-07 18:00 | 44476.75 | 0 | 13.6553 | 39.95
2021-10-07 18:30 | 44476.7708 | 0 | 13.8287 | 39.95
2021-10-07 19:00 | 44476.7917 | 0 | 13.6418 | 39.95
2021-10-07 19:30 | 44476.8125 | 0 | 13.3583 | 39.95
2021-10-07 20:00 | 44476.8333 | 0 | 12.909 | 39.95
2021-10-07 20:30 | 44476.8542 | 0 | 12.4122 | 39.95
2021-10-07 21:00 | 44476.875 | 0 | 11.8902 | 39.95
2021-10-07 21:30 | 44476.8958 | 0 | 11.5906 | 39.95
2021-10-07 22:00 | 44476.9167 | 0 | 11.0738 | 39.95
2021-10-07 22:30 | 44476.9375 | 0 | 10.1722 | 39.95
2021-10-07 23:00 | 44476.9583 | 0 | 9.6566 | 39.95
2021-10-07 23:30 | 44476.9792 | 0 | 9.2226 | 39.95
2021-10-08 | 44477 | 0 | 8.7979 | 39.95
2021-10-08 00:30 | 44477.0208 | 0 | 8.5683 | 39.95
2021-10-08 01:00 | 44477.0417 | 0 | 8.2404 | 39.95
2021-10-08 01:30 | 44477.0625 | 0 | 8.0587 | 39.95
2021-10-08 02:00 | 44477.0833 | 0 | 7.9917 | 39.95
2021-10-08 02:30 | 44477.1042 | 0 | 7.9471 | 39.95
2021-10-08 03:00 | 44477.125 | 0 | 7.8354 | 39.95
2021-10-08 03:30 | 44477.1458 | 0 | 7.8968 | 39.95
2021-10-08 04:00 | 44477.1667 | 0 | 8.2333 | 39.95
2021-10-08 04:30 | 44477.1875 | 0 | 8.7027 | 39.95
2021-10-08 05:00 | 44477.2083 | 0 | 9.0513 | 39.95
2021-10-08 05:30 | 44477.2292 | 0 | 9.4311 | 39.95
2021-10-08 06:00 | 44477.25 | 0 | 9.8413 | 39.95
2021-10-08 06:30 | 44477.2708 | 0 | 10.2388 | 39.95
2021-10-08 07:00 | 44477.2917 | 0 | 10.5823 | 39.95
2021-10-08 07:30 | 44477.3125 | 0 | 10.3184 | 39.95
2021-10-08 08:00 | 44477.3333 | 0 | 10.1416 | 39.95
2021-10-08 08:30 | 44477.3542 | 0 | 9.9654 | 39.95
2021-10-08 09:00 | 44477.375 | 0 | 9.6693 | 39.95
2021-10-08 09:30 | 44477.3958 | 0 | 9.5617 | 39.95
2021-10-08 10:00 | 44477.4167 | 0 | 9.6377 | 39.95
2021-10-08 10:30 | 44477.4375 | 0 | 9.7017 | 39.95
2021-10-08 11:00 | 44477.4583 | 0 | 9.727 | 39.95
2021-10-08 11:30 | 44477.4792 | 0 | 10.1366 | 39.95
2021-10-08 12:00 | 44477.5 | 0 | 9.7925 | 39.95
2021-10-08 12:30 | 44477.5208 | 0 | 10.1282 | 39.95
2021-10-08 13:00 | 44477.5417 | 0 | 10.2019 | 39.95
2021-10-08 13:30 | 44477.5625 | 0 | 10.3757 | 39.95
2021-10-08 14:00 | 44477.5833 | 0 | 10.6761 | 39.95
2021-10-08 14:30 | 44477.6042 | 0 | 11.4193 | 39.95
2021-10-08 15:00 | 44477.625 | 0 | 11.7983 | 39.95
2021-10-08 15:30 | 44477.6458 | 0 | 12.4091 | 39.95
2021-10-08 16:00 | 44477.6667 | 0 | 13.0493 | 39.95
2021-10-08 16:30 | 44477.6875 | 0 | 13.6017 | 39.95
2021-10-08 17:00 | 44477.7083 | 0 | 13.6114 | 39.95
2021-10-08 17:30 | 44477.7292 | 0 | 13.5708 | 39.95
2021-10-08 18:00 | 44477.75 | 0 | 13.8496 | 39.95
2021-10-08 18:30 | 44477.7708 | 0 | 14.1217 | 39.95
2021-10-08 19:00 | 44477.7917 | 0 | 13.7982 | 39.95
2021-10-08 19:30 | 44477.8125 | 0 | 13.3224 | 39.95
2021-10-08 20:00 | 44477.8333 | 0 | 12.9001 | 39.95
2021-10-08 20:30 | 44477.8542 | 0 | 12.4709 | 39.95
2021-10-08 21:00 | 44477.875 | 0 | 11.9803 | 39.95
2021-10-08 21:30 | 44477.8958 | 0 | 11.7582 | 39.95
2021-10-08 22:00 | 44477.9167 | 0 | 11.4662 | 39.95
2021-10-08 22:30 | 44477.9375 | 0 | 10.6162 | 39.95
2021-10-08 23:00 | 44477.9583 | 0 | 10.129 | 39.95
2021-10-08 23:30 | 44477.9792 | 0 | 9.605 | 39.95
2021-10-09 | 44478 | 0 | 9.0598 | 39.95
2021-10-09 00:30 | 44478.0208 | 0 | 8.6733 | 39.95
2021-10-09 01:00 | 44478.0417 | 0 | 8.3077 | 39.95
2021-10-09 01:30 | 44478.0625 | 0 | 8.1467 | 39.95
2021-10-09 02:00 | 44478.0833 | 0 | 8.071 | 39.95
2021-10-09 02:30 | 44478.1042 | 0 | 7.8298 | 39.95
2021-10-09 03:00 | 44478.125 | 0 | 7.7029 | 39.95
2021-10-09 03:30 | 44478.1458 | 0 | 7.8455 | 39.95
2021-10-09 04:00 | 44478.1667 | 0 | 7.9247 | 39.95
2021-10-09 04:30 | 44478.1875 | 0 | 7.9381 | 39.95
2021-10-09 05:00 | 44478.2083 | 0 | 8.2158 | 39.95
2021-10-09 05:30 | 44478.2292 | 0 | 8.3714 | 39.95
2021-10-09 06:00 | 44478.25 | 0 | 8.3055 | 39.95
2021-10-09 06:30 | 44478.2708 | 0 | 8.2076 | 39.95
2021-10-09 07:00 | 44478.2917 | 0 | 8.297 | 39.95
2021-10-09 07:30 | 44478.3125 | 0 | 8.7529 | 39.95
2021-10-09 08:00 | 44478.3333 | 0 | 8.7179 | 39.95
2021-10-09 08:30 | 44478.3542 | 0 | 8.3176 | 39.95
2021-10-09 09:00 | 44478.375 | 0 | 8.8951 | 39.95
2021-10-09 09:30 | 44478.3958 | 0 | 8.7205 | 39.95
2021-10-09 10:00 | 44478.4167 | 0 | 8.1158 | 39.95
2021-10-09 10:30 | 44478.4375 | 0 | 7.3709 | 39.95
2021-10-09 11:00 | 44478.4583 | 0 | 7.2715 | 39.95
2021-10-09 11:30 | 44478.4792 | 0 | 7.3002 | 39.95
2021-10-09 12:00 | 44478.5 | 0 | 7.225 | 39.95
2021-10-09 12:30 | 44478.5208 | 0 | 7.3162 | 39.95
2021-10-09 13:00 | 44478.5417 | 0 | 7.627 | 39.95
2021-10-09 13:30 | 44478.5625 | 0 | 8.0237 | 39.95
2021-10-09 14:00 | 44478.5833 | 0 | 8.3575 | 39.95
2021-10-09 14:30 | 44478.6042 | 0 | 8.8445 | 39.95
2021-10-09 15:00 | 44478.625 | 0 | 9.5101 | 39.95
2021-10-09 15:30 | 44478.6458 | 0 | 10.0865 | 39.95
2021-10-09 16:00 | 44478.6667 | 0 | 10.5595 | 39.95
2021-10-09 16:30 | 44478.6875 | 0 | 11.058 | 39.95
2021-10-09 17:00 | 44478.7083 | 0 | 11.4518 | 39.95
2021-10-09 17:30 | 44478.7292 | 0 | 11.6264 | 39.95
2021-10-09 18:00 | 44478.75 | 0 | 11.923 | 39.95
2021-10-09 18:30 | 44478.7708 | 0 | 12.2196 | 39.95
2021-10-09 19:00 | 44478.7917 | 0 | 11.9208 | 39.95
2021-10-09 19:30 | 44478.8125 | 0 | 11.6314 | 39.95
2021-10-09 20:00 | 44478.8333 | 0 | 11.3219 | 39.95
2021-10-09 20:30 | 44478.8542 | 0 | 10.9714 | 39.95
2021-10-09 21:00 | 44478.875 | 0 | 10.7305 | 39.95
2021-10-09 21:30 | 44478.8958 | 0 | 10.4997 | 39.95
2021-10-09 22:00 | 44478.9167 | 0 | 10.1923 | 39.95
2021-10-09 22:30 | 44478.9375 | 0 | 9.5875 | 39.95
2021-10-09 23:00 | 44478.9583 | 0 | 9.2383 | 39.95
2021-10-09 23:30 | 44478.9792 | 0 | 8.8273 | 39.95
2021-10-10 | 44479 | 0 | 8.406 | 39.95
2021-10-10 00:30 | 44479.0208 | 0 | 8.0648 | 39.95
2021-10-10 01:00 | 44479.0417 | 0 | 7.9984 | 39.95
2021-10-10 01:30 | 44479.0625 | 0 | 7.7197 | 39.95
2021-10-10 02:00 | 44479.0833 | 0 | 7.6567 | 39.95
2021-10-10 02:30 | 44479.1042 | 0 | 7.5012 | 39.95
2021-10-10 03:00 | 44479.125 | 0 | 7.6412 | 39.95
2021-10-10 03:30 | 44479.1458 | 0 | 7.6757 | 39.95
2021-10-10 04:00 | 44479.1667 | 0 | 7.6154 | 39.95
2021-10-10 04:30 | 44479.1875 | 0 | 7.5105 | 39.95
2021-10-10 05:00 | 44479.2083 | 0 | 7.5417 | 39.95
2021-10-10 05:30 | 44479.2292 | 0 | 7.3988 | 39.95
2021-10-10 06:00 | 44479.25 | 0 | 7.2183 | 39.95
2021-10-10 06:30 | 44479.2708 | 0 | 6.9935 | 39.95
2021-10-10 07:00 | 44479.2917 | 0 | 6.8692 | 39.95
2021-10-10 07:30 | 44479.3125 | 0 | 6.557 | 39.95
2021-10-10 08:00 | 44479.3333 | 0 | 6.4608 | 39.95
2021-10-10 08:30 | 44479.3542 | 0 | 6.4698 | 39.95
2021-10-10 09:00 | 44479.375 | 0 | 6.4162 | 39.95
2021-10-10 09:30 | 44479.3958 | 0 | 6.4028 | 39.95
2021-10-10 10:00 | 44479.4167 | 0 | 6.2282 | 39.95
2021-10-10 10:30 | 44479.4375 | 0 | 6.3938 | 39.95
2021-10-10 11:00 | 44479.4583 | 0 | 6.4128 | 39.95
2021-10-10 11:30 | 44479.4792 | 0 | 6.4541 | 39.95
2021-10-10 12:00 | 44479.5 | 0 | 6.4899 | 39.95
2021-10-10 12:30 | 44479.5208 | 0 | 6.6641 | 39.95
2021-10-10 13:00 | 44479.5417 | 0 | 7.109 | 39.95
2021-10-10 13:30 | 44479.5625 | 0 | 7.632 | 39.95
2021-10-10 14:00 | 44479.5833 | 0 | 8.0911 | 39.95
2021-10-10 14:30 | 44479.6042 | 0 | 8.462 | 39.95
2021-10-10 15:00 | 44479.625 | 0 | 9.2802 | 39.95
2021-10-10 15:30 | 44479.6458 | 0 | 9.8659 | 39.95
2021-10-10 16:00 | 44479.6667 | 0 | 10.3102 | 39.95
2021-10-10 16:30 | 44479.6875 | 0 | 10.9955 | 39.95
2021-10-10 17:00 | 44479.7083 | 0 | 11.3763 | 39.95
2021-10-10 17:30 | 44479.7292 | 0 | 11.6643 | 39.95
2021-10-10 18:00 | 44479.75 | 0 | 12.2103 | 39.95
2021-10-10 18:30 | 44479.7708 | 0 | 12.4244 | 39.95
2021-10-10 19:00 | 44479.7917 | 0 | 12.2688 | 39.95
2021-10-10 19:30 | 44479.8125 | 0 | 12.0183 | 39.95
2021-10-10 20:00 | 44479.8333 | 0 | 11.5418 | 39.95
2021-10-10 20:30 | 44479.8542 | 0 | 11.2141 | 39.95
2021-10-10 21:00 | 44479.875 | 0 | 10.822 | 39.95
2021-10-10 21:30 | 44479.8958 | 0 | 10.4037 | 39.95
2021-10-10 22:00 | 44479.9167 | 0 | 9.8604 | 39.95
2021-10-10 22:30 | 44479.9375 | 0 | 9.2537 | 39.95
2021-10-10 23:00 | 44479.9583 | 0 | 8.761 | 39.95
2021-10-10 23:30 | 44479.9792 | 0 | 8.4027 | 39.95
2021-10-11 | 44480 | 0 | 8.0287 | 39.95
2021-10-11 00:30 | 44480.0208 | 0 | 7.8678 | 39.95
2021-10-11 01:00 | 44480.0417 | 0 | 7.6757 | 39.95
2021-10-11 01:30 | 44480.0625 | 0 | 7.4222 | 39.95
2021-10-11 02:00 | 44480.0833 | 0 | 7.4524 | 39.95
2021-10-11 02:30 | 44480.1042 | 0 | 7.3631 | 39.95
2021-10-11 03:00 | 44480.125 | 0 | 7.2879 | 39.95
2021-10-11 03:30 | 44480.1458 | 0 | 7.5855 | 39.95
2021-10-11 04:00 | 44480.1667 | 0 | 7.7702 | 39.95
2021-10-11 04:30 | 44480.1875 | 0 | 8.2828 | 39.95
2021-10-11 05:00 | 44480.2083 | 0 | 8.6019 | 39.95
2021-10-11 05:30 | 44480.2292 | 0 | 9.4652 | 39.95
2021-10-11 06:00 | 44480.25 | 0 | 9.7984 | 39.95
2021-10-11 06:30 | 44480.2708 | 0 | 10.121 | 39.95
2021-10-11 07:00 | 44480.2917 | 0 | 10.9453 | 39.95
2021-10-11 07:30 | 44480.3125 | 0 | 10.7603 | 39.95
2021-10-11 08:00 | 44480.3333 | 0 | 11.4552 | 39.95
2021-10-11 08:30 | 44480.3542 | 0 | 10.859 | 39.95
2021-10-11 09:00 | 44480.375 | 0 | 10.456 | 39.95
2021-10-11 09:30 | 44480.3958 | 0 | 9.9408 | 39.95
2021-10-11 10:00 | 44480.4167 | 0 | 9.7345 | 39.95
2021-10-11 10:30 | 44480.4375 | 0 | 10.1956 | 39.95
2021-10-11 11:00 | 44480.4583 | 0 | 10.6308 | 39.95
2021-10-11 11:30 | 44480.4792 | 0 | 11.079 | 39.95
2021-10-11 12:00 | 44480.5 | 0 | 10.5263 | 39.95
2021-10-11 12:30 | 44480.5208 | 0 | 11.9719 | 39.95
2021-10-11 13:00 | 44480.5417 | 0 | 12.2248 | 39.95
2021-10-11 13:30 | 44480.5625 | 0 | 12.7602 | 39.95
2021-10-11 14:00 | 44480.5833 | 0 | 12.1305 | 39.95
2021-10-11 14:30 | 44480.6042 | 0 | 12.9923 | 39.95
2021-10-11 15:00 | 44480.625 | 0 | 12.5319 | 39.95
2021-10-11 15:30 | 44480.6458 | 0 | 12.6465 | 39.95
2021-10-11 16:00 | 44480.6667 | 0 | 13.5271 | 39.95
2021-10-11 16:30 | 44480.6875 | 0 | 14.0703 | 39.95
2021-10-11 17:00 | 44480.7083 | 0 | 14.1399 | 39.95
2021-10-11 17:30 | 44480.7292 | 0 | 14.5284 | 39.95
2021-10-11 18:00 | 44480.75 | 0 | 14.6793 | 39.95
2021-10-11 18:30 | 44480.7708 | 0 | 14.9668 | 39.95
2021-10-11 19:00 | 44480.7917 | 0 | 14.6826 | 39.95
2021-10-11 19:30 | 44480.8125 | 0 | 14.4317 | 39.95
2021-10-11 20:00 | 44480.8333 | 0 | 13.9186 | 39.95
2021-10-11 20:30 | 44480.8542 | 0 | 13.3606 | 39.95
2021-10-11 21:00 | 44480.875 | 0 | 12.7399 | 39.95
2021-10-11 21:30 | 44480.8958 | 0 | 12.2219 | 39.95
2021-10-11 22:00 | 44480.9167 | 0 | 11.7117 | 39.95
2021-10-11 22:30 | 44480.9375 | 0 | 10.7012 | 39.95
2021-10-11 23:00 | 44480.9583 | 0 | 10.0396 | 39.95
2021-10-11 23:30 | 44480.9792 | 0 | 9.7175 | 39.95
2021-10-12 | 44481 | 0 | 9.1694 | 39.95
2021-10-12 00:30 | 44481.0208 | 0 | 8.7272 | 39.95
2021-10-12 01:00 | 44481.0417 | 0 | 8.4953 | 39.95
2021-10-12 01:30 | 44481.0625 | 0 | 8.1831 | 39.95
2021-10-12 02:00 | 44481.0833 | 0 | 8.0744 | 39.95
2021-10-12 02:30 | 44481.1042 | 0 | 8.0107 | 39.95
2021-10-12 03:00 | 44481.125 | 0 | 7.8164 | 39.95
2021-10-12 03:30 | 44481.1458 | 0 | 7.9314 | 39.95
2021-10-12 04:00 | 44481.1667 | 0 | 8.0803 | 39.95
2021-10-12 04:30 | 44481.1875 | 0 | 8.7612 | 39.95
2021-10-12 05:00 | 44481.2083 | 0 | 9.4122 | 39.95
2021-10-12 05:30 | 44481.2292 | 0 | 9.8521 | 39.95
2021-10-12 06:00 | 44481.25 | 0 | 10.679 | 39.95
2021-10-12 06:30 | 44481.2708 | 0 | 11.5387 | 39.95
2021-10-12 07:00 | 44481.2917 | 0 | 12.2602 | 39.95
2021-10-12 07:30 | 44481.3125 | 0 | 12.4825 | 39.95
2021-10-12 08:00 | 44481.3333 | 0 | 11.6044 | 39.95
2021-10-12 08:30 | 44481.3542 | 0 | 11.5981 | 39.95
2021-10-12 09:00 | 44481.375 | 0 | 11.5309 | 39.95
2021-10-12 09:30 | 44481.3958 | 0 | 11.2323 | 39.95
2021-10-12 10:00 | 44481.4167 | 0 | 11.7765 | 39.95
2021-10-12 10:30 | 44481.4375 | 0 | 11.5908 | 39.95
2021-10-12 11:00 | 44481.4583 | 0 | 11.4971 | 39.95
2021-10-12 11:30 | 44481.4792 | 0 | 11.3107 | 39.95
2021-10-12 12:00 | 44481.5 | 0 | 12.1295 | 39.95
2021-10-12 12:30 | 44481.5208 | 0 | 11.4784 | 39.95
2021-10-12 13:00 | 44481.5417 | 0 | 10.5935 | 39.95
2021-10-12 13:30 | 44481.5625 | 0 | 12.2838 | 39.95
2021-10-12 14:00 | 44481.5833 | 0 | 12.0892 | 39.95
2021-10-12 14:30 | 44481.6042 | 0 | 11.7035 | 39.95
2021-10-12 15:00 | 44481.625 | 0 | 12.3608 | 39.95
2021-10-12 15:30 | 44481.6458 | 0 | 12.8929 | 39.95
2021-10-12 16:00 | 44481.6667 | 0 | 12.3424 | 39.95
2021-10-12 16:30 | 44481.6875 | 0 | 12.532 | 39.95
2021-10-12 17:00 | 44481.7083 | 0 | 12.5461 | 39.95
2021-10-12 17:30 | 44481.7292 | 0 | 13.0453 | 39.95
2021-10-12 18:00 | 44481.75 | 0 | 13.5044 | 39.95
2021-10-12 18:30 | 44481.7708 | 0 | 13.7055 | 39.95
2021-10-12 19:00 | 44481.7917 | 0 | 13.5149 | 39.95
2021-10-12 19:30 | 44481.8125 | 0 | 13.2846 | 39.95
2021-10-12 20:00 | 44481.8333 | 0 | 12.89 | 39.95
2021-10-12 20:30 | 44481.8542 | 0 | 12.3552 | 39.95
2021-10-12 21:00 | 44481.875 | 0 | 12.0026 | 39.95
2021-10-12 21:30 | 44481.8958 | 0 | 11.6253 | 39.95
2021-10-12 22:00 | 44481.9167 | 0 | 10.924 | 39.95
2021-10-12 22:30 | 44481.9375 | 0 | 10.0102 | 39.95
2021-10-12 23:00 | 44481.9583 | 0 | 9.641 | 39.95
2021-10-12 23:30 | 44481.9792 | 0 | 9.3012 | 39.95
2021-10-13 | 44482 | 0 | 8.7553 | 39.95
2021-10-13 00:30 | 44482.0208 | 0 | 8.2857 | 39.95
2021-10-13 01:00 | 44482.0417 | 0 | 7.9661 | 39.95
2021-10-13 01:30 | 44482.0625 | 0 | 7.9024 | 39.95
2021-10-13 02:00 | 44482.0833 | 0 | 7.9504 | 39.95
2021-10-13 02:30 | 44482.1042 | 0 | 7.7893 | 39.95
2021-10-13 03:00 | 44482.125 | 0 | 7.6601 | 39.95
2021-10-13 03:30 | 44482.1458 | 0 | 7.9166 | 39.95
2021-10-13 04:00 | 44482.1667 | 0 | 8.2936 | 39.95
2021-10-13 04:30 | 44482.1875 | 0 | 8.744 | 39.95
2021-10-13 05:00 | 44482.2083 | 0 | 9.4167 | 39.95
2021-10-13 05:30 | 44482.2292 | 0 | 9.9822 | 39.95
2021-10-13 06:00 | 44482.25 | 0 | 10.4756 | 39.95
2021-10-13 06:30 | 44482.2708 | 0 | 11.1473 | 39.95
2021-10-13 07:00 | 44482.2917 | 0 | 11.111 | 39.95
2021-10-13 07:30 | 44482.3125 | 0 | 10.7848 | 39.95
2021-10-13 08:00 | 44482.3333 | 0 | 11.815 | 39.95
2021-10-13 08:30 | 44482.3542 | 0 | 10.9842 | 39.95
2021-10-13 09:00 | 44482.375 | 0 | 10.9573 | 39.95
2021-10-13 09:30 | 44482.3958 | 0 | 11.2795 | 39.95
2021-10-13 10:00 | 44482.4167 | 0 | 11.4284 | 39.95
2021-10-13 10:30 | 44482.4375 | 0 | 10.9422 | 39.95
2021-10-13 11:00 | 44482.4583 | 0 | 9.2988 | 39.95
2021-10-13 11:30 | 44482.4792 | 0 | 10.6747 | 39.95
2021-10-13 12:00 | 44482.5 | 0 | 10.7806 | 39.95
2021-10-13 12:30 | 44482.5208 | 0 | 9.6874 | 39.95
2021-10-13 13:00 | 44482.5417 | 0 | 10.7856 | 39.95
2021-10-13 13:30 | 44482.5625 | 0 | 11.4915 | 39.95
2021-10-13 14:00 | 44482.5833 | 0 | 12.0941 | 39.95
2021-10-13 14:30 | 44482.6042 | 0 | 11.3781 | 39.95
2021-10-13 15:00 | 44482.625 | 0 | 10.7065 | 39.95
2021-10-13 15:30 | 44482.6458 | 0 | 11.4482 | 39.95
2021-10-13 16:00 | 44482.6667 | 0 | 12.5353 | 39.95
2021-10-13 16:30 | 44482.6875 | 0 | 12.8777 | 39.95
2021-10-13 17:00 | 44482.7083 | 0 | 12.9414 | 39.95
2021-10-13 17:30 | 44482.7292 | 0 | 13.4733 | 39.95
2021-10-13 18:00 | 44482.75 | 0 | 13.9214 | 39.95
2021-10-13 18:30 | 44482.7708 | 0 | 14.2302 | 39.95
2021-10-13 19:00 | 44482.7917 | 0 | 14.0403 | 39.95
2021-10-13 19:30 | 44482.8125 | 0 | 13.6966 | 39.95
2021-10-13 20:00 | 44482.8333 | 0 | 13.2211 | 39.95
2021-10-13 20:30 | 44482.8542 | 0 | 12.8433 | 39.95
2021-10-13 21:00 | 44482.875 | 0 | 12.3366 | 39.95
2021-10-13 21:30 | 44482.8958 | 0 | 11.9115 | 39.95
2021-10-13 22:00 | 44482.9167 | 0 | 11.4952 | 39.95
2021-10-13 22:30 | 44482.9375 | 0 | 10.6055 | 39.95
2021-10-13 23:00 | 44482.9583 | 0 | 10.0746 | 39.95
2021-10-13 23:30 | 44482.9792 | 0 | 9.4267 | 39.95
2021-10-14 | 44483 | 0 | 8.9983 | 39.95
2021-10-14 00:30 | 44483.0208 | 0 | 8.5757 | 39.95
2021-10-14 01:00 | 44483.0417 | 0 | 8.492 | 39.95
2021-10-14 01:30 | 44483.0625 | 0 | 8.2132 | 39.95
2021-10-14 02:00 | 44483.0833 | 0 | 8.2482 | 39.95
2021-10-14 02:30 | 44483.1042 | 0 | 8.1258 | 39.95
2021-10-14 03:00 | 44483.125 | 0 | 8.0431 | 39.95
2021-10-14 03:30 | 44483.1458 | 0 | 8.3431 | 39.95
2021-10-14 04:00 | 44483.1667 | 0 | 8.5514 | 39.95
2021-10-14 04:30 | 44483.1875 | 0 | 8.8735 | 39.95
2021-10-14 05:00 | 44483.2083 | 0 | 9.6049 | 39.95
2021-10-14 05:30 | 44483.2292 | 0 | 10.532 | 39.95
2021-10-14 06:00 | 44483.25 | 0 | 11.4308 | 39.95
2021-10-14 06:30 | 44483.2708 | 0 | 12.0519 | 39.95
2021-10-14 07:00 | 44483.2917 | 0 | 13.0276 | 39.95
2021-10-14 07:30 | 44483.3125 | 0 | 13.3665 | 39.95
2021-10-14 08:00 | 44483.3333 | 0 | 13.6229 | 39.95
2021-10-14 08:30 | 44483.3542 | 0 | 13.1003 | 39.95
2021-10-14 09:00 | 44483.375 | 0 | 12.5522 | 39.95
2021-10-14 09:30 | 44483.3958 | 0 | 11.0659 | 39.95
2021-10-14 10:00 | 44483.4167 | 0 | 10.3091 | 39.95
2021-10-14 10:30 | 44483.4375 | 0 | 10.9571 | 39.95
2021-10-14 11:00 | 44483.4583 | 0 | 11.2333 | 39.95
2021-10-14 11:30 | 44483.4792 | 0 | 11.0523 | 39.95
2021-10-14 12:00 | 44483.5 | 0 | 11.0754 | 39.95
2021-10-14 12:30 | 44483.5208 | 0 | 10.335 | 39.95
2021-10-14 13:00 | 44483.5417 | 0 | 9.7623 | 39.95
2021-10-14 13:30 | 44483.5625 | 0 | 9.9827 | 39.95
2021-10-14 14:00 | 44483.5833 | 0 | 9.9504 | 39.95
2021-10-14 14:30 | 44483.6042 | 0 | 10.5161 | 39.95
2021-10-14 15:00 | 44483.625 | 0 | 11.1161 | 39.95
2021-10-14 15:30 | 44483.6458 | 0 | 12.1402 | 39.95
2021-10-14 16:00 | 44483.6667 | 0 | 12.6151 | 39.95
2021-10-14 16:30 | 44483.6875 | 0 | 13.1919 | 39.95
2021-10-14 17:00 | 44483.7083 | 0 | 13.3804 | 39.95
2021-10-14 17:30 | 44483.7292 | 0 | 13.8902 | 39.95
2021-10-14 18:00 | 44483.75 | 0 | 14.2613 | 39.95
2021-10-14 18:30 | 44483.7708 | 0 | 14.3642 | 39.95
2021-10-14 19:00 | 44483.7917 | 0 | 13.9661 | 39.95
2021-10-14 19:30 | 44483.8125 | 0 | 13.9091 | 39.95
2021-10-14 20:00 | 44483.8333 | 0 | 13.5437 | 39.95
2021-10-14 20:30 | 44483.8542 | 0 | 13.0199 | 39.95
2021-10-14 21:00 | 44483.875 | 0 | 12.7521 | 39.95
2021-10-14 21:30 | 44483.8958 | 0 | 12.3928 | 39.95
2021-10-14 22:00 | 44483.9167 | 0 | 12.0217 | 39.95
2021-10-14 22:30 | 44483.9375 | 0 | 11.1129 | 39.95
2021-10-14 23:00 | 44483.9583 | 0 | 10.5823 | 39.95
2021-10-14 23:30 | 44483.9792 | 0 | 10.1224 | 39.95
2021-10-15 | 44484 | 0 | 9.4472 | 39.95
2021-10-15 00:30 | 44484.0208 | 0 | 8.9789 | 39.95
2021-10-15 01:00 | 44484.0417 | 0 | 8.8415 | 39.95
2021-10-15 01:30 | 44484.0625 | 0 | 8.7246 | 39.95
2021-10-15 02:00 | 44484.0833 | 0 | 8.6617 | 39.95
2021-10-15 02:30 | 44484.1042 | 0 | 8.5914 | 39.95
2021-10-15 03:00 | 44484.125 | 0 | 8.4417 | 39.95
2021-10-15 03:30 | 44484.1458 | 0 | 8.6956 | 39.95
2021-10-15 04:00 | 44484.1667 | 0 | 8.9688 | 39.95
2021-10-15 04:30 | 44484.1875 | 0 | 9.4033 | 39.95
2021-10-15 05:00 | 44484.2083 | 0 | 9.9579 | 39.95
2021-10-15 05:30 | 44484.2292 | 0 | 10.4301 | 39.95
2021-10-15 06:00 | 44484.25 | 0 | 11.0885 | 39.95
2021-10-15 06:30 | 44484.2708 | 0 | 11.9227 | 39.95
2021-10-15 07:00 | 44484.2917 | 0 | 11.9203 | 39.95
2021-10-15 07:30 | 44484.3125 | 0 | 12.9223 | 39.95
2021-10-15 08:00 | 44484.3333 | 0 | 13.6293 | 39.95
2021-10-15 08:30 | 44484.3542 | 0 | 12.796 | 39.95
2021-10-15 09:00 | 44484.375 | 0 | 11.0144 | 39.95
2021-10-15 09:30 | 44484.3958 | 0 | 13.0149 | 39.95
2021-10-15 10:00 | 44484.4167 | 0 | 13.0503 | 39.95
2021-10-15 10:30 | 44484.4375 | 0 | 12.4461 | 39.95
2021-10-15 11:00 | 44484.4583 | 0 | 11.2689 | 39.95
2021-10-15 11:30 | 44484.4792 | 0 | 10.6365 | 39.95
2021-10-15 12:00 | 44484.5 | 0 | 9.7757 | 39.95
2021-10-15 12:30 | 44484.5208 | 0 | 9.7914 | 39.95
2021-10-15 13:00 | 44484.5417 | 0 | 10.003 | 39.95
2021-10-15 13:30 | 44484.5625 | 0 | 10.2317 | 39.95
2021-10-15 14:00 | 44484.5833 | 0 | 10.8844 | 39.95
2021-10-15 14:30 | 44484.6042 | 0 | 11.5145 | 39.95
2021-10-15 15:00 | 44484.625 | 0 | 12.1681 | 39.95
2021-10-15 15:30 | 44484.6458 | 0 | 13.093 | 39.95
2021-10-15 16:00 | 44484.6667 | 0 | 13.7687 | 39.95
2021-10-15 16:30 | 44484.6875 | 0 | 14.3564 | 39.95
2021-10-15 17:00 | 44484.7083 | 0 | 14.4172 | 39.95
2021-10-15 17:30 | 44484.7292 | 0 | 14.5706 | 39.95
2021-10-15 18:00 | 44484.75 | 0 | 14.4005 | 39.95
2021-10-15 18:30 | 44484.7708 | 0 | 14.7801 | 39.95
2021-10-15 19:00 | 44484.7917 | 0 | 14.3239 | 39.95
2021-10-15 19:30 | 44484.8125 | 0 | 13.9192 | 39.95
2021-10-15 20:00 | 44484.8333 | 0 | 13.1807 | 39.95
2021-10-15 20:30 | 44484.8542 | 0 | 12.4625 | 39.95
2021-10-15 21:00 | 44484.875 | 0 | 11.8932 | 39.95
2021-10-15 21:30 | 44484.8958 | 0 | 11.4451 | 39.95
2021-10-15 22:00 | 44484.9167 | 0 | 10.8175 | 39.95
2021-10-15 22:30 | 44484.9375 | 0 | 10.2039 | 39.95
2021-10-15 23:00 | 44484.9583 | 0 | 9.6466 | 39.95
2021-10-15 23:30 | 44484.9792 | 0 | 9.1264 | 39.95
2021-10-16 | 44485 | 0 | 8.5813 | 39.95
2021-10-16 00:30 | 44485.0208 | 0 | 8.1313 | 39.95
2021-10-16 01:00 | 44485.0417 | 0 | 8.01 | 39.95
2021-10-16 01:30 | 44485.0625 | 0 | 7.8388 | 39.95
2021-10-16 02:00 | 44485.0833 | 0 | 7.638 | 39.95
2021-10-16 02:30 | 44485.1042 | 0 | 7.57 | 39.95
2021-10-16 03:00 | 44485.125 | 0 | 7.4301 | 39.95
2021-10-16 03:30 | 44485.1458 | 0 | 7.4692 | 39.95
2021-10-16 04:00 | 44485.1667 | 0 | 7.5295 | 39.95
2021-10-16 04:30 | 44485.1875 | 0 | 7.5797 | 39.95
2021-10-16 05:00 | 44485.2083 | 0 | 7.777 | 39.95
2021-10-16 05:30 | 44485.2292 | 0 | 7.7048 | 39.95
2021-10-16 06:00 | 44485.25 | 0 | 7.5317 | 39.95
2021-10-16 06:30 | 44485.2708 | 0 | 7.2838 | 39.95
2021-10-16 07:00 | 44485.2917 | 0 | 6.9813 | 39.95
2021-10-16 07:30 | 44485.3125 | 0 | 6.6477 | 39.95
2021-10-16 08:00 | 44485.3333 | 0 | 6.4251 | 39.95
2021-10-16 08:30 | 44485.3542 | 0 | 6.0593 | 39.95
2021-10-16 09:00 | 44485.375 | 0 | 5.9561 | 39.95
2021-10-16 09:30 | 44485.3958 | 0 | 5.7287 | 39.95
2021-10-16 10:00 | 44485.4167 | 0 | 5.4012 | 39.95
2021-10-16 10:30 | 44485.4375 | 0 | 5.3598 | 39.95
2021-10-16 11:00 | 44485.4583 | 0 | 5.2746 | 39.95
2021-10-16 11:30 | 44485.4792 | 0 | 5.2482 | 39.95
2021-10-16 12:00 | 44485.5 | 0 | 5.2962 | 39.95
2021-10-16 12:30 | 44485.5208 | 0 | 5.3252 | 39.95
2021-10-16 13:00 | 44485.5417 | 0 | 5.7059 | 39.95
2021-10-16 13:30 | 44485.5625 | 0 | 6.0354 | 39.95
2021-10-16 14:00 | 44485.5833 | 0 | 6.3849 | 39.95
2021-10-16 14:30 | 44485.6042 | 0 | 6.8643 | 39.95
2021-10-16 15:00 | 44485.625 | 0 | 7.4466 | 39.95
2021-10-16 15:30 | 44485.6458 | 0 | 8.1475 | 39.95
2021-10-16 16:00 | 44485.6667 | 0 | 8.83 | 39.95
2021-10-16 16:30 | 44485.6875 | 0 | 9.5875 | 39.95
2021-10-16 17:00 | 44485.7083 | 0 | 10.202 | 39.95
2021-10-16 17:30 | 44485.7292 | 0 | 10.56 | 39.95
2021-10-16 18:00 | 44485.75 | 0 | 10.9047 | 39.95
2021-10-16 18:30 | 44485.7708 | 0 | 11.2102 | 39.95
2021-10-16 19:00 | 44485.7917 | 0 | 10.9687 | 39.95
2021-10-16 19:30 | 44485.8125 | 0 | 10.9023 | 39.95
2021-10-16 20:00 | 44485.8333 | 0 | 10.6119 | 39.95
2021-10-16 20:30 | 44485.8542 | 0 | 10.1829 | 39.95
2021-10-16 21:00 | 44485.875 | 0 | 9.7921 | 39.95
2021-10-16 21:30 | 44485.8958 | 0 | 9.5305 | 39.95
2021-10-16 22:00 | 44485.9167 | 0 | 9.2519 | 39.95
2021-10-16 22:30 | 44485.9375 | 0 | 8.6948 | 39.95
2021-10-16 23:00 | 44485.9583 | 0 | 8.2614 | 39.95
2021-10-16 23:30 | 44485.9792 | 0 | 8.1058 | 39.95
2021-10-17 | 44486 | 0 | 7.5992 | 39.95
2021-10-17 00:30 | 44486.0208 | 0 | 7.3739 | 39.95
2021-10-17 01:00 | 44486.0417 | 0 | 7.0984 | 39.95
2021-10-17 01:30 | 44486.0625 | 0 | 6.9495 | 39.95
2021-10-17 02:00 | 44486.0833 | 0 | 6.9008 | 39.95
2021-10-17 02:30 | 44486.1042 | 0 | 6.9015 | 39.95
2021-10-17 03:00 | 44486.125 | 0 | 6.8595 | 39.95
2021-10-17 03:30 | 44486.1458 | 0 | 6.9131 | 39.95
2021-10-17 04:00 | 44486.1667 | 0 | 6.7992 | 39.95
2021-10-17 04:30 | 44486.1875 | 0 | 6.8528 | 39.95
2021-10-17 05:00 | 44486.2083 | 0 | 6.9041 | 39.95
2021-10-17 05:30 | 44486.2292 | 0 | 6.7791 | 39.95
2021-10-17 06:00 | 44486.25 | 0 | 6.5941 | 39.95
2021-10-17 06:30 | 44486.2708 | 0 | 6.2826 | 39.95
2021-10-17 07:00 | 44486.2917 | 0 | 5.7983 | 39.95
2021-10-17 07:30 | 44486.3125 | 0 | 5.4934 | 39.95
2021-10-17 08:00 | 44486.3333 | 0 | 5.3152 | 39.95
2021-10-17 08:30 | 44486.3542 | 0 | 5.2266 | 39.95
2021-10-17 09:00 | 44486.375 | 0 | 5.1607 | 39.95
2021-10-17 09:30 | 44486.3958 | 0 | 5.0851 | 39.95
2021-10-17 10:00 | 44486.4167 | 0 | 4.7995 | 39.95
2021-10-17 10:30 | 44486.4375 | 0 | 4.6095 | 39.95
2021-10-17 11:00 | 44486.4583 | 0 | 4.7088 | 39.95
2021-10-17 11:30 | 44486.4792 | 0 | 4.7156 | 39.95
2021-10-17 12:00 | 44486.5 | 0 | 4.7825 | 39.95
2021-10-17 12:30 | 44486.5208 | 0 | 4.8618 | 39.95
2021-10-17 13:00 | 44486.5417 | 0 | 5.3085 | 39.95
2021-10-17 13:30 | 44486.5625 | 0 | 5.7532 | 39.95
2021-10-17 14:00 | 44486.5833 | 0 | 6.1936 | 39.95
2021-10-17 14:30 | 44486.6042 | 0 | 6.9307 | 39.95
2021-10-17 15:00 | 44486.625 | 0 | 7.6973 | 39.95
2021-10-17 15:30 | 44486.6458 | 0 | 8.3874 | 39.95
2021-10-17 16:00 | 44486.6667 | 0 | 9.0771 | 39.95
2021-10-17 16:30 | 44486.6875 | 0 | 9.9744 | 39.95
2021-10-17 17:00 | 44486.7083 | 0 | 10.7623 | 39.95
2021-10-17 17:30 | 44486.7292 | 0 | 11.0487 | 39.95
2021-10-17 18:00 | 44486.75 | 0 | 11.634 | 39.95
2021-10-17 18:30 | 44486.7708 | 0 | 12.006 | 39.95
2021-10-17 19:00 | 44486.7917 | 0 | 11.6923 | 39.95
2021-10-17 19:30 | 44486.8125 | 0 | 11.2784 | 39.95
2021-10-17 20:00 | 44486.8333 | 0 | 10.9382 | 39.95
2021-10-17 20:30 | 44486.8542 | 0 | 10.6328 | 39.95
2021-10-17 21:00 | 44486.875 | 0 | 10.1383 | 39.95
2021-10-17 21:30 | 44486.8958 | 0 | 9.8231 | 39.95
2021-10-17 22:00 | 44486.9167 | 0 | 9.2206 | 39.95
2021-10-17 22:30 | 44486.9375 | 0 | 8.6915 | 39.95
2021-10-17 23:00 | 44486.9583 | 0 | 8.1728 | 39.95
2021-10-17 23:30 | 44486.9792 | 0 | 7.7556 | 39.95
2021-10-18 | 44487 | 0 | 7.4457 | 39.95
2021-10-18 00:30 | 44487.0208 | 0 | 7.3218 | 39.95
2021-10-18 01:00 | 44487.0417 | 0 | 7.1714 | 39.95
2021-10-18 01:30 | 44487.0625 | 0 | 7.0895 | 39.95
2021-10-18 02:00 | 44487.0833 | 0 | 7.1297 | 39.95
2021-10-18 02:30 | 44487.1042 | 0 | 7.2194 | 39.95
2021-10-18 03:00 | 44487.125 | 0 | 7.152 | 39.95
2021-10-18 03:30 | 44487.1458 | 0 | 7.4278 | 39.95
2021-10-18 04:00 | 44487.1667 | 0 | 7.6634 | 39.95
2021-10-18 04:30 | 44487.1875 | 0 | 8.1019 | 39.95
2021-10-18 05:00 | 44487.2083 | 0 | 8.6426 | 39.95
2021-10-18 05:30 | 44487.2292 | 0 | 9.2863 | 39.95
2021-10-18 06:00 | 44487.25 | 0 | 9.6434 | 39.95
2021-10-18 06:30 | 44487.2708 | 0 | 10.1183 | 39.95
2021-10-18 07:00 | 44487.2917 | 0 | 9.6726 | 39.95
2021-10-18 07:30 | 44487.3125 | 0 | 10.6111 | 39.95
2021-10-18 08:00 | 44487.3333 | 0 | 10.4865 | 39.95
2021-10-18 08:30 | 44487.3542 | 0 | 10.8379 | 39.95
2021-10-18 09:00 | 44487.375 | 0 | 11.6356 | 39.95
2021-10-18 09:30 | 44487.3958 | 0 | 11.1497 | 39.95
2021-10-18 10:00 | 44487.4167 | 0 | 9.9739 | 39.95
2021-10-18 10:30 | 44487.4375 | 0 | 10.8204 | 39.95
2021-10-18 11:00 | 44487.4583 | 0 | 11.4371 | 39.95
2021-10-18 11:30 | 44487.4792 | 0 | 10.6706 | 39.95
2021-10-18 12:00 | 44487.5 | 0 | 11.328 | 39.95
2021-10-18 12:30 | 44487.5208 | 0 | 12.9923 | 39.95
2021-10-18 13:00 | 44487.5417 | 0 | 11.8203 | 39.95
2021-10-18 13:30 | 44487.5625 | 0 | 12.9859 | 39.95
2021-10-18 14:00 | 44487.5833 | 0 | 13.0009 | 39.95
2021-10-18 14:30 | 44487.6042 | 0 | 13.5979 | 39.95
2021-10-18 15:00 | 44487.625 | 0 | 13.4908 | 39.95
2021-10-18 15:30 | 44487.6458 | 0 | 13.8163 | 39.95
2021-10-18 16:00 | 44487.6667 | 0 | 13.1305 | 39.95
2021-10-18 16:30 | 44487.6875 | 0 | 12.9156 | 39.95
2021-10-18 17:00 | 44487.7083 | 0 | 13.1707 | 39.95
2021-10-18 17:30 | 44487.7292 | 0 | 13.4331 | 39.95
2021-10-18 18:00 | 44487.75 | 0 | 13.6073 | 39.95
2021-10-18 18:30 | 44487.7708 | 0 | 13.8524 | 39.95
2021-10-18 19:00 | 44487.7917 | 0 | 13.3944 | 39.95
2021-10-18 19:30 | 44487.8125 | 0 | 13.0735 | 39.95
2021-10-18 20:00 | 44487.8333 | 0 | 12.5394 | 39.95
2021-10-18 20:30 | 44487.8542 | 0 | 12.0691 | 39.95
2021-10-18 21:00 | 44487.875 | 0 | 11.4921 | 39.95
2021-10-18 21:30 | 44487.8958 | 0 | 11.1083 | 39.95
2021-10-18 22:00 | 44487.9167 | 0 | 10.5337 | 39.95
2021-10-18 22:30 | 44487.9375 | 0 | 9.7397 | 39.95
2021-10-18 23:00 | 44487.9583 | 0 | 9.1628 | 39.95
2021-10-18 23:30 | 44487.9792 | 0 | 8.6978 | 39.95
2021-10-19 | 44488 | 0 | 8.3111 | 39.95
2021-10-19 00:30 | 44488.0208 | 0 | 8.0125 | 39.95
2021-10-19 01:00 | 44488.0417 | 0 | 7.7948 | 39.95
2021-10-19 01:30 | 44488.0625 | 0 | 7.6247 | 39.95
2021-10-19 02:00 | 44488.0833 | 0 | 7.6567 | 39.95
2021-10-19 02:30 | 44488.1042 | 0 | 7.5931 | 39.95
2021-10-19 03:00 | 44488.125 | 0 | 7.5295 | 39.95
2021-10-19 03:30 | 44488.1458 | 0 | 7.7569 | 39.95
2021-10-19 04:00 | 44488.1667 | 0 | 7.7859 | 39.95
2021-10-19 04:30 | 44488.1875 | 0 | 8.4003 | 39.95
2021-10-19 05:00 | 44488.2083 | 0 | 8.9119 | 39.95
2021-10-19 05:30 | 44488.2292 | 0 | 9.3447 | 39.95
2021-10-19 06:00 | 44488.25 | 0 | 9.5319 | 39.95
2021-10-19 06:30 | 44488.2708 | 0 | 10.5267 | 39.95
2021-10-19 07:00 | 44488.2917 | 0 | 10.5953 | 39.95
2021-10-19 07:30 | 44488.3125 | 0 | 10.7655 | 39.95
2021-10-19 08:00 | 44488.3333 | 0 | 8.8667 | 39.95
2021-10-19 08:30 | 44488.3542 | 0 | 8.5873 | 39.95
2021-10-19 09:00 | 44488.375 | 0 | 8.2333 | 39.95
2021-10-19 09:30 | 44488.3958 | 0 | 8.3881 | 39.95
2021-10-19 10:00 | 44488.4167 | 0 | 7.987 | 39.95
2021-10-19 10:30 | 44488.4375 | 0 | 8.3909 | 39.95
2021-10-19 11:00 | 44488.4583 | 0 | 8.2705 | 39.95
2021-10-19 11:30 | 44488.4792 | 0 | 8.3591 | 39.95
2021-10-19 12:00 | 44488.5 | 0 | 8.4004 | 39.95
2021-10-19 12:30 | 44488.5208 | 0 | 8.8443 | 39.95
2021-10-19 13:00 | 44488.5417 | 0 | 9.0447 | 39.95
2021-10-19 13:30 | 44488.5625 | 0 | 9.6973 | 39.95
2021-10-19 14:00 | 44488.5833 | 0 | 10.4129 | 39.95
2021-10-19 14:30 | 44488.6042 | 0 | 10.8918 | 39.95
2021-10-19 15:00 | 44488.625 | 0 | 11.3621 | 39.95
2021-10-19 15:30 | 44488.6458 | 0 | 11.6297 | 39.95
2021-10-19 16:00 | 44488.6667 | 0 | 12.7023 | 39.95
2021-10-19 16:30 | 44488.6875 | 0 | 13.1176 | 39.95
2021-10-19 17:00 | 44488.7083 | 0 | 13.6832 | 39.95
2021-10-19 17:30 | 44488.7292 | 0 | 13.982 | 39.95
2021-10-19 18:00 | 44488.75 | 0 | 14.1678 | 39.95
2021-10-19 18:30 | 44488.7708 | 0 | 14.6063 | 39.95
2021-10-19 19:00 | 44488.7917 | 0 | 14.3897 | 39.95
2021-10-19 19:30 | 44488.8125 | 0 | 14.1243 | 39.95
2021-10-19 20:00 | 44488.8333 | 0 | 13.586 | 39.95
2021-10-19 20:30 | 44488.8542 | 0 | 12.9269 | 39.95
2021-10-19 21:00 | 44488.875 | 0 | 12.4493 | 39.95
2021-10-19 21:30 | 44488.8958 | 0 | 12.0169 | 39.95
2021-10-19 22:00 | 44488.9167 | 0 | 11.3411 | 39.95
2021-10-19 22:30 | 44488.9375 | 0 | 10.2904 | 39.95
2021-10-19 23:00 | 44488.9583 | 0 | 9.6014 | 39.95
2021-10-19 23:30 | 44488.9792 | 0 | 9.0084 | 39.95
2021-10-20 | 44489 | 0 | 8.7414 | 39.95
2021-10-20 00:30 | 44489.0208 | 0 | 8.4565 | 39.95
2021-10-20 01:00 | 44489.0417 | 0 | 8.2575 | 39.95
2021-10-20 01:30 | 44489.0625 | 0 | 8.0364 | 39.95
2021-10-20 02:00 | 44489.0833 | 0 | 8.1291 | 39.95
2021-10-20 02:30 | 44489.1042 | 0 | 8.0141 | 39.95
2021-10-20 03:00 | 44489.125 | 0 | 7.9058 | 39.95
2021-10-20 03:30 | 44489.1458 | 0 | 8.1563 | 39.95
2021-10-20 04:00 | 44489.1667 | 0 | 8.2515 | 39.95
2021-10-20 04:30 | 44489.1875 | 0 | 8.6271 | 39.95
2021-10-20 05:00 | 44489.2083 | 0 | 9.1884 | 39.95
2021-10-20 05:30 | 44489.2292 | 0 | 9.6753 | 39.95
2021-10-20 06:00 | 44489.25 | 0 | 10.3105 | 39.95
2021-10-20 06:30 | 44489.2708 | 0 | 10.5544 | 39.95
2021-10-20 07:00 | 44489.2917 | 0 | 10.7163 | 39.95
2021-10-20 07:30 | 44489.3125 | 0 | 10.5444 | 39.95
2021-10-20 08:00 | 44489.3333 | 0 | 10.0566 | 39.95
2021-10-20 08:30 | 44489.3542 | 0 | 9.919 | 39.95
2021-10-20 09:00 | 44489.375 | 0 | 9.8133 | 39.95
2021-10-20 09:30 | 44489.3958 | 0 | 10.1513 | 39.95
2021-10-20 10:00 | 44489.4167 | 0 | 9.9447 | 39.95
2021-10-20 10:30 | 44489.4375 | 0 | 9.9198 | 39.95
2021-10-20 11:00 | 44489.4583 | 0 | 9.9983 | 39.95
2021-10-20 11:30 | 44489.4792 | 0 | 9.9927 | 39.95
2021-10-20 12:00 | 44489.5 | 0 | 9.9436 | 39.95
2021-10-20 12:30 | 44489.5208 | 0 | 11.0443 | 39.95
2021-10-20 13:00 | 44489.5417 | 0 | 9.9544 | 39.95
2021-10-20 13:30 | 44489.5625 | 0 | 10.8933 | 39.95
2021-10-20 14:00 | 44489.5833 | 0 | 12.8341 | 39.95
2021-10-20 14:30 | 44489.6042 | 0 | 13.392 | 39.95
2021-10-20 15:00 | 44489.625 | 0 | 13.4449 | 39.95
2021-10-20 15:30 | 44489.6458 | 0 | 12.8407 | 39.95
2021-10-20 16:00 | 44489.6667 | 0 | 13.3564 | 39.95
2021-10-20 16:30 | 44489.6875 | 0 | 13.272 | 39.95
2021-10-20 17:00 | 44489.7083 | 0 | 13.8261 | 39.95
2021-10-20 17:30 | 44489.7292 | 0 | 14.2123 | 39.95
2021-10-20 18:00 | 44489.75 | 0 | 14.6655 | 39.95
2021-10-20 18:30 | 44489.7708 | 0 | 14.7581 | 39.95
2021-10-20 19:00 | 44489.7917 | 0 | 14.3836 | 39.95
2021-10-20 19:30 | 44489.8125 | 0 | 14.1533 | 39.95
2021-10-20 20:00 | 44489.8333 | 0 | 13.5667 | 39.95
2021-10-20 20:30 | 44489.8542 | 0 | 12.6671 | 39.95
2021-10-20 21:00 | 44489.875 | 0 | 12.1108 | 39.95
2021-10-20 21:30 | 44489.8958 | 0 | 11.6819 | 39.95
2021-10-20 22:00 | 44489.9167 | 0 | 11.1224 | 39.95
2021-10-20 22:30 | 44489.9375 | 0 | 10.2762 | 39.95
2021-10-20 23:00 | 44489.9583 | 0 | 9.6982 | 39.95
2021-10-20 23:30 | 44489.9792 | 0 | 9.2606 | 39.95
2021-10-21 | 44490 | 0 | 8.7988 | 39.95
2021-10-21 00:30 | 44490.0208 | 0 | 8.4127 | 39.95
2021-10-21 01:00 | 44490.0417 | 0 | 8.2393 | 39.95
2021-10-21 01:30 | 44490.0625 | 0 | 8.1514 | 39.95
2021-10-21 02:00 | 44490.0833 | 0 | 8.0669 | 39.95
2021-10-21 02:30 | 44490.1042 | 0 | 7.8767 | 39.95
2021-10-21 03:00 | 44490.125 | 0 | 7.8198 | 39.95
2021-10-21 03:30 | 44490.1458 | 0 | 8.0945 | 39.95
2021-10-21 04:00 | 44490.1667 | 0 | 8.2392 | 39.95
2021-10-21 04:30 | 44490.1875 | 0 | 8.5501 | 39.95
2021-10-21 05:00 | 44490.2083 | 0 | 9.1415 | 39.95
2021-10-21 05:30 | 44490.2292 | 0 | 9.5562 | 39.95
2021-10-21 06:00 | 44490.25 | 0 | 9.9968 | 39.95
2021-10-21 06:30 | 44490.2708 | 0 | 10.646 | 39.95
2021-10-21 07:00 | 44490.2917 | 0 | 10.7468 | 39.95
2021-10-21 07:30 | 44490.3125 | 0 | 10.2473 | 39.95
2021-10-21 08:00 | 44490.3333 | 0 | 10.4303 | 39.95
2021-10-21 08:30 | 44490.3542 | 0 | 11.4045 | 39.95
2021-10-21 09:00 | 44490.375 | 0 | 11.3606 | 39.95
2021-10-21 09:30 | 44490.3958 | 0 | 11.2762 | 39.95
2021-10-21 10:00 | 44490.4167 | 0 | 10.7841 | 39.95
2021-10-21 10:30 | 44490.4375 | 0 | 10.8853 | 39.95
2021-10-21 11:00 | 44490.4583 | 0 | 10.7705 | 39.95
2021-10-21 11:30 | 44490.4792 | 0 | 11.1387 | 39.95
2021-10-21 12:00 | 44490.5 | 0 | 11.0562 | 39.95
2021-10-21 12:30 | 44490.5208 | 0 | 12.397 | 39.95
2021-10-21 13:00 | 44490.5417 | 0 | 13.2409 | 39.95
2021-10-21 13:30 | 44490.5625 | 0 | 12.0989 | 39.95
2021-10-21 14:00 | 44490.5833 | 0 | 12.2959 | 39.95
2021-10-21 14:30 | 44490.6042 | 0 | 12.982 | 39.95
2021-10-21 15:00 | 44490.625 | 0 | 10.4717 | 39.95
2021-10-21 15:30 | 44490.6458 | 0 | 12.0699 | 39.95
2021-10-21 16:00 | 44490.6667 | 0 | 13.4016 | 39.95
2021-10-21 16:30 | 44490.6875 | 0 | 13.6136 | 39.95
2021-10-21 17:00 | 44490.7083 | 0 | 13.9408 | 39.95
2021-10-21 17:30 | 44490.7292 | 0 | 14.2729 | 39.95
2021-10-21 18:00 | 44490.75 | 0 | 14.2449 | 39.95
2021-10-21 18:30 | 44490.7708 | 0 | 14.4373 | 39.95
2021-10-21 19:00 | 44490.7917 | 0 | 13.8745 | 39.95
2021-10-21 19:30 | 44490.8125 | 0 | 13.7223 | 39.95
2021-10-21 20:00 | 44490.8333 | 0 | 13.4335 | 39.95
2021-10-21 20:30 | 44490.8542 | 0 | 12.7313 | 39.95
2021-10-21 21:00 | 44490.875 | 0 | 12.1523 | 39.95
2021-10-21 21:30 | 44490.8958 | 0 | 12.1679 | 39.95
2021-10-21 22:00 | 44490.9167 | 0 | 11.4907 | 39.95
2021-10-21 22:30 | 44490.9375 | 0 | 10.5981 | 39.95
2021-10-21 23:00 | 44490.9583 | 0 | 10.005 | 39.95
2021-10-21 23:30 | 44490.9792 | 0 | 9.4867 | 39.95
2021-10-22 | 44491 | 0 | 8.9138 | 39.95
2021-10-22 00:30 | 44491.0208 | 0 | 8.6617 | 39.95
2021-10-22 01:00 | 44491.0417 | 0 | 8.454 | 39.95
2021-10-22 01:30 | 44491.0625 | 0 | 8.3085 | 39.95
2021-10-22 02:00 | 44491.0833 | 0 | 8.2832 | 39.95
2021-10-22 02:30 | 44491.1042 | 0 | 8.195 | 39.95
2021-10-22 03:00 | 44491.125 | 0 | 8.1953 | 39.95
2021-10-22 03:30 | 44491.1458 | 0 | 8.3398 | 39.95
2021-10-22 04:00 | 44491.1667 | 0 | 8.4775 | 39.95
2021-10-22 04:30 | 44491.1875 | 0 | 9.0458 | 39.95
2021-10-22 05:00 | 44491.2083 | 0 | 9.5498 | 39.95
2021-10-22 05:30 | 44491.2292 | 0 | 10.0102 | 39.95
2021-10-22 06:00 | 44491.25 | 0 | 10.7718 | 39.95
2021-10-22 06:30 | 44491.2708 | 0 | 11.2381 | 39.95
2021-10-22 07:00 | 44491.2917 | 0 | 11.5337 | 39.95
2021-10-22 07:30 | 44491.3125 | 0 | 12.3306 | 39.95
2021-10-22 08:00 | 44491.3333 | 0 | 12.694 | 39.95
2021-10-22 08:30 | 44491.3542 | 0 | 13.7942 | 39.95
2021-10-22 09:00 | 44491.375 | 0 | 14.5683 | 39.95
2021-10-22 09:30 | 44491.3958 | 0 | 14.6346 | 39.95
2021-10-22 10:00 | 44491.4167 | 0 | 13.3103 | 39.95
2021-10-22 10:30 | 44491.4375 | 0 | 11.2974 | 39.95
2021-10-22 11:00 | 44491.4583 | 0 | 9.4919 | 39.95
2021-10-22 11:30 | 44491.4792 | 0 | 9.4641 | 39.95
2021-10-22 12:00 | 44491.5 | 0 | 9.173 | 39.95
2021-10-22 12:30 | 44491.5208 | 0 | 10.6336 | 39.95
2021-10-22 13:00 | 44491.5417 | 0 | 12.1261 | 39.95
2021-10-22 13:30 | 44491.5625 | 0 | 10.7587 | 39.95
2021-10-22 14:00 | 44491.5833 | 0 | 10.6869 | 39.95
2021-10-22 14:30 | 44491.6042 | 0 | 10.9281 | 39.95
2021-10-22 15:00 | 44491.625 | 0 | 11.8079 | 39.95
2021-10-22 15:30 | 44491.6458 | 0 | 12.716 | 39.95
2021-10-22 16:00 | 44491.6667 | 0 | 13.2168 | 39.95
2021-10-22 16:30 | 44491.6875 | 0 | 13.6715 | 39.95
2021-10-22 17:00 | 44491.7083 | 0 | 13.8455 | 39.95
2021-10-22 17:30 | 44491.7292 | 0 | 14.0011 | 39.95
2021-10-22 18:00 | 44491.75 | 0 | 14.2895 | 39.95
2021-10-22 18:30 | 44491.7708 | 0 | 14.3352 | 39.95
2021-10-22 19:00 | 44491.7917 | 0 | 13.8645 | 39.95
2021-10-22 19:30 | 44491.8125 | 0 | 13.8131 | 39.95
2021-10-22 20:00 | 44491.8333 | 0 | 13.3069 | 39.95
2021-10-22 20:30 | 44491.8542 | 0 | 13.2135 | 39.95
2021-10-22 21:00 | 44491.875 | 0 | 12.7831 | 39.95
2021-10-22 21:30 | 44491.8958 | 0 | 12.5096 | 39.95
2021-10-22 22:00 | 44491.9167 | 0 | 12.133 | 39.95
2021-10-22 22:30 | 44491.9375 | 0 | 11.2136 | 39.95
2021-10-22 23:00 | 44491.9583 | 0 | 10.5613 | 39.95
2021-10-22 23:30 | 44491.9792 | 0 | 10.1232 | 39.95
2021-10-23 | 44492 | 0 | 9.4657 | 39.95
2021-10-23 00:30 | 44492.0208 | 0 | 8.9849 | 39.95
2021-10-23 01:00 | 44492.0417 | 0 | 8.68 | 39.95
2021-10-23 01:30 | 44492.0625 | 0 | 8.4913 | 39.95
2021-10-23 02:00 | 44492.0833 | 0 | 8.4161 | 39.95
2021-10-23 02:30 | 44492.1042 | 0 | 8.1987 | 39.95
2021-10-23 03:00 | 44492.125 | 0 | 8.0431 | 39.95
2021-10-23 03:30 | 44492.1458 | 0 | 8.1001 | 39.95
2021-10-23 04:00 | 44492.1667 | 0 | 8.1257 | 39.95
2021-10-23 04:30 | 44492.1875 | 0 | 8.416 | 39.95
2021-10-23 05:00 | 44492.2083 | 0 | 8.5501 | 39.95
2021-10-23 05:30 | 44492.2292 | 0 | 8.6576 | 39.95
2021-10-23 06:00 | 44492.25 | 0 | 8.926 | 39.95
2021-10-23 06:30 | 44492.2708 | 0 | 9.0864 | 39.95
2021-10-23 07:00 | 44492.2917 | 0 | 9.3241 | 39.95
2021-10-23 07:30 | 44492.3125 | 0 | 9.2246 | 39.95
2021-10-23 08:00 | 44492.3333 | 0 | 10.3016 | 39.95
2021-10-23 08:30 | 44492.3542 | 0 | 10.3251 | 39.95
2021-10-23 09:00 | 44492.375 | 0 | 10.7872 | 39.95
2021-10-23 09:30 | 44492.3958 | 0 | 10.2233 | 39.95
2021-10-23 10:00 | 44492.4167 | 0 | 9.2739 | 39.95
2021-10-23 10:30 | 44492.4375 | 0 | 9.8776 | 39.95
2021-10-23 11:00 | 44492.4583 | 0 | 9.1631 | 39.95
2021-10-23 11:30 | 44492.4792 | 0 | 9.2172 | 39.95
2021-10-23 12:00 | 44492.5 | 0 | 8.5328 | 39.95
2021-10-23 12:30 | 44492.5208 | 0 | 8.8044 | 39.95
2021-10-23 13:00 | 44492.5417 | 0 | 9.092 | 39.95
2021-10-23 13:30 | 44492.5625 | 0 | 9.7304 | 39.95
2021-10-23 14:00 | 44492.5833 | 0 | 10.1759 | 39.95
2021-10-23 14:30 | 44492.6042 | 0 | 10.5444 | 39.95
2021-10-23 15:00 | 44492.625 | 0 | 11.1699 | 39.95
2021-10-23 15:30 | 44492.6458 | 0 | 12.0438 | 39.95
2021-10-23 16:00 | 44492.6667 | 0 | 13.5817 | 39.95
2021-10-23 16:30 | 44492.6875 | 0 | 13.48 | 39.95
2021-10-23 17:00 | 44492.7083 | 0 | 12.9179 | 39.95
2021-10-23 17:30 | 44492.7292 | 0 | 13.2271 | 39.95
2021-10-23 18:00 | 44492.75 | 0 | 13.2109 | 39.95
2021-10-23 18:30 | 44492.7708 | 0 | 13.7439 | 39.95
2021-10-23 19:00 | 44492.7917 | 0 | 13.5112 | 39.95
2021-10-23 19:30 | 44492.8125 | 0 | 13.2053 | 39.95
2021-10-23 20:00 | 44492.8333 | 0 | 13.0689 | 39.95
2021-10-23 20:30 | 44492.8542 | 0 | 12.5685 | 39.95
2021-10-23 21:00 | 44492.875 | 0 | 12.2472 | 39.95
2021-10-23 21:30 | 44492.8958 | 0 | 11.8165 | 39.95
2021-10-23 22:00 | 44492.9167 | 0 | 11.2928 | 39.95
2021-10-23 22:30 | 44492.9375 | 0 | 10.5751 | 39.95
2021-10-23 23:00 | 44492.9583 | 0 | 10.1223 | 39.95
2021-10-23 23:30 | 44492.9792 | 0 | 9.7427 | 39.95
2021-10-24 | 44493 | 0 | 9.2115 | 39.95
2021-10-24 00:30 | 44493.0208 | 0 | 8.9386 | 39.95
2021-10-24 01:00 | 44493.0417 | 0 | 8.7496 | 39.95
2021-10-24 01:30 | 44493.0625 | 0 | 8.3988 | 39.95
2021-10-24 02:00 | 44493.0833 | 0 | 8.3185 | 39.95
2021-10-24 02:30 | 44493.1042 | 0 | 8.1068 | 39.95
2021-10-24 03:00 | 44493.125 | 0 | 8.0621 | 39.95
2021-10-24 03:30 | 44493.1458 | 0 | 8.0654 | 39.95
2021-10-24 04:00 | 44493.1667 | 0 | 7.9147 | 39.95
2021-10-24 04:30 | 44493.1875 | 0 | 7.8801 | 39.95
2021-10-24 05:00 | 44493.2083 | 0 | 7.7941 | 39.95
2021-10-24 05:30 | 44493.2292 | 0 | 7.6907 | 39.95
2021-10-24 06:00 | 44493.25 | 0 | 7.5912 | 39.95
2021-10-24 06:30 | 44493.2708 | 0 | 7.2381 | 39.95
2021-10-24 07:00 | 44493.2917 | 0 | 7.6693 | 39.95
2021-10-24 07:30 | 44493.3125 | 0 | 7.323 | 39.95
2021-10-24 08:00 | 44493.3333 | 0 | 7.828 | 39.95
2021-10-24 08:30 | 44493.3542 | 0 | 7.6858 | 39.95
2021-10-24 09:00 | 44493.375 | 0 | 7.7826 | 39.95
2021-10-24 09:30 | 44493.3958 | 0 | 8.1034 | 39.95
2021-10-24 10:00 | 44493.4167 | 0 | 8.0621 | 39.95
2021-10-24 10:30 | 44493.4375 | 0 | 8.254 | 39.95
2021-10-24 11:00 | 44493.4583 | 0 | 8.5303 | 39.95
2021-10-24 11:30 | 44493.4792 | 0 | 8.6506 | 39.95
2021-10-24 12:00 | 44493.5 | 0 | 9.2089 | 39.95
2021-10-24 12:30 | 44493.5208 | 0 | 9.3464 | 39.95
2021-10-24 13:00 | 44493.5417 | 0 | 10.3921 | 39.95
2021-10-24 13:30 | 44493.5625 | 0 | 10.7366 | 39.95
2021-10-24 14:00 | 44493.5833 | 0 | 11.7646 | 39.95
2021-10-24 14:30 | 44493.6042 | 0 | 12.0699 | 39.95
2021-10-24 15:00 | 44493.625 | 0 | 13.7462 | 39.95
2021-10-24 15:30 | 44493.6458 | 0 | 14.8791 | 39.95
2021-10-24 16:00 | 44493.6667 | 0 | 14.5013 | 39.95
2021-10-24 16:30 | 44493.6875 | 0 | 14.6859 | 39.95
2021-10-24 17:00 | 44493.7083 | 0 | 14.7113 | 39.95
2021-10-24 17:30 | 44493.7292 | 0 | 15.436 | 39.95
2021-10-24 18:00 | 44493.75 | 0 | 15.8859 | 39.95
2021-10-24 18:30 | 44493.7708 | 0 | 16.3441 | 39.95
2021-10-24 19:00 | 44493.7917 | 0 | 15.7973 | 39.95
2021-10-24 19:30 | 44493.8125 | 0 | 15.449 | 39.95
2021-10-24 20:00 | 44493.8333 | 0 | 14.7352 | 39.95
2021-10-24 20:30 | 44493.8542 | 0 | 14.0732 | 39.95
2021-10-24 21:00 | 44493.875 | 0 | 13.3538 | 39.95
2021-10-24 21:30 | 44493.8958 | 0 | 12.6619 | 39.95
2021-10-24 22:00 | 44493.9167 | 0 | 11.6514 | 39.95
2021-10-24 22:30 | 44493.9375 | 0 | 10.6159 | 39.95
2021-10-24 23:00 | 44493.9583 | 0 | 9.8677 | 39.95
2021-10-24 23:30 | 44493.9792 | 0 | 9.602 | 39.95
2021-10-25 | 44494 | 0 | 9.1754 | 39.95
2021-10-25 00:30 | 44494.0208 | 0 | 8.9444 | 39.95
2021-10-25 01:00 | 44494.0417 | 0 | 8.6625 | 39.95
2021-10-25 01:30 | 44494.0625 | 0 | 8.5344 | 39.95
2021-10-25 02:00 | 44494.0833 | 0 | 8.4797 | 39.95
2021-10-25 02:30 | 44494.1042 | 0 | 8.4539 | 39.95
2021-10-25 03:00 | 44494.125 | 0 | 8.3275 | 39.95
2021-10-25 03:30 | 44494.1458 | 0 | 8.6141 | 39.95
2021-10-25 04:00 | 44494.1667 | 0 | 8.9047 | 39.95
2021-10-25 04:30 | 44494.1875 | 0 | 9.1227 | 39.95
2021-10-25 05:00 | 44494.2083 | 0 | 9.6523 | 39.95
2021-10-25 05:30 | 44494.2292 | 0 | 10.1154 | 39.95
2021-10-25 06:00 | 44494.25 | 0 | 11.1404 | 39.95
2021-10-25 06:30 | 44494.2708 | 0 | 11.6779 | 39.95
2021-10-25 07:00 | 44494.2917 | 0 | 12.1238 | 39.95
2021-10-25 07:30 | 44494.3125 | 0 | 12.3514 | 39.95
2021-10-25 08:00 | 44494.3333 | 0 | 12.4496 | 39.95
2021-10-25 08:30 | 44494.3542 | 0 | 11.7588 | 39.95
2021-10-25 09:00 | 44494.375 | 0 | 12.1601 | 39.95
2021-10-25 09:30 | 44494.3958 | 0 | 13.0647 | 39.95
2021-10-25 10:00 | 44494.4167 | 0 | 12.0679 | 39.95
2021-10-25 10:30 | 44494.4375 | 0 | 12.5948 | 39.95
2021-10-25 11:00 | 44494.4583 | 0 | 12.9067 | 39.95
2021-10-25 11:30 | 44494.4792 | 0 | 15.1009 | 39.95
2021-10-25 12:00 | 44494.5 | 0 | 15.5856 | 39.95
2021-10-25 12:30 | 44494.5208 | 0 | 15.2312 | 39.95
2021-10-25 13:00 | 44494.5417 | 0 | 14.681 | 39.95
2021-10-25 13:30 | 44494.5625 | 0 | 14.1341 | 39.95
2021-10-25 14:00 | 44494.5833 | 0 | 12.8716 | 39.95
2021-10-25 14:30 | 44494.6042 | 0 | 13.5561 | 39.95
2021-10-25 15:00 | 44494.625 | 0 | 13.2812 | 39.95
2021-10-25 15:30 | 44494.6458 | 0 | 13.5465 | 39.95
2021-10-25 16:00 | 44494.6667 | 0 | 14.23 | 39.95
2021-10-25 16:30 | 44494.6875 | 0 | 14.412 | 39.95
2021-10-25 17:00 | 44494.7083 | 0 | 14.7931 | 39.95
2021-10-25 17:30 | 44494.7292 | 0 | 15.1036 | 39.95
2021-10-25 18:00 | 44494.75 | 0 | 15.3046 | 39.95
2021-10-25 18:30 | 44494.7708 | 0 | 15.3602 | 39.95
2021-10-25 19:00 | 44494.7917 | 0 | 15.0663 | 39.95
2021-10-25 19:30 | 44494.8125 | 0 | 14.5424 | 39.95
2021-10-25 20:00 | 44494.8333 | 0 | 14.2077 | 39.95
2021-10-25 20:30 | 44494.8542 | 0 | 13.504 | 39.95
2021-10-25 21:00 | 44494.875 | 0 | 12.8808 | 39.95
2021-10-25 21:30 | 44494.8958 | 0 | 12.5321 | 39.95
2021-10-25 22:00 | 44494.9167 | 0 | 11.982 | 39.95
2021-10-25 22:30 | 44494.9375 | 0 | 11.0986 | 39.95
2021-10-25 23:00 | 44494.9583 | 0 | 10.4614 | 39.95
2021-10-25 23:30 | 44494.9792 | 0 | 9.8561 | 39.95
2021-10-26 | 44495 | 0 | 9.4053 | 39.95
2021-10-26 00:30 | 44495.0208 | 0 | 8.8513 | 39.95
2021-10-26 01:00 | 44495.0417 | 0 | 8.738 | 39.95
2021-10-26 01:30 | 44495.0625 | 0 | 8.684 | 39.95
2021-10-26 02:00 | 44495.0833 | 0 | 8.6015 | 39.95
2021-10-26 02:30 | 44495.1042 | 0 | 8.5244 | 39.95
2021-10-26 03:00 | 44495.125 | 0 | 8.4641 | 39.95
2021-10-26 03:30 | 44495.1458 | 0 | 8.6509 | 39.95
2021-10-26 04:00 | 44495.1667 | 0 | 8.8389 | 39.95
2021-10-26 04:30 | 44495.1875 | 0 | 9.4375 | 39.95
2021-10-26 05:00 | 44495.2083 | 0 | 9.9311 | 39.95
2021-10-26 05:30 | 44495.2292 | 0 | 10.4078 | 39.95
2021-10-26 06:00 | 44495.25 | 0 | 10.8817 | 39.95
2021-10-26 06:30 | 44495.2708 | 0 | 11.6887 | 39.95
2021-10-26 07:00 | 44495.2917 | 0 | 12.2966 | 39.95
2021-10-26 07:30 | 44495.3125 | 0 | 12.6475 | 39.95
2021-10-26 08:00 | 44495.3333 | 0 | 12.5159 | 39.95
2021-10-26 08:30 | 44495.3542 | 0 | 13.1959 | 39.95
2021-10-26 09:00 | 44495.375 | 0 | 13.7176 | 39.95
2021-10-26 09:30 | 44495.3958 | 0 | 13.8321 | 39.95
2021-10-26 10:00 | 44495.4167 | 0 | 11.932 | 39.95
2021-10-26 10:30 | 44495.4375 | 0 | 11.0819 | 39.95
2021-10-26 11:00 | 44495.4583 | 0 | 11.5952 | 39.95
2021-10-26 11:30 | 44495.4792 | 0 | 12.4733 | 39.95
2021-10-26 12:00 | 44495.5 | 0 | 12.9366 | 39.95
2021-10-26 12:30 | 44495.5208 | 0 | 11.959 | 39.95
2021-10-26 13:00 | 44495.5417 | 0 | 12.1098 | 39.95
2021-10-26 13:30 | 44495.5625 | 0 | 13.3562 | 39.95
2021-10-26 14:00 | 44495.5833 | 0 | 13.564 | 39.95
2021-10-26 14:30 | 44495.6042 | 0 | 13.0301 | 39.95
2021-10-26 15:00 | 44495.625 | 0 | 13.9746 | 39.95
2021-10-26 15:30 | 44495.6458 | 0 | 14.5784 | 39.95
2021-10-26 16:00 | 44495.6667 | 0 | 14.4987 | 39.95
2021-10-26 16:30 | 44495.6875 | 0 | 14.498 | 39.95
2021-10-26 17:00 | 44495.7083 | 0 | 14.5799 | 39.95
2021-10-26 17:30 | 44495.7292 | 0 | 14.4634 | 39.95
2021-10-26 18:00 | 44495.75 | 0 | 14.6508 | 39.95
2021-10-26 18:30 | 44495.7708 | 0 | 15.2465 | 39.95
2021-10-26 19:00 | 44495.7917 | 0 | 15.007 | 39.95
2021-10-26 19:30 | 44495.8125 | 0 | 14.7585 | 39.95
2021-10-26 20:00 | 44495.8333 | 0 | 14.2475 | 39.95
2021-10-26 20:30 | 44495.8542 | 0 | 13.7841 | 39.95
2021-10-26 21:00 | 44495.875 | 0 | 13.3384 | 39.95
2021-10-26 21:30 | 44495.8958 | 0 | 12.9358 | 39.95
2021-10-26 22:00 | 44495.9167 | 0 | 12.2463 | 39.95
2021-10-26 22:30 | 44495.9375 | 0 | 11.4073 | 39.95
2021-10-26 23:00 | 44495.9583 | 0 | 10.9148 | 39.95
2021-10-26 23:30 | 44495.9792 | 0 | 10.2465 | 39.95
2021-10-27 | 44496 | 0 | 9.6244 | 39.95
2021-10-27 00:30 | 44496.0208 | 0 | 9.3648 | 39.95
2021-10-27 01:00 | 44496.0417 | 0 | 9.2349 | 39.95
2021-10-27 01:30 | 44496.0625 | 0 | 8.8824 | 39.95
2021-10-27 02:00 | 44496.0833 | 0 | 8.8784 | 39.95
2021-10-27 02:30 | 44496.1042 | 0 | 8.7395 | 39.95
2021-10-27 03:00 | 44496.125 | 0 | 8.5884 | 39.95
2021-10-27 03:30 | 44496.1458 | 0 | 8.8378 | 39.95
2021-10-27 04:00 | 44496.1667 | 0 | 9.0671 | 39.95
2021-10-27 04:30 | 44496.1875 | 0 | 9.5226 | 39.95
2021-10-27 05:00 | 44496.2083 | 0 | 10.137 | 39.95
2021-10-27 05:30 | 44496.2292 | 0 | 10.6437 | 39.95
2021-10-27 06:00 | 44496.25 | 0 | 11.0916 | 39.95
2021-10-27 06:30 | 44496.2708 | 0 | 12.2635 | 39.95
2021-10-27 07:00 | 44496.2917 | 0 | 12.6479 | 39.95
2021-10-27 07:30 | 44496.3125 | 0 | 12.0401 | 39.95
2021-10-27 08:00 | 44496.3333 | 0 | 11.8086 | 39.95
2021-10-27 08:30 | 44496.3542 | 0 | 11.8518 | 39.95
2021-10-27 09:00 | 44496.375 | 0 | 12.3696 | 39.95
2021-10-27 09:30 | 44496.3958 | 0 | 12.2729 | 39.95
2021-10-27 10:00 | 44496.4167 | 0 | 12.0107 | 39.95
2021-10-27 10:30 | 44496.4375 | 0 | 12.945 | 39.95
2021-10-27 11:00 | 44496.4583 | 0 | 13.5134 | 39.95
2021-10-27 11:30 | 44496.4792 | 0 | 12.5454 | 39.95
2021-10-27 12:00 | 44496.5 | 0 | 12.2026 | 39.95
2021-10-27 12:30 | 44496.5208 | 0 | 12.3392 | 39.95
2021-10-27 13:00 | 44496.5417 | 0 | 12.7422 | 39.95
2021-10-27 13:30 | 44496.5625 | 0 | 13.1539 | 39.95
2021-10-27 14:00 | 44496.5833 | 0 | 13.7906 | 39.95
2021-10-27 14:30 | 44496.6042 | 0 | 13.8273 | 39.95
2021-10-27 15:00 | 44496.625 | 0 | 14.0017 | 39.95
2021-10-27 15:30 | 44496.6458 | 0 | 14.8841 | 39.95
2021-10-27 16:00 | 44496.6667 | 0 | 15.3235 | 39.95
2021-10-27 16:30 | 44496.6875 | 0 | 15.9755 | 39.95
2021-10-27 17:00 | 44496.7083 | 0 | 15.8655 | 39.95
2021-10-27 17:30 | 44496.7292 | 0 | 16.0959 | 39.95
2021-10-27 18:00 | 44496.75 | 0 | 16.1666 | 39.95
2021-10-27 18:30 | 44496.7708 | 0 | 16.6293 | 39.95
2021-10-27 19:00 | 44496.7917 | 0 | 16.604 | 39.95
2021-10-27 19:30 | 44496.8125 | 0 | 16.0374 | 39.95
2021-10-27 20:00 | 44496.8333 | 0 | 15.7066 | 39.95
2021-10-27 20:30 | 44496.8542 | 0 | 15.0445 | 39.95
2021-10-27 21:00 | 44496.875 | 0 | 14.6388 | 39.95
2021-10-27 21:30 | 44496.8958 | 0 | 14.2933 | 39.95
2021-10-27 22:00 | 44496.9167 | 0 | 13.3568 | 39.95
2021-10-27 22:30 | 44496.9375 | 0 | 12.4065 | 39.95
2021-10-27 23:00 | 44496.9583 | 0 | 11.6198 | 39.95
2021-10-27 23:30 | 44496.9792 | 0 | 11.069 | 39.95
2021-10-28 | 44497 | 0 | 10.5489 | 39.95
2021-10-28 00:30 | 44497.0208 | 0 | 10.1256 | 39.95
2021-10-28 01:00 | 44497.0417 | 0 | 9.9224 | 39.95
2021-10-28 01:30 | 44497.0625 | 0 | 9.6308 | 39.95
2021-10-28 02:00 | 44497.0833 | 0 | 9.5896 | 39.95
2021-10-28 02:30 | 44497.1042 | 0 | 9.4244 | 39.95
2021-10-28 03:00 | 44497.125 | 0 | 9.3805 | 39.95
2021-10-28 03:30 | 44497.1458 | 0 | 9.5528 | 39.95
2021-10-28 04:00 | 44497.1667 | 0 | 9.7869 | 39.95
2021-10-28 04:30 | 44497.1875 | 0 | 10.3151 | 39.95
2021-10-28 05:00 | 44497.2083 | 0 | 10.8153 | 39.95
2021-10-28 05:30 | 44497.2292 | 0 | 11.4341 | 39.95
2021-10-28 06:00 | 44497.25 | 0 | 12.1618 | 39.95
2021-10-28 06:30 | 44497.2708 | 0 | 12.4939 | 39.95
2021-10-28 07:00 | 44497.2917 | 0 | 13.4197 | 39.95
2021-10-28 07:30 | 44497.3125 | 0 | 13.8495 | 39.95
2021-10-28 08:00 | 44497.3333 | 0 | 14.1774 | 39.95
2021-10-28 08:30 | 44497.3542 | 0 | 13.9732 | 39.95
2021-10-28 09:00 | 44497.375 | 0 | 13.1673 | 39.95
2021-10-28 09:30 | 44497.3958 | 0 | 13.1408 | 39.95
2021-10-28 10:00 | 44497.4167 | 0 | 13.6709 | 39.95
2021-10-28 10:30 | 44497.4375 | 0 | 13.5086 | 39.95
2021-10-28 11:00 | 44497.4583 | 0 | 13.522 | 39.95
2021-10-28 11:30 | 44497.4792 | 0 | 13.6843 | 39.95
2021-10-28 12:00 | 44497.5 | 0 | 13.8206 | 39.95
2021-10-28 12:30 | 44497.5208 | 0 | 13.7859 | 39.95
2021-10-28 13:00 | 44497.5417 | 0 | 13.9899 | 39.95
2021-10-28 13:30 | 44497.5625 | 0 | 14.1074 | 39.95
2021-10-28 14:00 | 44497.5833 | 0 | 14.6918 | 39.95
2021-10-28 14:30 | 44497.6042 | 0 | 15.4917 | 39.95
2021-10-28 15:00 | 44497.625 | 0 | 15.7825 | 39.95
2021-10-28 15:30 | 44497.6458 | 0 | 16.6176 | 39.95
2021-10-28 16:00 | 44497.6667 | 0 | 17.2226 | 39.95
2021-10-28 16:30 | 44497.6875 | 0 | 17.4872 | 39.95
2021-10-28 17:00 | 44497.7083 | 0 | 17.1109 | 39.95
2021-10-28 17:30 | 44497.7292 | 0 | 16.9151 | 39.95
2021-10-28 18:00 | 44497.75 | 0 | 16.8866 | 39.95
2021-10-28 18:30 | 44497.7708 | 0 | 17.2207 | 39.95
2021-10-28 19:00 | 44497.7917 | 0 | 16.8204 | 39.95
2021-10-28 19:30 | 44497.8125 | 0 | 16.7305 | 39.95
2021-10-28 20:00 | 44497.8333 | 0 | 16.2442 | 39.95
2021-10-28 20:30 | 44497.8542 | 0 | 15.7411 | 39.95
2021-10-28 21:00 | 44497.875 | 0 | 15.1469 | 39.95
2021-10-28 21:30 | 44497.8958 | 0 | 14.5879 | 39.95
2021-10-28 22:00 | 44497.9167 | 0 | 13.7607 | 39.95
2021-10-28 22:30 | 44497.9375 | 0 | 12.7455 | 39.95
2021-10-28 23:00 | 44497.9583 | 0 | 12.1065 | 39.95
2021-10-28 23:30 | 44497.9792 | 0 | 11.4673 | 39.95
2021-10-29 | 44498 | 0 | 10.7739 | 39.95
2021-10-29 00:30 | 44498.0208 | 0 | 10.3578 | 39.95
2021-10-29 01:00 | 44498.0417 | 0 | 9.932 | 39.95
2021-10-29 01:30 | 44498.0625 | 0 | 9.7536 | 39.95
2021-10-29 02:00 | 44498.0833 | 0 | 9.6436 | 39.95
2021-10-29 02:30 | 44498.1042 | 0 | 9.3708 | 39.95
2021-10-29 03:00 | 44498.125 | 0 | 9.1287 | 39.95
2021-10-29 03:30 | 44498.1458 | 0 | 9.3649 | 39.95
2021-10-29 04:00 | 44498.1667 | 0 | 9.4921 | 39.95
2021-10-29 04:30 | 44498.1875 | 0 | 9.4623 | 39.95
2021-10-29 05:00 | 44498.2083 | 0 | 9.5427 | 39.95
2021-10-29 05:30 | 44498.2292 | 0 | 9.4914 | 39.95
2021-10-29 06:00 | 44498.25 | 0 | 9.6444 | 39.95
2021-10-29 06:30 | 44498.2708 | 0 | 9.536 | 39.95
2021-10-29 07:00 | 44498.2917 | 0 | 9.7679 | 39.95
2021-10-29 07:30 | 44498.3125 | 0 | 10.2234 | 39.95
2021-10-29 08:00 | 44498.3333 | 0 | 11.4275 | 39.95
2021-10-29 08:30 | 44498.3542 | 0 | 11.8504 | 39.95
2021-10-29 09:00 | 44498.375 | 0 | 11.3879 | 39.95
2021-10-29 09:30 | 44498.3958 | 0 | 10.0851 | 39.95
2021-10-29 10:00 | 44498.4167 | 0 | 11.4865 | 39.95
2021-10-29 10:30 | 44498.4375 | 0 | 11.5416 | 39.95
2021-10-29 11:00 | 44498.4583 | 0 | 11.6578 | 39.95
2021-10-29 11:30 | 44498.4792 | 0 | 12.3234 | 39.95
2021-10-29 12:00 | 44498.5 | 0 | 11.9607 | 39.95
2021-10-29 12:30 | 44498.5208 | 0 | 12.1923 | 39.95
2021-10-29 13:00 | 44498.5417 | 0 | 11.2684 | 39.95
2021-10-29 13:30 | 44498.5625 | 0 | 11.9006 | 39.95
2021-10-29 14:00 | 44498.5833 | 0 | 13.0592 | 39.95
2021-10-29 14:30 | 44498.6042 | 0 | 13.5846 | 39.95
2021-10-29 15:00 | 44498.625 | 0 | 12.9315 | 39.95
2021-10-29 15:30 | 44498.6458 | 0 | 12.4124 | 39.95
2021-10-29 16:00 | 44498.6667 | 0 | 12.2093 | 39.95
2021-10-29 16:30 | 44498.6875 | 0 | 12.2227 | 39.95
2021-10-29 17:00 | 44498.7083 | 0 | 12.2952 | 39.95
2021-10-29 17:30 | 44498.7292 | 0 | 12.2897 | 39.95
2021-10-29 18:00 | 44498.75 | 0 | 12.4333 | 39.95
2021-10-29 18:30 | 44498.7708 | 0 | 12.5766 | 39.95
2021-10-29 19:00 | 44498.7917 | 0 | 12.4501 | 39.95
2021-10-29 19:30 | 44498.8125 | 0 | 12.2688 | 39.95
2021-10-29 20:00 | 44498.8333 | 0 | 11.9521 | 39.95
2021-10-29 20:30 | 44498.8542 | 0 | 11.6164 | 39.95
2021-10-29 21:00 | 44498.875 | 0 | 11.3599 | 39.95
2021-10-29 21:30 | 44498.8958 | 0 | 11.0584 | 39.95
2021-10-29 22:00 | 44498.9167 | 0 | 10.7212 | 39.95
2021-10-29 22:30 | 44498.9375 | 0 | 9.9899 | 39.95
2021-10-29 23:00 | 44498.9583 | 0 | 9.5034 | 39.95
2021-10-29 23:30 | 44498.9792 | 0 | 9.1936 | 39.95
2021-10-30 | 44499 | 0 | 8.7653 | 39.95
2021-10-30 00:30 | 44499.0208 | 0 | 8.454 | 39.95
2021-10-30 01:00 | 44499.0417 | 0 | 8.1764 | 39.95
2021-10-30 01:30 | 44499.0625 | 0 | 8.0243 | 39.95
2021-10-30 02:00 | 44499.0833 | 0 | 8.0878 | 39.95
2021-10-30 02:30 | 44499.1042 | 0 | 8.0107 | 39.95
2021-10-30 03:00 | 44499.125 | 0 | 7.8767 | 39.95
2021-10-30 03:30 | 44499.1458 | 0 | 7.8834 | 39.95
2021-10-30 04:00 | 44499.1667 | 0 | 7.9225 | 39.95
2021-10-30 04:30 | 44499.1875 | 0 | 8.215 | 39.95
2021-10-30 05:00 | 44499.2083 | 0 | 8.125 | 39.95
2021-10-30 05:30 | 44499.2292 | 0 | 7.9728 | 39.95
2021-10-30 06:00 | 44499.25 | 0 | 7.9337 | 39.95
2021-10-30 06:30 | 44499.2708 | 0 | 7.892 | 39.95
2021-10-30 07:00 | 44499.2917 | 0 | 8.5192 | 39.95
2021-10-30 07:30 | 44499.3125 | 0 | 8.4767 | 39.95
2021-10-30 08:00 | 44499.3333 | 0 | 8.226 | 39.95
2021-10-30 08:30 | 44499.3542 | 0 | 8.098 | 39.95
2021-10-30 09:00 | 44499.375 | 0 | 8.1526 | 39.95
2021-10-30 09:30 | 44499.3958 | 0 | 8.2422 | 39.95
2021-10-30 10:00 | 44499.4167 | 0 | 8.3846 | 39.95
2021-10-30 10:30 | 44499.4375 | 0 | 9.287 | 39.95
2021-10-30 11:00 | 44499.4583 | 0 | 10.1746 | 39.95
2021-10-30 11:30 | 44499.4792 | 0 | 10.0483 | 39.95
2021-10-30 12:00 | 44499.5 | 0 | 10.519 | 39.95
2021-10-30 12:30 | 44499.5208 | 0 | 10.6736 | 39.95
2021-10-30 13:00 | 44499.5417 | 0 | 12.262 | 39.95
2021-10-30 13:30 | 44499.5625 | 0 | 12.7467 | 39.95
2021-10-30 14:00 | 44499.5833 | 0 | 13.3826 | 39.95
2021-10-30 14:30 | 44499.6042 | 0 | 14.2895 | 39.95
2021-10-30 15:00 | 44499.625 | 0 | 14.4238 | 39.95
2021-10-30 15:30 | 44499.6458 | 0 | 15.5587 | 39.95
2021-10-30 16:00 | 44499.6667 | 0 | 15.2207 | 39.95
2021-10-30 16:30 | 44499.6875 | 0 | 14.9733 | 39.95
2021-10-30 17:00 | 44499.7083 | 0 | 14.8278 | 39.95
2021-10-30 17:30 | 44499.7292 | 0 | 14.0759 | 39.95
2021-10-30 18:00 | 44499.75 | 0 | 13.6955 | 39.95
2021-10-30 18:30 | 44499.7708 | 0 | 13.7413 | 39.95
2021-10-30 19:00 | 44499.7917 | 0 | 13.5538 | 39.95
2021-10-30 19:30 | 44499.8125 | 0 | 13.0869 | 39.95
2021-10-30 20:00 | 44499.8333 | 0 | 12.5351 | 39.95
2021-10-30 20:30 | 44499.8542 | 0 | 11.8834 | 39.95
2021-10-30 21:00 | 44499.875 | 0 | 11.5023 | 39.95
2021-10-30 21:30 | 44499.8958 | 0 | 11.0926 | 39.95
2021-10-30 22:00 | 44499.9167 | 0 | 10.5065 | 39.95
2021-10-30 22:30 | 44499.9375 | 0 | 10.0181 | 39.95
2021-10-30 23:00 | 44499.9583 | 0 | 9.708 | 39.95
2021-10-30 23:30 | 44499.9792 | 0 | 9.3327 | 39.95
2021-10-31 | 44500 | 0 | 8.709 | 39.95
2021-10-31 00:30 | 44500.0208 | 0 | 8.4727 | 39.95
2021-10-31 01:00 | 44500.0417 | 0 | 8.3733 | 39.95
2021-10-31 01:30 | 44500.0625 | 0 | 8.1224 | 39.95
2021-10-31 02:00 | 44500.0833 | 0 | 8.0141 | 39.95
2021-10-31 02:30 | 44500.1042 | 0 | 7.8501 | 39.95
2021-10-31 03:00 | 44500.125 | 0 | 7.7535 | 39.95
2021-10-31 03:30 | 44500.1458 | 0 | 7.7941 | 39.95
2021-10-31 04:00 | 44500.1667 | 0 | 7.7472 | 39.95
2021-10-31 04:30 | 44500.1875 | 0 | 7.6973 | 39.95
2021-10-31 05:00 | 44500.2083 | 0 | 7.6467 | 39.95
2021-10-31 05:30 | 44500.2292 | 0 | 7.3549 | 39.95
2021-10-31 06:00 | 44500.25 | 0 | 7.2812 | 39.95
2021-10-31 06:30 | 44500.2708 | 0 | 7.0407 | 39.95
2021-10-31 07:00 | 44500.2917 | 0 | 6.7958 | 39.95
2021-10-31 07:30 | 44500.3125 | 0 | 6.9778 | 39.95
2021-10-31 08:00 | 44500.3333 | 0 | 7.2364 | 39.95
2021-10-31 08:30 | 44500.3542 | 0 | 6.7347 | 39.95
2021-10-31 09:00 | 44500.375 | 0 | 6.6095 | 39.95
2021-10-31 09:30 | 44500.3958 | 0 | 6.7585 | 39.95
2021-10-31 10:00 | 44500.4167 | 0 | 7.9172 | 39.95
2021-10-31 10:30 | 44500.4375 | 0 | 7.0417 | 39.95
2021-10-31 11:00 | 44500.4583 | 0 | 7.9904 | 39.95
2021-10-31 11:30 | 44500.4792 | 0 | 7.6295 | 39.95
2021-10-31 12:00 | 44500.5 | 0 | 7.7068 | 39.95
2021-10-31 12:30 | 44500.5208 | 0 | 7.7379 | 39.95
2021-10-31 13:00 | 44500.5417 | 0 | 7.089 | 39.95
2021-10-31 13:30 | 44500.5625 | 0 | 8.6423 | 39.95
2021-10-31 14:00 | 44500.5833 | 0 | 7.6743 | 39.95
2021-10-31 14:30 | 44500.6042 | 0 | 7.6772 | 39.95
2021-10-31 15:00 | 44500.625 | 0 | 7.4052 | 39.95
2021-10-31 15:30 | 44500.6458 | 0 | 8.7128 | 39.95
2021-10-31 16:00 | 44500.6667 | 0 | 8.5028 | 39.95
2021-10-31 16:30 | 44500.6875 | 0 | 9.1251 | 39.95
2021-10-31 17:00 | 44500.7083 | 0 | 9.7082 | 39.95
2021-10-31 17:30 | 44500.7292 | 0 | 10.3183 | 39.95
2021-10-31 18:00 | 44500.75 | 0 | 10.8935 | 39.95
2021-10-31 18:30 | 44500.7708 | 0 | 11.2962 | 39.95
2021-10-31 19:00 | 44500.7917 | 0 | 11.1663 | 39.95
2021-10-31 19:30 | 44500.8125 | 0 | 10.8544 | 39.95
2021-10-31 20:00 | 44500.8333 | 0 | 10.5756 | 39.95
2021-10-31 20:30 | 44500.8542 | 0 | 10.2917 | 39.95
2021-10-31 21:00 | 44500.875 | 0 | 9.8375 | 39.95
2021-10-31 21:30 | 44500.8958 | 0 | 9.421 | 39.95
2021-10-31 22:00 | 44500.9167 | 0 | 9.0451 | 39.95
2021-10-31 22:30 | 44500.9375 | 0 | 8.356 | 39.95
2021-10-31 23:00 | 44500.9583 | 0 | 8.0007 | 39.95
2021-10-31 23:30 | 44500.9792 | 0 | 7.7438 | 39.95
2021-11-01 | 44501 | 0 | 7.4555 | 37.78
2021-11-01 00:30 | 44501.0208 | 0 | 7.2622 | 37.78
2021-11-01 01:00 | 44501.0417 | 0 | 7.3218 | 37.78
2021-11-01 01:30 | 44501.0625 | 0 | 7.1044 | 37.78
2021-11-01 02:00 | 44501.0833 | 0 | 7.0761 | 37.78
2021-11-01 02:30 | 44501.1042 | 0 | 7.1267 | 37.78
2021-11-01 03:00 | 44501.125 | 0 | 7.1424 | 37.78
2021-11-01 03:30 | 44501.1458 | 0 | 7.3348 | 37.78
2021-11-01 04:00 | 44501.1667 | 0 | 7.3128 | 37.78
2021-11-01 04:30 | 44501.1875 | 0 | 7.8673 | 37.78
2021-11-01 05:00 | 44501.2083 | 0 | 8.5549 | 37.78
2021-11-01 05:30 | 44501.2292 | 0 | 8.8802 | 37.78
2021-11-01 06:00 | 44501.25 | 0 | 9.5413 | 37.78
2021-11-01 06:30 | 44501.2708 | 0 | 10.6646 | 37.78
2021-11-01 07:00 | 44501.2917 | 0 | 11.2021 | 37.78
2021-11-01 07:30 | 44501.3125 | 0 | 11.1851 | 37.78
2021-11-01 08:00 | 44501.3333 | 0 | 11.1929 | 37.78
2021-11-01 08:30 | 44501.3542 | 0 | 10.5364 | 37.78
2021-11-01 09:00 | 44501.375 | 0 | 10.9396 | 37.78
2021-11-01 09:30 | 44501.3958 | 0 | 10.3835 | 37.78
2021-11-01 10:00 | 44501.4167 | 0 | 10.4076 | 37.78
2021-11-01 10:30 | 44501.4375 | 0 | 10.428 | 37.78
2021-11-01 11:00 | 44501.4583 | 0 | 9.8887 | 37.78
2021-11-01 11:30 | 44501.4792 | 0 | 9.394 | 37.78
2021-11-01 12:00 | 44501.5 | 0 | 9.5347 | 37.78
2021-11-01 12:30 | 44501.5208 | 0 | 9.9736 | 37.78
2021-11-01 13:00 | 44501.5417 | 0 | 10.5572 | 37.78
2021-11-01 13:30 | 44501.5625 | 0 | 10.6876 | 37.78
2021-11-01 14:00 | 44501.5833 | 0 | 10.3384 | 37.78
2021-11-01 14:30 | 44501.6042 | 0 | 11.7903 | 37.78
2021-11-01 15:00 | 44501.625 | 0 | 11.8247 | 37.78
2021-11-01 15:30 | 44501.6458 | 0 | 11.9214 | 37.78
2021-11-01 16:00 | 44501.6667 | 0 | 12.0771 | 37.78
2021-11-01 16:30 | 44501.6875 | 0 | 12.2349 | 37.78
2021-11-01 17:00 | 44501.7083 | 0 | 12.3391 | 37.78
2021-11-01 17:30 | 44501.7292 | 0 | 12.9698 | 37.78
2021-11-01 18:00 | 44501.75 | 0 | 13.1952 | 37.78
2021-11-01 18:30 | 44501.7708 | 0 | 13.7641 | 37.78
2021-11-01 19:00 | 44501.7917 | 0 | 13.3416 | 37.78
2021-11-01 19:30 | 44501.8125 | 0 | 13.0557 | 37.78
2021-11-01 20:00 | 44501.8333 | 0 | 12.7367 | 37.78
2021-11-01 20:30 | 44501.8542 | 0 | 12.2241 | 37.78
2021-11-01 21:00 | 44501.875 | 0 | 11.7029 | 37.78
2021-11-01 21:30 | 44501.8958 | 0 | 11.3388 | 37.78
2021-11-01 22:00 | 44501.9167 | 0 | 10.7212 | 37.78
2021-11-01 22:30 | 44501.9375 | 0 | 9.9514 | 37.78
2021-11-01 23:00 | 44501.9583 | 0 | 9.4651 | 37.78
2021-11-01 23:30 | 44501.9792 | 0 | 9.0952 | 37.78
2021-11-02 | 44502 | 0 | 8.5683 | 37.78
2021-11-02 00:30 | 44502.0208 | 0 | 8.2494 | 37.78
2021-11-02 01:00 | 44502.0417 | 0 | 8.052 | 37.78
2021-11-02 01:30 | 44502.0625 | 0 | 7.8801 | 37.78
2021-11-02 02:00 | 44502.0833 | 0 | 7.7535 | 37.78
2021-11-02 02:30 | 44502.1042 | 0 | 7.7472 | 37.78
2021-11-02 03:00 | 44502.125 | 0 | 7.7163 | 37.78
2021-11-02 03:30 | 44502.1458 | 0 | 7.7602 | 37.78
2021-11-02 04:00 | 44502.1667 | 0 | 7.9735 | 37.78
2021-11-02 04:30 | 44502.1875 | 0 | 8.3956 | 37.78
2021-11-02 05:00 | 44502.2083 | 0 | 9.0118 | 37.78
2021-11-02 05:30 | 44502.2292 | 0 | 9.4574 | 37.78
2021-11-02 06:00 | 44502.25 | 0 | 9.942 | 37.78
2021-11-02 06:30 | 44502.2708 | 0 | 10.8945 | 37.78
2021-11-02 07:00 | 44502.2917 | 0 | 11.5488 | 37.78
2021-11-02 07:30 | 44502.3125 | 0 | 11.8229 | 37.78
2021-11-02 08:00 | 44502.3333 | 0 | 11.9093 | 37.78
2021-11-02 08:30 | 44502.3542 | 0 | 11.602 | 37.78
2021-11-02 09:00 | 44502.375 | 0 | 11.0114 | 37.78
2021-11-02 09:30 | 44502.3958 | 0 | 11.9178 | 37.78
2021-11-02 10:00 | 44502.4167 | 0 | 10.8817 | 37.78
2021-11-02 10:30 | 44502.4375 | 0 | 11.3616 | 37.78
2021-11-02 11:00 | 44502.4583 | 0 | 9.6441 | 37.78
2021-11-02 11:30 | 44502.4792 | 0 | 9.8376 | 37.78
2021-11-02 12:00 | 44502.5 | 0 | 10.2493 | 37.78
2021-11-02 12:30 | 44502.5208 | 0 | 9.8894 | 37.78
2021-11-02 13:00 | 44502.5417 | 0 | 10.7767 | 37.78
2021-11-02 13:30 | 44502.5625 | 0 | 10.9107 | 37.78
2021-11-02 14:00 | 44502.5833 | 0 | 11.6538 | 37.78
2021-11-02 14:30 | 44502.6042 | 0 | 12.4522 | 37.78
2021-11-02 15:00 | 44502.625 | 0 | 12.6872 | 37.78
2021-11-02 15:30 | 44502.6458 | 0 | 12.3593 | 37.78
2021-11-02 16:00 | 44502.6667 | 0 | 12.3414 | 37.78
2021-11-02 16:30 | 44502.6875 | 0 | 12.8238 | 37.78
2021-11-02 17:00 | 44502.7083 | 0 | 12.8026 | 37.78
2021-11-02 17:30 | 44502.7292 | 0 | 13.0585 | 37.78
2021-11-02 18:00 | 44502.75 | 0 | 13.3888 | 37.78
2021-11-02 18:30 | 44502.7708 | 0 | 13.7312 | 37.78
2021-11-02 19:00 | 44502.7917 | 0 | 13.5737 | 37.78
2021-11-02 19:30 | 44502.8125 | 0 | 13.3125 | 37.78
2021-11-02 20:00 | 44502.8333 | 0 | 12.8938 | 37.78
2021-11-02 20:30 | 44502.8542 | 0 | 12.3114 | 37.78
2021-11-02 21:00 | 44502.875 | 0 | 11.9364 | 37.78
2021-11-02 21:30 | 44502.8958 | 0 | 11.5161 | 37.78
2021-11-02 22:00 | 44502.9167 | 0 | 11.142 | 37.78
2021-11-02 22:30 | 44502.9375 | 0 | 10.2074 | 37.78
2021-11-02 23:00 | 44502.9583 | 0 | 9.6817 | 37.78
2021-11-02 23:30 | 44502.9792 | 0 | 9.2853 | 37.78
2021-11-03 | 44503 | 0 | 8.8579 | 37.78
2021-11-03 00:30 | 44503.0208 | 0 | 8.5767 | 37.78
2021-11-03 01:00 | 44503.0417 | 0 | 8.3118 | 37.78
2021-11-03 01:30 | 44503.0625 | 0 | 8.24 | 37.78
2021-11-03 02:00 | 44503.0833 | 0 | 8.0331 | 37.78
2021-11-03 02:30 | 44503.1042 | 0 | 7.9538 | 37.78
2021-11-03 03:00 | 44503.125 | 0 | 7.8312 | 37.78
2021-11-03 03:30 | 44503.1458 | 0 | 8.0308 | 37.78
2021-11-03 04:00 | 44503.1667 | 0 | 8.2822 | 37.78
2021-11-03 04:30 | 44503.1875 | 0 | 8.5668 | 37.78
2021-11-03 05:00 | 44503.2083 | 0 | 9.2876 | 37.78
2021-11-03 05:30 | 44503.2292 | 0 | 9.4568 | 37.78
2021-11-03 06:00 | 44503.25 | 0 | 9.8874 | 37.78
2021-11-03 06:30 | 44503.2708 | 0 | 9.9324 | 37.78
2021-11-03 07:00 | 44503.2917 | 0 | 10.2466 | 37.78
2021-11-03 07:30 | 44503.3125 | 0 | 9.9611 | 37.78
2021-11-03 08:00 | 44503.3333 | 0 | 9.6066 | 37.78
2021-11-03 08:30 | 44503.3542 | 0 | 10.1517 | 37.78
2021-11-03 09:00 | 44503.375 | 0 | 11.4033 | 37.78
2021-11-03 09:30 | 44503.3958 | 0 | 11.9122 | 37.78
2021-11-03 10:00 | 44503.4167 | 0 | 12.2549 | 37.78
2021-11-03 10:30 | 44503.4375 | 0 | 11.1056 | 37.78
2021-11-03 11:00 | 44503.4583 | 0 | 11.2022 | 37.78
2021-11-03 11:30 | 44503.4792 | 0 | 10.5284 | 37.78
2021-11-03 12:00 | 44503.5 | 0 | 10.8199 | 37.78
2021-11-03 12:30 | 44503.5208 | 0 | 10.9462 | 37.78