## Notes
Sub-Transmission Feeders Forecasts (Energex Distribution Annual Planning Report 2023-24 to 2027-28)
This workbook provides 5 year forecast capacity and loading information for sub-transmission feeders in the Energex network.
Energex Distribution Annual Planning Report is prepared and made available solely for information purposes. While care was taken in the preparation of the information in this report, and it is provided in good faith, Energex accepts no responsibility or liability (including without limitation, liability to any person by reason of negligence or negligent mis-statement) for any loss or damage that may be incurred by any person acting in reliance on this information or assumptions drawn from it, except to the extent that liability under any applicable Queensland or Commonwealth of Australia statute cannot be excluded.
It contains assumptions regarding, among other things, economic growth and load forecasts which may or may not prove to be correct. The forecasts included in the document involve subjective judgements and analysis which are subject to significant uncertainties and contingencies, many of which are out of the control of Energex. Furthermore, forecasted data is subject to ongoing variation as new information becomes available. Energex makes no representation or warranty as to the accuracy, reliability, completeness or suitability for any particular purpose of the information in this document. All information should be independently investigated, reviewed, analysed and verified, and must not be relied upon in connection with any investment proposal or decision.
The following sections list the 33kV feeders, their forecast loads, power factor, customer category and available load transfers. The feeder loads are calculated from load flow results using forecast substation demands. For the transmission and sub-transmission feeders, load flow studies are conducted for system normal and single contingency situations.
The forecast and capacity accounts for committed projects, the project cut-off date for the winter season is 1 June of each year, and for the summer season is 1 December of each year. For example, 2024 winter forecast includes all committed projects with a proposed commissioning date up to 1 June 2024, and the 2023/24 summer forecast includes all committed projects with a proposed commissioning date up to 1 December 2023. The committed status of projects used in the forecast are taken as of 1 May 2023.
Assessment of 33kV feeders is performed under four possible risk periods: winter day, winter night, summer day and summer night. The worst case (highest) load between day and night has been represented in the table.
Peak, reconciled, compensated load forecasts have been used in the 33kV feeder analyses, with 50 PoE forecast load used for single contingency studies, and 10 PoE forecast load used for system normal studies.
Feeder capacities are shown for ECC and NCC. These ratings have also been adjusted for known committed projects. All load transfers associated with contingent condition include acceptable feeder voltage profiles.
Although the conductor rating is generally the limiting factor for feeder capacity, there are other significant items of plant, such as the feeder circuit breaker, that can also restrict capacity. Furthermore, other factors such as voltage constraints and load sharing between parallel underground feeders can sometimes de‑rate the capacity of the feeders due to thermal characteristic constraints. Each of these factors has been taken into account in the production of the forecast tables.
Interconnected feeders that supply multiple customers are examined in the following tables. Feeders exclusively supplying a customer owned substation or dedicated to a customer are not included in these tables.
A definition of terms is shown in the table below.
Definition of Terms Feeder Capacity and Forecast Tables
Term | Definition
NCC Rating (A) | Normal Cyclic Capacity - the total capacity with all network components and equipment intact. This is the maximum permissible peak daily loading for a given load cycle that a feeder can supply each day of its life. For overhead feeders, the NCC is the conductor rating with an assumed 1m/s wind, orthogonal to the line. For underground cables, the NCC assumes that there are sufficient temperature and current operating margins from the thermal inertia of the cable and its surroundings.
10 PoE Load (A) | Peak load forecast with 10% probability of being exceeded (one in every 10 years will be exceeded). Based on normal expected growth rates and weather corrected starting loads.
Power Factor | Lowest power factor along the feeder at 10 PoE Peak Load. Where the Power Factor is either 0 the feeder is a normally open feeder that does not have load under System Normal conditions.
ECC Rating (A) | Emergency Cyclic Capacity – the long term firm delivery capacity under single contingency conditions. Some underground cables are installed in close proximity to other circuits and are normally de‑rated to allow for the heat generated by the adjacent cables. ECC is the higher capacity available when any adjacent circuits have been unloaded. For overhead conductors which do not benefit from this phenomenon, the ECC is synonymous with the NCC.
50 PoE Load (A) | Peak load forecast with 50% probability of being exceeded (one in every two years will be exceeded). Based on normal expected growth rates & weather corrected starting loads. This is the worst case (highest) load forecast beween summer day and summer night.
Security Standard | For security standard application, the general type of customer a sub-transmission, or transmission feeder is supplying.
Transfers | This is the total amount of load transfers that are available following the worst case network contingency. This includes automatic transfers that are controlled automatically through SCADA and are generally implemented within a minute, load transfers that can be implemented through screen switching by a network controller, manual transfers that are deployed via manually controlled switchgear locally by field staff, and mobile generation which can be deployed by field staff by moving generation to specific sites. It should be noted under the Safety Net in the Distribution Authority, it is generally assumed that 4MVA (70A) of generation is available for Urban feeders to meet this criteria and 10MVA (170A) is available for Rural feeders. These values have been used as a default in the forecast tables where these are sufficient to reduce the 50PoE load below the ECC rating. Where the load is still above the ECC rating, specific load transfers have been calculated for the feeder to determine whether the Safety Net criteria is met.
Hours PA > 95% Peak Load | The forecast number of hours per annum where the load exceeded 95% of the peak 50 PoE demand. This information is not readily available for every feeder without significant analysis being undertaken. As such, this has only been provided where a feeder does not meet the Safety Net criteria or is otherwise in the Limitations and Proposed Solutions table.

## 33kV Feeders - Winter
Bulk Supply Name | Feeder | From Substation | To Substation | Attributes | 2024 | 2025 | 2026 | 2027 | 2028 | Security Standard | Transfers | Hours above 95%
Abermain Bulk | 357-1 | Abermain BS | 357 Tee1 | NCC Rating (A) | 554 | 554 | 554 | 554 | 554 | Urban | 70
|  |  |  | 10 POE Load (A) | 106 | 106 | 106 | 106 | 106
|  |  |  | Power Factor | 0.99667 | 0.99667 | 0.99667 | 0.99675 | 0.99667
|  |  |  | ECC Rating (A) | 554 | 554 | 554 | 554 | 554
|  |  |  | 50 POE Load (A) | 250 | 250 | 248 | 248 | 250
Abermain Bulk | 357-2 | 357 Tee1 | Redbank | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 3.1281e-06 | 3.1282e-06 | 3.128e-06 | 3.1281e-06 | 3.128e-06
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 203 | 204 | 208 | 211 | 216
Abermain Bulk | 357-3 | 357 Tee1 | Moggill | NCC Rating (A) | 840 | 840 | 840 | 840 | 840 | Urban | 70
|  |  |  | 10 POE Load (A) | 107 | 107 | 107 | 106 | 107
|  |  |  | Power Factor | 0.9953 | 0.9953 | 0.9953 | 0.99534 | 0.9953
|  |  |  | ECC Rating (A) | 840 | 840 | 840 | 840 | 840
|  |  |  | 50 POE Load (A) | 251 | 251 | 249 | 249 | 251
Abermain Bulk | 358-1 | Abermain BS | Ebbw Vale | NCC Rating (A) | 525 | 525 | 525 | 525 | 525 | Rural | 170
|  |  |  | 10 POE Load (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 7.0412e-06 | 7.0414e-06 | 7.0413e-06 | 7.0412e-06 | 7.0411e-06
|  |  |  | ECC Rating (A) | 525 | 525 | 525 | 525 | 525
|  |  |  | 50 POE Load (A) | 1 | 1 | 1 | 1 | 1
Abermain Bulk | 364-1 | Marburg | Rosewood | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
|  |  |  | 10 POE Load (A) | 51 | 52 | 53 | 54 | 55
|  |  |  | Power Factor | 0.99777 | 0.99782 | 0.99776 | 0.99772 | 0.9979
|  |  |  | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | 50 POE Load (A) | 104 | 110 | 114 | 121 | 130
Abermain Bulk | 365-1 | Abermain BS | 365 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 259 | 266 | 271 | 277 | 284
|  |  |  | Power Factor | 0.98057 | 0.98015 | 0.97984 | 0.9796 | 0.97898
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 480 | 490 | 499 | 509 | 523
Abermain Bulk | 365-2 | 365 Tee1 | 366 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 2.0191e-05 | 2.0192e-05 | 2.0193e-05 | 2.019e-05 | 2.0192e-05
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Abermain Bulk | 365-3 | 365 Tee1 | Karrabin | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 259 | 266 | 271 | 277 | 284
|  |  |  | Power Factor | 0.98072 | 0.98031 | 0.98 | 0.97977 | 0.97915
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 480 | 490 | 499 | 509 | 523
Abermain Bulk | 366-1 | Abermain BS | 366 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 283 | 290 | 296 | 303 | 310
|  |  |  | Power Factor | 0.97176 | 0.97098 | 0.9704 | 0.96986 | 0.96883
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 484 | 494 | 503 | 513 | 527
Abermain Bulk | 366-2 | 366 Tee1 | Karrabin | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 283 | 291 | 296 | 303 | 310
|  |  |  | Power Factor | 0.98033 | 0.9799 | 0.97957 | 0.97933 | 0.97869
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 484 | 494 | 503 | 513 | 527
Abermain Bulk | 366-3 | 366 Tee1 | 365 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 9.0322e-06 | 9.0317e-06 | 9.0324e-06 | 9.0319e-06 | 9.032e-06
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Abermain Bulk | 367-1 | Abermain BS | Mt Crosby West | NCC Rating (A) | 581 | 581 | 581 | 581 | 581 | Rural | 170
|  |  |  | 10 POE Load (A) | 214 | 217 | 217 | 217 | 217
|  |  |  | Power Factor | 0.94688 | 0.9474 | 0.9474 | 0.9474 | 0.9474
|  |  |  | ECC Rating (A) | 581 | 581 | 581 | 581 | 581
|  |  |  | 50 POE Load (A) | 376 | 375 | 375 | 375 | 375
Abermain Bulk | 368-1 | Abermain BS | Mt Crosby | NCC Rating (A) | 552 | 552 | 552 | 552 | 552 | HighSec | 0
|  |  |  | 10 POE Load (A) | 170 | 171 | 171 | 171 | 171
|  |  |  | Power Factor | 0.93113 | 0.93023 | 0.93023 | 0.93023 | 0.93023
|  |  |  | ECC Rating (A) | 552 | 552 | 552 | 552 | 552
|  |  |  | 50 POE Load (A) | 378 | 378 | 378 | 378 | 378
Abermain Bulk | 369-1 | Abermain BS | Nth Ipswich | NCC Rating (A) | 548 | 548 | 548 | 548 | 548 | Urban | 70
|  |  |  | 10 POE Load (A) | 158 | 159 | 161 | 161 | 162
|  |  |  | Power Factor | 0.98903 | 0.98897 | 0.98885 | 0.98885 | 0.98872
|  |  |  | ECC Rating (A) | 548 | 548 | 548 | 548 | 548
|  |  |  | 50 POE Load (A) | 299 | 300 | 302 | 304 | 306
Abermain Bulk | 370-1 | Abermain BS | Nth Ipswich | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70
|  |  |  | 10 POE Load (A) | 161 | 162 | 164 | 164 | 165
|  |  |  | Power Factor | 0.98971 | 0.98966 | 0.98954 | 0.98954 | 0.98942
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 299 | 300 | 302 | 304 | 306
Abermain Bulk | 387-1 | Abermain BS | Marburg | NCC Rating (A) | 290 | 290 | 290 | 290 | 290 | Rural | 170 | 4
|  |  |  | 10 POE Load (A) | 135 | 142 | 146 | 152 | 159
|  |  |  | Power Factor | 0.99977 | 0.99966 | 0.99959 | 0.99946 | 0.99932
|  |  |  | ECC Rating (A) | 290 | 290 | 290 | 290 | 290
|  |  |  | 50 POE Load (A) | 176 | 186 | 195 | 205 | 221
Abermain Bulk | 3901-1 | Karrabin | Amberley | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 126 | 129 | 132 | 136 | 139
|  |  |  | Power Factor | 0.97102 | 0.97056 | 0.97024 | 0.96971 | 0.96925
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 229 | 233 | 237 | 242 | 248
Abermain Bulk | 420-1 | Mt Crosby West | Mt Crosby | NCC Rating (A) | 490 | 490 | 490 | 490 | 490 | HighSec | 0
|  |  |  | 10 POE Load (A) | 44 | 45 | 46 | 46 | 46
|  |  |  | Power Factor | 0.66656 | 0.98441 | 0.68478 | 0.68478 | 0.68478
|  |  |  | ECC Rating (A) | 490 | 490 | 490 | 490 | 490
|  |  |  | 50 POE Load (A) | 207 | 206 | 206 | 206 | 206
Abermain Bulk | 436-1 | Amberley | 436 Tee1 | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Rural | 170 | 12
|  |  |  | 10 POE Load (A) | 57 | 64 | 67 | 74 | 80
|  |  |  | Power Factor | 0.90453 | 0.91036 | 0.91215 | 0.91586 | 0.91901
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | 50 POE Load (A) | 178 | 188 | 196 | 207 | 221
Abermain Bulk | 436-4 | 436 Tee1 | Rosewood | NCC Rating (A) | 416 | 416 | 416 | 416 | 416 | Rural | 170
|  |  |  | 10 POE Load (A) | 57 | 64 | 67 | 74 | 81
|  |  |  | Power Factor | 0.90261 | 0.90931 | 0.91144 | 0.9158 | 0.91952
|  |  |  | ECC Rating (A) | 416 | 416 | 416 | 416 | 416
|  |  |  | 50 POE Load (A) | 178 | 188 | 196 | 207 | 222
Abermain Bulk | 445-1 | Abermain BS | Moggill | NCC Rating (A) | 776 | 776 | 776 | 776 | 776 | Urban | 70
|  |  |  | 10 POE Load (A) | 144 | 144 | 144 | 143 | 144
|  |  |  | Power Factor | 0.99588 | 0.99588 | 0.99588 | 0.99594 | 0.99588
|  |  |  | ECC Rating (A) | 776 | 776 | 776 | 776 | 776
|  |  |  | 50 POE Load (A) | 248 | 248 | 246 | 246 | 248
Abermain Bulk | 475-1 | Karrabin | Amberley | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 124 | 127 | 130 | 133 | 137
|  |  |  | Power Factor | 0.97164 | 0.97118 | 0.97086 | 0.97035 | 0.96989
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 229 | 233 | 237 | 242 | 248
Abermain Bulk | 673-1 | Moggill | Kenmore | NCC Rating (A) | 636 | 636 | 636 | 636 | 636 | Urban | 70
|  |  |  | 10 POE Load (A) | 3 | 3 | 3 | 3 | 3
|  |  |  | Power Factor | 4.7649e-05 | 4.7649e-05 | 4.7649e-05 | 4.7649e-05 | 4.7649e-05
|  |  |  | ECC Rating (A) | 636 | 636 | 636 | 636 | 636
|  |  |  | 50 POE Load (A) | 3 | 3 | 3 | 3 | 3
Algester Bulk | 3400-1 | Algester BS | Calamvale | NCC Rating (A) | 735 | 735 | 735 | 735 | 735 | Urban | 70
|  |  |  | 10 POE Load (A) | 271 | 272 | 273 | 273 | 276
|  |  |  | Power Factor | 0.99173 | 0.99162 | 0.99156 | 0.99156 | 0.9914
|  |  |  | ECC Rating (A) | 735 | 735 | 735 | 735 | 735
|  |  |  | 50 POE Load (A) | 516 | 521 | 521 | 523 | 529
Algester Bulk | 3402-1 | Algester BS | Acacia Ridge | NCC Rating (A) | 728 | 728 | 728 | 728 | 728 | Urban | 70
|  |  |  | 10 POE Load (A) | 148 | 148 | 148 | 147 | 148
|  |  |  | Power Factor | 0.94541 | 0.94541 | 0.94541 | 0.94554 | 0.94541
|  |  |  | ECC Rating (A) | 728 | 728 | 728 | 728 | 728
|  |  |  | 50 POE Load (A) | 280 | 282 | 282 | 280 | 282
Algester Bulk | 3403-1 | Algester BS | Acacia Ridge | NCC Rating (A) | 728 | 728 | 728 | 728 | 728 | Urban | 70
|  |  |  | 10 POE Load (A) | 148 | 148 | 148 | 147 | 148
|  |  |  | Power Factor | 0.94544 | 0.94544 | 0.94544 | 0.94556 | 0.94544
|  |  |  | ECC Rating (A) | 728 | 728 | 728 | 728 | 728
|  |  |  | 50 POE Load (A) | 280 | 282 | 282 | 280 | 282
Algester Bulk | 3405-1 | Algester BS | Calamvale | NCC Rating (A) | 735 | 735 | 735 | 735 | 735 | Urban | 70
|  |  |  | 10 POE Load (A) | 271 | 273 | 274 | 274 | 276
|  |  |  | Power Factor | 0.99173 | 0.99162 | 0.99157 | 0.99157 | 0.9914
|  |  |  | ECC Rating (A) | 735 | 735 | 735 | 735 | 735
|  |  |  | 50 POE Load (A) | 516 | 521 | 521 | 523 | 529
Archerfield Bulk | 597-1 | Rocklea | Salisbury | NCC Rating (A) | 710 | 710 | 710 | 710 | 710 | Urban | 70
|  |  |  | 10 POE Load (A) | 168 | 170 | 170 | 170 | 171
|  |  |  | Power Factor | 0.98227 | 0.98211 | 0.98211 | 0.98211 | 0.98196
|  |  |  | ECC Rating (A) | 710 | 710 | 710 | 710 | 710
|  |  |  | 50 POE Load (A) | 150 | 150 | 150 | 150 | 152
Archerfield Bulk | 635-1 | Archerfield BS | Coopers Plains | NCC Rating (A) | 573 | 573 | 573 | 573 | 573 | Urban | 70
|  |  |  | 10 POE Load (A) | 327 | 334 | 332 | 329 | 331
|  |  |  | Power Factor | 0.93762 | 0.93704 | 0.93718 | 0.93748 | 0.93733
|  |  |  | ECC Rating (A) | 573 | 573 | 573 | 573 | 573
|  |  |  | 50 POE Load (A) | 308 | 317 | 314 | 312 | 312
Archerfield Bulk | 650-1 | Archerfield BS | Rocklea | NCC Rating (A) | 688 | 688 | 688 | 688 | 688 | Urban | 70
|  |  |  | 10 POE Load (A) | 215 | 215 | 214 | 214 | 217
|  |  |  | Power Factor | 0.97795 | 0.97797 | 0.97785 | 0.97785 | 0.97784
|  |  |  | ECC Rating (A) | 688 | 688 | 688 | 688 | 688
|  |  |  | 50 POE Load (A) | 392 | 390 | 390 | 390 | 393
Archerfield Bulk | 651-1 | Archerfield BS | Rocklea | NCC Rating (A) | 688 | 688 | 688 | 688 | 688 | Urban | 70
|  |  |  | 10 POE Load (A) | 213 | 213 | 212 | 212 | 214
|  |  |  | Power Factor | 0.97789 | 0.97791 | 0.97779 | 0.97779 | 0.97779
|  |  |  | ECC Rating (A) | 688 | 688 | 688 | 688 | 688
|  |  |  | 50 POE Load (A) | 392 | 390 | 390 | 390 | 393
Ashgrove West Bulk | 432-1 | Ashgrove West BS | Toowong | NCC Rating (A) | 516 | 516 | 516 | 516 | 516 | Urban | 70
|  |  |  | 10 POE Load (A) | 14 | 14 | 14 | 14 | 14
|  |  |  | Power Factor | 4.2657e-05 | 4.2657e-05 | 4.2657e-05 | 4.2657e-05 | 4.2657e-05
|  |  |  | ECC Rating (A) | 516 | 516 | 516 | 516 | 516
|  |  |  | 50 POE Load (A) | 14 | 14 | 14 | 14 | 14
Ashgrove West Bulk | 552-1 | Ashgrove West BS | Ashgrove | NCC Rating (A) | 634 | 634 | 634 | 634 | 634 | Urban | 70
|  |  |  | 10 POE Load (A) | 135 | 135 | 135 | 136 | 137
|  |  |  | Power Factor | 0.99992 | 0.99993 | 0.99993 | 0.99995 | 0.99996
|  |  |  | ECC Rating (A) | 634 | 634 | 634 | 634 | 634
|  |  |  | 50 POE Load (A) | 205 | 206 | 206 | 206 | 209
Ashgrove West Bulk | 565-1 | Ashgrove West BS | Ashgrove | NCC Rating (A) | 882 | 882 | 882 | 882 | 882 | Urban | 70
|  |  |  | 10 POE Load (A) | 93 | 94 | 94 | 94 | 95
|  |  |  | Power Factor | 0.99061 | 0.99047 | 0.99047 | 0.99034 | 0.99006
|  |  |  | ECC Rating (A) | 882 | 882 | 882 | 882 | 882
|  |  |  | 50 POE Load (A) | 143 | 144 | 144 | 144 | 146
Ashgrove West Bulk | 570-1 | Ashgrove West BS | Ashgrove | NCC Rating (A) | 634 | 634 | 634 | 634 | 634 | Urban | 70
|  |  |  | 10 POE Load (A) | 132 | 132 | 132 | 133 | 134
|  |  |  | Power Factor | 0.99856 | 0.99862 | 0.99862 | 0.99869 | 0.99881
|  |  |  | ECC Rating (A) | 634 | 634 | 634 | 634 | 634
|  |  |  | 50 POE Load (A) | 203 | 204 | 204 | 204 | 207
Ashgrove West Bulk | 585-1 | Ashgrove West BS | The Gap | NCC Rating (A) | 659 | 659 | 659 | 659 | 659 | Urban | 70
|  |  |  | 10 POE Load (A) | 138 | 138 | 138 | 138 | 139
|  |  |  | Power Factor | 0.99775 | 0.99775 | 0.99775 | 0.99777 | 0.99772
|  |  |  | ECC Rating (A) | 659 | 659 | 659 | 659 | 659
|  |  |  | 50 POE Load (A) | 132 | 132 | 132 | 131 | 132
Ashgrove West Bulk | 586-1 | Ashgrove West BS | The Gap | NCC Rating (A) | 659 | 659 | 659 | 659 | 659 | Urban | 70
|  |  |  | 10 POE Load (A) | 138 | 138 | 138 | 138 | 139
|  |  |  | Power Factor | 0.99737 | 0.99737 | 0.99737 | 0.99741 | 0.99734
|  |  |  | ECC Rating (A) | 659 | 659 | 659 | 659 | 659
|  |  |  | 50 POE Load (A) | 132 | 132 | 132 | 131 | 132
Ashgrove West Bulk | 590-1 | Ashgrove BS | Toowong | NCC Rating (A) | 705 | 705 | 705 | 705 | 705 | Urban | 70
|  |  |  | 10 POE Load (A) | 268 | 293 | 293 | 294 | 296
|  |  |  | Power Factor | 0.98339 | 0.98267 | 0.98267 | 0.98263 | 0.9825
|  |  |  | ECC Rating (A) | 705 | 705 | 705 | 705 | 705
|  |  |  | 50 POE Load (A) | 508 | 558 | 558 | 560 | 563
Ashgrove West Bulk | 591-1 | Ashgrove BS | Toowong | NCC Rating (A) | 705 | 705 | 705 | 705 | 705 | Urban | 70
|  |  |  | 10 POE Load (A) | 268 | 293 | 293 | 294 | 296
|  |  |  | Power Factor | 0.98334 | 0.98262 | 0.98262 | 0.98258 | 0.98245
|  |  |  | ECC Rating (A) | 705 | 705 | 705 | 705 | 705
|  |  |  | 50 POE Load (A) | 508 | 558 | 558 | 560 | 563
Ashgrove West Bulk | 675-1 | Ashgrove | Newmarket | NCC Rating (A) | 527 | 527 | 527 | 527 | 527 | Urban | 70
|  |  |  | 10 POE Load (A) | 17 | 17 | 17 | 17 | 17
|  |  |  | Power Factor | 3.5471e-05 | 3.5471e-05 | 3.5471e-05 | 3.5471e-05 | 3.5471e-05
|  |  |  | ECC Rating (A) | 527 | 527 | 527 | 527 | 527
|  |  |  | 50 POE Load (A) | 17 | 17 | 17 | 17 | 17
Ashgrove West Bulk | 676-1 | Ashgrove | Newmarket | NCC Rating (A) | 527 | 527 | 527 | 527 | 527 | Urban | 70
|  |  |  | 10 POE Load (A) | 17 | 17 | 17 | 17 | 17
|  |  |  | Power Factor | 3.4731e-05 | 3.4731e-05 | 3.4731e-05 | 3.4731e-05 | 3.4731e-05
|  |  |  | ECC Rating (A) | 527 | 527 | 527 | 527 | 527
|  |  |  | 50 POE Load (A) | 17 | 17 | 17 | 17 | 17
Beaudesert Bulk | 314-1 | Beaudesert BS | Jimboomba | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Rural | 170 | 1
|  |  |  | 10 POE Load (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 1.6107e-05 | 1.6107e-05 | 1.6107e-05 | 1.6107e-05 | 1.6107e-05
|  |  |  | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
|  |  |  | 50 POE Load (A) | 1 | 1 | 1 | 1 | 1
Beaudesert Bulk | 404-1 | Beaudesert | Innisplain | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170 | 4
|  |  |  | 10 POE Load (A) | 74 | 74 | 76 | 76 | 76
|  |  |  | Power Factor | 0.98435 | 0.98434 | 0.98394 | 0.98394 | 0.98393
|  |  |  | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | 50 POE Load (A) | 71 | 73 | 73 | 74 | 76
Beaudesert Bulk | 466-1 | Beaudesert BS | Bromelton | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170
|  |  |  | 10 POE Load (A) | 86 | 87 | 87 | 88 | 89
|  |  |  | Power Factor | 0.99618 | 0.99614 | 0.99614 | 0.9961 | 0.99606
|  |  |  | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
|  |  |  | 50 POE Load (A) | 138 | 140 | 140 | 142 | 143
Beaudesert Bulk | 467-1 | Beaudesert BS | Bromelton | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170
|  |  |  | 10 POE Load (A) | 58 | 58 | 58 | 59 | 60
|  |  |  | Power Factor | 0.99916 | 0.99917 | 0.99917 | 0.99919 | 0.99921
|  |  |  | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
|  |  |  | 50 POE Load (A) | 139 | 141 | 141 | 143 | 144
Beaudesert Bulk | 468-1 | Beaudesert BS | Beaudesert | NCC Rating (A) | 579 | 579 | 579 | 579 | 579 | Rural | 170
|  |  |  | 10 POE Load (A) | 254 | 257 | 260 | 261 | 264
|  |  |  | Power Factor | 0.96045 | 0.96003 | 0.96013 | 0.96005 | 0.95944
|  |  |  | ECC Rating (A) | 579 | 579 | 579 | 579 | 579
|  |  |  | 50 POE Load (A) | 346 | 350 | 349 | 351 | 354
Beaudesert Bulk | 469-1 | Beaudesert BS | 469 Tee1 | NCC Rating (A) | 537 | 537 | 537 | 537 | 537 | Rural | 170 | 1
|  |  |  | 10 POE Load (A) | 262 | 265 | 268 | 268 | 272
|  |  |  | Power Factor | 0.98363 | 0.98335 | 0.98341 | 0.98336 | 0.98295
|  |  |  | ECC Rating (A) | 537 | 537 | 537 | 537 | 537
|  |  |  | 50 POE Load (A) | 500 | 507 | 509 | 513 | 520
Beaudesert Bulk | 469-2 | 469 Tee1 | Beaudesert | NCC Rating (A) | 579 | 579 | 579 | 579 | 579 | Rural | 170
|  |  |  | 10 POE Load (A) | 77 | 79 | 80 | 83 | 86
|  |  |  | Power Factor | 0.99544 | 0.99471 | 0.99445 | 0.9941 | 0.99337
|  |  |  | ECC Rating (A) | 579 | 579 | 579 | 579 | 579
|  |  |  | 50 POE Load (A) | 317 | 325 | 328 | 332 | 339
Beaudesert Bulk | 469-3 | 469 Tee1 | Mt Tamborine Bus 2 | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Rural | 170
|  |  |  | 10 POE Load (A) | 188 | 188 | 188 | 186 | 188
|  |  |  | Power Factor | 0.97835 | 0.97834 | 0.97833 | 0.97869 | 0.97831
|  |  |  | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
|  |  |  | 50 POE Load (A) | 390 | 390 | 385 | 385 | 385
Beenleigh Bulk | 3590-1 | Beenleigh BS | Loganholme | NCC Rating (A) | 810 | 810 | 810 | 810 | 810 | Urban | 70
|  |  |  | 10 POE Load (A) | 302 | 299 | 296 | 295 | 295
|  |  |  | Power Factor | 0.9961 | 0.99614 | 0.99621 | 0.99623 | 0.99623
|  |  |  | ECC Rating (A) | 810 | 810 | 810 | 810 | 810
|  |  |  | 50 POE Load (A) | 478 | 475 | 471 | 468 | 471
Beenleigh Bulk | 3591-1 | Cornubia | Loganholme | NCC Rating (A) | 859 | 859 | 859 | 859 | 859 | Urban | 70
|  |  |  | 10 POE Load (A) | 34 | 32 | 31 | 30 | 31
|  |  |  | Power Factor | 0.97643 | 0.97594 | 0.97557 | 0.97536 | 0.97557
|  |  |  | ECC Rating (A) | 859 | 859 | 859 | 859 | 859
|  |  |  | 50 POE Load (A) | 306 | 303 | 299 | 297 | 299
Beenleigh Bulk | 3601-1 | Yatala | Stapylton | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Rural | 170
|  |  |  | 10 POE Load (A) | 84 | 84 | 83 | 83 | 83
|  |  |  | Power Factor | 0.98016 | 0.98016 | 0.98025 | 0.98025 | 0.98025
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 162 | 162 | 161 | 161 | 161
Beenleigh Bulk | 3620-1 | Beenleigh BS | Logan Village | NCC Rating (A) | 490 | 490 | 490 | 490 | 490 | Rural | 170
|  |  |  | 10 POE Load (A) | 2 | 2 | 2 | 2 | 2
|  |  |  | Power Factor | 0.00018079 | 0.00018079 | 0.00018079 | 0.00018079 | 0.00018079
|  |  |  | ECC Rating (A) | 490 | 490 | 490 | 490 | 490
|  |  |  | 50 POE Load (A) | 287 | 297 | 305 | 312 | 318
Beenleigh Bulk | 402-1 | Beenleigh BS | 402 Tee1 | NCC Rating (A) | 579 | 579 | 579 | 579 | 579 | Urban | 70
|  |  |  | 10 POE Load (A) | 259 | 259 | 259 | 257 | 257
|  |  |  | Power Factor | 0.9807 | 0.9807 | 0.9807 | 0.98104 | 0.98103
|  |  |  | ECC Rating (A) | 579 | 579 | 579 | 579 | 579
|  |  |  | 50 POE Load (A) | 489 | 489 | 482 | 482 | 482
Beenleigh Bulk | 402-2 | 402 Tee1 | Tamborine Village | NCC Rating (A) | 469 | 469 | 469 | 469 | 469 | Urban | 70
|  |  |  | 10 POE Load (A) | 68 | 68 | 68 | 67 | 67
|  |  |  | Power Factor | 0.99422 | 0.99422 | 0.99422 | 0.99423 | 0.99423
|  |  |  | ECC Rating (A) | 469 | 469 | 469 | 469 | 469
|  |  |  | 50 POE Load (A) | 71 | 71 | 70 | 70 | 70
Beenleigh Bulk | 402-3 | 402 Tee1 | Mt Tamborine Bus 1 | NCC Rating (A) | 812 | 812 | 812 | 812 | 812 | Urban | 70
|  |  |  | 10 POE Load (A) | 192 | 192 | 192 | 190 | 190
|  |  |  | Power Factor | 0.98627 | 0.98627 | 0.98627 | 0.98653 | 0.98653
|  |  |  | ECC Rating (A) | 812 | 812 | 812 | 812 | 812
|  |  |  | 50 POE Load (A) | 419 | 419 | 412 | 412 | 412
Beenleigh Bulk | 405-1 | Beenleigh BS | 405 Tee1 | NCC Rating (A) | 868 | 868 | 868 | 868 | 868 | Urban | 70
|  |  |  | 10 POE Load (A) | 221 | 219 | 217 | 217 | 217
|  |  |  | Power Factor | 0.99117 | 0.99126 | 0.9914 | 0.99144 | 0.99144
|  |  |  | ECC Rating (A) | 868 | 868 | 868 | 868 | 868
|  |  |  | 50 POE Load (A) | 484 | 480 | 477 | 473 | 477
Beenleigh Bulk | 405-3 | 405 Tee1 | Cornubia | NCC Rating (A) | 820 | 820 | 820 | 820 | 820 | Urban | 70
|  |  |  | 10 POE Load (A) | 221 | 219 | 217 | 217 | 217
|  |  |  | Power Factor | 0.99387 | 0.99392 | 0.99401 | 0.99403 | 0.99403
|  |  |  | ECC Rating (A) | 820 | 820 | 820 | 820 | 820
|  |  |  | 50 POE Load (A) | 484 | 481 | 477 | 473 | 477
Beenleigh Bulk | 419-1 | Loganholme | Tanah Merah | NCC Rating (A) | 892 | 892 | 892 | 892 | 892 | Urban | 70
|  |  |  | 10 POE Load (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 2.0557e-06 | 2.0558e-06 | 2.0557e-06 | 2.0558e-06 | 2.0557e-06
|  |  |  | ECC Rating (A) | 892 | 892 | 892 | 892 | 892
|  |  |  | 50 POE Load (A) | 239 | 239 | 237 | 237 | 237
Beenleigh Bulk | 426-1 | Beenleigh BS | Stapylton | NCC Rating (A) | 785 | 785 | 785 | 785 | 785 | Rural | 170
|  |  |  | 10 POE Load (A) | 87 | 87 | 87 | 87 | 87
|  |  |  | Power Factor | 0.98457 | 0.98457 | 0.98471 | 0.98471 | 0.98471
|  |  |  | ECC Rating (A) | 785 | 785 | 785 | 785 | 785
|  |  |  | 50 POE Load (A) | 162 | 162 | 160 | 160 | 160
Beenleigh Bulk | 427-1 | Beenleigh BS | Yatala | NCC Rating (A) | 785 | 785 | 785 | 785 | 785 | Rural | 170
|  |  |  | 10 POE Load (A) | 84 | 84 | 83 | 83 | 83
|  |  |  | Power Factor | 0.98261 | 0.98261 | 0.98276 | 0.98276 | 0.98276
|  |  |  | ECC Rating (A) | 785 | 785 | 785 | 785 | 785
|  |  |  | 50 POE Load (A) | 162 | 162 | 160 | 160 | 160
Beenleigh Bulk | 453-1 | Beenleigh BS | Beenleigh Nth | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 713
|  |  |  | 10 POE Load (A) | 639 | 642 | 644 | 646 | 649
|  |  |  | Power Factor | 0.98622 | 0.98611 | 0.98622 | 0.98617 | 0.98606
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 598 | 601 | 603 | 603 | 608
Beenleigh Bulk | 496-1 | Beenleigh Nth | Bethania | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
|  |  |  | 10 POE Load (A) | 320 | 322 | 322 | 322 | 324
|  |  |  | Power Factor | 0.99061 | 0.99053 | 0.99053 | 0.99053 | 0.99046
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 334 | 337 | 339 | 339 | 343
Beerwah Bulk | 3190-1 | Woodford | Kilcoy | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | 0 | 0
|  |  |  | 10 POE Load (A) | 119 | 119 | 119 | 118 | 118
|  |  |  | Power Factor | 0.94287 | 0.94287 | 0.94287 | 0.94788 | 0.94788
|  |  |  | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | 50 POE Load (A) | 170 | 170 | 168 | 168 | 168
Beerwah Bulk | 324-1 | Woodford | Kilcoy | NCC Rating (A) | 348 | 348 | 348 | 348 | 348 | Rural | 170
|  |  |  | 10 POE Load (A) | 61 | 61 | 61 | 61 | 61
|  |  |  | Power Factor | 0.99205 | 0.99205 | 0.99205 | 0.99 | 0.99
|  |  |  | ECC Rating (A) | 348 | 348 | 348 | 348 | 348
|  |  |  | 50 POE Load (A) | 59 | 59 | 58 | 58 | 58
Beerwah Bulk | 428-1 | Beerwah BS | Woodford | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Rural | 170
|  |  |  | 10 POE Load (A) | 190 | 190 | 190 | 187 | 187
|  |  |  | Power Factor | 0.97316 | 0.97316 | 0.97316 | 0.97664 | 0.97664
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | 50 POE Load (A) | 183 | 183 | 181 | 180 | 180
Beerwah Bulk | 447-1 | Somerset Dam | Kilcoy | NCC Rating (A)
10 POE Load (A)
Power Factor
ECC Rating (A)
50 POE Load (A)
Beerwah Bulk | 477-1 | 477 Tee1 | Maleny | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
|  |  |  | 10 POE Load (A) | 2 | 2 | 2 | 2 | 2
|  |  |  | Power Factor | 3.5253e-05 | 3.5253e-05 | 3.5253e-05 | 3.5253e-05 | 3.5253e-05
|  |  |  | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | 50 POE Load (A) | 2 | 2 | 2 | 2 | 2
Beerwah Bulk | 477-2 | 477 Tee1 | Woodford | NCC Rating (A) | 293 | 293 | 775 | 775 | 775 | Rural | 170
|  |  |  | 10 POE Load (A) | 165 | 163 | 157 | 157 | 157
|  |  |  | Power Factor | 0.98762 | 0.98782 | 0.99081 | 0.99081 | 0.99081
|  |  |  | ECC Rating (A) | 293 | 293 | 775 | 775 | 775
|  |  |  | 50 POE Load (A) | 151 | 149 | 144 | 144 | 144
Beerwah Bulk | 477-3 | Beerwah | 477 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 165 | 163 | 157 | 157 | 157
|  |  |  | Power Factor | 0.98278 | 0.98315 | 0.98404 | 0.98404 | 0.98404
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 151 | 149 | 144 | 144 | 144
Beerwah Bulk | 608-1 | Beerwah BS | Landsborough | NCC Rating (A) | 412 | 412 | 412 | 412 | 412 | Rural | 170
|  |  |  | 10 POE Load (A) | 240 | 242 | 240 | 240 | 244
|  |  |  | Power Factor | 0.9869 | 0.98674 | 0.9869 | 0.9869 | 0.98657
|  |  |  | ECC Rating (A) | 412 | 412 | 412 | 412 | 412
|  |  |  | 50 POE Load (A) | 220 | 220 | 220 | 220 | 222
Belmont Bulk | 527-1 | Mt Gravatt | Upper Mt Gravatt | NCC Rating (A) | 631 | 631 | 631 | 631 | 631 | Urban | 70
|  |  |  | 10 POE Load (A) | 45 | 45 | 45 | 44 | 44
|  |  |  | Power Factor | 0.7633 | 0.75465 | 0.74857 | 0.73308 | 0.72073
|  |  |  | ECC Rating (A) | 631 | 631 | 631 | 631 | 631
|  |  |  | 50 POE Load (A) | 106 | 106 | 105 | 104 | 105
Belmont Bulk | 631-1 | Belmont BS | Mt Gravatt | NCC Rating (A) | 446 | 446 | 446 | 446 | 446 | Urban | 70
|  |  |  | 10 POE Load (A) | 240 | 242 | 241 | 242 | 246
|  |  |  | Power Factor | 0.9916 | 0.99149 | 0.99149 | 0.99138 | 0.99117
|  |  |  | ECC Rating (A) | 446 | 446 | 446 | 446 | 446
|  |  |  | 50 POE Load (A) | 381 | 383 | 384 | 385 | 390
Belmont Bulk | 632-1 | Belmont BS | Mt Gravatt | NCC Rating (A) | 446 | 446 | 446 | 446 | 446 | Urban | 70
|  |  |  | 10 POE Load (A) | 239 | 240 | 240 | 241 | 244
|  |  |  | Power Factor | 0.99152 | 0.99142 | 0.99141 | 0.99131 | 0.9911
|  |  |  | ECC Rating (A) | 446 | 446 | 446 | 446 | 446
|  |  |  | 50 POE Load (A) | 381 | 382 | 383 | 384 | 390
Belmont Bulk | 647-1 | Belmont BS | Eight Mile Plains Bus 2 | NCC Rating (A) | 566 | 566 | 566 | 566 | 566 | Urban | 270 | 2
|  |  |  | 10 POE Load (A) | 230 | 231 | 233 | 254 | 276
|  |  |  | Power Factor | 0.9913 | 0.99114 | 0.99099 | 0.98921 | 0.98707
|  |  |  | ECC Rating (A) | 566 | 566 | 566 | 566 | 566
|  |  |  | 50 POE Load (A) | 496 | 498 | 498 | 539 | 584
Belmont Bulk | 660-1 | Belmont BS | Scrub Road | NCC Rating (A) | 716 | 716 | 716 | 716 | 716 | Urban | 70
|  |  |  | 10 POE Load (A) | 188 | 186 | 184 | 181 | 180
|  |  |  | Power Factor | 0.99269 | 0.99277 | 0.99289 | 0.993 | 0.99304
|  |  |  | ECC Rating (A) | 716 | 716 | 716 | 716 | 716
|  |  |  | 50 POE Load (A) | 363 | 360 | 356 | 351 | 349
Belmont Bulk | 661-1 | Belmont BS | Scrub Road | NCC Rating (A) | 716 | 716 | 716 | 716 | 716 | Urban | 70
|  |  |  | 10 POE Load (A) | 190 | 188 | 186 | 183 | 182
|  |  |  | Power Factor | 0.99269 | 0.99277 | 0.99289 | 0.993 | 0.99304
|  |  |  | ECC Rating (A) | 716 | 716 | 716 | 716 | 716
|  |  |  | 50 POE Load (A) | 363 | 360 | 356 | 351 | 349
Belmont Bulk | 662-1 | Belmont BS | Upper Mt Gravatt | NCC Rating (A) | 695 | 695 | 695 | 695 | 695 | Urban | 70
|  |  |  | 10 POE Load (A) | 152 | 152 | 151 | 151 | 152
|  |  |  | Power Factor | 0.97509 | 0.97494 | 0.97494 | 0.97478 | 0.97448
|  |  |  | ECC Rating (A) | 695 | 695 | 695 | 695 | 695
|  |  |  | 50 POE Load (A) | 218 | 218 | 218 | 218 | 220
Belmont Bulk | 663-1 | Belmont BS | Upper Mt Gravatt | NCC Rating (A) | 695 | 695 | 695 | 695 | 695 | Urban | 70
|  |  |  | 10 POE Load (A) | 153 | 154 | 153 | 153 | 154
|  |  |  | Power Factor | 0.9753 | 0.97515 | 0.97515 | 0.97499 | 0.9747
|  |  |  | ECC Rating (A) | 695 | 695 | 695 | 695 | 695
|  |  |  | 50 POE Load (A) | 219 | 220 | 219 | 219 | 221
Belmont Bulk | 692-1 | Belmont BS | Holland Pk East | NCC Rating (A) | 447 | 447 | 447 | 447 | 447 | Urban | 70
|  |  |  | 10 POE Load (A) | 153 | 153 | 154 | 154 | 155
|  |  |  | Power Factor | 0.98656 | 0.98656 | 0.98649 | 0.98649 | 0.98642
|  |  |  | ECC Rating (A) | 447 | 447 | 447 | 447 | 447
|  |  |  | 50 POE Load (A) | 286 | 288 | 288 | 288 | 290
Belmont Bulk | 693-1 | Belmont BS | Holland Pk East | NCC Rating (A) | 447 | 447 | 447 | 447 | 447 | Urban | 70
|  |  |  | 10 POE Load (A) | 155 | 155 | 156 | 156 | 156
|  |  |  | Power Factor | 0.98678 | 0.98678 | 0.98672 | 0.98672 | 0.98665
|  |  |  | ECC Rating (A) | 447 | 447 | 447 | 447 | 447
|  |  |  | 50 POE Load (A) | 286 | 288 | 288 | 288 | 289
Brendale Bulk | 303-1 | Brendale BS | Albany Ck | NCC Rating (A) | 788 | 788 | 788 | 788 | 788 | Urban | 70
|  |  |  | 10 POE Load (A) | 184 | 184 | 184 | 183 | 184
|  |  |  | Power Factor | 0.99568 | 0.99568 | 0.99572 | 0.99576 | 0.99572
|  |  |  | ECC Rating (A) | 788 | 788 | 788 | 788 | 788
|  |  |  | 50 POE Load (A) | 344 | 344 | 342 | 340 | 342
Brendale Bulk | 309-1 | Brendale BS | 309 Tee1 | NCC Rating (A) | 810 | 810 | 810 | 810 | 810 | Rural | 170
|  |  |  | 10 POE Load (A) | 243 | 244 | 244 | 244 | 245
|  |  |  | Power Factor | 0.98923 | 0.98913 | 0.98913 | 0.98917 | 0.989
|  |  |  | ECC Rating (A) | 810 | 810 | 810 | 810 | 810
|  |  |  | 50 POE Load (A) | 472 | 474 | 474 | 473 | 478
Brendale Bulk | 309-2 | 309 Tee1 | Samford | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 79 | 79 | 79 | 81 | 81
|  |  |  | Power Factor | 0.99999 | 0.99999 | 0.99999 | 0.99997 | 0.99997
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 239 | 241 | 241 | 241 | 244
Brendale Bulk | 309-3 | 309 Tee1 | Arana Hills | NCC Rating (A) | 838 | 838 | 838 | 838 | 838 | Rural | 170
|  |  |  | 10 POE Load (A) | 165 | 165 | 165 | 164 | 165
|  |  |  | Power Factor | 0.98797 | 0.98789 | 0.98789 | 0.98796 | 0.9878
|  |  |  | ECC Rating (A) | 838 | 838 | 838 | 838 | 838
|  |  |  | 50 POE Load (A) | 499 | 501 | 501 | 499 | 504
Brendale Bulk | 310-1 | Brendale BS | 310 Tee1 | NCC Rating (A) | 715 | 715 | 715 | 715 | 715 | Urban | 70
|  |  |  | 10 POE Load (A) | 353 | 355 | 355 | 354 | 357
|  |  |  | Power Factor | 0.99215 | 0.99208 | 0.99208 | 0.99213 | 0.99201
|  |  |  | ECC Rating (A) | 715 | 715 | 715 | 715 | 715
|  |  |  | 50 POE Load (A) | 486 | 488 | 488 | 486 | 490
Brendale Bulk | 310-2 | 310 Tee1 | Arana Hills | NCC Rating (A) | 838 | 838 | 838 | 838 | 838 | Urban | 70
|  |  |  | 10 POE Load (A) | 353 | 355 | 355 | 354 | 357
|  |  |  | Power Factor | 0.99409 | 0.99404 | 0.99404 | 0.99408 | 0.99399
|  |  |  | ECC Rating (A) | 838 | 838 | 838 | 838 | 838
|  |  |  | 50 POE Load (A) | 486 | 488 | 488 | 486 | 490
Brendale Bulk | 333-1 | Brendale BS | Lawnton | NCC Rating (A) | 826 | 826 | 826 | 826 | 826 | Urban | 70
|  |  |  | 10 POE Load (A) | 257 | 260 | 261 | 263 | 268
|  |  |  | Power Factor | 0.98419 | 0.98411 | 0.98414 | 0.98413 | 0.98397
|  |  |  | ECC Rating (A) | 826 | 826 | 826 | 826 | 826
|  |  |  | 50 POE Load (A) | 424 | 430 | 433 | 436 | 443
Brendale Bulk | 3340-1 | Brendale Bs | Strathpine | NCC Rating (A) | 561 | 561 | 561 | 561 | 561 | Urban | 70
|  |  |  | 10 POE Load (A) | 125 | 125 | 124 | 123 | 123
|  |  |  | Power Factor | 0.98894 | 0.989 | 0.98906 | 0.98919 | 0.98919
|  |  |  | ECC Rating (A) | 561 | 561 | 561 | 561 | 561
|  |  |  | 50 POE Load (A) | 191 | 190 | 189 | 187 | 188
Brendale Bulk | 334-1 | Lawnton | 334 Tee1 | NCC Rating (A) | 645 | 645 | 645 | 645 | 645 | Rural | 170
|  |  |  | 10 POE Load (A) | 50 | 48 | 47 | 45 | 43
|  |  |  | Power Factor | 0.61205 | 0.58676 | 0.57045 | 0.54466 | 0.50704
|  |  |  | ECC Rating (A) | 645 | 645 | 645 | 645 | 645
|  |  |  | 50 POE Load (A) | 201 | 199 | 198 | 196 | 196
Brendale Bulk | 334-2 | 334 Tee1 | Whiteside | NCC Rating (A) | 860 | 860 | 860 | 860 | 860 | Rural | 170
|  |  |  | 10 POE Load (A) | 77 | 76 | 75 | 74 | 73
|  |  |  | Power Factor | 0.94051 | 0.94061 | 0.94077 | 0.94088 | 0.9511
|  |  |  | ECC Rating (A) | 860 | 860 | 860 | 860 | 860
|  |  |  | 50 POE Load (A) | 142 | 140 | 138 | 136 | 136
Brendale Bulk | 334-3 | 334 Tee1 | Nth Pine Dam | NCC Rating (A) | 645 | 645 | 645 | 645 | 645 | Rural | 170
|  |  |  | 10 POE Load (A) | 57 | 58 | 59 | 60 | 62
|  |  |  | Power Factor | 0.99704 | 0.99748 | 0.99784 | 0.99822 | 0.99874
|  |  |  | ECC Rating (A) | 645 | 645 | 645 | 645 | 645
|  |  |  | 50 POE Load (A) | 127 | 130 | 131 | 133 | 136
Brendale Bulk | 335-1 | Brendale BS | 335 Tee1 | NCC Rating (A) | 531 | 531 | 531 | 531 | 531 | Rural | 170
|  |  |  | 10 POE Load (A) | 182 | 184 | 183 | 183 | 186
|  |  |  | Power Factor | 0.96676 | 0.96674 | 0.96691 | 0.96707 | 0.967
|  |  |  | ECC Rating (A) | 531 | 531 | 531 | 531 | 531
|  |  |  | 50 POE Load (A) | 249 | 251 | 252 | 252 | 255
Brendale Bulk | 335-2 | 335 Tee | Whiteside | NCC Rating (A) | 860 | 860 | 860 | 860 | 860 | Rural | 170
|  |  |  | 10 POE Load (A) | 86 | 86 | 85 | 84 | 84
|  |  |  | Power Factor | 0.96048 | 0.9605 | 0.96054 | 0.96081 | 0.96084
|  |  |  | ECC Rating (A) | 860 | 860 | 860 | 860 | 860
|  |  |  | 50 POE Load (A) | 142 | 140 | 138 | 136 | 134
Brendale Bulk | 335-3 | 335 Tee | Nth Pine Dam | NCC Rating (A) | 531 | 531 | 531 | 531 | 531 | Rural | 170
|  |  |  | 10 POE Load (A) | 97 | 98 | 99 | 100 | 102
|  |  |  | Power Factor | 0.97955 | 0.9795 | 0.97941 | 0.97932 | 0.97922
|  |  |  | ECC Rating (A) | 531 | 531 | 531 | 531 | 531
|  |  |  | 50 POE Load (A) | 168 | 171 | 172 | 173 | 177
Brendale Bulk | 336-1 | Brendale BS | Strathpine | NCC Rating (A) | 515 | 515 | 515 | 515 | 515 | Urban | 70
|  |  |  | 10 POE Load (A) | 143 | 143 | 142 | 141 | 141
|  |  |  | Power Factor | 0.99818 | 0.99821 | 0.99824 | 0.99829 | 0.99829
|  |  |  | ECC Rating (A) | 515 | 515 | 515 | 515 | 515
|  |  |  | 50 POE Load (A) | 203 | 202 | 201 | 199 | 200
Brendale Bulk | 3364-1 | Brendale BS | Albany Ck | NCC Rating (A) | 788 | 788 | 788 | 788 | 788 | Urban | 70
|  |  |  | 10 POE Load (A) | 189 | 189 | 188 | 187 | 188
|  |  |  | Power Factor | 0.99562 | 0.99562 | 0.99566 | 0.9957 | 0.99566
|  |  |  | ECC Rating (A) | 788 | 788 | 788 | 788 | 788
|  |  |  | 50 POE Load (A) | 343 | 343 | 342 | 340 | 342
Brendale Bulk | 337-1 | Brendale BS | Strathpine | NCC Rating (A) | 537 | 537 | 537 | 537 | 537 | Urban | 70
|  |  |  | 10 POE Load (A) | 118 | 117 | 117 | 115 | 115
|  |  |  | Power Factor | 0.99568 | 0.99573 | 0.99577 | 0.99586 | 0.99586
|  |  |  | ECC Rating (A) | 537 | 537 | 537 | 537 | 537
|  |  |  | 50 POE Load (A) | 179 | 178 | 177 | 175 | 176
Brendale Bulk | 342-1 | Brendale BS | Bald Hills Bus 2 | NCC Rating (A) | 654 | 654 | 654 | 654 | 654 | Urban | 70
|  |  |  | 10 POE Load (A) | 108 | 108 | 108 | 108 | 108
|  |  |  | Power Factor | 0.99219 | 0.99219 | 0.99219 | 0.99219 | 0.99219
|  |  |  | ECC Rating (A) | 654 | 654 | 654 | 654 | 654
|  |  |  | 50 POE Load (A) | 200 | 200 | 200 | 200 | 200
Brendale Bulk | 349-1 | Brendale BS | Lawnton | NCC Rating (A) | 805 | 805 | 805 | 805 | 805 | Urban | 70
|  |  |  | 10 POE Load (A) | 277 | 280 | 282 | 284 | 290
|  |  |  | Power Factor | 0.98038 | 0.98024 | 0.98024 | 0.98018 | 0.9799
|  |  |  | ECC Rating (A) | 805 | 805 | 805 | 805 | 805
|  |  |  | 50 POE Load (A) | 434 | 439 | 442 | 445 | 452
Brendale Bulk | 464-1 | Brendale BS | Samford | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 180 | 181 | 181 | 182 | 183
|  |  |  | Power Factor | 0.99149 | 0.9914 | 0.9914 | 0.99139 | 0.99126
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 264 | 266 | 266 | 265 | 268
Browns Plains Bulk | 406A-1 | Bethania | Kingston | NCC Rating (A) | 647 | 647 | 647 | 647 | 647 | Urban | 70 | 1.5
|  |  |  | 10 POE Load (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 6.321e-06 | 6.3211e-06 | 6.3212e-06 | 6.3212e-06 | 6.3209e-06
|  |  |  | ECC Rating (A) | 647 | 647 | 647 | 647 | 647
|  |  |  | 50 POE Load (A) | 645 | 650 | 652 | 652 | 658
Browns Plains Bulk | 406B-1 | Crestmead | Kingston | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
|  |  |  | 10 POE Load (A) | 2 | 2 | 2 | 2 | 2
|  |  |  | Power Factor | 4.3754e-05 | 4.3755e-05 | 4.3755e-05 | 4.3755e-05 | 4.3754e-05
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 645 | 650 | 652 | 652 | 658
Browns Plains Bulk | 478-1 | Browns Plains BS | Nth Maclean | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 2 | 2 | 2 | 2 | 2
|  |  |  | Power Factor | 3.0986e-05 | 3.0986e-05 | 3.0986e-05 | 3.0986e-05 | 3.0986e-05
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 489 | 497 | 499 | 514 | 533
Browns Plains Bulk | 481-1 | Browns Plains BS | Cresmead | NCC Rating (A) | 741 | 741 | 741 | 741 | 741 | Urban | 70
|  |  |  | 10 POE Load (A) | 244 | 248 | 247 | 247 | 249
|  |  |  | Power Factor | 0.96341 | 0.96376 | 0.96387 | 0.96387 | 0.96201
|  |  |  | ECC Rating (A) | 741 | 741 | 741 | 741 | 741
|  |  |  | 50 POE Load (A) | 554 | 560 | 560 | 560 | 566
Browns Plains Bulk | 482-1 | Browns Plains BS | Cresmead | NCC Rating (A) | 741 | 741 | 741 | 741 | 741 | Urban | 70
|  |  |  | 10 POE Load (A) | 246 | 249 | 248 | 248 | 250
|  |  |  | Power Factor | 0.96328 | 0.96363 | 0.96375 | 0.96375 | 0.96188
|  |  |  | ECC Rating (A) | 741 | 741 | 741 | 741 | 741
|  |  |  | 50 POE Load (A) | 557 | 564 | 563 | 563 | 569
Browns Plains Bulk | 542-1 | Browns Plains BS | Heathwood | NCC Rating (A) | 745 | 745 | 745 | 745 | 745 | Urban | 70
|  |  |  | 10 POE Load (A) | 459 | 457 | 456 | 454 | 456
|  |  |  | Power Factor | 0.97753 | 0.97766 | 0.97779 | 0.97793 | 0.97779
|  |  |  | ECC Rating (A) | 745 | 745 | 745 | 745 | 745
|  |  |  | 50 POE Load (A) | 444 | 444 | 440 | 439 | 440
Burleigh Heads Bulk | 3751-1 | Burleigh Hds BS | Currumbin | NCC Rating (A) | 606 | 606 | 606 | 606 | 606 | Urban | 321 | 3
|  |  |  | 10 POE Load (A) | 572 | 575 | 576 | 576 | 581
|  |  |  | Power Factor | 0.97441 | 0.97427 | 0.97425 | 0.97423 | 0.97416
|  |  |  | ECC Rating (A) | 695 | 695 | 695 | 695 | 695
|  |  |  | 50 POE Load (A) | 920 | 924 | 926 | 927 | 932
Burleigh Heads Bulk | 3755-1 | Burleigh Hds BS | Currumbin | NCC Rating (A) | 606 | 606 | 606 | 606 | 606 | Urban | 321 | 3
|  |  |  | 10 POE Load (A) | 572 | 575 | 576 | 576 | 581
|  |  |  | Power Factor | 0.97441 | 0.97427 | 0.97425 | 0.97423 | 0.97416
|  |  |  | ECC Rating (A) | 695 | 695 | 695 | 695 | 695
|  |  |  | 50 POE Load (A) | 920 | 923 | 926 | 927 | 932
Burleigh Heads Bulk | 3756-1 | Burleigh Hds BS | 3756 Tee1 | NCC Rating (A) | 715 | 715 | 715 | 715 | 715 | Urban | 70
|  |  |  | 10 POE Load (A) | 181 | 182 | 182 | 182 | 183
|  |  |  | Power Factor | 0.98782 | 0.98771 | 0.9877 | 0.9877 | 0.98763
|  |  |  | ECC Rating (A) | 715 | 715 | 715 | 715 | 715
|  |  |  | 50 POE Load (A) | 270 | 271 | 272 | 272 | 273
Burleigh Heads Bulk | 3756-2 | 3756 Tee1 | Palm Beach | NCC Rating (A) | 614 | 614 | 614 | 614 | 614 | Urban | 70
|  |  |  | 10 POE Load (A) | 160 | 162 | 162 | 160 | 162
|  |  |  | Power Factor | 0.99625 | 0.99614 | 0.99615 | 0.99627 | 0.99614
|  |  |  | ECC Rating (A) | 614 | 614 | 614 | 614 | 614
|  |  |  | 50 POE Load (A) | 350 | 352 | 352 | 352 | 353
Burleigh Heads Bulk | 3756-3 | 3756 Tee1 | 3756 Tee2 | NCC Rating (A) | 636 | 636 | 636 | 636 | 636 | Urban | 70
|  |  |  | 10 POE Load (A) | 47 | 47 | 48 | 48 | 48
|  |  |  | Power Factor | 0.78262 | 0.77848 | 0.78309 | 0.78541 | 0.78508
|  |  |  | ECC Rating (A) | 636 | 636 | 636 | 636 | 636
|  |  |  | 50 POE Load (A) | 235 | 237 | 237 | 238 | 239
Burleigh Heads Bulk | 3756-4 | 3756 Tee2 | Currumbin | NCC Rating (A) | 790 | 790 | 790 | 790 | 790 | Urban | 70
|  |  |  | 10 POE Load (A) | 47 | 47 | 48 | 48 | 48
|  |  |  | Power Factor | 0.77916 | 0.77499 | 0.77966 | 0.78202 | 0.78169
|  |  |  | ECC Rating (A) | 790 | 790 | 790 | 790 | 790
|  |  |  | 50 POE Load (A) | 235 | 237 | 237 | 238 | 239
Burleigh Heads Bulk | 393-1 | Currumbin | Kirra | NCC Rating (A) | 582 | 636 | 636 | 636 | 636 | Urban | 70
|  |  |  | 10 POE Load (A) | 274 | 275 | 277 | 279 | 283
|  |  |  | Power Factor | 0.98596 | 0.98951 | 0.98943 | 0.98936 | 0.9892
|  |  |  | ECC Rating (A) | 582 | 636 | 636 | 636 | 636
|  |  |  | 50 POE Load (A) | 263 | 265 | 267 | 269 | 271
Burleigh Heads Bulk | 395-1 | Burleigh Hds BS | Miami | NCC Rating (A) | 747 | 747 | 747 | 747 | 747 | Urban | 70
|  |  |  | 10 POE Load (A) | 442 | 452 | 457 | 467 | 478
|  |  |  | Power Factor | 0.99229 | 0.99209 | 0.99197 | 0.99177 | 0.99153
|  |  |  | ECC Rating (A) | 747 | 747 | 747 | 747 | 747
|  |  |  | 50 POE Load (A) | 417 | 424 | 431 | 439 | 452
Burleigh Heads Bulk | 396-1 | Burleigh Hds BS | Palm Beach | NCC Rating (A) | 806 | 806 | 806 | 806 | 806 | Urban | 70
|  |  |  | 10 POE Load (A) | 207 | 208 | 208 | 208 | 210
|  |  |  | Power Factor | 0.98582 | 0.9857 | 0.98568 | 0.98569 | 0.98561
|  |  |  | ECC Rating (A) | 806 | 806 | 806 | 806 | 806
|  |  |  | 50 POE Load (A) | 352 | 353 | 353 | 353 | 355
Burleigh Heads Bulk | 397-1 | Burleigh Hds BS | 397 Tee1 | NCC Rating (A) | 659 | 659 | 659 | 659 | 659 | Urban | 70
|  |  |  | 10 POE Load (A) | 3 | 3 | 3 | 3 | 3
|  |  |  | Power Factor | 1.8279e-05 | 1.8279e-05 | 1.8279e-05 | 1.8279e-05 | 1.8279e-05
|  |  |  | ECC Rating (A) | 659 | 659 | 659 | 659 | 659
|  |  |  | 50 POE Load (A) | 3 | 3 | 3 | 3 | 3
Burleigh Heads Bulk | 397-2 | 397 Tee1 | 396 Tee | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | 0 | 0
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 4.7615e-05 | 4.7615e-05 | 4.7615e-05 | 4.7615e-05 | 4.7615e-05
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Burleigh Heads Bulk | 397-3 | 397 Tee1 | 397 Tee2 | NCC Rating (A) | 706 | 706 | 706 | 706 | 706 | Urban | 70
|  |  |  | 10 POE Load (A) | 2 | 2 | 2 | 2 | 2
|  |  |  | Power Factor | 2.6349e-05 | 2.6349e-05 | 2.6349e-05 | 2.6349e-05 | 2.6349e-05
|  |  |  | ECC Rating (A) | 706 | 706 | 706 | 706 | 706
|  |  |  | 50 POE Load (A) | 2 | 2 | 2 | 2 | 2
Burleigh Heads Bulk | 397-4 | 397 Tee2 | 3700 Tee1 | NCC Rating (A) | 362 | 362 | 362 | 362 | 362 | Urban | 70
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 8.6437e-07 | 8.6437e-07 | 8.6437e-07 | 8.6437e-07 | 8.6437e-07
|  |  |  | ECC Rating (A) | 362 | 362 | 362 | 362 | 362
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Burleigh Heads Bulk | 397-5 | 397 Tee2 | Mudgeeraba BS | NCC Rating (A) | 863 | 863 | 863 | 863 | 863 | Urban | 70
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 1.8984e-06 | 1.8984e-06 | 1.8984e-06 | 1.8984e-06 | 1.8984e-06
|  |  |  | ECC Rating (A) | 863 | 863 | 863 | 863 | 863
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Caboolture Bulk | 321-1 | Caboolture BS | Caboolture West | NCC Rating (A) | 688 | 688 | 688 | 688 | 688 | Urban | 70
|  |  |  | 10 POE Load (A) | 224 | 225 | 224 | 226 | 231
|  |  |  | Power Factor | 0.99351 | 0.99345 | 0.99348 | 0.99332 | 0.99308
|  |  |  | ECC Rating (A) | 688 | 688 | 688 | 688 | 688
|  |  |  | 50 POE Load (A) | 323 | 323 | 323 | 326 | 332
Caboolture Bulk | 322-1 | Caboolture BS | Caboolture West | NCC Rating (A) | 688 | 688 | 688 | 688 | 688 | Urban | 70
|  |  |  | 10 POE Load (A) | 235 | 236 | 235 | 238 | 243
|  |  |  | Power Factor | 0.98903 | 0.98895 | 0.989 | 0.98879 | 0.98848
|  |  |  | ECC Rating (A) | 688 | 688 | 688 | 688 | 688
|  |  |  | 50 POE Load (A) | 330 | 331 | 330 | 333 | 340
Caboolture Bulk | 323-1 | Caboolture West | 323 Tee1 | NCC Rating (A) | 344 | 344 | 344 | 344 | 344 | Rural | 170
|  |  |  | 10 POE Load (A) | 66 | 66 | 66 | 66 | 67
|  |  |  | Power Factor | 0.99963 | 0.99963 | 0.99963 | 0.99963 | 0.99958
|  |  |  | ECC Rating (A) | 344 | 344 | 344 | 344 | 344
|  |  |  | 50 POE Load (A) | 64 | 64 | 64 | 64 | 66
Caboolture Bulk | 323-2 | 323 Tee1 | Wamuran | NCC Rating (A) | 489 | 489 | 489 | 489 | 489 | Rural | 170
|  |  |  | 10 POE Load (A) | 66 | 66 | 66 | 66 | 67
|  |  |  | Power Factor | 0.99898 | 0.99898 | 0.99898 | 0.99898 | 0.99892
|  |  |  | ECC Rating (A) | 489 | 489 | 489 | 489 | 489
|  |  |  | 50 POE Load (A) | 64 | 64 | 64 | 64 | 66
Caboolture Bulk | 323-3 | 323 Tee1 | Woodford | NCC Rating (A) | 348 | 348 | 348 | 348 | 348 | Rural | 170
|  |  |  | 10 POE Load (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 1.5118e-05 | 1.5119e-05 | 1.5119e-05 | 1.5118e-05 | 1.5119e-05
|  |  |  | ECC Rating (A) | 348 | 348 | 348 | 348 | 348
|  |  |  | 50 POE Load (A) | 1 | 1 | 1 | 1 | 1
Caboolture Bulk | 350-1 | Caboolture BS | Ningi | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 402 | 402 | 400 | 397 | 398
|  |  |  | Power Factor | 0.97994 | 0.97994 | 0.98012 | 0.98044 | 0.98032
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 693 | 693 | 690 | 685 | 685
Caboolture Bulk | 412-1 | Caboolture BS | Toorbul Pt | NCC Rating (A) | 823 | 823 | 823 | 823 | 823 | Rural | 170 | 4.5
|  |  |  | 10 POE Load (A) | 336 | 336 | 334 | 332 | 333
|  |  |  | Power Factor | 0.97638 | 0.97638 | 0.97657 | 0.97688 | 0.97675
|  |  |  | ECC Rating (A) | 823 | 823 | 823 | 823 | 823
|  |  |  | 50 POE Load (A) | 717 | 717 | 714 | 709 | 709
Caboolture Bulk | 417-1 | Ningi | Toorbul Pt | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 231 | 231 | 229 | 228 | 229
|  |  |  | Power Factor | 0.99086 | 0.99086 | 0.991 | 0.99115 | 0.99105
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 535 | 535 | 532 | 528 | 528
Caboolture Bulk | 431-1 | Toorbul Point | Bribie Is | NCC Rating (A) | 419 | 419 | 419 | 419 | 419 | Urban | 70
|  |  |  | 10 POE Load (A) | 220 | 220 | 219 | 217 | 218
|  |  |  | Power Factor | 0.98931 | 0.98931 | 0.98938 | 0.98953 | 0.98946
|  |  |  | ECC Rating (A) | 419 | 419 | 419 | 419 | 419
|  |  |  | 50 POE Load (A) | 377 | 377 | 375 | 373 | 373
Caboolture Bulk | 448-1 | Morayfield Nth | 448 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
|  |  |  | 10 POE Load (A) | 487 | 491 | 495 | 503 | 514
|  |  |  | Power Factor | 0.98837 | 0.98821 | 0.98804 | 0.9877 | 0.98719
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 552 | 554 | 558 | 566 | 578
Caboolture Bulk | 448-2 | 448 Tee1 | Morayfield | NCC Rating (A) | 737 | 737 | 737 | 737 | 737 | Urban | 70
|  |  |  | 10 POE Load (A) | 468 | 472 | 477 | 485 | 496
|  |  |  | Power Factor | 0.99408 | 0.99399 | 0.99384 | 0.99364 | 0.99332
|  |  |  | ECC Rating (A) | 737 | 737 | 737 | 737 | 737
|  |  |  | 50 POE Load (A) | 439 | 441 | 446 | 454 | 463
Caboolture Bulk | 448-3 | 448 Tee1 | Caboolture West | NCC Rating (A) | 504 | 504 | 504 | 504 | 504 | Urban | 70
|  |  |  | 10 POE Load (A) | 21 | 21 | 19 | 20 | 19
|  |  |  | Power Factor | 0.97384 | 0.97407 | 0.97484 | 0.97576 | 0.97683
|  |  |  | ECC Rating (A) | 504 | 504 | 504 | 504 | 504
|  |  |  | 50 POE Load (A) | 109 | 108 | 107 | 109 | 109
Caboolture Bulk | 457-1 | Toorbul Pt | Bribie Island | NCC Rating (A) | 425 | 425 | 425 | 425 | 425 | Urban | 70
|  |  |  | 10 POE Load (A) | 219 | 219 | 217 | 215 | 216
|  |  |  | Power Factor | 0.99122 | 0.99122 | 0.99129 | 0.99142 | 0.99136
|  |  |  | ECC Rating (A) | 425 | 425 | 425 | 425 | 425
|  |  |  | 50 POE Load (A) | 377 | 377 | 375 | 373 | 373
Caboolture Bulk | 461-1 | Caboolture BS | Morayfield Nth | NCC Rating (A) | 762 | 762 | 762 | 762 | 762 | Urban | 260
|  |  |  | 10 POE Load (A) | 428 | 430 | 432 | 435 | 444
|  |  |  | Power Factor | 0.98968 | 0.98959 | 0.98949 | 0.98931 | 0.98893
|  |  |  | ECC Rating (A) | 762 | 762 | 762 | 762 | 762
|  |  |  | 50 POE Load (A) | 731 | 734 | 736 | 742 | 756
Caboolture Bulk | 499-1 | Caboolture BS | Morayfield Nth | NCC Rating (A) | 762 | 762 | 762 | 762 | 762 | Urban | 260 | 6.5
|  |  |  | 10 POE Load (A) | 432 | 433 | 435 | 438 | 447
|  |  |  | Power Factor | 0.9897 | 0.98961 | 0.98951 | 0.98933 | 0.98895
|  |  |  | ECC Rating (A) | 762 | 762 | 762 | 762 | 762
|  |  |  | 50 POE Load (A) | 732 | 735 | 737 | 743 | 757
Cleveland Bulk | 3550-1 | Cleveland BS | Victoria Pt | NCC Rating (A) | 775 | 775 | 775 | 775 | 775 | Urban | 70
|  |  |  | 10 POE Load (A) | 455 | 456 | 454 | 455 | 458
|  |  |  | Power Factor | 0.99258 | 0.99256 | 0.9926 | 0.99258 | 0.99251
|  |  |  | ECC Rating (A) | 775 | 775 | 775 | 775 | 775
|  |  |  | 50 POE Load (A) | 575 | 575 | 573 | 573 | 577
Cleveland Bulk | 3570-1 | Capalaba South | Capalaba | NCC Rating (A) | 649 | 649 | 649 | 649 | 649 | Urban | 70
|  |  |  | 10 POE Load (A) | 66 | 66 | 65 | 64 | 65
|  |  |  | Power Factor | 0.92408 | 0.92388 | 0.924 | 0.92441 | 0.92488
|  |  |  | ECC Rating (A) | 649 | 649 | 649 | 649 | 649
|  |  |  | 50 POE Load (A) | 243 | 242 | 241 | 239 | 240
Cleveland Bulk | 3580-1 | Redland Bay | 3580 Tee1 | NCC Rating (A) | 848 | 848 | 848 | 848 | 848 | Urban | 70
|  |  |  | 10 POE Load (A) | 37 | 38 | 39 | 39 | 40
|  |  |  | Power Factor | 0.99499 | 0.99524 | 0.99571 | 0.99593 | 0.9964
|  |  |  | ECC Rating (A) | 848 | 848 | 848 | 848 | 848
|  |  |  | 50 POE Load (A) | 289 | 291 | 291 | 291 | 295
Cleveland Bulk | 3580-2 | 3580 Tee1 | Mt Cotton | NCC Rating (A) | 715 | 715 | 715 | 715 | 715 | Urban | 70
|  |  |  | 10 POE Load (A) | 38 | 38 | 39 | 39 | 40
|  |  |  | Power Factor | 0.9919 | 0.99227 | 0.99295 | 0.99327 | 0.99396
|  |  |  | ECC Rating (A) | 715 | 715 | 715 | 715 | 715
|  |  |  | 50 POE Load (A) | 289 | 291 | 291 | 291 | 295
Cleveland Bulk | 3580-3 | 3580 Tee1 | Cornubia | NCC Rating (A) | 926 | 926 | 926 | 926 | 926 | Urban | 70
|  |  |  | 10 POE Load (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 2.2663e-06 | 2.2666e-06 | 2.2667e-06 | 2.2672e-06 | 2.2667e-06
|  |  |  | ECC Rating (A) | 926 | 926 | 926 | 926 | 926
|  |  |  | 50 POE Load (A) | 1 | 1 | 1 | 1 | 1
Cleveland Bulk | 371-1 | Cleveland BS | Birkdale | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
|  |  |  | 10 POE Load (A) | 383 | 383 | 381 | 378 | 379
|  |  |  | Power Factor | 0.98638 | 0.98634 | 0.98649 | 0.98667 | 0.9866
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 476 | 475 | 473 | 469 | 470
Cleveland Bulk | 372-1 | Cleveland BS | Raby Bay | NCC Rating (A) | 648 | 648 | 648 | 648 | 648 | Urban | 361
|  |  |  | 10 POE Load (A) | 340 | 341 | 341 | 340 | 342
|  |  |  | Power Factor | 0.99516 | 0.99513 | 0.99516 | 0.99521 | 0.99514
|  |  |  | ECC Rating (A) | 648 | 648 | 648 | 648 | 648
|  |  |  | 50 POE Load (A) | 621 | 623 | 623 | 621 | 627
Cleveland Bulk | 373-1 | Raby Bay | Capalaba | NCC Rating (A) | 715 | 715 | 715 | 715 | 715 | Urban | 70
|  |  |  | 10 POE Load (A) | 282 | 281 | 279 | 276 | 277
|  |  |  | Power Factor | 0.99575 | 0.99575 | 0.99582 | 0.99588 | 0.99586
|  |  |  | ECC Rating (A) | 715 | 715 | 715 | 715 | 715
|  |  |  | 50 POE Load (A) | 450 | 449 | 446 | 443 | 443
Cleveland Bulk | 374-1 | Cleveland BS | Capalaba South | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
|  |  |  | 10 POE Load (A) | 326 | 326 | 323 | 321 | 321
|  |  |  | Power Factor | 0.98809 | 0.9881 | 0.98825 | 0.9884 | 0.98836
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 482 | 482 | 479 | 475 | 476
Cleveland Bulk | 375-1 | Cleveland BS | 375 Tee1 | NCC Rating (A) | 649 | 649 | 649 | 649 | 649 | Rural | 170
|  |  |  | 10 POE Load (A) | 178 | 178 | 177 | 178 | 179
|  |  |  | Power Factor | 0.9958 | 0.99577 | 0.99584 | 0.99581 | 0.99576
|  |  |  | ECC Rating (A) | 649 | 649 | 649 | 649 | 649
|  |  |  | 50 POE Load (A) | 428 | 428 | 428 | 426 | 430
Cleveland Bulk | 375-2 | 375 Tee1 | Mt Cotton | NCC Rating (A) | 678 | 678 | 678 | 678 | 678 | Rural | 170
|  |  |  | 10 POE Load (A) | 178 | 178 | 177 | 178 | 179
|  |  |  | Power Factor | 0.9979 | 0.99789 | 0.99792 | 0.99791 | 0.99788
|  |  |  | ECC Rating (A) | 678 | 678 | 678 | 678 | 678
|  |  |  | 50 POE Load (A) | 428 | 428 | 428 | 427 | 430
Cleveland Bulk | 375-3 | 375 Tee1 | 425 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0.00030474 | 0.0003051 | 0.00030462 | 0.00030433 | 0.00030489
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Cleveland Bulk | 413-1 | Cleveland BS | Raby Bay | NCC Rating (A) | 648 | 648 | 648 | 648 | 648 | Urban | 370 | 9.5
|  |  |  | 10 POE Load (A) | 344 | 345 | 345 | 344 | 347
|  |  |  | Power Factor | 0.99518 | 0.99515 | 0.99518 | 0.99523 | 0.99516
|  |  |  | ECC Rating (A) | 648 | 648 | 648 | 648 | 648
|  |  |  | 50 POE Load (A) | 621 | 624 | 624 | 622 | 627
Cleveland Bulk | 425-1 | Cleveland BS | Victoria Pt | NCC Rating (A) | 705 | 705 | 705 | 705 | 705 | Urban | 70
|  |  |  | 10 POE Load (A) | 201 | 202 | 201 | 201 | 203
|  |  |  | Power Factor | 0.99825 | 0.99824 | 0.99826 | 0.99825 | 0.99821
|  |  |  | ECC Rating (A) | 705 | 705 | 705 | 705 | 705
|  |  |  | 50 POE Load (A) | 512 | 512 | 511 | 510 | 514
Cleveland Bulk | 465-1 | Victoria Pt | Redland Bay | NCC Rating (A) | 562 | 562 | 562 | 562 | 562 | Urban | 70
|  |  |  | 10 POE Load (A) | 271 | 272 | 271 | 272 | 275
|  |  |  | Power Factor | 0.99543 | 0.9954 | 0.99543 | 0.9954 | 0.99535
|  |  |  | ECC Rating (A) | 562 | 562 | 562 | 562 | 562
|  |  |  | 50 POE Load (A) | 417 | 417 | 417 | 415 | 419
Cleveland Bulk | 484-1 | Capalaba | Birkdale | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
|  |  |  | 10 POE Load (A) | 127 | 129 | 129 | 128 | 129
|  |  |  | Power Factor | 0.99222 | 0.99205 | 0.99206 | 0.99223 | 0.99211
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 482 | 482 | 480 | 478 | 478
Coomera Bulk | 3640-1 | Coomera BS | Hope Is | NCC Rating (A) | 759 | 759 | 759 | 759 | 759 | Urban | 70
|  |  |  | 10 POE Load (A) | 269 | 270 | 271 | 272 | 276
|  |  |  | Power Factor | 0.99001 | 0.98995 | 0.98983 | 0.98977 | 0.98976
|  |  |  | ECC Rating (A) | 759 | 759 | 759 | 759 | 759
|  |  |  | 50 POE Load (A) | 489 | 491 | 493 | 494 | 502
Coomera Bulk | 3641-1 | Coomera BS | Pimpama East | NCC Rating (A) | 848 | 848 | 848 | 848 | 848 | Urban | 200 | 4.5
|  |  |  | 10 POE Load (A) | 327 | 373 | 384 | 399 | 416
|  |  |  | Power Factor | 0.97769 | 0.97291 | 0.97169 | 0.97111 | 0.96916
|  |  |  | ECC Rating (A) | 848 | 848 | 848 | 848 | 848
|  |  |  | 50 POE Load (A) | 607 | 698 | 721 | 747 | 784
Coomera Bulk | 3642-1 | Coomera BS | Pimpama East | NCC Rating (A) | 848 | 848 | 848 | 848 | 848 | Urban | 200 | 4.5
|  |  |  | 10 POE Load (A) | 330 | 376 | 387 | 402 | 419
|  |  |  | Power Factor | 0.9776 | 0.97282 | 0.9716 | 0.97101 | 0.96906
|  |  |  | ECC Rating (A) | 848 | 848 | 848 | 848 | 848
|  |  |  | 50 POE Load (A) | 606 | 698 | 721 | 747 | 783
Coomera Bulk | 394-1 | Coomera BS | Hope Is | NCC Rating (A) | 759 | 759 | 759 | 759 | 759 | Urban | 70
|  |  |  | 10 POE Load (A) | 275 | 276 | 278 | 279 | 282
|  |  |  | Power Factor | 0.99337 | 0.99332 | 0.99322 | 0.99317 | 0.99316
|  |  |  | ECC Rating (A) | 759 | 759 | 759 | 759 | 759
|  |  |  | 50 POE Load (A) | 489 | 491 | 493 | 495 | 502
Coorparoo Bulk | 3429-1 | Coorparoo BS | Holland Park | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
|  |  |  | 10 POE Load (A) | 182 | 187 | 188 | 188 | 190
|  |  |  | Power Factor | 0.99588 | 0.98731 | 0.9873 | 0.9873 | 0.98726
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 347 | 349 | 351 | 351 | 355
Coorparoo Bulk | 3430-1 | Coorparoo BS | Holland Park | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
|  |  |  | 10 POE Load (A) | 179 | 178 | 179 | 179 | 181
|  |  |  | Power Factor | 0.99586 | 0.99972 | 0.99971 | 0.99971 | 0.99967
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 348 | 350 | 352 | 352 | 356
Coorparoo Bulk | 584-4 | 584 Tee2 | Coorparoo BS | NCC Rating (A) | 764 | 764 | 764 | 764 | 764 | Urban | 70
|  |  |  | 10 POE Load (A) | 2 | 2 | 2 | 2 | 2
|  |  |  | Power Factor | 7.9103e-07 | 7.9103e-07 | 7.9103e-07 | 7.9103e-07 | 7.9103e-07
|  |  |  | ECC Rating (A) | 764 | 764 | 764 | 764 | 764
|  |  |  | 50 POE Load (A) | 2 | 2 | 2 | 2 | 2
Coorparoo Bulk | 612-1 | Coorparoo BS | Camp Hill | NCC Rating (A) | 820 | 820 | 820 | 820 | 820 | Urban | 70
|  |  |  | 10 POE Load (A) | 277 | 277 | 277 | 277 | 278
|  |  |  | Power Factor | 0.99159 | 0.99154 | 0.99159 | 0.99159 | 0.99148
|  |  |  | ECC Rating (A) | 820 | 820 | 820 | 820 | 820
|  |  |  | 50 POE Load (A) | 512 | 512 | 512 | 510 | 516
Coorparoo Bulk | 613-1 | Coorparoo BS | Camp Hill | NCC Rating (A) | 820 | 820 | 820 | 820 | 820 | Urban | 70
|  |  |  | 10 POE Load (A) | 277 | 277 | 277 | 277 | 278
|  |  |  | Power Factor | 0.99159 | 0.99154 | 0.99159 | 0.99159 | 0.99148
|  |  |  | ECC Rating (A) | 820 | 820 | 820 | 820 | 820
|  |  |  | 50 POE Load (A) | 512 | 512 | 512 | 510 | 516
Coorparoo Bulk | 648-1 | Scrub Rd | 648 Tee1 | NCC Rating (A) | 654 | 654 | 654 | 654 | 654 | Urban | 70
|  |  |  | 10 POE Load (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 1.232e-06 | 1.2324e-06 | 1.2324e-06 | 1.2328e-06 | 1.2324e-06
|  |  |  | ECC Rating (A) | 654 | 654 | 654 | 654 | 654
|  |  |  | 50 POE Load (A) | 1 | 1 | 1 | 1 | 1
Coorparoo Bulk | 648-2 | 648 Tee1 | 584 Tee1 | NCC Rating (A) | 348 | 348 | 348 | 348 | 348 | Urban | 70
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 1.549e-05 | 1.5487e-05 | 1.5487e-05 | 1.5489e-05 | 1.5488e-05
|  |  |  | ECC Rating (A) | 348 | 348 | 348 | 348 | 348
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Coorparoo Bulk | 648-3 | 648 Tee1 | Camp Hill | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
|  |  |  | 10 POE Load (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 1.1765e-05 | 1.1765e-05 | 1.1765e-05 | 1.1765e-05 | 1.1765e-05
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 1 | 1 | 1 | 1 | 1
Doboy Bulk | 3426-1 | Queensport | Bulimba | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
|  |  |  | 10 POE Load (A) | 206 | 207 | 207 | 208 | 211
|  |  |  | Power Factor | 0.9958 | 0.99576 | 0.99576 | 0.99571 | 0.99557
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 337 | 339 | 338 | 340 | 345
Doboy Bulk | 414-1 | Doboy BS | Tingalpa | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 70
|  |  |  | 10 POE Load (A) | 136 | 136 | 135 | 134 | 136
|  |  |  | Power Factor | 0.99684 | 0.99684 | 0.99688 | 0.99692 | 0.99685
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | 50 POE Load (A) | 300 | 302 | 300 | 298 | 302
Doboy Bulk | 416-1 | Doboy BS | Murarrie | NCC Rating (A) | 397 | 397 | 397 | 397 | 397 | Urban | 70
|  |  |  | 10 POE Load (A) | 152 | 152 | 152 | 151 | 152
|  |  |  | Power Factor | 0.96077 | 0.96087 | 0.96087 | 0.96098 | 0.96087
|  |  |  | ECC Rating (A) | 397 | 397 | 397 | 397 | 397
|  |  |  | 50 POE Load (A) | 291 | 289 | 289 | 287 | 287
Doboy Bulk | 443-1 | Queensport | Bulimba | NCC Rating (A) | 652 | 652 | 652 | 652 | 652 | Urban | 70
|  |  |  | 10 POE Load (A) | 146 | 146 | 146 | 147 | 149
|  |  |  | Power Factor | 0.99765 | 0.99761 | 0.99761 | 0.99758 | 0.99747
|  |  |  | ECC Rating (A) | 652 | 652 | 652 | 652 | 652
|  |  |  | 50 POE Load (A) | 338 | 340 | 340 | 341 | 347
Doboy Bulk | 446-11 | Doboy BS | Wellington Rd | NCC Rating (A) | 521 | 521 | 521 | 521 | 521 | 0 | 0
|  |  |  | 10 POE Load (A) | 106 | 106 | 106 | 106 | 106
|  |  |  | Power Factor | 0.96691 | 0.96693 | 0.96693 | 0.96695 | 0.96702
|  |  |  | ECC Rating (A) | 521 | 521 | 521 | 521 | 521
|  |  |  | 50 POE Load (A) | 182 | 182 | 182 | 182 | 182
Doboy Bulk | 446-12 | Wellington Rd | Queensport | NCC Rating (A) | 455 | 455 | 455 | 455 | 455 | 0 | 0
|  |  |  | 10 POE Load (A) | 40 | 40 | 40 | 40 | 40
|  |  |  | Power Factor | 0.8885 | 0.88845 | 0.88845 | 0.8884 | 0.88788
|  |  |  | ECC Rating (A) | 455 | 455 | 455 | 455 | 455
|  |  |  | 50 POE Load (A) | 91 | 91 | 91 | 91 | 91
Doboy Bulk | 558-1 | Hemmant | Tingalpa | NCC Rating (A) | 680 | 680 | 680 | 680 | 680 | Urban | 70
|  |  |  | 10 POE Load (A) | 180 | 180 | 179 | 178 | 180
|  |  |  | Power Factor | 0.99645 | 0.99645 | 0.9965 | 0.99653 | 0.99645
|  |  |  | ECC Rating (A) | 680 | 680 | 680 | 680 | 680
|  |  |  | 50 POE Load (A) | 299 | 300 | 299 | 297 | 300
Doboy Bulk | 563-1 | Doboy BS | Hemmant | NCC Rating (A) | 389 | 389 | 389 | 389 | 389 | Urban | 70
|  |  |  | 10 POE Load (A) | 154 | 154 | 154 | 152 | 153
|  |  |  | Power Factor | 0.99327 | 0.99327 | 0.9933 | 0.99336 | 0.99331
|  |  |  | ECC Rating (A) | 389 | 389 | 389 | 389 | 389
|  |  |  | 50 POE Load (A) | 280 | 281 | 280 | 279 | 281
Doboy Bulk | 564-1 | Doboy BS | Hemmant | NCC Rating (A) | 389 | 389 | 389 | 389 | 389 | Urban | 70
|  |  |  | 10 POE Load (A) | 148 | 148 | 148 | 146 | 147
|  |  |  | Power Factor | 0.99128 | 0.99128 | 0.99131 | 0.99138 | 0.99132
|  |  |  | ECC Rating (A) | 389 | 389 | 389 | 389 | 389
|  |  |  | 50 POE Load (A) | 279 | 280 | 279 | 278 | 280
Doboy Bulk | 575C-1 | Doboy BS | Murarrie | NCC Rating (A) | 397 | 397 | 397 | 397 | 397 | Urban | 70
|  |  |  | 10 POE Load (A) | 144 | 143 | 143 | 142 | 143
|  |  |  | Power Factor | 0.95852 | 0.95863 | 0.95863 | 0.95874 | 0.95863
|  |  |  | ECC Rating (A) | 397 | 397 | 397 | 397 | 397
|  |  |  | 50 POE Load (A) | 291 | 289 | 289 | 287 | 287
Doboy Bulk | 581-1 | Doboy BS | Queensport | NCC Rating (A) | 699 | 699 | 699 | 699 | 699 | Urban | 166 | 10
|  |  |  | 10 POE Load (A) | 401 | 401 | 400 | 400 | 403
|  |  |  | Power Factor | 0.98482 | 0.98485 | 0.9849 | 0.98493 | 0.98487
|  |  |  | ECC Rating (A) | 828 | 828 | 828 | 828 | 828
|  |  |  | 50 POE Load (A) | 744 | 744 | 743 | 743 | 749
Doboy Bulk | 645-1 | Doboy BS | Gibson Island | NCC Rating (A) | 468 | 468 | 468 | 468 | 468 | HighSec | 0
|  |  |  | 10 POE Load (A) | 5 | 5 | 5 | 5 | 5
|  |  |  | Power Factor | 1.3174e-06 | 1.3174e-06 | 1.3174e-06 | 1.3174e-06 | 1.3174e-06
|  |  |  | ECC Rating (A) | 468 | 468 | 468 | 468 | 468
|  |  |  | 50 POE Load (A) | 5 | 5 | 5 | 5 | 5
Doboy Bulk | 677-1 | Doboy BS | Queensport | NCC Rating (A) | 699 | 699 | 699 | 699 | 699 | Urban | 166 | 7
|  |  |  | 10 POE Load (A) | 400 | 400 | 399 | 399 | 402
|  |  |  | Power Factor | 0.98481 | 0.98485 | 0.98489 | 0.98493 | 0.98486
|  |  |  | ECC Rating (A) | 828 | 828 | 828 | 828 | 828
|  |  |  | 50 POE Load (A) | 744 | 744 | 743 | 743 | 749
Gatton Bulk | 377-1 | Gatton BS | 377 Tee1 | NCC Rating (A) | 891 | 891 | 891 | 891 | 891 | Rural | 170
|  |  |  | 10 POE Load (A) | 189 | 190 | 189 | 187 | 189
|  |  |  | Power Factor | 0.97624 | 0.97618 | 0.97624 | 0.97653 | 0.97632
|  |  |  | ECC Rating (A) | 891 | 891 | 891 | 891 | 891
|  |  |  | 50 POE Load (A) | 277 | 277 | 277 | 277 | 279
Gatton Bulk | 377-2 | 377 Tee1 | 487 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 4.5088e-05 | 4.5168e-05 | 4.5088e-05 | 4.5136e-05 | 4.511e-05
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Gatton Bulk | 377-3 | 377 Tee1 | 377 Tee2 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 189 | 190 | 189 | 187 | 189
|  |  |  | Power Factor | 0.97623 | 0.97618 | 0.97623 | 0.97653 | 0.97631
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 277 | 277 | 277 | 277 | 279
Gatton Bulk | 377-4 | 377 Tee2 | Gatton | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 189 | 190 | 189 | 187 | 189
|  |  |  | Power Factor | 0.98002 | 0.98 | 0.98002 | 0.98025 | 0.98011
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 277 | 277 | 277 | 277 | 279
Gatton Bulk | 377-5 | 377 Tee2 | Glenmore Grove | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Rural | 170
|  |  |  | 10 POE Load (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 2.1626e-05 | 2.1626e-05 | 2.1626e-05 | 2.1626e-05 | 2.1626e-05
|  |  |  | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
|  |  |  | 50 POE Load (A) | 1 | 1 | 1 | 1 | 1
Gatton Bulk | 3859-1 | Gatton BS | Springfield Central | NCC Rating (A) | 809 | 809 | 809 | 809 | 809 | Rural | 170
|  |  |  | 10 POE Load (A) | 25 | 25 | 25 | 24 | 24
|  |  |  | Power Factor | 0.91081 | 0.91081 | 0.91081 | 0.9111 | 0.9111
|  |  |  | ECC Rating (A) | 809 | 809 | 809 | 809 | 809
|  |  |  | 50 POE Load (A) | 47 | 47 | 47 | 45 | 45
Gatton Bulk | 3860-1 | Gatton BS | Springfield Central | NCC Rating (A) | 809 | 809 | 809 | 809 | 809 | Rural | 170
|  |  |  | 10 POE Load (A) | 25 | 25 | 25 | 24 | 24
|  |  |  | Power Factor | 0.91045 | 0.91045 | 0.91045 | 0.91073 | 0.91073
|  |  |  | ECC Rating (A) | 809 | 809 | 809 | 809 | 809
|  |  |  | 50 POE Load (A) | 47 | 47 | 47 | 45 | 45
Gatton Bulk | 487-1 | Gatton BS | 487 Tee1 | NCC Rating (A) | 891 | 891 | 891 | 891 | 891 | Rural | 170
|  |  |  | 10 POE Load (A) | 201 | 202 | 201 | 199 | 200
|  |  |  | Power Factor | 0.97469 | 0.97465 | 0.97469 | 0.97509 | 0.97493
|  |  |  | ECC Rating (A) | 891 | 891 | 891 | 891 | 891
|  |  |  | 50 POE Load (A) | 370 | 370 | 370 | 370 | 372
Gatton Bulk | 487-2 | 487 Tee1 | 377 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 4.3548e-05 | 4.3535e-05 | 4.3548e-05 | 4.3551e-05 | 4.3551e-05
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Gatton Bulk | 487-3 | 487 Tee1 | 487 Tee2 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 202 | 202 | 202 | 199 | 201
|  |  |  | Power Factor | 0.97348 | 0.97347 | 0.97348 | 0.97382 | 0.97371
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 371 | 371 | 371 | 371 | 372
Gatton Bulk | 487-6 | 487 Tee3 | 3844 Tee1 | NCC Rating (A) | 348 | 348 | 348 | 348 | 348 | Rural | 170
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 2.4768e-05 | 2.4773e-05 | 2.4768e-05 | 2.4771e-05 | 2.4773e-05
|  |  |  | ECC Rating (A) | 348 | 348 | 348 | 348 | 348
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Gatton Bulk | 487-8 | 487 Tee4 | 3844 Tee2 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0.00046923 | 0.00046702 | 0.00046923 | 0.00046572 | 0.00046576
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Gatton Bulk | 487-9 | 487 Tee2 | Gatton | NCC Rating (A) | 878 | 878 | 878 | 878 | 878 | Rural | 170
|  |  |  | 10 POE Load (A) | 109 | 110 | 109 | 109 | 110
|  |  |  | Power Factor | 0.988 | 0.98794 | 0.988 | 0.98801 | 0.98776
|  |  |  | ECC Rating (A) | 878 | 878 | 878 | 878 | 878
|  |  |  | 50 POE Load (A) | 281 | 281 | 281 | 281 | 282
Gatton Bulk | 531-1 | Gatton | Tenthill | NCC Rating (A) | 290 | 290 | 290 | 290 | 290 | Rural | 170
|  |  |  | 10 POE Load (A) | 63 | 63 | 63 | 61 | 63
|  |  |  | Power Factor | 0.95571 | 0.95571 | 0.95571 | 0.95576 | 0.95571
|  |  |  | ECC Rating (A) | 290 | 290 | 290 | 290 | 290
|  |  |  | 50 POE Load (A) | 59 | 59 | 59 | 59 | 59
Gatton Bulk | 532-1 | Tenthill | 532 Tee1 | NCC Rating (A) | 416 | 416 | 416 | 416 | 416 | Rural | 170
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 8.2544e-05 | 8.2598e-05 | 8.2544e-05 | 8.2596e-05 | 8.2615e-05
|  |  |  | ECC Rating (A) | 416 | 416 | 416 | 416 | 416
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Gatton Bulk | 533-1 | Tenthill | Mt Sylvia | NCC Rating (A) | 144 | 144 | 144 | 144 | 144 | Rural | 170
|  |  |  | 10 POE Load (A) | 16 | 16 | 16 | 16 | 16
|  |  |  | Power Factor | 0.84929 | 0.84929 | 0.84929 | 0.84929 | 0.84929
|  |  |  | ECC Rating (A) | 144 | 144 | 144 | 144 | 144
|  |  |  | 50 POE Load (A) | 15 | 15 | 15 | 15 | 15
Goodna Bulk | 3800-1 | Goodna BS | Cooneana | NCC Rating (A) | 695 | 695 | 695 | 695 | 695 | Rural | 170
|  |  |  | 10 POE Load (A) | 46 | 86 | 90 | 93 | 96
|  |  |  | Power Factor | 0.99617 | 0.99043 | 0.98986 | 0.98927 | 0.98867
|  |  |  | ECC Rating (A) | 695 | 695 | 695 | 695 | 695
|  |  |  | 50 POE Load (A) | 89 | 173 | 180 | 186 | 191
Goodna Bulk | 3801-1 | Goodna BS | Carol Pk Central | NCC Rating (A) | 793 | 793 | 793 | 793 | 793 | Urban | 70
|  |  |  | 10 POE Load (A) | 294 | 296 | 295 | 295 | 295
|  |  |  | Power Factor | 0.99232 | 0.99209 | 0.99211 | 0.99207 | 0.99359
|  |  |  | ECC Rating (A) | 793 | 793 | 793 | 793 | 793
|  |  |  | 50 POE Load (A) | 512 | 515 | 517 | 515 | 517
Goodna Bulk | 3802-1 | Goodna BS | Springfield | NCC Rating (A) | 627 | 627 | 627 | 627 | 627 | Urban | 70
|  |  |  | 10 POE Load (A) | 264 | 276 | 279 | 285 | 291
|  |  |  | Power Factor | 0.98788 | 0.9866 | 0.98621 | 0.98548 | 0.99315
|  |  |  | ECC Rating (A) | 627 | 627 | 627 | 627 | 627
|  |  |  | 50 POE Load (A) | 483 | 506 | 512 | 523 | 535
Goodna Bulk | 3803-1 | Goodna BS | Carol Park | NCC Rating (A) | 550 | 550 | 550 | 550 | 550 | Urban | 70
|  |  |  | 10 POE Load (A) | 222 | 230 | 232 | 235 | 239
|  |  |  | Power Factor | 0.99736 | 0.99672 | 0.99653 | 0.99617 | 0.99909
|  |  |  | ECC Rating (A) | 550 | 550 | 550 | 550 | 550
|  |  |  | 50 POE Load (A) | 317 | 329 | 338 | 341 | 348
Goodna Bulk | 3805-1 | Goodna BS | Carol Park | NCC Rating (A) | 550 | 550 | 550 | 550 | 550 | Urban | 70
|  |  |  | 10 POE Load (A) | 203 | 210 | 212 | 215 | 218
|  |  |  | Power Factor | 0.99628 | 0.99554 | 0.99531 | 0.9949 | 0.99842
|  |  |  | ECC Rating (A) | 550 | 550 | 550 | 550 | 550
|  |  |  | 50 POE Load (A) | 305 | 316 | 324 | 328 | 335
Goodna Bulk | 3806-1 | Goodna BS | Springfield | NCC Rating (A) | 627 | 627 | 627 | 627 | 627 | Urban | 70
|  |  |  | 10 POE Load (A) | 262 | 275 | 277 | 284 | 290
|  |  |  | Power Factor | 0.98782 | 0.98654 | 0.98615 | 0.98543 | 0.99311
|  |  |  | ECC Rating (A) | 627 | 627 | 627 | 627 | 627
|  |  |  | 50 POE Load (A) | 483 | 506 | 512 | 522 | 535
Goodna Bulk | 3807-1 | Goodna BS | Redbank | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
|  |  |  | 10 POE Load (A) | 210 | 211 | 215 | 218 | 223
|  |  |  | Power Factor | 0.98522 | 0.98527 | 0.98517 | 0.98507 | 0.98492
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 203 | 204 | 208 | 211 | 216
Goodna Bulk | 3808-1 | Goodna BS | Carol Pk Central | NCC Rating (A) | 751 | 751 | 751 | 751 | 751 | Urban | 70
|  |  |  | 10 POE Load (A) | 294 | 297 | 296 | 296 | 296
|  |  |  | Power Factor | 0.99243 | 0.9922 | 0.99222 | 0.99218 | 0.99369
|  |  |  | ECC Rating (A) | 751 | 751 | 751 | 751 | 751
|  |  |  | 50 POE Load (A) | 512 | 515 | 517 | 515 | 517
Goodna Bulk | 3809-1 | Goodna BS | Cooneana | NCC Rating (A) | 695 | 695 | 695 | 695 | 695 | Rural | 170
|  |  |  | 10 POE Load (A) | 52 | 98 | 101 | 105 | 109
|  |  |  | Power Factor | 0.99651 | 0.99101 | 0.99045 | 0.98989 | 0.9893
|  |  |  | ECC Rating (A) | 695 | 695 | 695 | 695 | 695
|  |  |  | 50 POE Load (A) | 89 | 173 | 180 | 185 | 191
Goodna Bulk | 3880-1 | Carol Park | Springfield Central | NCC Rating (A) | 794 | 794 | 794 | 794 | 794 | Urban | 70
|  |  |  | 10 POE Load (A) | 142 | 164 | 171 | 183 | 189
|  |  |  | Power Factor | 0.9787 | 0.97639 | 0.97565 | 0.9744 | 0.9973
|  |  |  | ECC Rating (A) | 794 | 794 | 794 | 794 | 794
|  |  |  | 50 POE Load (A) | 278 | 326 | 339 | 360 | 373
Goodna Bulk | 3881-1 | Springfield | Springfield Central | NCC Rating (A) | 794 | 794 | 794 | 794 | 794 | Urban | 70
|  |  |  | 10 POE Load (A) | 172 | 196 | 204 | 216 | 222
|  |  |  | Power Factor | 0.97151 | 0.96877 | 0.9679 | 0.96648 | 0.99326
|  |  |  | ECC Rating (A) | 794 | 794 | 794 | 794 | 794
|  |  |  | 50 POE Load (A) | 275 | 321 | 334 | 355 | 368
Goodna Bulk | 456-1 | Wacol Sth | 456 Tee1 | NCC Rating (A) | 813 | 813 | 813 | 813 | 813 | Urban | 70
|  |  |  | 10 POE Load (A) | 75 | 80 | 82 | 85 | 87
|  |  |  | Power Factor | 0.99656 | 0.9951 | 0.99458 | 0.99369 | 0.9996
|  |  |  | ECC Rating (A) | 813 | 813 | 813 | 813 | 813
|  |  |  | 50 POE Load (A) | 153 | 162 | 168 | 172 | 177
Goodna Bulk | 456-2 | 456 Tee1 | Carol Pk Central | NCC Rating (A) | 493 | 493 | 493 | 493 | 493 | Urban | 70
|  |  |  | 10 POE Load (A) | 75 | 80 | 82 | 85 | 87
|  |  |  | Power Factor | 0.99654 | 0.99507 | 0.99454 | 0.99364 | 0.99958
|  |  |  | ECC Rating (A) | 493 | 493 | 493 | 493 | 493
|  |  |  | 50 POE Load (A) | 153 | 162 | 168 | 172 | 177
Goodna Bulk | 456-3 | 456 Tee1 | Carol Pk | NCC Rating (A) | 493 | 493 | 493 | 493 | 493 | Urban | 70
|  |  |  | 10 POE Load (A) | 75 | 80 | 82 | 85 | 87
|  |  |  | Power Factor | 0.99537 | 0.99383 | 0.99328 | 0.99235 | 0.99923
|  |  |  | ECC Rating (A) | 493 | 493 | 493 | 493 | 493
|  |  |  | 50 POE Load (A) | 153 | 162 | 168 | 172 | 177
Griffin Bulk | 312-1 | Kallangur | Narangba | NCC Rating (A) | 489 | 489 | 489 | 489 | 489 | Urban | 70 | 2.5
|  |  |  | 10 POE Load (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 1.4388e-05 | 1.4388e-05 | 1.4388e-05 | 1.4388e-05 | 1.4388e-05
|  |  |  | ECC Rating (A) | 489 | 489 | 489 | 489 | 489
|  |  |  | 50 POE Load (A) | 1 | 1 | 1 | 1 | 1
Griffin Bulk | 320-1 | Griffin BS | 320 Tee1 | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70 | 3.5
|  |  |  | 10 POE Load (A) | 287 | 292 | 338 | 340 | 342
|  |  |  | Power Factor | 0.99892 | 0.99883 | 0.99791 | 0.99788 | 0.99784
|  |  |  | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | 50 POE Load (A) | 403 | 411 | 508 | 514 | 517
Griffin Bulk | 320-2 | 320 Tee1 | Mango Hill Bus 2 | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 220
|  |  |  | 10 POE Load (A) | 207 | 208 | 197 | 189 | 190
|  |  |  | Power Factor | 0.99998 | 0.99999 | 0.99916 | 0.99991 | 0.99992
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | 50 POE Load (A) | 412 | 414 | 394 | 413 | 414
Griffin Bulk | 320-3 | 320 Tee1 | Kalangur | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 70
|  |  |  | 10 POE Load (A) | 81 | 85 | 147 | 152 | 153
|  |  |  | Power Factor | 0.98685 | 0.98722 | 0.98952 | 0.98975 | 0.98974
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | 50 POE Load (A) | 251 | 261 | 389 | 399 | 402
Griffin Bulk | 3329-1 | Griffin BS | 3329 Tee1 | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70
|  |  |  | 10 POE Load (A) | 318 | 326 | 413 | 420 | 422
|  |  |  | Power Factor | 0.99401 | 0.99363 | 0.98848 | 0.98812 | 0.988
|  |  |  | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | 50 POE Load (A) | 368 | 379 | 491 | 502 | 505
Griffin Bulk | 3329-2 | 3329 Tee1 | 3330 Tee1 | NCC Rating (A) | 865 | 865 | 865 | 865 | 865 | Urban | 70
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 6.7994e-06 | 6.7994e-06 | 6.7988e-06 | 6.7997e-06 | 6.7991e-06
|  |  |  | ECC Rating (A) | 865 | 865 | 865 | 865 | 865
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Griffin Bulk | 3329-3 | 3329 Tee1 | Kallangur | NCC Rating (A) | 762 | 762 | 762 | 762 | 762 | Urban | 70
|  |  |  | 10 POE Load (A) | 319 | 327 | 414 | 420 | 423
|  |  |  | Power Factor | 0.99431 | 0.99401 | 0.98993 | 0.98965 | 0.98956
|  |  |  | ECC Rating (A) | 762 | 762 | 762 | 762 | 762
|  |  |  | 50 POE Load (A) | 369 | 380 | 492 | 502 | 506
Griffin Bulk | 3330-1 | Griffin BS | 3330 Tee1 | NCC Rating (A) | 893 | 893 | 893 | 893 | 893 | Urban | 70
|  |  |  | 10 POE Load (A) | 163 | 167 | 246 | 248 | 250
|  |  |  | Power Factor | 0.99711 | 0.99687 | 0.98808 | 0.98789 | 0.98783
|  |  |  | ECC Rating (A) | 893 | 893 | 893 | 893 | 893
|  |  |  | 50 POE Load (A) | 279 | 287 | 388 | 394 | 396
Griffin Bulk | 3330-2 | 3330 Tee1 | 3329 Tee1 | NCC Rating (A) | 793 | 793 | 793 | 793 | 793 | Urban | 70
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 2.7968e-05 | 2.797e-05 | 2.7963e-05 | 2.7964e-05 | 2.7958e-05
|  |  |  | ECC Rating (A) | 793 | 793 | 793 | 793 | 793
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Griffin Bulk | 3330-3 | 3330 Tee1 | APM | NCC Rating (A) | 865 | 865 | 865 | 865 | 865 | Urban | 70
|  |  |  | 10 POE Load (A) | 163 | 167 | 246 | 248 | 250
|  |  |  | Power Factor | 0.99743 | 0.99721 | 0.98913 | 0.98896 | 0.98891
|  |  |  | ECC Rating (A) | 865 | 865 | 865 | 865 | 865
|  |  |  | 50 POE Load (A) | 279 | 287 | 389 | 394 | 396
Griffin Bulk | 3331-1 | 3331 Tee1 | Kallangur | NCC Rating (A) | 926 | 926 | 926 | 926 | 926 | Urban | 70
|  |  |  | 10 POE Load (A) | 128 | 132 | 124 | 116 | 118
|  |  |  | Power Factor | 0.99999 | 0.99996 | 0.99861 | 0.61968 | 0.64688
|  |  |  | ECC Rating (A) | 926 | 926 | 926 | 926 | 926
|  |  |  | 50 POE Load (A) | 244 | 251 | 238 | 259 | 261
Griffin Bulk | 3331-3 | APM | 3331 Tee1 | NCC Rating (A) | 840 | 840 | 840 | 840 | 840 | Urban | 70
|  |  |  | 10 POE Load (A) | 163 | 167 | 159 | 154 | 156
|  |  |  | Power Factor | 0.99755 | 0.99737 | 0.99396 | 0.97436 | 0.97627
|  |  |  | ECC Rating (A) | 840 | 840 | 840 | 840 | 840
|  |  |  | 50 POE Load (A) | 280 | 287 | 275 | 295 | 297
Griffin Bulk | 3359-1 | 3359 Tee1 | Hays Inlet | NCC Rating (A) | 880 | 880 | 880 | 880 | 880 | Urban | 70
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 1.5907e-06 | 1.5908e-06 | 1.5911e-06 | 1.5908e-06 | 1.5893e-06
|  |  |  | ECC Rating (A) | 880 | 880 | 880 | 880 | 880
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Griffin Bulk | 3359-2 | 3359 Tee1 | 3359 Tee2 | NCC Rating (A) | 912 | 912 | 912 | 912 | 912 | Urban | 70
|  |  |  | 10 POE Load (A) | 225 | 228 | 243 | 243 | 244
|  |  |  | Power Factor | 0.98031 | 0.98023 | 0.98149 | 0.98179 | 0.98172
|  |  |  | ECC Rating (A) | 912 | 912 | 912 | 912 | 912
|  |  |  | 50 POE Load (A) | 409 | 411 | 413 | 409 | 411
Griffin Bulk | 3359-3 | 3359 Tee2 | 3359 Tee3 | NCC Rating (A) | 912 | 912 | 912 | 912 | 912 | Urban | 70
|  |  |  | 10 POE Load (A) | 225 | 228 | 243 | 243 | 244
|  |  |  | Power Factor | 0.98041 | 0.98033 | 0.9816 | 0.9819 | 0.98183
|  |  |  | ECC Rating (A) | 912 | 912 | 912 | 912 | 912
|  |  |  | 50 POE Load (A) | 409 | 411 | 413 | 409 | 411
Griffin Bulk | 3359-4 | 3359 Tee3 | Mango Hill Bus 2 | NCC Rating (A) | 806 | 806 | 806 | 806 | 806 | Urban | 70
|  |  |  | 10 POE Load (A) | 226 | 228 | 243 | 243 | 244
|  |  |  | Power Factor | 0.98001 | 0.97997 | 0.98145 | 0.98175 | 0.98169
|  |  |  | ECC Rating (A) | 806 | 806 | 806 | 806 | 806
|  |  |  | 50 POE Load (A) | 409 | 411 | 413 | 409 | 411
Griffin Bulk | 3359-5 | 3359 Tee2 | P51001-D | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 70
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 6.7087e-06 | 6.7087e-06 | 6.7087e-06 | 6.7084e-06 | 6.7089e-06
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Griffin Bulk | 3359-6 | 3359 Tee3 | X18574-E | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 70
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 3.3931e-06 | 3.3931e-06 | 3.3931e-06 | 3.3931e-06 | 3.3931e-06
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Griffin Bulk | 3359-7 | Griffin BS | 3359 Tee1 | NCC Rating (A) | 917 | 917 | 917 | 917 | 917 | Urban | 70
|  |  |  | 10 POE Load (A) | 225 | 228 | 243 | 243 | 244
|  |  |  | Power Factor | 0.97765 | 0.97752 | 0.97863 | 0.97896 | 0.97887
|  |  |  | ECC Rating (A) | 917 | 917 | 917 | 917 | 917
|  |  |  | 50 POE Load (A) | 409 | 411 | 413 | 409 | 411
Griffin Bulk | 338-1 | Griffin BS | Strathpine | NCC Rating (A) | 348 | 348 | 348 | 348 | 348 | Urban | 70
|  |  |  | 10 POE Load (A) | 2 | 2 | 2 | 2 | 2
|  |  |  | Power Factor | 0.00011716 | 0.00011716 | 0.00011716 | 0.00011716 | 0.00011716
|  |  |  | ECC Rating (A) | 348 | 348 | 348 | 348 | 348
|  |  |  | 50 POE Load (A) | 2 | 2 | 2 | 2 | 2
Gympie Bulk | 3004-1 | Coondoo Ck Reg | Tin Can Bay | NCC Rating (A) | 246 | 246 | 246 | 246 | 246 | Rural | 170
|  |  |  | 10 POE Load (A) | 82 | 82 | 82 | 81 | 81
|  |  |  | Power Factor | 0.99218 | 0.99218 | 0.99218 | 0.99232 | 0.99232
|  |  |  | ECC Rating (A) | 246 | 246 | 246 | 246 | 246
|  |  |  | 50 POE Load (A) | 73 | 73 | 73 | 72 | 72
Gympie Bulk | 3005-1 | Coondoo Ck Reg | Tin Can Bay | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170
|  |  |  | 10 POE Load (A) | 78 | 78 | 78 | 77 | 77
|  |  |  | Power Factor | 0.99348 | 0.99348 | 0.99348 | 0.99336 | 0.99336
|  |  |  | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
|  |  |  | 50 POE Load (A) | 70 | 70 | 70 | 69 | 69
Gympie Bulk | 3009-1 | Gympie BS | Gympie Nth | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70
|  |  |  | 10 POE Load (A) | 116 | 115 | 114 | 113 | 113
|  |  |  | Power Factor | 0.99616 | 0.9962 | 0.99624 | 0.99629 | 0.99629
|  |  |  | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | 50 POE Load (A) | 218 | 218 | 216 | 215 | 215
Gympie Bulk | 3011-1 | Gympie BS | Gympie Nth | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70
|  |  |  | 10 POE Load (A) | 116 | 115 | 114 | 113 | 113
|  |  |  | Power Factor | 0.99614 | 0.99619 | 0.99623 | 0.99628 | 0.99628
|  |  |  | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | 50 POE Load (A) | 218 | 218 | 216 | 215 | 215
Gympie Bulk | 339/2-1 | Amamoor | 339 Tee1 | NCC Rating (A) | 293 | 293 | 582 | 582 | 582 | Rural | 170
|  |  |  | 10 POE Load (A) | 66 | 66 | 65 | 65 | 65
|  |  |  | Power Factor | 0.88412 | 0.88412 | 0.8971 | 0.89715 | 0.89715
|  |  |  | ECC Rating (A) | 293 | 293 | 582 | 582 | 582
|  |  |  | 50 POE Load (A) | 62 | 62 | 62 | 62 | 62
Gympie Bulk | 339/2-2 | 339 Tee1 | Imbil | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
|  |  |  | 10 POE Load (A) | 54 | 54 | 52 | 52 | 52
|  |  |  | Power Factor | 0.87704 | 0.87704 | 0.89307 | 0.8931 | 0.8931
|  |  |  | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | 50 POE Load (A) | 49 | 49 | 50 | 49 | 49
Gympie Bulk | 339/2-5 | 339 Tee2 | 340 Tee2 | NCC Rating (A) | 293 | 293 | 582 | 582 | 582 | Rural | 170
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 3.5512e-06 | 3.5512e-06 | 2.4497e-06 | 2.4497e-06 | 2.4497e-06
|  |  |  | ECC Rating (A) | 293 | 293 | 582 | 582 | 582
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Gympie Bulk | 339-1 | Gympie BS | 339 Tee1 | NCC Rating (A) | 322 | 322 | 322 | 322 | 322 | Rural | 170 | 6
|  |  |  | 10 POE Load (A) | 172 | 172 | 172 | 170 | 170
|  |  |  | Power Factor | 0.94906 | 0.94906 | 0.94912 | 0.94924 | 0.94924
|  |  |  | ECC Rating (A) | 322 | 322 | 322 | 322 | 322
|  |  |  | 50 POE Load (A) | 161 | 161 | 161 | 159 | 159
Gympie Bulk | 339-2 | 339 Tee1 | Amamoor | NCC Rating (A) | 322 | 322 | 322 | 322 | 322 | Rural | 170
|  |  |  | 10 POE Load (A) | 172 | 172 | 172 | 170 | 170
|  |  |  | Power Factor | 0.95012 | 0.95012 | 0.95018 | 0.95028 | 0.95028
|  |  |  | ECC Rating (A) | 322 | 322 | 322 | 322 | 322
|  |  |  | 50 POE Load (A) | 162 | 162 | 161 | 159 | 159
Gympie Bulk | 339-3 | 339 Tee1 | 340 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0.00059185 | 0.00059185 | 0.00059108 | 0.00059463 | 0.00059463
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Gympie Bulk | 340-1 | Gympie BS | 340 Tee1 | NCC Rating (A) | 490 | 490 | 490 | 490 | 490 | Rural | 170
|  |  |  | 10 POE Load (A) | 70 | 70 | 69 | 69 | 69
|  |  |  | Power Factor | 0.96937 | 0.96937 | 0.96162 | 0.96966 | 0.96966
|  |  |  | ECC Rating (A) | 490 | 490 | 490 | 490 | 490
|  |  |  | 50 POE Load (A) | 147 | 147 | 146 | 145 | 145
Gympie Bulk | 340-2 | 340 Tee1 | 339 Tee1 | NCC Rating (A) | 490 | 490 | 490 | 490 | 490 | Rural | 170
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0.00010591 | 0.0001058 | 0.00010579 | 0.00010587 | 0.00010587
|  |  |  | ECC Rating (A) | 490 | 490 | 490 | 490 | 490
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Gympie Bulk | 340-4 | 340 Tee1 | 340 Tee2 | NCC Rating (A) | 490 | 490 | 490 | 490 | 490 | Rural | 170
|  |  |  | 10 POE Load (A) | 70 | 70 | 69 | 69 | 69
|  |  |  | Power Factor | 0.96913 | 0.96913 | 0.96132 | 0.9694 | 0.9694
|  |  |  | ECC Rating (A) | 490 | 490 | 490 | 490 | 490
|  |  |  | 50 POE Load (A) | 147 | 147 | 146 | 145 | 145
Gympie Bulk | 340-5 | 340 Tee2 | 340 Tee3 | NCC Rating (A) | 401 | 401 | 401 | 401 | 401 | Rural | 170
|  |  |  | 10 POE Load (A) | 3 | 3 | 3 | 3 | 3
|  |  |  | Power Factor | 0.00072412 | 0.00072412 | 0.00072412 | 0.00072412 | 0.00072412
|  |  |  | ECC Rating (A) | 401 | 401 | 401 | 401 | 401
|  |  |  | 50 POE Load (A) | 3 | 3 | 3 | 3 | 3
Gympie Bulk | 340-6 | 340 Tee3 | 339 Tee2 | NCC Rating (A) | 412 | 412 | 412 | 412 | 412 | Rural | 170
|  |  |  | 10 POE Load (A) | 2 | 2 | 2 | 2 | 2
|  |  |  | Power Factor | 0.00013902 | 0.00013902 | 0.00013902 | 0.00013902 | 0.00013902
|  |  |  | ECC Rating (A) | 412 | 412 | 412 | 412 | 412
|  |  |  | 50 POE Load (A) | 2 | 2 | 2 | 2 | 2
Gympie Bulk | 340-7 | 339 Tee2 | Kenilworth | NCC Rating (A) | 416 | 416 | 416 | 416 | 416 | Rural | 170
|  |  |  | 10 POE Load (A) | 2 | 2 | 2 | 2 | 2
|  |  |  | Power Factor | 0.00013861 | 0.00013861 | 0.00013861 | 0.00013861 | 0.00013861
|  |  |  | ECC Rating (A) | 416 | 416 | 416 | 416 | 416
|  |  |  | 50 POE Load (A) | 2 | 2 | 2 | 2 | 2
Gympie Bulk | 340-8 | 340 Tee3 | Black Mountain | NCC Rating (A) | 401 | 401 | 401 | 401 | 401 | Rural | 170
|  |  |  | 10 POE Load (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 1.7204e-05 | 1.7204e-05 | 1.7204e-05 | 1.7204e-05 | 1.7204e-05
|  |  |  | ECC Rating (A) | 401 | 401 | 401 | 401 | 401
|  |  |  | 50 POE Load (A) | 1 | 1 | 1 | 1 | 1
Gympie Bulk | 340-9 | 340 Tee2 | Gympie South | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170
|  |  |  | 10 POE Load (A) | 71 | 71 | 70 | 70 | 70
|  |  |  | Power Factor | 0.95659 | 0.95659 | 0.94742 | 0.95675 | 0.95675
|  |  |  | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
|  |  |  | 50 POE Load (A) | 148 | 148 | 147 | 146 | 146
Gympie Bulk | 341-1 | Gympie BS | 341 Tee1 | NCC Rating (A) | 455 | 455 | 455 | 455 | 455 | Rural | 170 | 6
|  |  |  | 10 POE Load (A) | 241 | 241 | 241 | 239 | 239
|  |  |  | Power Factor | 0.98524 | 0.98524 | 0.98524 | 0.98536 | 0.98536
|  |  |  | ECC Rating (A) | 455 | 455 | 455 | 455 | 455
|  |  |  | 50 POE Load (A) | 229 | 229 | 229 | 228 | 228
Gympie Bulk | 341-3 | 341 Tee1 | Coondoo Ck Reg | NCC Rating (A) | 292 | 292 | 292 | 292 | 292 | Rural | 170
|  |  |  | 10 POE Load (A) | 168 | 168 | 168 | 165 | 165
|  |  |  | Power Factor | 0.99149 | 0.99149 | 0.99149 | 0.99156 | 0.99156
|  |  |  | ECC Rating (A) | 292 | 292 | 292 | 292 | 292
|  |  |  | 50 POE Load (A) | 150 | 150 | 150 | 147 | 147
Gympie Bulk | 341-4 | Coondoo Ck Reg | 341 Tee2 | NCC Rating (A) | 926 | 926 | 926 | 926 | 926 | Rural | 170
|  |  |  | 10 POE Load (A) | 160 | 160 | 160 | 157 | 157
|  |  |  | Power Factor | 0.99179 | 0.99179 | 0.99179 | 0.99185 | 0.99185
|  |  |  | ECC Rating (A) | 926 | 926 | 926 | 926 | 926
|  |  |  | 50 POE Load (A) | 143 | 143 | 143 | 140 | 140
Gympie Bulk | 351-1 | Gympie BS | Gympie Sth | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Rural | 170
|  |  |  | 10 POE Load (A) | 80 | 80 | 79 | 79 | 79
|  |  |  | Power Factor | 0.96488 | 0.96488 | 0.95663 | 0.96518 | 0.96518
|  |  |  | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
|  |  |  | 50 POE Load (A) | 148 | 148 | 146 | 146 | 146
Gympie Bulk | 429-1 | Gympie BS | 429 Tee1 | NCC Rating (A) | 786 | 786 | 786 | 786 | 786 | Rural | 170
|  |  |  | 10 POE Load (A) | 329 | 329 | 329 | 326 | 326
|  |  |  | Power Factor | 0.9263 | 0.9263 | 0.9263 | 0.92641 | 0.92641
|  |  |  | ECC Rating (A) | 786 | 786 | 786 | 786 | 786
|  |  |  | 50 POE Load (A) | 398 | 398 | 398 | 398 | 398
Gympie Bulk | 429-2 | 429 Tee1 | Goomboorian | NCC Rating (A) | 492 | 492 | 492 | 492 | 492 | Rural | 170
|  |  |  | 10 POE Load (A) | 49 | 49 | 49 | 47 | 47
|  |  |  | Power Factor | 0.99542 | 0.99542 | 0.99542 | 0.99552 | 0.99552
|  |  |  | ECC Rating (A) | 492 | 492 | 492 | 492 | 492
|  |  |  | 50 POE Load (A) | 46 | 46 | 46 | 46 | 46
Hays Inlet Bulk | 305-1 | Hays Inlet BS | Deception Bay | NCC Rating (A) | 759 | 759 | 759 | 759 | 759 | Urban | 430
|  |  |  | 10 POE Load (A) | 564 | 569 | 571 | 574 | 583
|  |  |  | Power Factor | 0.99165 | 0.99145 | 0.99133 | 0.99118 | 0.99078
|  |  |  | ECC Rating (A) | 759 | 759 | 759 | 759 | 759
|  |  |  | 50 POE Load (A) | 828 | 837 | 843 | 850 | 868
Hays Inlet Bulk | 311-1 | Hays Inlet BS | Deception Bay | NCC Rating (A) | 681 | 681 | 681 | 681 | 681 | Urban | 210 | 3
|  |  |  | 10 POE Load (A) | 187 | 188 | 189 | 190 | 193
|  |  |  | Power Factor | 0.99665 | 0.99652 | 0.99645 | 0.99635 | 0.99609
|  |  |  | ECC Rating (A) | 681 | 681 | 681 | 681 | 681
|  |  |  | 50 POE Load (A) | 589 | 594 | 597 | 600 | 610
Hays Inlet Bulk | 3250-1 | Deception Bay | Burpengary | NCC Rating (A) | 849 | 849 | 849 | 849 | 849 | Urban | 430
|  |  |  | 10 POE Load (A) | 349 | 355 | 358 | 363 | 372
|  |  |  | Power Factor | 0.99192 | 0.99163 | 0.99146 | 0.9912 | 0.99072
|  |  |  | ECC Rating (A) | 849 | 849 | 849 | 849 | 849
|  |  |  | 50 POE Load (A) | 724 | 734 | 742 | 754 | 775
Hays Inlet Bulk | 325-1 | Hays Inlet BS | Scarborough | NCC Rating (A) | 734 | 734 | 734 | 734 | 734 | Urban | 70
|  |  |  | 10 POE Load (A) | 286 | 287 | 287 | 298 | 312
|  |  |  | Power Factor | 0.99594 | 0.99592 | 0.99593 | 0.99566 | 0.99528
|  |  |  | ECC Rating (A) | 734 | 734 | 734 | 734 | 734
|  |  |  | 50 POE Load (A) | 376 | 378 | 377 | 394 | 416
Hays Inlet Bulk | 3251-1 | Burpengary | Morayfield | NCC Rating (A) | 508 | 508 | 508 | 508 | 508 | Urban | 120 | 2
|  |  |  | 10 POE Load (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 1.0517e-05 | 1.0517e-05 | 1.0517e-05 | 1.0516e-05 | 1.0517e-05
|  |  |  | ECC Rating (A) | 508 | 508 | 508 | 508 | 508
|  |  |  | 50 POE Load (A) | 456 | 458 | 464 | 472 | 483
Hays Inlet Bulk | 326-1 | Redcliffe | Scarborough | NCC Rating (A) | 688 | 688 | 688 | 688 | 688 | Urban | 70
|  |  |  | 10 POE Load (A) | 59 | 58 | 58 | 49 | 41
|  |  |  | Power Factor | 0.96779 | 0.96757 | 0.9676 | 0.96316 | 0.958
|  |  |  | ECC Rating (A) | 688 | 688 | 688 | 688 | 688
|  |  |  | 50 POE Load (A) | 320 | 322 | 320 | 322 | 328
Hays Inlet Bulk | 327-1 | Hays Inlet BS | Mango Hill Bus 1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
|  |  |  | 10 POE Load (A) | 288 | 293 | 297 | 297 | 301
|  |  |  | Power Factor | 0.97444 | 0.97304 | 0.97261 | 0.97261 | 0.97218
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 257 | 262 | 264 | 266 | 269
Hays Inlet Bulk | 329-1 | Redcliffe | Duffield Rd | NCC Rating (A) | 864 | 864 | 864 | 864 | 864 | Urban | 70
|  |  |  | 10 POE Load (A) | 93 | 93 | 94 | 108 | 122
|  |  |  | Power Factor | 0.9932 | 0.99322 | 0.99313 | 0.99147 | 0.98974
|  |  |  | ECC Rating (A) | 864 | 864 | 864 | 864 | 864
|  |  |  | 50 POE Load (A) | 227 | 228 | 227 | 250 | 274
Hays Inlet Bulk | 330-1 | Hays Inlet BS | Duffield Rd | NCC Rating (A) | 595 | 595 | 595 | 595 | 595 | Urban | 70
|  |  |  | 10 POE Load (A) | 244 | 245 | 244 | 251 | 261
|  |  |  | Power Factor | 0.99191 | 0.99187 | 0.9919 | 0.99159 | 0.99113
|  |  |  | ECC Rating (A) | 595 | 595 | 595 | 595 | 595
|  |  |  | 50 POE Load (A) | 364 | 365 | 365 | 375 | 390
Hays Inlet Bulk | 331-1 | Hays Inlet BS | Duffield Rd | NCC Rating (A) | 595 | 595 | 595 | 595 | 595 | Urban | 70
|  |  |  | 10 POE Load (A) | 245 | 246 | 246 | 253 | 262
|  |  |  | Power Factor | 0.9897 | 0.98965 | 0.98968 | 0.98933 | 0.98881
|  |  |  | ECC Rating (A) | 595 | 595 | 595 | 595 | 595
|  |  |  | 50 POE Load (A) | 364 | 366 | 366 | 376 | 391
Hays Inlet Bulk | 332-1 | Hays Inlet BS | Redcliffe | NCC Rating (A) | 677 | 677 | 677 | 677 | 677 | Urban | 70
|  |  |  | 10 POE Load (A) | 259 | 260 | 260 | 274 | 290
|  |  |  | Power Factor | 0.98248 | 0.98241 | 0.98244 | 0.98155 | 0.98038
|  |  |  | ECC Rating (A) | 677 | 677 | 677 | 677 | 677
|  |  |  | 50 POE Load (A) | 380 | 382 | 381 | 400 | 424
Hays Inlet Bulk | 451-1 | Narangba | Burpengary | NCC Rating (A) | 489 | 489 | 489 | 489 | 489 | Urban | 385
|  |  |  | 10 POE Load (A) | 11 | 11 | 11 | 12 | 13
|  |  |  | Power Factor | 0.52167 | 0.33991 | 0.20801 | 0.060125 | 0.30683
|  |  |  | ECC Rating (A) | 489 | 489 | 489 | 489 | 489
|  |  |  | 50 POE Load (A) | 384 | 392 | 398 | 408 | 422
Hays Inlet Bulk | 497-1 | Hays Inlet BS | Narangba | NCC Rating (A) | 720 | 720 | 720 | 720 | 720 | Urban | 385
|  |  |  | 10 POE Load (A) | 406 | 413 | 417 | 423 | 434
|  |  |  | Power Factor | 0.99007 | 0.98978 | 0.98961 | 0.98932 | 0.98883
|  |  |  | ECC Rating (A) | 720 | 720 | 720 | 720 | 720
|  |  |  | 50 POE Load (A) | 718 | 728 | 736 | 748 | 768
Jimboomba Bulk | 470-1 | Jimboomba BS | Logan Village | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Rural | 170
|  |  |  | 10 POE Load (A) | 305 | 315 | 324 | 328 | 336
|  |  |  | Power Factor | 0.97985 | 0.97892 | 0.97796 | 0.97756 | 0.97676
|  |  |  | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
|  |  |  | 50 POE Load (A) | 286 | 296 | 303 | 309 | 315
Jimboomba Bulk | 479-1 | Jimboomba BS | Nth Maclean | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 551 | 559 | 563 | 581 | 602
|  |  |  | Power Factor | 0.98025 | 0.97764 | 0.9774 | 0.9738 | 0.97335
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 495 | 502 | 505 | 521 | 539
Lockrose Bulk | 378-1 | Lockrose BS | 378 Tee1 | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
|  |  |  | 10 POE Load (A) | 116 | 139 | 138 | 138 | 139
|  |  |  | Power Factor | 0.97662 | 0.97063 | 0.97059 | 0.97055 | 0.97025
|  |  |  | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | 50 POE Load (A) | 192 | 244 | 243 | 241 | 243
Lockrose Bulk | 378-2 | 378 Tee1 | Glenmore Grove | NCC Rating (A) | 473 | 473 | 473 | 473 | 473 | Rural | 170
|  |  |  | 10 POE Load (A) | 35 | 35 | 34 | 34 | 33
|  |  |  | Power Factor | 0.98988 | 0.9899 | 0.98995 | 0.98999 | 0.99003
|  |  |  | ECC Rating (A) | 473 | 473 | 473 | 473 | 473
|  |  |  | 50 POE Load (A) | 33 | 32 | 32 | 31 | 31
Lockrose Bulk | 378-3 | 378 Tee1 | 378 Tee2 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 82 | 105 | 105 | 105 | 106
|  |  |  | Power Factor | 0.97218 | 0.96599 | 0.96599 | 0.96599 | 0.96573
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 160 | 212 | 212 | 210 | 212
Lockrose Bulk | 378-4 | 378 Tee2 | 532 Tee1 | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
|  |  |  | 10 POE Load (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 6.0726e-05 | 6.0726e-05 | 6.0726e-05 | 6.0726e-05 | 6.0726e-05
|  |  |  | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | 50 POE Load (A) | 1 | 1 | 1 | 1 | 1
Lockrose Bulk | 378-5 | 378 Tee2 | Laidley | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 82 | 105 | 105 | 105 | 106
|  |  |  | Power Factor | 0.97159 | 0.96823 | 0.96823 | 0.96824 | 0.96808
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 160 | 212 | 212 | 210 | 212
Lockrose Bulk | 380-1 | Murrumba | 380 Tee1 | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
|  |  |  | 10 POE Load (A) | 38 | 38 | 39 | 34 | 34
|  |  |  | Power Factor | 0.99055 | 0.99055 | 0.99008 | 0.99826 | 0.99826
|  |  |  | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | 50 POE Load (A) | 112 | 112 | 112 | 111 | 115
Lockrose Bulk | 380-2 | 380 Tee1 | Somerset Dam | NCC Rating (A) | 324 | 324 | 324 | 324 | 324 | Rural | 170
|  |  |  | 10 POE Load (A) | 7 | 7 | 7 | 7 | 7
|  |  |  | Power Factor | 0.99901 | 0.99901 | 0.99901 | 0.99901 | 0.99901
|  |  |  | ECC Rating (A) | 324 | 324 | 324 | 324 | 324
|  |  |  | 50 POE Load (A) | 6 | 6 | 6 | 5 | 7
Lockrose Bulk | 380-3 | 380 Tee1 | Toogoolahwah | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
|  |  |  | 10 POE Load (A) | 31 | 31 | 32 | 27 | 27
|  |  |  | Power Factor | 0.98154 | 0.98154 | 0.98116 | 0.99819 | 0.99819
|  |  |  | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | 50 POE Load (A) | 107 | 107 | 107 | 106 | 108
Lockrose Bulk | 381-1 | Lockrose BS | 381 Tee1 | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
|  |  |  | 10 POE Load (A) | 123 | 123 | 124 | 124 | 124
|  |  |  | Power Factor | 0.98022 | 0.97939 | 0.97916 | 0.98015 | 0.9796
|  |  |  | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | 50 POE Load (A) | 229 | 229 | 231 | 231 | 235
Lockrose Bulk | 381-2 | 381 Tee1 | 382 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 3.3483e-05 | 3.3485e-05 | 3.3475e-05 | 3.3474e-05 | 3.3481e-05
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lockrose Bulk | 381-3 | 381 Tee1 | 381 Tee2 | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
|  |  |  | 10 POE Load (A) | 123 | 123 | 124 | 124 | 124
|  |  |  | Power Factor | 0.98211 | 0.9813 | 0.9811 | 0.98205 | 0.98151
|  |  |  | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | 50 POE Load (A) | 229 | 229 | 232 | 231 | 236
Lockrose Bulk | 381-4 | 381 Tee2 | 383 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 3.3873e-05 | 3.3866e-05 | 3.3866e-05 | 3.3872e-05 | 3.3867e-05
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lockrose Bulk | 381-5 | 381 Tee2 | 381 Tee3 | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
|  |  |  | 10 POE Load (A) | 123 | 124 | 124 | 124 | 124
|  |  |  | Power Factor | 0.98252 | 0.98172 | 0.98153 | 0.98247 | 0.98194
|  |  |  | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | 50 POE Load (A) | 229 | 229 | 232 | 231 | 236
Lockrose Bulk | 381-6 | 381 Tee3 | Coominya TR2 | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170
|  |  |  | 10 POE Load (A) | 40 | 40 | 40 | 40 | 40
|  |  |  | Power Factor | 0.99109 | 0.98978 | 0.98978 | 0.99108 | 0.98978
|  |  |  | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
|  |  |  | 50 POE Load (A) | 39 | 39 | 39 | 39 | 39
Lockrose Bulk | 381-7 | 381 Tee3 | 381 Tee4 | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
|  |  |  | 10 POE Load (A) | 83 | 83 | 84 | 84 | 84
|  |  |  | Power Factor | 0.98271 | 0.98237 | 0.98217 | 0.9827 | 0.98275
|  |  |  | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | 50 POE Load (A) | 190 | 190 | 193 | 192 | 197
Lockrose Bulk | 381-8 | 381 Tee4 | Coominya TR1 | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170
|  |  |  | 10 POE Load (A) | 40 | 40 | 40 | 40 | 40
|  |  |  | Power Factor | 0.99059 | 0.98925 | 0.98925 | 0.99059 | 0.99016
|  |  |  | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
|  |  |  | 50 POE Load (A) | 39 | 39 | 39 | 39 | 39
Lockrose Bulk | 381-9 | 381 Tee4 | Paddys Gully | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
|  |  |  | 10 POE Load (A) | 43 | 43 | 44 | 44 | 44
|  |  |  | Power Factor | 0.97166 | 0.95858 | 0.97273 | 0.97189 | 0.95824
|  |  |  | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | 50 POE Load (A) | 152 | 147 | 154 | 153 | 151
Lockrose Bulk | 382-1 | Lockrose BS | 382 Tee1 | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
|  |  |  | 10 POE Load (A) | 106 | 106 | 107 | 107 | 107
|  |  |  | Power Factor | 0.98488 | 0.98451 | 0.98426 | 0.98481 | 0.98457
|  |  |  | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | 50 POE Load (A) | 145 | 145 | 147 | 146 | 150
Lockrose Bulk | 382-2 | 382 Tee1 | 381 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 1.9424e-05 | 1.9423e-05 | 1.9423e-05 | 1.9425e-05 | 1.9424e-05
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lockrose Bulk | 382-3 | 382 Tee1 | Paddys Gully | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
|  |  |  | 10 POE Load (A) | 106 | 106 | 107 | 107 | 107
|  |  |  | Power Factor | 0.98994 | 0.98962 | 0.98951 | 0.98995 | 0.98974
|  |  |  | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | 50 POE Load (A) | 145 | 145 | 147 | 147 | 151
Lockrose Bulk | 3828-1 | Paddy's Gully | Esk | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
|  |  |  | 10 POE Load (A) | 73 | 73 | 73 | 78 | 78
|  |  |  | Power Factor | 0.99345 | 0.99344 | 0.99334 | 0.98079 | 0.98079
|  |  |  | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | 50 POE Load (A) | 140 | 140 | 142 | 138 | 142
Lockrose Bulk | 3829-1 | Paddy's Gully | Murrumba | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170 | 2
|  |  |  | 10 POE Load (A) | 68 | 68 | 69 | 64 | 64
|  |  |  | Power Factor | 0.9729 | 0.9729 | 0.97273 | 0.98996 | 0.98996
|  |  |  | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | 50 POE Load (A) | 141 | 141 | 143 | 142 | 146
Lockrose Bulk | 3831-1 | Lockrose BS | Tarampa | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Rural | 170
|  |  |  | 10 POE Load (A) | 108 | 108 | 108 | 108 | 108
|  |  |  | Power Factor | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 0.98311
|  |  |  | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
|  |  |  | 50 POE Load (A) | 100 | 100 | 100 | 100 | 100
Lockrose Bulk | 3832-1 | Tarampa | 3832 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 3.7174e-05 | 3.718e-05 | 3.7174e-05 | 3.7179e-05 | 3.7179e-05
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lockrose Bulk | 3832-3 | 3832 Tee1 | Lowood | NCC Rating (A) | 434 | 434 | 434 | 434 | 434 | Rural | 170
|  |  |  | 10 POE Load (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 5.5523e-06 | 5.5524e-06 | 5.5524e-06 | 5.5523e-06 | 5.5523e-06
|  |  |  | ECC Rating (A) | 434 | 434 | 434 | 434 | 434
|  |  |  | 50 POE Load (A) | 1 | 1 | 1 | 1 | 1
Lockrose Bulk | 3840-1 | Esk | Toogoolawah | NCC Rating (A) | 293 | 293 | 293 | 884 | 884 | Rural | 170
|  |  |  | 10 POE Load (A) | 32 | 32 | 33 | 38 | 38
|  |  |  | Power Factor | 0.98582 | 0.98582 | 0.98597 | 0.95298 | 0.95298
|  |  |  | ECC Rating (A) | 293 | 293 | 293 | 884 | 884
|  |  |  | 50 POE Load (A) | 101 | 101 | 103 | 99 | 103
Lockrose Bulk | 384-1 | Lockrose BS | 384 Tee1 | NCC Rating (A) | 451 | 451 | 451 | 451 | 451 | Rural | 170
|  |  |  | 10 POE Load (A) | 121 | 144 | 144 | 144 | 144
|  |  |  | Power Factor | 0.99341 | 0.9911 | 0.99113 | 0.99116 | 0.99107
|  |  |  | ECC Rating (A) | 451 | 451 | 451 | 451 | 451
|  |  |  | 50 POE Load (A) | 193 | 246 | 246 | 243 | 245
Lockrose Bulk | 384-2 | 384 Tee1 | Glenmore Grove | NCC Rating (A) | 689 | 689 | 689 | 689 | 689 | Rural | 170
|  |  |  | 10 POE Load (A) | 35 | 34 | 34 | 34 | 33
|  |  |  | Power Factor | 0.99004 | 0.99007 | 0.99011 | 0.99015 | 0.99019
|  |  |  | ECC Rating (A) | 689 | 689 | 689 | 689 | 689
|  |  |  | 50 POE Load (A) | 32 | 32 | 32 | 31 | 31
Lockrose Bulk | 384-3 | 384 Tee1 | Laidley1 | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Rural | 170
|  |  |  | 10 POE Load (A) | 86 | 110 | 110 | 110 | 111
|  |  |  | Power Factor | 0.99682 | 0.99544 | 0.99544 | 0.99544 | 0.99538
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | 50 POE Load (A) | 161 | 214 | 214 | 212 | 214
Lockrose Bulk | 3870-1 | Lockrose BS | Lowood | NCC Rating (A) | 898 | 898 | 898 | 898 | 898 | Rural | 170
|  |  |  | 10 POE Load (A) | 122 | 122 | 122 | 124 | 124
|  |  |  | Power Factor | 0.99097 | 0.99097 | 0.99097 | 0.99088 | 0.99088
|  |  |  | ECC Rating (A) | 898 | 898 | 898 | 898 | 898
|  |  |  | 50 POE Load (A) | 115 | 115 | 115 | 117 | 117
Lockrose Bulk | 3871-1 | Lowood | Wivenhoe | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
|  |  |  | 10 POE Load (A) | 86 | 86 | 86 | 88 | 88
|  |  |  | Power Factor | 0.99146 | 0.98614 | 0.98614 | 0.99134 | 0.99134
|  |  |  | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | 50 POE Load (A) | 82 | 82 | 82 | 84 | 84
Loganlea Bulk | 407-1 | Loganlea BS | Woodridge | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
|  |  |  | 10 POE Load (A) | 280 | 281 | 280 | 279 | 281
|  |  |  | Power Factor | 0.98244 | 0.98237 | 0.98244 | 0.98251 | 0.98237
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 476 | 478 | 476 | 474 | 478
Loganlea Bulk | 408-1 | Loganlea BS | Kingston | NCC Rating (A) | 724 | 724 | 724 | 724 | 724 | Urban | 280
|  |  |  | 10 POE Load (A) | 341 | 337 | 338 | 341 | 345
|  |  |  | Power Factor | 0.9799 | 0.98027 | 0.98018 | 0.9799 | 0.97953
|  |  |  | ECC Rating (A) | 724 | 724 | 724 | 724 | 724
|  |  |  | 50 POE Load (A) | 552 | 545 | 546 | 550 | 557
Loganlea Bulk | 409-1 | Loganlea BS | Woodridge | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
|  |  |  | 10 POE Load (A) | 250 | 251 | 250 | 249 | 251
|  |  |  | Power Factor | 0.98499 | 0.98492 | 0.98499 | 0.98505 | 0.98492
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 478 | 480 | 478 | 476 | 480
Loganlea Bulk | 418-1 | Loganlea BS | Tanah Merah | NCC Rating (A) | 692 | 692 | 692 | 692 | 692 | Urban | 70
|  |  |  | 10 POE Load (A) | 250 | 250 | 250 | 249 | 249
|  |  |  | Power Factor | 0.99807 | 0.99807 | 0.99807 | 0.9981 | 0.9981
|  |  |  | ECC Rating (A) | 692 | 692 | 692 | 692 | 692
|  |  |  | 50 POE Load (A) | 236 | 236 | 235 | 235 | 235
Loganlea Bulk | 452-1 | Loganlea BS | Kingston | NCC Rating (A) | 567 | 567 | 567 | 567 | 567 | Urban | 280
|  |  |  | 10 POE Load (A) | 277 | 273 | 274 | 277 | 280
|  |  |  | Power Factor | 0.98455 | 0.98486 | 0.98478 | 0.98455 | 0.98424
|  |  |  | ECC Rating (A) | 567 | 567 | 567 | 567 | 567
|  |  |  | 50 POE Load (A) | 555 | 547 | 549 | 553 | 560
Lytton Bulk | 3302-1 | Lytton BS | Fisherman Is B | NCC Rating (A) | 690 | 690 | 690 | 690 | 690 | Urban | 70
|  |  |  | 10 POE Load (A) | 265 | 279 | 306 | 320 | 320
|  |  |  | Power Factor | 0.93394 | 0.93495 | 0.93538 | 0.93531 | 0.93531
|  |  |  | ECC Rating (A) | 690 | 690 | 690 | 690 | 690
|  |  |  | 50 POE Load (A) | 527 | 556 | 611 | 639 | 639
Lytton Bulk | 3303-1 | Lytton BS | Fisherman Is B | NCC Rating (A) | 650 | 650 | 650 | 650 | 650 | Urban | 70 | 18.5
|  |  |  | 10 POE Load (A) | 264 | 278 | 306 | 319 | 319
|  |  |  | Power Factor | 0.9339 | 0.93491 | 0.93534 | 0.93527 | 0.93527
|  |  |  | ECC Rating (A) | 650 | 650 | 650 | 650 | 650
|  |  |  | 50 POE Load (A) | 527 | 556 | 611 | 639 | 639
Lytton Bulk | 490-1 | Lytton BS | Gibson Island | NCC Rating (A) | 664 | 664 | 664 | 664 | 664 | HighSec | 0
|  |  |  | 10 POE Load (A) | 176 | 176 | 176 | 174 | 174
|  |  |  | Power Factor | 0.96905 | 0.96894 | 0.96905 | 0.97146 | 0.97146
|  |  |  | ECC Rating (A) | 664 | 664 | 664 | 664 | 664
|  |  |  | 50 POE Load (A) | 342 | 342 | 340 | 338 | 338
Lytton Bulk | 491-1 | Lytton BS | Lytton | NCC Rating (A) | 511 | 511 | 511 | 511 | 511 | HighSec | 140 | 4.5
|  |  |  | 10 POE Load (A) | 229 | 259 | 258 | 257 | 258
|  |  |  | Power Factor | 0.98888 | 0.99978 | 0.99978 | 0.98255 | 0.9825
|  |  |  | ECC Rating (A) | 511 | 511 | 511 | 511 | 511
|  |  |  | 50 POE Load (A) | 455 | 515 | 511 | 511 | 511
Lytton Bulk | 492-1 | Lytton BS | Gibson Island | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | HighSec | 0
|  |  |  | 10 POE Load (A) | 168 | 169 | 168 | 167 | 167
|  |  |  | Power Factor | 0.99201 | 0.99196 | 0.99201 | 0.99321 | 0.99321
|  |  |  | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
|  |  |  | 50 POE Load (A) | 342 | 342 | 340 | 338 | 338
Lytton Bulk | 493-1 | Lytton BS | Lytton | NCC Rating (A) | 573 | 573 | 573 | 573 | 573 | HighSec | 140 | 24.5
|  |  |  | 10 POE Load (A) | 230 | 260 | 259 | 258 | 258
|  |  |  | Power Factor | 0.95272 | 0.98592 | 0.98598 | 0.94026 | 0.94015
|  |  |  | ECC Rating (A) | 573 | 573 | 573 | 573 | 573
|  |  |  | 50 POE Load (A) | 455 | 514 | 510 | 510 | 510
Lytton Bulk | 494-1 | Fisherman Is B | Fishermans Is | NCC Rating (A) | 546 | 546 | 546 | 546 | 546 | Urban | 70
|  |  |  | 10 POE Load (A) | 141 | 154 | 181 | 194 | 194
|  |  |  | Power Factor | 0.98967 | 0.98892 | 0.98686 | 0.98581 | 0.98581
|  |  |  | ECC Rating (A) | 546 | 546 | 546 | 546 | 546
|  |  |  | 50 POE Load (A) | 278 | 305 | 359 | 386 | 386
Lytton Bulk | 495-1 | Fisherman Is B | Fisherman Is | NCC Rating (A) | 600 | 600 | 600 | 600 | 600 | Urban | 70
|  |  |  | 10 POE Load (A) | 143 | 157 | 184 | 198 | 198
|  |  |  | Power Factor | 0.94136 | 0.93928 | 0.93414 | 0.93163 | 0.93163
|  |  |  | ECC Rating (A) | 600 | 600 | 600 | 600 | 600
|  |  |  | 50 POE Load (A) | 277 | 304 | 358 | 384 | 384
Lytton Bulk | 560-1 | Lytton BS | 560 Tee1 | NCC Rating (A) | 527 | 527 | 527 | 527 | 527 | Urban | 70
|  |  |  | 10 POE Load (A) | 143 | 144 | 144 | 143 | 144
|  |  |  | Power Factor | 0.99764 | 0.99759 | 0.99759 | 0.99764 | 0.99759
|  |  |  | ECC Rating (A) | 527 | 527 | 527 | 527 | 527
|  |  |  | 50 POE Load (A) | 422 | 423 | 423 | 422 | 423
Lytton Bulk | 560-2 | 560 Tee1 | Tingalpa | NCC Rating (A) | 600 | 600 | 600 | 600 | 600 | Urban | 70
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 1.9412e-06 | 1.9412e-06 | 1.9412e-06 | 1.9407e-06 | 1.9412e-06
|  |  |  | ECC Rating (A) | 600 | 600 | 600 | 600 | 600
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lytton Bulk | 560-3 | 560 Tee1 | 560 Tee2 | NCC Rating (A) | 600 | 600 | 600 | 600 | 600 | Urban | 70
|  |  |  | 10 POE Load (A) | 143 | 144 | 144 | 143 | 144
|  |  |  | Power Factor | 0.99824 | 0.99821 | 0.99821 | 0.99824 | 0.99821
|  |  |  | ECC Rating (A) | 600 | 600 | 600 | 600 | 600
|  |  |  | 50 POE Load (A) | 422 | 424 | 424 | 422 | 424
Lytton Bulk | 560-5 | Lota | 560 Tee2 | NCC Rating (A) | 775 | 775 | 775 | 775 | 775 | Urban | 70
|  |  |  | 10 POE Load (A) | 84 | 85 | 85 | 84 | 85
|  |  |  | Power Factor | 0.99834 | 0.99831 | 0.99831 | 0.99834 | 0.99831
|  |  |  | ECC Rating (A) | 775 | 775 | 775 | 775 | 775
|  |  |  | 50 POE Load (A) | 248 | 249 | 249 | 248 | 249
Lytton Bulk | 569-1 | Lytton BS | Lota | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Urban | 70
|  |  |  | 10 POE Load (A) | 296 | 297 | 297 | 296 | 297
|  |  |  | Power Factor | 0.98253 | 0.98241 | 0.98241 | 0.98253 | 0.98241
|  |  |  | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
|  |  |  | 50 POE Load (A) | 409 | 410 | 410 | 409 | 410
Lytton Bulk | 599-1 | Hemmant | Lindum | NCC Rating (A) | 630 | 630 | 630 | 630 | 630 | Urban | 70
|  |  |  | 10 POE Load (A) | 2 | 2 | 2 | 2 | 2
|  |  |  | Power Factor | 2.5274e-05 | 2.5275e-05 | 2.5274e-05 | 2.5275e-05 | 2.5274e-05
|  |  |  | ECC Rating (A) | 630 | 630 | 630 | 630 | 630
|  |  |  | 50 POE Load (A) | 2 | 2 | 2 | 2 | 2
Lytton Bulk | 681-1 | Lindum | Wynnum | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70
|  |  |  | 10 POE Load (A) | 188 | 189 | 189 | 189 | 190
|  |  |  | Power Factor | 0.98669 | 0.98662 | 0.98662 | 0.98662 | 0.98655
|  |  |  | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | 50 POE Load (A) | 343 | 345 | 345 | 343 | 346
Lytton Bulk | 682-1 | Lindum | Wynnum | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70
|  |  |  | 10 POE Load (A) | 180 | 181 | 181 | 181 | 182
|  |  |  | Power Factor | 0.98643 | 0.98637 | 0.98637 | 0.98637 | 0.9863
|  |  |  | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | 50 POE Load (A) | 343 | 345 | 345 | 343 | 347
Lytton Bulk | 687-1 | Lytton BS | 687 Tee1 | NCC Rating (A) | 759 | 759 | 759 | 759 | 759 | Urban | 70
|  |  |  | 10 POE Load (A) | 134 | 134 | 134 | 134 | 135
|  |  |  | Power Factor | 0.99897 | 0.99894 | 0.99894 | 0.99894 | 0.99891
|  |  |  | ECC Rating (A) | 759 | 759 | 759 | 759 | 759
|  |  |  | 50 POE Load (A) | 335 | 337 | 337 | 335 | 339
Lytton Bulk | 687-2 | 687 Tee1 | Lytton | NCC Rating (A) | 517 | 517 | 517 | 517 | 517 | Urban | 70
|  |  |  | 10 POE Load (A) | 2 | 2 | 2 | 2 | 2
|  |  |  | Power Factor | 1.3253e-06 | 1.3249e-06 | 1.3251e-06 | 1.3249e-06 | 1.3251e-06
|  |  |  | ECC Rating (A) | 517 | 517 | 517 | 517 | 517
|  |  |  | 50 POE Load (A) | 2 | 2 | 2 | 2 | 2
Lytton Bulk | 687-3 | 687 Tee1 | Lindum | NCC Rating (A) | 636 | 636 | 636 | 636 | 636 | Urban | 70
|  |  |  | 10 POE Load (A) | 134 | 135 | 135 | 135 | 135
|  |  |  | Power Factor | 0.99812 | 0.99808 | 0.99808 | 0.99808 | 0.99805
|  |  |  | ECC Rating (A) | 636 | 636 | 636 | 636 | 636
|  |  |  | 50 POE Load (A) | 335 | 337 | 337 | 335 | 339
Lytton Bulk | 688-1 | Lytton BS | Lindum | NCC Rating (A) | 636 | 636 | 636 | 636 | 636 | Urban | 70
|  |  |  | 10 POE Load (A) | 233 | 234 | 234 | 234 | 235
|  |  |  | Power Factor | 0.98453 | 0.98442 | 0.98442 | 0.98442 | 0.98432
|  |  |  | ECC Rating (A) | 636 | 636 | 636 | 636 | 636
|  |  |  | 50 POE Load (A) | 335 | 337 | 337 | 335 | 338
Meeandah Bulk | 3374-1 | Whinstanes | Hamilton Lands | NCC Rating (A) | 546 | 546 | 546 | 546 | 546 | Urban | 70
|  |  |  | 10 POE Load (A) | 41 | 40 | 39 | 37 | 36
|  |  |  | Power Factor | 0.93324 | 0.93318 | 0.9334 | 0.93377 | 0.94584
|  |  |  | ECC Rating (A) | 546 | 546 | 546 | 546 | 546
|  |  |  | 50 POE Load (A) | 133 | 133 | 133 | 131 | 129
Meeandah Bulk | 506-1 | Meeandah BS | Hamilton Lands | NCC Rating (A) | 771 | 771 | 771 | 771 | 771 | Urban | 70
|  |  |  | 10 POE Load (A) | 135 | 139 | 142 | 145 | 148
|  |  |  | Power Factor | 0.94509 | 0.94476 | 0.94431 | 0.9439 | 0.94333
|  |  |  | ECC Rating (A) | 771 | 771 | 771 | 771 | 771
|  |  |  | 50 POE Load (A) | 228 | 233 | 238 | 243 | 249
Meeandah Bulk | 513-1 | Meeandah BS | Hamilton Lands | NCC Rating (A) | 771 | 771 | 771 | 771 | 771 | Urban | 70
|  |  |  | 10 POE Load (A) | 134 | 138 | 141 | 144 | 147
|  |  |  | Power Factor | 0.94498 | 0.94465 | 0.9442 | 0.94379 | 0.94322
|  |  |  | ECC Rating (A) | 771 | 771 | 771 | 771 | 771
|  |  |  | 50 POE Load (A) | 228 | 233 | 238 | 242 | 249
Meeandah Bulk | 556-1 | Meeandah BS | Whinstanes | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
|  |  |  | 10 POE Load (A) | 97 | 99 | 100 | 100 | 101
|  |  |  | Power Factor | 0.95213 | 0.95189 | 0.95162 | 0.95149 | 0.95113
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 132 | 132 | 132 | 132 | 135
Meeandah Bulk | 609-1 | Meeandah BS | Myrtletown | NCC Rating (A) | 813 | 813 | 813 | 813 | 813 | Urban | 70
|  |  |  | 10 POE Load (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 2.9586e-06 | 2.9588e-06 | 2.9587e-06 | 2.9589e-06 | 2.9587e-06
|  |  |  | ECC Rating (A) | 813 | 813 | 813 | 813 | 813
|  |  |  | 50 POE Load (A) | 1 | 1 | 1 | 1 | 1
Meeandah Bulk | 610-1 | Meeandah BS | Myrtletown | NCC Rating (A) | 841 | 841 | 841 | 841 | 841 | Urban | 70
|  |  |  | 10 POE Load (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 8.8417e-06 | 8.8417e-06 | 8.8417e-06 | 8.8417e-06 | 8.8417e-06
|  |  |  | ECC Rating (A) | 841 | 841 | 841 | 841 | 841
|  |  |  | 50 POE Load (A) | 1 | 1 | 1 | 1 | 1
Molendinar Bulk | 3670-1 | Molendinar BS | Parkwood | NCC Rating (A) | 790 | 790 | 790 | 790 | 790 | Urban | 70
|  |  |  | 10 POE Load (A) | 268 | 287 | 287 | 288 | 291
|  |  |  | Power Factor | 0.99169 | 0.99108 | 0.99105 | 0.99098 | 0.99078
|  |  |  | ECC Rating (A) | 790 | 790 | 790 | 790 | 790
|  |  |  | 50 POE Load (A) | 439 | 462 | 463 | 464 | 469
Molendinar Bulk | 3671-1 | Molendinar BS | Parkwood | NCC Rating (A) | 758 | 758 | 758 | 758 | 758 | Urban | 70
|  |  |  | 10 POE Load (A) | 213 | 228 | 228 | 229 | 231
|  |  |  | Power Factor | 0.99568 | 0.99521 | 0.99519 | 0.99513 | 0.99498
|  |  |  | ECC Rating (A) | 758 | 758 | 758 | 758 | 758
|  |  |  | 50 POE Load (A) | 351 | 377 | 378 | 378 | 382
Molendinar Bulk | 389-1 | Parkwood | 389 Tee1 | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
|  |  |  | 10 POE Load (A) | 281 | 273 | 275 | 276 | 281
|  |  |  | Power Factor | 0.9926 | 0.99256 | 0.99248 | 0.99237 | 0.99209
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 593 | 594 | 595 | 599 | 608
Molendinar Bulk | 389-2 | F389 Tee1 | Labrador | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
|  |  |  | 10 POE Load (A) | 214 | 215 | 218 | 223 | 229
|  |  |  | Power Factor | 0.98191 | 0.98145 | 0.98132 | 0.9811 | 0.98073
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 343 | 349 | 351 | 356 | 365
Molendinar Bulk | 389-3 | F389 Tee1 | Hollywell | NCC Rating (A) | 659 | 659 | 659 | 659 | 659 | Urban | 70
|  |  |  | 10 POE Load (A) | 69 | 61 | 60 | 57 | 56
|  |  |  | Power Factor | 0.99172 | 0.98517 | 0.98354 | 0.9801 | 0.97692
|  |  |  | ECC Rating (A) | 659 | 659 | 659 | 659 | 659
|  |  |  | 50 POE Load (A) | 501 | 503 | 503 | 503 | 507
Molendinar Bulk | 390-1 | Molendinar BS | F390 Tee1 | NCC Rating (A) | 637 | 637 | 637 | 637 | 637 | Urban | 70
|  |  |  | 10 POE Load (A) | 85 | 84 | 83 | 82 | 81
|  |  |  | Power Factor | 0.9942 | 0.99429 | 0.99437 | 0.99453 | 0.99445
|  |  |  | ECC Rating (A) | 637 | 637 | 637 | 637 | 637
|  |  |  | 50 POE Load (A) | 189 | 188 | 186 | 182 | 180
Molendinar Bulk | 390-2 | F390 Tee | Bundall | NCC Rating (A) | 701 | 701 | 701 | 701 | 701 | Urban | 70
|  |  |  | 10 POE Load (A) | 85 | 84 | 84 | 82 | 82
|  |  |  | Power Factor | 0.99083 | 0.99087 | 0.99092 | 0.991 | 0.99086
|  |  |  | ECC Rating (A) | 701 | 701 | 701 | 701 | 701
|  |  |  | 50 POE Load (A) | 190 | 188 | 186 | 183 | 181
Molendinar Bulk | 390-3 | F390 Tee | Miami | NCC Rating (A) | 687 | 687 | 687 | 687 | 687 | Urban | 70
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 7.1417e-06 | 7.1418e-06 | 7.1421e-06 | 7.1423e-06 | 7.1415e-06
|  |  |  | ECC Rating (A) | 687 | 687 | 687 | 687 | 687
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Molendinar Bulk | 391-1 | Molendinar BS | Bundall | NCC Rating (A) | 688 | 688 | 688 | 688 | 688 | Urban | 70
|  |  |  | 10 POE Load (A) | 106 | 105 | 104 | 102 | 101
|  |  |  | Power Factor | 0.98277 | 0.98286 | 0.98296 | 0.98315 | 0.98307
|  |  |  | ECC Rating (A) | 688 | 688 | 688 | 688 | 688
|  |  |  | 50 POE Load (A) | 187 | 185 | 183 | 180 | 178
Molendinar Bulk | 392-1 | Molendinar BS | Gaven | NCC Rating (A) | 758 | 758 | 758 | 758 | 758 | Urban | 70
|  |  |  | 10 POE Load (A) | 210 | 212 | 212 | 212 | 214
|  |  |  | Power Factor | 0.99412 | 0.99401 | 0.99401 | 0.99401 | 0.9939
|  |  |  | ECC Rating (A) | 758 | 758 | 758 | 758 | 758
|  |  |  | 50 POE Load (A) | 379 | 383 | 383 | 383 | 386
Molendinar Bulk | 421-1 | Molendinar BS | Arundel | NCC Rating (A) | 713 | 713 | 713 | 713 | 713 | Urban | 450
|  |  |  | 10 POE Load (A) | 374 | 378 | 378 | 377 | 381
|  |  |  | Power Factor | 0.99152 | 0.99142 | 0.9914 | 0.99139 | 0.9912
|  |  |  | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
|  |  |  | 50 POE Load (A) | 639 | 646 | 645 | 644 | 649
Molendinar Bulk | 458-1 | Molendinar BS | Labrador | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
|  |  |  | 10 POE Load (A) | 157 | 161 | 161 | 163 | 165
|  |  |  | Power Factor | 0.99494 | 0.99484 | 0.99477 | 0.99467 | 0.99445
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 350 | 356 | 358 | 363 | 373
Molendinar Bulk | 473-1 | Molendinar BS | Gaven | NCC Rating (A) | 794 | 794 | 794 | 794 | 794 | Urban | 70
|  |  |  | 10 POE Load (A) | 211 | 212 | 212 | 212 | 214
|  |  |  | Power Factor | 0.9941 | 0.99399 | 0.99399 | 0.99399 | 0.99388
|  |  |  | ECC Rating (A) | 794 | 794 | 794 | 794 | 794
|  |  |  | 50 POE Load (A) | 379 | 383 | 383 | 383 | 386
Molendinar Bulk | 474A-1 | Arundel | Hollywell | NCC Rating (A) | 659 | 659 | 659 | 659 | 659 | Urban | 70
|  |  |  | 10 POE Load (A) | 451 | 462 | 463 | 466 | 471
|  |  |  | Power Factor | 0.99078 | 0.99064 | 0.99059 | 0.9905 | 0.99029
|  |  |  | ECC Rating (A) | 659 | 659 | 659 | 659 | 659
|  |  |  | 50 POE Load (A) | 506 | 523 | 524 | 526 | 532
Molendinar Bulk | 474B-1 | Hope Is | Hollywell | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
|  |  |  | 10 POE Load (A) | 4 | 4 | 4 | 4 | 4
|  |  |  | Power Factor | 4.6061e-06 | 4.6061e-06 | 4.6061e-06 | 4.6061e-06 | 4.6061e-06
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 4 | 4 | 4 | 4 | 4
Molendinar Bulk | 486-1 | Molendinar BS | Arundel | NCC Rating (A) | 713 | 713 | 713 | 713 | 713 | Urban | 450
|  |  |  | 10 POE Load (A) | 375 | 379 | 378 | 378 | 381
|  |  |  | Power Factor | 0.99149 | 0.99139 | 0.99138 | 0.99136 | 0.99118
|  |  |  | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
|  |  |  | 50 POE Load (A) | 639 | 646 | 645 | 644 | 649
Mudgeeraba Bulk | 3700-1 | Mudgeeraba BS | 3700 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 189 | 191 | 192 | 192 | 195
|  |  |  | Power Factor | 0.99465 | 0.99455 | 0.9945 | 0.99445 | 0.9943
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 375 | 378 | 380 | 382 | 385
Mudgeeraba Bulk | 3700-2 | 3700 Tee1 | 3701 Tee1 | NCC Rating (A) | 1094 | 1094 | 1094 | 1094 | 1094 | Rural | 170
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 6.6097e-05 | 6.6093e-05 | 6.6127e-05 | 6.6127e-05 | 6.6109e-05
|  |  |  | ECC Rating (A) | 1094 | 1094 | 1094 | 1094 | 1094
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Mudgeeraba Bulk | 3700-3 | 3700 Tee1 | 3700 Tee2 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 189 | 191 | 192 | 193 | 195
|  |  |  | Power Factor | 0.99522 | 0.99513 | 0.99508 | 0.99504 | 0.9949
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 375 | 378 | 380 | 382 | 385
Mudgeeraba Bulk | 3700-4 | 3700 Tee2 | 3702 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 8.687e-06 | 8.6877e-06 | 8.6893e-06 | 8.6893e-06 | 8.6884e-06
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Mudgeeraba Bulk | 3700-5 | 3700 Tee2 | Mudgeeraba Pkg | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 189 | 191 | 192 | 193 | 195
|  |  |  | Power Factor | 0.9955 | 0.99542 | 0.99538 | 0.99533 | 0.99521
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 375 | 378 | 380 | 382 | 385
Mudgeeraba Bulk | 3701-1 | Mudgeeraba | Mudgeeraba Pkg | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170
|  |  |  | 10 POE Load (A) | 205 | 207 | 208 | 208 | 211
|  |  |  | Power Factor | 0.99255 | 0.99246 | 0.99241 | 0.99236 | 0.99222
|  |  |  | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
|  |  |  | 50 POE Load (A) | 374 | 377 | 379 | 381 | 385
Nambour Bulk | 307-1 | Nambour BS | 307 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 98 | 99 | 100 | 99 | 100
|  |  |  | Power Factor | 0.96322 | 0.96288 | 0.96253 | 0.96288 | 0.96253
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 630 | 633 | 631 | 625 | 627
Nambour Bulk | 307-2 | 307 Tee1 | Yandina | NCC Rating (A) | 799 | 799 | 799 | 799 | 799 | Rural | 170
|  |  |  | 10 POE Load (A) | 99 | 99 | 100 | 99 | 100
|  |  |  | Power Factor | 0.96018 | 0.95995 | 0.95971 | 0.95995 | 0.95971
|  |  |  | ECC Rating (A) | 799 | 799 | 799 | 799 | 799
|  |  |  | 50 POE Load (A) | 164 | 166 | 166 | 166 | 166
Nambour Bulk | 344-1 | Nambour BS | Maleny | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
|  |  |  | 10 POE Load (A) | 194 | 194 | 194 | 194 | 196
|  |  |  | Power Factor | 0.98503 | 0.98503 | 0.98503 | 0.98503 | 0.98479
|  |  |  | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | 50 POE Load (A) | 171 | 171 | 171 | 171 | 173
Nambour Bulk | 345-1 | Nambour BS | Kenilworth | NCC Rating (A) | 416 | 416 | 416 | 416 | 416 | Rural | 170 | 4
|  |  |  | 10 POE Load (A) | 85 | 85 | 85 | 83 | 85
|  |  |  | Power Factor | 0.99228 | 0.99228 | 0.99228 | 0.99226 | 0.99228
|  |  |  | ECC Rating (A) | 416 | 416 | 416 | 416 | 416
|  |  |  | 50 POE Load (A) | 81 | 81 | 81 | 81 | 81
Nambour Bulk | 347-1 | Nambour BS | 347 Tee1 | NCC Rating (A) | 412 | 412 | 412 | 412 | 412 | Rural | 170
|  |  |  | 10 POE Load (A) | 189 | 190 | 191 | 191 | 192
|  |  |  | Power Factor | 0.97967 | 0.97955 | 0.97943 | 0.97943 | 0.97919
|  |  |  | ECC Rating (A) | 412 | 412 | 412 | 412 | 412
|  |  |  | 50 POE Load (A) | 412 | 416 | 416 | 416 | 421
Nambour Bulk | 347-2 | 347 Tee1 | Palmwoods Central | NCC Rating (A) | 515 | 515 | 515 | 515 | 515 | Rural | 170
|  |  |  | 10 POE Load (A) | 189 | 190 | 191 | 191 | 193
|  |  |  | Power Factor | 0.97975 | 0.97964 | 0.97954 | 0.97954 | 0.97933
|  |  |  | ECC Rating (A) | 515 | 515 | 515 | 515 | 515
|  |  |  | 50 POE Load (A) | 412 | 417 | 417 | 417 | 421
Nambour Bulk | 347-3 | 347 Tee1 | Landsborough | NCC Rating (A) | 412 | 412 | 412 | 412 | 412 | Rural | 170
|  |  |  | 10 POE Load (A) | 2 | 2 | 2 | 2 | 2
|  |  |  | Power Factor | 7.6423e-05 | 7.6423e-05 | 7.6423e-05 | 7.6423e-05 | 7.6423e-05
|  |  |  | ECC Rating (A) | 412 | 412 | 412 | 412 | 412
|  |  |  | 50 POE Load (A) | 240 | 240 | 240 | 240 | 242
Nambour Bulk | 348-1 | Nambour BS | Palmwoods Central | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170
|  |  |  | 10 POE Load (A) | 241 | 242 | 243 | 243 | 246
|  |  |  | Power Factor | 0.97083 | 0.97067 | 0.97052 | 0.97052 | 0.9702
|  |  |  | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
|  |  |  | 50 POE Load (A) | 401 | 406 | 406 | 406 | 410
Nambour Bulk | 489-1 | Nambour BS | Yandina | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170 | 1.5
|  |  |  | 10 POE Load (A) | 89 | 90 | 91 | 90 | 91
|  |  |  | Power Factor | 0.99275 | 0.99288 | 0.993 | 0.99288 | 0.993
|  |  |  | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | 50 POE Load (A) | 280 | 281 | 280 | 278 | 279
Nudgee Bulk | 3280-1 | Hendra | Clayfield | NCC Rating (A) | 725 | 725 | 725 | 725 | 725 | Urban | 70
|  |  |  | 10 POE Load (A) | 121 | 122 | 122 | 122 | 123
|  |  |  | Power Factor | 0.99836 | 0.99834 | 0.99834 | 0.99834 | 0.99829
|  |  |  | ECC Rating (A) | 725 | 725 | 725 | 725 | 725
|  |  |  | 50 POE Load (A) | 226 | 228 | 228 | 228 | 231
Nudgee Bulk | 540-1 | Hendra | Nundah | NCC Rating (A) | 814 | 814 | 814 | 814 | 814 | Urban | 70
|  |  |  | 10 POE Load (A) | 146 | 147 | 155 | 156 | 159
|  |  |  | Power Factor | 0.98739 | 0.98732 | 0.9896 | 0.98973 | 0.99026
|  |  |  | ECC Rating (A) | 814 | 814 | 814 | 814 | 814
|  |  |  | 50 POE Load (A) | 313 | 315 | 315 | 313 | 315
Nudgee Bulk | 593-1 | Nudgee BS | Nundah | NCC Rating (A) | 778 | 778 | 778 | 778 | 778 | Urban | 100
|  |  |  | 10 POE Load (A) | 472 | 474 | 482 | 482 | 487
|  |  |  | Power Factor | 0.9988 | 0.99878 | 0.99877 | 0.99876 | 0.99872
|  |  |  | ECC Rating (A) | 778 | 778 | 778 | 778 | 778
|  |  |  | 50 POE Load (A) | 581 | 584 | 597 | 596 | 602
Nudgee Bulk | 604-1 | Nudgee BS | Geebung | NCC Rating (A) | 459 | 459 | 459 | 459 | 459 | Urban | 70
|  |  |  | 10 POE Load (A) | 176 | 174 | 172 | 170 | 171
|  |  |  | Power Factor | 0.97835 | 0.97864 | 0.97892 | 0.9792 | 0.97911
|  |  |  | ECC Rating (A) | 459 | 459 | 459 | 459 | 459
|  |  |  | 50 POE Load (A) | 249 | 247 | 243 | 241 | 242
Nudgee Bulk | 605-1 | Nudgee BS | Geebung | NCC Rating (A) | 459 | 459 | 459 | 459 | 459 | Urban | 70
|  |  |  | 10 POE Load (A) | 176 | 174 | 172 | 171 | 171
|  |  |  | Power Factor | 0.97838 | 0.97866 | 0.97895 | 0.97923 | 0.97914
|  |  |  | ECC Rating (A) | 459 | 459 | 459 | 459 | 459
|  |  |  | 50 POE Load (A) | 249 | 247 | 243 | 241 | 242
Nudgee Bulk | 622-1 | Nudgee BS | Hendra | NCC Rating (A) | 758 | 758 | 758 | 758 | 758 | Urban | 70
|  |  |  | 10 POE Load (A) | 308 | 309 | 319 | 320 | 323
|  |  |  | Power Factor | 0.99769 | 0.99767 | 0.99757 | 0.99756 | 0.99749
|  |  |  | ECC Rating (A) | 758 | 758 | 758 | 758 | 758
|  |  |  | 50 POE Load (A) | 517 | 520 | 534 | 534 | 540
Nudgee Bulk | 623-1 | Nudgee BS | Hendra | NCC Rating (A) | 758 | 758 | 758 | 758 | 758 | Urban | 70
|  |  |  | 10 POE Load (A) | 308 | 309 | 319 | 320 | 323
|  |  |  | Power Factor | 0.99769 | 0.99767 | 0.99757 | 0.99756 | 0.99749
|  |  |  | ECC Rating (A) | 758 | 758 | 758 | 758 | 758
|  |  |  | 50 POE Load (A) | 517 | 520 | 534 | 534 | 540
Nudgee Bulk | 636-1 | Hendra | Clayfield | NCC Rating (A) | 725 | 725 | 725 | 725 | 725 | Urban | 70
|  |  |  | 10 POE Load (A) | 121 | 122 | 122 | 122 | 124
|  |  |  | Power Factor | 0.9984 | 0.99837 | 0.99837 | 0.99837 | 0.99832
|  |  |  | ECC Rating (A) | 725 | 725 | 725 | 725 | 725
|  |  |  | 50 POE Load (A) | 226 | 228 | 228 | 228 | 231
Nudgee Bulk | 643-1 | Hendra | Hamilton | NCC Rating (A) | 753 | 753 | 753 | 753 | 753 | Urban | 70
|  |  |  | 10 POE Load (A) | 145 | 145 | 146 | 147 | 150
|  |  |  | Power Factor | 0.99768 | 0.99768 | 0.99765 | 0.99762 | 0.99754
|  |  |  | ECC Rating (A) | 753 | 753 | 753 | 753 | 753
|  |  |  | 50 POE Load (A) | 281 | 283 | 283 | 285 | 290
Sandgate Bulk | 664-1 | Geebung | Zillmere | NCC Rating (A) | 441 | 441 | 441 | 441 | 441 | Urban | 70
|  |  |  | 10 POE Load (A) | 25 | 25 | 25 | 25 | 25
|  |  |  | Power Factor | 7.3809e-05 | 7.3809e-05 | 7.3809e-05 | 7.3809e-05 | 7.3809e-05
|  |  |  | ECC Rating (A) | 441 | 441 | 441 | 441 | 441
|  |  |  | 50 POE Load (A) | 25 | 25 | 25 | 25 | 25
Nudgee Bulk | 674-1 | Hendra | Hamilton | NCC Rating (A) | 753 | 753 | 753 | 753 | 753 | Urban | 70
|  |  |  | 10 POE Load (A) | 145 | 145 | 146 | 147 | 150
|  |  |  | Power Factor | 0.99767 | 0.99767 | 0.99764 | 0.99761 | 0.99753
|  |  |  | ECC Rating (A) | 753 | 753 | 753 | 753 | 753
|  |  |  | 50 POE Load (A) | 281 | 283 | 283 | 285 | 290
Nudgee Bulk | 683-1 | Nudgee BS | Geebung | NCC Rating (A) | 488 | 488 | 488 | 488 | 488 | Urban | 70
|  |  |  | 10 POE Load (A) | 172 | 170 | 168 | 167 | 167
|  |  |  | Power Factor | 0.97314 | 0.97353 | 0.97392 | 0.97431 | 0.97418
|  |  |  | ECC Rating (A) | 488 | 488 | 488 | 488 | 488
|  |  |  | 50 POE Load (A) | 244 | 242 | 238 | 236 | 237
Postmans Ridge Bulk | 376-1 | Postmans Ridge BS | Helidon | NCC Rating (A) | 290 | 582 | 582 | 582 | 582 | Rural | 170
|  |  |  | 10 POE Load (A) | 41 | 41 | 41 | 41 | 41
|  |  |  | Power Factor | 0.99074 | 0.99022 | 0.99022 | 0.99022 | 0.99022
|  |  |  | ECC Rating (A) | 290 | 582 | 582 | 582 | 582
|  |  |  | 50 POE Load (A) | 40 | 40 | 40 | 40 | 40
Postmans Ridge Bulk | 379-1 | Postmans Ridge BS | Carpendale | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
|  |  |  | 10 POE Load (A) | 26 | 26 | 26 | 26 | 26
|  |  |  | Power Factor | 0.99355 | 0.99355 | 0.99355 | 0.99355 | 0.99355
|  |  |  | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | 50 POE Load (A) | 24 | 24 | 24 | 24 | 24
Postmans Ridge Bulk | 379-2 | Carpendale | Tenthill | NCC Rating (A) | 290 | 290 | 290 | 290 | 290 | Rural | 170
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 1.8788e-05 | 1.8788e-05 | 1.8788e-05 | 1.8788e-05 | 1.8788e-05
|  |  |  | ECC Rating (A) | 290 | 290 | 290 | 290 | 290
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Raceview Bulk | 354-1 | Raceview BS | Roderick St | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Urban | 70
|  |  |  | 10 POE Load (A) | 220 | 222 | 223 | 223 | 226
|  |  |  | Power Factor | 0.98908 | 0.9891 | 0.98915 | 0.9892 | 0.98916
|  |  |  | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
|  |  |  | 50 POE Load (A) | 327 | 329 | 329 | 329 | 331
Raceview Bulk | 355-1 | Roderick St | Booval | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 70
|  |  |  | 10 POE Load (A) | 118 | 118 | 117 | 116 | 117
|  |  |  | Power Factor | 0.98186 | 0.98159 | 0.98142 | 0.98125 | 0.98096
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | 50 POE Load (A) | 329 | 331 | 331 | 331 | 333
Raceview Bulk | 361-1 | Raceview BS | Booval | NCC Rating (A) | 870 | 870 | 870 | 870 | 870 | Urban | 70
|  |  |  | 10 POE Load (A) | 253 | 258 | 261 | 266 | 272
|  |  |  | Power Factor | 0.9899 | 0.98971 | 0.9896 | 0.98945 | 0.98923
|  |  |  | ECC Rating (A) | 870 | 870 | 870 | 870 | 870
|  |  |  | 50 POE Load (A) | 415 | 423 | 430 | 436 | 445
Raceview Bulk | 362-1 | Raceview BS | 362 Tee1 | NCC Rating (A) | 515 | 515 | 515 | 515 | 515 | Rural | 170
|  |  |  | 10 POE Load (A) | 130 | 134 | 134 | 134 | 135
|  |  |  | Power Factor | 0.98915 | 0.98881 | 0.98884 | 0.98888 | 0.98884
|  |  |  | ECC Rating (A) | 515 | 515 | 515 | 515 | 515
|  |  |  | 50 POE Load (A) | 320 | 332 | 336 | 337 | 343
Raceview Bulk | 362-2 | 362 Tee1 | Flinders | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 21 | 22 | 23 | 23 | 23
|  |  |  | Power Factor | 0.48823 | 0.62069 | 0.62616 | 0.63123 | 0.65417
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 199 | 210 | 214 | 217 | 222
Raceview Bulk | 362-3 | 362 Tee1 | Kalbar | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 124 | 124 | 124 | 124 | 124
|  |  |  | Power Factor | 0.96713 | 0.96704 | 0.96703 | 0.96703 | 0.96701
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 224 | 224 | 224 | 220 | 222
Raceview Bulk | 363-1 | Raceview BS | 363 Tee1 | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Rural | 170 | 5.5
|  |  |  | 10 POE Load (A) | 126 | 130 | 130 | 130 | 131
|  |  |  | Power Factor | 0.99127 | 0.99085 | 0.99088 | 0.9909 | 0.99084
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | 50 POE Load (A) | 303 | 313 | 317 | 318 | 323
Raceview Bulk | 363-2 | 363 Tee1 | Flinders | NCC Rating (A) | 579 | 579 | 579 | 579 | 579 | Rural | 170
|  |  |  | 10 POE Load (A) | 24 | 28 | 28 | 28 | 28
|  |  |  | Power Factor | 0.90879 | 0.92225 | 0.92338 | 0.92413 | 0.92537
|  |  |  | ECC Rating (A) | 579 | 579 | 579 | 579 | 579
|  |  |  | 50 POE Load (A) | 174 | 183 | 186 | 188 | 192
Raceview Bulk | 363-3 | 363 Tee1 | Kalbar | NCC Rating (A) | 537 | 537 | 537 | 537 | 537 | Rural | 170
|  |  |  | 10 POE Load (A) | 104 | 104 | 104 | 104 | 104
|  |  |  | Power Factor | 0.999 | 0.99897 | 0.99897 | 0.99897 | 0.99897
|  |  |  | ECC Rating (A) | 537 | 537 | 537 | 537 | 537
|  |  |  | 50 POE Load (A) | 233 | 234 | 234 | 229 | 231
Raceview Bulk | 3960-1 | Ipswich Sth | Yamanto | NCC Rating (A) | 760 | 760 | 760 | 760 | 760 | Urban | 70
|  |  |  | 10 POE Load (A) | 324 | 333 | 338 | 343 | 348
|  |  |  | Power Factor | 0.97082 | 0.97019 | 0.97037 | 0.97053 | 0.97052
|  |  |  | ECC Rating (A) | 760 | 760 | 760 | 760 | 760
|  |  |  | 50 POE Load (A) | 389 | 400 | 405 | 408 | 414
Raceview Bulk | 3972-1 | Yamanto | Flinders | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
|  |  |  | 10 POE Load (A) | 156 | 160 | 160 | 159 | 160
|  |  |  | Power Factor | 0.91476 | 0.91405 | 0.91358 | 0.91314 | 0.91261
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 312 | 318 | 326 | 332 | 340
Raceview Bulk | 3980-1 | Kalbar | Boonah | NCC Rating (A) | 841 | 841 | 841 | 841 | 841 | Rural | 170
|  |  |  | 10 POE Load (A) | 57 | 57 | 57 | 57 | 57
|  |  |  | Power Factor | 0.99035 | 0.99034 | 0.99034 | 0.99034 | 0.99034
|  |  |  | ECC Rating (A) | 841 | 841 | 841 | 841 | 841
|  |  |  | 50 POE Load (A) | 107 | 107 | 107 | 105 | 107
Raceview Bulk | 401-1 | Kalbar | Boonah | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
|  |  |  | 10 POE Load (A) | 55 | 55 | 55 | 55 | 55
|  |  |  | Power Factor | 0.99762 | 0.9976 | 0.9976 | 0.9976 | 0.9976
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 107 | 107 | 107 | 105 | 107
Raceview Bulk | 411-1 | Raceview BS | Booval | NCC Rating (A) | 618 | 618 | 618 | 618 | 618 | Urban | 70
|  |  |  | 10 POE Load (A) | 214 | 218 | 221 | 225 | 230
|  |  |  | Power Factor | 0.99547 | 0.99534 | 0.99526 | 0.99515 | 0.995
|  |  |  | ECC Rating (A) | 618 | 618 | 618 | 618 | 618
|  |  |  | 50 POE Load (A) | 402 | 410 | 417 | 423 | 432
Raceview Bulk | 509A-1 | Raceview BS | Ipswich Sth | NCC Rating (A) | 763 | 763 | 763 | 763 | 763 | Urban | 70 | 2
|  |  |  | 10 POE Load (A) | 305 | 313 | 319 | 324 | 332
|  |  |  | Power Factor | 0.98822 | 0.98778 | 0.98773 | 0.98766 | 0.98753
|  |  |  | ECC Rating (A) | 763 | 763 | 763 | 763 | 763
|  |  |  | 50 POE Load (A) | 577 | 593 | 605 | 613 | 627
Raceview Bulk | 509B-1 | Raceview BS | Cooneana | NCC Rating (A) | 509 | 509 | 509 | 509 | 509 | Rural | 170
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 8.6762e-06 | 8.6761e-06 | 8.6752e-06 | 8.6757e-06 | 8.6762e-06
|  |  |  | ECC Rating (A) | 509 | 509 | 509 | 509 | 509
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Raceview Bulk | 510A-1 | Raceview BS | Ipswich Sth | NCC Rating (A) | 763 | 763 | 763 | 763 | 763 | Urban | 70 | 2
|  |  |  | 10 POE Load (A) | 302 | 310 | 316 | 321 | 328
|  |  |  | Power Factor | 0.98819 | 0.98775 | 0.9877 | 0.98764 | 0.9875
|  |  |  | ECC Rating (A) | 763 | 763 | 763 | 763 | 763
|  |  |  | 50 POE Load (A) | 576 | 593 | 605 | 613 | 627
Raceview Bulk | 510B-1 | Raceview BS | Cooneana | NCC Rating (A) | 476 | 476 | 476 | 476 | 476 | Rural | 170
|  |  |  | 10 POE Load (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 1.6339e-05 | 1.6338e-05 | 1.6339e-05 | 1.6339e-05 | 1.6338e-05
|  |  |  | ECC Rating (A) | 476 | 476 | 476 | 476 | 476
|  |  |  | 50 POE Load (A) | 1 | 1 | 1 | 1 | 1
Richlands Bulk | 3818-1 | Richlands BS | Wacol | NCC Rating (A) | 760 | 760 | 760 | 760 | 760 | Urban | 70
|  |  |  | 10 POE Load (A) | 107 | 107 | 107 | 106 | 106
|  |  |  | Power Factor | 0.9695 | 0.9695 | 0.96955 | 0.96965 | 0.9697
|  |  |  | ECC Rating (A) | 760 | 760 | 760 | 760 | 760
|  |  |  | 50 POE Load (A) | 217 | 217 | 215 | 213 | 213
Richlands Bulk | 454-1 | Richlands BS | Wacol Sth | NCC Rating (A) | 475 | 475 | 475 | 475 | 475 | Urban | 70
|  |  |  | 10 POE Load (A) | 189 | 190 | 189 | 188 | 189
|  |  |  | Power Factor | 0.98293 | 0.98284 | 0.98293 | 0.98302 | 0.98293
|  |  |  | ECC Rating (A) | 475 | 475 | 475 | 475 | 475
|  |  |  | 50 POE Load (A) | 371 | 373 | 373 | 371 | 373
Richlands Bulk | 455-1 | Richlands BS | Wacol Sth | NCC Rating (A) | 475 | 475 | 475 | 475 | 475 | Urban | 70
|  |  |  | 10 POE Load (A) | 190 | 191 | 190 | 190 | 190
|  |  |  | Power Factor | 0.98297 | 0.98288 | 0.98297 | 0.98305 | 0.98297
|  |  |  | ECC Rating (A) | 475 | 475 | 475 | 475 | 475
|  |  |  | 50 POE Load (A) | 371 | 373 | 373 | 371 | 373
Richlands Bulk | 543-1 | Inala | 543 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
|  |  |  | 10 POE Load (A) | 3 | 3 | 3 | 3 | 3
|  |  |  | Power Factor | 0.00012567 | 0.00012567 | 0.00012567 | 0.00012567 | 0.00012567
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 469 | 469 | 465 | 463 | 465
Richlands Bulk | 543-2 | 543 Tee1 | Coopers Plains | NCC Rating (A) | 348 | 348 | 348 | 348 | 348 | Urban | 70
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 5.5492e-06 | 5.5492e-06 | 5.5492e-06 | 5.5492e-06 | 5.5492e-06
|  |  |  | ECC Rating (A) | 348 | 348 | 348 | 348 | 348
|  |  |  | 50 POE Load (A) | 308 | 317 | 314 | 312 | 312
Richlands Bulk | 543-3 | 543 Tee1 | Heathwood | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
|  |  |  | 10 POE Load (A) | 2 | 2 | 2 | 2 | 2
|  |  |  | Power Factor | 8.8129e-05 | 8.8129e-05 | 8.8129e-05 | 8.8129e-05 | 8.8129e-05
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 469 | 469 | 465 | 463 | 465
Richlands Bulk | 616-1 | Richlands BS | Darra | NCC Rating (A) | 434 | 434 | 434 | 434 | 434 | Urban | 70
|  |  |  | 10 POE Load (A) | 217 | 220 | 223 | 223 | 224
|  |  |  | Power Factor | 0.86168 | 0.87065 | 0.87917 | 0.87846 | 0.88215
|  |  |  | ECC Rating (A) | 434 | 434 | 434 | 434 | 434
|  |  |  | 50 POE Load (A) | 329 | 335 | 340 | 339 | 342
Richlands Bulk | 617-1 | Richlands BS | Darra | NCC Rating (A) | 434 | 434 | 434 | 434 | 434 | Urban | 70
|  |  |  | 10 POE Load (A) | 224 | 227 | 231 | 230 | 232
|  |  |  | Power Factor | 0.86208 | 0.87103 | 0.87954 | 0.87883 | 0.88251
|  |  |  | ECC Rating (A) | 434 | 434 | 434 | 434 | 434
|  |  |  | 50 POE Load (A) | 334 | 339 | 345 | 344 | 347
Richlands Bulk | 618-1 | Richlands BS | Inala | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
|  |  |  | 10 POE Load (A) | 320 | 323 | 324 | 325 | 329
|  |  |  | Power Factor | 0.9911 | 0.99096 | 0.99089 | 0.99083 | 0.99055
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 580 | 582 | 580 | 580 | 586
Richlands Bulk | 619-1 | Richlands BS | Inala | NCC Rating (A) | 603 | 603 | 603 | 603 | 603 | Urban | 70
|  |  |  | 10 POE Load (A) | 207 | 208 | 209 | 210 | 213
|  |  |  | Power Factor | 0.99271 | 0.9926 | 0.99255 | 0.99249 | 0.99227
|  |  |  | ECC Rating (A) | 603 | 603 | 603 | 603 | 603
|  |  |  | 50 POE Load (A) | 488 | 492 | 494 | 496 | 503
Richlands Bulk | 620-1 | Richlands BS | Oxley | NCC Rating (A) | 342 | 342 | 342 | 342 | 342 | Urban | 70
|  |  |  | 10 POE Load (A) | 164 | 165 | 165 | 165 | 166
|  |  |  | Power Factor | 0.98504 | 0.98497 | 0.98497 | 0.98497 | 0.9849
|  |  |  | ECC Rating (A) | 342 | 342 | 342 | 342 | 342
|  |  |  | 50 POE Load (A) | 323 | 325 | 325 | 323 | 325
Richlands Bulk | 621-1 | Richlands BS | Oxley | NCC Rating (A) | 342 | 342 | 342 | 342 | 342 | Urban | 70
|  |  |  | 10 POE Load (A) | 156 | 157 | 157 | 157 | 158
|  |  |  | Power Factor | 0.98168 | 0.9816 | 0.9816 | 0.9816 | 0.98152
|  |  |  | ECC Rating (A) | 342 | 342 | 342 | 342 | 342
|  |  |  | 50 POE Load (A) | 323 | 325 | 325 | 323 | 325
Richlands Bulk | 641-1 | Darra | Jindalee | NCC Rating (A) | 744 | 744 | 744 | 744 | 744 | Urban | 70
|  |  |  | 10 POE Load (A) | 90 | 89 | 88 | 88 | 88
|  |  |  | Power Factor | 0.99679 | 0.99665 | 0.99651 | 0.99635 | 0.99651
|  |  |  | ECC Rating (A) | 744 | 744 | 744 | 744 | 744
|  |  |  | 50 POE Load (A) | 162 | 162 | 160 | 158 | 160
Richlands Bulk | 642-1 | Darra | Jindalee | NCC Rating (A) | 744 | 744 | 744 | 744 | 744 | Urban | 70
|  |  |  | 10 POE Load (A) | 88 | 87 | 87 | 86 | 87
|  |  |  | Power Factor | 0.99702 | 0.99688 | 0.99674 | 0.99659 | 0.99674
|  |  |  | ECC Rating (A) | 744 | 744 | 744 | 744 | 744
|  |  |  | 50 POE Load (A) | 162 | 162 | 160 | 158 | 160
Richlands Bulk | 679-1 | Richlands BS | Wacol | NCC Rating (A) | 663 | 663 | 663 | 663 | 663 | Urban | 70
|  |  |  | 10 POE Load (A) | 109 | 109 | 108 | 107 | 107
|  |  |  | Power Factor | 0.97039 | 0.97039 | 0.97044 | 0.97054 | 0.97059
|  |  |  | ECC Rating (A) | 663 | 663 | 663 | 663 | 663
|  |  |  | 50 POE Load (A) | 217 | 217 | 215 | 213 | 213
Richlands Bulk | 680-1 | Richlands BS | Wacol | NCC Rating (A) | 760 | 760 | 760 | 760 | 760 | Urban | 70
|  |  |  | 10 POE Load (A) | 220 | 220 | 218 | 217 | 216
|  |  |  | Power Factor | 0.9565 | 0.9565 | 0.95739 | 0.95763 | 0.95775
|  |  |  | ECC Rating (A) | 760 | 760 | 760 | 760 | 760
|  |  |  | 50 POE Load (A) | 217 | 217 | 215 | 213 | 213
Richlands Bulk | 700-1 | Richlands BS | Darra | NCC Rating (A) | 551 | 551 | 551 | 551 | 551 | Urban | 70
|  |  |  | 10 POE Load (A) | 171 | 174 | 177 | 176 | 178
|  |  |  | Power Factor | 0.89925 | 0.90697 | 0.91426 | 0.91365 | 0.91679
|  |  |  | ECC Rating (A) | 551 | 551 | 551 | 551 | 551
|  |  |  | 50 POE Load (A) | 260 | 265 | 269 | 268 | 270
Runcorn Bulk | 3440-1 | Runcorn BS | Sunnybank | NCC Rating (A) | 601 | 601 | 601 | 601 | 601 | Urban | 70
|  |  |  | 10 POE Load (A) | 344 | 346 | 344 | 343 | 354
|  |  |  | Power Factor | 0.9879 | 0.98785 | 0.9879 | 0.98795 | 0.98754
|  |  |  | ECC Rating (A) | 601 | 601 | 601 | 601 | 601
|  |  |  | 50 POE Load (A) | 404 | 406 | 404 | 402 | 416
Runcorn Bulk | 433-1 | Runcorn BS | Calamvale | NCC Rating (A) | 450 | 450 | 450 | 450 | 450 | Urban | 70
|  |  |  | 10 POE Load (A) | 2 | 2 | 2 | 2 | 2
|  |  |  | Power Factor | 1.7626e-05 | 1.7626e-05 | 1.7626e-05 | 1.7626e-05 | 1.7626e-05
|  |  |  | ECC Rating (A) | 450 | 450 | 450 | 450 | 450
|  |  |  | 50 POE Load (A) | 2 | 2 | 2 | 2 | 2
Runcorn Bulk | 434-1 | Runcorn | Calamvale | NCC Rating (A) | 450 | 450 | 450 | 450 | 450 | Urban | 70
|  |  |  | 10 POE Load (A) | 2 | 2 | 2 | 2 | 2
|  |  |  | Power Factor | 5.1614e-05 | 5.1614e-05 | 5.1614e-05 | 5.1614e-05 | 5.1614e-05
|  |  |  | ECC Rating (A) | 450 | 450 | 450 | 450 | 450
|  |  |  | 50 POE Load (A) | 2 | 2 | 2 | 2 | 2
Runcorn Bulk | 459A-1 | Upper Mt Gravatt | Sunnybank | NCC Rating (A) | 799 | 799 | 799 | 799 | 799 | Urban | 70
|  |  |  | 10 POE Load (A) | 73 | 73 | 73 | 73 | 75
|  |  |  | Power Factor | 0.9295 | 0.92942 | 0.9295 | 0.92958 | 0.92895
|  |  |  | ECC Rating (A) | 799 | 799 | 799 | 799 | 799
|  |  |  | 50 POE Load (A) | 411 | 413 | 411 | 409 | 424
Runcorn Bulk | 459B-1 | Runcorn BS | Upper Mt Gravatt | NCC Rating (A) | 848 | 848 | 848 | 848 | 848 | Urban | 70
|  |  |  | 10 POE Load (A) | 72 | 72 | 72 | 71 | 74
|  |  |  | Power Factor | 0.94458 | 0.94445 | 0.94458 | 0.94472 | 0.94363
|  |  |  | ECC Rating (A) | 848 | 848 | 848 | 848 | 848
|  |  |  | 50 POE Load (A) | 410 | 412 | 410 | 408 | 423
Runcorn Bulk | 667-1 | Runcorn BS | Acacia Ridge | NCC Rating (A) | 453 | 453 | 453 | 453 | 453 | Urban | 70
|  |  |  | 10 POE Load (A) | 28 | 28 | 28 | 28 | 28
|  |  |  | Power Factor | 9.2863e-05 | 9.2863e-05 | 9.2863e-05 | 9.2863e-05 | 9.2863e-05
|  |  |  | ECC Rating (A) | 453 | 453 | 453 | 453 | 453
|  |  |  | 50 POE Load (A) | 28 | 28 | 28 | 28 | 28
Runcorn Bulk | 668-1 | Runcorn BS | Acacia Ridge | NCC Rating (A) | 453 | 453 | 453 | 453 | 453 | Urban | 70
|  |  |  | 10 POE Load (A) | 28 | 28 | 28 | 28 | 28
|  |  |  | Power Factor | 9.3774e-05 | 9.3774e-05 | 9.3774e-05 | 9.3774e-05 | 9.3774e-05
|  |  |  | ECC Rating (A) | 453 | 453 | 453 | 453 | 453
|  |  |  | 50 POE Load (A) | 28 | 28 | 28 | 28 | 28
Runcorn Bulk | 690-1 | Runcorn BS | Runcorn | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
|  |  |  | 10 POE Load (A) | 210 | 212 | 213 | 214 | 216
|  |  |  | Power Factor | 0.99571 | 0.99562 | 0.99557 | 0.99552 | 0.99539
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 361 | 366 | 368 | 368 | 373
Runcorn Bulk | 691-1 | Runcorn BS | Runcorn | NCC Rating (A) | 685 | 685 | 685 | 685 | 685 | Urban | 70
|  |  |  | 10 POE Load (A) | 166 | 167 | 168 | 169 | 171
|  |  |  | Power Factor | 0.99639 | 0.99631 | 0.99627 | 0.99623 | 0.99612
|  |  |  | ECC Rating (A) | 685 | 685 | 685 | 685 | 685
|  |  |  | 50 POE Load (A) | 361 | 367 | 369 | 369 | 374
Runcorn Bulk | 694-1 | Runcorn BS | Eight Mile Plains Bus 1 | NCC Rating (A) | 581 | 581 | 581 | 581 | 581 | Urban | 230
|  |  |  | 10 POE Load (A) | 265 | 265 | 263 | 275 | 293
|  |  |  | Power Factor | 0.99348 | 0.99348 | 0.99356 | 0.99294 | 0.99199
|  |  |  | ECC Rating (A) | 581 | 581 | 581 | 581 | 581
|  |  |  | 50 POE Load (A) | 471 | 473 | 473 | 509 | 546
Sandgate Bulk | 3290-1 | Sandgate BS | Bald Hills Bus 1 | NCC Rating (A) | 912 | 912 | 912 | 912 | 912 | Urban | 70
|  |  |  | 10 POE Load (A) | 107 | 107 | 107 | 107 | 107
|  |  |  | Power Factor | 0.99256 | 0.99256 | 0.99256 | 0.99256 | 0.99256
|  |  |  | ECC Rating (A) | 912 | 912 | 912 | 912 | 912
|  |  |  | 50 POE Load (A) | 198 | 198 | 198 | 198 | 198
Sandgate Bulk | 505-1 | Sandgate BS | Zilmere | NCC Rating (A) | 912 | 912 | 912 | 912 | 912 | Urban | 70
|  |  |  | 10 POE Load (A) | 227 | 227 | 227 | 226 | 227
|  |  |  | Power Factor | 0.97956 | 0.97943 | 0.97956 | 0.97968 | 0.97943
|  |  |  | ECC Rating (A) | 912 | 912 | 912 | 912 | 912
|  |  |  | 50 POE Load (A) | 312 | 312 | 311 | 311 | 312
Sandgate Bulk | 524-1 | Sandgate BS | Geebung | NCC Rating (A) | 521 | 521 | 521 | 521 | 521 | Urban | 70
|  |  |  | 10 POE Load (A) | 153 | 153 | 153 | 152 | 153
|  |  |  | Power Factor | 0.99095 | 0.99086 | 0.99095 | 0.99104 | 0.99086
|  |  |  | ECC Rating (A) | 521 | 521 | 521 | 521 | 521
|  |  |  | 50 POE Load (A) | 263 | 263 | 262 | 262 | 263
Sandgate Bulk | 524-2 | Geebung | Zillmere | NCC Rating (A) | 441 | 441 | 441 | 441 | 441 | Urban | 70
|  |  |  | 10 POE Load (A) | 158 | 158 | 158 | 157 | 158
|  |  |  | Power Factor | 0.96113 | 0.96112 | 0.96113 | 0.96115 | 0.96112
|  |  |  | ECC Rating (A) | 441 | 441 | 441 | 441 | 441
|  |  |  | 50 POE Load (A) | 268 | 268 | 267 | 267 | 268
Sandgate Bulk | 561-1 | Sandgate BS | Brighton TR1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
|  |  |  | 10 POE Load (A) | 80 | 80 | 80 | 80 | 80
|  |  |  | Power Factor | 0.99292 | 0.99292 | 0.99292 | 0.99292 | 0.99292
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 151 | 152 | 151 | 151 | 152
Sandgate Bulk | 656-1 | Sandgate BS | Brighton TR2 | NCC Rating (A) | 379 | 379 | 379 | 379 | 379 | Urban | 70
|  |  |  | 10 POE Load (A) | 77 | 77 | 77 | 77 | 77
|  |  |  | Power Factor | 0.99904 | 0.99904 | 0.99904 | 0.99904 | 0.99904
|  |  |  | ECC Rating (A) | 379 | 379 | 379 | 379 | 379
|  |  |  | 50 POE Load (A) | 152 | 154 | 152 | 152 | 154
Sandgate Bulk | 671-1 | Sandagate BS | Zillmere | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 70
|  |  |  | 10 POE Load (A) | 134 | 134 | 134 | 133 | 134
|  |  |  | Power Factor | 0.99465 | 0.99459 | 0.99465 | 0.99471 | 0.99459
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | 50 POE Load (A) | 231 | 231 | 230 | 230 | 231
Brendale Bulk | 310-3 | 310 Tee1 | 569 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 2.0848e-06 | 2.0848e-06 | 2.0848e-06 | 2.0849e-06 | 2.0848e-06
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Stafford Bulk | 548-1 | Stafford BS | Enoggera | NCC Rating (A) | 886 | 886 | 886 | 886 | 886 | Urban | 150
|  |  |  | 10 POE Load (A) | 448 | 449 | 448 | 448 | 448
|  |  |  | Power Factor | 0.99257 | 0.99257 | 0.99259 | 0.9926 | 0.9926
|  |  |  | ECC Rating (A) | 1020 | 1020 | 1020 | 1020 | 1020
|  |  |  | 50 POE Load (A) | 853 | 855 | 853 | 851 | 855
Stafford Bulk | 550-1 | Stafford BS | Chermside | NCC Rating (A) | 748 | 748 | 748 | 748 | 748 | Urban | 70
|  |  |  | 10 POE Load (A) | 262 | 262 | 261 | 259 | 259
|  |  |  | Power Factor | 0.99077 | 0.99077 | 0.99081 | 0.9909 | 0.9909
|  |  |  | ECC Rating (A) | 748 | 748 | 748 | 748 | 748
|  |  |  | 50 POE Load (A) | 493 | 493 | 491 | 488 | 490
Stafford Bulk | 551-1 | Stafford BS | Chermside | NCC Rating (A) | 748 | 748 | 748 | 748 | 748 | Urban | 70
|  |  |  | 10 POE Load (A) | 261 | 261 | 261 | 259 | 259
|  |  |  | Power Factor | 0.99076 | 0.99076 | 0.9908 | 0.99089 | 0.99089
|  |  |  | ECC Rating (A) | 748 | 748 | 748 | 748 | 748
|  |  |  | 50 POE Load (A) | 493 | 493 | 491 | 488 | 490
Stafford Bulk | 567-1 | Stafford BS | Kedron | NCC Rating (A) | 613 | 613 | 613 | 613 | 613 | Urban | 70
|  |  |  | 10 POE Load (A) | 212 | 214 | 214 | 214 | 215
|  |  |  | Power Factor | 0.99054 | 0.99042 | 0.99042 | 0.99025 | 0.99014
|  |  |  | ECC Rating (A) | 613 | 613 | 613 | 613 | 613
|  |  |  | 50 POE Load (A) | 408 | 409 | 409 | 418 | 422
Stafford Bulk | 568-1 | Stafford BS | Kedron | NCC Rating (A) | 613 | 613 | 613 | 613 | 613 | Urban | 70
|  |  |  | 10 POE Load (A) | 214 | 215 | 215 | 216 | 217
|  |  |  | Power Factor | 0.99035 | 0.99024 | 0.99024 | 0.9904 | 0.99029
|  |  |  | ECC Rating (A) | 613 | 613 | 613 | 613 | 613
|  |  |  | 50 POE Load (A) | 407 | 409 | 409 | 418 | 421
Stafford Bulk | 594-1 | Stafford BS | Enoggera | NCC Rating (A) | 886 | 886 | 886 | 886 | 886 | Urban | 150
|  |  |  | 10 POE Load (A) | 446 | 447 | 446 | 445 | 446
|  |  |  | Power Factor | 0.99255 | 0.99255 | 0.99257 | 0.99259 | 0.99259
|  |  |  | ECC Rating (A) | 1020 | 1020 | 1020 | 1020 | 1020
|  |  |  | 50 POE Load (A) | 853 | 855 | 853 | 851 | 855
Stafford Bulk | 595-1 | Enoggera | Grovely | NCC Rating (A) | 720 | 720 | 720 | 720 | 720 | Urban | 70
|  |  |  | 10 POE Load (A) | 171 | 170 | 169 | 167 | 166
|  |  |  | Power Factor | 0.99658 | 0.99661 | 0.99668 | 0.99675 | 0.99678
|  |  |  | ECC Rating (A) | 720 | 720 | 720 | 720 | 720
|  |  |  | 50 POE Load (A) | 326 | 324 | 320 | 317 | 317
Stafford Bulk | 596-1 | Enoggera | Grovely | NCC Rating (A) | 720 | 720 | 720 | 720 | 720 | Urban | 70
|  |  |  | 10 POE Load (A) | 172 | 172 | 170 | 168 | 167
|  |  |  | Power Factor | 0.9966 | 0.99663 | 0.9967 | 0.99677 | 0.9968
|  |  |  | ECC Rating (A) | 720 | 720 | 720 | 720 | 720
|  |  |  | 50 POE Load (A) | 325 | 324 | 320 | 316 | 316
Stafford Bulk | 607-1 | Chermside | Zillmere | NCC Rating (A) | 416 | 416 | 416 | 416 | 416 | Urban | 70
|  |  |  | 10 POE Load (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 1.1685e-05 | 1.1685e-05 | 1.1685e-05 | 1.1685e-05 | 1.1685e-05
|  |  |  | ECC Rating (A) | 416 | 416 | 416 | 416 | 416
|  |  |  | 50 POE Load (A) | 1 | 1 | 1 | 1 | 1
Sunrise Hills Bulk | 308-1 | Perigian | 308 Tee1 | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
|  |  |  | 10 POE Load (A) | 495 | 497 | 497 | 492 | 494
|  |  |  | Power Factor | 0.98931 | 0.9892 | 0.98922 | 0.98943 | 0.98933
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 465 | 468 | 467 | 463 | 465
Sunrise Hills Bulk | 308-2 | 308 Tee1 | Coolum | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
|  |  |  | 10 POE Load (A) | 495 | 497 | 497 | 492 | 495
|  |  |  | Power Factor | 0.99305 | 0.99298 | 0.99299 | 0.99313 | 0.99306
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 465 | 468 | 467 | 463 | 465
Sunrise Hills Bulk | 308-3 | 308 Tee1 | 307 Tee2 | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 2.622e-05 | 2.6225e-05 | 2.6224e-05 | 2.6231e-05 | 2.6227e-05
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Sunrise Hills Bulk | 3100-1 | Sunrise Hills BS | 3100 Tee1 | NCC Rating (A) | 888 | 888 | 888 | 888 | 888 | Urban | 70 | 7
|  |  |  | 10 POE Load (A) | 734 | 736 | 734 | 728 | 730
|  |  |  | Power Factor | 0.96557 | 0.96533 | 0.9655 | 0.96612 | 0.96589
|  |  |  | ECC Rating (A) | 888 | 888 | 888 | 888 | 888
|  |  |  | 50 POE Load (A) | 681 | 683 | 681 | 674 | 676
Sunrise Hills Bulk | 3100-2 | 3100 Tee1 | Peregian | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
|  |  |  | 10 POE Load (A) | 734 | 736 | 734 | 728 | 730
|  |  |  | Power Factor | 0.98665 | 0.98654 | 0.9866 | 0.98686 | 0.98676
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 681 | 683 | 681 | 674 | 677
Sunrise Hills Bulk | 343-1 | Sunrise Hills BS | 343 Tee1 | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Rural | 170
|  |  |  | 10 POE Load (A) | 405 | 404 | 400 | 398 | 398
|  |  |  | Power Factor | 0.98812 | 0.98813 | 0.98831 | 0.98842 | 0.98842
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 645 | 643 | 637 | 630 | 630
Sunrise Hills Bulk | 343-2 | 343 Tee1 | Tewantin | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Rural | 170
|  |  |  | 10 POE Load (A) | 135 | 133 | 131 | 128 | 128
|  |  |  | Power Factor | 0.98971 | 0.98997 | 0.9902 | 0.9905 | 0.9905
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 389 | 387 | 382 | 377 | 375
Sunrise Hills Bulk | 343-3 | 343 Tee1 | Cooroy | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Rural | 170
|  |  |  | 10 POE Load (A) | 270 | 272 | 270 | 270 | 270
|  |  |  | Power Factor | 0.99578 | 0.99575 | 0.99578 | 0.99578 | 0.99578
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | 50 POE Load (A) | 256 | 255 | 255 | 253 | 255
Sunrise Hills Bulk | 346-1 | Sunrise Hills BS | 346 Tee1 | NCC Rating (A) | 1108 | 1108 | 1108 | 1108 | 1108 | Urban | 70
|  |  |  | 10 POE Load (A) | 274 | 273 | 270 | 267 | 267
|  |  |  | Power Factor | 0.98766 | 0.98774 | 0.98794 | 0.98811 | 0.98811
|  |  |  | ECC Rating (A) | 1108 | 1108 | 1108 | 1108 | 1108
|  |  |  | 50 POE Load (A) | 388 | 386 | 380 | 375 | 373
Sunrise Hills Bulk | 346-2 | 346 Tee1 | Tewantin | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
|  |  |  | 10 POE Load (A) | 274 | 273 | 270 | 267 | 267
|  |  |  | Power Factor | 0.98766 | 0.98774 | 0.98794 | 0.98811 | 0.98811
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 388 | 386 | 380 | 375 | 373
Sunrise Hills Bulk | 346-3 | 346 Tee1 | 3100 Tee1 | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0.00030708 | 0.00030726 | 0.00030646 | 0.000308 | 0.00030662
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Sunrise Hills Bulk | 488-1 | Cooroy | 488 Tee1 | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170
|  |  |  | 10 POE Load (A) | 128 | 128 | 128 | 128 | 128
|  |  |  | Power Factor | 0.9928 | 0.99279 | 0.9928 | 0.9928 | 0.9928
|  |  |  | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
|  |  |  | 50 POE Load (A) | 122 | 121 | 121 | 121 | 121
Sunrise Hills Bulk | 488-3 | 488 Tee1 | 488 Tee2 | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
|  |  |  | 10 POE Load (A) | 128 | 128 | 128 | 128 | 128
|  |  |  | Power Factor | 0.99308 | 0.99307 | 0.99308 | 0.99308 | 0.99308
|  |  |  | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | 50 POE Load (A) | 122 | 121 | 121 | 121 | 121
Sunrise Hills Bulk | 488-4 | 488 Tee2 | Black Mtn | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
|  |  |  | 10 POE Load (A) | 46 | 46 | 46 | 46 | 46
|  |  |  | Power Factor | 0.98675 | 0.98674 | 0.98675 | 0.98675 | 0.98675
|  |  |  | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | 50 POE Load (A) | 45 | 44 | 44 | 44 | 44
Sunrise Hills Bulk | 488-5 | 488 Tee2 | 488 Tee3 | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
|  |  |  | 10 POE Load (A) | 83 | 83 | 83 | 83 | 83
|  |  |  | Power Factor | 0.99616 | 0.99615 | 0.99616 | 0.99616 | 0.99616
|  |  |  | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | 50 POE Load (A) | 77 | 77 | 77 | 77 | 77
Sunrise Hills Bulk | 488-6 | 488 Tee3 | Eumundi | NCC Rating (A) | 468 | 468 | 468 | 468 | 468 | Rural | 170
|  |  |  | 10 POE Load (A) | 83 | 83 | 83 | 83 | 83
|  |  |  | Power Factor | 0.99506 | 0.99505 | 0.99506 | 0.99506 | 0.99506
|  |  |  | ECC Rating (A) | 468 | 468 | 468 | 468 | 468
|  |  |  | 50 POE Load (A) | 77 | 77 | 77 | 77 | 77
Sunrise Hills Bulk | 488-7 | 488 Tee3 | Yandina | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
|  |  |  | 10 POE Load (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 3.6886e-05 | 3.6886e-05 | 3.6886e-05 | 3.6886e-05 | 3.6886e-05
|  |  |  | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | 50 POE Load (A) | 1 | 1 | 1 | 1 | 1
Tennyson Bulk | 3390-1 | Taringa | Indooroopilly | NCC Rating (A) | 779 | 779 | 779 | 779 | 779 | Urban | 70
|  |  |  | 10 POE Load (A) | 96 | 97 | 97 | 96 | 97
|  |  |  | Power Factor | 0.97932 | 0.9792 | 0.97913 | 0.97911 | 0.97882
|  |  |  | ECC Rating (A) | 779 | 779 | 779 | 779 | 779
|  |  |  | 50 POE Load (A) | 133 | 134 | 134 | 134 | 135
Tennyson Bulk | 3393-1 | Tennyson BS | St Lucia TR1 | NCC Rating (A) | 650 | 650 | 650 | 650 | 650 | Urban | 70
|  |  |  | 10 POE Load (A) | 98 | 99 | 98 | 98 | 98
|  |  |  | Power Factor | 0.97473 | 0.97467 | 0.97469 | 0.97473 | 0.97468
|  |  |  | ECC Rating (A) | 650 | 650 | 650 | 650 | 650
|  |  |  | 50 POE Load (A) | 190 | 191 | 190 | 189 | 189
Tennyson Bulk | 3394-1 | Tennyson BS | St Lucia TR2 | NCC Rating (A) | 650 | 650 | 650 | 650 | 650 | Urban | 70
|  |  |  | 10 POE Load (A) | 199 | 200 | 199 | 199 | 199
|  |  |  | Power Factor | 0.96288 | 0.96276 | 0.96288 | 0.963 | 0.963
|  |  |  | ECC Rating (A) | 650 | 650 | 650 | 650 | 650
|  |  |  | 50 POE Load (A) | 190 | 190 | 190 | 189 | 189
Tennyson Bulk | 3460-1 | Annerley | Buranda | NCC Rating (A) | 859 | 859 | 859 | 859 | 859 | Urban | 70
|  |  |  | 10 POE Load (A) | 190 | 193 | 197 | 200 | 204
|  |  |  | Power Factor | 0.98606 | 0.98578 | 0.98782 | 0.98529 | 0.98493
|  |  |  | ECC Rating (A) | 859 | 859 | 859 | 859 | 859
|  |  |  | 50 POE Load (A) | 370 | 377 | 382 | 389 | 396
Tennyson Bulk | 3461-1 | Annerley | Buranda | NCC Rating (A) | 859 | 859 | 859 | 859 | 859 | Urban | 70
|  |  |  | 10 POE Load (A) | 190 | 194 | 197 | 200 | 204
|  |  |  | Power Factor | 0.98608 | 0.9858 | 0.98784 | 0.98531 | 0.98495
|  |  |  | ECC Rating (A) | 859 | 859 | 859 | 859 | 859
|  |  |  | 50 POE Load (A) | 370 | 377 | 382 | 389 | 396
Tennyson Bulk | 410-1 | Sherwood | Indooroopilly | NCC Rating (A) | 425 | 425 | 425 | 425 | 425 | Urban | 70
|  |  |  | 10 POE Load (A) | 172 | 172 | 173 | 173 | 174
|  |  |  | Power Factor | 0.99394 | 0.99389 | 0.9939 | 0.99391 | 0.99379
|  |  |  | ECC Rating (A) | 425 | 425 | 425 | 425 | 425
|  |  |  | 50 POE Load (A) | 266 | 268 | 268 | 268 | 271
Tennyson Bulk | 460-1 | Tennyson BS | Sherwood | NCC Rating (A) | 774 | 774 | 774 | 774 | 774 | Urban | 70
|  |  |  | 10 POE Load (A) | 312 | 314 | 314 | 313 | 316
|  |  |  | Power Factor | 0.99548 | 0.99539 | 0.99539 | 0.99542 | 0.99528
|  |  |  | ECC Rating (A) | 774 | 774 | 774 | 774 | 774
|  |  |  | 50 POE Load (A) | 420 | 422 | 422 | 422 | 426
Tennyson Bulk | 480-1 | Taringa | St Lucia | NCC Rating (A) | 650 | 650 | 650 | 650 | 650 | Urban | 70
|  |  |  | 10 POE Load (A) | 98 | 98 | 98 | 98 | 97
|  |  |  | Power Factor | 0.97509 | 0.97506 | 0.97512 | 0.97518 | 0.97522
|  |  |  | ECC Rating (A) | 640 | 640 | 640 | 640 | 640
|  |  |  | 50 POE Load (A) | 189 | 190 | 189 | 188 | 188
Tennyson Bulk | 504-1 | Tennyson BS | Taringa | NCC Rating (A) | 637 | 637 | 637 | 637 | 637 | Urban | 70
|  |  |  | 10 POE Load (A) | 245 | 247 | 247 | 247 | 249
|  |  |  | Power Factor | 0.99717 | 0.99713 | 0.99713 | 0.99714 | 0.99705
|  |  |  | ECC Rating (A) | 637 | 637 | 637 | 637 | 637
|  |  |  | 50 POE Load (A) | 354 | 357 | 356 | 357 | 360
Tennyson Bulk | 507A-1 | Toowong | Indooroopilly | NCC Rating (A) | 786 | 786 | 786 | 786 | 786 | Urban | 70
|  |  |  | 10 POE Load (A) | 98 | 99 | 99 | 98 | 99
|  |  |  | Power Factor | 0.98278 | 0.98267 | 0.9826 | 0.98258 | 0.98232
|  |  |  | ECC Rating (A) | 786 | 786 | 786 | 786 | 786
|  |  |  | 50 POE Load (A) | 135 | 135 | 136 | 135 | 136
Tennyson Bulk | 507B-1 | Toowong | Taringa | NCC Rating (A) | 783 | 783 | 783 | 783 | 783 | Urban | 70
|  |  |  | 10 POE Load (A) | 97 | 98 | 98 | 97 | 98
|  |  |  | Power Factor | 0.99272 | 0.9926 | 0.99257 | 0.99256 | 0.99233
|  |  |  | ECC Rating (A) | 783 | 783 | 783 | 783 | 783
|  |  |  | 50 POE Load (A) | 134 | 134 | 135 | 134 | 135
Tennyson Bulk | 511-1 | Tennyson BS | Moorooka | NCC Rating (A) | 801 | 801 | 801 | 801 | 801 | Urban | 70
|  |  |  | 10 POE Load (A) | 147 | 148 | 149 | 149 | 151
|  |  |  | Power Factor | 0.98363 | 0.98355 | 0.98348 | 0.98348 | 0.98332
|  |  |  | ECC Rating (A) | 801 | 801 | 801 | 801 | 801
|  |  |  | 50 POE Load (A) | 134 | 135 | 136 | 136 | 138
Tennyson Bulk | 514-1 | Tennyson BS | Moorooka | NCC Rating (A) | 801 | 801 | 801 | 801 | 801 | Urban | 70
|  |  |  | 10 POE Load (A) | 147 | 148 | 149 | 149 | 151
|  |  |  | Power Factor | 0.9839 | 0.98382 | 0.98375 | 0.98375 | 0.9836
|  |  |  | ECC Rating (A) | 801 | 801 | 801 | 801 | 801
|  |  |  | 50 POE Load (A) | 134 | 135 | 136 | 136 | 138
Tennyson Bulk | 515-1 | Tennyson BS | Sherwood | NCC Rating (A) | 768 | 768 | 768 | 768 | 768 | Urban | 70
|  |  |  | 10 POE Load (A) | 331 | 333 | 333 | 332 | 335
|  |  |  | Power Factor | 0.99709 | 0.99701 | 0.99701 | 0.99704 | 0.99692
|  |  |  | ECC Rating (A) | 768 | 768 | 768 | 768 | 768
|  |  |  | 50 POE Load (A) | 445 | 448 | 448 | 448 | 452
Tennyson Bulk | 523A-1 | Tennyson BS | Rocklea | NCC Rating (A) | 688 | 688 | 688 | 688 | 688 | Urban | 70
|  |  |  | 10 POE Load (A) | 8 | 8 | 8 | 8 | 8
|  |  |  | Power Factor | 8.7628e-06 | 8.7628e-06 | 8.7628e-06 | 8.7628e-06 | 8.7627e-06
|  |  |  | ECC Rating (A) | 688 | 688 | 688 | 688 | 688
|  |  |  | 50 POE Load (A) | 8 | 8 | 8 | 8 | 8
Tennyson Bulk | 539-1 | Sherwood | Kenmore | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 260
|  |  |  | 10 POE Load (A) | 215 | 216 | 216 | 216 | 218
|  |  |  | Power Factor | 0.99582 | 0.99576 | 0.99576 | 0.99577 | 0.99562
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | 50 POE Load (A) | 471 | 474 | 474 | 474 | 478
Tennyson Bulk | 554-1 | Tennyson BS | Sherwood | NCC Rating (A) | 768 | 768 | 768 | 768 | 768 | Urban | 70
|  |  |  | 10 POE Load (A) | 351 | 353 | 353 | 352 | 356
|  |  |  | Power Factor | 0.99568 | 0.99559 | 0.99559 | 0.99562 | 0.99549
|  |  |  | ECC Rating (A) | 768 | 768 | 768 | 768 | 768
|  |  |  | 50 POE Load (A) | 461 | 464 | 464 | 464 | 468
Tennyson Bulk | 571-1 | Indooroopilly | Kenmore | NCC Rating (A) | 527 | 527 | 527 | 527 | 527 | Urban | 260
|  |  |  | 10 POE Load (A) | 281 | 282 | 282 | 282 | 285
|  |  |  | Power Factor | 0.98946 | 0.98938 | 0.98938 | 0.98938 | 0.98916
|  |  |  | ECC Rating (A) | 527 | 527 | 527 | 527 | 527
|  |  |  | 50 POE Load (A) | 465 | 469 | 469 | 469 | 473
Tennyson Bulk | 606-1 | Tennyson BS | Taringa | NCC Rating (A) | 637 | 637 | 637 | 637 | 637 | Urban | 70
|  |  |  | 10 POE Load (A) | 246 | 248 | 248 | 248 | 250
|  |  |  | Power Factor | 0.99718 | 0.99714 | 0.99715 | 0.99716 | 0.99707
|  |  |  | ECC Rating (A) | 637 | 637 | 637 | 637 | 637
|  |  |  | 50 POE Load (A) | 355 | 357 | 357 | 357 | 361
Tennyson Bulk | 637-1 | Tennyson BS | Annerley | NCC Rating (A) | 765 | 765 | 765 | 765 | 765 | Urban | 70
|  |  |  | 10 POE Load (A) | 322 | 326 | 330 | 333 | 339
|  |  |  | Power Factor | 0.99108 | 0.99087 | 0.99071 | 0.99052 | 0.99024
|  |  |  | ECC Rating (A) | 765 | 765 | 765 | 765 | 765
|  |  |  | 50 POE Load (A) | 621 | 630 | 637 | 646 | 654
Tennyson Bulk | 638-1 | Tennyson BS | Annerley | NCC Rating (A) | 765 | 765 | 765 | 765 | 765 | Urban | 70
|  |  |  | 10 POE Load (A) | 323 | 327 | 331 | 334 | 341
|  |  |  | Power Factor | 0.99109 | 0.99088 | 0.99072 | 0.99053 | 0.99025
|  |  |  | ECC Rating (A) | 765 | 765 | 765 | 765 | 765
|  |  |  | 50 POE Load (A) | 621 | 630 | 637 | 646 | 654
Tennyson Bulk | F703-1 | Sherwood | Indooroopilly | NCC Rating (A) | 425 | 425 | 425 | 425 | 425 | Urban | 70
|  |  |  | 10 POE Load (A) | 173 | 174 | 174 | 174 | 176
|  |  |  | Power Factor | 0.99413 | 0.99408 | 0.99409 | 0.9941 | 0.99398
|  |  |  | ECC Rating (A) | 425 | 425 | 425 | 425 | 425
|  |  |  | 50 POE Load (A) | 267 | 269 | 269 | 269 | 272
Victoria Park Bulk | 627-1 | Victoria Pk BS | Astor Tce | NCC Rating (A) | 525 | 525 | 525 | 525 | 525 | Urban | 70
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0.96802 | 0.96802 | 0.96802 | 0.96802 | 0.96802
|  |  |  | ECC Rating (A) | 525 | 525 | 525 | 525 | 525
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Victoria Park Bulk | 628-1 | Victoria Pk BS | Astor Tce | NCC Rating (A) | 502 | 502 | 502 | 502 | 502 | Urban | 70 | 2
|  |  |  | 10 POE Load (A) | 138 | 139 | 139 | 139 | 140
|  |  |  | Power Factor | 0.97438 | 0.97429 | 0.97429 | 0.97429 | 0.9742
|  |  |  | ECC Rating (A) | 502 | 502 | 502 | 502 | 502
|  |  |  | 50 POE Load (A) | 278 | 280 | 280 | 280 | 282
Victoria Park Bulk | 639-1 | Victoria Pk BS | Newmarket | NCC Rating (A) | 536 | 536 | 536 | 536 | 536 | Urban | 70
|  |  |  | 10 POE Load (A) | 158 | 159 | 159 | 158 | 160
|  |  |  | Power Factor | 0.99701 | 0.99698 | 0.99698 | 0.99701 | 0.99694
|  |  |  | ECC Rating (A) | 536 | 536 | 536 | 536 | 536
|  |  |  | 50 POE Load (A) | 300 | 300 | 300 | 300 | 303
Victoria Park Bulk | 649-1 | Victoria Pk BS | Astor Tce | NCC Rating (A) | 525 | 525 | 525 | 525 | 525 | Urban | 70 | 17
|  |  |  | 10 POE Load (A) | 140 | 141 | 141 | 141 | 142
|  |  |  | Power Factor | 0.97453 | 0.97444 | 0.97444 | 0.97444 | 0.97435
|  |  |  | ECC Rating (A) | 525 | 525 | 525 | 525 | 525
|  |  |  | 50 POE Load (A) | 278 | 280 | 280 | 280 | 282
Victoria Park Bulk | 653-1 | Victoria Pk BS | Newmarket | NCC Rating (A) | 536 | 536 | 536 | 536 | 536 | Urban | 70
|  |  |  | 10 POE Load (A) | 158 | 159 | 159 | 158 | 160
|  |  |  | Power Factor | 0.99701 | 0.99698 | 0.99698 | 0.99701 | 0.99694
|  |  |  | ECC Rating (A) | 536 | 536 | 536 | 536 | 536
|  |  |  | 50 POE Load (A) | 300 | 300 | 300 | 300 | 303
Victoria Park Bulk | 689-1 | Victoria Pk BS | Astor Tce | NCC Rating (A) | 588 | 588 | 588 | 588 | 588 | Urban | 70
|  |  |  | 10 POE Load (A) | 9 | 9 | 9 | 9 | 9
|  |  |  | Power Factor | 1.0298e-05 | 1.0298e-05 | 1.0298e-05 | 1.0298e-05 | 1.0298e-05
|  |  |  | ECC Rating (A) | 588 | 588 | 588 | 588 | 588
|  |  |  | 50 POE Load (A) | 9 | 9 | 9 | 9 | 9