## Index
Index
Notes
ARG - Acacia Ridge (33/11kV)
ACR - Albany Creek (33/11kV)
AHD - Alexandra Headland (132/11kV)
AGT - Algester (33/11kV)
AMR - Amamoor (33/11kV)
ABY - Amberley (33/11kV)
AST - Ann St (110/11kV)
ALY - Annerley (33/11kV)
AHL - Arana Hills (33/11kV)
AFD - Archerfield (33/11kV)
ARL - Arundel (33/11kV)
AGE - Ashgrove (33/11kV)
ATC - Astor Terrace (33/11kV)
BHL - Bald Hills Bus 1 (33/11kV)
BHL - Bald Hills Bus 2 (33/11kV)
BDT - Beaudesert (33/11kV)
BLH - Beenleigh (33/11kV)
BLN - Beenleigh North (33/11kV)
BWH - Beerwah (33/11kV)
BBS - Belmont (33/11kV)
BTA - Bethania (33/11kV)
BKD - Birkdale (33/11kV)
BTY - Birtinya (132/11kV)
BMT - Black Mountain (33/11kV)
BNH - Boonah (33/11kV)
BVL - Booval (33/11kV)
BRD - Brendale (33/11kV)
BIS - Bribie Island (33/11kV)
BRT - Brighton (33/11kV)
BBH - Broadbeach (110/11kV)
BTN - Bromelton (33/11kV)
BPN - Browns Plains (33/11kV)
BLB - Bulimba (33/11kV)
BDL - Bundall (33/11kV)
BDB - Bundamba (110/11kV)
BDA - Buranda (33/11kV)
BHD - Burleigh Heads (110/11kV)
BGY - Burpengary (33/11kV)
CBT - Caboolture (33/11kV)
CBW - Caboolture West (33/11kV)
CCY - Cades County (110/11kV)
CMV - Calamvale (33/11kV)
CLD - Caloundra (132/11kV)
CHL - Camp Hill (33/11kV)
CPB - Capalaba (33/11kV)
CPS - Capalaba South (33/11kV)
CPK - Carole Park (33/11kV)
CPC - Carole Park Central (33/11kV)
CPD - Carpendale (33/11kV)
CST - Charlotte St (110/11kV)
CSE - Chermside (33/11kV)
CFD - Clayfield (33/11kV)
CVL - Cleveland (33/11kV)
CLM - Coolum (33/11kV)
CMA - Coomera (33/11kV)
CMY - Coominya (33/11kV)
CNA - Cooneana (33/11kV)
CPL - Coopers Plains (33/11kV)
COR - Cooran (132/11kV)
CRY - Cooroy (33/11kV)
CPR - Coorparoo (33/11kV)
CNB - Cornubia (33/11kV)
CRM - Crestmead (33/11kV)
CMD - Currimundi (132/11kV)
CRB - Currumbin (33/11kV)
DRA - Darra (33/11kV)
DBY - Deception Bay (33/11kV)
DBS - Doboy (33/11kV)
DRD - Duffield Road (33/11kV)
EMP - Eight Mile Plains Bus 1 (33/11kV)
EMP - Eight Mile Plains Bus 2 (33/11kV)
ENG - Enoggera (33/11kV)
ESK - Esk (33/11kV)
EMD - Eumundi (33/11kV)
FIS - Fisherman Is A (33/11kV)
FBS - Fisherman Is B (33/11kV)
FDS - Flinders (33/11kV)
GTN - Gatton A (33/11kV)
GVN - Gaven (33/11kV)
GBG - Geebung (33/11kV)
GIS - Gibson Island (33/11kV)
GGR - Glenore Grove (33/11kV)
GNA - Goodna (33/11kV)
GBN - Goomboorian (33/11kV)
GLY - Grovely (33/11kV)
GYM - Gympie (132/11kV)
GYN - Gympie North (33/11kV)
GYS - Gympie South (33/11kV)
HTN - Hamilton (33/11kV)
HTL - Hamilton Lands (33/11kV)
HWD - Heathwood (33/11kV)
HDN - Helidon (33/11kV)
HMT - Hemmant (33/11kV)
HDA - Hendra (33/11kV)
HPK - Holland Park (33/11kV)
HPE - Holland Park East (33/11kV)
HWL - Hollywell (33/11kV)
HIS - Hope Island (33/11kV)
IBS - Ibis (33/11kV)
IBL - Imbil (33/11kV)
INA - Inala (33/11kV)
IDY - Indooroopilly (33/11kV)
IPL - Innisplain (33/11kV)
IPS - Ipswich South (33/11kV)
JBB - Jimboomba (33/11kV)
JDL - Jindalee (33/11kV)
KBR - Kalbar (33/11kV)
KLG - Kallangur (33/11kV)
KBN - Karrabin (33/11kV)
KWA - Kawana (132/11kV)
KRN - Kedron (33/11kV)
KVG - Kelvin Grove (110/11kV)
KWH - Kenilworth (33/11kV)
KMR - Kenmore (33/11kV)
KCY - Kilcoy (33/11kV)
KSN - Kingston (33/11kV)
KRA - Kirra (33/11kV)
LDR - Labrador (33/11kV)
LLY - Laidley (33/11kV)
LBH - Landsborough (33/11kV)
LTN - Lawnton (33/11kV)
LRE - Lockrose (33/11kV)
LGV - Logan Village (33/11kV)
LHM - Loganholme (33/11kV)
LGL - Loganlea (33/11kV)
LTA - Lota (33/11kV)
LWD - Lowood (33/11kV)
LYT - Lytton (33/11kV)
LBS - Lytton B (33/11kV)
MST - Makerston St (110/11kV)
MLY - Maleny (33/11kV)
MHL - Mango Hill Bus 1 (33/11kV)
MHL - Mango Hill Bus 2 (33/11kV)
MBG - Marburg (33/11kV)
MLS - McLachlan St (110/11kV)
MDH - Meeandah (33/11kV)
MMC - Merrimac (110/11kV)
MAI - Miami (33/11kV)
MLT - Milton (110/11kV)
MGL - Moggill (33/11kV)
MDR - Molendinar (110/11kV)
MLB - Mooloolaba (132/11kV)
MRK - Moorooka (33/11kV)
MFD - Morayfield (33/11kV)
MFN - Morayfield North (33/11kV)
MCN - Mt Cotton (33/11kV)
MCW - Mt Crosby West (33/11kV)
MTG - Mt Gravatt (33/11kV)
MSV - Mt Sylvia (33/11kV)
MTB - Mt Tamborine Bus 1 (33/11kV)
MTB - Mt Tamborine Bus 2 (33/11kV)
MGP - Mudgeeraba West Pkg (33/11kV)
MRE - Murarrie (33/11kV)
MRB - Murrumba (33/11kV)
MTN - Myrtletown (33/11kV)
NBR - Nambour (33/11kV)
NRA - Narangba (33/11kV)
NRG - Nerang (110/11kV)
NMK - Newmarket (33/11kV)
NSD - Newstead (110/11kV)
NGI - Ningi (33/11kV)
NVL - Noosaville (132/11kV)
NMC - North Maclean (33/11kV)
NSW - North Springwood (110/11kV)
NIP - Nth Ipswich (33/11kV)
NPD - Nth Pine Dam (33/11kV)
NGE - Nudgee (33/11kV)
NDH - Nundah (33/11kV)
OXL - Oxley (33/11kV)
PBH - Palm Beach (33/11kV)
PWC - Palmwoods Central (33/11kV)
PKW - Parkwood (33/11kV)
PGN - Peregian (33/11kV)
PPE - Pimpama East (33/11kV)
PRG - Postmans Ridge (33/11kV)
QPT - Queensport (33/11kV)
RBY - Raby Bay (33/11kV)
RBK - Redbank (33/11kV)
RCF - Redcliffe (33/11kV)
RLB - Redland Bay (33/11kV)
RBA - Robina (110/11kV)
RLA - Rocklea (33/11kV)
RST - Roderick St (33/11kV)
RWD - Rosewood (33/11kV)
RCN - Runcorn (33/11kV)
RIS - Russell Island (110/11kV)
SBY - Salisbury (33/11kV)
SMF - Samford (33/11kV)
SGT - Sandgate (33/11kV)
SBH - Scarborough (33/11kV)
SRD - Scrub Road (33/11kV)
SHW - Sherwood (33/11kV)
SDM - Somerset Dam (33/11kV)
SPO - Southport (110/11kV)
SPC - Spring Creek (33/11kV)
SPF - Springfield (33/11kV)
SFC - Springfield Central (33/11kV)
STL - St Lucia (33/11kV)
SFD - Stafford (33/11kV)
STT - Stapylton (33/11kV)
SIS - Stradbroke Is (33/11kV)
SPE - Strathpine (33/11kV)
SMR - Sumner (110/11kV)
SBK - Sunnybank (33/11kV)
SPD - Surfers Paradise (110/11kV)
TBV - Tamborine Village (33/11kV)
TMH - Tanah Merah (33/11kV)
TRP - Tarampa (33/11kV)
TRG - Taringa (33/11kV)
TSN - Tennyson (33/11kV)
THL - Tenthill (33/11kV)
TWT - Tewantin (33/11kV)
GAP - The Gap (33/11kV)
TCB - Tin Can Bay (33/11kV)
TGP - Tingalpa (33/11kV)
TGW - Toogoolawah (33/11kV)
TPT - Toorbul Point (33/11kV)
TWG - Toowong (33/11kV)
UMG - Upper Mt Gravatt (33/11kV)
VSL - Varsity Lakes (110/11kV)
VPK - Victoria Park (110/11kV)
VPT - Victoria Point (33/11kV)
WCL - Wacol (33/11kV)
WSO - Wacol South (33/11kV)
WMR - Wamuran (33/11kV)
WRD - Wellington Rd (110/11kV)
WED - West End (110/11kV)
WMD - West Maroochydore (132/11kV)
WSS - Whinstanes (33/11kV)
WSE - Whiteside (33/11kV)
WHO - Wivenhoe (33/11kV)
WFD - Woodford (33/11kV)
WRG - Woodridge (33/11kV)
WNM - Wynnum (33/11kV)
YMT - Yamanto (33/11kV)
YDA - Yandina (33/11kV)
YTA - Yatala (110/11kV)
ZMR - Zillmere (33/11kV)

## Notes
Zone Substations Forecasts (Energex Distribution Annual Planning Report (2023-24 to 2027-28)
This workbook provides 5 year forecast capacity and loading information for Zone Substations in the Energex network.
Energex Distribution Annual Planning Report is prepared and made available solely for information purposes. While care was taken in the preparation of the information in this report, and it is provided in good faith, Energex accepts no responsibility or liability (including without limitation, liability to any person by reason of negligence or negligent mis-statement) for any loss or damage that may be incurred by any person acting in reliance on this information or assumptions drawn from it, except to the extent that liability under any applicable Queensland or Commonwealth of Australia statute cannot be excluded.
It contains assumptions regarding, among other things, economic growth and load forecasts which may or may not prove to be correct. The forecasts included in the document involve subjective judgements and analysis which are subject to significant uncertainties and contingencies, many of which are out of the control of Energex. Furthermore, forecasted data is subject to ongoing variation as new information becomes available. Energex makes no representation or warranty as to the accuracy, reliability, completeness or suitability for any particular purpose of the information in this document. All information should be independently investigated, reviewed, analysed and verified, and must not be relied upon in connection with any investment proposal or decision.
Each summary sheet contains a brief description of the substation, including its location, land area, construction type, installed transformers and capacity of known embedded generation connected to the substation. Localities give a general view of the areas serviced by the substation. Load categories indicate the type of loads supplied. Growth rates for the zone substations provide a projection of the expected growth rates for the next five years for planning purposes.
With respect to growth rates:
· Large individual or block loads (existing and new) are treated on an individual basis and not listed in these substation summaries, but these are factored into load forecasts.
The next section includes a summary of performance and capability.
The latest compensated peak demand is displayed along with the typical daily compensated load profile. In addition, the compensated descriptor refers to the slightly reduced transformer load experienced when available capacitors are in service. Entries in the major loads section indicate there are significant or large customers connected to the substation. Both summer and winter profiles are presented where available. Where a substation has less than 12 months of metering data available, such as small substations and newly established substations, the graphs and the information against these fields is either blank or not applicable (N/A).
The forecast and capacity accounts for committed projects, the project cut-off date for the winter season is 1 June of each year, and for the summer season is 1 December of each year. For example, 2024 winter forecast includes all committed projects with a proposed commissioning date up to 1 June 2024, and the 2023/24 summer forecast includes all committed projects with a proposed commissioning date up to 1 December 2023. The committed status of projects used in the forecast are taken as of 1 May 2023.
Term | Definition
Peak Risk Period | The time period over which the load is highest (Day/Night).
NCC Rating (MVA) | Normal Cyclic Capacity – the total capacity with all network components and equipment in service.
The maximum permissible peak daily loading for a given load cycle that plant can supply each day of its life. Taking impedance mismatch into consideration, it is considered the maximum rating for a transformer to be loaded under normal load conditions.
Contracted non-network (MVA) | The amount of embedded generation and contracted curtailed demand management capacity available within the supply area of a substation during peak times. The impacts of these have been incorporated into the load forecasts. Solar PV connections are not included in the reported figure.
10 PoE Load (MVA) | Peak load forecast with 10% probability of being exceeded (one in every 10 years will be exceeded). Based on normal expected growth rates & weather corrected starting loads.
LARn (MVA) | Security standard load at risk under system normal condition, expressed in MVA.
LARn (MW) | Security standard load at risk under system normal condition, expressed in MW.
Power Factor at Peak Load | Compensated power factor at 50 PoE Load. Capacitive compensation is switched according to the size of the capacitor banks installed at the substation, compensation is generally limited to prevent a substation from going into leading power factor.
ECC Rating (MVA) | Emergency Cyclic Capacity – the long term firm delivery capacity under a single contingent condition.
The maximum permissible peak emergency loading for a given load cycle that an item of plant can supply for an extended period of time without unacceptable damage. For substations with multiple transformers, the ECC is the minimum emergency cyclic capacity of all transformer combinations taking impedance mismatches into consideration, with one transformer off line.
50 PoE Load (MVA) | Peak load forecast with 50% probability of being exceeded (one in every two years will be exceeded). Based on normal expected growth rates and weather corrected starting loads.
50 PoE Load > 95% (MVA) | The amount of load greater than 95% 50 PoE Load.
(50 PoE Load – 0.95 x 50 PoE Load)
Hours PA > 95% Peak Load | The number of hours per annum (maximum over the last 3 years) where the load exceeded 95% of the peak 50 PoE demand.
Raw LAR (MVA) | The amount of load exceeding ECC rating.
(50 PoE Load – ECC Rating)
2-Hour Rating (MVA) | Two-Hour Emergency Capacity (2HEC) – the short term or firm delivery capacity under a single contingent condition.
The maximum permissible peak emergency loading for a given load cycle that an item of plant can supply up to two hours without causing unacceptable damage. For substations with multiple transformers, the 2HEC is the minimum two hour emergency rating of all transformer combinations taking impedance mismatches into consideration, with one transformer off line.
Auto Trans Avail (MVA) | SCADA or automatically controlled load transfers that can be implemented within one minute.
Remote Trans Avail (MVA) | Load transfers that can be implemented through SCADA switching procedures by the network control officer. It is assumed that this can generally be achieved within 30 minutes excluding complex or prolonged restoration procedures.
Manual Trans Avail (MVA) | Load transfers can also be deployed via manually controlled switchgear locally by field staff. It is assumed that the implementation of manual switching procedures to isolate the faulted portion of the network to restore supply to healthy parts of the network can be fully implemented within three hours (urban) or four hours (rural).
Manual transfers are obtained from load flow studies performed on each 11 kV distribution feeder, with the sum of all available 11 kV transfers at a substation is multiplied by a 0.75 factor to account for diversity and to provide a margin of error to avoid voltage collapse. The same approach applies throughout the forward planning period.
Mobile Plant Avail (MVA) | The capacity of mobile substation or mobile generation that can be deployed within the timeframe prescribed by the security standard.
The maximum allowable mobile generator capacity is limited to 4 MVA for urban and 10 MVA for rural. The maximum mobile substation capacity is 15 MVA.
POPS | Plant Overload Protection Scheme consists of several applications which continuously monitor specific items of plant for overload conditions. If overload conditions are detected and validated, POPS will initiate predefined actions in order to relieve the overload condition.
Bus Configuration | An indication of the electrical configuration of the substation 11 kV bus (e.g. split bus or solid bus)
Capacity for Embedded Generation (MVA) | The total capacity for embedded generation to transfer power from lower voltage network to higher voltage network with all network components and equipment in service.
N-1 Capacity for Embedded Generation (MVA) | The firm capacity for embedded generation to transfer power from lower voltage network to higher voltage network under a single contingent condition.
LARc (MVA) | Security standard load at risk for single contingent conditions.
LARc (MW) | Estimated generation / load reduction required to defer the forecast system limitation. This is the security standard load at risk for a single contingency, expressed in MW.
Customer Category | For security standard application, the general type of customer a substation or feeder supplying the area.
The load at risk is evaluated for both normal (LARn) and contingent (LARc) conditions. Under normal conditions, the loadings on a substation are not to exceed the normal cyclic capacity (NCC) of a major network component such as a zone substation transformer. Under contingent conditions, the loadings of a substation are not to exceed the available emergency supply under contingency whilst taking into consideration the security of supply standards of the substation.
Load at risk is the shortfall between the forecast load (either 10 PoE or 50 PoE) and the available supply. The general equations for LAR are as follows:
· LARn = 10 PoE – NCC where NCC is the normal cyclic capacity
· LARc = 50 PoE – available capacity – available supply (within security standard timeframe)
Network security standards are not being met if LARn or LARc is greater than 0.
Generally, there are two available capacities and five available sources of supply that can be deployed upon loss of a major network component such as a transformer.
Types of available capacity:
· Emergency Cyclic Capacity (ECC) – The maximum permissible peak emergency loading for a given load cycle that a plant can supply for an extended period of time without doing unacceptable damage. For substations with multiple transformers, the ECC is the minimum emergency cyclic capacity of all transformer combinations taking impedance mismatches into consideration, with one transformer off line.
· Two Hour Emergency Capacity (2HEC) – The maximum permissible peak emergency loading for a given load cycle that a plant can supply up to two hours without doing unacceptable damage. For substations with multiple transformer, the 2HEC is the minimum 2 hour emergency rating of all transformer combinations taking impedance mismatches into consideration, with one transformer off line. By the end of the 2 hours, the transformer load must be reduced to or below ECC.
Types of available supply:
· Automatic Transfers (AT) – SCADA or automatically controlled load transfers that can be implemented within 1 minute. Examples include auto changeover switching capacity from adjacent bus sections, standby transformers or via dedicated tie feeders from other substations. Such capacity has been considered at a number of substations where it is available.
· Remote Transfers (RT) – Load transfer capacity can be deployed via remotely controlled switchgear. The implementation of a series of SCADA controlled switching procedures to isolate the faulted portion of the network whilst restoring supply to fault free portions can be fully implemented within 30 minutes and is available for extended periods. At present, only remote transfers to other substations or standby transformers, using SCADA control of substation circuit breakers, have been considered.
· Manual Transfers (MT) – Load transfer capacity can be deployed via manually controlled switchgear. The implementation of a series of manual switching procedures to isolate the faulted portion of the network whilst restoring supply to fault free portions can be fully implemented within 3 hours (urban) or 4 hours (rural) and is available for extended periods. Some manual transfers are likely to be implemented within 2 hours but this has not been quantified at this time. Analysis done to identify the available 11 kV transfer capability in the systems for every substation. To accommodate future 11 kV network changes and system coincidence peak, a 75% factor is applied to ensure the transfers are practical and achievable throughout the analysis period. The manual switching of standby transformers, which do not have automatic switching, has also been included where available.
· Mobile Generation (MG) – Alternate supply from mobile generators can be sourced within 8 hours (urban) or 12 hours (rural). These are generally smaller 500 kVA units that do not require transport permits or police escorts and can be rapidly deployed. Up to 4 MVA (urban) or 10 MVA (rural) of mobile generation may be committed to a single contingency event.
· Mobile Substation (MS) – Alternate supply provided through deployment of a mobile substation within 8 hours (urban and non-urban) – only applies to 33/11 kV zone substation contingencies. These mobile substations generally do not require transport permits or police escorts and can be rapidly deployed. The standard size of the mobile substation transformer is 18 MVA however a capacity of 15 MVA is used in the assessment of zone substation security standard compliance. Use of the mobile substation may be committed to a single contingency event.
Back to Index

## ARG
Zone Summary Information and Peak Load Forecast
Substation | ARG - Acacia Ridge (33/11kV) | [5 empty] | Supply | AGT - Algester BS
Description | Land area is 4020 sqm, Construction is conventional all indoor class
Transformer size is 2x15/20MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.5% W 0.2%, 2025 S -1.3% W 0.3%,2026 S -0.7% W -0.2%2027 S -1.3% W -0.5
Load Category | Industrial
Localities | Supplies Acacia Ridge, Coopers Plains, Sunnybank, Sunnybank Hills
|  |  |  | Latest Peak Compensated Load |  |  |  | 16.3 MVA on 01/02/2023 at 15:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 41.9 | 41.9 | 41.9 | 41.9 | 41.9 | 41.9 | 41.9 | 41.9 | 41.9 | 41.9
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 18 | 17.7 | 17.6 | 17.4 | 17.3 | 16.8 | 16.9 | 16.9 | 16.9 | 16.8
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.999 | 1 | 1 | 1 | 1 | 0.965 | 0.965 | 0.965 | 0.965 | 0.965
ECC Rating (MVA) | 23 | 23 | 23 | 23 | 23 | 26 | 26 | 26 | 26 | 26
50 PoE Load (MVA) | 17.2 | 17.6 | 17.5 | 17.3 | 17.2 | 16 | 16 | 16.1 | 16.1 | 16
50 PoE Load > 95% (MVA) | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
Hours PA > 95% Peak Load | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5
Raw LAR (MVA)
2HR Rating (MVA) | 25 | 25 | 25 | 25 | 25 | 28 | 28 | 28 | 28 | 28
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95
N-1 Capacity for Embedded Generation (MVA) | 2.475 | 2.475 | 2.475 | 2.475 | 2.475 | 2.475 | 2.475 | 2.475 | 2.475 | 2.475
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## ACR
Zone Summary Information and Peak Load Forecast
Substation | ACR - Albany Creek (33/11kV) | [5 empty] | Supply | BRD - Brendale BS
Description | Land area is 3170 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x14.5/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.7% W -0.1%,2025 S -2.1% W 0.0%,2026 S -0.9% W -0.2%2027 S -1.5% W -0.4
Load Category | Domestic
Localities | Supplies Albany Creek, Bridgeman Downs, Bunya, Draper, Eatons Hill, Mcdowall
|  |  |  | Latest Peak Compensated Load |  |  |  | 27.3 MVA on 17/03/2023 at 16:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 28.7 | 28.1 | 27.9 | 27.5 | 27.4 | 21.8 | 21.8 | 21.8 | 21.7 | 21.6
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 30.5 | 30.5 | 30.5 | 30.5 | 30.5 | 33.5 | 33.5 | 33.5 | 33.5 | 33.5
50 PoE Load (MVA) | 27.1 | 26.5 | 26.3 | 25.9 | 25.8 | 19.8 | 19.8 | 19.8 | 19.7 | 19.6
50 PoE Load > 95% (MVA) | 1.4 | 1.3 | 1.3 | 1.3 | 1.3 | 1 | 1 | 1 | 1 | 1
Hours PA > 95% Peak Load | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5
Raw LAR (MVA)
2HR Rating (MVA) | 33.5 | 33.5 | 33.5 | 33.5 | 33.5 | 36.6 | 36.6 | 36.6 | 36.6 | 36.6
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
N-1 Capacity for Embedded Generation (MVA) | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## AHD
Zone Summary Information and Peak Load Forecast
Substation | AHD - Alexandra Headland (132/11kV) | [5 empty] | Supply | PWD - PALMWOODS 132 CP
Description | Land area is 4880 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x36/60MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.0% W 0.4%, 2025 S -2.2% W 0.4%,2026 S -1.5% W -0.2%2027 S -2.0% W -0.3
Load Category | Domestic
Localities | Supplies Alexandra Headland, Bli Bli, Buderim, Maroochydore, Minyama, Mooloolaba, Mountain Creek, Pacific Paradise, Parrearra, Twin Waters
|  |  |  | Latest Peak Compensated Load |  |  |  | 72.8 MVA on 03/02/2023 at 14:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 130.2 | 130.2 | 130.2 | 130.2 | 130.2 | 144 | 144 | 144 | 144 | 144
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 73.6 | 72 | 70.9 | 70.4 | 69.8 | 61.7 | 62 | 62.2 | 62.8 | 62.6
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.994 | 0.994 | 0.994 | 0.994 | 0.995 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998
ECC Rating (MVA) | 75.1 | 75.1 | 75.1 | 75.1 | 75.1 | 83.1 | 83.1 | 83.1 | 83.1 | 83.1
50 PoE Load (MVA) | 70.7 | 69.2 | 68.2 | 67.7 | 67.1 | 58.5 | 58.8 | 59 | 59.6 | 59.5
50 PoE Load > 95% (MVA) | 3.5 | 3.5 | 3.4 | 3.4 | 3.4 | 2.9 | 2.9 | 3 | 3 | 3
Hours PA > 95% Peak Load | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Raw LAR (MVA)
2HR Rating (MVA) | 83.8 | 83.8 | 83.8 | 83.8 | 83.8 | 91.5 | 91.5 | 91.5 | 91.5 | 91.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO
Capacity for Embedded Generation (MVA) | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
N-1 Capacity for Embedded Generation (MVA) | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## AGT
Zone Summary Information and Peak Load Forecast
Substation | AGT - Algester (33/11kV) | [5 empty] | Supply | AGT - Algester BS
Description | Land area is 39150 sqm, Construction is multiple modular class
Transformer size is 2x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 2.8 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.9% W 0.7%, 2025 S -1.7% W 1.0%,2026 S -0.7% W 0.6%,2027 S -0.3% W 1.3%
Load Category | Mixed Domestic
Localities | Supplies Acacia Ridge, Algester, Larapinta, Pallara, Sunnybank Hills, Willawong
|  |  |  | Latest Peak Compensated Load |  |  |  | 21.5 MVA on 17/03/2023 at 15:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Day | Day | Day | Day
NCC Rating (MVA) | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 22.5 | 22.1 | 22 | 21.9 | 22.1 | 18.5 | 18.6 | 18.8 | 18.9 | 19.2
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.984 | 0.984 | 0.984 | 0.984 | 0.984 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
ECC Rating (MVA) | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5
50 PoE Load (MVA) | 20.5 | 20.1 | 20 | 19.9 | 20.1 | 17.2 | 17.3 | 17.5 | 17.6 | 17.8
50 PoE Load > 95% (MVA) | 1 | 1 | 1 | 1 | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Hours PA > 95% Peak Load | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Raw LAR (MVA)
2HR Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## AMR
Zone Summary Information and Peak Load Forecast
Substation | AMR - Amamoor (33/11kV) | [5 empty] | Supply | GYM - Gympie BS
Description | Land area is 4050 sqm, Construction is pipework and shed class
Transformer size is 1x5/8MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.2% W -0.5%,2025 S -1.5% W -0.3%2026 S -0.8% W -0.6%2027 S -1.5% W -0.8
Load Category | Domestic
Localities | Supplies Amamoor, Amamoor Creek, Bollier, Calico Creek, Coles Creek, Cooran, Dagun, Gilldora, Imbil, Jones Hill, Kandanga, Kandanga Creek, Kybong, Lagoon Pocket, Langshaw, Long Flat, Melawondi, Mooloo, The Dawn, Traveston, Tuchekoi, Upper Kandanga
|  |  |  | Latest Peak Compensated Load |  |  |  | 5.7 MVA on 04/07/2022 at 17:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 5.4 | 5.3 | 5.2 | 5.2 | 5.1 | 5.9 | 5.8 | 5.8 | 5.8 | 5.7
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.987 | 0.987 | 0.987 | 0.987 | 0.987 | 0.994 | 0.994 | 0.994 | 0.994 | 0.994
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 5 | 4.9 | 4.9 | 4.8 | 4.8 | 5.5 | 5.4 | 5.4 | 5.4 | 5.3
50 PoE Load > 95% (MVA) | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Hours PA > 95% Peak Load | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
Raw LAR (MVA) | 5 | 4.9 | 4.9 | 4.8 | 4.8 | 5.5 | 5.4 | 5.4 | 5.4 | 5.3
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3
Mobile Plant Avail (MVA) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## ABY
Zone Summary Information and Peak Load Forecast
Substation | ABY - Amberley (33/11kV) | [5 empty] | Supply | ABM - Abermain BS
Description | Land area is 5604 sqm, Construction is single modular class
Transformer size is 1x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.9 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.5% W 0.8%, 2025 S -1.3% W 0.9%,2026 S -0.6% W 0.4%,2027 S -1.0% W 0.5%
Load Category | Industrial
Localities | Supplies Amberley
|  |  |  | Latest Peak Compensated Load |  |  |  | 2 MVA on 17/03/2023 at 17:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 26.3 | 26.3 | 26.3 | 26.3 | 26.3 | 26.3 | 26.3 | 26.3 | 26.3 | 26.3
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 1.7 | 1.7 | 1.7 | 1.8 | 1.8
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.981 | 0.981 | 0.981 | 0.981 | 0.981 | 0.978 | 0.978 | 0.978 | 0.978 | 0.978
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
50 PoE Load > 95% (MVA) | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Hours PA > 95% Peak Load | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
Raw LAR (MVA) | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4
Mobile Plant Avail (MVA) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## AST
Zone Summary Information and Peak Load Forecast
Substation | AST - Ann St (110/11kV) | [5 empty] | Supply | BMH - BELMONT 110 CP
Description | Land area is 1563 sqm, Construction is conventional all indoor class
Transformer size is 3x36/60MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 17.1 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.2% W 0.0%, 2025 S -1.5% W 0.2%,2026 S -0.9% W -0.4%2027 S -1.5% W -0.6
Load Category | Industrial
Localities | Supplies Brisbane City, Spring Hill
|  |  |  | Latest Peak Compensated Load |  |  |  | 38.8 MVA on 13/02/2023 at 08:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Day | Day | Day | Day
NCC Rating (MVA) | 188.1 | 188.1 | 188.1 | 188.1 | 188.1 | 188.1 | 188.1 | 188.1 | 188.1 | 188.1
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 41.4 | 43.7 | 43.3 | 51.4 | 51.2 | 25.8 | 25.8 | 27.8 | 31.6 | 33.2
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 1 | 1 | 1 | 0.999 | 0.999 | 0.993 | 0.993 | 0.993 | 0.993 | 1
ECC Rating (MVA) | 137.2 | 137.2 | 137.2 | 137.2 | 137.2 | 155.1 | 155.1 | 155.1 | 155.1 | 155.1
50 PoE Load (MVA) | 40.2 | 42.3 | 42 | 50.1 | 49.9 | 25.3 | 25.3 | 27.3 | 31.1 | 32.6
50 PoE Load > 95% (MVA) | 2 | 2.1 | 2.1 | 2.5 | 2.5 | 1.3 | 1.3 | 1.4 | 1.6 | 1.6
Hours PA > 95% Peak Load | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
Raw LAR (MVA)
2HR Rating (MVA) | 149.1 | 149.1 | 149.1 | 149.1 | 149.1 | 167 | 167 | 167 | 167 | 167
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Mobile Plant Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108
N-1 Capacity for Embedded Generation (MVA) | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
LARc (MVA)
LARc (MW)
Customer Category | CBD | CBD | CBD | CBD | CBD | CBD | CBD | CBD | CBD | CBD
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## ALY
Zone Summary Information and Peak Load Forecast
Substation | ALY - Annerley (33/11kV) | [5 empty] | Supply | TSN - Tennyson BS
Description | Land area is 1370 sqm, Construction is conventional all indoor class
Transformer size is 2x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.8% W 0.9%, 2025 S -0.9% W 1.0%,2026 S 0.0% W 0.5%, 2027 S -0.8% W 0.2%
Load Category | Domestic
Localities | Supplies Annerley, Dutton Park, Fairfield, Greenslopes, Moorooka, Woolloongabba, Yeronga
|  |  |  | Latest Peak Compensated Load |  |  |  | 16.5 MVA on 17/03/2023 at 16:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 59.2 | 59.2 | 59.2 | 59.2 | 59.2 | 59.2 | 59.2 | 59.2 | 59.2 | 59.2
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 17.7 | 17.6 | 17.6 | 17.5 | 17.5 | 15.4 | 15.6 | 15.7 | 15.8 | 15.8
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
50 PoE Load (MVA) | 16.9 | 16.8 | 16.8 | 16.6 | 16.7 | 14.6 | 14.7 | 14.8 | 14.9 | 15
50 PoE Load > 95% (MVA) | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8
Hours PA > 95% Peak Load | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Raw LAR (MVA)
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## AHL
Zone Summary Information and Peak Load Forecast
Substation | AHL - Arana Hills (33/11kV) | [5 empty] | Supply | BRD - Brendale BS
Description | Land area is 3780 sqm, Construction is pipework and shed class
Transformer size is 2x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.3% W 0.2%, 2025 S -1.4% W 0.3%,2026 S -0.7% W -0.2%2027 S -1.2% W -0.2
Load Category | Domestic
Localities | Supplies Albany Creek, Arana Hills, Bridgeman Downs, Bunya, Everton Hills, Everton Park, Ferny Grove, Ferny Hills, Keperra, Mcdowall, Mitchelton
|  |  |  | Latest Peak Compensated Load |  |  |  | 32.7 MVA on 17/03/2023 at 16:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 35.4 | 34.9 | 34.6 | 34.2 | 34.1 | 29.3 | 29.3 | 29.4 | 29.4 | 29.3
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
50 PoE Load (MVA) | 33.5 | 33 | 32.8 | 32.4 | 32.3 | 27.2 | 27.2 | 27.3 | 27.3 | 27.2
50 PoE Load > 95% (MVA) | 1.7 | 1.7 | 1.6 | 1.6 | 1.6 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
Hours PA > 95% Peak Load | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
Raw LAR (MVA) | SUMMER 2023/24: 2.2; SUMMER 2024/25: 1.7; SUMMER 2025/26: 1.5; SUMMER 2026/27: 1.1; SUMMER 2027/28: 1
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## AFD
Zone Summary Information and Peak Load Forecast
Substation | AFD - Archerfield (33/11kV) | [5 empty] | Supply | AFD - Archerfield BS
Description | Land area is 12540 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.4% W -0.9%,2025 S -2.9% W -1.4%2026 S -2.3% W -2.1%2027 S -3.0% W -2.3
Load Category | Industrial
Localities | Supplies Archerfield, Rocklea
|  |  |  | Latest Peak Compensated Load |  |  |  | 20.8 MVA on 13/02/2023 at 11:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Day | Day | Day | Day
NCC Rating (MVA) | 54.3 | 54.3 | 54.3 | 54.3 | 54.3 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 20.7 | 20.1 | 20.3 | 19.7 | 19.4 | 19.3 | 19.2 | 18.9 | 18.5 | 18.1
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 1 | 1 | 0.964 | 0.964 | 0.964 | 0.972 | 0.972 | 0.972 | 0.972 | 0.972
ECC Rating (MVA) | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 31.6 | 31.6 | 31.6 | 31.6 | 31.6
50 PoE Load (MVA) | 20 | 20.1 | 19.6 | 19.1 | 18.7 | 18.5 | 18.4 | 18.1 | 17.7 | 17.3
50 PoE Load > 95% (MVA) | 1 | 1 | 1 | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Hours PA > 95% Peak Load | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
Raw LAR (MVA)
2HR Rating (MVA) | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 34.8 | 34.8 | 34.8 | 34.8 | 34.8
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## ARL
Zone Summary Information and Peak Load Forecast
Substation | ARL - Arundel (33/11kV) | [5 empty] | Supply | MDR - Molendinar BS
Description | Land area is 3810 sqm, Construction is multiple modular class
Transformer size is 2x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 2.4 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.1% W -1.2%,2025 S -3.3% W -1.1%2026 S -1.2% W -0.8%2027 S -1.8% W -0.9
Load Category | Mixed Domestic
Localities | Supplies Arundel, Biggera Waters, Coombabah, Helensvale, Molendinar, Parkwood, Southport
|  |  |  | Latest Peak Compensated Load |  |  |  | 20.1 MVA on 17/03/2023 at 16:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Day | Day | Day | Day
NCC Rating (MVA) | 53.2 | 53.2 | 53.2 | 53.2 | 53.2 | 53.2 | 53.2 | 53.2 | 53.2 | 53.2
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 23.2 | 22.4 | 22.2 | 21.8 | 21.7 | 17.9 | 17.7 | 17.5 | 17.4 | 17.2
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.991 | 0.991 | 0.991 | 0.991 | 0.991 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
ECC Rating (MVA) | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5
50 PoE Load (MVA) | 21.9 | 21.2 | 21 | 20.6 | 20.6 | 17.3 | 17.1 | 16.9 | 16.7 | 16.6
50 PoE Load > 95% (MVA) | 1.1 | 1.1 | 1.1 | 1 | 1 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8
Hours PA > 95% Peak Load | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
Raw LAR (MVA)
2HR Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## AGE
Zone Summary Information and Peak Load Forecast
Substation | AGE - Ashgrove (33/11kV) | [5 empty] | Supply | AGW - Ashgrove West BS
Description | Land area is 3660 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.4% W 0.3%, 2025 S -1.7% W 0.4%,2026 S -0.9% W 0.2%,2027 S -1.4% W 0.2%
Load Category | Domestic
Localities | Supplies Ashgrove, Bardon, Enoggera, Newmarket, Paddington, Red Hill, The Gap
|  |  |  | Latest Peak Compensated Load |  |  |  | 25.1 MVA on 17/03/2023 at 16:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 59.9 | 59.9 | 59.9 | 59.9 | 59.9 | 59.9 | 59.9 | 59.9 | 59.9 | 59.9
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 26.1 | 25.7 | 25.5 | 25.1 | 25.2 | 21 | 21.1 | 21.2 | 21.2 | 21.3
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998
ECC Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
50 PoE Load (MVA) | 24.5 | 24.1 | 23.9 | 23.6 | 23.6 | 20.2 | 20.3 | 20.4 | 20.4 | 20.4
50 PoE Load > 95% (MVA) | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1 | 1 | 1 | 1 | 1
Hours PA > 95% Peak Load | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5
Raw LAR (MVA)
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## ATC
Zone Summary Information and Peak Load Forecast
Substation | ATC - Astor Terrace (33/11kV) | [5 empty] | Supply | VPK - Victoria Park BS
Description | Land area is 810 sqm, Construction is conventional all indoor class
Transformer size is 2x15/25MVA ONAN/ODAF;1x15/25MVA ONAN/ODAF(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.7% W 0.7%, 2025 S -1.2% W 0.6%,2026 S -0.6% W 0.0%,2027 S -1.3% W -0.3
Load Category | Industrial
Localities | Supplies Brisbane City, Fortitude Valley, Spring Hill
|  |  |  | Latest Peak Compensated Load |  |  |  | 24.2 MVA on 13/02/2023 at 13:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Day | Day | Day | Day
NCC Rating (MVA) | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 25.5 | 25.2 | 25 | 24.7 | 24.6 | 16.1 | 16.2 | 16.3 | 16.3 | 16.3
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 1 | 1 | 1 | 1 | 1 | 0.987 | 0.987 | 0.987 | 0.987 | 0.987
ECC Rating (MVA) | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5
50 PoE Load (MVA) | 24.4 | 24.1 | 24.6 | 24.3 | 24.2 | 15.8 | 15.9 | 16 | 16 | 16
50 PoE Load > 95% (MVA) | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
Hours PA > 95% Peak Load | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
Raw LAR (MVA)
2HR Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
Auto Trans Avail (MVA) | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## BHL
Zone Summary Information and Peak Load Forecast
Substation | BHL - Bald Hills Bus 1 (33/11kV) | [5 empty] | Supply | SGT - Sandgate BS
Description | Land area is 3640 sqm, Construction is conventional all indoor class
Transformer size is 1x10.0MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.9% W 0.1%, 2025 S -1.8% W 0.3%,2026 S -1.2% W -0.2%2027 S -1.7% W -0.3
Load Category | Domestic
Localities | Supplies Bald Hills, Bracken Ridge, Bridgeman Downs, Carseldine
|  |  |  | Latest Peak Compensated Load |  |  |  | 9.5 MVA on 17/03/2023 at 17:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Day | Day | Day | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 10.1 | 9.9 | 9.8 | 9.6 | 9.6 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 1 | 1 | 1 | 1 | 1 | 0.995 | 0.995 | 0.995 | 0.995 | 0.995
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 9.4 | 9.2 | 9.1 | 8.9 | 8.9 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8
50 PoE Load > 95% (MVA) | 0.5 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Hours PA > 95% Peak Load | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5
Raw LAR (MVA) | 9.4 | 9.2 | 9.1 | 8.9 | 8.9 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 20.4 | 20.7 | 20.9 | 21.2 | 21.4 | 28.1 | 28.1 | 28.1 | 28.1 | 28.2
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO
Capacity for Embedded Generation (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## BHL2
Zone Summary Information and Peak Load Forecast
Substation | BHL - Bald Hills Bus 2 (33/11kV) | [5 empty] | Supply | BRD - Brendale BS
Description | Land area is 3640 sqm, Construction is conventional all indoor class
Transformer size is 1x20/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 1.8% W -0.1%,2025 S -3.2% W 0.0%,2026 S -2.6% W -0.6%2027 S -2.9% W -0.6
Load Category | Domestic
Localities | Supplies Bald Hills, Bracken Ridge, Bridgeman Downs, Carseldine
|  |  |  | Latest Peak Compensated Load |  |  |  | 11.7 MVA on 17/03/2023 at 16:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 12.3 | 11.9 | 11.6 | 11.3 | 11.2 | 7.5 | 7.5 | 7.5 | 7.5 | 7.4
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.992 | 0.992 | 0.992 | 0.992 | 0.992 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 11 | 10.6 | 10.4 | 10.1 | 10 | 6.9 | 6.9 | 6.9 | 6.9 | 6.8
50 PoE Load > 95% (MVA) | 0.6 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Hours PA > 95% Peak Load | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
Raw LAR (MVA) | 11 | 10.6 | 10.4 | 10.1 | 10 | 6.9 | 6.9 | 6.9 | 6.9 | 6.8
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 3.2 | 3.3 | 3.4 | 3.6 | 3.7 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO
Capacity for Embedded Generation (MVA) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## BDT
Zone Summary Information and Peak Load Forecast
Substation | BDT - Beaudesert (33/11kV) | [5 empty] | Supply | BDS - Beaudesert BS
Description | Land area is 6070 sqm, Construction is pipework and shed class
Transformer size is 1x15/25MVA ONAN/ODAF;1x15/25MVA ONAN/ODAF(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 4.0% W 2.5%, 2025 S 0.8% W 2.1%, 2026 S 1.3% W 1.4%, 2027 S 0.6% W 1.2%
Load Category | Domestic
Localities | Supplies Allenview, Beaudesert, Benobble, Biddaddaba, Birnam, Boyland, Cainbable, Canungra, Cedar Vale, Cryna, Darlington, Gleneagle, Josephville, Kerry, Mundoolun, Nindooinbah, Sarabah, Tabragalba, Tamborine Mountain, Veresdale, Veresdale Scrub, Woodhill
|  |  |  | Latest Peak Compensated Load |  |  |  | 17.7 MVA on 03/02/2023 at 15:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 18.6 | 18.8 | 19 | 19.1 | 19.4 | 14.1 | 14.5 | 14.8 | 15 | 15.2
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.976 | 0.976 | 0.976 | 0.976 | 0.976 | 0.992 | 0.992 | 0.992 | 0.992 | 0.992
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 17.7 | 17.9 | 18.1 | 18.2 | 18.5 | 13.6 | 13.9 | 14.2 | 14.4 | 14.6
50 PoE Load > 95% (MVA) | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Hours PA > 95% Peak Load | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
Raw LAR (MVA) | 17.7 | 17.9 | 18.1 | 18.2 | 18.5 | 13.6 | 13.9 | 14.2 | 14.4 | 14.6
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 23.8 | 23.8 | 23.8 | 23.8 | 23.8 | 25 | 25 | 25 | 25 | 25
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1
Mobile Plant Avail (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## BLH
Zone Summary Information and Peak Load Forecast
Substation | BLH - Beenleigh (33/11kV) | [5 empty] | Supply | BLH - Beenleigh BS
Description | Land area is 32220 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x15/25MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 2.8 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.7% W -0.6%,2025 S -2.3% W -0.8%2026 S -1.5% W -1.2%2027 S -1.4% W -1.1
Load Category | Mixed Industrial
Localities | Supplies Alberton, Bahrs Scrub, Bannockburn, Beenleigh, Belivah, Carbrook, Cedar Creek, Eagleby, Luscombe, Mount Warren Park, Stapylton, Tamborine, Windaroo, Wolffdene, Woongoolba, Yatala
|  |  |  | Latest Peak Compensated Load |  |  |  | 34.2 MVA on 17/03/2023 at 17:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 54.9 | 54.9 | 54.9 | 54.9 | 54.9 | 54.9 | 54.9 | 54.9 | 54.9 | 54.9
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 36 | 35.1 | 34.6 | 34.1 | 34 | 28 | 27.8 | 27.6 | 27.2 | 26.9
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
ECC Rating (MVA) | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5
50 PoE Load (MVA) | 32.9 | 32.1 | 31.6 | 31.2 | 31.1 | 26.5 | 26.4 | 26.2 | 25.8 | 25.6
50 PoE Load > 95% (MVA) | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
Hours PA > 95% Peak Load | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
Raw LAR (MVA) | SUMMER 2023/24: 4.1; SUMMER 2024/25: 3.3; SUMMER 2025/26: 2.8; SUMMER 2026/27: 2.4; SUMMER 2027/28: 2.3
2HR Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## BLN
Zone Summary Information and Peak Load Forecast
Substation | BLN - Beenleigh North (33/11kV) | [5 empty] | Supply | BLH - Beenleigh BS
Description | Land area is 1389 sqm, Construction is single modular class
Transformer size is 1x15/25MVA ONAN/ODAF;1x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.2% W 0.7%, 2025 S -0.9% W 0.8%,2026 S -0.3% W 0.2%,2027 S -0.5% W 0.4%
Load Category | Mixed Industrial
Localities | Supplies Beenleigh, Holmview
|  |  |  | Latest Peak Compensated Load |  |  |  | 19.5 MVA on 17/03/2023 at 17:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 54.5 | 54.5 | 54.5 | 54.5 | 54.5 | 54.5 | 54.5 | 54.5 | 54.5 | 54.5
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 20.1 | 19.9 | 19.8 | 19.7 | 19.7 | 18.5 | 18.6 | 18.7 | 18.8 | 18.9
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.991 | 0.991 | 0.991 | 0.991 | 0.991 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
ECC Rating (MVA) | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5
50 PoE Load (MVA) | 19 | 18.8 | 18.7 | 18.6 | 18.6 | 17.8 | 17.9 | 18 | 18.1 | 18.1
50 PoE Load > 95% (MVA) | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Hours PA > 95% Peak Load | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
Raw LAR (MVA)
2HR Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## BWH
Zone Summary Information and Peak Load Forecast
Substation | BWH - Beerwah (33/11kV) | [5 empty] | Supply | BWH - Beerwah BS
Description | Land area is 4050 sqm, Construction is pipework and shed class
Transformer size is 2x15/25MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.2% W -0.3%,2025 S -1.0% W 0.0%,2026 S -0.4% W -0.6%2027 S -1.5% W -1.3
Load Category | Domestic
Localities | Supplies Bald Knob, Beerburrum, Beerwah, Booroobin, Coochin Creek, Crohamhurst, Glass House Mountains, Maleny, Mount Mellum, Peachester, Wootha
|  |  |  | Latest Peak Compensated Load |  |  |  | 16.4 MVA on 13/02/2023 at 17:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 57.2 | 57.2 | 57.2 | 57.2 | 57.2 | 60 | 60 | 60 | 60 | 60
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 19.3 | 19.1 | 19 | 18.7 | 18.6 | 15.7 | 15.7 | 15.7 | 15.6 | 15.4
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.993 | 0.993 | 0.993 | 0.993 | 0.993 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 33.5 | 33.5 | 33.5 | 33.5 | 33.5
50 PoE Load (MVA) | 17.4 | 17.2 | 17.2 | 16.9 | 16.8 | 14.4 | 14.4 | 14.4 | 14.3 | 14.1
50 PoE Load > 95% (MVA) | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Hours PA > 95% Peak Load | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
Raw LAR (MVA)
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7
Mobile Plant Avail (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## BBS
Zone Summary Information and Peak Load Forecast
Substation | BBS - Belmont (33/11kV) | [5 empty] | Supply | BBS - Belmont BS
Description | Land area is 4060 sqm, Construction is conventional indoor/outdoor class
Transformer size is 1x12.5/17.0MVA ONAN/ONAF;1x15/25MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 3.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 1.7% W 0.1%, 2025 S -3.1% W 0.4%,2026 S -1.7% W -0.1%2027 S -1.5% W 0.0%
Load Category | Domestic
Localities | Supplies Belmont, Burbank, Carina Heights, Carindale, Chandler, Mackenzie, Mansfield, Rochedale, Wishart
|  |  |  | Latest Peak Compensated Load |  |  |  | 20.3 MVA on 17/03/2023 at 17:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 21.1 | 20.5 | 20.1 | 19.8 | 19.7 | 16.1 | 16.1 | 16.1 | 16.1 | 16.1
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 19.1 | 19.1 | 19.1 | 19.1 | 19.1 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4
50 PoE Load (MVA) | 18.9 | 18.3 | 18 | 17.7 | 17.6 | 15.1 | 15.1 | 15.2 | 15.2 | 15.2
50 PoE Load > 95% (MVA) | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
Hours PA > 95% Peak Load | bar: SUMMER 2023/24 to WINTER 2027
Raw LAR (MVA)
2HR Rating (MVA) | 23 | 23 | 23 | 23 | 23 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5
N-1 Capacity for Embedded Generation (MVA) | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## BTA
Zone Summary Information and Peak Load Forecast
Substation | BTA - Bethania (33/11kV) | [5 empty] | Supply | BLH - Beenleigh BS
Description | Land area is 4000 sqm, Construction is multiple modular class
Transformer size is 1x15/20MVA ONAN/ONAF;1x15/25MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.9% W 0.4%, 2025 S -0.7% W 0.5%,2026 S -0.1% W -0.1%2027 S -0.7% W -0.1
Load Category | Domestic
Localities | Supplies Bahrs Scrub, Beenleigh, Bethania, Buccan, Edens Landing, Holmview, Waterford, Waterford West
|  |  |  | Latest Peak Compensated Load |  |  |  | 22.5 MVA on 17/03/2023 at 19:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 47.8 | 47.8 | 47.8 | 47.8 | 47.8 | 47.8 | 47.8 | 47.8 | 47.8 | 47.8
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 24.5 | 24.4 | 24.3 | 24.2 | 24.2 | 18.5 | 18.5 | 18.6 | 18.6 | 18.6
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 25 | 25 | 25 | 25 | 25 | 28 | 28 | 28 | 28 | 28
50 PoE Load (MVA) | 22.4 | 22.3 | 22.2 | 22.1 | 22.1 | 16.8 | 16.9 | 17 | 17 | 17
50 PoE Load > 95% (MVA) | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9
Hours PA > 95% Peak Load | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Raw LAR (MVA)
2HR Rating (MVA) | 27 | 27 | 27 | 27 | 27 | 30 | 30 | 30 | 30 | 30
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## BKD
Zone Summary Information and Peak Load Forecast
Substation | BKD - Birkdale (33/11kV) | [5 empty] | Supply | CVL - Cleveland BS
Description | Land area is 9290 sqm, Construction is multiple modular class
Transformer size is 2x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 1.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.5% W 0.0%, 2025 S -1.2% W 0.1%,2026 S -0.5% W -0.4%2027 S -1.2% W -0.6
Load Category | Domestic
Localities | Supplies Alexandra Hills, Birkdale, Thorneside, Wellington Point
|  |  |  | Latest Peak Compensated Load |  |  |  | 30.4 MVA on 03/02/2023 at 19:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 59.9 | 59.9 | 59.9 | 59.9 | 59.9 | 59.9 | 59.9 | 59.9 | 59.9 | 59.9
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 33.8 | 33.4 | 33.2 | 32.8 | 32.7 | 28.9 | 28.9 | 29 | 28.9 | 28.7
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
50 PoE Load (MVA) | 31.4 | 31.1 | 30.9 | 30.5 | 30.4 | 26.6 | 26.6 | 26.6 | 26.5 | 26.4
50 PoE Load > 95% (MVA) | 1.6 | 1.6 | 1.5 | 1.5 | 1.5 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
Hours PA > 95% Peak Load | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Raw LAR (MVA) | SUMMER 2023/24: 0.1
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## BTY
Zone Summary Information and Peak Load Forecast
Substation | BTY - Birtinya (132/11kV) | [5 empty] | Supply | PWD - PALMWOODS 132 CP
Description | Construction is conventional all indoor class
Transformer size is 2x15/20/30MVA ONAN/ODAN/ODAF 132/11kV
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.8% W 0.6%, 2025 S -0.9% W 0.8%,2026 S -0.2% W 0.3%,2027 S -0.7% W 0.1%
Load Category | Mixed Domestic
Localities | Supplies Birtinya, Currimundi, Meridan Plains, Wurtulla
|  |  |  | Latest Peak Compensated Load |  |  |  | 20.5 MVA on 13/02/2023 at 17:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 21.7 | 21.5 | 21.4 | 21.3 | 21.3 | 19.3 | 19.4 | 19.5 | 19.6 | 19.6
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 1 | 1 | 1 | 1 | 1 | 0.996 | 0.996 | 0.996 | 0.996 | 0.996
ECC Rating (MVA) | 34.5 | 34.5 | 34.5 | 34.5 | 34.5 | 39 | 39 | 39 | 39 | 39
50 PoE Load (MVA) | 20.5 | 20.3 | 20.3 | 20.1 | 20.2 | 18 | 18.1 | 18.3 | 18.3 | 18.4
50 PoE Load > 95% (MVA) | 1 | 1 | 1 | 1 | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Hours PA > 95% Peak Load | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5
Raw LAR (MVA)
2HR Rating (MVA) | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 42 | 42 | 42 | 42 | 42
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## BMT
Zone Summary Information and Peak Load Forecast
Substation | BMT - Black Mountain (33/11kV) | [5 empty] | Supply | SRH - Sunrise Hills BS
Description | Land area is 3830 sqm, Construction is pipework and shed class
Transformer size is 1x5/8MVA ONAN/ONAF 33/11kV
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.5% W -0.3%,2025 S -1.3% W -0.3%2026 S -0.6% W -0.2%2027 S -1.4% W -0.4
Load Category | Domestic
Localities | Supplies Belli Park, Black Mountain, Bollier, Boreen Point, Carters Ridge, Como, Cooran, Cooroy, Cootharaba, Federal, Kin Kin, Lake Macdonald, Pinbarren, Pomona, Ridgewood, Ringtail Creek, Toolara Forest, Tuchekoi
|  |  |  | Latest Peak Compensated Load |  |  |  | 6.1 MVA on 12/02/2023 at 16:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 6.9 | 6.8 | 6.7 | 6.6 | 6.6 | 5 | 5 | 5 | 5 | 5
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.994 | 0.994 | 0.994 | 0.994 | 0.994 | 0.991 | 0.991 | 0.991 | 0.991 | 0.991
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 6.3 | 6.2 | 6.2 | 6.1 | 6.1 | 4.9 | 4.9 | 4.8 | 4.8 | 4.8
50 PoE Load > 95% (MVA) | 6.3 | 6.2 | 6.2 | 6.1 | 6.1 | 4.9 | 4.9 | 4.8 | 4.8 | 4.8
Hours PA > 95% Peak Load | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
Raw LAR (MVA)
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3
Mobile Plant Avail (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
N-1 Capacity for Embedded Generation (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## BNH
Zone Summary Information and Peak Load Forecast
Substation | BNH - Boonah (33/11kV) | [5 empty] | Supply | RVW - Raceview BS
Description | Land area is 5030 sqm, Construction is mini-modular (skid) class
Transformer size is 1x5/8MVA ONAN/ONAF(Standby);1x15MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.4% W 0.2%, 2025 S -1.3% W 0.3%,2026 S -0.6% W -0.2%2027 S -1.3% W -0.4
Load Category | Domestic
Localities | Supplies Boonah, Bunburra, Bunjurgen, Burnett Creek, Cannon Creek, Carneys Creek, Charlwood, Coochin, Coulson, Croftby, Dugandan, Frenches Creek, Hoya, Kents Pocket, Milford, Moogerah, Mount Alford, Mount French, Templin, Wallaces Creek
|  |  |  | Latest Peak Compensated Load |  |  |  | 7.2 MVA on 12/02/2023 at 18:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 8.2 | 8.1 | 8 | 7.9 | 7.9 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.995 | 0.995 | 0.995 | 0.995 | 0.995 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 7.5 | 7.4 | 7.4 | 7.3 | 7.2 | 5.8 | 5.8 | 5.8 | 5.8 | 5.7
50 PoE Load > 95% (MVA) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Hours PA > 95% Peak Load | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5
Raw LAR (MVA) | 7.5 | 7.4 | 7.4 | 7.3 | 7.2 | 5.8 | 5.8 | 5.8 | 5.8 | 5.7
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 10 | 10 | 10 | 10 | 10 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1
Mobile Plant Avail (MVA) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
N-1 Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## BVL
Zone Summary Information and Peak Load Forecast
Substation | BVL - Booval (33/11kV) | [5 empty] | Supply | RVW - Raceview BS
Description | Land area is 2023 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x10MVA;1x14.5/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 1.4 MVA
Growth Rates | 2023 W 1.0%, 2024 S 5.2% W 2.9%, 2025 S 0.0% W 2.8%, 2026 S 0.8% W 2.3%, 2027 S 0.6% W 1.9%
Load Category | Domestic
Localities | Supplies Basin Pocket, Blackstone, Booval, Bundamba, East Ipswich, Eastern Heights, Ebbw Vale, Flinders View, Ipswich, Karalee, New Chum, Newtown, North Booval, North Tivoli, Raceview, Silkstone
|  |  |  | Latest Peak Compensated Load |  |  |  | 27.4 MVA on 03/02/2023 at 17:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 37.2 | 37.2 | 37.2 | 37.2 | 37.2 | 37.2 | 37.2 | 37.2 | 37.2 | 37.2
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 29.3 | 29.3 | 29.6 | 29.7 | 30.2 | 20.5 | 21.1 | 21.7 | 22.1 | 22.6
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.989 | 0.989 | 0.989 | 0.989 | 0.989 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 26.4 | 26.4 | 26.4 | 26.4 | 26.4 | 32.2 | 32.2 | 32.2 | 32.2 | 32.2
50 PoE Load (MVA) | 27.2 | 27.2 | 27.4 | 27.6 | 28 | 19.7 | 20.3 | 20.8 | 21.3 | 21.7
50 PoE Load > 95% (MVA) | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1 | 1 | 1 | 1.1 | 1.1
Hours PA > 95% Peak Load | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5
Raw LAR (MVA) | SUMMER 2023/24: 0.8; SUMMER 2024/25: 0.8; SUMMER 2025/26: 1; SUMMER 2026/27: 1.2; SUMMER 2027/28: 1.6
2HR Rating (MVA) | 30.1 | 30.1 | 30.1 | 30.1 | 30.1 | 34.1 | 34.1 | 34.1 | 34.1 | 34.1
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30.7 | 30.7 | 30.7 | 30.7 | 30.7 | 30.7 | 30.7 | 30.7 | 30.7 | 30.7
N-1 Capacity for Embedded Generation (MVA) | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## BRD
Zone Summary Information and Peak Load Forecast
Substation | BRD - Brendale (33/11kV) | [5 empty] | Supply | BRD - Brendale BS
Description | Land area is 314650 sqm, Construction is multiple modular class
Transformer size is 1x14.5/25MVA ONAN/ONAF;1x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.5% W 0.5%, 2025 S -1.3% W 0.7%,2026 S -0.6% W 0.2%,2027 S -1.3% W -0.1
Load Category | Domestic
Localities | Supplies Albany Creek, Brendale, Cashmere, Clear Mountain, Draper, Eatons Hill, Joyner, Strathpine, Warner
|  |  |  | Latest Peak Compensated Load |  |  |  | 35.5 MVA on 17/03/2023 at 17:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 58.8 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 38.9 | 38.4 | 38.2 | 37.7 | 37.5 | 31.2 | 31.3 | 31.6 | 31.6 | 31.6
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.994 | 0.994 | 0.994 | 0.994 | 0.994 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
50 PoE Load (MVA) | 36.7 | 36.2 | 36 | 35.5 | 35.4 | 29.1 | 29.2 | 29.4 | 29.5 | 29.4
50 PoE Load > 95% (MVA) | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
Hours PA > 95% Peak Load | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5
Raw LAR (MVA) | SUMMER 2023/24: 5.4; SUMMER 2024/25: 4.9; SUMMER 2025/26: 4.7; SUMMER 2026/27: 4.2; SUMMER 2027/28: 4.1
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5
N-1 Capacity for Embedded Generation (MVA) | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## BIS
Zone Summary Information and Peak Load Forecast
Substation | BIS - Bribie Island (33/11kV) | [5 empty] | Supply | CBT - Caboolture BS
Description | Land area is 7040 sqm, Construction is single modular class
Transformer size is 2x15/18MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.6% W 0.0%, 2025 S -1.2% W 0.0%,2026 S -0.5% W -0.4%2027 S -1.2% W -0.6
Load Category | Domestic
Localities | Supplies Banksia Beach, Bellara, Bongaree, Sandstone Point, White Patch, Woorim
|  |  |  | Latest Peak Compensated Load |  |  |  | 23.4 MVA on 04/07/2022 at 17:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 41.6 | 41.6 | 41.6 | 41.6 | 41.6 | 41.6 | 41.6 | 41.6 | 41.6 | 41.6
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 23.3 | 23 | 22.9 | 22.6 | 22.5 | 23.8 | 23.8 | 23.8 | 23.7 | 23.5
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.998 | 0.998 | 0.998 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2
50 PoE Load (MVA) | 21.8 | 21.5 | 21.4 | 21.1 | 21.1 | 20.7 | 20.7 | 20.7 | 20.6 | 20.5
50 PoE Load > 95% (MVA) | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1 | 1 | 1 | 1 | 1
Hours PA > 95% Peak Load | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
Raw LAR (MVA)
2HR Rating (MVA) | 24.3 | 24.3 | 24.3 | 24.3 | 24.3 | 27 | 27 | 27 | 27 | 27
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## BRT
Zone Summary Information and Peak Load Forecast
Substation | BRT - Brighton (33/11kV) | [5 empty] | Supply | SGT - Sandgate BS
Description | Land area is 4070 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x10/15MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.9 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.6% W -0.3%,2025 S -1.1% W 0.3%,2026 S -0.5% W -0.2%2027 S -1.1% W -0.4
Load Category | Domestic
Localities | Supplies Brighton, Sandgate
|  |  |  | Latest Peak Compensated Load |  |  |  | 11 MVA on 03/02/2023 at 19:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 35.9 | 35.9 | 35.9 | 35.9 | 35.9 | 35.9 | 35.9 | 35.9 | 35.9 | 35.9
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 11.3 | 11.2 | 11.2 | 11 | 11 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 1 | 1 | 1 | 1 | 1 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 18.8 | 18.8 | 18.8 | 18.8 | 18.8 | 21 | 21 | 21 | 21 | 21
50 PoE Load (MVA) | 10.6 | 10.5 | 10.5 | 10.3 | 10.3 | 8.9 | 8.8 | 8.9 | 8.8 | 8.8
50 PoE Load > 95% (MVA) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Hours PA > 95% Peak Load | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Raw LAR (MVA)
2HR Rating (MVA) | 20.3 | 20.3 | 20.3 | 20.3 | 20.3 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
N-1 Capacity for Embedded Generation (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## BBH
Zone Summary Information and Peak Load Forecast
Substation | BBH - Broadbeach (110/11kV) | [5 empty] | Supply | MGB - MUDGEERABA 110 CP
Description | Land area is 4090 sqm, Construction is conventional all indoor class
Transformer size is 2x36/45/60MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.0% W 0.1%, 2025 S -1.8% W 0.2%,2026 S -1.1% W -0.3%2027 S -1.7% W -0.5
Load Category | Mixed Domestic
Localities | Supplies Broadbeach, Broadbeach Waters, Bundall, Clear Island Waters, Mermaid Beach, Mermaid Waters, Surfers Paradise
|  |  |  | Latest Peak Compensated Load |  |  |  | 58.7 MVA on 17/03/2023 at 16:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 118.2 | 118.2 | 118.2 | 118.2 | 118.2 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 62.1 | 61 | 60.3 | 59.3 | 58.9 | 46.4 | 46.4 | 46.5 | 46.3 | 46.1
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 67.9 | 67.9 | 67.9 | 67.9 | 67.9 | 72.7 | 72.7 | 72.7 | 72.7 | 72.7
50 PoE Load (MVA) | 57.2 | 56.2 | 55.5 | 54.6 | 54.2 | 44.1 | 44.1 | 44.2 | 44.1 | 43.9
50 PoE Load > 95% (MVA) | 2.9 | 2.8 | 2.8 | 2.7 | 2.7 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2
Hours PA > 95% Peak Load | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Raw LAR (MVA)
2HR Rating (MVA) | 83.8 | 83.8 | 83.8 | 83.8 | 83.8 | 87.6 | 87.6 | 87.6 | 87.6 | 87.6
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO
Capacity for Embedded Generation (MVA) | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
N-1 Capacity for Embedded Generation (MVA) | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## BTN
Zone Summary Information and Peak Load Forecast
Substation | BTN - Bromelton (33/11kV) | [5 empty] | Supply | BDS - Beaudesert BS
Description | Land area is 4550 sqm, Construction is pipework and shed class
Transformer size is 2x15MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 1.4 MVA
Growth Rates | 2023 W 1.0%, 2024 S 4.8% W 1.2%, 2025 S 0.1% W 1.3%, 2026 S 0.8% W 0.7%, 2027 S 0.1% W 0.5%
Load Category | Industrial
Localities | Supplies Allenview, Beaudesert, Bromelton, Gleneagle, Josephville, Kooralbyn, Laravale, Wyaralong
|  |  |  | Latest Peak Compensated Load |  |  |  | 8 MVA on 10/06/2022 at 07:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Day | Day | Day | Day
NCC Rating (MVA) | 30.6 | 30.6 | 30.6 | 30.6 | 30.6 | 31.4 | 31.4 | 31.4 | 31.4 | 31.4
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 8.6 | 8.6 | 8.7 | 8.7 | 8.8 | 8.3 | 8.4 | 8.5 | 8.5 | 8.6
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.987 | 0.987 | 0.987 | 0.987 | 0.987 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 18 | 18 | 18 | 18 | 18
50 PoE Load (MVA) | 8.2 | 8.2 | 8.3 | 8.3 | 8.3 | 8 | 8.1 | 8.2 | 8.2 | 8.3
50 PoE Load > 95% (MVA) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Hours PA > 95% Peak Load | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
Raw LAR (MVA)
2HR Rating (MVA) | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 21.8 | 21.8 | 21.8 | 21.8 | 21.8
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
Mobile Plant Avail (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## BPN
Zone Summary Information and Peak Load Forecast
Substation | BPN - Browns Plains (33/11kV) | [5 empty] | Supply | BPN - Browns Plains BS
Description | Land area is 7242 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x15/25MVA ONAN/OFDAF;1x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 1.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 1.5% W 0.2%, 2025 S -3.6% W 0.4%,2026 S -2.0% W -0.2%2027 S -1.7% W 0.0%
Load Category | Mixed Domestic
Localities | Supplies Boronia Heights, Browns Plains, Calamvale, Drewvale, Forestdale, Greenbank, Heritage Park, Hillcrest, Park Ridge, Parkinson, Regents Park, Stretton
|  |  |  | Latest Peak Compensated Load |  |  |  | 51 MVA on 17/03/2023 at 17:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 80.4 | 80.4 | 80.4 | 80.4 | 80.4 | 80.4 | 80.4 | 80.4 | 80.4 | 80.4
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 54 | 52.2 | 51.2 | 50.4 | 50 | 43.6 | 43.6 | 43.8 | 43.8 | 43.8
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 1 | 1 | 1 | 1 | 1 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5
50 PoE Load (MVA) | 51 | 49.3 | 48.4 | 47.6 | 47.2 | 41.7 | 41.8 | 42 | 41.9 | 41.9
50 PoE Load > 95% (MVA) | 2.6 | 2.5 | 2.4 | 2.4 | 2.4 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1
Hours PA > 95% Peak Load | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
Raw LAR (MVA)
2HR Rating (MVA) | 60.1 | 60.1 | 60.1 | 60.1 | 60.1 | 67.3 | 67.3 | 67.3 | 67.3 | 67.3
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## BLB
Zone Summary Information and Peak Load Forecast
Substation | BLB - Bulimba (33/11kV) | [5 empty] | Supply | DBS - Doboy BS
Description | Land area is 3470 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x15/25MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.3% W 0.2%, 2025 S -1.8% W 0.5%,2026 S -1.1% W 0.0%,2027 S -1.2% W 0.5%
Load Category | Domestic
Localities | Supplies Balmoral, Bulimba, Hawthorne, Morningside, New Farm, Norman Park
|  |  |  | Latest Peak Compensated Load |  |  |  | 26.4 MVA on 17/03/2023 at 16:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 58.3 | 58.3 | 58.3 | 58.3 | 58.3 | 59.2 | 59.2 | 59.2 | 59.2 | 59.2
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 27.3 | 26.8 | 26.5 | 26.2 | 26.2 | 20.6 | 20.6 | 20.7 | 20.7 | 20.8
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.993 | 0.993 | 0.993 | 0.993 | 0.993 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 34.4 | 34.4 | 34.4 | 34.4 | 34.4
50 PoE Load (MVA) | 25.5 | 25.1 | 24.8 | 24.5 | 24.5 | 19.7 | 19.7 | 19.8 | 19.8 | 19.9
50 PoE Load > 95% (MVA) | 1.3 | 1.3 | 1.2 | 1.2 | 1.2 | 1 | 1 | 1 | 1 | 1
Hours PA > 95% Peak Load | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
Raw LAR (MVA)
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## BDL
Zone Summary Information and Peak Load Forecast
Substation | BDL - Bundall (33/11kV) | [5 empty] | Supply | MDR - Molendinar BS
Description | Land area is 1530 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x10/14MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.2% W 0.0%, 2025 S -2.1% W -0.8%2026 S -1.7% W -1.5%2027 S -2.4% W -1.8
Load Category | Mixed Industrial
Localities | Supplies Ashmore, Benowa, Bundall, Southport, Surfers Paradise
|  |  |  | Latest Peak Compensated Load |  |  |  | 13.3 MVA on 13/02/2023 at 15:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Day | Day | Day | Day
NCC Rating (MVA) | 30.5 | 30.5 | 30.5 | 30.5 | 30.5 | 30.5 | 30.5 | 30.5 | 30.5 | 30.5
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 14.7 | 16.4 | 16.1 | 15.8 | 15.6 | 9.7 | 11.1 | 11 | 10.9 | 10.7
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.965 | 0.965 | 0.965 | 0.965 | 0.965 | 0.994 | 0.994 | 0.994 | 0.994 | 0.994
ECC Rating (MVA) | 16.1 | 16.1 | 16.1 | 16.1 | 16.1 | 18.2 | 18.2 | 18.2 | 18.2 | 18.2
50 PoE Load (MVA) | 13.6 | 15.3 | 15.1 | 14.8 | 14.6 | 9.3 | 10.7 | 10.6 | 10.5 | 10.3
50 PoE Load > 95% (MVA) | 0.7 | 0.8 | 0.8 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hours PA > 95% Peak Load | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
Raw LAR (MVA)
2HR Rating (MVA) | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 19.6 | 19.6 | 19.6 | 19.6 | 19.6
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
N-1 Capacity for Embedded Generation (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## BDB
Zone Summary Information and Peak Load Forecast
Substation | BDB - Bundamba (110/11kV) | [5 empty] | Supply | BDB - BUNDAMBA 110 CP
Description | Land area is 32660 sqm, Construction is single modular class
Transformer size is 1x30/60MVA ONAN/ODAF;1x36/60MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.3% W 0.4%, 2025 S -1.5% W 0.7%,2026 S -0.8% W 0.1%,2027 S -1.7% W -0.4
Load Category | Industrial
Localities | Supplies Bundamba, Riverview
|  |  |  | Latest Peak Compensated Load |  |  |  | 34.4 MVA on 31/01/2023 at 15:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 114.4 | 114.4 | 114.4 | 114.4 | 114.4 | 122 | 122 | 122 | 122 | 122
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 37.9 | 37.3 | 37 | 36.4 | 36.1 | 30.4 | 30.6 | 30.8 | 30.8 | 30.7
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 62.9 | 62.9 | 62.9 | 62.9 | 62.9 | 66.3 | 66.3 | 66.3 | 66.3 | 66.3
50 PoE Load (MVA) | 35.5 | 35 | 34.7 | 34.1 | 33.8 | 29.7 | 29.4 | 29.6 | 29.6 | 29.5
50 PoE Load > 95% (MVA) | 1.8 | 1.8 | 1.7 | 1.7 | 1.7 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
Hours PA > 95% Peak Load | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5
Raw LAR (MVA)
2HR Rating (MVA) | 75 | 75 | 75 | 75 | 75 | 84 | 84 | 84 | 84 | 84
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66
N-1 Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## BDA
Zone Summary Information and Peak Load Forecast
Substation | BDA - Buranda (33/11kV) | [5 empty] | Supply | TSN - Tennyson BS
Description | Land area is 5120 sqm, Construction is multiple modular class
Transformer size is 2x15/25MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 3.3 MVA
Growth Rates | 2023 W 1.0%, 2024 S 5.0% W 2.8%, 2025 S -0.0% W 2.7%,2026 S 0.6% W 2.1%, 2027 S 0.2% W 2.1%
Load Category | Mixed Industrial
Localities | Supplies Annerley, Dutton Park, Highgate Hill, South Brisbane, Woolloongabba
|  |  |  | Latest Peak Compensated Load |  |  |  | 19.5 MVA on 13/02/2023 at 15:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Day | Day | Day | Day
NCC Rating (MVA) | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 20.6 | 29 | 29.1 | 29.1 | 29.4 | 14.8 | 22.1 | 22.5 | 22.9 | 23.2
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.989 | 0.989 | 0.989 | 0.989 | 0.989 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998
ECC Rating (MVA) | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5
50 PoE Load (MVA) | 19.6 | 27.9 | 28 | 28.1 | 28.3 | 14.2 | 21.5 | 21.9 | 22.2 | 22.6
50 PoE Load > 95% (MVA) | 1 | 1.4 | 1.4 | 1.4 | 1.4 | 0.7 | 1.1 | 1.1 | 1.1 | 1.1
Hours PA > 95% Peak Load | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Raw LAR (MVA)
2HR Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## BHD
Zone Summary Information and Peak Load Forecast
Substation | BHD - Burleigh Heads (110/11kV) | [5 empty] | Supply | MGB - MUDGEERABA 110 CP
Description | Land area is 25760 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x36/60MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 2.4 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.6% W 0.7%, 2025 S -2.2% W 0.8%,2026 S -0.7% W 0.2%,2027 S -1.3% W 0.1%
Load Category | Domestic
Localities | Supplies Burleigh Heads, Burleigh Waters, Elanora, Palm Beach, Reedy Creek, Tallebudgera, Tallebudgera Valley, Varsity Lakes
|  |  |  | Latest Peak Compensated Load |  |  |  | 56.5 MVA on 17/03/2023 at 17:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 120.4 | 120.4 | 120.4 | 120.4 | 120.4 | 129.9 | 129.9 | 129.9 | 129.9 | 129.9
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 60.1 | 58.8 | 58.3 | 57.6 | 57.5 | 53.1 | 53.5 | 53.9 | 54 | 54
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 70.3 | 70.3 | 70.3 | 70.3 | 70.3 | 73.7 | 73.7 | 73.7 | 73.7 | 73.7
50 PoE Load (MVA) | 54.8 | 53.6 | 53.2 | 52.5 | 52.4 | 50.5 | 50.8 | 51.2 | 51.3 | 51.4
50 PoE Load > 95% (MVA) | 2.7 | 2.7 | 2.7 | 2.6 | 2.6 | 2.5 | 2.5 | 2.6 | 2.6 | 2.6
Hours PA > 95% Peak Load | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
Raw LAR (MVA)
2HR Rating (MVA) | 81 | 81 | 81 | 81 | 81 | 90 | 90 | 90 | 90 | 90
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO
Capacity for Embedded Generation (MVA) | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
N-1 Capacity for Embedded Generation (MVA) | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## BGY
Zone Summary Information and Peak Load Forecast
Substation | BGY - Burpengary (33/11kV) | [5 empty] | Supply | HIL - Hays Inlet BS
Description | Land area is 5320 sqm, Construction is multiple modular class
Transformer size is 1x15/25MVA ONAN/ODAF;1x25MVA ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.8% W 0.9%, 2025 S -1.1% W 1.0%,2026 S -0.4% W 0.4%,2027 S -0.8% W 0.5%
Load Category | Domestic
Localities | Supplies Burpengary, Deception Bay, Narangba
|  |  |  | Latest Peak Compensated Load |  |  |  | 25.5 MVA on 01/02/2023 at 17:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 27 | 26.7 | 26.6 | 26.4 | 26.4 | 20 | 20.2 | 20.4 | 20.5 | 20.6
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
50 PoE Load (MVA) | 25.4 | 25.1 | 25 | 24.8 | 24.9 | 18.7 | 18.9 | 19 | 19.1 | 19.2
50 PoE Load > 95% (MVA) | 1.3 | 1.3 | 1.3 | 1.2 | 1.2 | 0.9 | 0.9 | 1 | 1 | 1
Hours PA > 95% Peak Load | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
Raw LAR (MVA)
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## CBT
Zone Summary Information and Peak Load Forecast
Substation | CBT - Caboolture (33/11kV) | [5 empty] | Supply | CBT - Caboolture BS
Description | Land area is 47630 sqm, Construction is a mixture of various construction classes
Transformer size is 2x15/25MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 2.8 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.0% W -0.3%,2025 S -2.0% W -0.5%2026 S -1.2% W -0.5%2027 S -1.5% W -0.2
Load Category | Domestic
Localities | Supplies Beerburrum, Caboolture, Donnybrook, Elimbah, Meldale, Toorbul
|  |  |  | Latest Peak Compensated Load |  |  |  | 25.4 MVA on 01/02/2023 at 17:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 59.2 | 59.2 | 59.2 | 59.2 | 59.2 | 59.2 | 59.2 | 59.2 | 59.2 | 59.2
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 28.8 | 28.3 | 28 | 27.6 | 27.5 | 19.9 | 19.9 | 19.8 | 19.7 | 19.7
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
50 PoE Load (MVA) | 26.4 | 26 | 25.7 | 25.3 | 25.2 | 18.8 | 18.8 | 18.7 | 18.6 | 18.6
50 PoE Load > 95% (MVA) | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Hours PA > 95% Peak Load | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
Raw LAR (MVA)
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## CBW
Zone Summary Information and Peak Load Forecast
Substation | CBW - Caboolture West (33/11kV) | [5 empty] | Supply | CBT - Caboolture BS
Description | Land area is 8630 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x15/25MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 1.1 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.4% W 0.2%, 2025 S -1.5% W 0.1%,2026 S -1.0% W -0.6%2027 S -0.9% W 1.0%
Load Category | Domestic
Localities | Supplies Bellmere, Bracalba, Caboolture, Caboolture South, Dayboro, Elimbah, King Scrub, Moodlu, Moorina, Ocean View, Rocksberg, Upper Caboolture, Wamuran, Wamuran Basin
|  |  |  | Latest Peak Compensated Load |  |  |  | 28.7 MVA on 01/02/2023 at 17:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 58.5 | 58.5 | 58.5 | 58.5 | 58.5 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 30.1 | 29.7 | 29.4 | 29.1 | 29 | 24.2 | 23.8 | 23.9 | 23.7 | 24
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.991 | 0.991 | 0.991 | 0.991 | 0.991 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998
ECC Rating (MVA) | 30.5 | 30.5 | 30.5 | 30.5 | 30.5 | 33.5 | 33.5 | 33.5 | 33.5 | 33.5
50 PoE Load (MVA) | 28.7 | 28.2 | 28 | 27.7 | 27.6 | 21.9 | 21.5 | 21.5 | 21.4 | 21.6
50 PoE Load > 95% (MVA) | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1
Hours PA > 95% Peak Load | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Raw LAR (MVA)
2HR Rating (MVA) | 33.5 | 33.5 | 33.5 | 33.5 | 33.5 | 36.6 | 36.6 | 36.6 | 36.6 | 36.6
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## CCY
Zone Summary Information and Peak Load Forecast
Substation | CCY - Cades County (110/11kV) | [5 empty] | Supply | MAR - MOLENDINAR 110 CP
Description | Land area is 8690 sqm, Construction is conventional indoor/outdoor class
Transformer size is 1x30/60MVA ONAN/ODAF;1x36/60MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.0% W -0.2%,2025 S -3.0% W -0.2%2026 S -2.4% W -0.7%2027 S -3.0% W -0.9
Load Category | Domestic
Localities | Supplies Coomera, Gaven, Helensvale, Maudsland, Oxenford, Pacific Pines, Upper Coomera
|  |  |  | Latest Peak Compensated Load |  |  |  | 61.8 MVA on 17/03/2023 at 16:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 125.3 | 125.3 | 125.3 | 125.3 | 125.3 | 133.6 | 133.6 | 133.6 | 133.6 | 133.6
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 65.3 | 63.4 | 61.9 | 60 | 59.2 | 52.7 | 52.6 | 52.5 | 52.1 | 51.7
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 68.6 | 68.6 | 68.6 | 68.6 | 68.6 | 73.2 | 73.2 | 73.2 | 73.2 | 73.2
50 PoE Load (MVA) | 62.5 | 60.6 | 59.2 | 57.4 | 56.6 | 47.8 | 47.7 | 47.6 | 47.3 | 46.8
50 PoE Load > 95% (MVA) | 3.1 | 3 | 3 | 2.9 | 2.8 | 2.4 | 2.4 | 2.4 | 2.4 | 2.3
Hours PA > 95% Peak Load | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
Raw LAR (MVA)
2HR Rating (MVA) | 81 | 81 | 81 | 81 | 81 | 90 | 90 | 90 | 90 | 90
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66
N-1 Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## CMV
Zone Summary Information and Peak Load Forecast
Substation | CMV - Calamvale (33/11kV) | [5 empty] | Supply | AGT - Algester BS
Description | Land area is 11420 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x14.5/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.5% W 0.6%, 2025 S -1.3% W 0.8%,2026 S -0.6% W 0.3%,2027 S -1.2% W 0.1%
Load Category | Domestic
Localities | Supplies Algester, Calamvale, Parkinson, Runcorn, Stretton, Sunnybank Hills
|  |  |  | Latest Peak Compensated Load |  |  |  | 36.2 MVA on 17/03/2023 at 17:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 59.1 | 59.1 | 59.1 | 59.1 | 59.1 | 59.1 | 59.1 | 59.1 | 59.1 | 59.1
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 38.6 | 38.1 | 37.9 | 37.4 | 37.4 | 30.6 | 31.3 | 31.5 | 31.6 | 31.6
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
50 PoE Load (MVA) | 37.2 | 36.7 | 36.5 | 36.1 | 36 | 29.2 | 29.8 | 30.1 | 30.1 | 30.2
50 PoE Load > 95% (MVA) | 1.9 | 1.8 | 1.8 | 1.8 | 1.8 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
Hours PA > 95% Peak Load | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Raw LAR (MVA) | SUMMER 2023/24: 5.9; SUMMER 2024/25: 5.4; SUMMER 2025/26: 5.2; SUMMER 2026/27: 4.8; SUMMER 2027/28: 4.7
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
N-1 Capacity for Embedded Generation (MVA) | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## CLD
Zone Summary Information and Peak Load Forecast
Substation | CLD - Caloundra (132/11kV) | [5 empty] | Supply | PWD - PALMWOODS 132 CP
Description | Land area is 4390 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x36/45/60MVA ONAN/ONAF/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 4.6% W 0.6%, 2025 S -0.2% W 0.7%,2026 S 0.4% W 0.6%, 2027 S -0.2% W 0.5%
Load Category | Domestic
Localities | Supplies Aroona, Battery Hill, Bells Creek, Caloundra, Caloundra West, Coochin Creek, Currimundi, Dicky Beach, Golden Beach, Kings Beach, Little Mountain, Meridan Plains, Moffat Beach, Pelican Waters, Shelly Beach
|  |  |  | Latest Peak Compensated Load |  |  |  | 54.8 MVA on 05/07/2022 at 17:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 115.1 | 115.1 | 115.1 | 115.1 | 115.1 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 59.5 | 59.4 | 63.3 | 63.2 | 63.6 | 54.6 | 54.9 | 58.3 | 58.7 | 59
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 64.5 | 64.5 | 64.5 | 64.5 | 64.5 | 67.4 | 67.4 | 67.4 | 67.4 | 67.4
50 PoE Load (MVA) | 57.2 | 57 | 61 | 60.9 | 61.3 | 50.4 | 50.7 | 54.2 | 54.5 | 54.7
50 PoE Load > 95% (MVA) | 2.9 | 2.9 | 3.1 | 3 | 3.1 | 2.5 | 2.5 | 2.7 | 2.7 | 2.7
Hours PA > 95% Peak Load | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
Raw LAR (MVA)
2HR Rating (MVA) | 81 | 81 | 81 | 81 | 81 | 90 | 90 | 90 | 90 | 90
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO
Capacity for Embedded Generation (MVA) | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
N-1 Capacity for Embedded Generation (MVA) | 14.5 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## CHL
Zone Summary Information and Peak Load Forecast
Substation | CHL - Camp Hill (33/11kV) | [5 empty] | Supply | CPR - Coorparoo BS
Description | Land area is 3880 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x20/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.8% W 0.2%, 2025 S -0.9% W 0.2%,2026 S -0.2% W -0.2%2027 S -0.9% W -0.2
Load Category | Domestic
Localities | Supplies Camp Hill, Cannon Hill, Carina, Carina Heights, Carindale, Coorparoo, Morningside, Norman Park, Seven Hills
|  |  |  | Latest Peak Compensated Load |  |  |  | 35.7 MVA on 03/02/2023 at 19:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 37.8 | 37.4 | 37.4 | 37 | 37.1 | 31.9 | 32 | 32.1 | 32 | 32
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
50 PoE Load (MVA) | 36.2 | 35.9 | 35.8 | 35.5 | 35.5 | 29.5 | 29.6 | 29.6 | 29.6 | 29.5
50 PoE Load > 95% (MVA) | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
Hours PA > 95% Peak Load | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5
Raw LAR (MVA) | SUMMER 2023/24: 4.9; SUMMER 2024/25: 4.6; SUMMER 2025/26: 4.5; SUMMER 2026/27: 4.2; SUMMER 2027/28: 4.2
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO
Capacity for Embedded Generation (MVA) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
N-1 Capacity for Embedded Generation (MVA) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## CPB
Zone Summary Information and Peak Load Forecast
Substation | CPB - Capalaba (33/11kV) | [5 empty] | Supply | CVL - Cleveland BS
Description | Land area is 1400 sqm, Construction is conventional indoor/outdoor class
Transformer size is 1x10/12.5MVA ONAN/ONAF;1x15/25MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.9% W -0.4%,2025 S -2.1% W -0.6%2026 S -1.5% W -1.2%2027 S -2.1% W -1.4
Load Category | Mixed Domestic
Localities | Supplies Alexandra Hills, Birkdale, Capalaba, Capalaba West, Chandler, Gumdale, Ransome
|  |  |  | Latest Peak Compensated Load |  |  |  | 16.5 MVA on 17/03/2023 at 16:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 29.3 | 29.3 | 29.3 | 29.3 | 29.3 | 29.3 | 29.3 | 29.3 | 29.3 | 29.3
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 17.7 | 17.4 | 17.1 | 16.7 | 16.5 | 12.4 | 12.4 | 12.3 | 12.1 | 12
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.975 | 0.975 | 0.975 | 0.975 | 0.975 | 0.994 | 0.994 | 0.994 | 0.994 | 0.994
ECC Rating (MVA) | 14.4 | 14.4 | 14.4 | 14.4 | 14.4 | 16 | 16 | 16 | 16 | 16
50 PoE Load (MVA) | 16.7 | 16.3 | 16.1 | 15.8 | 15.6 | 11.8 | 11.8 | 11.7 | 11.6 | 11.4
50 PoE Load > 95% (MVA) | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
Hours PA > 95% Peak Load | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Raw LAR (MVA) | SUMMER 2023/24: 2.3; SUMMER 2024/25: 1.9; SUMMER 2025/26: 1.7; SUMMER 2026/27: 1.4; SUMMER 2027/28: 1.2
2HR Rating (MVA) | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
N-1 Capacity for Embedded Generation (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## CPS
Zone Summary Information and Peak Load Forecast
Substation | CPS - Capalaba South (33/11kV) | [5 empty] | Supply | CVL - Cleveland BS
Description | Land area is 3780 sqm, Construction is multiple modular class
Transformer size is 2x15/25MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.6% W -0.7%,2025 S -2.8% W -0.2%2026 S -1.3% W -0.6%2027 S -1.6% W -0.7
Load Category | Domestic
Localities | Supplies Alexandra Hills, Capalaba
|  |  |  | Latest Peak Compensated Load |  |  |  | 16.7 MVA on 03/02/2023 at 13:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 17.5 | 17 | 16.8 | 16.5 | 16.4 | 15.2 | 15.1 | 15.1 | 15 | 14.9
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.986 | 0.986 | 0.986 | 0.986 | 0.986 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
50 PoE Load (MVA) | 16.4 | 15.9 | 15.7 | 15.5 | 15.4 | 13.8 | 13.7 | 13.7 | 13.6 | 13.5
50 PoE Load > 95% (MVA) | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Hours PA > 95% Peak Load | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5
Raw LAR (MVA)
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## CPK
Zone Summary Information and Peak Load Forecast
Substation | CPK - Carole Park (33/11kV) | [5 empty] | Supply | GNA - Goodna BS
Description | Land area is 6920 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 4.4 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.9% W -0.3%,2025 S -1.9% W -0.3%2026 S -1.2% W -0.8%2027 S -1.7% W -0.5
Load Category | Industrial
Localities | Supplies Camira, Carole Park, Gailes, Goodna, Springfield, Springfield Lakes, Wacol
|  |  |  | Latest Peak Compensated Load |  |  |  | 23.6 MVA on 17/03/2023 at 17:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Day | Day | Day | Night | Night
NCC Rating (MVA) | 42.1 | 42.1 | 42.1 | 42.1 | 42.1 | 46.6 | 46.6 | 46.6 | 46.6 | 46.6
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 24.1 | 23.6 | 23.4 | 23 | 22.8 | 21.2 | 21.1 | 21 | 20.8 | 20.7
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.997 | 0.997 | 0.997 | 0.998 | 0.998 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 25.1 | 25.1 | 25.1 | 25.1 | 25.1 | 27 | 27 | 27 | 27 | 27
50 PoE Load (MVA) | 23.5 | 23 | 22.7 | 22.3 | 22.2 | 20.4 | 20.3 | 20.3 | 20.7 | 20.6
50 PoE Load > 95% (MVA) | 1.2 | 1.2 | 1.1 | 1.1 | 1.1 | 1 | 1 | 1 | 1 | 1
Hours PA > 95% Peak Load | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
Raw LAR (MVA)
2HR Rating (MVA) | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 34 | 34 | 34 | 34 | 34
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95
N-1 Capacity for Embedded Generation (MVA) | 2.475 | 2.475 | 2.475 | 2.475 | 2.475 | 2.475 | 2.475 | 2.475 | 2.475 | 2.475
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## CPC
Zone Summary Information and Peak Load Forecast
Substation | CPC - Carole Park Central (33/11kV) | [5 empty] | Supply | GNA - Goodna BS
Description | Land area is 5660 sqm, Construction is single modular class
Transformer size is 2x15/25MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.1% W -0.3%,2025 S -1.7% W -0.2%2026 S -0.8% W -0.7%2027 S -1.4% W -0.9
Load Category | Industrial
Localities | Supplies Camira, Carole Park, Ellen Grove, Forest Lake, Greenbank, Wacol
|  |  |  | Latest Peak Compensated Load |  |  |  | 24.8 MVA on 14/07/2022 at 07:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 52.4 | 52.4 | 52.4 | 52.4 | 52.4 | 52.4 | 52.4 | 52.4 | 52.4 | 52.4
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 28.3 | 32.3 | 32 | 31.6 | 31.5 | 26.1 | 29.8 | 29.8 | 29.6 | 29.4
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.984 | 0.996 | 0.996 | 0.996 | 0.996 | 0.981 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 32.7 | 32.7 | 32.7 | 32.7 | 32.7 | 34.3 | 34.3 | 34.3 | 34.3 | 34.3
50 PoE Load (MVA) | 25.2 | 29.1 | 28.9 | 28.6 | 28.4 | 25.4 | 29.1 | 29 | 28.9 | 28.6
50 PoE Load > 95% (MVA) | 1.3 | 1.5 | 1.4 | 1.4 | 1.4 | 1.3 | 1.5 | 1.5 | 1.4 | 1.4
Hours PA > 95% Peak Load | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
Raw LAR (MVA)
2HR Rating (MVA) | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 39.9 | 39.9 | 39.9 | 39.9 | 39.9
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## CPD
Zone Summary Information and Peak Load Forecast
Substation | CPD - Carpendale (33/11kV) | [5 empty] | Supply | PRG - Postmans Ridge BS
Description | Land area is 920 sqm, Construction is pipework and shed class
Transformer size is 1x5/8MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.4% W 0.1%, 2025 S -1.3% W 0.2%,2026 S -0.6% W -0.3%2027 S -1.3% W -0.5
Load Category | Domestic
Localities | Supplies Carpendale, Derrymore, Flagstone Creek, Fordsdale, Helidon Spa, Iredale, Lilydale, Middle Ridge, Postmans Ridge, Preston, Rockmount, Silver Ridge, Stockyard, Upper Flagstone, Veradilla
|  |  |  | Latest Peak Compensated Load |  |  |  | 1.8 MVA on 12/02/2023 at 19:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.989 | 0.989 | 0.989 | 0.989 | 0.989 | 0.993 | 0.993 | 0.993 | 0.993 | 0.993
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 1.8 | 1.7 | 1.7 | 1.7 | 1.7 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
50 PoE Load > 95% (MVA) | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Hours PA > 95% Peak Load | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
Raw LAR (MVA) | 1.8 | 1.7 | 1.7 | 1.7 | 1.7 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
Mobile Plant Avail (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## CST
Zone Summary Information and Peak Load Forecast
Substation | CST - Charlotte St (110/11kV) | [5 empty] | Supply | BMH - BELMONT 110 CP
Description | Land area is 1613 sqm, Construction is conventional all indoor class
Transformer size is 3x36/45/60MVA ONAN/OFAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 1.9 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.3% W 0.1%, 2025 S -1.5% W 0.2%,2026 S -0.9% W -0.4%2027 S -1.5% W -0.6
Load Category | Industrial
Localities | Supplies Brisbane City
|  |  |  | Latest Peak Compensated Load |  |  |  | 81.7 MVA on 13/02/2023 at 13:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Day | Day | Day | Day
NCC Rating (MVA) | 186.9 | 186.9 | 186.9 | 186.9 | 186.9 | 186.9 | 186.9 | 186.9 | 186.9 | 186.9
Contracted non-network (MVA) | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
10 PoE Load (MVA) | 88.2 | 87 | 93.5 | 99.2 | 98.7 | 52.9 | 56.2 | 61.8 | 66.7 | 66.4
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | bar: SUMMER 2023/24 to WINTER 2027
ECC Rating (MVA) | 135.7 | 135.7 | 135.7 | 135.7 | 135.7 | 149.9 | 149.9 | 149.9 | 149.9 | 149.9
50 PoE Load (MVA) | 86.3 | 85.1 | 91.7 | 97.3 | 96.9 | 52 | 55.3 | 60.9 | 65.8 | 65.5
50 PoE Load > 95% (MVA) | 4.3 | 4.3 | 4.6 | 4.9 | 4.8 | 2.6 | 2.8 | 3 | 3.3 | 3.3
Hours PA > 95% Peak Load | 33.5 | 33.5 | 33.5 | 33.5 | 33.5 | 33.5 | 33.5 | 33.5 | 33.5 | 33.5
Raw LAR (MVA)
2HR Rating (MVA) | 147.5 | 147.5 | 147.5 | 147.5 | 147.5 | 149.9 | 149.9 | 149.9 | 149.9 | 149.9
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
Mobile Plant Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108
N-1 Capacity for Embedded Generation (MVA) | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
LARc (MVA)
LARc (MW)
Customer Category | CBD | CBD | CBD | CBD | CBD | CBD | CBD | CBD | CBD | CBD
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## CSE
Zone Summary Information and Peak Load Forecast
Substation | CSE - Chermside (33/11kV) | [5 empty] | Supply | SFD - Stafford BS
Description | Land area is 2650 sqm, Construction is conventional indoor/outdoor class
Transformer size is 1x15/20/25;1x15/20MVA ONAN/ONAF;1x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 7.7 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.2% W 0.0%, 2025 S -1.6% W 0.0%,2026 S -0.9% W -0.5%2027 S -1.5% W -0.6
Load Category | Mixed Industrial
Localities | Supplies Aspley, Chermside, Chermside West, Geebung, Kedron, Nundah, Wavell Heights
|  |  |  | Latest Peak Compensated Load |  |  |  | 41 MVA on 03/02/2023 at 14:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 67.5 | 67.5 | 67.5 | 67.5 | 67.5 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 43.6 | 42.9 | 42.5 | 41.9 | 41.7 | 30.4 | 30.4 | 30.4 | 30.3 | 30.1
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.998 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3
50 PoE Load (MVA) | 41.3 | 40.6 | 40.2 | 39.6 | 39.4 | 28.6 | 28.6 | 28.6 | 28.5 | 28.3
50 PoE Load > 95% (MVA) | 2.1 | 2 | 2 | 2 | 2 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
Hours PA > 95% Peak Load | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
Raw LAR (MVA)
2HR Rating (MVA) | 49.3 | 49.3 | 49.3 | 49.3 | 49.3 | 51.8 | 51.8 | 51.8 | 51.8 | 51.8
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO
Capacity for Embedded Generation (MVA) | 31.975 | 31.975 | 31.975 | 31.975 | 31.975 | 31.975 | 31.975 | 31.975 | 31.975 | 31.975
N-1 Capacity for Embedded Generation (MVA) | 16.975 | 16.975 | 16.975 | 16.975 | 16.975 | 16.975 | 16.975 | 16.975 | 16.975 | 16.975
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## CFD
Zone Summary Information and Peak Load Forecast
Substation | CFD - Clayfield (33/11kV) | [5 empty] | Supply | NGE - Nudgee BS
Description | Land area is 820 sqm, Construction is conventional all indoor class
Transformer size is 2x15/25MVA ONAN/ONAF 33/11kV
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.6 MVA
Growth Rates | 2023 W 1.0%, 2024 S 4.1% W 0.6%, 2025 S -0.7% W 0.6%,2026 S -0.0% W 0.1%,2027 S -0.5% W 0.2%
Load Category | Mixed Industrial
Localities | Supplies Albion, Ascot, Bowen Hills, Clayfield, Kedron, Lutwyche, Windsor, Wooloowin
|  |  |  | Latest Peak Compensated Load |  |  |  | 18.8 MVA on 03/02/2023 at 14:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 19.5 | 19.4 | 19.4 | 19.3 | 19.4 | 13.9 | 14 | 14.1 | 14.1 | 14.1
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 28.75 | 28.75 | 28.75 | 28.75 | 28.75 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5
50 PoE Load (MVA) | 18.7 | 18.6 | 18.6 | 18.5 | 18.6 | 12.9 | 13 | 13.1 | 13.1 | 13.1
50 PoE Load > 95% (MVA) | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.7 | 0.7 | 0.7 | 0.7
Hours PA > 95% Peak Load | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
Raw LAR (MVA)
2HR Rating (MVA) | 31.25 | 31.25 | 31.25 | 31.25 | 31.25 | 35 | 35 | 35 | 35 | 35
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## CVL
Zone Summary Information and Peak Load Forecast
Substation | CVL - Cleveland (33/11kV) | [5 empty] | Supply | CVL - Cleveland BS
Description | Land area is 40420 sqm, Construction is conventional indoor/outdoor class
Transformer size is 1x15/25MVA ONAN/ONAF;2x15MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.3% W 0.1%, 2025 S -1.5% W 0.2%,2026 S -0.8% W -0.4%2027 S -1.7% W -0.8
Load Category | Domestic
Localities | Supplies Alexandra Hills, Capalaba, Cleveland, Mount Cotton, Ormiston, Sheldon, Thornlands
|  |  |  | Latest Peak Compensated Load |  |  |  | 26.9 MVA on 17/03/2023 at 17:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 29.2 | 28.8 | 28.6 | 28.1 | 27.9 | 25.1 | 25.1 | 25.1 | 25 | 24.8
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 43.8 | 43.8 | 43.8 | 43.8 | 43.8
50 PoE Load (MVA) | 27.2 | 26.8 | 26.6 | 26.2 | 25.9 | 23.3 | 23.3 | 23.3 | 23.2 | 23
50 PoE Load > 95% (MVA) | 1.4 | 1.3 | 1.3 | 1.3 | 1.3 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2
Hours PA > 95% Peak Load | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5
Raw LAR (MVA)
2HR Rating (MVA) | 42.3 | 42.3 | 42.3 | 42.3 | 42.3 | 46.7 | 46.7 | 46.7 | 46.7 | 46.7
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## CLM
Zone Summary Information and Peak Load Forecast
Substation | CLM - Coolum (33/11kV) | [5 empty] | Supply | SRH - Sunrise Hills BS
Description | Land area is 5369 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x15/25MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.8% W 0.0%, 2025 S -0.9% W 0.4%,2026 S -0.2% W -0.1%2027 S -1.3% W -0.7
Load Category | Domestic
Localities | Supplies Bli Bli, Coolum Beach, Marcoola, Mount Coolum, Mudjimba, Pacific Paradise, Peregian Beach, Point Arkwright, Valdora, Verrierdale, Yandina Creek, Yaroomba
|  |  |  | Latest Peak Compensated Load |  |  |  | 26.6 MVA on 04/07/2022 at 17:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 59.5 | 59.5 | 59.5 | 59.5 | 59.5 | 59.5 | 59.5 | 59.5 | 59.5 | 59.5
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 27.5 | 27.2 | 27.1 | 26.8 | 26.7 | 25.9 | 25.9 | 26 | 26 | 25.8
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.981 | 0.982 | 0.982 | 0.982 | 0.982 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 30.5 | 30.5 | 30.5 | 30.5 | 30.5 | 33.5 | 33.5 | 33.5 | 33.5 | 33.5
50 PoE Load (MVA) | 25 | 24.7 | 24.7 | 24.3 | 24.3 | 24.6 | 24.6 | 24.7 | 24.7 | 24.5
50 PoE Load > 95% (MVA) | 1.3 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2
Hours PA > 95% Peak Load | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
Raw LAR (MVA)
2HR Rating (MVA) | 33.5 | 33.5 | 33.5 | 33.5 | 33.5 | 36.6 | 36.6 | 36.6 | 36.6 | 36.6
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## CMA
Zone Summary Information and Peak Load Forecast
Substation | CMA - Coomera (33/11kV) | [5 empty] | Supply | CMA - Coomera BS
Description | Land area is 16100 sqm, Construction is multiple modular class
Transformer size is 1x14.5/25MVA ONAN/ONAF;1x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 1.6% W 0.9%, 2025 S -2.8% W 1.0%,2026 S -1.0% W 0.4%,2027 S -2.0% W -0.2
Load Category | Domestic
Localities | Supplies Coomera, Pimpama, Upper Coomera, Willow Vale
|  |  |  | Latest Peak Compensated Load |  |  |  | 45.4 MVA on 17/03/2023 at 17:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 47.5 | 42.2 | 41.8 | 43.8 | 46.2 | 33.4 | 33.7 | 30.6 | 30.8 | 32.7
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
50 PoE Load (MVA) | 44.4 | 39.2 | 38.8 | 40.9 | 43.3 | 31.4 | 31.7 | 28.6 | 28.8 | 30.7
50 PoE Load > 95% (MVA) | 2.2 | 2 | 1.9 | 2 | 2.2 | 1.6 | 1.6 | 1.4 | 1.4 | 1.5
Hours PA > 95% Peak Load | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Raw LAR (MVA) | SUMMER 2023/24: 13.1; SUMMER 2024/25: 7.9; SUMMER 2025/26: 7.5; SUMMER 2026/27: 9.6; SUMMER 2027/28: 12
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
Manual Trans Avail (MVA) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5
N-1 Capacity for Embedded Generation (MVA) | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5
LARc (MVA) | SUMMER 2023/24: 0.6
LARc (MW) | SUMMER 2023/24: 0.6
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## CMY
Zone Summary Information and Peak Load Forecast
Substation | CMY - Coominya (33/11kV) | [5 empty] | Supply | LRE - Lockrose BS
Description | Land area is 1950 sqm, Construction is a mixture of various construction classes
Transformer size is 1x5/6.5MVA ONAN/ONAF;1x5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.3% W 0.2%, 2025 S -1.4% W 0.4%,2026 S -0.6% W -0.2%2027 S -1.2% W -0.3
Load Category | Mixed Industrial
Localities | Supplies Atkinsons Dam, Buaraba, Churchable, Clarendon, Coominya, Moombra, Mount Hallen, Wivenhoe Hill
|  |  |  | Latest Peak Compensated Load |  |  |  | 5.6 MVA on 13/02/2023 at 17:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 5.9 | 5.9 | 5.8 | 5.8 | 5.7 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.995 | 0.995 | 0.994 | 0.994 | 0.995
ECC Rating (MVA) | 6 | 6 | 6 | 6 | 6 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8
50 PoE Load (MVA) | 5.6 | 5.5 | 5.5 | 5.4 | 5.4 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
50 PoE Load > 95% (MVA) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hours PA > 95% Peak Load | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Raw LAR (MVA)
2HR Rating (MVA) | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
Mobile Plant Avail (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO
Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
N-1 Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## CNA
Zone Summary Information and Peak Load Forecast
Substation | CNA - Cooneana (33/11kV) | [5 empty] | Supply | GNA - Goodna BS
Description | Land area is 8250 sqm, Construction is conventional all indoor class
Transformer size is 1x15/25MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 10.6% W 8.8%,2025 S 4.9% W 8.0%, 2026 S 5.1% W 6.8%, 2027 S 3.6% W 5.5%
Load Category | Industrial
Localities | Supplies Blackstone, Flinders View, New Chum, Raceview, Redbank Plains, Swanbank
|  |  |  | Latest Peak Compensated Load |  |  |  | 10.5 MVA on 12/02/2023 at 18:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 26.3 | 26.3 | 26.3 | 26.3 | 26.3 | 26.3 | 26.3 | 26.3 | 26.3 | 26.3
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 8.7 | 14.5 | 14.9 | 15.3 | 15.7 | 8.4 | 5.8 | 10.7 | 11.1 | 11.5
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 1 | 1 | 1 | 1 | 1 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 7.8 | 13.5 | 13.9 | 14.3 | 14.6 | 7.8 | 5.2 | 10 | 10.4 | 10.7
50 PoE Load > 95% (MVA) | 0.4 | 0.7 | 0.7 | 0.7 | 0.7 | 0.4 | 0.3 | 0.5 | 0.5 | 0.5
Hours PA > 95% Peak Load | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Raw LAR (MVA) | 7.8 | 13.5 | 13.9 | 14.3 | 14.6 | 7.8 | 5.2 | 10 | 10.4 | 10.7
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 1 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Manual Trans Avail (MVA) | 6.1 | 4 | 4 | 4 | 4 | 6.1 | 4 | 4 | 4 | 4
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA) | SUMMER 2026/27: 0.3; SUMMER 2027/28: 0.6
LARc (MW) | SUMMER 2026/27: 0.3; SUMMER 2027/28: 0.6
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes
Back to Index

## CPL
Zone Summary Information and Peak Load Forecast
Substation | CPL - Coopers Plains (33/11kV) | [5 empty] | Supply | AFD - Archerfield BS
Description | Land area is 3270 sqm, Construction is conventional all indoor class
Transformer size is 1x15/25MVA ONAN/ODAF;1x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.9% W -0.4%,2025 S -2.8% W -0.7%2026 S -2.2% W -0.8%2027 S -2.4% W -0.9
Load Category | Industrial
Localities | Supplies Acacia Ridge, Archerfield, Coopers Plains, Durack, Willawong
|  |  |  | Latest Peak Compensated Load |  |  |  | 19 MVA on 13/02/2023 at 14:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Day | Day | Day | Day
NCC Rating (MVA) | 52.1 | 52.1 | 52.1 | 52.1 | 52.1 | 52.1 | 52.1 | 52.1 | 52.1 | 52.1
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 21.2 | 21.4 | 20.9 | 20.5 | 20.4 | 18.4 | 18.4 | 18.8 | 18.7 | 18.5
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.997 | 0.997 | 0.997 | 0.997 | 0.998 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
ECC Rating (MVA) | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5
50 PoE Load (MVA) | 20 | 20.2 | 19.8 | 19.4 | 19.3 | 17.4 | 17.4 | 17.9 | 17.7 | 17.6
50 PoE Load > 95% (MVA) | 1 | 1 | 1 | 1 | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Hours PA > 95% Peak Load | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Raw LAR (MVA)
2HR Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## COR
Zone Summary Information and Peak Load Forecast
Substation | COR - Cooran (132/11kV) | [5 empty] | Supply | WLG - WOOLOOGA 132 CP
Description | Land area is 15130 sqm, Construction is single modular class
Transformer size is 1x18/22.5/30MVA ONAN/ODAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.6% W 0.0%, 2025 S -1.2% W 0.1%,2026 S -0.2% W -0.4%2027 S -0.9% W -0.6
Load Category | Domestic
Localities | Supplies Cooran, Cootharaba, Kin Kin, Pinbarren, Pomona, Traveston
|  |  |  | Latest Peak Compensated Load |  |  |  | 6.9 MVA on 04/07/2022 at 17:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 36 | 36 | 36 | 36 | 36
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 6.8 | 6.7 | 6.7 | 6.6 | 6.6 | 6.7 | 6.7 | 6.7 | 6.7 | 6.6
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 6.1 | 6 | 6 | 5.9 | 5.9 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3
50 PoE Load > 95% (MVA) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Hours PA > 95% Peak Load | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5
Raw LAR (MVA) | 6.1 | 6 | 6 | 5.9 | 5.9 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3
Mobile Plant Avail (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## CRY
Zone Summary Information and Peak Load Forecast
Substation | CRY - Cooroy (33/11kV) | [5 empty] | Supply | SRH - Sunrise Hills BS
Description | Land area is 110240 sqm, Construction is single modular class
Transformer size is 1x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.8% W 0.2%, 2025 S -1.0% W 0.3%,2026 S -0.3% W -0.2%2027 S -1.0% W -0.5
Load Category | Domestic
Localities | Supplies Belli Park, Cooloolabin, Cooroy, Cooroy Mountain, Doonan, Eerwah Vale, Eumundi, Lake Macdonald, Pomona, Ringtail Creek, Tinbeerwah
|  |  |  | Latest Peak Compensated Load |  |  |  | 7.2 MVA on 04/07/2022 at 18:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 7.9 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.9 | 7.8 | 7.8
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 7.3 | 7.2 | 7.2 | 7.1 | 7.1 | 7.4 | 7.4 | 7.4 | 7.4 | 7.3
50 PoE Load > 95% (MVA) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Hours PA > 95% Peak Load | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Raw LAR (MVA) | 7.3 | 7.2 | 7.2 | 7.1 | 7.1 | 7.4 | 7.4 | 7.4 | 7.4 | 7.3
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
Mobile Plant Avail (MVA) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## CPR
Zone Summary Information and Peak Load Forecast
Substation | CPR - Coorparoo (33/11kV) | [5 empty] | Supply | CPR - Coorparoo BS
Description | Land area is 3860 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x15/25MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.9% W 0.7%, 2025 S -2.0% W 0.8%,2026 S -0.8% W 0.3%,2027 S -1.1% W 0.3%
Load Category | Mixed Industrial
Localities | Supplies Camp Hill, Coorparoo, East Brisbane, Greenslopes, Norman Park
|  |  |  | Latest Peak Compensated Load |  |  |  | 20.8 MVA on 17/03/2023 at 16:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 22 | 21.5 | 21.4 | 21.1 | 21.2 | 17.1 | 17.2 | 17.4 | 17.4 | 17.5
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.995 | 0.995 | 0.995 | 0.995 | 0.995 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5
50 PoE Load (MVA) | 20.4 | 20 | 19.8 | 19.6 | 19.6 | 16.2 | 16.3 | 16.4 | 16.5 | 16.5
50 PoE Load > 95% (MVA) | 1 | 1 | 1 | 1 | 1 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
Hours PA > 95% Peak Load | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5
Raw LAR (MVA)
2HR Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## CNB
Zone Summary Information and Peak Load Forecast
Substation | CNB - Cornubia (33/11kV) | [5 empty] | Supply | BLH - Beenleigh BS
Description | Land area is 15300 sqm, Construction is single modular class
Transformer size is 1x25MVA ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.0% W -0.1%,2025 S -1.7% W 0.1%,2026 S -1.0% W -0.4%2027 S -1.5% W -0.5
Load Category | Domestic
Localities | Supplies Carbrook, Cornubia, Mount Cotton, Redland Bay, Shailer Park
|  |  |  | Latest Peak Compensated Load |  |  |  | 12.2 MVA on 17/03/2023 at 17:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 13.2 | 13 | 12.9 | 12.7 | 12.6 | 11.4 | 11.4 | 11.4 | 11.3 | 11.3
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 12.2 | 11.9 | 11.8 | 11.6 | 11.6 | 10.2 | 10.2 | 10.2 | 10.2 | 10.1
50 PoE Load > 95% (MVA) | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hours PA > 95% Peak Load | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
Raw LAR (MVA) | 12.2 | 11.9 | 11.8 | 11.6 | 11.6 | 10.2 | 10.2 | 10.2 | 10.2 | 10.1
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5
Mobile Plant Avail (MVA) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA) | SUMMER 2023/24: 0.2
LARc (MW) | SUMMER 2023/24: 0.2
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## CRM
Zone Summary Information and Peak Load Forecast
Substation | CRM - Crestmead (33/11kV) | [5 empty] | Supply | BPN - Browns Plains BS
Description | Land area is 4860 sqm, Construction is single modular class
Transformer size is 1x14.5/25MVA ONAN/ODAF;1x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 2.4 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.5% W -0.4%,2025 S -2.1% W -0.5%2026 S -1.6% W -0.4%2027 S -2.0% W -0.0
Load Category | Industrial
Localities | Supplies Berrinba, Browns Plains, Crestmead, Drewvale, Heritage Park, Karawatha, Kingston, Logan Central, Marsden, Park Ridge, Regents Park
|  |  |  | Latest Peak Compensated Load |  |  |  | 30.8 MVA on 17/03/2023 at 16:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 51.5 | 51.5 | 51.5 | 51.5 | 51.5 | 51.5 | 51.5 | 51.5 | 51.5 | 51.5
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 31.1 | 31.1 | 30.6 | 30 | 29.8 | 28.8 | 28 | 28.4 | 28.3 | 28.3
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.989 | 0.989 | 0.989 | 0.99 | 0.99 | 0.986 | 0.987 | 0.987 | 0.987 | 0.987
ECC Rating (MVA) | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5
50 PoE Load (MVA) | 28.9 | 29 | 28.5 | 27.9 | 27.8 | 27.3 | 26.5 | 27 | 26.8 | 26.8
50 PoE Load > 95% (MVA) | 1.4 | 1.5 | 1.4 | 1.4 | 1.4 | 1.4 | 1.3 | 1.4 | 1.3 | 1.3
Hours PA > 95% Peak Load | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
Raw LAR (MVA) | SUMMER 2023/24: 0.1; SUMMER 2024/25: 0.2
2HR Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5
N-1 Capacity for Embedded Generation (MVA) | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## CMD
Zone Summary Information and Peak Load Forecast
Substation | CMD - Currimundi (132/11kV) | [5 empty] | Supply | PWD - PALMWOODS 132 CP
Description | Land area is 5570 sqm, Construction is a mixture of various construction classes
Transformer size is 1x15/20/30 MVA ONAN/ODAN/ODAF;1x15/20/30MVA ONAN/ODAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 8.0% W 4.6%, 2025 S 2.8% W 4.5%, 2026 S 3.3% W 3.8%, 2027 S 3.6% W 4.6%
Load Category | Domestic
Localities | Supplies Aroona, Battery Hill, Birtinya, Bokarina, Caloundra West, Currimundi, Dicky Beach, Little Mountain, Meridan Plains, Wurtulla
|  |  |  | Latest Peak Compensated Load |  |  |  | 19.2 MVA on 13/02/2023 at 18:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 21.2 | 21.8 | 22.5 | 23.4 | 24.4 | 18.9 | 19.8 | 20.7 | 21.5 | 22.5
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 1 | 1 | 1 | 1 | 1 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 41.9 | 41.9 | 41.9 | 41.9 | 41.9
50 PoE Load (MVA) | 19.3 | 19.8 | 20.5 | 21.2 | 22.2 | 17.7 | 18.5 | 19.3 | 20.1 | 21
50 PoE Load > 95% (MVA) | 1 | 1 | 1 | 1.1 | 1.1 | 0.9 | 0.9 | 1 | 1 | 1.1
Hours PA > 95% Peak Load | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Raw LAR (MVA)
2HR Rating (MVA) | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 45 | 45 | 45 | 45 | 45
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## CRB
Zone Summary Information and Peak Load Forecast
Substation | CRB - Currumbin (33/11kV) | [5 empty] | Supply | BHD - Burleigh Heads BS
Description | Land area is 10815 sqm, Construction is multiple modular class
Transformer size is 1x15/25MVA ONAN/ONAF;1x15MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.2% W 0.6%, 2025 S -1.2% W 0.7%,2026 S -0.6% W 0.2%,2027 S -1.1% W 0.1%
Load Category | Domestic
Localities | Supplies Bilinga, Currumbin, Currumbin Valley, Currumbin Waters, Palm Beach, Tallebudgera, Tallebudgera Valley, Tugun
|  |  |  | Latest Peak Compensated Load |  |  |  | 20.9 MVA on 13/07/2022 at 18:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 22 | 21.7 | 21.6 | 21.4 | 21.4 | 21.8 | 21.9 | 22.1 | 22.1 | 22.1
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 20.3 | 20.3 | 20.3 | 20.3 | 20.3 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5
50 PoE Load (MVA) | 21.1 | 20.8 | 20.7 | 20.5 | 20.5 | 21 | 21.1 | 21.2 | 21.3 | 21.3
50 PoE Load > 95% (MVA) | 1.1 | 1 | 1 | 1 | 1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1
Hours PA > 95% Peak Load | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5
Raw LAR (MVA) | SUMMER 2023/24: 0.8; SUMMER 2024/25: 0.5; SUMMER 2025/26: 0.4; SUMMER 2026/27: 0.2; SUMMER 2027/28: 0.2
2HR Rating (MVA) | 21.8 | 21.8 | 21.8 | 21.8 | 21.8 | 24 | 24 | 24 | 24 | 24
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## DRA
Zone Summary Information and Peak Load Forecast
Substation | DRA - Darra (33/11kV) | [5 empty] | Supply | RLD - Richlands BS
Description | Land area is 3040 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x15/25MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.2% W 0.0%, 2025 S -1.8% W -0.3%2026 S -1.1% W -0.8%2027 S -1.2% W 0.1%
Load Category | Industrial
Localities | Supplies Darra, Inala, Oxley, Richlands, Sumner, Wacol
|  |  |  | Latest Peak Compensated Load |  |  |  | 23.2 MVA on 15/03/2023 at 12:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Day | Day | Day | Day
NCC Rating (MVA) | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 26.9 | 29.5 | 30.2 | 29.9 | 29.9 | 19.9 | 21.6 | 22.5 | 23.4 | 23.4
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 1 | 0.999 | 0.999 | 0.999 | 0.999 | 0.981 | 0.981 | 0.981 | 0.981 | 0.981
ECC Rating (MVA) | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 32 | 32 | 32 | 32 | 32
50 PoE Load (MVA) | 24.6 | 27.2 | 28 | 27.7 | 27.7 | 19.4 | 21.1 | 22 | 22.9 | 23
50 PoE Load > 95% (MVA) | 1.2 | 1.4 | 1.4 | 1.4 | 1.4 | 1 | 1.1 | 1.1 | 1.1 | 1.2
Hours PA > 95% Peak Load | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5
Raw LAR (MVA)
2HR Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35.1 | 35.1 | 35.1 | 35.1 | 35.1
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## DBY
Zone Summary Information and Peak Load Forecast
Substation | DBY - Deception Bay (33/11kV) | [5 empty] | Supply | HIL - Hays Inlet BS
Description | Land area is 7710 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x15/25MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.8% W 0.3%, 2025 S -2.1% W 0.4%,2026 S -0.6% W -0.1%2027 S -1.3% W -0.3
Load Category | Domestic
Localities | Supplies Deception Bay, Mango Hill, Narangba, Rothwell
|  |  |  | Latest Peak Compensated Load |  |  |  | 28.4 MVA on 17/03/2023 at 17:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 56.9 | 56.9 | 56.9 | 56.9 | 56.9 | 60 | 60 | 60 | 60 | 60
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 29.9 | 29.3 | 29.1 | 28.8 | 28.7 | 23.3 | 23.4 | 23.4 | 23.4 | 23.3
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 34.8 | 34.8 | 34.8 | 34.8 | 34.8
50 PoE Load (MVA) | 27.9 | 27.3 | 27.2 | 26.8 | 26.7 | 21.9 | 22 | 22.1 | 22.1 | 22
50 PoE Load > 95% (MVA) | 1.4 | 1.4 | 1.4 | 1.3 | 1.3 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1
Hours PA > 95% Peak Load | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
Raw LAR (MVA)
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## DBS
Zone Summary Information and Peak Load Forecast
Substation | DBS - Doboy (33/11kV) | [5 empty] | Supply | DBS - Doboy BS
Description | Land area is 18760 sqm, Construction is multiple modular class
Transformer size is 2x15/25MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 1.9% W -1.6%,2025 S -3.0% W -0.7%2026 S -2.5% W -1.3%2027 S -3.0% W -1.4
Load Category | Mixed Industrial
Localities | Supplies Hemmant, Murarrie
|  |  |  | Latest Peak Compensated Load |  |  |  | 13.3 MVA on 13/02/2023 at 11:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Day | Day | Day | Day
NCC Rating (MVA) | 52.3 | 52.3 | 52.3 | 52.3 | 52.3 | 52.3 | 52.3 | 52.3 | 52.3 | 52.3
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 13.8 | 15.4 | 15 | 14.6 | 14.4 | 10.5 | 12 | 11.9 | 11.8 | 11.7
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.964 | 0.964 | 0.964 | 0.964 | 0.964 | 0.972 | 0.972 | 0.972 | 0.972 | 0.972
ECC Rating (MVA) | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 31.6 | 31.6 | 31.6 | 31.6 | 31.6
50 PoE Load (MVA) | 13.5 | 15 | 14.7 | 14.3 | 14.1 | 9.8 | 11.3 | 11.2 | 11.1 | 11
50 PoE Load > 95% (MVA) | 0.7 | 0.8 | 0.7 | 0.7 | 0.7 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6
Hours PA > 95% Peak Load | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
Raw LAR (MVA)
2HR Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## DRD
Zone Summary Information and Peak Load Forecast
Substation | DRD - Duffield Road (33/11kV) | [5 empty] | Supply | HIL - Hays Inlet BS
Description | Land area is 4610 sqm, Construction is multiple modular class
Transformer size is 2x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.8% W 0.4%, 2025 S -0.9% W 0.4%,2026 S -0.3% W -0.1%2027 S -0.8% W -0.1
Load Category | Domestic
Localities | Supplies Clontarf, Kippa-ring, Margate, Rothwell, Woody Point
|  |  |  | Latest Peak Compensated Load |  |  |  | 24.2 MVA on 03/02/2023 at 19:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 55 | 55 | 55 | 55 | 55 | 59.9 | 59.9 | 59.9 | 59.9 | 59.9
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 25 | 24.8 | 24.7 | 24.5 | 24.5 | 22.7 | 22.8 | 22.9 | 22.8 | 22.8
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 32.2 | 32.2 | 32.2 | 32.2 | 32.2
50 PoE Load (MVA) | 23.7 | 23.5 | 23.4 | 23.2 | 23.3 | 21.3 | 21.4 | 21.5 | 21.5 | 21.4
50 PoE Load > 95% (MVA) | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1
Hours PA > 95% Peak Load | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Raw LAR (MVA)
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## EMP
Zone Summary Information and Peak Load Forecast
Substation | EMP - Eight Mile Plains Bus 1 (33/11kV) | [5 empty] | Supply | RBS - Runcorn BS
Description | Land area is 2580 sqm, Construction is conventional all indoor class
Transformer size is 1x20/23.8MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 1.3% W -0.1%,2025 S -3.9% W -0.2%2026 S -1.7% W -0.7%2027 S -1.3% W -0.4
Load Category | Mixed Industrial
Localities | Supplies Burbank, Eight Mile Plains, Macgregor, Priestdale, Rochedale, Rochedale South, Runcorn, Sheldon, Sunnybank, Upper Mount Gravatt
|  |  |  | Latest Peak Compensated Load |  |  |  | 15.3 MVA on 17/03/2023 at 16:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 26.2 | 26.2 | 26.2 | 26.2 | 26.2 | 26.2 | 26.2 | 26.2 | 26.2 | 26.2
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 18.3 | 17.8 | 17.5 | 18.3 | 19.2 | 12.4 | 15.3 | 15.3 | 15.2 | 15.9
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.989 | 0.989 | 0.989 | 0.989 | 0.989 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 17.4 | 16.9 | 16.6 | 17.4 | 18.3 | 11.6 | 14.4 | 14.4 | 14.3 | 15.1
50 PoE Load > 95% (MVA) | 0.9 | 0.8 | 0.8 | 0.9 | 0.9 | 0.6 | 0.7 | 0.7 | 0.7 | 0.8
Hours PA > 95% Peak Load | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
Raw LAR (MVA) | 17.4 | 16.9 | 16.6 | 17.4 | 18.3 | 11.6 | 14.4 | 14.4 | 14.3 | 15.1
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 11.6 | 11.8 | 11.9 | 11.2 | 10.3 | 22.4 | 20.2 | 20.1 | 20 | 18.9
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO
Capacity for Embedded Generation (MVA) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## EMP2
Zone Summary Information and Peak Load Forecast
Substation | EMP - Eight Mile Plains Bus 2 (33/11kV) | [5 empty] | Supply | BBS - Belmont BS
Description | Land area is 2580 sqm, Construction is conventional all indoor class
Transformer size is 1x14.5/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.3% W 0.9%, 2025 S -1.6% W 1.0%,2026 S -1.0% W 0.5%,2027 S -1.3% W 0.7%
Load Category | Mixed Industrial
Localities | Supplies Burbank, Eight Mile Plains, Macgregor, Priestdale, Rochedale, Rochedale South, Runcorn, Sunnybank, Upper Mount Gravatt
|  |  |  | Latest Peak Compensated Load |  |  |  | 13.4 MVA on 17/03/2023 at 16:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 18.2 | 17.9 | 17.8 | 18.5 | 19.4 | 10.9 | 13.1 | 13.2 | 13.3 | 14.4
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.988 | 0.988 | 0.988 | 0.988 | 0.988 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 17.2 | 17 | 16.9 | 17.6 | 18.5 | 10.1 | 12.3 | 12.4 | 12.5 | 13.6
50 PoE Load > 95% (MVA) | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.5 | 0.6 | 0.6 | 0.6 | 0.7
Hours PA > 95% Peak Load | 24.5 | 24.5 | 24.5 | 24.5 | 24.5 | 24.5 | 24.5 | 24.5 | 24.5 | 24.5
Raw LAR (MVA) | 17.2 | 17 | 16.9 | 17.6 | 18.5 | 10.1 | 12.3 | 12.4 | 12.5 | 13.6
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 10 | 10.5 | 10.8 | 10 | 9.1 | 19.3 | 16.5 | 16.5 | 16.6 | 15.8
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO
Capacity for Embedded Generation (MVA) | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## ENG
Zone Summary Information and Peak Load Forecast
Substation | ENG - Enoggera (33/11kV) | [5 empty] | Supply | SFD - Stafford BS
Description | Land area is 1690 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.7% W 1.0%, 2025 S -1.0% W 1.0%,2026 S -0.3% W 0.5%,2027 S -0.9% W 0.4%
Load Category | Domestic
Localities | Supplies Alderley, Ashgrove, Enoggera, Everton Park, Gaythorne, Mitchelton, Stafford
|  |  |  | Latest Peak Compensated Load |  |  |  | 19.8 MVA on 17/03/2023 at 16:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 55 | 55 | 55 | 55 | 55 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 21 | 20.8 | 20.7 | 20.6 | 20.6 | 17.1 | 17.2 | 17.4 | 17.5 | 17.6
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.993 | 0.993 | 0.993 | 0.993 | 0.993 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 30.6 | 30.6 | 30.6 | 30.6 | 30.6 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5
50 PoE Load (MVA) | 19.1 | 19 | 18.9 | 18.7 | 18.8 | 16.1 | 16.2 | 16.4 | 16.5 | 16.6
50 PoE Load > 95% (MVA) | 1 | 1 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
Hours PA > 95% Peak Load | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Raw LAR (MVA)
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## ESK
Zone Summary Information and Peak Load Forecast
Substation | ESK - Esk (33/11kV) | [5 empty] | Supply | LRE - Lockrose BS
Description | Land area is 5615 sqm, Construction is single modular class
Transformer size is 1x8MVA ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.5% W 0.1%, 2025 S -1.3% W 0.1%,2026 S -0.6% W -0.3%2027 S -1.2% W -0.4
Load Category | Domestic
Localities | Supplies Biarra, Coal Creek, Esk, Lake Wivenhoe, Mount Hallen, Murrumba, Ottaba, Redbank Creek
|  |  |  | Latest Peak Compensated Load |  |  |  | 2.9 MVA on 12/02/2023 at 18:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 3.6 | 3.5 | 3.5 | 3.5 | 3.5 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.988 | 0.988 | 0.988 | 0.988 | 0.988 | 0.996 | 0.996 | 0.996 | 0.996 | 0.996
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 3.2 | 3.2 | 3.1 | 3.1 | 3.1 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3
50 PoE Load > 95% (MVA) | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Hours PA > 95% Peak Load | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
Raw LAR (MVA) | 3.2 | 3.2 | 3.1 | 3.1 | 3.1 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | bar: SUMMER 2023/24 to WINTER 2027
Mobile Plant Avail (MVA) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## EMD
Zone Summary Information and Peak Load Forecast
Substation | EMD - Eumundi (33/11kV) | [5 empty] | Supply | SRH - Sunrise Hills BS
Description | Land area is 6560 sqm, Construction is mini-modular (skid) class
Transformer size is 1x5/8MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 4.1% W 0.5%, 2025 S -0.8% W 0.5%,2026 S 0.0% W 0.0%, 2027 S -0.5% W 0.0%
Load Category | Domestic
Localities | Supplies Doonan, Eerwah Vale, Eumundi, Ninderry, North Arm, Verrierdale, Yandina Creek
|  |  |  | Latest Peak Compensated Load |  |  |  | 4.2 MVA on 04/07/2022 at 18:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.4 | 4.5 | 4.5 | 4.5 | 4.5
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 1 | 1 | 1 | 1 | 1 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 4 | 3.9 | 3.9 | 3.9 | 3.9 | 4.1 | 4.2 | 4.2 | 4.2 | 4.2
50 PoE Load > 95% (MVA) | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hours PA > 95% Peak Load | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Raw LAR (MVA) | 4 | 3.9 | 3.9 | 3.9 | 3.9 | 4.1 | 4.2 | 4.2 | 4.2 | 4.2
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3
Mobile Plant Avail (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## FIS
Zone Summary Information and Peak Load Forecast
Substation | FIS - Fisherman Is A (33/11kV) | [5 empty] | Supply | LBS - Lytton BS
Description | Land area is 3068 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x15/18MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.1% W -0.2%,2025 S -1.5% W 0.1%,2026 S -0.8% W -0.4%2027 S -1.5% W -0.6
Load Category | Industrial
Localities | Supplies Port Of Brisbane
|  |  |  | Latest Peak Compensated Load |  |  |  | 9.4 MVA on 08/03/2023 at 20:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 10 | 19.1 | 22.4 | 23.9 | 23.9 | 9.4 | 15.9 | 17.4 | 20.3 | 21.7
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.981 | 0.981 | 0.981 | 0.981 | 0.981 | 0.982 | 0.982 | 0.982 | 0.982 | 0.982
ECC Rating (MVA) | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5
50 PoE Load (MVA) | 9.7 | 18.8 | 22.1 | 23.7 | 23.6 | 9 | 15.6 | 17.1 | 20 | 21.4
50 PoE Load > 95% (MVA) | 0.5 | 0.9 | 1.1 | 1.2 | 1.2 | 0.5 | 0.8 | 0.9 | 1 | 1.1
Hours PA > 95% Peak Load | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
Raw LAR (MVA) | SUMMER 2025/26: 1.4; SUMMER 2026/27: 3; SUMMER 2027/28: 2.9
2HR Rating (MVA) | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## FBS
Zone Summary Information and Peak Load Forecast
Substation | FBS - Fisherman Is B (33/11kV) | [5 empty] | Supply | LBS - Lytton BS
Description | Construction is single modular class
Transformer size is 1x15/25MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.2% W 0.0%, 2025 S -1.5% W 0.2%,2026 S -0.9% W -0.4%2027 S -1.5% W -0.6
Load Category | Industrial
Localities | Supplies Port Of Brisbane
|  |  |  | Latest Peak Compensated Load |  |  |  | 4 MVA on 17/03/2023 at 12:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Day | Day
NCC Rating (MVA) | 26.3 | 26.3 | 26.3 | 26.3 | 26.3 | 26.3 | 26.3 | 26.3 | 26.3 | 26.3
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 4.3 | 4.8 | 4.8 | 4.7 | 4.7 | 4.2 | 4.6 | 4.6 | 4.5 | 4.5
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.938 | 0.938 | 0.938 | 0.946 | 0.946
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 4.1 | 4.7 | 4.7 | 4.6 | 4.6 | 3.9 | 4.3 | 4.3 | 4.2 | 4.2
50 PoE Load > 95% (MVA) | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hours PA > 95% Peak Load | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
Raw LAR (MVA) | 4.1 | 4.7 | 4.7 | 4.6 | 4.6 | 3.9 | 4.3 | 4.3 | 4.2 | 4.2
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 4.1 | 4.7 | 4.7 | 4.6 | 4.6 | 3.9 | 4.3 | 4.3 | 4.2 | 4.2
Manual Trans Avail (MVA) | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## FDS
Zone Summary Information and Peak Load Forecast
Substation | FDS - Flinders (33/11kV) | [5 empty] | Supply | RVW - Raceview BS
Description | Land area is 6242 sqm, Construction is pipework and shed class
Transformer size is 2x5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.5% W 0.7%, 2025 S -1.2% W 0.7%,2026 S -0.6% W 0.2%,2027 S -1.1% W 0.1%
Load Category | Domestic
Localities | Supplies Anthony, Blantyre, Coleyville, Goolman, Harrisville, Limestone Ridges, Milbong, Milora, Mount Forbes, Mount Walker, Munbilla, Mutdapilly, Peak Crossing, Purga, Radford, Rosevale, Silverdale, Undullah, Warrill View, Washpool, Wilsons Plains, Woolooman
|  |  |  | Latest Peak Compensated Load |  |  |  | 5 MVA on 12/02/2023 at 17:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 5.6 | 5.5 | 6.4 | 6.3 | 6.3 | 4.3 | 4.3 | 4.9 | 4.9 | 4.9
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.958 | 0.958 | 0.958 | 0.958 | 0.958 | 0.974 | 0.974 | 0.974 | 0.974 | 0.974
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 5.2 | 5.1 | 6 | 5.9 | 5.9 | 4 | 4 | 4.7 | 4.7 | 4.7
50 PoE Load > 95% (MVA) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hours PA > 95% Peak Load | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Raw LAR (MVA) | 5.2 | 5.1 | 6 | 5.9 | 5.9 | 4 | 4 | 4.7 | 4.7 | 4.7
2HR Rating (MVA)
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3
Mobile Plant Avail (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
N-1 Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## GTN
Zone Summary Information and Peak Load Forecast
Substation | GTN - Gatton A (33/11kV) | [5 empty] | Supply | GBS - Gatton BS
Description | Land area is 36390 sqm, Construction is pipework and shed class
Transformer size is 2x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.6% W 0.5%, 2025 S -1.4% W 0.5%,2026 S -0.7% W -0.1%2027 S -1.3% W -0.2
Load Category | Domestic
Localities | Supplies Adare, College View, Gatton, Grantham, Lake Clarendon, Lawes, Lower Tenthill, Placid Hills, Ringwood, Spring Creek, Veradilla, Vinegar Hill, Winwill, Woodlands
|  |  |  | Latest Peak Compensated Load |  |  |  | 15.8 MVA on 17/03/2023 at 16:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 18.7 | 18.5 | 18.3 | 18.1 | 18 | 13.4 | 13.5 | 13.6 | 13.5 | 13.5
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.976 | 0.976 | 0.976 | 0.976 | 0.976 | 0.995 | 0.995 | 0.995 | 0.995 | 0.995
ECC Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
50 PoE Load (MVA) | 17.2 | 16.9 | 16.8 | 16.6 | 16.5 | 12.4 | 12.5 | 12.5 | 12.5 | 12.5
50 PoE Load > 95% (MVA) | 0.9 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
Hours PA > 95% Peak Load | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
Raw LAR (MVA)
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4
Mobile Plant Avail (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## GVN
Zone Summary Information and Peak Load Forecast
Substation | GVN - Gaven (33/11kV) | [5 empty] | Supply | MDR - Molendinar BS
Description | Land area is 9670 sqm, Construction is single modular class
Transformer size is 1x14.5/25MVA ONAN/ONAF;1x25MVA ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.3% W -1.2%,2025 S -1.5% W 0.7%,2026 S -0.8% W 0.2%,2027 S -1.6% W -0.2
Load Category | Domestic
Localities | Supplies Arundel, Gaven, Helensvale, Molendinar, Nerang, Oxenford, Pacific Pines, Parkwood
|  |  |  | Latest Peak Compensated Load |  |  |  | 29.6 MVA on 17/03/2023 at 17:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 31 | 30.5 | 30.3 | 29.8 | 29.6 | 24.9 | 24.6 | 24.8 | 24.8 | 24.8
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
50 PoE Load (MVA) | 29 | 28.5 | 28.3 | 27.9 | 27.6 | 22.4 | 22.1 | 22.3 | 22.3 | 22.3
50 PoE Load > 95% (MVA) | 1.5 | 1.4 | 1.4 | 1.4 | 1.4 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1
Hours PA > 95% Peak Load | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
Raw LAR (MVA)
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## GBG
Zone Summary Information and Peak Load Forecast
Substation | GBG - Geebung (33/11kV) | [5 empty] | Supply | NGE - Nudgee BS
Description | Land area is 5040 sqm, Construction is conventional indoor/outdoor class
Transformer size is 1x15/25MVA ONAN/ODAF;2x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.6% W -0.7%,2025 S -2.6% W -1.2%2026 S -1.9% W -1.2%2027 S -1.7% W -0.8
Load Category | Industrial
Localities | Supplies Banyo, Boondall, Geebung, Northgate, Nudgee, Virginia
|  |  |  | Latest Peak Compensated Load |  |  |  | 34.5 MVA on 31/01/2023 at 14:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Day | Day | Day | Day
NCC Rating (MVA) | 78.7 | 78.7 | 78.7 | 78.7 | 78.7 | 78.7 | 78.7 | 78.7 | 78.7 | 78.7
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 36.3 | 36.9 | 36.2 | 35.6 | 35.4 | 29 | 30.1 | 29.8 | 29.5 | 29.2
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.996 | 0.995 | 0.996 | 0.996 | 0.996 | 0.985 | 0.985 | 0.985 | 0.985 | 0.985
ECC Rating (MVA) | 57.4 | 57.4 | 57.4 | 57.4 | 57.4 | 64.9 | 64.9 | 64.9 | 64.9 | 64.9
50 PoE Load (MVA) | 34.6 | 35.2 | 34.5 | 33.9 | 33.7 | 27.2 | 28.4 | 28.1 | 27.7 | 27.5
50 PoE Load > 95% (MVA) | 1.7 | 1.8 | 1.7 | 1.7 | 1.7 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
Hours PA > 95% Peak Load | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Raw LAR (MVA)
2HR Rating (MVA) | 62.4 | 62.4 | 62.4 | 62.4 | 62.4 | 69.9 | 69.9 | 69.9 | 69.9 | 69.9
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## GIS
Zone Summary Information and Peak Load Forecast
Substation | GIS - Gibson Island (33/11kV) | [5 empty] | Supply | LBS - Lytton BS
Description | Land area is 4730 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x14.5/25MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.1% W -0.2%,2025 S -1.5% W 0.1%,2026 S -0.9% W -0.4%2027 S -1.5% W -0.6
Load Category | Continuous
Localities | Supplies Hemmant, Murarrie
|  |  |  | Latest Peak Compensated Load |  |  |  | 17 MVA on 07/12/2022 at 13:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Day | Day | Day | Day
NCC Rating (MVA) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 17.8 | 20.8 | 20.6 | 20.3 | 20.2 | 17.2 | 19.7 | 19.8 | 19.7 | 19.6
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.996 | 0.992 | 0.992 | 0.992 | 0.993 | 0.998 | 0.994 | 0.994 | 0.994 | 0.995
ECC Rating (MVA) | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8
50 PoE Load (MVA) | 17.6 | 20.6 | 20.4 | 20.2 | 20 | 17.1 | 19.6 | 19.6 | 19.5 | 19.4
50 PoE Load > 95% (MVA) | 0.9 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1
Hours PA > 95% Peak Load | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Raw LAR (MVA)
2HR Rating (MVA) | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mobile Plant Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
N-1 Capacity for Embedded Generation (MVA) | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5
LARc (MVA)
LARc (MW)
Customer Category | HighSec | HighSec | HighSec | HighSec | HighSec | HighSec | HighSec | HighSec | HighSec | HighSec
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## GGR
Zone Summary Information and Peak Load Forecast
Substation | GGR - Glenore Grove (33/11kV) | [5 empty] | Supply | LRE - Lockrose BS
Description | Land area is 4050 sqm, Construction is pipework and shed class
Transformer size is 1x5/8MVA ONAN/ODAF;1x5/8MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 4.0% W -0.8%,2025 S -0.8% W -1.2%2026 S -0.2% W -1.6%2027 S -0.8% W -1.7
Load Category | Domestic
Localities | Supplies College View, Crowley Vale, Forest Hill, Glenore Grove, Grandchester, Hatton Vale, Laidley North, Lake Clarendon, Lawes, Lockrose, Morton Vale, Plainland, Regency Downs, Summerholm, Woolshed
|  |  |  | Latest Peak Compensated Load |  |  |  | 9.2 MVA on 12/02/2023 at 18:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 9.7 | 10 | 10 | 9.9 | 9.9 | 7.8 | 8 | 7.9 | 7.8 | 7.7
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 1 | 1 | 1 | 1 | 1 | 0.993 | 0.993 | 0.993 | 0.993 | 0.993
ECC Rating (MVA) | 10 | 10 | 10 | 10 | 10 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2
50 PoE Load (MVA) | 9.3 | 9.6 | 9.6 | 9.5 | 9.5 | 7.2 | 7.4 | 7.3 | 7.2 | 7.1
50 PoE Load > 95% (MVA) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Hours PA > 95% Peak Load | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Raw LAR (MVA)
2HR Rating (MVA) | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 12 | 12 | 12 | 12 | 12
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6
Mobile Plant Avail (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO
Capacity for Embedded Generation (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
N-1 Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## GNA
Zone Summary Information and Peak Load Forecast
Substation | GNA - Goodna (33/11kV) | [5 empty] | Supply | GNA - Goodna BS
Description | Land area is 183300 sqm, Construction is single modular class
Transformer size is 1x15/25MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 6.2% W 3.4%, 2025 S 0.9% W 3.0%, 2026 S 1.5% W 3.0%, 2027 S 1.4% W 3.7%
Load Category | Mixed Domestic
Localities | Supplies Collingwood Park, Goodna, Redbank Plains
|  |  |  | Latest Peak Compensated Load |  |  |  | 15.4 MVA on 12/02/2023 at 18:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 16.8 | 16 | 16.2 | 16.5 | 16.9 | 12.7 | 12.5 | 12.8 | 13.2 | 13.7
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 15.6 | 14.8 | 15 | 15.2 | 15.7 | 12.1 | 11.8 | 12.2 | 12.6 | 13
50 PoE Load > 95% (MVA) | 0.8 | 0.7 | 0.8 | 0.8 | 0.8 | 0.6 | 0.6 | 0.6 | 0.6 | 0.7
Hours PA > 95% Peak Load | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
Raw LAR (MVA) | 15.6 | 14.8 | 15 | 15.2 | 15.7 | 12.1 | 11.8 | 12.2 | 12.6 | 13
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Manual Trans Avail (MVA) | 14 | 14 | 16 | 16 | 16 | 14 | 14 | 16 | 16 | 16
Mobile Plant Avail (MVA) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## GBN
Zone Summary Information and Peak Load Forecast
Substation | GBN - Goomboorian (33/11kV) | [5 empty] | Supply | GYM - Gympie BS
Description | Land area is 8895 sqm, Construction is mini-modular (skid) class
Transformer size is 1x5/8MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.3% W -0.1%,2025 S -1.4% W 0.1%,2026 S -0.7% W -0.4%2027 S -1.3% W -0.6
Load Category | Mixed Domestic
Localities | Supplies Anderleigh, Coondoo, Downsfield, Greens Creek, Kia Ora, Neerdie, North Deep Creek, Veteran, Wolvi
|  |  |  | Latest Peak Compensated Load |  |  |  | 2.9 MVA on 13/02/2023 at 19:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 3 | 3 | 3 | 2.9 | 2.9 | 2.7 | 2.7 | 2.7 | 2.7 | 2.6
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 2.8 | 2.7 | 2.7 | 2.7 | 2.7 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
50 PoE Load > 95% (MVA) | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Hours PA > 95% Peak Load | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
Raw LAR (MVA) | 2.8 | 2.7 | 2.7 | 2.7 | 2.7 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
Mobile Plant Avail (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## GLY
Zone Summary Information and Peak Load Forecast
Substation | GLY - Grovely (33/11kV) | [5 empty] | Supply | SFD - Stafford BS
Description | Land area is 2364 sqm, Construction is conventional all indoor class
Transformer size is 2x15/25MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.3% W -0.5%,2025 S -2.1% W -0.6%2026 S -1.5% W -1.2%2027 S -1.8% W -1.0
Load Category | Domestic
Localities | Supplies Ferny Grove, Keperra, Mitchelton, Upper Kedron
|  |  |  | Latest Peak Compensated Load |  |  |  | 24.7 MVA on 17/03/2023 at 16:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 26.7 | 26.1 | 25.7 | 25.3 | 25 | 20.1 | 20 | 19.9 | 19.7 | 19.5
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
50 PoE Load (MVA) | 24.7 | 24.2 | 23.8 | 23.4 | 23.2 | 18.8 | 18.7 | 18.6 | 18.4 | 18.2
50 PoE Load > 95% (MVA) | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Hours PA > 95% Peak Load | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Raw LAR (MVA)
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## GYM
Zone Summary Information and Peak Load Forecast
Substation | GYM - Gympie (132/11kV) | [5 empty] | Supply | WLG - WOOLOOGA 132 CP
Description | Land area is 21870 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x20/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.0% W -0.1%,2025 S -2.5% W -0.2%2026 S -0.6% W -0.7%2027 S -1.2% W -0.8
Load Category | Mixed Domestic
Localities | Supplies Anderleigh, Araluen, Banks Pocket, Bells Bridge, Calico Creek, Canina, Cedar Pocket, Chatsworth, Coondoo, Corella, Curra, Downsfield, East Deep Creek, Fishermans Pocket, Gilldora, Goomboorian, Greens Creek, Gympie, Jones Hill, Kia Ora, Lagoon Pocket, Langshaw, Long Flat, Mcintosh Creek, Monkland, Mooloo, Neerdie, North Deep Creek, Pie Creek, Ross Creek, Southside, Tamaree, The Palms, Two Mile, Veteran, Victory Heights, Widgee Crossing North, Widgee Crossing South, Wilsons Pocket, Wolvi
|  |  |  | Latest Peak Compensated Load |  |  |  | 25 MVA on 13/02/2023 at 17:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 27.9 | 27.2 | 27 | 26.7 | 26.7 | 20.2 | 21.4 | 21.3 | 21.2 | 21
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998
ECC Rating (MVA) | 30.5 | 30.5 | 30.5 | 30.5 | 30.5 | 32 | 32 | 32 | 32 | 32
50 PoE Load (MVA) | 26.3 | 25.6 | 25.5 | 25.2 | 25.1 | 19.3 | 20.5 | 20.4 | 20.3 | 20.1
50 PoE Load > 95% (MVA) | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1 | 1 | 1 | 1 | 1
Hours PA > 95% Peak Load | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
Raw LAR (MVA)
2HR Rating (MVA) | 33.5 | 33.5 | 33.5 | 33.5 | 33.5 | 35.1 | 35.1 | 35.1 | 35.1 | 35.1
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO
Capacity for Embedded Generation (MVA) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
N-1 Capacity for Embedded Generation (MVA) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## GYN
Zone Summary Information and Peak Load Forecast
Substation | GYN - Gympie North (33/11kV) | [5 empty] | Supply | GYM - Gympie BS
Description | Land area is 3350 sqm, Construction is single modular class
Transformer size is 2x15/25MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.3% W -0.2%,2025 S -1.5% W -0.2%2026 S -0.8% W -0.8%2027 S -1.4% W -0.9
Load Category | Domestic
Localities | Supplies Fishermans Pocket, Glastonbury, Gympie, Langshaw, Marys Creek, Nahrunda, Pie Creek, Scrubby Creek, Southside, The Palms, Upper Glastonbury, Widgee Crossing North, Widgee Crossing South
|  |  |  | Latest Peak Compensated Load |  |  |  | 17.2 MVA on 12/02/2023 at 18:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 18.7 | 18.4 | 18.2 | 18 | 17.9 | 13.6 | 13.6 | 13.5 | 13.4 | 13.3
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.995 | 0.995 | 0.995 | 0.995 | 0.995 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
50 PoE Load (MVA) | 15.8 | 15.5 | 15.4 | 15.2 | 15.1 | 12.9 | 12.8 | 12.8 | 12.7 | 12.6
50 PoE Load > 95% (MVA) | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
Hours PA > 95% Peak Load | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Raw LAR (MVA)
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## GYS
Zone Summary Information and Peak Load Forecast
Substation | GYS - Gympie South (33/11kV) | [5 empty] | Supply | GYM - Gympie BS
Description | Land area is 3440 sqm, Construction is single modular class
Transformer size is 1x15MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.7% W -0.3%,2025 S -2.2% W -0.1%2026 S -1.4% W -0.6%2027 S -2.0% W -0.8
Load Category | Industrial
Localities | Supplies Beenaam Valley, Cedar Pocket, Cooran, East Deep Creek, Glanmire, Greens Creek, Jones Hill, Kin Kin, Kybong, Monkland, Mothar Mountain, Neusa Vale, Tandur, The Dawn, Traveston, Wolvi, Woondum
|  |  |  | Latest Peak Compensated Load |  |  |  | 7.3 MVA on 13/02/2023 at 16:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Day | Night
NCC Rating (MVA) | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 7.7 | 8.9 | 8.8 | 8.6 | 8.6 | 7.5 | 8.7 | 8.7 | 8.6 | 8.6
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.967 | 0.967 | 0.967 | 0.967 | 0.967 | 0.978 | 0.978 | 0.978 | 0.971 | 0.978
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 7.4 | 8.6 | 8.5 | 8.4 | 8.3 | 7.3 | 8.5 | 8.5 | 8.4 | 8.4
50 PoE Load > 95% (MVA) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Hours PA > 95% Peak Load | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
Raw LAR (MVA) | 7.4 | 8.6 | 8.5 | 8.4 | 8.3 | 7.3 | 8.5 | 8.5 | 8.4 | 8.4
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 5.9 | 5.9 | 5.9 | 5.9 | 5.9 | 5.9 | 5.9 | 5.9 | 5.9 | 5.9
Mobile Plant Avail (MVA) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## HTN
Zone Summary Information and Peak Load Forecast
Substation | HTN - Hamilton (33/11kV) | [5 empty] | Supply | NGE - Nudgee BS
Description | Land area is 1910 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x15/25MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.8% W 0.5%, 2025 S -1.8% W 0.4%,2026 S -0.6% W 0.2%,2027 S -0.8% W 0.8%
Load Category | Mixed Industrial
Localities | Supplies Albion, Ascot, Bulimba, Eagle Farm, Hamilton, Newstead
|  |  |  | Latest Peak Compensated Load |  |  |  | 20.5 MVA on 17/03/2023 at 16:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 54.9 | 54.9 | 54.9 | 54.9 | 54.9 | 54.9 | 54.9 | 54.9 | 54.9 | 54.9
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 23 | 22.7 | 22.5 | 22.4 | 22.4 | 16.7 | 16.8 | 16.8 | 16.9 | 17
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.989 | 0.989 | 0.989 | 0.989 | 0.989 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5
50 PoE Load (MVA) | 21.8 | 21.4 | 21.3 | 21.2 | 21.2 | 16 | 16.1 | 16.2 | 16.2 | 16.3
50 PoE Load > 95% (MVA) | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
Hours PA > 95% Peak Load | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
Raw LAR (MVA)
2HR Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## HTL
Zone Summary Information and Peak Load Forecast
Substation | HTL - Hamilton Lands (33/11kV) | [5 empty] | Supply | MDH - Meeandah BS
Description | Land area is 2760 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x15/25MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 6.3% W 4.3%, 2025 S 2.5% W 4.4%, 2026 S 2.8% W 3.6%, 2027 S 2.1% W 3.3%
Load Category | Industrial
Localities | Supplies Eagle Farm, Hamilton
|  |  |  | Latest Peak Compensated Load |  |  |  | 11.9 MVA on 01/02/2023 at 11:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Day | Day | Day | Day
NCC Rating (MVA) | 52.4 | 52.4 | 52.4 | 52.4 | 52.4 | 52.4 | 52.4 | 52.4 | 52.4 | 52.4
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 13.9 | 14.9 | 15.3 | 15.6 | 16 | 10.3 | 11.1 | 11.6 | 12 | 12.4
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.944 | 0.944 | 0.944 | 0.944 | 0.944 | 0.953 | 0.953 | 0.953 | 0.953 | 0.953
ECC Rating (MVA) | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 31.3 | 31.3 | 31.3 | 31.3 | 31.3
50 PoE Load (MVA) | 13.6 | 14.5 | 14.9 | 15.2 | 15.7 | 9.9 | 10.8 | 11.2 | 11.6 | 12
50 PoE Load > 95% (MVA) | 0.7 | 0.7 | 0.7 | 0.8 | 0.8 | 0.5 | 0.5 | 0.6 | 0.6 | 0.6
Hours PA > 95% Peak Load | 20.5 | 20.5 | 20.5 | 20.5 | 20.5 | 20.5 | 20.5 | 20.5 | 20.5 | 20.5
Raw LAR (MVA)
2HR Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## HWD
Zone Summary Information and Peak Load Forecast
Substation | HWD - Heathwood (33/11kV) | [5 empty] | Supply | BPN - Browns Plains BS
Description | Land area is 3530 sqm, Construction is multiple modular class
Transformer size is 2x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 1.1 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.1% W -0.3%,2025 S -1.8% W -0.2%2026 S -1.1% W -0.6%2027 S -1.8% W -0.4
Load Category | Industrial
Localities | Supplies Doolandella, Forest Lake, Forestdale, Heathwood, Larapinta, Pallara
|  |  |  | Latest Peak Compensated Load |  |  |  | 30.9 MVA on 17/03/2023 at 17:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 52.1 | 52.1 | 52.1 | 52.1 | 52.1 | 52.1 | 52.1 | 52.1 | 52.1 | 52.1
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 31.9 | 31.3 | 31 | 30.4 | 30.1 | 26 | 25.9 | 25.8 | 25.7 | 25.6
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998
ECC Rating (MVA) | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5
50 PoE Load (MVA) | 29.9 | 29.4 | 29 | 28.5 | 28.3 | 25.2 | 25.1 | 25.1 | 24.9 | 24.8
50 PoE Load > 95% (MVA) | 1.5 | 1.5 | 1.5 | 1.4 | 1.4 | 1.3 | 1.3 | 1.3 | 1.2 | 1.2
Hours PA > 95% Peak Load | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
Raw LAR (MVA) | SUMMER 2023/24: 1.1; SUMMER 2024/25: 0.6; SUMMER 2025/26: 0.2
2HR Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## HDN
Zone Summary Information and Peak Load Forecast
Substation | HDN - Helidon (33/11kV) | [5 empty] | Supply | PRG - Postmans Ridge BS
Description | Land area is 15935 sqm, Construction is pipework and shed class
Transformer size is 1x5/8MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.1% W 0.7%, 2025 S -2.2% W 0.7%,2026 S -1.5% W 0.2%,2027 S -1.9% W 0.1%
Load Category | Domestic
Localities | Supplies Carpendale, Grantham, Helidon, Helidon Spa, Iredale, Ringwood, Veradilla
|  |  |  | Latest Peak Compensated Load |  |  |  | 2.7 MVA on 04/01/2023 at 16:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 3.1 | 3 | 3 | 2.9 | 2.9 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.973 | 0.973 | 0.973 | 0.973 | 0.973 | 0.993 | 0.993 | 0.993 | 0.993 | 0.993
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 2.9 | 2.8 | 2.8 | 2.7 | 2.7 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3
50 PoE Load > 95% (MVA) | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Hours PA > 95% Peak Load | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Raw LAR (MVA) | 2.9 | 2.8 | 2.8 | 2.7 | 2.7 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1
Mobile Plant Avail (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## HMT
Zone Summary Information and Peak Load Forecast
Substation | HMT - Hemmant (33/11kV) | [5 empty] | Supply | DBS - Doboy BS
Description | Land area is 2180 sqm, Construction is conventional indoor/outdoor class
Transformer size is 1x10/12.5/15MVA ONAN/ONAF/OFAF 33/11kV;1x15/25MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.9% W -1.2%,2025 S -0.9% W -0.0%2026 S -0.4% W -0.3%2027 S -1.1% W -0.8
Load Category | Industrial
Localities | Supplies Hemmant, Murarrie, Tingalpa
|  |  |  | Latest Peak Compensated Load |  |  |  | 8.2 MVA on 31/01/2023 at 15:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Day | Day | Day | Day
NCC Rating (MVA) | 37.7 | 37.7 | 37.7 | 37.7 | 37.7 | 37.7 | 37.7 | 37.7 | 37.7 | 37.7
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 10.7 | 10.6 | 10.6 | 10.5 | 10.4 | 6.5 | 7.7 | 7.7 | 7.7 | 7.6
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.983 | 0.983 | 0.983 | 0.983 | 0.983 | 0.989 | 0.989 | 0.989 | 0.989 | 0.989
ECC Rating (MVA) | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5
50 PoE Load (MVA) | 10.3 | 10.2 | 10.2 | 10.1 | 10 | 6.4 | 7.6 | 7.6 | 7.6 | 7.5
50 PoE Load > 95% (MVA) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4
Hours PA > 95% Peak Load | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
Raw LAR (MVA)
2HR Rating (MVA) | 18.8 | 18.8 | 18.8 | 18.8 | 18.8 | 21 | 21 | 21 | 21 | 21
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
N-1 Capacity for Embedded Generation (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## HDA
Zone Summary Information and Peak Load Forecast
Substation | HDA - Hendra (33/11kV) | [5 empty] | Supply | NGE - Nudgee BS
Description | Land area is 2270 sqm, Construction is conventional indoor/outdoor class
Transformer size is 1x15/25MVA ONAN/ODAF;1x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.4% W 0.3%, 2025 S -2.8% W 0.3%,2026 S -1.0% W 0.0%,2027 S -1.5% W -0.1
Load Category | Domestic
Localities | Supplies Ascot, Clayfield, Eagle Farm, Hamilton, Hendra, Nundah
|  |  |  | Latest Peak Compensated Load |  |  |  | 17.7 MVA on 17/03/2023 at 16:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 18.5 | 18 | 17.8 | 19.6 | 19.5 | 13.1 | 13.2 | 13.2 | 14.8 | 14.8
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.987 | 0.987 | 0.987 | 0.987 | 0.987 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
50 PoE Load (MVA) | 17.1 | 16.7 | 16.5 | 18.3 | 18.2 | 12.6 | 12.7 | 12.7 | 14.3 | 14.3
50 PoE Load > 95% (MVA) | 0.9 | 0.8 | 0.8 | 0.9 | 0.9 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7
Hours PA > 95% Peak Load | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Raw LAR (MVA)
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## HPK
Zone Summary Information and Peak Load Forecast
Substation | HPK - Holland Park (33/11kV) | [5 empty] | Supply | CPR - Coorparoo BS
Description | Land area is 1120 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x15/20MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.9% W 0.6%, 2025 S -2.2% W 0.7%,2026 S -0.8% W 0.2%,2027 S -1.2% W 0.1%
Load Category | Domestic
Localities | Supplies Annerley, Coorparoo, Greenslopes, Holland Park, Holland Park West, Tarragindi
|  |  |  | Latest Peak Compensated Load |  |  |  | 24.3 MVA on 17/03/2023 at 16:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 42.4 | 42.4 | 42.4 | 42.4 | 42.4 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 26.1 | 25.5 | 25.3 | 25 | 25 | 20.9 | 21 | 21.2 | 21.3 | 21.3
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.994 | 0.994 | 0.994 | 0.994 | 0.994 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 22.4 | 22.4 | 22.4 | 22.4 | 22.4 | 26.3 | 26.3 | 26.3 | 26.3 | 26.3
50 PoE Load (MVA) | 24.9 | 24.3 | 24.1 | 23.8 | 23.8 | 19.7 | 19.9 | 20 | 20.1 | 20.1
50 PoE Load > 95% (MVA) | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1 | 1 | 1 | 1 | 1
Hours PA > 95% Peak Load | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
Raw LAR (MVA) | SUMMER 2023/24: 2.5; SUMMER 2024/25: 1.9; SUMMER 2025/26: 1.7; SUMMER 2026/27: 1.4; SUMMER 2027/28: 1.4
2HR Rating (MVA) | 27 | 27 | 27 | 27 | 27 | 30 | 30 | 30 | 30 | 30
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95
N-1 Capacity for Embedded Generation (MVA) | 2.475 | 2.475 | 2.475 | 2.475 | 2.475 | 2.475 | 2.475 | 2.475 | 2.475 | 2.475
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## HPE
Zone Summary Information and Peak Load Forecast
Substation | HPE - Holland Park East (33/11kV) | [5 empty] | Supply | BBS - Belmont BS
Description | Land area is 1820 sqm, Construction is multiple modular class
Transformer size is 2x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.5% W 0.5%, 2025 S -1.4% W 0.5%,2026 S -0.7% W 0.1%,2027 S -1.2% W 0.0%
Load Category | Domestic
Localities | Supplies Camp Hill, Carina Heights, Carindale, Coorparoo, Holland Park, Holland Park West, Mansfield, Mount Gravatt, Mount Gravatt East
|  |  |  | Latest Peak Compensated Load |  |  |  | 19.2 MVA on 17/03/2023 at 16:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 59.9 | 59.9 | 59.9 | 59.9 | 59.9 | 59.9 | 59.9 | 59.9 | 59.9 | 59.9
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 20.8 | 20.5 | 20.4 | 20.1 | 20.1 | 17.8 | 17.9 | 17.9 | 18 | 18
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.991 | 0.991 | 0.991 | 0.991 | 0.991 | 0.996 | 0.996 | 0.996 | 0.996 | 0.996
ECC Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
50 PoE Load (MVA) | 19.8 | 19.5 | 19.4 | 19.1 | 19.1 | 16.5 | 16.6 | 16.7 | 16.7 | 16.7
50 PoE Load > 95% (MVA) | 1 | 1 | 1 | 1 | 1 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
Hours PA > 95% Peak Load | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Raw LAR (MVA)
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## HWL
Zone Summary Information and Peak Load Forecast
Substation | HWL - Hollywell (33/11kV) | [5 empty] | Supply | MDR - Molendinar BS
Description | Land area is 6000 sqm, Construction is multiple modular class
Transformer size is 2x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.7% W 0.4%, 2025 S -0.9% W 0.5%,2026 S -0.1% W 0.0%,2027 S -0.8% W -0.1
Load Category | Domestic
Localities | Supplies Arundel, Biggera Waters, Coombabah, Hollywell, Paradise Point, Runaway Bay
|  |  |  | Latest Peak Compensated Load |  |  |  | 36.6 MVA on 03/02/2023 at 18:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 40.7 | 40.3 | 40.3 | 40 | 40 | 30 | 30.1 | 30.2 | 30.2 | 30.2
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
50 PoE Load (MVA) | 37.2 | 36.8 | 36.8 | 36.5 | 36.6 | 28.5 | 28.6 | 28.7 | 28.7 | 28.7
50 PoE Load > 95% (MVA) | 1.9 | 1.8 | 1.8 | 1.8 | 1.8 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
Hours PA > 95% Peak Load | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
Raw LAR (MVA) | SUMMER 2023/24: 5.9; SUMMER 2024/25: 5.5; SUMMER 2025/26: 5.5; SUMMER 2026/27: 5.2; SUMMER 2027/28: 5.3
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## HIS
Zone Summary Information and Peak Load Forecast
Substation | HIS - Hope Island (33/11kV) | [5 empty] | Supply | CMA - Coomera BS
Description | Land area is 23770 sqm, Construction is multiple modular class
Transformer size is 2x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.5% W 0.4%, 2025 S -1.0% W 0.3%,2026 S -0.2% W 0.4%,2027 S -0.4% W 0.3%
Load Category | Domestic
Localities | Supplies Helensvale, Hope Island, Paradise Point
|  |  |  | Latest Peak Compensated Load |  |  |  | 38.5 MVA on 03/02/2023 at 17:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 58.1 | 58.1 | 58.1 | 58.1 | 58.1 | 58.1 | 58.1 | 58.1 | 58.1 | 58.1
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 39 | 38.6 | 38.5 | 38.4 | 38.7 | 31.4 | 31.5 | 31.6 | 31.8 | 31.9
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
50 PoE Load (MVA) | 36.3 | 36 | 35.9 | 35.8 | 36 | 28.1 | 28.2 | 28.3 | 28.4 | 28.5
50 PoE Load > 95% (MVA) | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
Hours PA > 95% Peak Load | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Raw LAR (MVA) | SUMMER 2023/24: 5; SUMMER 2024/25: 4.7; SUMMER 2025/26: 4.6; SUMMER 2026/27: 4.5; SUMMER 2027/28: 4.7
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## IBS
Zone Summary Information and Peak Load Forecast
Substation | IBS - Ibis (33/11kV) | [5 empty] | Supply | IBS - Ibis BS
Description | Land area is 14800 sqm, Construction is pipework and shed class
Transformer size is 1x5/8MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.9% W 0.4%, 2025 S -1.3% W 0.3%,2026 S -0.4% W -0.1%2027 S -0.5% W 0.0%
Load Category | Domestic
Localities | Supplies Karragarra Island, Lamb Island, Macleay Island, North Stradbroke Is, Russell Island
|  |  |  | Latest Peak Compensated Load |  |  |  | 0.5 MVA on 04/07/2022 at 17:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.974 | 0.974 | 0.974 | 0.974 | 0.974 | 0.934 | 0.934 | 0.934 | 0.934 | 0.934
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
50 PoE Load > 95% (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hours PA > 95% Peak Load | 1572.5 | 1572.5 | 1572.5 | 1572.5 | 1572.5 | 1572.5 | 1572.5 | 1572.5 | 1572.5 | 1572.5
Raw LAR (MVA) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mobile Plant Avail (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## IBL
Zone Summary Information and Peak Load Forecast
Substation | IBL - Imbil (33/11kV) | [5 empty] | Supply | GYM - Gympie BS
Description | Land area is 2264 sqm, Construction is pipework and shed class
Transformer size is 1x5/8MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.0% W -0.4%,2025 S -1.8% W -0.3%2026 S -1.1% W -0.8%2027 S -1.7% W -0.9
Load Category | Industrial
Localities | Supplies Bella Creek, Belli Park, Bollier, Brooloo, Imbil, Lake Borumba, Moy Pocket
|  |  |  | Latest Peak Compensated Load |  |  |  | 2.6 MVA on 08/12/2022 at 14:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Night | Night | Night | Night | Day | Day | Day | Day | Day
NCC Rating (MVA) | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 2.5 | 2.2 | 2.2 | 2.2 | 2.2 | 2.8 | 2.8 | 2.8 | 2.7 | 2.7
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.997 | 0.999 | 1 | 1 | 1 | 0.891 | 0.891 | 0.891 | 0.891 | 0.891
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 2.3 | 2.5 | 2.5 | 2.5 | 2.5 | 2.7 | 2.6 | 2.6 | 2.6 | 2.6
50 PoE Load > 95% (MVA) | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Hours PA > 95% Peak Load | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5
Raw LAR (MVA) | 2.3 | 2.5 | 2.5 | 2.5 | 2.5 | 2.7 | 2.6 | 2.6 | 2.6 | 2.6
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Mobile Plant Avail (MVA) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## INA
Zone Summary Information and Peak Load Forecast
Substation | INA - Inala (33/11kV) | [5 empty] | Supply | RLD - Richlands BS
Description | Land area is 2200 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.6% W 0.6%, 2025 S -1.1% W 0.8%,2026 S -0.4% W 0.3%,2027 S -0.7% W 0.4%
Load Category | Domestic
Localities | Supplies Darra, Doolandella, Durack, Ellen Grove, Forest Lake, Inala, Oxley, Richlands, Wacol
|  |  |  | Latest Peak Compensated Load |  |  |  | 31.3 MVA on 17/03/2023 at 17:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 59.9 | 59.9 | 59.9 | 59.9 | 59.9 | 59.9 | 59.9 | 59.9 | 59.9 | 59.9
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 32.9 | 32.6 | 32.5 | 32.2 | 32.3 | 30.2 | 30.4 | 30.6 | 30.7 | 30.8
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
50 PoE Load (MVA) | 31.1 | 30.7 | 30.6 | 30.4 | 30.5 | 27.7 | 27.9 | 28.1 | 28.2 | 28.3
50 PoE Load > 95% (MVA) | 1.6 | 1.5 | 1.5 | 1.5 | 1.5 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
Hours PA > 95% Peak Load | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
Raw LAR (MVA)
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## IDY
Zone Summary Information and Peak Load Forecast
Substation | IDY - Indooroopilly (33/11kV) | [5 empty] | Supply | TSN - Tennyson BS
Description | Land area is 3100 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.1% W -0.1%,2025 S -1.8% W 0.4%,2026 S -1.1% W -0.1%2027 S -1.6% W -0.1
Load Category | Mixed Industrial
Localities | Supplies Chapel Hill, Indooroopilly, Taringa, Toowong
|  |  |  | Latest Peak Compensated Load |  |  |  | 22.8 MVA on 03/02/2023 at 12:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Day | Day | Night | Day
NCC Rating (MVA) | 54.1 | 54.1 | 54.1 | 54.1 | 54.1 | 54.1 | 54.1 | 54.1 | 54.1 | 54.1
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 23.8 | 23.3 | 23.1 | 22.7 | 22.6 | 15.2 | 15.1 | 15.2 | 15.2 | 15.2
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.987 | 0.987 | 0.987 | 0.987 | 0.987 | 0.999 | 0.999 | 0.999 | 0.998 | 0.999
ECC Rating (MVA) | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5
50 PoE Load (MVA) | 22.6 | 22.2 | 22 | 21.6 | 21.5 | 14.5 | 14.5 | 14.6 | 14.6 | 14.5
50 PoE Load > 95% (MVA) | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Hours PA > 95% Peak Load | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5
Raw LAR (MVA)
2HR Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## IPL
Zone Summary Information and Peak Load Forecast
Substation | IPL - Innisplain (33/11kV) | [5 empty] | Supply | BDS - Beaudesert BS
Description | Land area is 4050 sqm, Construction is mini-modular (skid) class
Transformer size is 1x5/8MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 4.5% W 1.3%, 2025 S -0.4% W 1.3%,2026 S 0.2% W 0.7%, 2027 S -0.5% W 0.5%
Load Category | Domestic
Localities | Supplies Barney View, Chinghee Creek, Christmas Creek, Croftby, Darlington, Hillview, Innisplain, Josephville, Knapp Creek, Kooralbyn, Lamington, Laravale, Maroon, Mount Barney, Mount Gipps, Mount Lindesay, Oaky Creek, O'reilly, Palen Creek, Rathdowney, Running Creek, Tabooba, Tamrookum, Tamrookum Creek
|  |  |  | Latest Peak Compensated Load |  |  |  | 4.1 MVA on 18/03/2023 at 18:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4 | 4.1 | 4.1 | 4.2 | 4.2
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.988 | 0.988 | 0.988 | 0.988 | 0.988 | 0.993 | 0.993 | 0.993 | 0.993 | 0.993
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 3.9 | 3.9 | 4 | 4 | 4
50 PoE Load > 95% (MVA) | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hours PA > 95% Peak Load | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5
Raw LAR (MVA) | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 3.9 | 3.9 | 4 | 4 | 4
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8
Mobile Plant Avail (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## IPS
Zone Summary Information and Peak Load Forecast
Substation | IPS - Ipswich South (33/11kV) | [5 empty] | Supply | RVW - Raceview BS
Description | Land area is 4050 sqm, Construction is single modular class
Transformer size is 2x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 5.6% W 3.0%, 2025 S 0.6% W 2.9%, 2026 S 1.3% W 2.3%, 2027 S 0.4% W 1.9%
Load Category | Domestic
Localities | Supplies Amberley, Churchill, Deebing Heights, Eastern Heights, Flinders View, Ipswich, Leichhardt, One Mile, Purga, Raceview, Ripley, South Ripley, West Ipswich, Wulkuraka, Yamanto
|  |  |  | Latest Peak Compensated Load |  |  |  | 22.2 MVA on 12/02/2023 at 17:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 24.6 | 24.7 | 25 | 25.1 | 25.5 | 16.3 | 16.8 | 17.3 | 17.7 | 18
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
50 PoE Load (MVA) | 22.4 | 22.5 | 22.8 | 22.9 | 23.3 | 15.7 | 16.2 | 16.7 | 17.1 | 17.4
50 PoE Load > 95% (MVA) | 1.1 | 1.1 | 1.1 | 1.1 | 1.2 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9
Hours PA > 95% Peak Load | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Raw LAR (MVA)
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## JBB
Zone Summary Information and Peak Load Forecast
Substation | JBB - Jimboomba (33/11kV) | [5 empty] | Supply | JBB - Jimboomba BS
Description | Land area is 40470 sqm, Construction is multiple modular class
Transformer size is 1x15/25MVA ONAN/ONAF;1x15MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 4.4% W 1.6%, 2025 S -0.5% W 1.9%,2026 S 0.3% W 1.4%, 2027 S -0.9% W 0.5%
Load Category | Domestic
Localities | Supplies Allenview, Cedar Grove, Cedar Vale, Chambers Flat, Jimboomba, Kagaru, Logan Reserve, Logan Village, Mundoolun, Munruben, North Maclean, South Maclean, Stockleigh, Tamborine, Undullah, Veresdale Scrub, Woodhill, Yarrabilba
|  |  |  | Latest Peak Compensated Load |  |  |  | 33.8 MVA on 12/02/2023 at 17:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 37.9 | 37.7 | 39.9 | 41.3 | 43.4 | 25.3 | 25.7 | 26.2 | 28.5 | 31.7
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.995 | 0.995 | 0.995 | 0.995 | 0.995 | 0.995 | 0.995 | 0.995 | 0.995 | 0.995
ECC Rating (MVA) | 20.3 | 20.3 | 20.3 | 20.3 | 20.3 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5
50 PoE Load (MVA) | 33.9 | 33.7 | 35.9 | 37.3 | 39.4 | 23.9 | 24.3 | 24.8 | 27.1 | 30.3
50 PoE Load > 95% (MVA) | 1.7 | 1.7 | 1.8 | 1.9 | 2 | 1.2 | 1.2 | 1.2 | 1.4 | 1.5
Hours PA > 95% Peak Load | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
Raw LAR (MVA) | 13.6 | 13.4 | 15.6 | 17 | 19.1 | 1.4 | 1.8 | 2.3 | 4.6 | 7.8
2HR Rating (MVA) | 21.8 | 21.8 | 21.8 | 21.8 | 21.8 | 24 | 24 | 24 | 24 | 24
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9
Mobile Plant Avail (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA) | SUMMER 2025/26: 0.7; SUMMER 2026/27: 2.1; SUMMER 2027/28: 4.2
LARc (MW) | SUMMER 2025/26: 0.6965; SUMMER 2026/27: 2.0895; SUMMER 2027/28: 4.179
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes
Back to Index

## JDL
Zone Summary Information and Peak Load Forecast
Substation | JDL - Jindalee (33/11kV) | [5 empty] | Supply | RLD - Richlands BS
Description | Land area is 1561 sqm, Construction is conventional all indoor class
Transformer size is 2x12.5/15MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.8% W -0.5%,2025 S -2.0% W -0.6%2026 S -1.3% W -0.8%2027 S -1.9% W -0.7
Load Category | Domestic
Localities | Supplies Jindalee, Kenmore, Middle Park, Mount Ommaney, Seventeen Mile Rocks, Sinnamon Park, Westlake
|  |  |  | Latest Peak Compensated Load |  |  |  | 13.9 MVA on 17/03/2023 at 17:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Night | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 14.8 | 14.5 | 14.3 | 14 | 13.9 | 10.4 | 10.4 | 10.3 | 10.2 | 10.1
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.994 | 0.995 | 0.994 | 0.994 | 0.994 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 18.8 | 18.8 | 18.8 | 18.8 | 18.8 | 21 | 21 | 21 | 21 | 21
50 PoE Load (MVA) | 13.8 | 13.6 | 13.4 | 13.1 | 13 | 9.5 | 9.4 | 9.4 | 9.3 | 9.2
50 PoE Load > 95% (MVA) | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hours PA > 95% Peak Load | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
Raw LAR (MVA)
2HR Rating (MVA) | 20.3 | 20.3 | 20.3 | 20.3 | 20.3 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
N-1 Capacity for Embedded Generation (MVA) | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## KBR
Zone Summary Information and Peak Load Forecast
Substation | KBR - Kalbar (33/11kV) | [5 empty] | Supply | RVW - Raceview BS
Description | Land area is 6294 sqm, Construction is pipework and shed class
Transformer size is 1x15MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.5% W 0.3%, 2025 S -1.3% W 0.3%,2026 S -0.7% W -0.3%2027 S -1.3% W -0.5
Load Category | Domestic
Localities | Supplies Anthony, Aratula, Blantyre, Boonah, Charlwood, Clumber, Coulson, Fassifern, Fassifern Valley, Frazerview, Hoya, Kalbar, Kents Lagoon, Kents Pocket, Kulgun, Milbong, Milora, Moogerah, Moorang, Morwincha, Mount Alford, Mount Edwards, Munbilla, Obum Obum, Roadvale, Rosevale, Silverdale, Tarome, Templin, Teviotville, Wyaralong
|  |  |  | Latest Peak Compensated Load |  |  |  | 7.7 MVA on 07/12/2022 at 18:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 17.8 | 17.8 | 17.8 | 17.8 | 17.8 | 18 | 18 | 18 | 18 | 18
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 8.9 | 8.8 | 8.7 | 8.6 | 8.6 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.999 | 1 | 1 | 1 | 1 | 0.981 | 0.981 | 0.981 | 0.981 | 0.981
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 8.1 | 8.1 | 8 | 7.9 | 7.9 | 5.9 | 6 | 6 | 6 | 5.9
50 PoE Load > 95% (MVA) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Hours PA > 95% Peak Load | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
Raw LAR (MVA) | 8.1 | 8.1 | 8 | 7.9 | 7.9 | 5.9 | 6 | 6 | 6 | 5.9
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4
Mobile Plant Avail (MVA) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## KLG
Zone Summary Information and Peak Load Forecast
Substation | KLG - Kallangur (33/11kV) | [5 empty] | Supply | GFN - Griffin BS
Description | Land area is 2020 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x10/12MVA ONAN/ONAF;1x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.7% W 0.4%, 2025 S -1.9% W 0.7%,2026 S -0.7% W 0.2%,2027 S -1.3% W 0.1%
Load Category | Domestic
Localities | Supplies Griffin, Kallangur, Kurwongbah, Lawnton, Mango Hill, Murrumba Downs, Petrie
|  |  |  | Latest Peak Compensated Load |  |  |  | 37.6 MVA on 17/03/2023 at 17:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 40.6 | 39.8 | 40.5 | 41.9 | 42.8 | 30.4 | 30.5 | 31.4 | 33 | 33.8
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 29.9 | 29.9 | 29.9 | 29.9 | 29.9 | 32.9 | 32.9 | 32.9 | 32.9 | 32.9
50 PoE Load (MVA) | 37.3 | 36.6 | 37.3 | 38.8 | 39.6 | 28.3 | 28.4 | 29.4 | 30.9 | 31.7
50 PoE Load > 95% (MVA) | 1.9 | 1.8 | 1.9 | 1.9 | 2 | 1.4 | 1.4 | 1.5 | 1.5 | 1.6
Hours PA > 95% Peak Load | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Raw LAR (MVA) | SUMMER 2023/24: 7.4; SUMMER 2024/25: 6.7; SUMMER 2025/26: 7.4; SUMMER 2026/27: 8.9; SUMMER 2027/28: 9.7
2HR Rating (MVA) | 32.3 | 32.3 | 32.3 | 32.3 | 32.3 | 35.8 | 35.8 | 35.8 | 35.8 | 35.8
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
LARc (MVA) | SUMMER 2027/28: 0.3
LARc (MW) | SUMMER 2027/28: 0.3
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes
Back to Index

## KBN
Zone Summary Information and Peak Load Forecast
Substation | KBN - Karrabin (33/11kV) | [5 empty] | Supply | ABM - Abermain BS
Description | Land area is 3807 sqm, Construction is multiple modular class
Transformer size is 1x15/25MVA ONAN/ONAF;1x15MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 4.7% W 2.3%, 2025 S -0.2% W 2.4%,2026 S 0.7% W 1.8%, 2027 S 0.1% W 1.7%
Load Category | Domestic
Localities | Supplies Amberley, Blacksoil, Borallon, Brassall, Coalfalls, Fairney View, Fernvale, Haigslea, Ironbark, Karrabin, Leichhardt, Muirlea, Pine Mountain, Rosewood, Sadliers Crossing, Thagoona, Walloon, Wanora, Wulkuraka
|  |  |  | Latest Peak Compensated Load |  |  |  | 19.9 MVA on 12/02/2023 at 17:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 34.5 | 34.5 | 34.5 | 34.5 | 34.5 | 34.5 | 34.5 | 34.5 | 34.5 | 34.5
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 21.6 | 21.6 | 21.8 | 21.8 | 22 | 16.2 | 16.6 | 17 | 17.3 | 17.6
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.996 | 0.996 | 0.996 | 0.996 | 0.996
ECC Rating (MVA) | 20.3 | 20.3 | 20.3 | 20.3 | 20.3 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5
50 PoE Load (MVA) | 19.9 | 19.9 | 20 | 20.1 | 20.3 | 14.9 | 15.3 | 15.6 | 15.9 | 16.2
50 PoE Load > 95% (MVA) | 1 | 1 | 1 | 1 | 1 | 0.7 | 0.8 | 0.8 | 0.8 | 0.8
Hours PA > 95% Peak Load | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5
Raw LAR (MVA)
2HR Rating (MVA) | 21.8 | 21.8 | 21.8 | 21.8 | 21.8 | 24 | 24 | 24 | 24 | 24
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7
Mobile Plant Avail (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## KWA
Zone Summary Information and Peak Load Forecast
Substation | KWA - Kawana (132/11kV) | [5 empty] | Supply | PWD - PALMWOODS 132 CP
Description | Land area is 5120 sqm, Construction is conventional indoor/outdoor class
Transformer size is 1x18/22.5/30MVA ONAN/ODAN/ODAF;1x30MVA ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.3% W -1.0%,2025 S -1.6% W -1.2%2026 S -1.0% W -0.6%2027 S -1.6% W -0.7
Load Category | Mixed Industrial
Localities | Supplies Birtinya, Bokarina, Buddina, Currimundi, Minyama, Mooloolaba, Parrearra, Warana
|  |  |  | Latest Peak Compensated Load |  |  |  | 26.2 MVA on 13/02/2023 at 17:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 27.9 | 27.4 | 27.1 | 26.7 | 26.7 | 22.4 | 22.2 | 21.9 | 21.8 | 21.6
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.991 | 0.991 | 0.991 | 0.991 | 0.991 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 34.5 | 34.5 | 34.5 | 34.5 | 34.5 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6
50 PoE Load (MVA) | 25.7 | 25.3 | 25 | 24.6 | 24.6 | 21.3 | 21.1 | 20.8 | 20.7 | 20.6
50 PoE Load > 95% (MVA) | 1.3 | 1.3 | 1.3 | 1.2 | 1.2 | 1.1 | 1.1 | 1 | 1 | 1
Hours PA > 95% Peak Load | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Raw LAR (MVA)
2HR Rating (MVA) | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 42 | 42 | 42 | 42 | 42
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO
Capacity for Embedded Generation (MVA) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## KRN
Zone Summary Information and Peak Load Forecast
Substation | KRN - Kedron (33/11kV) | [5 empty] | Supply | SFD - Stafford BS
Description | Land area is 2289 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.5% W 0.6%, 2025 S -1.4% W 0.6%,2026 S -0.7% W 0.1%,2027 S -1.3% W -0.1
Load Category | Domestic
Localities | Supplies Albion, Bowen Hills, Chermside, Clayfield, Gordon Park, Grange, Kedron, Lutwyche, Stafford, Stafford Heights, Wavell Heights, Windsor, Wooloowin
|  |  |  | Latest Peak Compensated Load |  |  |  | 29.7 MVA on 17/03/2023 at 16:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 56.1 | 56.1 | 56.1 | 56.1 | 56.1 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 32 | 31.6 | 31.3 | 30.9 | 30.9 | 24.6 | 24.7 | 24.9 | 24.9 | 24.9
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
50 PoE Load (MVA) | 30.1 | 29.7 | 29.5 | 29.1 | 29 | 23.5 | 23.6 | 23.7 | 23.7 | 23.7
50 PoE Load > 95% (MVA) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2
Hours PA > 95% Peak Load | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Raw LAR (MVA)
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 24.75 | 24.75 | 24.75 | 24.75 | 24.75 | 24.75 | 24.75 | 24.75 | 24.75 | 24.75
N-1 Capacity for Embedded Generation (MVA) | 12.375 | 12.375 | 12.375 | 12.375 | 12.375 | 12.375 | 12.375 | 12.375 | 12.375 | 12.375
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## KVG
Zone Summary Information and Peak Load Forecast
Substation | KVG - Kelvin Grove (110/11kV) | [5 empty] | Supply | CBW - ASHGROVE WEST 110 CP
Description | Land area is 3564 sqm, Construction is conventional all indoor class
Transformer size is 2x30/60MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.7% W 0.4%, 2025 S -2.3% W 0.3%,2026 S -1.0% W -0.2%2027 S -1.3% W -0.4
Load Category | Mixed Industrial
Localities | Supplies Kelvin Grove, Milton
|  |  |  | Latest Peak Compensated Load |  |  |  | 18.2 MVA on 17/03/2023 at 16:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Day | Day | Day | Day
NCC Rating (MVA) | 131.6 | 131.6 | 131.6 | 131.6 | 131.6 | 131.6 | 131.6 | 131.6 | 131.6 | 131.6
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 19.4 | 18.9 | 18.7 | 18.5 | 18.5 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.995 | 0.995 | 0.995 | 0.995 | 0.995 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998
ECC Rating (MVA) | 69 | 69 | 69 | 69 | 69 | 78 | 78 | 78 | 78 | 78
50 PoE Load (MVA) | 18.1 | 17.7 | 17.5 | 17.3 | 17.2 | 12.7 | 12.8 | 12.8 | 12.8 | 12.8
50 PoE Load > 95% (MVA) | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
Hours PA > 95% Peak Load | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
Raw LAR (MVA)
2HR Rating (MVA) | 75 | 75 | 75 | 75 | 75 | 84 | 84 | 84 | 84 | 84
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
N-1 Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## KWH
Zone Summary Information and Peak Load Forecast
Substation | KWH - Kenilworth (33/11kV) | [5 empty] | Supply | NBR - Nambour BS
Description | Land area is 4810 sqm, Construction is pipework and shed class
Transformer size is 1x5/6MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.5% W 0.0%, 2025 S -1.3% W 0.1%,2026 S -0.7% W -0.5%2027 S -1.4% W -0.7
Load Category | Domestic
Localities | Supplies Belli Park, Brooloo, Cambroon, Conondale, Coolabine, Curramore, Gheerulla, Kenilworth, Kidaman Creek, Mapleton, Moy Pocket, Obi Obi
|  |  |  | Latest Peak Compensated Load |  |  |  | 4.7 MVA on 05/07/2022 at 15:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Day | Day | Day | Day | Day
NCC Rating (MVA) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 4.5 | 4.4 | 4.4 | 4.3 | 4.3 | 4.8 | 4.8 | 4.8 | 4.8 | 4.7
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 4.2 | 4.1 | 4.1 | 4 | 4 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6
50 PoE Load > 95% (MVA) | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hours PA > 95% Peak Load | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
Raw LAR (MVA) | 4.2 | 4.1 | 4.1 | 4 | 4 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
Mobile Plant Avail (MVA) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## KMR
Zone Summary Information and Peak Load Forecast
Substation | KMR - Kenmore (33/11kV) | [5 empty] | Supply | TSN - Tennyson BS
Description | Land area is 1940 sqm, Construction is conventional indoor/outdoor class
Transformer size is 1x14.5/25MVA ONAN/ONAF;1x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.1% W 0.3%, 2025 S -1.7% W 0.4%,2026 S -1.0% W 0.0%,2027 S -1.4% W 0.0%
Load Category | Domestic
Localities | Supplies Brookfield, Chapel Hill, Fig Tree Pocket, Kenmore, Kenmore Hills, Mount Coot-tha, Pinjarra Hills, Pullenvale, Upper Brookfield
|  |  |  | Latest Peak Compensated Load |  |  |  | 31.6 MVA on 12/02/2023 at 17:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 59.7 | 59.7 | 59.7 | 59.7 | 59.7 | 59.7 | 59.7 | 59.7 | 59.7 | 59.7
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 34.1 | 33.5 | 33.2 | 32.7 | 32.6 | 28.4 | 28.5 | 28.6 | 28.6 | 28.6
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
50 PoE Load (MVA) | 30.7 | 30.1 | 29.8 | 29.4 | 29.3 | 26.5 | 26.5 | 26.7 | 26.7 | 26.7
50 PoE Load > 95% (MVA) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
Hours PA > 95% Peak Load | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5
Raw LAR (MVA)
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5
N-1 Capacity for Embedded Generation (MVA) | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## KCY
Zone Summary Information and Peak Load Forecast
Substation | KCY - Kilcoy (33/11kV) | [5 empty] | Supply | BWH - Beerwah BS
Description | Land area is 4050 sqm, Construction is pipework and shed class
Transformer size is 1x15/25MVA ONAN/ONAF 33/11kV;1x5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.5% W -0.0%,2025 S -1.3% W 0.1%,2026 S -0.6% W -0.5%2027 S -1.2% W -0.6
Load Category | Mixed Industrial
Localities | Supplies Glenfern, Gregors Creek, Harlin, Hazeldean, Jimna, Kilcoy, Kingaham, Mount Archer, Mount Delaney, Mount Kilcoy, Neurum, Royston, Sandy Creek, Sheep Station Creek, Stony Creek, Villeneuve, Winya, Woolmar
|  |  |  | Latest Peak Compensated Load |  |  |  | 12.2 MVA on 12/02/2023 at 17:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Day | Day | Day | Day | Day
NCC Rating (MVA) | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 15.3 | 27.5 | 27.5 | 27.5 | 27.5
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 13.3 | 13.1 | 13 | 12.9 | 12.8 | 10.1 | 10.1 | 10.1 | 10.1 | 10
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.998
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 12.2 | 12 | 11.9 | 11.8 | 11.8 | 9.7 | 9.7 | 9.7 | 9.6 | 9.6
50 PoE Load > 95% (MVA) | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hours PA > 95% Peak Load | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
Raw LAR (MVA) | 12.2 | 12 | 11.9 | 11.8 | 11.8 | 9.7 | 9.7 | 9.7 | 9.6 | 9.6
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 6 | 6 | 6 | 6 | 6 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8
Manual Trans Avail (MVA) | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Mobile Plant Avail (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
N-1 Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## KSN
Zone Summary Information and Peak Load Forecast
Substation | KSN - Kingston (33/11kV) | [5 empty] | Supply | LGL - Loganlea BS
Description | Land area is 3080 sqm, Construction is conventional indoor/outdoor class
Transformer size is 1x15/25MVA ONAN/ODAF;1x15/25MVA ONAN/OFDAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 4.5% W 0.1%, 2025 S -0.3% W 0.6%,2026 S 0.3% W 0.4%, 2027 S 0.0% W 0.6%
Load Category | Domestic
Localities | Supplies Bethania, Crestmead, Kingston, Logan Reserve, Loganlea, Marsden, Meadowbrook, Park Ridge, Waterford, Waterford West
|  |  |  | Latest Peak Compensated Load |  |  |  | 35.7 MVA on 03/02/2023 at 19:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 59.4 | 59.4 | 59.4 | 59.4 | 59.4 | 59.4 | 59.4 | 59.4 | 59.4 | 59.4
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 38 | 37.2 | 37.3 | 37.4 | 37.7 | 35.3 | 35.4 | 35 | 35.1 | 35.4
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.994 | 0.994 | 0.994 | 0.994 | 0.994 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 30.5 | 30.5 | 30.5 | 30.5 | 30.5 | 32 | 32 | 32 | 32 | 32
50 PoE Load (MVA) | 36.5 | 35.7 | 35.8 | 35.8 | 36.1 | 31.6 | 31.6 | 31.2 | 31.3 | 31.5
50 PoE Load > 95% (MVA) | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
Hours PA > 95% Peak Load | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
Raw LAR (MVA) | SUMMER 2023/24: 6; SUMMER 2024/25: 5.2; SUMMER 2025/26: 5.3; SUMMER 2026/27: 5.3; SUMMER 2027/28: 5.6
2HR Rating (MVA) | 33.5 | 33.5 | 33.5 | 33.5 | 33.5 | 35.1 | 35.1 | 35.1 | 35.1 | 35.1
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## KRA
Zone Summary Information and Peak Load Forecast
Substation | KRA - Kirra (33/11kV) | [5 empty] | Supply | BHD - Burleigh Heads BS
Description | Land area is 5660 sqm, Construction is conventional indoor/outdoor class
Transformer size is 1x10/11MVA ONAN/ONAF;1x10/12.5MVA ONAN/ONAF;1x30MVA ONAN (66/11kV)(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 2.2 MVA
Growth Rates | 2023 W 1.0%, 2024 S 4.3% W 1.1%, 2025 S -0.4% W 1.1%,2026 S 0.2% W 0.5%, 2027 S -0.4% W 0.4%
Load Category | Mixed Domestic
Localities | Supplies Bilinga, Coolangatta, Tugun
|  |  |  | Latest Peak Compensated Load |  |  |  | 17.9 MVA on 17/03/2023 at 16:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 24.1 | 24.1 | 24.1 | 24.1 | 24.1 | 24.1 | 24.1 | 24.1 | 24.1 | 24.1
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 19.5 | 19.5 | 19.5 | 19.4 | 19.5 | 15.2 | 15.4 | 15.5 | 15.6 | 15.7
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.988 | 0.988 | 0.988 | 0.988 | 0.988 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998
ECC Rating (MVA) | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 14.3 | 14.3 | 14.3 | 14.3 | 14.3
50 PoE Load (MVA) | 18.6 | 18.5 | 18.6 | 18.5 | 18.6 | 14.5 | 14.7 | 14.8 | 14.9 | 15
50 PoE Load > 95% (MVA) | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8
Hours PA > 95% Peak Load | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5
Raw LAR (MVA) | 6 | 5.9 | 6 | 5.9 | 6 | 0.2 | 0.4 | 0.5 | 0.6 | 0.7
2HR Rating (MVA) | 13.8 | 13.8 | 13.8 | 13.8 | 13.8 | 15.4 | 15.4 | 15.4 | 15.4 | 15.4
Auto Trans Avail (MVA) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | bar: SUMMER 2023/24 to WINTER 2027
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
N-1 Capacity for Embedded Generation (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## LDR
Zone Summary Information and Peak Load Forecast
Substation | LDR - Labrador (33/11kV) | [5 empty] | Supply | MDR - Molendinar BS
Description | Land area is 3120 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x15/25MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.9% W 1.3%, 2025 S -1.1% W 1.3%,2026 S -0.4% W 0.8%,2027 S -0.2% W 1.4%
Load Category | Domestic
Localities | Supplies Arundel, Biggera Waters, Labrador, Runaway Bay
|  |  |  | Latest Peak Compensated Load |  |  |  | 22.6 MVA on 17/03/2023 at 17:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 24.5 | 24.2 | 24.1 | 24.1 | 24.3 | 21.1 | 21.4 | 21.7 | 21.9 | 22.2
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998
ECC Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
50 PoE Load (MVA) | 22.7 | 22.5 | 22.4 | 22.3 | 22.5 | 19.6 | 19.8 | 20.1 | 20.2 | 20.5
50 PoE Load > 95% (MVA) | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1 | 1 | 1 | 1 | 1
Hours PA > 95% Peak Load | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Raw LAR (MVA)
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## LLY
Zone Summary Information and Peak Load Forecast
Substation | LLY - Laidley (33/11kV) | [5 empty] | Supply | LRE - Lockrose BS
Description | Land area is 5423 sqm, Construction is pipework and shed class
Transformer size is 2x5/8MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.5% W 0.4%, 2025 S -1.3% W 0.4%,2026 S -0.6% W -0.1%2027 S -1.2% W -0.2
Load Category | Domestic
Localities | Supplies Blenheim, Calvert, Forest Hill, Glen Cairn, Grandchester, Laidley, Laidley Creek West, Laidley Heights, Laidley North, Laidley South, Lower Mount Walker, Mount Berryman, Mount Mort, Mulgowie, Plainland, Rockside, Summerholm, Thornton, Townson
|  |  |  | Latest Peak Compensated Load |  |  |  | 12 MVA on 12/02/2023 at 18:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 19.1 | 19.1 | 19.1 | 19.1 | 19.1 | 19.1 | 19.1 | 19.1 | 19.1 | 19.1
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 13.2 | 13 | 15.6 | 15.4 | 15.4 | 9.3 | 9.4 | 11.9 | 11.9 | 11.9
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.999 | 0.999 | 0.998 | 0.999 | 0.999 | 0.995 | 0.995 | 0.995 | 0.995 | 0.995
ECC Rating (MVA) | 10 | 10 | 10 | 10 | 10 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2
50 PoE Load (MVA) | 12.3 | 12.2 | 14.7 | 14.6 | 14.6 | 8.7 | 8.8 | 11.4 | 11.4 | 11.3
50 PoE Load > 95% (MVA) | 0.6 | 0.6 | 0.7 | 0.7 | 0.7 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6
Hours PA > 95% Peak Load | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5
Raw LAR (MVA) | 2.3 | 2.2 | 4.7 | 4.6 | 4.6 |  |  | 0.2 | 0.2 | 0.1
2HR Rating (MVA) | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 12 | 12 | 12 | 12 | 12
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Mobile Plant Avail (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO
Capacity for Embedded Generation (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
N-1 Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## LBH
Zone Summary Information and Peak Load Forecast
Substation | LBH - Landsborough (33/11kV) | [5 empty] | Supply | BWH - Beerwah BS
Description | Construction is single modular class
Transformer size is 1x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 4.0% W 0.3%, 2025 S -0.8% W 0.3%,2026 S -0.1% W -0.2%2027 S -0.5% W 0.0%
Load Category | Domestic
Localities | Supplies Bald Knob, Beerwah, Bells Creek, Glenview, Landsborough, Meridan Plains, Mooloolah Valley, Mount Mellum, Palmview
|  |  |  | Latest Peak Compensated Load |  |  |  | 12.8 MVA on 05/07/2022 at 17:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 13.4 | 13.3 | 13.3 | 13.2 | 13.3 | 13.7 | 13.7 | 13.8 | 13.7 | 13.7
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 12.6 | 12.5 | 12.5 | 12.4 | 12.5 | 12.5 | 12.6 | 12.6 | 12.6 | 12.6
50 PoE Load > 95% (MVA) | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
Hours PA > 95% Peak Load | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
Raw LAR (MVA) | 12.6 | 12.5 | 12.5 | 12.4 | 12.5 | 12.5 | 12.6 | 12.6 | 12.6 | 12.6
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 2.1 | 2.1 | 2.1 | 1.6 | 1.6 | 2.1 | 2.1 | 2.1 | 1.6 | 1.6
Manual Trans Avail (MVA) | 3.9 | 3.9 | 3.9 | 2.9 | 2.9 | 3.9 | 3.9 | 3.9 | 2.9 | 2.9
Mobile Plant Avail (MVA) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## LTN
Zone Summary Information and Peak Load Forecast
Substation | LTN - Lawnton (33/11kV) | [5 empty] | Supply | BRD - Brendale BS
Description | Land area is 2190 sqm, Construction is pipework and shed class
Transformer size is 1x10/12.5MVA ONAN/ONAF;1x10/15MVA ONAN/ONAF;1x15/25MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.6 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.9% W 1.5%, 2025 S -0.6% W 1.6%,2026 S 0.1% W 1.0%, 2027 S -0.2% W 1.2%
Load Category | Domestic
Localities | Supplies Bray Park, Dayboro, Joyner, King Scrub, Kurwongbah, Laceys Creek, Lawnton, Mount Pleasant, Petrie, Rush Creek, Samsonvale, Strathpine, Warner, Whiteside
|  |  |  | Latest Peak Compensated Load |  |  |  | 33.3 MVA on 17/03/2023 at 17:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 38.3 | 38 | 38.1 | 38 | 38.3 | 29 | 29.5 | 29.9 | 30.2 | 30.6
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.995 | 0.995 | 0.995 | 0.995 | 0.995 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 32.3 | 32.3 | 32.3 | 32.3 | 32.3 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1
50 PoE Load (MVA) | 35.7 | 35.4 | 35.5 | 35.4 | 35.7 | 27.5 | 27.9 | 28.4 | 28.7 | 29
50 PoE Load > 95% (MVA) | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.4 | 1.4 | 1.4 | 1.4 | 1.5
Hours PA > 95% Peak Load | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
Raw LAR (MVA) | SUMMER 2023/24: 3.4; SUMMER 2024/25: 3.1; SUMMER 2025/26: 3.2; SUMMER 2026/27: 3.1; SUMMER 2027/28: 3.4
2HR Rating (MVA) | 34.9 | 34.9 | 34.9 | 34.9 | 34.9 | 38.7 | 38.7 | 38.7 | 38.7 | 38.7
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
N-1 Capacity for Embedded Generation (MVA) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## LRE
Zone Summary Information and Peak Load Forecast
Substation | LRE - Lockrose (33/11kV) | [5 empty] | Supply | LRE - Lockrose BS
Description | Land area is 38445 sqm, Construction is conventional indoor/outdoor class
Transformer size is 1x12.5/15MVA ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.5% W 0.5%, 2025 S -1.2% W 0.6%,2026 S -0.5% W 0.1%,2027 S -1.1% W -0.0
Load Category | Domestic
Localities | Supplies Atkinsons Dam, Brightview, Churchable, Glenore Grove, Hatton Vale, Kensington Grove, Kentville, Lockrose, Lockyer Waters, Lynford, Morton Vale, Mount Tarampa, Prenzlau, Regency Downs
|  |  |  | Latest Peak Compensated Load |  |  |  | 10 MVA on 12/02/2023 at 18:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 10.9 | 10.8 | 10.8 | 10.6 | 10.6 | 7.5 | 7.5 | 7.6 | 7.6 | 7.6
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 9.9 | 9.8 | 9.8 | 9.7 | 9.7 | 7.2 | 7.2 | 7.3 | 7.3 | 7.3
50 PoE Load > 95% (MVA) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Hours PA > 95% Peak Load | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
Raw LAR (MVA) | 9.9 | 9.8 | 9.8 | 9.7 | 9.7 | 7.2 | 7.2 | 7.3 | 7.3 | 7.3
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2
Mobile Plant Avail (MVA) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## LGV
Zone Summary Information and Peak Load Forecast
Substation | LGV - Logan Village (33/11kV) | [5 empty] | Supply | JBB - Jimboomba BS
Description | Land area is 2570 sqm, Construction is single modular class
Transformer size is 1x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 5.9% W 3.4%, 2025 S 0.9% W 3.3%, 2026 S 1.5% W 2.6%, 2027 S 0.0% W 1.4%
Load Category | Domestic
Localities | Supplies Buccan, Chambers Flat, Logan Reserve, Logan Village, Park Ridge, Park Ridge South, Waterford
|  |  |  | Latest Peak Compensated Load |  |  |  | 22 MVA on 17/03/2023 at 18:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 25.1 | 25.4 | 25.8 | 25.8 | 26 | 16.3 | 16.9 | 17.4 | 17.9 | 18.1
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 1 | 1 | 1 | 1 | 1 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 23 | 23.2 | 23.5 | 23.5 | 23.7 | 15.4 | 15.9 | 16.4 | 16.8 | 17.1
50 PoE Load > 95% (MVA) | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9
Hours PA > 95% Peak Load | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
Raw LAR (MVA) | 23 | 23.2 | 23.5 | 23.5 | 23.7 | 15.4 | 15.9 | 16.4 | 16.8 | 17.1
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2
Mobile Plant Avail (MVA) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA) | 8 | 8.2 | 8.5 | 8.5 | 8.7 | 0.4 | 0.9 | 1.4 | 1.8 | 2.1
LARc (MW) | 8 | 8.2 | 8.5 | 8.5 | 8.7 | 0.4 | 0.9 | 1.4 | 1.8 | 2.1
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | bar: SUMMER 2023/24 to WINTER 2027
Back to Index

## LHM
Zone Summary Information and Peak Load Forecast
Substation | LHM - Loganholme (33/11kV) | [5 empty] | Supply | BLH - Beenleigh BS
Description | Land area is 5900 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x10/12.5MVA ONAN/ONAF;1x15/25MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.6% W -0.9%,2025 S -2.7% W -1.4%2026 S -1.9% W -1.0%2027 S -2.2% W -0.6
Load Category | Mixed Domestic
Localities | Supplies Beenleigh, Bethania, Carbrook, Cornubia, Eagleby, Loganholme, Shailer Park, Tanah Merah
|  |  |  | Latest Peak Compensated Load |  |  |  | 25.2 MVA on 17/03/2023 at 17:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 39.8 | 39.8 | 39.8 | 39.8 | 39.8 | 43 | 43 | 43 | 43 | 43
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 26.9 | 26.2 | 25.7 | 25.1 | 24.8 | 19.3 | 19.1 | 18.9 | 18.7 | 18.6
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.991 | 0.991 | 0.991 | 0.991 | 0.991 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2
50 PoE Load (MVA) | 24.5 | 23.9 | 23.4 | 22.9 | 22.6 | 17.6 | 17.4 | 17.2 | 17 | 16.9
50 PoE Load > 95% (MVA) | 1.2 | 1.2 | 1.2 | 1.1 | 1.1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8
Hours PA > 95% Peak Load | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Raw LAR (MVA)
2HR Rating (MVA) | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 33.1 | 33.1 | 33.1 | 33.1 | 33.1
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 31.1 | 31.1 | 31.1 | 31.1 | 31.1 | 31.1 | 31.1 | 31.1 | 31.1 | 31.1
N-1 Capacity for Embedded Generation (MVA) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## LGL
Zone Summary Information and Peak Load Forecast
Substation | LGL - Loganlea (33/11kV) | [5 empty] | Supply | LGL - Loganlea BS
Description | Land area is 100800 sqm, Construction is multiple modular class
Transformer size is 2x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 4.3 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.5% W 0.2%, 2025 S -2.3% W 0.4%,2026 S -1.6% W -0.2%2027 S -1.9% W -0.2
Load Category | Mixed Domestic
Localities | Supplies Kingston, Logan Central, Loganlea, Meadowbrook, Slacks Creek
|  |  |  | Latest Peak Compensated Load |  |  |  | 17.4 MVA on 03/02/2023 at 13:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 54.9 | 54.9 | 54.9 | 54.9 | 54.9 | 54.9 | 54.9 | 54.9 | 54.9 | 54.9
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 18.1 | 17.6 | 17.4 | 17 | 16.9 | 15.2 | 15.3 | 15.3 | 15.3 | 15.3
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.983 | 0.983 | 0.983 | 0.983 | 0.983 | 0.994 | 0.994 | 0.994 | 0.994 | 0.994
ECC Rating (MVA) | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5
50 PoE Load (MVA) | 17.4 | 17 | 16.7 | 16.4 | 16.2 | 14.7 | 14.7 | 14.7 | 14.7 | 14.7
50 PoE Load > 95% (MVA) | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Hours PA > 95% Peak Load | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Raw LAR (MVA)
2HR Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## LTA
Zone Summary Information and Peak Load Forecast
Substation | LTA - Lota (33/11kV) | [5 empty] | Supply | LBS - Lytton BS
Description | Land area is 3360 sqm, Construction is conventional indoor/outdoor class
Transformer size is 1x12.5/17.0MVA ONAN/ONAF;1x25MVA ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.5% W 0.2%, 2025 S -1.2% W 0.4%,2026 S -0.5% W -0.1%2027 S -1.2% W -0.4
Load Category | Domestic
Localities | Supplies Birkdale, Lota, Manly, Manly West, Ransome, Thorneside, Tingalpa, Wakerley, Wynnum, Wynnum West
|  |  |  | Latest Peak Compensated Load |  |  |  | 27 MVA on 03/02/2023 at 19:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 40.8 | 40.8 | 40.8 | 40.8 | 40.8 | 41.3 | 41.3 | 41.3 | 41.3 | 41.3
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 28.2 | 27.9 | 27.8 | 27.4 | 27.4 | 25.1 | 25.2 | 25.3 | 25.3 | 25.2
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.995 | 0.995 | 0.995 | 0.995 | 0.995 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 22.4 | 22.4 | 22.4 | 22.4 | 22.4
50 PoE Load (MVA) | 26.9 | 26.6 | 26.5 | 26.2 | 26.1 | 23.3 | 23.3 | 23.4 | 23.4 | 23.3
50 PoE Load > 95% (MVA) | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2
Hours PA > 95% Peak Load | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
Raw LAR (MVA) | 6 | 5.7 | 5.6 | 5.3 | 5.2 | 0.9 | 0.9 | 1 | 1 | 0.9
2HR Rating (MVA) | 23 | 23 | 23 | 23 | 23 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
N-1 Capacity for Embedded Generation (MVA) | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## LWD
Zone Summary Information and Peak Load Forecast
Substation | LWD - Lowood (33/11kV) | [5 empty] | Supply | LRE - Lockrose BS
Description | Land area is 5150 sqm, Construction is mini-modular (skid) class
Transformer size is 1x5/8MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.7% W -0.2%,2025 S -2.5% W -0.4%2026 S -1.7% W -0.8%2027 S -1.9% W -0.7
Load Category | Domestic
Localities | Supplies Lowood, Patrick Estate, Vernor, Wivenhoe Pocket
|  |  |  | Latest Peak Compensated Load |  |  |  | 2.7 MVA on 13/02/2023 at 17:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 3.2 | 3.1 | 3 | 3 | 3 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.984 | 0.984 | 0.984 | 0.984 | 0.984 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 2.9 | 2.8 | 2.8 | 2.7 | 2.7 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9
50 PoE Load > 95% (MVA) | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Hours PA > 95% Peak Load | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Raw LAR (MVA) | 2.9 | 2.8 | 2.8 | 2.7 | 2.7 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
Mobile Plant Avail (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## LYT
Zone Summary Information and Peak Load Forecast
Substation | LYT - Lytton (33/11kV) | [5 empty] | Supply | LBS - Lytton BS
Description | Land area is 6481 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x15/25MVA ONAN/ONAF;1x15MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.1% W -0.3%,2025 S -1.5% W 0.1%,2026 S -0.9% W -0.5%2027 S -1.5% W -0.6
Load Category | Continuous
Localities | Supplies Lytton
|  |  |  | Latest Peak Compensated Load |  |  |  | 28.1 MVA on 03/02/2023 at 11:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Day | Day | Day | Day
NCC Rating (MVA) | 64.9 | 64.9 | 64.9 | 64.9 | 64.9 | 64.9 | 64.9 | 64.9 | 64.9 | 64.9
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 28.4 | 29.9 | 32.6 | 32.2 | 32 | 26.2 | 26.1 | 29.8 | 29.7 | 29.5
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.999 | 0.998 | 0.994 | 0.995 | 0.995 | 0.988 | 0.988 | 1 | 1 | 1
ECC Rating (MVA) | 34.6 | 34.6 | 34.6 | 34.6 | 34.6 | 34.6 | 34.6 | 34.6 | 34.6 | 34.6
50 PoE Load (MVA) | 28.2 | 29.7 | 32.4 | 32 | 31.8 | 26 | 25.9 | 29.6 | 29.4 | 29.3
50 PoE Load > 95% (MVA) | 1.4 | 1.5 | 1.6 | 1.6 | 1.6 | 1.3 | 1.3 | 1.5 | 1.5 | 1.5
Hours PA > 95% Peak Load | 619.5 | 619.5 | 619.5 | 619.5 | 619.5 | 619.5 | 619.5 | 619.5 | 619.5 | 619.5
Raw LAR (MVA)
2HR Rating (MVA) | 34.6 | 34.6 | 34.6 | 34.6 | 34.6 | 34.6 | 34.6 | 34.6 | 34.6 | 34.6
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9
Mobile Plant Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO
Capacity for Embedded Generation (MVA) | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
N-1 Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
LARc (MVA)
LARc (MW)
Customer Category | HighSec | HighSec | HighSec | HighSec | HighSec | HighSec | HighSec | HighSec | HighSec | HighSec
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## LBS
Zone Summary Information and Peak Load Forecast
Substation | LBS - Lytton B (33/11kV) | [5 empty] | Supply | LBS - Lytton BS
Description | Land area is 30170 sqm, Construction is multiple modular class
Transformer size is 2x15/25MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 2.2 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.0% W -0.5%,2025 S -1.9% W -0.7%2026 S -1.4% W -1.5%2027 S -2.1% W -1.8
Load Category | Industrial
Localities | Supplies Hemmant, Lytton, Wynnum, Wynnum West
|  |  |  | Latest Peak Compensated Load |  |  |  | 18 MVA on 14/02/2023 at 11:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Day | Day | Day | Day
NCC Rating (MVA) | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 22.4 | 26.6 | 28.1 | 27.6 | 27.4 | 18.5 | 23.5 | 25.5 | 25.3 | 24.9
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.931 | 0.931 | 0.931 | 0.931 | 0.931 | 0.945 | 0.945 | 0.945 | 0.945 | 0.945
ECC Rating (MVA) | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5
50 PoE Load (MVA) | 21.8 | 25.9 | 27.4 | 27 | 26.8 | 17.8 | 22.8 | 24.8 | 24.5 | 24.2
50 PoE Load > 95% (MVA) | 1.1 | 1.3 | 1.4 | 1.4 | 1.3 | 0.9 | 1.1 | 1.2 | 1.2 | 1.2
Hours PA > 95% Peak Load | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Raw LAR (MVA)
2HR Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## MST
Zone Summary Information and Peak Load Forecast
Substation | MST - Makerston St (110/11kV) | [5 empty] | Supply | CBW - ASHGROVE WEST 110 CP
Description | Land area is 1310 sqm, Construction is conventional all indoor class
Transformer size is 3x30/50MVA ONAN/OFDAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 13.1 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.4% W 0.3%, 2025 S -1.4% W 0.3%,2026 S -0.7% W -0.2%2027 S -1.3% W -0.4
Load Category | Industrial
Localities | Supplies Brisbane City, Spring Hill
|  |  |  | Latest Peak Compensated Load |  |  |  | 58.3 MVA on 03/02/2023 at 13:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Day | Day | Day | Day
NCC Rating (MVA) | 157.3 | 157.3 | 157.3 | 157.3 | 157.3 | 157.3 | 157.3 | 157.3 | 157.3 | 157.3
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 61.2 | 60.3 | 59.9 | 61.5 | 61.3 | 42.8 | 42.9 | 43.1 | 42 | 43.7
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.999 | 0.999 | 1 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 114.7 | 114.7 | 114.7 | 114.7 | 114.7 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8
50 PoE Load (MVA) | 60.3 | 59.5 | 59 | 60.6 | 60.4 | 42.5 | 42.6 | 42.8 | 41.7 | 43.4
50 PoE Load > 95% (MVA) | 3 | 3 | 3 | 3 | 3 | 2.1 | 2.1 | 2.1 | 2.1 | 2.2
Hours PA > 95% Peak Load | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5
Raw LAR (MVA)
2HR Rating (MVA) | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 132.8 | 132.8 | 132.8 | 132.8 | 132.8
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 14.9 | 14.9 | 14.9 | 14.9 | 14.9 | 14.9 | 14.9 | 14.9 | 14.9 | 14.9
Mobile Plant Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
N-1 Capacity for Embedded Generation (MVA) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
LARc (MVA)
LARc (MW)
Customer Category | CBD | CBD | CBD | CBD | CBD | CBD | CBD | CBD | CBD | CBD
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## MLY
Zone Summary Information and Peak Load Forecast
Substation | MLY - Maleny (33/11kV) | [5 empty] | Supply | NBR - Nambour BS
Description | Land area is 1420 sqm, Construction is pipework and shed class
Transformer size is 2x5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.8% W 0.3%, 2025 S -1.1% W 0.3%,2026 S -0.4% W -0.2%2027 S -1.0% W -0.3
Load Category | Domestic
Localities | Supplies Bald Knob, Balmoral Ridge, Bellthorpe, Booroobin, Conondale, Curramore, Diamond Valley, Elaman Creek, Eudlo, Maleny, Montville, Mooloolah Valley, North Maleny, Reesville, Sandy Creek, Witta, Wootha
|  |  |  | Latest Peak Compensated Load |  |  |  | 10.8 MVA on 04/07/2022 at 17:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 7.9 | 7.8 | 7.8 | 7.7 | 7.7 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 7.5 | 7.4 | 7.4 | 7.3 | 7.3 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7
50 PoE Load > 95% (MVA) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hours PA > 95% Peak Load | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Raw LAR (MVA) | 7.5 | 7.4 | 7.4 | 7.3 | 7.3 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7
2HR Rating (MVA)
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3
Mobile Plant Avail (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
N-1 Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## MHL
Zone Summary Information and Peak Load Forecast
Substation | MHL - Mango Hill Bus 1 (33/11kV) | [5 empty] | Supply | HIL - Hays Inlet BS
Description | Land area is 4330 sqm, Construction is single modular class
Transformer size is 1x14.5/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 4.0% W 1.5%, 2025 S -0.9% W 1.7%,2026 S -0.3% W 1.1%,2027 S -0.5% W 0.3%
Load Category | Domestic
Localities | Supplies Deception Bay, Kippa-ring, Mango Hill, North Lakes, Rothwell
|  |  |  | Latest Peak Compensated Load |  |  |  | 24.2 MVA on 01/02/2023 at 17:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 30 | 30 | 30 | 30 | 30
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 22.9 | 22.7 | 22.7 | 22.5 | 22.7 | 16.2 | 16.4 | 16.7 | 16.9 | 16.9
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 1 | 1 | 1 | 1 | 1 | 0.996 | 0.996 | 0.996 | 0.996 | 0.996
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 21.4 | 21.2 | 21.1 | 21 | 21.1 | 14.5 | 14.7 | 15 | 15.1 | 15.2
50 PoE Load > 95% (MVA) | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 0.7 | 0.7 | 0.8 | 0.8 | 0.8
Hours PA > 95% Peak Load | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Raw LAR (MVA) | 21.4 | 21.2 | 21.1 | 21 | 21.1 | 14.5 | 14.7 | 15 | 15.1 | 15.2
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 28.1 | 29 | 29.8 | 30.9 | 31.7 | 46.6 | 46.4 | 46.3 | 46.2 | 46.4
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO
Capacity for Embedded Generation (MVA) | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## MHL2
Zone Summary Information and Peak Load Forecast
Substation | MHL - Mango Hill Bus 2 (33/11kV) | [5 empty] | Supply | GFN - Griffin BS
Description | Land area is 4330 sqm, Construction is single modular class
Transformer size is 1x14.5/25MVA ONAN/ODAF;1x15/25MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 1.5 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.3% W 0.8%, 2025 S -2.7% W 0.7%,2026 S -2.3% W 0.1%,2027 S -3.4% W -0.6
Load Category | Domestic
Localities | Supplies Deception Bay, Kippa-ring, Mango Hill, North Lakes, Rothwell
|  |  |  | Latest Peak Compensated Load |  |  |  | 33.4 MVA on 03/02/2023 at 15:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 59.9 | 59.9 | 59.9 | 59.9 | 59.9 | 59.9 | 59.9 | 59.9 | 59.9 | 59.9
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 37.1 | 36.1 | 35.3 | 34.5 | 33.5 | 24.6 | 24.8 | 25 | 25 | 24.8
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 1 | 1 | 1 | 0.988 | 0.988 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
50 PoE Load (MVA) | 35.1 | 34.6 | 33.8 | 32.7 | 31.8 | 23.3 | 23.5 | 23.6 | 23.7 | 23.5
50 PoE Load > 95% (MVA) | 1.8 | 1.7 | 1.7 | 1.6 | 1.6 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2
Hours PA > 95% Peak Load | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5
Raw LAR (MVA) | SUMMER 2023/24: 3.8; SUMMER 2024/25: 3.3; SUMMER 2025/26: 2.5; SUMMER 2026/27: 1.4; SUMMER 2027/28: 0.5
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO
Capacity for Embedded Generation (MVA) | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5
N-1 Capacity for Embedded Generation (MVA) | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## MBG
Zone Summary Information and Peak Load Forecast
Substation | MBG - Marburg (33/11kV) | [5 empty] | Supply | ABM - Abermain BS
Description | Land area is 4340 sqm, Construction is pipework and shed class
Transformer size is 1x5/6MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 8.5% W 5.7%, 2025 S 3.3% W 5.5%, 2026 S 3.8% W 4.7%, 2027 S 3.9% W 5.4%
Load Category | Domestic
Localities | Supplies Fairney View, Fernvale, Glamorgan Vale, Haigslea, Hatton Vale, Lark Hill, Marburg, Minden, Mount Marrow, Prenzlau, Rosewood, Tallegalla, Tarampa, The Bluff, Vernor, Walloon, Wanora
|  |  |  | Latest Peak Compensated Load |  |  |  | 4.8 MVA on 12/02/2023 at 18:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 5.3 | 5.5 | 5.7 | 5.9 | 6.2 | 4.4 | 4.7 | 5 | 5.2 | 5.5
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 4.9 | 5.1 | 5.2 | 5.4 | 5.7 | 3.8 | 4 | 4.2 | 4.4 | 4.6
50 PoE Load > 95% (MVA) | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hours PA > 95% Peak Load | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Raw LAR (MVA) | 4.9 | 5.1 | 5.2 | 5.4 | 5.7 | 3.8 | 4 | 4.2 | 4.4 | 4.6
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8
Mobile Plant Avail (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## MLS
Zone Summary Information and Peak Load Forecast
Substation | MLS - McLachlan St (110/11kV) | [5 empty] | Supply | BMH - BELMONT 110 CP
Description | Land area is 2700 sqm, Construction is conventional all indoor class
Transformer size is 2x36/60MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 1.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.5% W 0.7%, 2025 S -1.5% W 0.6%,2026 S -1.0% W 0.0%,2027 S -1.6% W -0.2
Load Category | Industrial
Localities | Supplies Bowen Hills, Brisbane City, East Brisbane, Fortitude Valley, New Farm, Spring Hill
|  |  |  | Latest Peak Compensated Load |  |  |  | 51.6 MVA on 03/02/2023 at 14:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9
Contracted non-network (MVA) | bar: SUMMER 2023/24 to WINTER 2027
10 PoE Load (MVA) | 51.8 | 51 | 50.5 | 49.7 | 49.5 | 31.6 | 31.9 | 32.1 | 32.1 | 32
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.997 | 0.997 | 0.997 | 0.997 | 0.998 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
ECC Rating (MVA) | 69 | 69 | 69 | 69 | 69 | 74.2 | 74.2 | 74.2 | 74.2 | 74.2
50 PoE Load (MVA) | 50.2 | 49.4 | 48.9 | 48.2 | 48 | 30.8 | 31 | 31.2 | 31.2 | 31.2
50 PoE Load > 95% (MVA) | 2.5 | 2.5 | 2.4 | 2.4 | 2.4 | 1.5 | 1.6 | 1.6 | 1.6 | 1.6
Hours PA > 95% Peak Load | 24.5 | 24.5 | 24.5 | 24.5 | 24.5 | 24.5 | 24.5 | 24.5 | 24.5 | 24.5
Raw LAR (MVA)
2HR Rating (MVA) | 75 | 75 | 75 | 75 | 75 | 84 | 84 | 84 | 84 | 84
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
N-1 Capacity for Embedded Generation (MVA) | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## MDH
Zone Summary Information and Peak Load Forecast
Substation | MDH - Meeandah (33/11kV) | [5 empty] | Supply | MDH - Meeandah BS
Description | Land area is 3720 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x15/25MVA ONAN/ODAF;1x15/25MVA ONAN/ODAF(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.3% W 0.0%, 2025 S -1.5% W 0.1%,2026 S -0.9% W -0.5%2027 S -1.5% W -0.6
Load Category | Industrial
Localities | Supplies Eagle Farm, Pinkenba
|  |  |  | Latest Peak Compensated Load |  |  |  | 21.7 MVA on 01/02/2023 at 12:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Day | Day | Day | Day
NCC Rating (MVA) | 52.4 | 52.4 | 52.4 | 52.4 | 52.4 | 52.4 | 52.4 | 52.4 | 52.4 | 52.4
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 21.8 | 25.7 | 25.5 | 25.2 | 25.1 | 17.8 | 21.6 | 21.7 | 21.6 | 21.5
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.979 | 0.999 | 0.999 | 1 | 1 | 0.99 | 0.981 | 0.981 | 0.982 | 0.982
ECC Rating (MVA) | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5
50 PoE Load (MVA) | 21.3 | 25.2 | 25 | 24.7 | 24.6 | 17.4 | 21.3 | 21.3 | 21.2 | 21.1
50 PoE Load > 95% (MVA) | 1.1 | 1.3 | 1.3 | 1.2 | 1.2 | 0.9 | 1.1 | 1.1 | 1.1 | 1.1
Hours PA > 95% Peak Load | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5
Raw LAR (MVA)
2HR Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## MMC
Zone Summary Information and Peak Load Forecast
Substation | MMC - Merrimac (110/11kV) | [5 empty] | Supply | MGB - MUDGEERABA 110 CP
Description | Land area is 2710 sqm, Construction is a mixture of various construction classes
Transformer size is 2x18/30MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.9% W 0.0%, 2025 S -1.6% W 0.0%,2026 S -0.9% W -0.4%2027 S -1.1% W -0.5
Load Category | Domestic
Localities | Supplies Benowa, Broadbeach Waters, Bundall, Carrara, Clear Island Waters, Mermaid Waters, Merrimac, Robina, Surfers Paradise
|  |  |  | Latest Peak Compensated Load |  |  |  | 27.9 MVA on 17/03/2023 at 17:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 63.4 | 63.4 | 63.4 | 63.4 | 63.4 | 67.2 | 67.2 | 67.2 | 67.2 | 67.2
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 29.9 | 29.4 | 29.1 | 28.8 | 28.8 | 22.7 | 22.7 | 22.8 | 22.6 | 22.5
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 34.7 | 34.7 | 34.7 | 34.7 | 34.7 | 36.4 | 36.4 | 36.4 | 36.4 | 36.4
50 PoE Load (MVA) | 27.9 | 27.4 | 27.2 | 26.9 | 26.9 | 21.6 | 21.6 | 21.6 | 21.5 | 21.4
50 PoE Load > 95% (MVA) | 1.4 | 1.4 | 1.4 | 1.3 | 1.3 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1
Hours PA > 95% Peak Load | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5
Raw LAR (MVA)
2HR Rating (MVA) | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 45 | 45 | 45 | 45 | 45
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO
Capacity for Embedded Generation (MVA) | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
N-1 Capacity for Embedded Generation (MVA) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## MAI
Zone Summary Information and Peak Load Forecast
Substation | MAI - Miami (33/11kV) | [5 empty] | Supply | BHD - Burleigh Heads BS
Description | Land area is 3100 sqm, Construction is conventional all indoor class
Transformer size is 1x12.5MVA ONAN;2x14MVA ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 5.5% W 1.9%, 2025 S 0.6% W 2.0%, 2026 S 1.2% W 1.4%, 2027 S 1.0% W 1.7%
Load Category | Domestic
Localities | Supplies Burleigh Heads, Burleigh Waters, Mermaid Beach, Mermaid Waters, Miami
|  |  |  | Latest Peak Compensated Load |  |  |  | 24.6 MVA on 04/07/2022 at 18:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 44.7 | 44.7 | 44.7 | 44.7 | 44.7 | 44.7 | 44.7 | 44.7 | 44.7 | 44.7
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 27.5 | 27.6 | 27.9 | 28.2 | 28.8 | 24.6 | 25.1 | 25.6 | 25.9 | 26.4
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 30.3 | 30.3 | 30.3 | 30.3 | 30.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3
50 PoE Load (MVA) | 25.3 | 25.4 | 25.7 | 26 | 26.5 | 23.2 | 23.7 | 24.1 | 24.5 | 24.9
50 PoE Load > 95% (MVA) | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2
Hours PA > 95% Peak Load | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5
Raw LAR (MVA)
2HR Rating (MVA) | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## MLT
Zone Summary Information and Peak Load Forecast
Substation | MLT - Milton (110/11kV) | [5 empty] | Supply | CBW - ASHGROVE WEST 110 CP
Description | Land area is 1320 sqm, Construction is conventional all indoor class
Transformer size is 2x36/60MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 2.2 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.9% W 0.2%, 2025 S -2.0% W 0.2%,2026 S -1.4% W -0.4%2027 S -2.1% W -0.5
Load Category | Industrial
Localities | Supplies Auchenflower, Bowen Hills, Brisbane City, Fortitude Valley, Herston, Kelvin Grove, Milton, Paddington, Red Hill, Spring Hill
|  |  |  | Latest Peak Compensated Load |  |  |  | 38 MVA on 17/03/2023 at 14:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Day | Day | Day | Day
NCC Rating (MVA) | 125.8 | 125.8 | 125.8 | 125.8 | 125.8 | 125.8 | 125.8 | 125.8 | 125.8 | 125.8
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 40.2 | 41.3 | 40.7 | 39.9 | 39.4 | 26.6 | 28.1 | 28.1 | 28 | 27.9
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 1 | 1 | 1 | 1 | 1 | 0.992 | 0.992 | 0.992 | 0.992 | 0.992
ECC Rating (MVA) | 69 | 69 | 69 | 69 | 69 | 78 | 78 | 78 | 78 | 78
50 PoE Load (MVA) | 39 | 40.1 | 39.6 | 38.8 | 38.3 | 25.8 | 27.2 | 27.3 | 27.1 | 27
50 PoE Load > 95% (MVA) | 2 | 2 | 2 | 1.9 | 1.9 | 1.3 | 1.4 | 1.4 | 1.4 | 1.4
Hours PA > 95% Peak Load | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17
Raw LAR (MVA)
2HR Rating (MVA) | 75 | 75 | 75 | 75 | 75 | 80 | 80 | 80 | 80 | 80
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
N-1 Capacity for Embedded Generation (MVA) | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## MGL
Zone Summary Information and Peak Load Forecast
Substation | MGL - Moggill (33/11kV) | [5 empty] | Supply | ABM - Abermain BS
Description | Land area is 10190 sqm, Construction is conventional indoor/outdoor class
Transformer size is 1x15/25MVA ONAN/ONAF;1x15MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.8% W -0.1%,2025 S -2.0% W 0.1%,2026 S -1.3% W -0.4%2027 S -1.7% W -0.4
Load Category | Domestic
Localities | Supplies Anstead, Bellbowrie, Kenmore, Moggill, Pinjarra Hills, Pullenvale, Upper Brookfield, Westlake
|  |  |  | Latest Peak Compensated Load |  |  |  | 19.4 MVA on 12/02/2023 at 17:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 20.7 | 20.3 | 20 | 19.7 | 19.6 | 14.5 | 14.5 | 14.5 | 14.5 | 14.4
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 20.3 | 20.3 | 20.3 | 20.3 | 20.3 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5
50 PoE Load (MVA) | 18.5 | 18.1 | 17.9 | 17.6 | 17.5 | 14.1 | 14.1 | 14.1 | 14 | 14
50 PoE Load > 95% (MVA) | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Hours PA > 95% Peak Load | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
Raw LAR (MVA)
2HR Rating (MVA) | 21.8 | 21.8 | 21.8 | 21.8 | 21.8 | 24 | 24 | 24 | 24 | 24
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## MDR
Zone Summary Information and Peak Load Forecast
Substation | MDR - Molendinar (110/11kV) | [5 empty] | Supply | MAR - MOLENDINAR 110 CP
Description | Land area is 74515 sqm, Construction is a mixture of various construction classes
Transformer size is 1x36/60MVA ONAN/ODAF;1x18/30MVA ONAN/ONAF(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 3.1 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.6% W 0.1%, 2025 S -2.5% W 0.5%,2026 S -1.7% W 0.0%,2027 S -1.4% W -0.1
Load Category | Mixed Domestic
Localities | Supplies Ashmore, Benowa, Carrara, Molendinar, Nerang, Parkwood, Southport
|  |  |  | Latest Peak Compensated Load |  |  |  | 39.9 MVA on 03/02/2023 at 16:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Day | Day | Day | Day
NCC Rating (MVA) | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 65.2 | 65.2 | 65.2 | 65.2 | 65.2
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 43.5 | 42.4 | 41.6 | 41.1 | 40.9 | 34.7 | 34.7 | 34.9 | 34.9 | 34.8
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.989 | 0.989 | 0.989 | 0.989 | 0.989
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 40.4 | 39.4 | 38.7 | 38.1 | 38 | 33.8 | 33.9 | 34 | 34 | 34
50 PoE Load > 95% (MVA) | 2 | 2 | 1.9 | 1.9 | 1.9 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7
Hours PA > 95% Peak Load | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Raw LAR (MVA) | 40.4 | 39.4 | 38.7 | 38.1 | 38 | 33.8 | 33.9 | 34 | 34 | 34
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 34.5 | 34.5 | 34.5 | 34.5 | 34.5 | 39 | 39 | 39 | 39 | 39
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
N-1 Capacity for Embedded Generation (MVA) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## MLB
Zone Summary Information and Peak Load Forecast
Substation | MLB - Mooloolaba (132/11kV) | [5 empty] | Supply | PWD - PALMWOODS 132 CP
Description | Land area is 49990 sqm, Construction is a mixture of various construction classes
Transformer size is 1x18/22.5/30MVA ONAN/ODAN/ODAF;1x30MVA ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 4.7% W 1.0%, 2025 S -0.2% W 1.0%,2026 S 0.5% W 0.8%, 2027 S 0.0% W 0.8%
Load Category | Domestic
Localities | Supplies Buderim, Chevallum, Forest Glen, Ilkley, Minyama, Mons, Mooloolaba, Mountain Creek, Palmview, Palmwoods, Parrearra, Sippy Downs, Tanawha
|  |  |  | Latest Peak Compensated Load |  |  |  | 42.3 MVA on 13/02/2023 at 18:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 67.8 | 67.8 | 67.8 | 67.8 | 67.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 46.1 | 46 | 46.2 | 46.2 | 46.7 | 37.8 | 38.2 | 38.5 | 38.8 | 39.2
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 1 | 1 | 1 | 1 | 1 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 34.9 | 34.9 | 34.9 | 34.9 | 34.9 | 36.6 | 36.6 | 36.6 | 36.6 | 36.6
50 PoE Load (MVA) | 41 | 40.9 | 41.1 | 41.1 | 41.5 | 35.8 | 36.1 | 36.5 | 36.8 | 37.1
50 PoE Load > 95% (MVA) | 2.1 | 2 | 2.1 | 2.1 | 2.1 | 1.8 | 1.8 | 1.8 | 1.8 | 1.9
Hours PA > 95% Peak Load | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
Raw LAR (MVA) | 6.1 | 6 | 6.2 | 6.2 | 6.6 |  |  |  | 0.2 | 0.5
2HR Rating (MVA) | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 45 | 45 | 45 | 45 | 45
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO
Capacity for Embedded Generation (MVA) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA) | SUMMER 2023/24: 0.5; SUMMER 2024/25: 0.4; SUMMER 2025/26: 0.6; SUMMER 2026/27: 0.6; SUMMER 2027/28: 1
LARc (MW) | SUMMER 2023/24: 0.5; SUMMER 2024/25: 0.4; SUMMER 2025/26: 0.6; SUMMER 2026/27: 0.6; SUMMER 2027/28: 1
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes
Back to Index

## MRK
Zone Summary Information and Peak Load Forecast
Substation | MRK - Moorooka (33/11kV) | [5 empty] | Supply | TSN - Tennyson BS
Description | Land area is 810 sqm, Construction is conventional indoor/outdoor class
Transformer size is 1x14.5/25MVA ONAN/ONAF;1x15/25MVA ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 4.0% W 1.0%, 2025 S -0.9% W 1.0%,2026 S -0.2% W 0.6%,2027 S -0.8% W -0.1
Load Category | Domestic
Localities | Supplies Annerley, Moorooka, Tarragindi, Tennyson, Yeerongpilly, Yeronga
|  |  |  | Latest Peak Compensated Load |  |  |  | 16.4 MVA on 13/02/2023 at 17:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 19.7 | 19.6 | 19.5 | 19.4 | 19.4 | 16.2 | 17.2 | 17.3 | 17.4 | 17.4
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.994 | 0.994 | 0.994 | 0.994 | 0.994
ECC Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
50 PoE Load (MVA) | 17.8 | 17.7 | 17.6 | 17.5 | 17.6 | 14.7 | 15.7 | 15.8 | 15.9 | 15.9
50 PoE Load > 95% (MVA) | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.8 | 0.8 | 0.8 | 0.8
Hours PA > 95% Peak Load | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5
Raw LAR (MVA)
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO
Capacity for Embedded Generation (MVA) | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5
N-1 Capacity for Embedded Generation (MVA) | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## MFD
Zone Summary Information and Peak Load Forecast
Substation | MFD - Morayfield (33/11kV) | [5 empty] | Supply | CBT - Caboolture BS
Description | Land area is 8100 sqm, Construction is multiple modular class
Transformer size is 1x14.5/25MVA ODAF;1x15/20MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.0% W 0.6%, 2025 S -1.2% W 0.7%,2026 S -0.6% W 1.0%,2027 S -0.8% W 1.6%
Load Category | Domestic
Localities | Supplies Burpengary, Morayfield
|  |  |  | Latest Peak Compensated Load |  |  |  | 31.3 MVA on 17/03/2023 at 17:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 47.8 | 47.8 | 47.8 | 47.8 | 47.8 | 47.8 | 47.8 | 47.8 | 47.8 | 47.8
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 35.7 | 35.3 | 35 | 34.8 | 34.7 | 26.5 | 26.6 | 26.8 | 27.1 | 27.5
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 25 | 25 | 25 | 25 | 25 | 28 | 28 | 28 | 28 | 28
50 PoE Load (MVA) | 33.8 | 33.4 | 33.2 | 32.9 | 32.9 | 24.7 | 24.9 | 25 | 25.3 | 25.7
50 PoE Load > 95% (MVA) | 1.7 | 1.7 | 1.7 | 1.6 | 1.6 | 1.2 | 1.2 | 1.3 | 1.3 | 1.3
Hours PA > 95% Peak Load | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
Raw LAR (MVA) | SUMMER 2023/24: 8.8; SUMMER 2024/25: 8.4; SUMMER 2025/26: 8.2; SUMMER 2026/27: 7.9; SUMMER 2027/28: 7.9
2HR Rating (MVA) | 27 | 27 | 27 | 27 | 27 | 30 | 30 | 30 | 30 | 30
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5
N-1 Capacity for Embedded Generation (MVA) | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5
LARc (MVA) | SUMMER 2023/24: 1.8; SUMMER 2024/25: 1.4; SUMMER 2025/26: 1.2; SUMMER 2026/27: 0.9; SUMMER 2027/28: 0.9
LARc (MW) | SUMMER 2023/24: 1.7928; SUMMER 2024/25: 1.3944; SUMMER 2025/26: 1.1952; SUMMER 2026/27: 0.8964; SUMMER 2027/28: 0.8964
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes
Back to Index

## MFN
Zone Summary Information and Peak Load Forecast
Substation | MFN - Morayfield North (33/11kV) | [5 empty] | Supply | CBT - Caboolture BS
Description | Land area is 2890 sqm, Construction is single modular class
Transformer size is 2x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.0% W -0.1%,2025 S -3.6% W 0.3%,2026 S -1.0% W -0.3%2027 S -1.2% W -0.2
Load Category | Mixed Industrial
Localities | Supplies Beachmere, Caboolture, Caboolture South, Morayfield, Upper Caboolture
|  |  |  | Latest Peak Compensated Load |  |  |  | 30.1 MVA on 17/03/2023 at 17:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 53.5 | 53.5 | 53.5 | 53.5 | 53.5 | 53.5 | 53.5 | 53.5 | 53.5 | 53.5
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 31.4 | 30.3 | 30 | 29.6 | 29.5 | 21.2 | 21.6 | 21.6 | 21.6 | 21.5
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.994 | 0.994 | 0.994 | 0.994 | 0.994 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5
50 PoE Load (MVA) | 29.7 | 28.6 | 28.3 | 27.9 | 27.8 | 20.5 | 20.8 | 20.9 | 20.8 | 20.8
50 PoE Load > 95% (MVA) | 1.5 | 1.4 | 1.4 | 1.4 | 1.4 | 1 | 1 | 1 | 1 | 1
Hours PA > 95% Peak Load | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5
Raw LAR (MVA) | SUMMER 2023/24: 0.9
2HR Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## MCN
Zone Summary Information and Peak Load Forecast
Substation | MCN - Mt Cotton (33/11kV) | [5 empty] | Supply | CVL - Cleveland BS
Description | Land area is 4050 sqm, Construction is mini-modular (skid) class
Transformer size is 1x5/6.25MVA ONAN/ONAF;1x5/8MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.5% W -0.4%,2025 S -2.2% W -0.2%2026 S -1.5% W -0.7%2027 S -2.0% W -0.8
Load Category | Mixed Domestic
Localities | Supplies Cornubia, Mount Cotton, Sheldon
|  |  |  | Latest Peak Compensated Load |  |  |  | 8.9 MVA on 13/02/2023 at 16:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 15.7 | 15.7 | 15.7 | 15.7 | 15.7 | 15.7 | 15.7 | 15.7 | 15.7 | 15.7
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 9.5 | 9.3 | 9.2 | 9 | 8.9 | 8.1 | 8.1 | 8.1 | 8 | 8
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.994 | 0.994 | 0.994 | 0.994 | 0.994 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998
ECC Rating (MVA) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1
50 PoE Load (MVA) | 8.9 | 8.7 | 8.6 | 8.4 | 8.4 | 7.8 | 7.8 | 7.7 | 7.7 | 7.6
50 PoE Load > 95% (MVA) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Hours PA > 95% Peak Load | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Raw LAR (MVA) | SUMMER 2023/24: 1.7; SUMMER 2024/25: 1.5; SUMMER 2025/26: 1.4; SUMMER 2026/27: 1.2; SUMMER 2027/28: 1.2
2HR Rating (MVA) | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7
Mobile Plant Avail (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO
Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## MCW
Zone Summary Information and Peak Load Forecast
Substation | MCW - Mt Crosby West (33/11kV) | [5 empty] | Supply | ABM - Abermain BS
Description | Land area is 3288 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x10/12.5MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.1% W 0.1%, 2025 S -1.6% W 0.3%,2026 S -0.9% W -0.2%2027 S -1.4% W -0.4
Load Category | Domestic
Localities | Supplies Chuwar, Karalee, Karana Downs, Kholo, Lake Manchester, Mount Crosby, Pine Mountain
|  |  |  | Latest Peak Compensated Load |  |  |  | 15.2 MVA on 12/02/2023 at 17:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 28.3 | 28.3 | 28.3 | 28.3 | 28.3 | 29.9 | 29.9 | 29.9 | 29.9 | 29.9
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 16.9 | 16.6 | 16.5 | 16.2 | 16.1 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.978 | 0.978 | 0.978 | 0.978 | 0.978 | 0.987 | 0.987 | 0.987 | 0.987 | 0.987
ECC Rating (MVA) | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3
50 PoE Load (MVA) | 14.8 | 14.5 | 14.4 | 14.2 | 14.1 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6
50 PoE Load > 95% (MVA) | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hours PA > 95% Peak Load | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
Raw LAR (MVA)
2HR Rating (MVA) | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 18.8 | 18.8 | 18.8 | 18.8 | 18.8
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8
Mobile Plant Avail (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
N-1 Capacity for Embedded Generation (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## MTG
Zone Summary Information and Peak Load Forecast
Substation | MTG - Mt Gravatt (33/11kV) | [5 empty] | Supply | BBS - Belmont BS
Description | Land area is 1870 sqm, Construction is conventional indoor/outdoor class
Transformer size is 1x15/25MVA ONAN/ODAF;1x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.5% W 0.6%, 2025 S -1.5% W 0.8%,2026 S -0.8% W 0.2%,2027 S -0.7% W 0.6%
Load Category | Domestic
Localities | Supplies Holland Park West, Macgregor, Mansfield, Mount Gravatt, Mount Gravatt East, Nathan, Upper Mount Gravatt, Wishart
|  |  |  | Latest Peak Compensated Load |  |  |  | 27.2 MVA on 17/03/2023 at 17:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 59.3
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 29.4 | 29 | 28.8 | 28.5 | 28.7 | 25.7 | 25.9 | 26.1 | 26.1 | 26.3
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.993 | 0.993 | 0.993 | 0.993 | 0.993 | 0.995 | 0.995 | 0.995 | 0.995 | 0.995
ECC Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
50 PoE Load (MVA) | 28 | 27.6 | 27.4 | 27.2 | 27.3 | 23.8 | 24 | 24.1 | 24.2 | 24.3
50 PoE Load > 95% (MVA) | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2
Hours PA > 95% Peak Load | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Raw LAR (MVA)
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## MSV
Zone Summary Information and Peak Load Forecast
Substation | MSV - Mt Sylvia (33/11kV) | [5 empty] | Supply | GBS - Gatton BS
Description | Land area is 1214 sqm, Construction is pipework and shed class
Transformer size is 1x5/6.5MVA retrofitted fans
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.4% W 0.3%, 2025 S -1.6% W 0.0%,2026 S -1.0% W -0.6%2027 S -1.6% W -0.7
Load Category | Domestic
Localities | Supplies Black Duck Creek, Caffey, East Haldon, Junction View, Lefthand Branch, Mount Sylvia, Upper Tenthill, West Haldon, Woodbine
|  |  |  | Latest Peak Compensated Load |  |  |  | 1.2 MVA on 23/01/2023 at 17:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Night | Day | Day | Day | Day | Day
NCC Rating (MVA) | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 1.3 | 1.3 | 1.2 | 1.2 | 1.2 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.889 | 0.889 | 0.889 | 0.889 | 0.916 | 0.858 | 0.858 | 0.858 | 0.858 | 0.858
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
50 PoE Load > 95% (MVA) | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0
Hours PA > 95% Peak Load | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5
Raw LAR (MVA) | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Mobile Plant Avail (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## MTB
Zone Summary Information and Peak Load Forecast
Substation | MTB - Mt Tamborine Bus 1 (33/11kV) | [5 empty] | Supply | BLH - Beenleigh BS
Description | Land area is 3800 sqm, Construction is single modular class
Transformer size is 1x15/18MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.9% W 0.0%, 2025 S -1.5% W 0.0%,2026 S -0.5% W -0.4%2027 S -1.1% W -0.6
Load Category | Domestic
Localities | Supplies Beechmont, Benobble, Binna Burra, Boyland, Canungra, Clagiraba, Ferny Glen, Flying Fox, Guanaba, Illinbah, Maudsland, Mount Nathan, Mundoolun, Natural Bridge, Nerang, Numinbah Valley, Oxenford, Sarabah, Tamborine, Tamborine Mountain, Upper Coomera, Witheren, Wonglepong
|  |  |  | Latest Peak Compensated Load |  |  |  | 9.8 MVA on 04/07/2022 at 17:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 8.7 | 8.6 | 8.5 | 8.4 | 8.4 | 10.2 | 10.2 | 10.2 | 10.2 | 10.1
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.995 | 0.995 | 0.995 | 0.995 | 0.995 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 7.9 | 7.8 | 7.8 | 7.7 | 7.7 | 9.5 | 9.5 | 9.5 | 9.4 | 9.4
50 PoE Load > 95% (MVA) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hours PA > 95% Peak Load | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
Raw LAR (MVA) | 7.9 | 7.8 | 7.8 | 7.7 | 7.7 | 9.5 | 9.5 | 9.5 | 9.4 | 9.4
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 11 | 11.1 | 11.1 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.3 | 11.3
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2
Mobile Plant Avail (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO
Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## MTB2
Zone Summary Information and Peak Load Forecast
Substation | MTB - Mt Tamborine Bus 2 (33/11kV) | [5 empty] | Supply | BDS - Beaudesert BS
Description | Land area is 3800 sqm, Construction is single modular class
Transformer size is 1x15MVA ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.3% W 0.0%, 2025 S -1.6% W 0.1%,2026 S -0.5% W -0.4%2027 S -1.1% W -0.5
Load Category | Domestic
Localities | Supplies Beechmont, Benobble, Binna Burra, Boyland, Canungra, Clagiraba, Ferny Glen, Flying Fox, Guanaba, Illinbah, Maudsland, Mount Nathan, Mundoolun, Numinbah Valley, Oxenford, Sarabah, Tamborine, Tamborine Mountain, Upper Coomera, Witheren, Wonglepong
|  |  |  | Latest Peak Compensated Load |  |  |  | 9.9 MVA on 04/07/2022 at 17:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 8.3 | 8.2 | 8.1 | 8.1 | 8.1 | 10.2 | 10.2 | 10.2 | 10.2 | 10.1
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.994 | 0.994 | 0.994 | 0.994 | 0.994 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 7.8 | 7.7 | 7.7 | 7.6 | 7.6 | 9.8 | 9.8 | 9.8 | 9.7 | 9.7
50 PoE Load > 95% (MVA) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hours PA > 95% Peak Load | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Raw LAR (MVA) | 7.8 | 7.7 | 7.7 | 7.6 | 7.6 | 9.8 | 9.8 | 9.8 | 9.7 | 9.7
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 14.6 | 14.7 | 14.7 | 14.8 | 14.8 | 15.7 | 15.7 | 15.7 | 15.8 | 15.8
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2
Mobile Plant Avail (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO
Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## MGP
Zone Summary Information and Peak Load Forecast
Substation | MGP - Mudgeeraba West Pkg (33/11kV) | [5 empty] | Supply | MGB - Mudgeeraba BS
Description | Land area is 3120 sqm, Construction is a mixture of various construction classes
Transformer size is 1x10/12.5MVA ONAN/ONAF;1x15/25MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.2% W 0.8%, 2025 S -1.1% W 1.0%,2026 S -0.4% W 0.5%,2027 S -1.1% W 0.2%
Load Category | Domestic
Localities | Supplies Advancetown, Austinville, Bonogin, Mudgeeraba, Natural Bridge, Numinbah Valley, Reedy Creek, Robina, Springbrook, Tallai
|  |  |  | Latest Peak Compensated Load |  |  |  | 22.2 MVA on 17/03/2023 at 17:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 24.3 | 24 | 23.9 | 23.7 | 23.6 | 22 | 22.2 | 22.4 | 22.5 | 22.6
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5
50 PoE Load (MVA) | 22.6 | 22.3 | 22.3 | 22 | 22 | 20.7 | 20.9 | 21.1 | 21.2 | 21.3
50 PoE Load > 95% (MVA) | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1 | 1 | 1.1 | 1.1 | 1.1
Hours PA > 95% Peak Load | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
Raw LAR (MVA) | 7 | 6.7 | 6.7 | 6.4 | 6.4 | 3.2 | 3.4 | 3.6 | 3.7 | 3.8
2HR Rating (MVA) | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 18.8 | 18.8 | 18.8 | 18.8 | 18.8
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO
Capacity for Embedded Generation (MVA) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
N-1 Capacity for Embedded Generation (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## MRE
Zone Summary Information and Peak Load Forecast
Substation | MRE - Murarrie (33/11kV) | [5 empty] | Supply | DBS - Doboy BS
Description | Land area is 1210 sqm, Construction is conventional all indoor class
Transformer size is 2x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.6% W -0.3%,2025 S -1.2% W -0.6%2026 S -0.6% W -0.1%2027 S -1.6% W -0.6
Load Category | Industrial
Localities | Supplies Cannon Hill, Murarrie, Tingalpa
|  |  |  | Latest Peak Compensated Load |  |  |  | 20.1 MVA on 01/02/2023 at 15:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Day | Day | Day | Day
NCC Rating (MVA) | 50.9 | 50.9 | 50.9 | 50.9 | 50.9 | 50.9 | 50.9 | 50.9 | 50.9 | 50.9
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 22.7 | 22.4 | 22.3 | 21.9 | 21.8 | 17.3 | 17.2 | 17.1 | 17.1 | 17
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.999 | 0.999 | 0.999 | 1 | 1 | 0.977 | 0.977 | 0.977 | 0.977 | 0.977
ECC Rating (MVA) | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4
50 PoE Load (MVA) | 21.5 | 21.3 | 21.1 | 20.8 | 20.7 | 16.6 | 16.5 | 16.4 | 16.4 | 16.3
50 PoE Load > 95% (MVA) | 1.1 | 1.1 | 1.1 | 1 | 1 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
Hours PA > 95% Peak Load | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Raw LAR (MVA)
2HR Rating (MVA) | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 34.9 | 34.9 | 34.9 | 34.9 | 34.9
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 24.5 | 24.5 | 24.5 | 24.5 | 24.5 | 24.5 | 24.5 | 24.5 | 24.5 | 24.5
N-1 Capacity for Embedded Generation (MVA) | 12.375 | 12.375 | 12.375 | 12.375 | 12.375 | 12.375 | 12.375 | 12.375 | 12.375 | 12.375
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## MRB
Zone Summary Information and Peak Load Forecast
Substation | MRB - Murrumba (33/11kV) | [5 empty] | Supply | LRE - Lockrose BS
Description | Land area is 3628 sqm, Construction is pipework and shed class
Transformer size is 1x5/8MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 4.2% W 1.1%, 2025 S -0.5% W 1.3%,2026 S 0.1% W 0.7%, 2027 S -0.6% W 0.5%
Load Category | Domestic
Localities | Supplies Coal Creek, Esk, Glen Esk, Lake Wivenhoe, Moombra, Mount Hallen, Murrumba
|  |  |  | Latest Peak Compensated Load |  |  |  | 1.9 MVA on 12/02/2023 at 18:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Day | Day | Night | Night
NCC Rating (MVA) | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.7 | 1.8 | 1.8 | 1.8 | 1.8
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.933 | 0.933 | 0.933 | 0.933 | 0.933 | 0.94 | 0.94 | 0.94 | 0.942 | 0.942
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 1.8 | 1.8 | 1.8 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.8 | 1.8
50 PoE Load > 95% (MVA) | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Hours PA > 95% Peak Load | 318.5 | 318.5 | 318.5 | 318.5 | 318.5 | 318.5 | 318.5 | 318.5 | 318.5 | 318.5
Raw LAR (MVA) | 1.8 | 1.8 | 1.8 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.8 | 1.8
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Mobile Plant Avail (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## MTN
Zone Summary Information and Peak Load Forecast
Substation | MTN - Myrtletown (33/11kV) | [5 empty] | Supply | MTN - Myrtletown BS
Description | Land area is 12550 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 1.4 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.3% W -0.2%,2025 S -0.7% W 0.4%,2026 S 0.2% W 0.5%, 2027 S -0.4% W 0.3%
Load Category | Continuous
Localities | Supplies Eagle Farm, Pinkenba
|  |  |  | Latest Peak Compensated Load |  |  |  | 16.8 MVA on 01/07/2022 at 08:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Night | Day | Day | Day | Day | Day | Day
NCC Rating (MVA) | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 17.4 | 17.3 | 17.3 | 17.2 | 17.3 | 17 | 17 | 17.1 | 17.2 | 17.2
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.999 | 0.999 | 0.999 | 0.952 | 0.999 | 0.953 | 0.953 | 0.953 | 0.953 | 0.953
ECC Rating (MVA) | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8
50 PoE Load (MVA) | 16.7 | 16.6 | 16.6 | 16.6 | 16.6 | 16.8 | 16.7 | 16.8 | 16.9 | 16.9
50 PoE Load > 95% (MVA) | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
Hours PA > 95% Peak Load | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Raw LAR (MVA)
2HR Rating (MVA) | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Mobile Plant Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 24.5 | 24.5 | 24.5 | 24.5 | 24.5 | 24.5 | 24.5 | 24.5 | 24.5 | 24.5
N-1 Capacity for Embedded Generation (MVA) | 12.3 | 12.3 | 12.3 | 12.3 | 12.3 | 12.3 | 12.3 | 12.3 | 12.3 | 12.3
LARc (MVA)
LARc (MW)
Customer Category | HighSec | HighSec | HighSec | HighSec | HighSec | HighSec | HighSec | HighSec | HighSec | HighSec
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## NBR
Zone Summary Information and Peak Load Forecast
Substation | NBR - Nambour (33/11kV) | [5 empty] | Supply | NBR - Nambour BS
Description | Land area is 20000 sqm, Construction is pipework and shed class
Transformer size is 1x14.5/25MVA ONAN/ONAF;1x15/25MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.5% W 0.2%, 2025 S -1.4% W 0.2%,2026 S -0.7% W -0.3%2027 S -1.4% W -0.3
Load Category | Mixed Industrial
Localities | Supplies Bli Bli, Burnside, Cooloolabin, Diddillibah, Dulong, Eerwah Vale, Eumundi, Flaxton, Highworth, Image Flat, Kiamba, Kiels Mountain, Kulangoor, Kureelpa, Mapleton, Maroochy River, Nambour, Parklands, Perwillowen, Rosemount, Valdora, Woombye, Yandina, Yandina Creek
|  |  |  | Latest Peak Compensated Load |  |  |  | 33.9 MVA on 13/02/2023 at 17:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 55 | 55 | 55 | 55 | 55 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 37.1 | 36.6 | 36.3 | 35.8 | 35.8 | 33.7 | 34.9 | 35 | 34.9 | 34.8
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.992 | 0.992 | 0.992 | 0.992 | 0.992 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
ECC Rating (MVA) | 30.6 | 30.6 | 30.6 | 30.6 | 30.6 | 32.3 | 32.3 | 32.3 | 32.3 | 32.3
50 PoE Load (MVA) | 35.2 | 34.7 | 34.4 | 34 | 33.9 | 32.3 | 33.6 | 33.6 | 33.5 | 33.4
50 PoE Load > 95% (MVA) | 1.8 | 1.7 | 1.7 | 1.7 | 1.7 | 1.6 | 1.7 | 1.7 | 1.7 | 1.7
Hours PA > 95% Peak Load | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
Raw LAR (MVA) | 4.6 | 4.1 | 3.8 | 3.4 | 3.3 |  | 1.3 | 1.3 | 1.2 | 1.1
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5
N-1 Capacity for Embedded Generation (MVA) | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## NRA
Zone Summary Information and Peak Load Forecast
Substation | NRA - Narangba (33/11kV) | [5 empty] | Supply | HIL - Hays Inlet BS
Description | Land area is 6000 sqm, Construction is multiple modular class
Transformer size is 1x15/20MVA ONAN/ONAF;1x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 1.3 MVA
Growth Rates | 2023 W 1.0%, 2024 S 4.9% W 2.0%, 2025 S 0.0% W 1.9%, 2026 S 0.8% W 1.4%, 2027 S 0.9% W 2.4%
Load Category | Domestic
Localities | Supplies Burpengary, Dakabin, Deception Bay, Kallangur, Kurwongbah, Moorina, Morayfield, Narangba
|  |  |  | Latest Peak Compensated Load |  |  |  | 26.4 MVA on 16/03/2023 at 17:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 28.7 | 28.7 | 29 | 29.3 | 29.8 | 22.3 | 22.7 | 23.2 | 23.5 | 24
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998
ECC Rating (MVA) | 25 | 25 | 25 | 25 | 25 | 28 | 28 | 28 | 28 | 28
50 PoE Load (MVA) | 27.1 | 27.1 | 27.3 | 27.6 | 28.1 | 20.4 | 20.8 | 21.2 | 21.5 | 22
50 PoE Load > 95% (MVA) | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1 | 1 | 1.1 | 1.1 | 1.1
Hours PA > 95% Peak Load | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5
Raw LAR (MVA) | SUMMER 2023/24: 2.1; SUMMER 2024/25: 2.1; SUMMER 2025/26: 2.3; SUMMER 2026/27: 2.6; SUMMER 2027/28: 3.1
2HR Rating (MVA) | 27 | 27 | 27 | 27 | 27 | 30 | 30 | 30 | 30 | 30
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## NRG
Zone Summary Information and Peak Load Forecast
Substation | NRG - Nerang (110/11kV) | [5 empty] | Supply | MAR - MOLENDINAR 110 CP
Description | Land area is 10060 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x36/60MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.7% W 0.3%, 2025 S -1.8% W 0.3%,2026 S -0.6% W -0.2%2027 S -1.2% W -0.3
Load Category | Mixed Domestic
Localities | Supplies Advancetown, Ashmore, Beechmont, Carrara, Clagiraba, Gilston, Highland Park, Lower Beechmont, Merrimac, Molendinar, Mount Nathan, Nerang, Tallai, Worongary
|  |  |  | Latest Peak Compensated Load |  |  |  | 51.8 MVA on 17/03/2023 at 17:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 54.6 | 53.6 | 53.2 | 52.6 | 52.5 | 44.8 | 45 | 45.1 | 45 | 44.9
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | bar: SUMMER 2023/24 to WINTER 2027
ECC Rating (MVA) | 69 | 69 | 69 | 69 | 69 | 78 | 78 | 78 | 78 | 78
50 PoE Load (MVA) | 50.8 | 49.9 | 49.5 | 48.9 | 48.8 | 42.5 | 42.7 | 42.8 | 42.7 | 42.6
50 PoE Load > 95% (MVA) | 2.5 | 2.5 | 2.5 | 2.4 | 2.4 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1
Hours PA > 95% Peak Load | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
Raw LAR (MVA)
2HR Rating (MVA) | 75 | 75 | 75 | 75 | 75 | 80.8 | 80.8 | 80.8 | 80.8 | 80.8
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO
Capacity for Embedded Generation (MVA) | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
N-1 Capacity for Embedded Generation (MVA) | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## NMK
Zone Summary Information and Peak Load Forecast
Substation | NMK - Newmarket (33/11kV) | [5 empty] | Supply | VPK - Victoria Park BS
Description | Land area is 1699 sqm, Construction is conventional all indoor class
Transformer size is 2x15/25MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.2% W 0.4%, 2025 S -1.9% W 0.5%,2026 S -1.0% W 0.0%,2027 S -1.6% W -0.1
Load Category | Domestic
Localities | Supplies Alderley, Ashgrove, Grange, Herston, Kelvin Grove, Newmarket, Stafford, Wilston, Windsor
|  |  |  | Latest Peak Compensated Load |  |  |  | 23.9 MVA on 17/03/2023 at 16:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 57.5 | 57.5 | 57.5 | 57.5 | 57.5 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 24.5 | 24.1 | 23.8 | 23.5 | 23.4 | 18.5 | 18.6 | 18.7 | 18.7 | 18.6
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.993 | 0.993 | 0.993 | 0.993 | 0.993 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 33.5 | 33.5 | 33.5 | 33.5 | 33.5
50 PoE Load (MVA) | 23.2 | 22.8 | 22.6 | 22.2 | 22.1 | 17.5 | 17.6 | 17.6 | 17.6 | 17.6
50 PoE Load > 95% (MVA) | 1.2 | 1.1 | 1.1 | 1.1 | 1.1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Hours PA > 95% Peak Load | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Raw LAR (MVA)
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## NSD
Zone Summary Information and Peak Load Forecast
Substation | NSD - Newstead (110/11kV) | [5 empty] | Supply | MRE - MURARRIE 110 CP
Description | Land area is 5060 sqm, Construction is conventional all indoor class
Transformer size is 2x36/60MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 1.9 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.8% W 1.1%, 2025 S -1.1% W 1.1%,2026 S -0.5% W 0.5%,2027 S -1.3% W 0.0%
Load Category | Mixed Industrial
Localities | Supplies Bowen Hills, Fortitude Valley, New Farm, Newstead, Spring Hill, Windsor
|  |  |  | Latest Peak Compensated Load |  |  |  | 44 MVA on 03/02/2023 at 12:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 51.2 | 51.3 | 53.7 | 53.1 | 53 | 24.4 | 28.9 | 29.2 | 31.1 | 31.1
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.998 | 0.998 | 0.997 | 0.997 | 0.997 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 69 | 69 | 69 | 69 | 69 | 78 | 78 | 78 | 78 | 78
50 PoE Load (MVA) | 49.2 | 49.3 | 51.7 | 51.1 | 51.1 | 23.7 | 28.2 | 28.5 | 30.3 | 30.4
50 PoE Load > 95% (MVA) | 2.5 | 2.5 | 2.6 | 2.6 | 2.6 | 1.2 | 1.4 | 1.4 | 1.5 | 1.5
Hours PA > 95% Peak Load | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5
Raw LAR (MVA)
2HR Rating (MVA) | 75 | 75 | 75 | 75 | 75 | 84 | 84 | 84 | 84 | 84
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
N-1 Capacity for Embedded Generation (MVA) | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## NGI
Zone Summary Information and Peak Load Forecast
Substation | NGI - Ningi (33/11kV) | [5 empty] | Supply | CBT - Caboolture BS
Description | Land area is 75310 sqm, Construction is single modular class
Transformer size is 1x10/15MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.6% W -1.2%,2025 S -1.1% W 0.0%,2026 S -0.5% W -0.4%2027 S -1.1% W -0.6
Load Category | Domestic
Localities | Supplies Beachmere, Caboolture, Donnybrook, Meldale, Ningi, Toorbul
|  |  |  | Latest Peak Compensated Load |  |  |  | 10 MVA on 13/02/2023 at 18:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 11.4 | 11.3 | 11.3 | 11.1 | 11.1 | 9.6 | 9.5 | 9.5 | 9.5 | 9.4
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.994 | 0.994 | 0.994 | 0.994 | 0.994 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 10.8 | 10.6 | 10.6 | 10.5 | 10.4 | 8.6 | 8.4 | 8.4 | 8.4 | 8.4
50 PoE Load > 95% (MVA) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Hours PA > 95% Peak Load | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
Raw LAR (MVA) | 10.8 | 10.6 | 10.6 | 10.5 | 10.4 | 8.6 | 8.4 | 8.4 | 8.4 | 8.4
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
Mobile Plant Avail (MVA) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## NVL
Zone Summary Information and Peak Load Forecast
Substation | NVL - Noosaville (132/11kV) | [5 empty] | Supply | WLG - WOOLOOGA 132 CP
Description | Land area is 3720 sqm, Construction is conventional all indoor class
Transformer size is 2x18/22.5/30MVA ONAN/ODAF;1x30/60MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.8% W -0.1%,2025 S -0.8% W -0.2%2026 S -0.1% W -0.3%2027 S -0.8% W -0.4
Load Category | Domestic
Localities | Supplies Castaways Beach, Marcus Beach, Noosa Heads, Noosaville, North Shore, Peregian Beach, Sunrise Beach, Sunshine Beach, Tewantin
|  |  |  | Latest Peak Compensated Load |  |  |  | 36.8 MVA on 04/07/2022 at 17:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 113.7 | 113.7 | 113.7 | 113.7 | 113.7 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 37.6 | 37.3 | 37.3 | 37 | 37.1 | 35.2 | 35.2 | 35.1 | 35 | 34.8
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | bar: SUMMER 2023/24 to WINTER 2027
ECC Rating (MVA) | 38.8 | 38.8 | 38.8 | 38.8 | 38.8 | 43.1 | 43.1 | 43.1 | 43.1 | 43.1
50 PoE Load (MVA) | 36 | 35.7 | 35.7 | 35.4 | 35.5 | 32.9 | 32.9 | 32.8 | 32.7 | 32.5
50 PoE Load > 95% (MVA) | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
Hours PA > 95% Peak Load | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Raw LAR (MVA)
2HR Rating (MVA) | 41.7 | 41.7 | 41.7 | 41.7 | 41.7 | 46 | 46 | 46 | 46 | 46
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO
Capacity for Embedded Generation (MVA) | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
N-1 Capacity for Embedded Generation (MVA) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## NMC
Zone Summary Information and Peak Load Forecast
Substation | NMC - North Maclean (33/11kV) | [5 empty] | Supply | BPN - Browns Plains BS
Description | Land area is 4590 sqm, Construction is multiple modular class
Transformer size is 2x14.5/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.6% W 1.0%, 2025 S -0.8% W 1.1%,2026 S -0.1% W 0.5%,2027 S 1.0% W 2.6%
Load Category | Domestic
Localities | Supplies Chambers Flat, Greenbank, Jimboomba, Lyons, Munruben, New Beith, North Maclean, Park Ridge, Park Ridge South, South Maclean, Stockleigh
|  |  |  | Latest Peak Compensated Load |  |  |  | 35.6 MVA on 12/02/2023 at 17:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 59.7 | 59.7 | 59.7 | 59.7 | 59.7 | 59.7 | 59.7 | 59.7 | 59.7 | 59.7
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 39.1 | 43.8 | 45.7 | 47.1 | 49.7 | 28.8 | 29.4 | 34.7 | 36.9 | 38.7
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.997 | 0.998 | 0.998 | 0.997 | 0.997 | 0.998 | 0.998 | 0.997 | 0.997 | 0.996
ECC Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
50 PoE Load (MVA) | 34.6 | 39.4 | 41.3 | 42.6 | 45.2 | 26.1 | 26.7 | 32 | 34.1 | 35.8
50 PoE Load > 95% (MVA) | 1.7 | 1.97 | 2.065 | 2.13 | 2.26 | 1.305 | 1.335 | 1.6 | 1.705 | 1.79
Hours PA > 95% Peak Load | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
Raw LAR (MVA) | 3.3 | 8.1 | 10 | 11.3 | 13.9 |  |  |  |  | 0.8
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4
Mobile Plant Avail (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
N-1 Capacity for Embedded Generation (MVA) | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5
LARc (MVA) | SUMMER 2027/28: 0.49
LARc (MW) | SUMMER 2027/28: 0.48853
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes
Back to Index

## NSW
Zone Summary Information and Peak Load Forecast
Substation | NSW - North Springwood (110/11kV) | [5 empty] | Supply | LGH - LOGANLEA 110 CP
Description | Land area is 5113 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x18/22.5/30MVA ONAN/ODAF;1x36/60MVA ONAN/OFDAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 3.9 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.1% W -0.1%,2025 S -2.1% W -0.3%2026 S -1.4% W -0.2%2027 S -1.9% W -0.4
Load Category | Domestic
Localities | Supplies Daisy Hill, Eight Mile Plains, Kuraby, Priestdale, Rochedale, Rochedale South, Slacks Creek, Springwood, Underwood, Woodridge
|  |  |  | Latest Peak Compensated Load |  |  |  | 47.6 MVA on 17/03/2023 at 16:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 124.5 | 124.5 | 124.5 | 124.5 | 124.5 | 134.6 | 134.6 | 134.6 | 134.6 | 134.6
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 51 | 50 | 49.4 | 48.4 | 48 | 36.8 | 36.8 | 36.7 | 36.6 | 36.4
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 1 | 1 | 0.999 | 0.999 | 0.999 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 69 | 69 | 69 | 69 | 69 | 74.3 | 74.3 | 74.3 | 74.3 | 74.3
50 PoE Load (MVA) | 45.7 | 44.8 | 44.2 | 43.3 | 43 | 34 | 34 | 33.8 | 33.8 | 33.6
50 PoE Load > 95% (MVA) | 2.3 | 2.2 | 2.2 | 2.2 | 2.2 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7
Hours PA > 95% Peak Load | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
Raw LAR (MVA)
2HR Rating (MVA) | 69 | 69 | 69 | 69 | 69 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO
Capacity for Embedded Generation (MVA) | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
N-1 Capacity for Embedded Generation (MVA) | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## NIP
Zone Summary Information and Peak Load Forecast
Substation | NIP - Nth Ipswich (33/11kV) | [5 empty] | Supply | ABM - Abermain BS
Description | Land area is 2220 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 4.0% W 0.9%, 2025 S -1.1% W 0.9%,2026 S -0.3% W 0.6%,2027 S -1.2% W 0.1%
Load Category | Domestic
Localities | Supplies Basin Pocket, Borallon, Brassall, Coalfalls, East Ipswich, Fernvale, Ipswich, Kholo, Moores Pocket, Muirlea, North Ipswich, Pine Mountain, Sadliers Crossing, Tivoli, Wanora, Woodend
|  |  |  | Latest Peak Compensated Load |  |  |  | 22.6 MVA on 17/03/2023 at 16:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 59.1 | 59.1 | 59.1 | 59.1 | 59.1 | 59.1 | 59.1 | 59.1 | 59.1 | 59.1
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 24 | 23.8 | 23.7 | 23.4 | 23.3 | 18.3 | 18.5 | 18.6 | 18.8 | 18.8
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.989 | 0.989 | 0.989 | 0.989 | 0.989 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998
ECC Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
50 PoE Load (MVA) | 22.5 | 22.3 | 22.2 | 21.9 | 21.9 | 16.8 | 17 | 17.1 | 17.2 | 17.3
50 PoE Load > 95% (MVA) | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9
Hours PA > 95% Peak Load | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Raw LAR (MVA)
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 4.95
N-1 Capacity for Embedded Generation (MVA) | 2.475 | 2.475 | 2.475 | 2.475 | 2.475 | 2.475 | 2.475 | 2.475 | 2.475 | 2.475
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## NPD
Zone Summary Information and Peak Load Forecast
Substation | NPD - Nth Pine Dam (33/11kV) | [5 empty] | Supply | BRD - Brendale BS
Description | Land area is 6868 sqm, Construction is pipework and shed class
Transformer size is 1x5/6.25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.2% W -0.1%,2025 S -1.5% W 0.2%,2026 S -0.9% W -0.4%2027 S -1.5% W -0.5
Load Category | Industrial
Localities | Supplies Joyner, Kurwongbah, Whiteside
|  |  |  | Latest Peak Compensated Load |  |  |  | 0.4 MVA on 09/02/2023 at 10:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Day | Day | Day | Day
NCC Rating (MVA) | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.989 | 0.989 | 0.989 | 0.989 | 0.989 | 0.964 | 0.964 | 0.964 | 0.964 | 0.964
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
50 PoE Load > 95% (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hours PA > 95% Peak Load | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Raw LAR (MVA) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
Mobile Plant Avail (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## NGE
Zone Summary Information and Peak Load Forecast
Substation | NGE - Nudgee (33/11kV) | [5 empty] | Supply | NGE - Nudgee BS
Description | Land area is 20450 sqm, Construction is conventional indoor/outdoor class
Transformer size is 1x15/25MVA ONAN/ODAF;1xTR2
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.8% W -0.4%,2025 S -2.2% W -0.6%2026 S -1.5% W -1.1%2027 S -2.1% W -0.7
Load Category | Industrial
Localities | Supplies Banyo, Northgate, Nudgee, Nudgee Beach
|  |  |  | Latest Peak Compensated Load |  |  |  | 22.6 MVA on 31/01/2023 at 14:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Day | Day | Day | Day
NCC Rating (MVA) | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 24.8 | 24.2 | 23.8 | 23.3 | 23.1 | 18.5 | 18.4 | 18.3 | 18.1 | 17.9
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 1 | 1 | 1 | 1 | 1 | 0.999 | 0.999 | 1 | 1 | 1
ECC Rating (MVA) | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 32 | 32 | 32 | 32 | 32
50 PoE Load (MVA) | 23.2 | 22.7 | 22.6 | 22.1 | 21.8 | 17.9 | 17.8 | 17.7 | 17.5 | 17.4
50 PoE Load > 95% (MVA) | 1.2 | 1.1 | 1.1 | 1.1 | 1.1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Hours PA > 95% Peak Load | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5
Raw LAR (MVA)
2HR Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO
Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## NDH
Zone Summary Information and Peak Load Forecast
Substation | NDH - Nundah (33/11kV) | [5 empty] | Supply | NGE - Nudgee BS
Description | Land area is 1671 sqm, Construction is conventional indoor/outdoor class
Transformer size is 1x15/20MVA ONAN/ONAF;1x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 2.6 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.6% W 0.2%, 2025 S -1.1% W 0.3%,2026 S -0.4% W -0.2%2027 S -1.0% W -0.3
Load Category | Mixed Industrial
Localities | Supplies Geebung, Hendra, Northgate, Nundah, Virginia, Wavell Heights
|  |  |  | Latest Peak Compensated Load |  |  |  | 21.6 MVA on 03/02/2023 at 19:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 24.6 | 24.4 | 24.3 | 24 | 24 | 19 | 19 | 19.1 | 19 | 19
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.995 | 0.995 | 0.995 | 0.995 | 0.995 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998
ECC Rating (MVA) | 23 | 23 | 23 | 23 | 23 | 26 | 26 | 26 | 26 | 26
50 PoE Load (MVA) | 22.8 | 22.5 | 22.4 | 22.2 | 22.2 | 17.9 | 17.9 | 18 | 18 | 17.9
50 PoE Load > 95% (MVA) | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Hours PA > 95% Peak Load | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
Raw LAR (MVA)
2HR Rating (MVA) | 25 | 25 | 25 | 25 | 25 | 28 | 28 | 28 | 28 | 28
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## OXL
Zone Summary Information and Peak Load Forecast
Substation | OXL - Oxley (33/11kV) | [5 empty] | Supply | RLD - Richlands BS
Description | Land area is 14350 sqm, Construction is conventional indoor/outdoor class
Transformer size is 1x15/25MVA ONAN/ODAF;1x15MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 1.8 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.1% W 0.6%, 2025 S -2.1% W 0.7%,2026 S -1.4% W 0.1%,2027 S -1.8% W -0.2
Load Category | Industrial
Localities | Supplies Archerfield, Corinda, Durack, Inala, Oxley, Rocklea, Seventeen Mile Rocks
|  |  |  | Latest Peak Compensated Load |  |  |  | 20.1 MVA on 03/02/2023 at 15:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Day | Day | Day | Day
NCC Rating (MVA) | 30.7 | 30.7 | 30.7 | 30.7 | 30.7 | 30.7 | 30.7 | 30.7 | 30.7 | 30.7
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 20.5 | 24.3 | 24 | 23.7 | 23.6 | 14.7 | 18.5 | 18.6 | 18.6 | 18.6
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.984 | 0.984 | 0.984 | 0.984 | 0.984 | 0.997 | 0.994 | 0.994 | 0.994 | 0.994
ECC Rating (MVA) | 18 | 18 | 18 | 18 | 18 | 20.3 | 20.3 | 20.3 | 20.3 | 20.3
50 PoE Load (MVA) | 18.9 | 22.8 | 22.5 | 22.2 | 22.1 | 14.5 | 18.3 | 18.4 | 18.4 | 18.3
50 PoE Load > 95% (MVA) | 0.9 | 1.1 | 1.1 | 1.1 | 1.1 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9
Hours PA > 95% Peak Load | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Raw LAR (MVA) | SUMMER 2023/24: 0.9; SUMMER 2024/25: 4.8; SUMMER 2025/26: 4.5; SUMMER 2026/27: 4.2; SUMMER 2027/28: 4.1
2HR Rating (MVA) | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 21.8 | 21.8 | 21.8 | 21.8 | 21.8
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## PBH
Zone Summary Information and Peak Load Forecast
Substation | PBH - Palm Beach (33/11kV) | [5 empty] | Supply | BHD - Burleigh Heads BS
Description | Land area is 3240 sqm, Construction is conventional indoor/outdoor class
Transformer size is 3x10/12.5MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.9% W 0.4%, 2025 S -0.9% W 0.5%,2026 S -0.2% W 0.0%,2027 S -0.8% W -0.2
Load Category | Domestic
Localities | Supplies Bilinga, Currumbin, Currumbin Waters, Elanora, Palm Beach
|  |  |  | Latest Peak Compensated Load |  |  |  | 20.5 MVA on 04/07/2022 at 17:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 60 | 60 | 60 | 60 | 60 | 44.8 | 60 | 60 | 60 | 60
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 21.3 | 21.1 | 21 | 20.9 | 20.9 | 21 | 21.1 | 21.3 | 21.3 | 21.2
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 34.8 | 35 | 35 | 35 | 35
50 PoE Load (MVA) | 20.1 | 19.9 | 19.9 | 19.7 | 19.7 | 20 | 20.1 | 20.2 | 20.2 | 20.2
50 PoE Load > 95% (MVA) | bar: SUMMER 2023/24 to WINTER 2027
Hours PA > 95% Peak Load | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5
Raw LAR (MVA)
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.3 | 37.5 | 37.5 | 37.5 | 37.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## PWC
Zone Summary Information and Peak Load Forecast
Substation | PWC - Palmwoods Central (33/11kV) | [5 empty] | Supply | NBR - Nambour BS
Description | Land area is 3030 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x15MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.9 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.8% W 0.4%, 2025 S -0.8% W 0.6%,2026 S -0.1% W 0.1%,2027 S -0.7% W 0.0%
Load Category | Domestic
Localities | Supplies Chevallum, Coes Creek, Diamond Valley, Dulong, Eudlo, Flaxton, Hunchy, Ilkley, Landers Shoot, Montville, Mooloolah Valley, North Maleny, Palmwoods, Perwillowen, Tanawha, Towen Mountain, West Woombye, Woombye
|  |  |  | Latest Peak Compensated Load |  |  |  | 23.3 MVA on 04/07/2022 at 17:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 30.3 | 30.3 | 30.3 | 30.3 | 30.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 26.4 | 26.2 | 26.2 | 26 | 26.1 | 23.9 | 24 | 24.1 | 24.2 | 24.2
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.991 | 0.991 | 0.991 | 0.991 | 0.991 | 0.995 | 0.995 | 0.995 | 0.995 | 0.995
ECC Rating (MVA) | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8
50 PoE Load (MVA) | 23.9 | 23.7 | 23.7 | 23.5 | 23.6 | 21.8 | 21.8 | 22 | 22 | 22
50 PoE Load > 95% (MVA) | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1
Hours PA > 95% Peak Load | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Raw LAR (MVA) | 8.7 | 8.5 | 8.5 | 8.3 | 8.4 | 5 | 5 | 5.2 | 5.2 | 5.2
2HR Rating (MVA) | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8
Mobile Plant Avail (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## PKW
Zone Summary Information and Peak Load Forecast
Substation | PKW - Parkwood (33/11kV) | [5 empty] | Supply | MDR - Molendinar BS
Description | Land area is 2970 sqm, Construction is conventional all indoor class
Transformer size is 2x15/25MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 12.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.9% W -0.2%,2025 S -1.8% W 0.1%,2026 S -1.1% W -0.4%2027 S -1.7% W -0.6
Load Category | Mixed Industrial
Localities | Supplies Arundel, Parkwood
|  |  |  | Latest Peak Compensated Load |  |  |  | 17 MVA on 03/02/2023 at 16:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Night | Night | Night | Night
NCC Rating (MVA) | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 17.8 | 19.5 | 20.4 | 20.1 | 19.9 | 11.7 | 11.8 | 14.2 | 14.1 | 14.1
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.988 | 0.988 | 0.988 | 0.988 | 0.988 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5
50 PoE Load (MVA) | 16.7 | 18.4 | 19.3 | 19 | 18.8 | 11.4 | 11.4 | 13.8 | 13.8 | 13.7
50 PoE Load > 95% (MVA) | 0.8 | 0.9 | 1 | 1 | 0.9 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7
Hours PA > 95% Peak Load | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Raw LAR (MVA)
2HR Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## PGN
Zone Summary Information and Peak Load Forecast
Substation | PGN - Peregian (33/11kV) | [5 empty] | Supply | SRH - Sunrise Hills BS
Description | Land area is 15260 sqm, Construction is single modular class
Transformer size is 1x15/25MVA ONAN/ONAF;1x8MVA ONAF(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 4.0% W 0.1%, 2025 S -0.7% W 0.1%,2026 S -0.0% W -0.4%2027 S -1.2% W -1.1
Load Category | Domestic
Localities | Supplies Doonan, Marcus Beach, Peregian Beach, Verrierdale
|  |  |  | Latest Peak Compensated Load |  |  |  | 12.6 MVA on 03/02/2023 at 18:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 14.3 | 14.2 | 14.2 | 14 | 14 | 12.8 | 12.9 | 12.9 | 12.8 | 12.7
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 1 | 1 | 1 | 1 | 1 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 12.7 | 12.6 | 12.6 | 12.5 | 12.5 | 11.7 | 11.7 | 11.7 | 11.6 | 11.5
50 PoE Load > 95% (MVA) | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
Hours PA > 95% Peak Load | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5
Raw LAR (MVA) | 12.7 | 12.6 | 12.6 | 12.5 | 12.5 | 11.7 | 11.7 | 11.7 | 11.6 | 11.5
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 10 | 10 | 10 | 10 | 10 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8
Mobile Plant Avail (MVA) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
N-1 Capacity for Embedded Generation (MVA) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## PPE
Zone Summary Information and Peak Load Forecast
Substation | PPE - Pimpama East (33/11kV) | [5 empty] | Supply | CMA - Coomera BS
Description | Land area is 5220 sqm, Construction is multiple modular class
Transformer size is 2x25MVA ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 2.2 MVA
Growth Rates | 2023 W 1.0%, 2024 S 4.3% W 3.7%, 2025 S 0.5% W 3.5%, 2026 S 1.2% W 2.8%, 2027 S 1.6% W 3.6%
Load Category | Domestic
Localities | Supplies Coomera, Jacobs Well, Norwell, Ormeau, Pimpama, Steiglitz, Upper Coomera, Woongoolba
|  |  |  | Latest Peak Compensated Load |  |  |  | 40.6 MVA on 17/03/2023 at 17:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 59.5 | 59.5 | 59.5 | 59.5 | 59.5 | 59.5 | 59.5 | 59.5 | 59.5 | 59.5
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 44.4 | 48.6 | 49.1 | 49.9 | 51.1 | 35.6 | 36.9 | 41.6 | 42.7 | 44.3
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 1 | 1 | 1 | 1 | 1 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998
ECC Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
50 PoE Load (MVA) | 41 | 45.2 | 45.7 | 46.4 | 47.5 | 32.2 | 33.4 | 37.9 | 39 | 40.3
50 PoE Load > 95% (MVA) | 2.1 | 2.3 | 2.3 | 2.3 | 2.4 | 1.6 | 1.7 | 1.9 | 2 | 2
Hours PA > 95% Peak Load | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
Raw LAR (MVA) | 9.7 | 13.9 | 14.4 | 15.1 | 16.2 |  |  | 2.9 | 4 | 5.3
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
N-1 Capacity for Embedded Generation (MVA) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
LARc (MVA) | 7.2 | 11.4 | 11.9 | 12.6 | 13.7 |  |  | 0.4 | 1.5 | 2.8
LARc (MW) | 7.2 | 11.4 | 11.9 | 12.6 | 13.7 |  |  | 0.4 | 1.5 | 2.8
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | No | No | No | No | No | Yes | Yes | No | No | No
Back to Index

## PRG
Zone Summary Information and Peak Load Forecast
Substation | PRG - Postmans Ridge (33/11kV) | [5 empty] | Supply | PRG - Postmans Ridge BS
Description | Land area is 37223 sqm, Construction is mini-modular (skid) class
Transformer size is 1x5.0/6.5MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.5% W 0.3%, 2025 S -1.3% W 0.4%,2026 S -0.6% W -0.1%2027 S -1.1% W -0.2
Load Category | Mixed Industrial
Localities | Supplies Ballard, Blanchview, Fifteen Mile, Helidon Spa, Lockyer, Murphys Creek, Postmans Ridge, Prince Henry Heights, Redwood, Silver Ridge, Upper Lockyer, Withcott
|  |  |  | Latest Peak Compensated Load |  |  |  | 6.1 MVA on 12/02/2023 at 18:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 6.7 | 6.6 | 6.6 | 6.5 | 6.5 | 5.2 | 5.2 | 5.3 | 5.3 | 5.2
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 5.9 | 5.8 | 5.8 | 5.7 | 5.7 | 4.9 | 5 | 5 | 5 | 5
50 PoE Load > 95% (MVA) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3
Hours PA > 95% Peak Load | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Raw LAR (MVA) | 5.9 | 5.8 | 5.8 | 5.7 | 5.7 | 4.9 | 5 | 5 | 5 | 5
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2
Mobile Plant Avail (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## QPT
Zone Summary Information and Peak Load Forecast
Substation | QPT - Queensport (33/11kV) | [5 empty] | Supply | DBS - Doboy BS
Description | Land area is 1840 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.3% W -0.3%,2025 S -1.6% W -0.4%2026 S -1.0% W -0.2%2027 S -1.7% W -0.5
Load Category | Industrial
Localities | Supplies Cannon Hill, Morningside, Murarrie
|  |  |  | Latest Peak Compensated Load |  |  |  | 26.9 MVA on 01/02/2023 at 16:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 52.4 | 52.4 | 52.4 | 52.4 | 52.4 | 52.4 | 52.4 | 52.4 | 52.4 | 52.4
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 29.6 | 29.1 | 28.9 | 28.4 | 28.3 | 21.9 | 21.9 | 21.8 | 21.7 | 21.6
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.985 | 0.985 | 0.985 | 0.985 | 0.985 | 0.994 | 0.994 | 0.994 | 0.994 | 0.994
ECC Rating (MVA) | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5
50 PoE Load (MVA) | 28.3 | 27.9 | 27.6 | 27.1 | 27 | 21.4 | 21.4 | 21.3 | 21.2 | 21.1
50 PoE Load > 95% (MVA) | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1
Hours PA > 95% Peak Load | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
Raw LAR (MVA)
2HR Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## RBY
Zone Summary Information and Peak Load Forecast
Substation | RBY - Raby Bay (33/11kV) | [5 empty] | Supply | CVL - Cleveland BS
Description | Land area is 7940 sqm, Construction is conventional indoor/outdoor class
Transformer size is 1x10/12.5/15MVA ONAF/ODAF;1x10/12.5MVA ONAN/ONAF;1x10/15MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 4.1% W 1.0%, 2025 S -0.8% W 0.9%,2026 S -0.1% W 0.4%,2027 S -0.9% W 0.1%
Load Category | Domestic
Localities | Supplies Alexandra Hills, Cleveland, Ormiston, Wellington Point
|  |  |  | Latest Peak Compensated Load |  |  |  | 28.3 MVA on 17/03/2023 at 17:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 30.8 | 30.6 | 30.6 | 30.3 | 30.4 | 23.2 | 23.4 | 23.6 | 23.7 | 23.7
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 31 | 31 | 31 | 31 | 31 | 34.7 | 34.7 | 34.7 | 34.7 | 34.7
50 PoE Load (MVA) | 29 | 28.7 | 28.7 | 28.4 | 28.5 | 22.2 | 22.4 | 22.6 | 22.7 | 22.7
50 PoE Load > 95% (MVA) | 1.5 | 1.4 | 1.4 | 1.4 | 1.4 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1
Hours PA > 95% Peak Load | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
Raw LAR (MVA)
2HR Rating (MVA) | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 37.1 | 37.1 | 37.1 | 37.1 | 37.1
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## RBK
Zone Summary Information and Peak Load Forecast
Substation | RBK - Redbank (33/11kV) | [5 empty] | Supply | GNA - Goodna BS
Description | Land area is 5090 sqm, Construction is conventional indoor/outdoor class
Transformer size is 1x10/12.5MVA ONAN/ODAF;1x10/12.5MVA ONAN/ONAF;1x15/25MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.8% W 1.1%, 2025 S -0.4% W 0.9%,2026 S 0.3% W 1.7%, 2027 S -0.3% W 1.6%
Load Category | Mixed Industrial
Localities | Supplies Collingwood Park, Goodna, Redbank
|  |  |  | Latest Peak Compensated Load |  |  |  | 16 MVA on 03/02/2023 at 14:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Day | Day | Day | Day
NCC Rating (MVA) | 43.1 | 43.1 | 43.1 | 43.1 | 43.1 | 43.1 | 43.1 | 43.1 | 43.1 | 43.1
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 18.2 | 19.1 | 19.1 | 19.1 | 19.2 | 11.3 | 12.2 | 12.3 | 12.5 | 12.7
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.985 | 0.985 | 0.985 | 0.985 | 0.985 | 0.992 | 0.992 | 0.992 | 0.992 | 0.992
ECC Rating (MVA) | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 31.9 | 31.9 | 31.9 | 31.9 | 31.9
50 PoE Load (MVA) | 17.2 | 18.1 | 18.2 | 18.1 | 18.3 | 10.9 | 11.8 | 11.9 | 12.1 | 12.3
50 PoE Load > 95% (MVA) | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6
Hours PA > 95% Peak Load | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
Raw LAR (MVA)
2HR Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
N-1 Capacity for Embedded Generation (MVA) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## RCF
Zone Summary Information and Peak Load Forecast
Substation | RCF - Redcliffe (33/11kV) | [5 empty] | Supply | HIL - Hays Inlet BS
Description | Land area is 6490 sqm, Construction is pipework and shed class
Transformer size is 1x15/25MVA ONAN/ODAF;1x15MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 3.5 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.5% W 0.6%, 2025 S -0.9% W 0.6%,2026 S -0.1% W 0.0%,2027 S -0.7% W -0.0
Load Category | Mixed Domestic
Localities | Supplies Clontarf, Kippa-ring, Margate, Redcliffe, Woody Point
|  |  |  | Latest Peak Compensated Load |  |  |  | 19.4 MVA on 03/02/2023 at 15:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 30.8 | 30.8 | 30.8 | 30.8 | 30.8 | 30.8 | 30.8 | 30.8 | 30.8 | 30.8
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 20.3 | 20.1 | 20.1 | 23.6 | 27.4 | 16.8 | 16.9 | 17 | 17 | 19.1
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.988 | 0.988 | 0.988 | 0.988 | 0.988 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998
ECC Rating (MVA) | 18 | 18 | 18 | 18 | 18 | 20.25 | 20.25 | 20.25 | 20.25 | 20.25
50 PoE Load (MVA) | 19.3 | 19.1 | 19.1 | 22.6 | 26.3 | 16.1 | 16.2 | 16.3 | 16.3 | 18.4
50 PoE Load > 95% (MVA) | 1 | 1 | 1 | 1.1 | 1.3 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9
Hours PA > 95% Peak Load | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Raw LAR (MVA) | SUMMER 2023/24: 1.3; SUMMER 2024/25: 1.1; SUMMER 2025/26: 1.1; SUMMER 2026/27: 4.6; SUMMER 2027/28: 8.3
2HR Rating (MVA) | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## RLB
Zone Summary Information and Peak Load Forecast
Substation | RLB - Redland Bay (33/11kV) | [5 empty] | Supply | CVL - Cleveland BS
Description | Land area is 9010 sqm, Construction is pipework and shed class
Transformer size is 1x15/25MVA ONAN/ODAF;1x15MVA ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.7% W 0.5%, 2025 S -1.2% W 0.5%,2026 S -0.4% W 0.1%,2027 S -0.5% W 0.2%
Load Category | Domestic
Localities | Supplies Carbrook, Mount Cotton, Redland Bay, Victoria Point
|  |  |  | Latest Peak Compensated Load |  |  |  | 18.6 MVA on 17/03/2023 at 17:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 32.2 | 32.2 | 32.2 | 32.2 | 32.2 | 32.2 | 32.2 | 32.2 | 32.2 | 32.2
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 19.9 | 19.7 | 19.6 | 19.5 | 19.6 | 17.6 | 17.7 | 17.8 | 17.8 | 17.9
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 18.8 | 18.8 | 18.8 | 18.8 | 18.8 | 21 | 21 | 21 | 21 | 21
50 PoE Load (MVA) | 18.8 | 18.6 | 18.6 | 18.5 | 18.5 | 15.9 | 16 | 16.1 | 16.1 | 16.1
50 PoE Load > 95% (MVA) | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
Hours PA > 95% Peak Load | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
Raw LAR (MVA)
2HR Rating (MVA) | 20.3 | 20.3 | 20.3 | 20.3 | 20.3 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1
Mobile Plant Avail (MVA) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## RBA
Zone Summary Information and Peak Load Forecast
Substation | RBA - Robina (110/11kV) | [5 empty] | Supply | MGB - MUDGEERABA 110 CP
Description | Land area is 6320 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x60MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 2.8 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.0% W 0.3%, 2025 S -2.0% W 0.6%,2026 S -1.3% W 0.1%,2027 S -1.9% W -0.1
Load Category | Mixed Industrial
Localities | Supplies Advancetown, Clear Island Waters, Gilston, Merrimac, Mudgeeraba, Reedy Creek, Robina, Tallai, Worongary
|  |  |  | Latest Peak Compensated Load |  |  |  | 48.8 MVA on 03/02/2023 at 16:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 131.4 | 131.4 | 131.4 | 131.4 | 131.4 | 131.4 | 131.4 | 131.4 | 131.4 | 131.4
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 50.4 | 49.4 | 48.8 | 47.8 | 47.4 | 35.5 | 35.6 | 35.8 | 35.8 | 35.8
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.995 | 0.995 | 0.995 | 0.995 | 0.995
ECC Rating (MVA) | 69 | 69 | 69 | 69 | 69 | 78 | 78 | 78 | 78 | 78
50 PoE Load (MVA) | 46.3 | 45.4 | 44.8 | 43.9 | 43.5 | 34.3 | 34.4 | 34.6 | 34.7 | 34.6
50 PoE Load > 95% (MVA) | 2.3 | 2.3 | 2.2 | 2.2 | 2.2 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7
Hours PA > 95% Peak Load | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
Raw LAR (MVA)
2HR Rating (MVA) | 75 | 75 | 75 | 75 | 75 | 84 | 84 | 84 | 84 | 84
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
N-1 Capacity for Embedded Generation (MVA) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## RLA
Zone Summary Information and Peak Load Forecast
Substation | RLA - Rocklea (33/11kV) | [5 empty] | Supply | AFD - Archerfield BS
Description | Land area is 2540 sqm, Construction is conventional indoor/outdoor class
Transformer size is 1x15/25MVA ONAN/ODAF;1x15MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 1.5% W -0.6%,2025 S -2.4% W -0.8%2026 S -0.6% W -0.3%2027 S -1.2% W 0.0%
Load Category | Industrial
Localities | Supplies Archerfield, Coopers Plains, Moorooka, Rocklea, Salisbury, Tarragindi, Yeerongpilly
|  |  |  | Latest Peak Compensated Load |  |  |  | 16 MVA on 01/02/2023 at 15:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 31.6 | 31.6 | 31.6 | 31.6 | 31.6 | 31.6 | 31.6 | 31.6 | 31.6 | 31.6
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 17.2 | 16.8 | 16.7 | 16.5 | 16.4 | 15.4 | 15.3 | 15.2 | 15.2 | 15.2
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.972 | 0.972 | 0.972 | 0.972 | 0.972 | 0.985 | 0.985 | 0.985 | 0.985 | 0.985
ECC Rating (MVA) | 18 | 18 | 18 | 18 | 18 | 20.3 | 20.3 | 20.3 | 20.3 | 20.3
50 PoE Load (MVA) | 16.4 | 16 | 15.9 | 15.7 | 15.7 | 14.3 | 14.3 | 14.1 | 14.1 | 14.1
50 PoE Load > 95% (MVA) | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Hours PA > 95% Peak Load | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Raw LAR (MVA)
2HR Rating (MVA) | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 21.8 | 21.8 | 21.8 | 21.8 | 21.8
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## RST
Zone Summary Information and Peak Load Forecast
Substation | RST - Roderick St (33/11kV) | [5 empty] | Supply | RVW - Raceview BS
Description | Land area is 3320 sqm, Construction is conventional indoor/outdoor class
Transformer size is 3x10/15MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 4.3% W 0.6%, 2025 S -0.7% W 0.6%,2026 S -0.1% W 0.0%,2027 S -0.6% W -0.1
Load Category | Mixed Industrial
Localities | Supplies Churchill, East Ipswich, Eastern Heights, Ipswich, Newtown, North Ipswich, Sadliers Crossing, West Ipswich, Woodend
|  |  |  | Latest Peak Compensated Load |  |  |  | 25.2 MVA on 01/02/2023 at 14:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Day | Day | Day | Day
NCC Rating (MVA) | 49.3 | 49.3 | 49.3 | 49.3 | 49.3 | 49.3 | 49.3 | 49.3 | 49.3 | 49.3
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 26.9 | 26.7 | 26.7 | 26.5 | 26.7 | 19.5 | 19.6 | 19.7 | 19.7 | 19.7
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 1 | 1 | 1 | 1 | 1 | 0.995 | 0.995 | 0.995 | 0.995 | 0.995
ECC Rating (MVA) | 44 | 44 | 44 | 44 | 44 | 44.8 | 44.8 | 44.8 | 44.8 | 44.8
50 PoE Load (MVA) | 26.1 | 25.9 | 25.9 | 25.7 | 25.8 | 18.7 | 18.9 | 19 | 19 | 19
50 PoE Load > 95% (MVA) | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 0.9 | 0.9 | 1 | 1 | 1
Hours PA > 95% Peak Load | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
Raw LAR (MVA)
2HR Rating (MVA) | 46.6 | 46.6 | 46.6 | 46.6 | 46.6 | 47.7 | 47.7 | 47.7 | 47.7 | 47.7
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## RWD
Zone Summary Information and Peak Load Forecast
Substation | RWD - Rosewood (33/11kV) | [5 empty] | Supply | ABM - Abermain BS
Description | Land area is 7284 sqm, Construction is pipework and shed class
Transformer size is 2x5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 8.5% W 5.6%, 2025 S 3.2% W 5.5%, 2026 S 3.5% W 4.6%, 2027 S 3.6% W 5.2%
Load Category | Domestic
Localities | Supplies Ashwell, Calvert, Coleyville, Ebenezer, Lanefield, Lower Mount Walker, Merryvale, Moorang, Mount Forbes, Mount Mort, Mount Walker, Mount Walker West, Rosevale, Rosewood, Tallegalla, The Bluff, Walloon, Willowbank
|  |  |  | Latest Peak Compensated Load |  |  |  | 6.4 MVA on 17/03/2023 at 17:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 7.6 | 7.8 | 8.1 | 8.4 | 8.7 | 5.5 | 5.8 | 6.2 | 6.4 | 6.8
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.986 | 0.986 | 0.986 | 0.986 | 0.986
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 7.1 | 7.4 | 7.6 | 7.9 | 8.2 | 5.2 | 5.5 | 5.8 | 6 | 6.3
50 PoE Load > 95% (MVA) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Hours PA > 95% Peak Load | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Raw LAR (MVA) | 7.1 | 7.4 | 7.6 | 7.9 | 8.2 | 5.2 | 5.5 | 5.8 | 6 | 6.3
2HR Rating (MVA)
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8
Mobile Plant Avail (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
N-1 Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## RCN
Zone Summary Information and Peak Load Forecast
Substation | RCN - Runcorn (33/11kV) | [5 empty] | Supply | RBS - Runcorn BS
Description | Land area is 3690 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x15/25MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 4.1% W 0.9%, 2025 S -0.7% W 1.0%,2026 S 0.0% W 0.5%, 2027 S -0.5% W 0.4%
Load Category | Domestic
Localities | Supplies Eight Mile Plains, Karawatha, Kuraby, Runcorn, Stretton, Sunnybank, Sunnybank Hills, Woodridge
|  |  |  | Latest Peak Compensated Load |  |  |  | 22.3 MVA on 17/03/2023 at 20:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 59.9 | 59.9 | 59.9 | 59.9 | 59.9 | 59.9 | 59.9 | 59.9 | 59.9 | 59.9
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 23.8 | 23.6 | 23.6 | 23.5 | 23.6 | 21.6 | 21.8 | 22 | 22.1 | 22.2
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
50 PoE Load (MVA) | 22.1 | 22 | 22 | 21.9 | 22 | 20.8 | 20.9 | 21.2 | 21.3 | 21.3
50 PoE Load > 95% (MVA) | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1 | 1 | 1.1 | 1.1 | 1.1
Hours PA > 95% Peak Load | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
Raw LAR (MVA)
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## RIS
Zone Summary Information and Peak Load Forecast
Substation | RIS - Russell Island (110/11kV) | [5 empty] | Supply | LGH - LOGANLEA 110 CP
Description | Land area is 11510 sqm, Construction is conventional outdoor bulk class
Transformer size is 1x18/25MVA ONAN/OFDAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 5.5% W 1.4%, 2025 S 0.6% W 1.3%, 2026 S 1.6% W 1.0%, 2027 S 1.3% W 1.8%
Load Category | Domestic
Localities | Supplies Karragarra Island, Lamb Island, Macleay Island, Russell Island
|  |  |  | Latest Peak Compensated Load |  |  |  | 7.4 MVA on 04/07/2022 at 17:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 20.6 | 20.6 | 20.6 | 20.6 | 20.6 | 22.1 | 22.1 | 22.1 | 22.1 | 22.1
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 6.8 | 6.9 | 7 | 7.1 | 7.2 | 6.9 | 7 | 7.1 | 7.2 | 7.3
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.993 | 0.993 | 0.993 | 0.993 | 0.993
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 6.3 | 6.3 | 6.4 | 6.5 | 6.7 | 6.7 | 6.8 | 6.9 | 6.9 | 7.1
50 PoE Load > 95% (MVA) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4
Hours PA > 95% Peak Load | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
Raw LAR (MVA) | 6.3 | 6.3 | 6.4 | 6.5 | 6.7 | 6.7 | 6.8 | 6.9 | 6.9 | 7.1
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Mobile Plant Avail (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## SBY
Zone Summary Information and Peak Load Forecast
Substation | SBY - Salisbury (33/11kV) | [5 empty] | Supply | AFD - Archerfield BS
Description | Land area is 800 sqm, Construction is conventional all indoor class
Transformer size is 1x15MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 2.2 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.9% W 0.2%, 2025 S -1.1% W 0.6%,2026 S -0.3% W 0.1%,2027 S -0.7% W 0.2%
Load Category | Industrial
Localities | Supplies Moorooka, Nathan, Salisbury, Tarragindi
|  |  |  | Latest Peak Compensated Load |  |  |  | 9.8 MVA on 31/01/2023 at 15:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Day | Day | Day | Day
NCC Rating (MVA) | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 10.6 | 10.5 | 10.4 | 10.4 | 10.4 | 9.7 | 9.7 | 9.8 | 9.8 | 9.8
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.976 | 0.976 | 0.976 | 0.976 | 0.976 | 0.994 | 0.994 | 0.994 | 0.994 | 0.994
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 9.9 | 9.8 | 9.8 | 9.7 | 9.7 | 8.6 | 8.7 | 8.7 | 8.7 | 8.7
50 PoE Load > 95% (MVA) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Hours PA > 95% Peak Load | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
Raw LAR (MVA) | 9.9 | 9.8 | 9.8 | 9.7 | 9.7 | 8.6 | 8.7 | 8.7 | 8.7 | 8.7
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 13.3 | 13.3 | 13.3 | 13.3 | 13.3 | 13.3 | 13.3 | 13.3 | 13.3 | 13.3
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## SMF
Zone Summary Information and Peak Load Forecast
Substation | SMF - Samford (33/11kV) | [5 empty] | Supply | BRD - Brendale BS
Description | Land area is 4780 sqm, Construction is multiple modular class
Transformer size is 1x15/25MVA ONAN/ODAF;1x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.3% W 0.5%, 2025 S -1.5% W 0.6%,2026 S -0.6% W 0.2%,2027 S -1.1% W 0.1%
Load Category | Domestic
Localities | Supplies Bunya, Camp Mountain, Cashmere, Cedar Creek, Clear Mountain, Closeburn, Dayboro, Draper, Enoggera Reservoir, Ferny Hills, Highvale, Jollys Lookout, Mount Glorious, Mount Nebo, Mount Samson, Rush Creek, Samford Valley, Samford Village, Samsonvale, Upper Kedron, Wights Mountain, Yugar
|  |  |  | Latest Peak Compensated Load |  |  |  | 16.4 MVA on 12/02/2023 at 17:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 59.2 | 59.2 | 59.2 | 59.2 | 59.2 | 59.2 | 59.2 | 59.2 | 59.2 | 59.2
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 17.5 | 17.3 | 17.2 | 17 | 17 | 14.8 | 14.8 | 14.9 | 14.9 | 15
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.995 | 0.995 | 0.995 | 0.995 | 0.995 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
50 PoE Load (MVA) | 15.9 | 15.6 | 15.5 | 15.4 | 15.3 | 13.3 | 13.4 | 13.5 | 13.5 | 13.5
50 PoE Load > 95% (MVA) | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Hours PA > 95% Peak Load | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
Raw LAR (MVA)
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
Mobile Plant Avail (MVA) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## SGT
Zone Summary Information and Peak Load Forecast
Substation | SGT - Sandgate (33/11kV) | [5 empty] | Supply | SGT - Sandgate BS
Description | Land area is 7910 sqm, Construction is conventional indoor/outdoor class
Transformer size is 1x15/25MVA ONAN/ODAF;1xTR1
Capacity of commissioned Embedded Generation (with Connection Agreements) is 1.4 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.0% W 0.2%, 2025 S -1.9% W 0.2%,2026 S -1.2% W -0.3%2027 S -1.7% W -0.4
Load Category | Domestic
Localities | Supplies Boondall, Bracken Ridge, Brighton, Deagon, Fitzgibbon, Sandgate, Shorncliffe, Taigum, Zillmere
|  |  |  | Latest Peak Compensated Load |  |  |  | 36 MVA on 17/03/2023 at 17:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 37.1 | 36.4 | 36 | 35.4 | 35.1 | 31.4 | 31.4 | 31.5 | 31.4 | 31.3
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
50 PoE Load (MVA) | 34.4 | 33.7 | 33.3 | 32.7 | 32.5 | 29.3 | 29.4 | 29.5 | 29.4 | 29.3
50 PoE Load > 95% (MVA) | 1.7 | 1.7 | 1.7 | 1.6 | 1.6 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
Hours PA > 95% Peak Load | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Raw LAR (MVA) | SUMMER 2023/24: 3.1; SUMMER 2024/25: 2.4; SUMMER 2025/26: 2; SUMMER 2026/27: 1.4; SUMMER 2027/28: 1.2
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## SBH
Zone Summary Information and Peak Load Forecast
Substation | SBH - Scarborough (33/11kV) | [5 empty] | Supply | HIL - Hays Inlet BS
Description | Land area is 3730 sqm, Construction is conventional indoor/outdoor class
Transformer size is 3x10/15MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 4.5% W 0.4%, 2025 S -0.2% W 0.2%,2026 S 0.4% W -0.2%,2027 S 0.2% W 0.5%
Load Category | Domestic
Localities | Supplies Kippa-ring, Redcliffe, Scarborough
|  |  |  | Latest Peak Compensated Load |  |  |  | 20.2 MVA on 03/02/2023 at 19:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 45.5 | 45.5 | 45.5 | 45.5 | 45.5 | 50.1 | 50.1 | 50.1 | 50.1 | 50.1
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 20.9 | 20.9 | 21 | 21 | 21.2 | 19.7 | 19.8 | 19.8 | 19.8 | 19.9
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 1 | 1 | 1 | 1 | 1 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998
ECC Rating (MVA) | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4
50 PoE Load (MVA) | 19.8 | 19.8 | 19.9 | 19.9 | 20.1 | 18.1 | 18.2 | 18.3 | 18.2 | 18.3
50 PoE Load > 95% (MVA) | 1 | 1 | 1 | 1 | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Hours PA > 95% Peak Load | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Raw LAR (MVA)
2HR Rating (MVA) | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 36.4 | 36.4 | 36.4 | 36.4 | 36.4
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## SRD
Zone Summary Information and Peak Load Forecast
Substation | SRD - Scrub Road (33/11kV) | [5 empty] | Supply | BBS - Belmont BS
Description | Land area is 9530 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x12.5/15MVA ONAN/ONAF;1x15MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 1.8 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.6% W -0.7%,2025 S -2.3% W -0.9%2026 S -1.6% W -1.3%2027 S -2.1% W -1.4
Load Category | Mixed Domestic
Localities | Supplies Carina, Carina Heights, Carindale
|  |  |  | Latest Peak Compensated Load |  |  |  | 30 MVA on 17/03/2023 at 16:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 46.7 | 46.7 | 46.7 | 46.7 | 46.7 | 46.7 | 46.7 | 46.7 | 46.7 | 46.7
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 32.2 | 31.4 | 31 | 30.3 | 30 | 22.1 | 22 | 21.8 | 21.5 | 21.2
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.993 | 0.993 | 0.993 | 0.993 | 0.993 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 34.4 | 34.4 | 34.4 | 34.4 | 34.4 | 38.7 | 38.7 | 38.7 | 38.7 | 38.7
50 PoE Load (MVA) | 29.2 | 28.5 | 28.1 | 27.5 | 27.2 | 21.3 | 21.1 | 20.9 | 20.7 | 20.4
50 PoE Load > 95% (MVA) | 1.5 | 1.4 | 1.4 | 1.4 | 1.4 | 1.1 | 1.1 | 1 | 1 | 1
Hours PA > 95% Peak Load | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
Raw LAR (MVA)
2HR Rating (MVA) | 37.3 | 37.3 | 37.3 | 37.3 | 37.3 | 41.6 | 41.6 | 41.6 | 41.6 | 41.6
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO
Capacity for Embedded Generation (MVA) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
N-1 Capacity for Embedded Generation (MVA) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## SHW
Zone Summary Information and Peak Load Forecast
Substation | SHW - Sherwood (33/11kV) | [5 empty] | Supply | TSN - Tennyson BS
Description | Land area is 4047 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x14.5/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.1% W 0.3%, 2025 S -1.7% W 0.5%,2026 S -0.9% W 0.0%,2027 S -1.5% W -0.1
Load Category | Domestic
Localities | Supplies Chelmer, Corinda, Fig Tree Pocket, Graceville, Indooroopilly, Sherwood
|  |  |  | Latest Peak Compensated Load |  |  |  | 28.8 MVA on 16/03/2023 at 17:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 59.7 | 59.7 | 59.7 | 59.7 | 59.7 | 59.7 | 59.7 | 59.7 | 59.7 | 59.7
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 30.3 | 32.1 | 31.8 | 31.3 | 31.2 | 23.5 | 25.5 | 25.7 | 25.7 | 25.6
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
50 PoE Load (MVA) | 27.8 | 29.6 | 29.3 | 28.9 | 28.8 | 22.3 | 24.4 | 24.5 | 24.5 | 24.5
50 PoE Load > 95% (MVA) | 1.4 | 1.5 | 1.5 | 1.4 | 1.4 | 1.1 | 1.2 | 1.2 | 1.2 | 1.2
Hours PA > 95% Peak Load | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Raw LAR (MVA)
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
N-1 Capacity for Embedded Generation (MVA) | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## SDM
Zone Summary Information and Peak Load Forecast
Substation | SDM - Somerset Dam (33/11kV) | [5 empty] | Supply | LRE - Lockrose BS
Description | Land area is 688 sqm, Construction is pipework and shed class
Transformer size is 1x5/8MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.7% W 0.7%, 2025 S -1.2% W 0.8%,2026 S -0.5% W 0.3%,2027 S -1.1% W 0.1%
Load Category | Domestic
Localities | Supplies Bryden, Crossdale, Lake Wivenhoe, Mount Byron, Somerset Dam
|  |  |  | Latest Peak Compensated Load |  |  |  | 0.4 MVA on 18/03/2023 at 17:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Day | Day | Day | Day
NCC Rating (MVA) | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
50 PoE Load > 95% (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hours PA > 95% Peak Load | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
Raw LAR (MVA) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mobile Plant Avail (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## SPO
Zone Summary Information and Peak Load Forecast
Substation | SPO - Southport (110/11kV) | [5 empty] | Supply | MAR - MOLENDINAR 110 CP
Description | Land area is 4430 sqm, Construction is conventional all indoor class
Transformer size is 2x36/45/60MVA ONAN/ODAF;1x36/60MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.8% W 1.2%, 2025 S -1.2% W 1.1%,2026 S -0.6% W 0.5%,2027 S -0.8% W 0.8%
Load Category | Mixed Industrial
Localities | Supplies Arundel, Ashmore, Labrador, Main Beach, Southport
|  |  |  | Latest Peak Compensated Load |  |  |  | 71.1 MVA on 17/03/2023 at 16:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 172.7 | 172.7 | 172.7 | 172.7 | 172.7 | 182.9 | 182.9 | 182.9 | 182.9 | 182.9
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 74.9 | 74 | 73.5 | 72.9 | 73 | 60 | 60.7 | 61.3 | 61.7 | 62.1
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998
ECC Rating (MVA) | 114.5 | 114.5 | 114.5 | 114.5 | 114.5 | 120.1 | 120.1 | 120.1 | 120.1 | 120.1
50 PoE Load (MVA) | 71.5 | 70.6 | 70.2 | 69.6 | 69.7 | 57 | 57.7 | 58.4 | 58.7 | 59.1
50 PoE Load > 95% (MVA) | 3.6 | 3.5 | 3.5 | 3.5 | 3.5 | 2.9 | 2.9 | 2.9 | 2.9 | 3
Hours PA > 95% Peak Load | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5
Raw LAR (MVA)
2HR Rating (MVA) | 143.3 | 143.3 | 143.3 | 143.3 | 143.3 | 160.5 | 160.5 | 160.5 | 160.5 | 160.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO
Capacity for Embedded Generation (MVA) | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108
N-1 Capacity for Embedded Generation (MVA) | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## SPC
Zone Summary Information and Peak Load Forecast
Substation | SPC - Spring Creek (33/11kV) | [5 empty] | Supply | GBS - Gatton BS
Description | Land area is 6400 sqm, Construction is single modular class
Transformer size is 1x15MVA ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 2.8 MVA
Growth Rates | 2023 W 1.0%, 2024 S 1.7% W -0.4%,2025 S -3.4% W -0.5%2026 S -1.3% W -1.0%2027 S -1.9% W -1.1
Load Category | Mixed Industrial
Localities | Supplies Adare, Atkinsons Dam, Buaraba, Churchable, Coominya, Lake Clarendon, Morton Vale, Spring Creek
|  |  |  | Latest Peak Compensated Load |  |  |  | 3.7 MVA on 31/01/2023 at 14:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Day | Day | Day | Day
NCC Rating (MVA) | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 4.1 | 3.9 | 3.9 | 3.8 | 3.8 | 2.9 | 2.9 | 2.9 | 2.9 | 2.8
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.905 | 0.905 | 0.905 | 0.905 | 0.905 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 3.8 | 3.7 | 3.6 | 3.5 | 3.5 | 2.7 | 2.7 | 2.7 | 2.7 | 2.6
50 PoE Load > 95% (MVA) | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Hours PA > 95% Peak Load | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
Raw LAR (MVA) | 3.8 | 3.7 | 3.6 | 3.5 | 3.5 | 2.7 | 2.7 | 2.7 | 2.7 | 2.6
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
Mobile Plant Avail (MVA) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## SPF
Zone Summary Information and Peak Load Forecast
Substation | SPF - Springfield (33/11kV) | [5 empty] | Supply | GNA - Goodna BS
Description | Land area is 4000 sqm, Construction is single modular class
Transformer size is 2x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 22.6 MVA
Growth Rates | 2023 W 1.0%, 2024 S 1.3% W 0.0%, 2025 S -2.5% W 0.0%,2026 S -1.1% W -0.2%2027 S -1.4% W 0.3%
Load Category | Domestic
Localities | Supplies Augustine Heights, Brookwater, Springfield, Springfield Lakes
|  |  |  | Latest Peak Compensated Load |  |  |  | 29.9 MVA on 17/03/2023 at 17:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 59.9 | 59.9 | 59.9 | 59.9 | 59.9 | 59.9 | 59.9 | 59.9 | 59.9 | 59.9
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 31.3 | 30.5 | 30.2 | 29.8 | 29.5 | 20.7 | 20.7 | 20.7 | 20.6 | 20.7
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.991 | 0.991 | 0.991 | 0.991 | 0.991 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
50 PoE Load (MVA) | 28.9 | 28.2 | 27.9 | 27.5 | 27.3 | 20 | 20 | 20 | 20 | 20
50 PoE Load > 95% (MVA) | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1 | 1 | 1 | 1 | 1
Hours PA > 95% Peak Load | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Raw LAR (MVA)
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## SFC
Zone Summary Information and Peak Load Forecast
Substation | SFC - Springfield Central (33/11kV) | [5 empty] | Supply | GNA - Goodna BS
Description | Construction is conventional indoor/outdoor class
Transformer size is 2x15/25MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 4.5% W 4.1%, 2025 S 0.7% W 4.4%, 2026 S 1.3% W 4.4%, 2027 S 3.3% W 6.6%
Load Category | Mixed Industrial
Localities | Supplies Springfield
|  |  |  | Latest Peak Compensated Load |  |  |  | 21.2 MVA on 17/03/2023 at 17:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 54.9 | 54.9 | 54.9 | 54.9 | 54.9 | 54.9 | 54.9 | 54.9 | 54.9 | 54.9
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 22.4 | 25.1 | 25.4 | 26.1 | 27.1 | 17.4 | 18.1 | 20.7 | 21.5 | 22.8
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.988 | 0.988 | 0.988 | 0.988 | 0.988
ECC Rating (MVA) | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5
50 PoE Load (MVA) | 20.6 | 23.3 | 23.5 | 24.2 | 25.1 | 15 | 15.6 | 18.1 | 18.8 | 19.9
50 PoE Load > 95% (MVA) | 1 | 1.2 | 1.2 | 1.2 | 1.3 | 0.8 | 0.8 | 0.9 | 0.9 | 1
Hours PA > 95% Peak Load | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Raw LAR (MVA)
2HR Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## STL
Zone Summary Information and Peak Load Forecast
Substation | STL - St Lucia (33/11kV) | [5 empty] | Supply | TSN - Tennyson BS
Description | Land area is 1010 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x10/12.5/15MVA ONAN/OFAF;1x14.5/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.0% W -0.1%,2025 S -1.6% W 0.1%,2026 S -0.9% W -0.4%2027 S -1.5% W -0.5
Load Category | Industrial
Localities | Supplies St Lucia, Taringa, Yeronga
|  |  |  | Latest Peak Compensated Load |  |  |  | 26.9 MVA on 16/03/2023 at 16:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Day | Day | Day | Day
NCC Rating (MVA) | 49.3 | 49.3 | 49.3 | 49.3 | 49.3 | 49.3 | 49.3 | 49.3 | 49.3 | 49.3
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 27.6 | 27.1 | 26.9 | 26.4 | 26.3 | 23 | 22.9 | 23 | 22.9 | 22.8
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.985 | 0.985 | 0.985 | 0.985 | 0.985
ECC Rating (MVA) | 34.5 | 34.5 | 34.5 | 34.5 | 34.5 | 39 | 39 | 39 | 39 | 39
50 PoE Load (MVA) | 26.3 | 25.9 | 25.7 | 25.3 | 25.1 | 21.9 | 21.8 | 21.9 | 21.8 | 21.7
50 PoE Load > 95% (MVA) | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1
Hours PA > 95% Peak Load | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5
Raw LAR (MVA)
2HR Rating (MVA) | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 42 | 42 | 42 | 42 | 42
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO
Capacity for Embedded Generation (MVA) | 34.5 | 34.5 | 34.5 | 34.5 | 34.5 | 34.5 | 34.5 | 34.5 | 34.5 | 34.5
N-1 Capacity for Embedded Generation (MVA) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## SFD
Zone Summary Information and Peak Load Forecast
Substation | SFD - Stafford (33/11kV) | [5 empty] | Supply | SFD - Stafford BS
Description | Land area is 9770 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x15/20/25MVA ONAN/ONAF/OFAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.2% W -0.1%,2025 S -1.6% W 0.1%,2026 S -0.9% W -0.4%2027 S -1.5% W -0.5
Load Category | Domestic
Localities | Supplies Aspley, Bridgeman Downs, Chermside, Chermside West, Everton Park, Kedron, Mcdowall, Stafford, Stafford Heights
|  |  |  | Latest Peak Compensated Load |  |  |  | 30.2 MVA on 17/03/2023 at 16:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 32.7 | 32.2 | 31.9 | 31.4 | 31.2 | 25.3 | 25.3 | 25.3 | 25.2 | 25.1
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 30 | 30 | 30 | 30 | 30
50 PoE Load (MVA) | 30.2 | 29.7 | 29.4 | 29 | 28.8 | 23.8 | 23.8 | 23.8 | 23.8 | 23.6
50 PoE Load > 95% (MVA) | 1.5 | 1.5 | 1.5 | 1.5 | 1.4 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2
Hours PA > 95% Peak Load | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
Raw LAR (MVA) | SUMMER 2023/24: 2.7; SUMMER 2024/25: 2.2; SUMMER 2025/26: 1.9; SUMMER 2026/27: 1.5; SUMMER 2027/28: 1.3
2HR Rating (MVA) | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 30 | 30 | 30 | 30 | 30
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO
Capacity for Embedded Generation (MVA) | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9
N-1 Capacity for Embedded Generation (MVA) | 2.475 | 2.475 | 2.475 | 2.475 | 2.475 | 2.475 | 2.475 | 2.475 | 2.475 | 2.475
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## STT
Zone Summary Information and Peak Load Forecast
Substation | STT - Stapylton (33/11kV) | [5 empty] | Supply | BLH - Beenleigh BS
Description | Land area is 47950 sqm, Construction is multiple modular class
Transformer size is 1x15/25MVA ONAN/ODAF;1x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.3% W -0.1%,2025 S -1.5% W 0.1%,2026 S -0.9% W -0.5%2027 S -1.5% W -0.6
Load Category | Mixed Industrial
Localities | Supplies Alberton, Ormeau, Russell Island, Staplyton, Steiglitz, Woongoolba, Yatala
|  |  |  | Latest Peak Compensated Load |  |  |  | 11 MVA on 23/03/2023 at 08:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 54.4 | 54.4 | 54.4 | 54.4 | 54.4 | 54.4 | 54.4 | 54.4 | 54.4 | 54.4
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 11.9 | 11.8 | 11.7 | 11.5 | 11.4 | 9.7 | 10.1 | 10.1 | 10 | 10
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.966 | 0.966 | 0.966 | 0.966 | 0.966 | 0.988 | 0.988 | 0.988 | 0.988 | 0.988
ECC Rating (MVA) | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5
50 PoE Load (MVA) | 11.7 | 11.5 | 11.4 | 11.3 | 11.2 | 9.1 | 9.5 | 9.5 | 9.4 | 9.4
50 PoE Load > 95% (MVA) | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hours PA > 95% Peak Load | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5
Raw LAR (MVA)
2HR Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4
Mobile Plant Avail (MVA) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## SIS
Zone Summary Information and Peak Load Forecast
Substation | SIS - Stradbroke Is (33/11kV) | [5 empty] | Supply | SIS - Stradbroke Is BS
Description | Land area is 19020 sqm, Construction is pipework and shed class
Transformer size is 1x5/6.25MVA ONAN/ONAF;1x5MVA ONAN(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.4% W 0.0%, 2025 S -1.3% W 0.1%,2026 S -0.7% W -0.4%2027 S -1.2% W -0.5
Load Category | Domestic
Localities | Supplies Amity, Dunwich, North Stradbroke Island, Point Lookout
|  |  |  | Latest Peak Compensated Load |  |  |  | 4.5 MVA on 01/01/2023 at 19:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 5.1 | 5 | 5 | 4.9 | 4.9 | 4.4 | 4.3 | 4.4 | 4.3 | 4.3
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.989 | 0.989 | 0.989 | 0.989 | 0.989 | 0.993 | 0.993 | 0.993 | 0.993 | 0.993
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 4.9 | 4.9 | 4.8 | 4.8 | 4.8 | 4 | 4 | 4 | 4 | 4
50 PoE Load > 95% (MVA) | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hours PA > 95% Peak Load | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5
Raw LAR (MVA) | 4.9 | 4.9 | 4.8 | 4.8 | 4.8 | 4 | 4 | 4 | 4 | 4
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 6.7 | 0 | 0 | 0 | 0 | 7.4 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mobile Plant Avail (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
N-1 Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## SPE
Zone Summary Information and Peak Load Forecast
Substation | SPE - Strathpine (33/11kV) | [5 empty] | Supply | BRD - Brendale BS
Description | Land area is 2560 sqm, Construction is a mixture of various construction classes
Transformer size is 2x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.9 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.7% W -0.6%,2025 S -2.3% W -0.4%2026 S -1.6% W -0.7%2027 S -2.1% W -0.7
Load Category | Mixed Industrial
Localities | Supplies Brendale, Strathpine
|  |  |  | Latest Peak Compensated Load |  |  |  | 28.3 MVA on 31/01/2023 at 14:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Day | Day | Day | Day
NCC Rating (MVA) | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 30 | 30.7 | 30.2 | 29.6 | 29.5 | 21.7 | 22.5 | 22.4 | 22.3 | 22.1
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.992 | 0.992 | 0.992 | 0.992 | 0.992 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 30.8 | 30.8 | 30.8 | 30.8 | 30.8 | 34.8 | 34.8 | 34.8 | 34.8 | 34.8
50 PoE Load (MVA) | 28.4 | 29.1 | 28.6 | 28 | 27.9 | 21.4 | 21.5 | 21.4 | 21.3 | 21.1
50 PoE Load > 95% (MVA) | 1.4 | 1.5 | 1.4 | 1.4 | 1.4 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1
Hours PA > 95% Peak Load | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
Raw LAR (MVA)
2HR Rating (MVA) | 30.8 | 30.8 | 30.8 | 30.8 | 30.8 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## SMR
Zone Summary Information and Peak Load Forecast
Substation | SMR - Sumner (110/11kV) | [5 empty] | Supply | SUM - SUMNER 110 CP
Description | Land area is 10610 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x36/60MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.8% W -0.5%,2025 S -2.3% W -0.6%2026 S -1.5% W -0.2%2027 S -2.1% W -0.3
Load Category | Mixed Industrial
Localities | Supplies Darra, Jamboree Heights, Middle Park, Mount Ommaney, Oxley, Riverhills, Seventeen Mile Rocks, Sinnamon Park, Sumner, Westlake
|  |  |  | Latest Peak Compensated Load |  |  |  | 32 MVA on 17/03/2023 at 15:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Day | Night | Day | Night
NCC Rating (MVA) | 129.6 | 129.6 | 129.6 | 129.6 | 129.6 | 131.9 | 131.9 | 131.9 | 131.9 | 131.9
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 35.2 | 34.4 | 33.9 | 33.2 | 32.9 | 25.3 | 25.1 | 25 | 24.9 | 24.9
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 69 | 69 | 69 | 69 | 69 | 76.3 | 76.3 | 76.3 | 76.3 | 76.3
50 PoE Load (MVA) | 32.7 | 31.9 | 31.4 | 30.8 | 30.5 | 24.3 | 24.1 | 24 | 23.9 | 23.9
50 PoE Load > 95% (MVA) | 1.6 | 1.6 | 1.6 | 1.5 | 1.5 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2
Hours PA > 95% Peak Load | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Raw LAR (MVA)
2HR Rating (MVA) | 75 | 75 | 75 | 75 | 75 | 84 | 84 | 84 | 84 | 84
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
N-1 Capacity for Embedded Generation (MVA) | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## SBK
Zone Summary Information and Peak Load Forecast
Substation | SBK - Sunnybank (33/11kV) | [5 empty] | Supply | RBS - Runcorn BS
Description | Land area is 3650 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x13 MVA ONAN;1x15MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.9 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.4% W 0.2%, 2025 S -1.4% W 0.3%,2026 S -0.7% W -0.3%2027 S -1.5% W -0.6
Load Category | Industrial
Localities | Supplies Coopers Plains, Eight Mile Plains, Macgregor, Nathan, Robertson, Sunnybank
|  |  |  | Latest Peak Compensated Load |  |  |  | 29.8 MVA on 03/02/2023 at 13:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Day | Day | Day | Day
NCC Rating (MVA) | 41.6 | 41.6 | 41.6 | 41.6 | 41.6 | 41.6 | 41.6 | 41.6 | 41.6 | 41.6
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 31.3 | 30.9 | 30.6 | 30.2 | 31 | 23.9 | 23.9 | 24 | 23.9 | 23.8
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.997 | 0.997 | 0.997 | 0.998 | 0.997 | 0.993 | 0.993 | 0.993 | 0.993 | 0.993
ECC Rating (MVA) | 30.9 | 30.9 | 30.9 | 30.9 | 30.9 | 33 | 33 | 33 | 33 | 33
50 PoE Load (MVA) | 29.6 | 29.2 | 29 | 28.6 | 29.4 | 23.2 | 23.2 | 23.3 | 23.2 | 23.1
50 PoE Load > 95% (MVA) | 1.5 | 1.5 | 1.5 | 1.4 | 1.5 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2
Hours PA > 95% Peak Load | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Raw LAR (MVA)
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.7 | 37.7 | 37.7 | 37.7 | 37.7
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
N-1 Capacity for Embedded Generation (MVA) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## SPD
Zone Summary Information and Peak Load Forecast
Substation | SPD - Surfers Paradise (110/11kV) | [5 empty] | Supply | MAR - MOLENDINAR 110 CP
Description | Land area is 1590 sqm, Construction is conventional all indoor class
Transformer size is 1x30/50MVA ONAN/OFDAF;1x36/60MVA ONAN/ODAF;1x36/60MVA ONAN/OFDAF 110/11kV
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.9 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.9% W 0.9%, 2025 S -1.2% W 1.0%,2026 S -0.6% W 0.4%,2027 S -1.3% W 0.2%
Load Category | Mixed Industrial
Localities | Supplies Main Beach, Surfers Paradise
|  |  |  | Latest Peak Compensated Load |  |  |  | 50.7 MVA on 04/07/2022 at 17:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 182 | 182 | 182 | 182 | 182 | 185 | 185 | 185 | 185 | 185
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 49.3 | 55.3 | 55.2 | 54.6 | 54.6 | 53.2 | 53.7 | 59.8 | 60 | 60.1
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.996 | 1 | 0.995 | 0.995 | 0.995 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 111.8 | 111.8 | 111.8 | 111.8 | 111.8 | 124.4 | 124.4 | 124.4 | 124.4 | 124.4
50 PoE Load (MVA) | 47.2 | 53.5 | 53.2 | 52.6 | 52.6 | 51.2 | 51.7 | 57.5 | 57.7 | 57.8
50 PoE Load > 95% (MVA) | 2.4 | 2.7 | 2.7 | 2.6 | 2.6 | 2.6 | 2.6 | 2.9 | 2.9 | 2.9
Hours PA > 95% Peak Load | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
Raw LAR (MVA)
2HR Rating (MVA) | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 136.1 | 136.1 | 136.1 | 136.1 | 136.1
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO
Capacity for Embedded Generation (MVA) | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92
N-1 Capacity for Embedded Generation (MVA) | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## TBV
Zone Summary Information and Peak Load Forecast
Substation | TBV - Tamborine Village (33/11kV) | [5 empty] | Supply | BLH - Beenleigh BS
Description | Construction is mini-modular (skid) class
Transformer size is 1x5/8MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.5% W 0.4%, 2025 S -1.2% W 0.6%,2026 S -0.6% W 0.1%,2027 S -1.2% W -0.2
Load Category | Domestic
Localities | Supplies Birnam, Mundoolun, Tamborine
|  |  |  | Latest Peak Compensated Load |  |  |  | 4.8 MVA on 17/03/2023 at 17:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 5 | 5 | 4.9 | 4.9 | 4.9 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 4.5 | 4.4 | 4.4 | 4.4 | 4.3 | 3.4 | 3.5 | 3.5 | 3.5 | 3.5
50 PoE Load > 95% (MVA) | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hours PA > 95% Peak Load | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Raw LAR (MVA) | 4.5 | 4.4 | 4.4 | 4.4 | 4.3 | 3.4 | 3.5 | 3.5 | 3.5 | 3.5
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | bar: SUMMER 2023/24 to WINTER 2027
Mobile Plant Avail (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
N-1 Capacity for Embedded Generation (MVA) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## TMH
Zone Summary Information and Peak Load Forecast
Substation | TMH - Tanah Merah (33/11kV) | [5 empty] | Supply | LGL - Loganlea BS
Description | Land area is 3880 sqm, Construction is single modular class
Transformer size is 2x15MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.9% W 0.0%, 2025 S -2.2% W 0.1%,2026 S -1.0% W -0.4%2027 S -1.5% W -0.6
Load Category | Domestic
Localities | Supplies Bethania, Daisy Hill, Meadowbrook, Shailer Park, Slacks Creek, Tanah Merah
|  |  |  | Latest Peak Compensated Load |  |  |  | 17 MVA on 17/03/2023 at 17:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 35.5 | 35.5 | 35.5 | 35.5 | 35.5 | 35.5 | 35.5 | 35.5 | 35.5 | 35.5
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 18.6 | 18.2 | 18 | 17.8 | 17.7 | 14.6 | 14.6 | 14.6 | 14.6 | 14.5
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 20.3 | 20.3 | 20.3 | 20.3 | 20.3 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5
50 PoE Load (MVA) | 17.6 | 17.2 | 17 | 16.8 | 16.7 | 13.8 | 13.8 | 13.8 | 13.7 | 13.7
50 PoE Load > 95% (MVA) | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Hours PA > 95% Peak Load | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
Raw LAR (MVA)
2HR Rating (MVA) | 21.8 | 21.8 | 21.8 | 21.8 | 21.8 | 24 | 24 | 24 | 24 | 24
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## TRP
Zone Summary Information and Peak Load Forecast
Substation | TRP - Tarampa (33/11kV) | [5 empty] | Supply | LRE - Lockrose BS
Description | Land area is 3030 sqm, Construction is pipework and shed class
Transformer size is 1x5/6.0MVA ONAN/ONAF;1x5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.6% W 0.5%, 2025 S -1.3% W 0.4%,2026 S -0.6% W -0.1%2027 S -1.2% W -0.3
Load Category | Domestic
Localities | Supplies Brightview, Clarendon, Coolana, Coominya, Glamorgan Vale, Hatton Vale, Lowood, Minden, Mount Tarampa, Patrick Estate, Prenzlau, Rifle Range, Tarampa
|  |  |  | Latest Peak Compensated Load |  |  |  | 7.5 MVA on 12/02/2023 at 18:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2 | 13.2
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 8.3 | 8.2 | 8.1 | 8.1 | 8 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.985 | 0.985 | 0.985 | 0.985 | 0.985 | 0.992 | 0.992 | 0.992 | 0.992 | 0.992
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 7.6 | 7.5 | 7.5 | 7.4 | 7.4 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7
50 PoE Load > 95% (MVA) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Hours PA > 95% Peak Load | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Raw LAR (MVA) | 7.6 | 7.5 | 7.5 | 7.4 | 7.4 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7
2HR Rating (MVA)
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 11.05 | 11.05 | 11.05 | 11.05 | 11.05 | 11.05 | 11.05 | 11.05 | 11.05 | 11.05
Mobile Plant Avail (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO
Capacity for Embedded Generation (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
N-1 Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## TRG
Zone Summary Information and Peak Load Forecast
Substation | TRG - Taringa (33/11kV) | [5 empty] | Supply | TSN - Tennyson BS
Description | Land area is 2601 sqm, Construction is conventional indoor/outdoor class
Transformer size is 1x15/25MVA ONAN/ODAF;1x15MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.5% W 0.7%, 2025 S -2.5% W 0.8%,2026 S -1.0% W 0.3%,2027 S -1.1% W 0.4%
Load Category | Domestic
Localities | Supplies Indooroopilly, St Lucia, Taringa, Toowong
|  |  |  | Latest Peak Compensated Load |  |  |  | 15.1 MVA on 17/03/2023 at 16:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 34.9 | 34.9 | 34.9 | 34.9 | 34.9 | 34.9 | 34.9 | 34.9 | 34.9 | 34.9
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 16 | 15.6 | 15.5 | 15.3 | 15.3 | 12.3 | 12.4 | 12.5 | 12.6 | 12.6
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 20.3 | 20.3 | 20.3 | 20.3 | 20.3 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5
50 PoE Load (MVA) | 14.4 | 14.1 | 13.9 | 13.8 | 13.8 | 11.4 | 11.5 | 11.6 | 11.6 | 11.7
50 PoE Load > 95% (MVA) | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
Hours PA > 95% Peak Load | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5
Raw LAR (MVA)
2HR Rating (MVA) | 21.8 | 21.8 | 21.8 | 21.8 | 21.8 | 24 | 24 | 24 | 24 | 24
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## TSN
Zone Summary Information and Peak Load Forecast
Substation | TSN - Tennyson (33/11kV) | [5 empty] | Supply | TSN - Tennyson BS
Description | Land area is 10400 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x15/25MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.0% W -0.2%,2025 S -1.6% W 0.0%,2026 S -1.0% W -0.6%2027 S -1.6% W -0.8
Load Category | Mixed Industrial
Localities | Supplies Graceville, Rocklea, Tennyson, Yeerongpilly
|  |  |  | Latest Peak Compensated Load |  |  |  | 10.7 MVA on 09/03/2023 at 10:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Day | Day | Day | Day
NCC Rating (MVA) | 54.5 | 54.5 | 54.5 | 54.5 | 54.5 | 54.5 | 54.5 | 54.5 | 54.5 | 54.5
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 11.6 | 11.4 | 11.3 | 11.1 | 11 | 9.3 | 9.3 | 9.3 | 9.3 | 9.2
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.981 | 0.981 | 0.981 | 0.981 | 0.981 | 0.989 | 0.989 | 0.989 | 0.989 | 0.989
ECC Rating (MVA) | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5
50 PoE Load (MVA) | 10.9 | 10.7 | 10.6 | 10.4 | 10.3 | 8.9 | 8.9 | 8.9 | 8.9 | 8.8
50 PoE Load > 95% (MVA) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Hours PA > 95% Peak Load | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5
Raw LAR (MVA)
2HR Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## THL
Zone Summary Information and Peak Load Forecast
Substation | THL - Tenthill (33/11kV) | [5 empty] | Supply | GBS - Gatton BS
Description | Land area is 2023 sqm, Construction is pipework and shed class
Transformer size is 1x5/8MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.4% W 0.1%, 2025 S -1.4% W 0.1%,2026 S -0.8% W -0.5%2027 S -1.4% W -0.6
Load Category | Domestic
Localities | Supplies Blenheim, Caffey, Egypt, Fordsdale, Gatton, Glen Cairn, Ingoldsby, Lilydale, Lower Tenthill, Ma Ma Creek, Mount Whitestone, Rockside, Ropeley, Upper Tenthill, West Haldon, Winwill, Woodlands
|  |  |  | Latest Peak Compensated Load |  |  |  | 3 MVA on 12/02/2023 at 18:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 3.2 | 3.1 | 3.1 | 3.1 | 3 | 2.7 | 2.7 | 2.7 | 2.7 | 2.6
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.984 | 0.984 | 0.984 | 0.984 | 0.984 | 0.975 | 0.975 | 0.975 | 0.975 | 0.975
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 3 | 3 | 2.9 | 2.9 | 2.9 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
50 PoE Load > 95% (MVA) | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Hours PA > 95% Peak Load | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
Raw LAR (MVA) | 3 | 3 | 2.9 | 2.9 | 2.9 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4
Mobile Plant Avail (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## TWT
Zone Summary Information and Peak Load Forecast
Substation | TWT - Tewantin (33/11kV) | [5 empty] | Supply | SRH - Sunrise Hills BS
Description | Land area is 4700 sqm, Construction is pipework and shed class
Transformer size is 2x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.4% W -0.5%,2025 S -1.3% W -0.6%2026 S -0.7% W -1.2%2027 S -1.3% W -1.5
Load Category | Domestic
Localities | Supplies Cooroibah, Doonan, Eumundi, Noosaville, North Shore, Peregian Beach, Ringtail Creek, Tewantin, Tinbeerwah, Verrierdale, Weyba Downs, Yandina Creek
|  |  |  | Latest Peak Compensated Load |  |  |  | 25.2 MVA on 03/02/2023 at 18:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 58.7 | 58.7 | 58.7 | 58.7 | 58.7 | 58.7 | 58.7 | 58.7 | 58.7 | 58.7
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 26.9 | 26.6 | 26.4 | 26 | 25.9 | 23.6 | 23.5 | 23.3 | 23 | 22.7
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.994 | 0.994 | 0.994 | 0.994 | 0.994 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
50 PoE Load (MVA) | 25 | 24.7 | 24.5 | 24.2 | 24.1 | 22.3 | 22.2 | 22.1 | 21.8 | 21.5
50 PoE Load > 95% (MVA) | 1.3 | 1.2 | 1.2 | 1.2 | 1.2 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1
Hours PA > 95% Peak Load | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
Raw LAR (MVA)
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## GAP
Zone Summary Information and Peak Load Forecast
Substation | GAP - The Gap (33/11kV) | [5 empty] | Supply | AGW - Ashgrove West BS
Description | Land area is 4470 sqm, Construction is conventional all indoor class
Transformer size is 2x15MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.1% W 0.1%, 2025 S -1.7% W 0.3%,2026 S -1.0% W -0.2%2027 S -1.5% W -0.3
Load Category | Domestic
Localities | Supplies Enoggera Reservoir, Keperra, Mount Coot-tha, The Gap
|  |  |  | Latest Peak Compensated Load |  |  |  | 17.2 MVA on 12/02/2023 at 17:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Day | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 18.7 | 18.3 | 18.2 | 17.8 | 17.8 | 16.1 | 16.2 | 16.2 | 16.2 | 16.1
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.999 | 0.999 | 0.999 | 0.998 | 0.999 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 20.3 | 20.3 | 20.3 | 20.3 | 20.3 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5
50 PoE Load (MVA) | 17.5 | 17.2 | 17 | 16.7 | 16.7 | 15.4 | 15.4 | 15.4 | 15.4 | 15.3
50 PoE Load > 95% (MVA) | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
Hours PA > 95% Peak Load | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Raw LAR (MVA)
2HR Rating (MVA) | 21.8 | 21.8 | 21.8 | 21.8 | 21.8 | 24 | 24 | 24 | 24 | 24
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## TCB
Zone Summary Information and Peak Load Forecast
Substation | TCB - Tin Can Bay (33/11kV) | [5 empty] | Supply | GYM - Gympie BS
Description | Land area is 4880 sqm, Construction is pipework and shed class
Transformer size is 1x5/6.5MVA ONAN/ONAF;1x5/8MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.5% W 0.2%, 2025 S -1.5% W 0.2%,2026 S -0.8% W -0.3%2027 S -1.4% W -0.5
Load Category | Domestic
Localities | Supplies Cooloola, Cooloola Cove, Inskip, Rainbow Beach, Tin Can Bay
|  |  |  | Latest Peak Compensated Load |  |  |  | 8.2 MVA on 13/02/2023 at 17:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 17.4 | 17.4 | 17.4 | 17.4 | 17.4 | 17.4 | 17.4 | 17.4 | 17.4 | 17.4
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 9 | 8.9 | 8.8 | 8.7 | 8.6 | 8.3 | 8.4 | 8.4 | 8.4 | 8.3
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.995 | 0.995 | 0.995 | 0.995 | 0.995 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998
ECC Rating (MVA) | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1
50 PoE Load (MVA) | 8.3 | 8.1 | 8.1 | 8 | 7.9 | 7.5 | 7.6 | 7.6 | 7.6 | 7.5
50 PoE Load > 95% (MVA) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Hours PA > 95% Peak Load | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
Raw LAR (MVA) | SUMMER 2023/24: 0.2
2HR Rating (MVA) | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mobile Plant Avail (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO | Split wo ACO
Capacity for Embedded Generation (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
N-1 Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## TGP
Zone Summary Information and Peak Load Forecast
Substation | TGP - Tingalpa (33/11kV) | [5 empty] | Supply | DBS - Doboy BS
Description | Land area is 4780 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.8% W 0.2%, 2025 S -2.1% W 0.1%,2026 S -0.8% W -0.4%2027 S -1.4% W -0.5
Load Category | Domestic
Localities | Supplies Belmont, Carindale, Gumdale, Hemmant, Manly West, Ransome, Tingalpa, Wakerley, Wynnum West
|  |  |  | Latest Peak Compensated Load |  |  |  | 22.8 MVA on 17/03/2023 at 17:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 58.6 | 58.6 | 58.6 | 58.6 | 58.6
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 24.4 | 23.9 | 23.7 | 23.4 | 23.3 | 18.4 | 18.5 | 18.5 | 18.4 | 18.3
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.995 | 0.995 | 0.995 | 0.995 | 0.995 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 30.5 | 30.5 | 30.5 | 30.5 | 30.5 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4
50 PoE Load (MVA) | 23.1 | 22.6 | 22.5 | 22.1 | 22.1 | 17.4 | 17.4 | 17.5 | 17.4 | 17.3
50 PoE Load > 95% (MVA) | 1.2 | 1.1 | 1.1 | 1.1 | 1.1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Hours PA > 95% Peak Load | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
Raw LAR (MVA)
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## TGW
Zone Summary Information and Peak Load Forecast
Substation | TGW - Toogoolawah (33/11kV) | [5 empty] | Supply | LRE - Lockrose BS
Description | Land area is 4050 sqm, Construction is pipework and shed class
Transformer size is 1x5/8MVA ONAN/ONAF;3x1.5MVA ONAN(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.8% W 0.7%, 2025 S -0.9% W 0.9%,2026 S -0.3% W 0.3%,2027 S -0.9% W 0.1%
Load Category | Domestic
Localities | Supplies Avoca Vale, Biarra, Braemore, Caboonbah, Coal Creek, Colinton, Cooeeimbardi, Cressbrook, Eskdale, Fulham, Gregors Creek, Harlin, Ivory Creek, Lake Wivenhoe, Linville, Lower Cressbrook, Monsildale, Moore, Mount Beppo, Mount Stanley, Ottaba, Scrub Creek, Toogoolawah, Woolmar, Yimbun
|  |  |  | Latest Peak Compensated Load |  |  |  | 4.7 MVA on 12/02/2023 at 18:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 5.1 | 5 | 5.1 | 5.1 | 5.1 | 3.6 | 3.6 | 3.6 | 3.7 | 3.7
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 1 | 1 | 0.978 | 0.978 | 0.978 | 0.993 | 0.993 | 0.993 | 0.993 | 0.993
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 4.6 | 4.6 | 4.5 | 4.5 | 4.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
50 PoE Load > 95% (MVA) | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hours PA > 95% Peak Load | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
Raw LAR (MVA) | 4.6 | 4.6 | 4.5 | 4.5 | 4.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 6.8 | 6.8 | 6.8 | 6.8 | 0 | 6.8 | 6.8 | 6.8 | 6.8 | 0
Manual Trans Avail (MVA) | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Mobile Plant Avail (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
N-1 Capacity for Embedded Generation (MVA) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## TPT
Zone Summary Information and Peak Load Forecast
Substation | TPT - Toorbul Point (33/11kV) | [5 empty] | Supply | CBT - Caboolture BS
Description | Land area is 5660 sqm, Construction is pipework and shed class
Transformer size is 2x5MVA ONAN;1x5MVA ONAN(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.6% W -0.0%,2025 S -1.2% W -0.0%2026 S -0.3% W -0.6%2027 S -0.9% W -0.8
Load Category | Domestic
Localities | Supplies Beachmere, Godwin Beach, Ningi, Sandstone Point
|  |  |  | Latest Peak Compensated Load |  |  |  | 6.8 MVA on 04/07/2022 at 17:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 17.6 | 17.6 | 17.6 | 17.6 | 17.6 | 17.6 | 17.6 | 17.6 | 17.6 | 17.6
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 7 | 6.9 | 6.9 | 6.9 | 6.9 | 7.1 | 7.1 | 7.1 | 7 | 7
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 6.5 | 6.5 | 6.5 | 6.4 | 6.4 | 6.3 | 6.3 | 6.3 | 6.3 | 6.2
50 PoE Load > 95% (MVA) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Hours PA > 95% Peak Load | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
Raw LAR (MVA) | 6.5 | 6.5 | 6.5 | 6.4 | 6.4 | 6.3 | 6.3 | 6.3 | 6.3 | 6.2
2HR Rating (MVA)
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 17.4 | 17.4 | 17.4 | 17.4 | 17.4
Mobile Plant Avail (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
N-1 Capacity for Embedded Generation (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## TWG
Zone Summary Information and Peak Load Forecast
Substation | TWG - Toowong (33/11kV) | [5 empty] | Supply | AGW - Ashgrove West BS
Description | Land area is 2480 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x15/25MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.7% W 0.4%, 2025 S -2.4% W 0.4%,2026 S -1.5% W 0.1%,2027 S -1.1% W 0.2%
Load Category | Mixed Industrial
Localities | Supplies Auchenflower, Bardon, Indooroopilly, Milton, Mount Coot-tha, Paddington, Taringa, Toowong
|  |  |  | Latest Peak Compensated Load |  |  |  | 30.5 MVA on 17/03/2023 at 16:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 45.4 | 45.4 | 45.4 | 45.4 | 45.4 | 48 | 48 | 48 | 48 | 48
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 31.8 | 31 | 34 | 33.7 | 33.7 | 23.4 | 23.5 | 26.3 | 26.3 | 26.4
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 1 | 1 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 24 | 24 | 24 | 24 | 24
50 PoE Load (MVA) | 29.3 | 28.6 | 31.6 | 31.3 | 31.3 | 21.8 | 21.9 | 24.7 | 24.7 | 24.8
50 PoE Load > 95% (MVA) | 1.5 | 1.4 | 1.6 | 1.6 | 1.6 | 1.1 | 1.1 | 1.2 | 1.2 | 1.2
Hours PA > 95% Peak Load | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
Raw LAR (MVA) | 6.4 | 5.7 | 8.7 | 8.4 | 8.4 |  |  | 0.7 | 0.7 | 0.8
2HR Rating (MVA) | 25.1 | 25.1 | 25.1 | 25.1 | 25.1 | 26.3 | 26.3 | 26.3 | 26.3 | 26.3
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## UMG
Zone Summary Information and Peak Load Forecast
Substation | UMG - Upper Mt Gravatt (33/11kV) | [5 empty] | Supply | BBS - Belmont BS
Description | Land area is 4040 sqm, Construction is multiple modular class
Transformer size is 1x15/25MVA ONAN/ODAF;2x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.3% W 0.1%, 2025 S -1.6% W 0.0%,2026 S -0.9% W -0.5%2027 S -1.2% W -0.3
Load Category | Mixed Domestic
Localities | Supplies Coopers Plains, Eight Mile Plains, Macgregor, Robertson, Salisbury, Upper Mount Gravatt, Wishart
|  |  |  | Latest Peak Compensated Load |  |  |  | 25.8 MVA on 03/02/2023 at 12:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 26.8 | 26.4 | 26.2 | 25.8 | 25.8 | 19.4 | 19.5 | 19.5 | 19.4 | 19.3
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.981 | 0.981 | 0.981 | 0.981 | 0.981 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998
ECC Rating (MVA) | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 63.9 | 63.9 | 63.9 | 63.9 | 63.9
50 PoE Load (MVA) | 25.8 | 25.4 | 25.1 | 24.8 | 24.8 | 18.6 | 18.6 | 18.6 | 18.5 | 18.5
50 PoE Load > 95% (MVA) | 1.3 | 1.3 | 1.3 | 1.2 | 1.2 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Hours PA > 95% Peak Load | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Raw LAR (MVA)
2HR Rating (MVA) | 61.5 | 61.5 | 61.5 | 61.5 | 61.5 | 68.8 | 68.8 | 68.8 | 68.8 | 68.8
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO
Capacity for Embedded Generation (MVA) | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
N-1 Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## VSL
Zone Summary Information and Peak Load Forecast
Substation | VSL - Varsity Lakes (110/11kV) | [5 empty] | Supply | MGB - MUDGEERABA 110 CP
Description | Land area is 3100 sqm, Construction is conventional all indoor class
Transformer size is 2x36/60MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.4% W -0.1%,2025 S -1.8% W 0.1%,2026 S -1.0% W -0.2%2027 S -1.4% W -0.2
Load Category | Domestic
Localities | Supplies Burleigh Waters, Clear Island Waters, Mermaid Waters, Reedy Creek, Robina, Varsity Lakes
|  |  |  | Latest Peak Compensated Load |  |  |  | 32.6 MVA on 17/03/2023 at 16:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 64.1 | 64.1 | 64.1 | 64.1 | 64.1 | 68 | 68 | 68 | 68 | 68
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 36.9 | 36.2 | 35.9 | 35.4 | 35.2 | 26 | 26 | 26 | 26 | 25.9
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.994 | 0.994 | 0.994 | 0.994 | 0.994 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 34.9 | 34.9 | 34.9 | 34.9 | 34.9 | 36.6 | 36.6 | 36.6 | 36.6 | 36.6
50 PoE Load (MVA) | 33.5 | 32.9 | 32.6 | 32.1 | 32 | 25.1 | 25 | 25.1 | 25 | 25
50 PoE Load > 95% (MVA) | 1.7 | 1.6 | 1.6 | 1.6 | 1.6 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
Hours PA > 95% Peak Load | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
Raw LAR (MVA)
2HR Rating (MVA) | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 45 | 45 | 45 | 45 | 45
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
N-1 Capacity for Embedded Generation (MVA) | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## VPK
Zone Summary Information and Peak Load Forecast
Substation | VPK - Victoria Park (110/11kV) | [5 empty] | Supply | MRE - MURARRIE 110 CP
Description | Land area is 10200 sqm, Construction is conventional all indoor class
Transformer size is 2x30/60MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 9.3 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.4% W 0.1%, 2025 S -1.4% W 0.2%,2026 S -0.8% W -0.4%2027 S -1.5% W -0.6
Load Category | Industrial
Localities | Supplies Bowen Hills, Brisbane City, Fortitude Valley, Herston, Newstead, Spring Hill
|  |  |  | Latest Peak Compensated Load |  |  |  | 42.5 MVA on 03/02/2023 at 14:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Day | Day | Day | Day
NCC Rating (MVA) | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 46.9 | 46.3 | 45.9 | 45.3 | 45 | 30.6 | 32.1 | 32.2 | 32.1 | 31.9
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 69 | 69 | 69 | 69 | 69 | 78 | 78 | 78 | 78 | 78
50 PoE Load (MVA) | 45.3 | 44.7 | 44.3 | 43.7 | 43.5 | 29.4 | 30.9 | 31 | 30.9 | 30.7
50 PoE Load > 95% (MVA) | 2.3 | 2.2 | 2.2 | 2.2 | 2.2 | 1.5 | 1.5 | 1.6 | 1.5 | 1.5
Hours PA > 95% Peak Load | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5
Raw LAR (MVA)
2HR Rating (MVA) | 75 | 75 | 75 | 75 | 75 | 84 | 84 | 84 | 84 | 84
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
N-1 Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## VPT
Zone Summary Information and Peak Load Forecast
Substation | VPT - Victoria Point (33/11kV) | [5 empty] | Supply | CVL - Cleveland BS
Description | Land area is 5264 sqm, Construction is multiple modular class
Transformer size is 1x14.5/25MVA ONAN/ONAF;1x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.3% W 0.1%, 2025 S -1.5% W 0.1%,2026 S -0.8% W -0.4%2027 S -1.4% W -0.3
Load Category | Domestic
Localities | Supplies Coochiemudlo Island, Mount Cotton, Thornlands, Victoria Point
|  |  |  | Latest Peak Compensated Load |  |  |  | 23.4 MVA on 17/03/2023 at 17:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 59.4 | 59.4 | 59.4 | 59.4 | 59.4 | 59.4 | 59.4 | 59.4 | 59.4 | 59.4
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 25.3 | 25 | 24.8 | 24.4 | 24.3 | 22.3 | 22.3 | 22.3 | 22.2 | 22.2
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
50 PoE Load (MVA) | 24 | 23.6 | 23.4 | 23.1 | 23 | 20 | 20 | 20 | 19.9 | 19.9
50 PoE Load > 95% (MVA) | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1 | 1 | 1 | 1 | 1
Hours PA > 95% Peak Load | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Raw LAR (MVA)
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5
Mobile Plant Avail (MVA) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5
N-1 Capacity for Embedded Generation (MVA) | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## WCL
Zone Summary Information and Peak Load Forecast
Substation | WCL - Wacol (33/11kV) | [5 empty] | Supply | RLD - Richlands BS
Description | Land area is 9570 sqm, Construction is conventional all indoor class
Transformer size is 1x14.5/25MVA ONAN/ONAF;2x15/25MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 2.2 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.8% W -0.2%,2025 S -2.3% W -0.2%2026 S -1.8% W -0.8%2027 S -2.6% W -1.0
Load Category | Industrial
Localities | Supplies Bellbowrie, Darra, Moggill, Richlands, Riverhills, Sumner, Wacol
|  |  |  | Latest Peak Compensated Load |  |  |  | 23.7 MVA on 01/02/2023 at 13:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Day | Day | Day | Day
NCC Rating (MVA) | 75.4 | 75.4 | 75.4 | 75.4 | 75.4 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 26 | 31.5 | 31 | 30.4 | 30 | 18.8 | 25 | 25 | 24.9 | 24.7
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.996 | 0.992 | 0.993 | 0.993 | 0.993 | 0.981 | 0.981 | 0.981 | 0.981 | 0.981
ECC Rating (MVA) | 46 | 46 | 46 | 46 | 46 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3
50 PoE Load (MVA) | 24.7 | 30.3 | 29.8 | 29.2 | 28.8 | 18.5 | 24.7 | 24.7 | 24.5 | 24.3
50 PoE Load > 95% (MVA) | 1.2 | 1.5 | 1.5 | 1.5 | 1.4 | 0.9 | 1.2 | 1.2 | 1.2 | 1.2
Hours PA > 95% Peak Load | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Raw LAR (MVA)
2HR Rating (MVA) | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 52.9 | 52.9 | 52.9 | 52.9 | 52.9
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO
Capacity for Embedded Generation (MVA) | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5
N-1 Capacity for Embedded Generation (MVA) | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## WSO
Zone Summary Information and Peak Load Forecast
Substation | WSO - Wacol South (33/11kV) | [5 empty] | Supply | RLD - Richlands BS
Description | Land area is 4000 sqm, Construction is multiple modular class
Transformer size is 2x15/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.1% W 0.2%, 2025 S -1.9% W 0.4%,2026 S -1.2% W -0.2%2027 S -1.8% W -0.4
Load Category | Industrial
Localities | Supplies Carole Park, Ellen Grove, Forest Lake, Richlands, Wacol
|  |  |  | Latest Peak Compensated Load |  |  |  | 21.6 MVA on 03/02/2023 at 15:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 23.8 | 24.8 | 24.5 | 24.1 | 24 | 20.5 | 21.8 | 21.9 | 21.8 | 21.7
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.991 | 0.991 | 0.991 | 0.991 | 0.991 | 0.996 | 0.996 | 0.996 | 0.996 | 0.996
ECC Rating (MVA) | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5
50 PoE Load (MVA) | 22.3 | 23.3 | 23 | 22.7 | 22.5 | 19.8 | 21.1 | 21.2 | 21.2 | 21.1
50 PoE Load > 95% (MVA) | 1.1 | 1.2 | 1.2 | 1.1 | 1.1 | 1 | 1.1 | 1.1 | 1.1 | 1.1
Hours PA > 95% Peak Load | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
Raw LAR (MVA)
2HR Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9 | 11.9
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## WMR
Zone Summary Information and Peak Load Forecast
Substation | WMR - Wamuran (33/11kV) | [5 empty] | Supply | CBT - Caboolture BS
Description | Land area is 9265 sqm, Construction is mini-modular (skid) class
Transformer size is 1x5/8MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.3% W 0.0%, 2025 S -1.5% W 0.2%,2026 S -0.8% W -0.2%2027 S -0.2% W 0.9%
Load Category | Domestic
Localities | Supplies Bellmere, Bracalba, Wamuran, Wamuran Basin
|  |  |  | Latest Peak Compensated Load |  |  |  | 4.2 MVA on 12/02/2023 at 18:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 4.6 | 4.5 | 4.5 | 4.5 | 4.5 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 4.3 | 4.2 | 4.2 | 4.2 | 4.2 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
50 PoE Load > 95% (MVA) | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hours PA > 95% Peak Load | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
Raw LAR (MVA) | 4.3 | 4.2 | 4.2 | 4.2 | 4.2 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1
Mobile Plant Avail (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## WRD
Zone Summary Information and Peak Load Forecast
Substation | WRD - Wellington Rd (110/11kV) | [5 empty] | Supply | BMH - BELMONT 110 CP
Description | Land area is 2530 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x36/60MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 32.6 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.4% W 0.5%, 2025 S -1.5% W 0.6%,2026 S -0.7% W 0.0%,2027 S -1.3% W -0.3
Load Category | Industrial
Localities | Supplies Coorparoo, East Brisbane, Greenslopes, Kangaroo Point, Norman Park, South Brisbane, Woolloongabba
|  |  |  | Latest Peak Compensated Load |  |  |  | 55.4 MVA on 03/02/2023 at 12:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 125.8 | 125.8 | 125.8 | 125.8 | 125.8 | 125.8 | 125.8 | 125.8 | 125.8 | 125.8
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 60.3 | 64.8 | 64.5 | 63.7 | 63.6 | 38 | 45.9 | 46.1 | 46.1 | 46
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 1 | 0.999 | 0.999 | 0.999 | 0.999 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
ECC Rating (MVA) | 69 | 69 | 69 | 69 | 69 | 78 | 78 | 78 | 78 | 78
50 PoE Load (MVA) | 58.5 | 63.2 | 62.8 | 62.1 | 61.9 | 36.2 | 44.1 | 44.3 | 44.3 | 44.2
50 PoE Load > 95% (MVA) | 2.9 | 3.2 | 3.1 | 3.1 | 3.1 | 1.8 | 2.2 | 2.2 | 2.2 | 2.2
Hours PA > 95% Peak Load | 20.5 | 20.5 | 20.5 | 20.5 | 20.5 | 20.5 | 20.5 | 20.5 | 20.5 | 20.5
Raw LAR (MVA)
2HR Rating (MVA) | 75 | 75 | 75 | 75 | 75 | 84 | 84 | 84 | 84 | 84
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
N-1 Capacity for Embedded Generation (MVA) | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## WED
Zone Summary Information and Peak Load Forecast
Substation | WED - West End (110/11kV) | [5 empty] | Supply | RLA - ROCKLEA 110 CP
Description | Land area is 1730 sqm, Construction is conventional all indoor class
Transformer size is 2x45/60MVA ODAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 2.8 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.4% W 0.3%, 2025 S -1.5% W 0.4%,2026 S -0.9% W -0.2%2027 S -1.4% W -0.2
Load Category | Industrial
Localities | Supplies Highgate Hill, South Brisbane, West End
|  |  |  | Latest Peak Compensated Load |  |  |  | 70 MVA on 17/03/2023 at 15:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 73.9 | 72.7 | 72.1 | 71 | 70.8 | 46.3 | 46.4 | 46.6 | 46.5 | 46.5
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.996 | 0.996 | 0.996 | 0.996 | 0.996
ECC Rating (MVA) | 69 | 69 | 69 | 69 | 69 | 78 | 78 | 78 | 78 | 78
50 PoE Load (MVA) | 71.7 | 70.6 | 69.9 | 68.9 | 68.7 | 44.8 | 44.9 | 45.1 | 45 | 45
50 PoE Load > 95% (MVA) | 3.6 | 3.5 | 3.5 | 3.4 | 3.4 | 2.2 | 2.2 | 2.3 | 2.3 | 2.3
Hours PA > 95% Peak Load | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17
Raw LAR (MVA) | SUMMER 2023/24: 2.7; SUMMER 2024/25: 1.6; SUMMER 2025/26: 0.9
2HR Rating (MVA) | 75 | 75 | 75 | 75 | 75 | 84 | 84 | 84 | 84 | 84
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO
Capacity for Embedded Generation (MVA) | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
N-1 Capacity for Embedded Generation (MVA) | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## WMD
Zone Summary Information and Peak Load Forecast
Substation | WMD - West Maroochydore (132/11kV) | [5 empty] | Supply | PWD - PALMWOODS 132 CP
Description | Land area is 11850 sqm, Construction is conventional indoor/outdoor class
Transformer size is 1x15/30MVA ONAN/ODAF;1x30/48/60MVA ONAN/ODAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 4.0% W 0.0%, 2025 S -0.6% W -0.1%2026 S 0.1% W -0.5%,2027 S -0.9% W -0.7
Load Category | Mixed Domestic
Localities | Supplies Bli Bli, Buderim, Diddillibah, Forest Glen, Kiels Mountain, Kuluin, Kunda Park, Marcoola, Maroochydore, Mons, Mudjimba, Pacific Paradise, Rosemount, Tanawha, Twin Waters, Woombye
|  |  |  | Latest Peak Compensated Load |  |  |  | 33.9 MVA on 05/07/2022 at 17:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 85.5 | 85.5 | 85.5 | 85.5 | 85.5 | 90.8 | 90.8 | 90.8 | 90.8 | 90.8
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 35.6 | 35.4 | 35.4 | 35.1 | 35.2 | 33 | 33 | 33 | 32.8 | 32.6
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 34.5 | 34.5 | 34.5 | 34.5 | 34.5 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8
50 PoE Load (MVA) | 33.5 | 33.3 | 33.3 | 33 | 33 | 31.2 | 31.2 | 31.1 | 31 | 30.8
50 PoE Load > 95% (MVA) | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.6 | 1.6 | 1.6 | 1.6 | 1.5
Hours PA > 95% Peak Load | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Raw LAR (MVA)
2HR Rating (MVA) | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 42 | 42 | 42 | 42 | 42
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO
Capacity for Embedded Generation (MVA) | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## WSS
Zone Summary Information and Peak Load Forecast
Substation | WSS - Whinstanes (33/11kV) | [5 empty] | Supply | MDH - Meeandah BS
Description | Land area is 3825 sqm, Construction is multiple modular class
Transformer size is 2x15/25MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.1% W -0.2%,2025 S -1.5% W 0.1%,2026 S -0.9% W -0.4%2027 S -1.5% W -0.6
Load Category | Industrial
Localities | Supplies Eagle Farm
|  |  |  | Latest Peak Compensated Load |  |  |  | 9.4 MVA on 31/01/2023 at 13:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Day | Day | Day | Day
NCC Rating (MVA) | 52.4 | 52.4 | 52.4 | 52.4 | 52.4 | 52.4 | 52.4 | 52.4 | 52.4 | 52.4
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 10 | 9.8 | 9.7 | 9.6 | 9.5 | 8.1 | 8.1 | 8.1 | 8.1 | 8
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.944 | 0.944 | 0.944 | 0.944 | 0.944 | 0.952 | 0.952 | 0.952 | 0.952 | 0.952
ECC Rating (MVA) | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 32.2 | 32.2 | 32.2 | 32.2 | 32.2
50 PoE Load (MVA) | 9.6 | 9.4 | 9.3 | 9.2 | 9.1 | 7.7 | 7.7 | 7.7 | 7.7 | 7.6
50 PoE Load > 95% (MVA) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Hours PA > 95% Peak Load | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Raw LAR (MVA)
2HR Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## WSE
Zone Summary Information and Peak Load Forecast
Substation | WSE - Whiteside (33/11kV) | [5 empty] | Supply | BRD - Brendale BS
Description | Construction is single modular class
Transformer size is 1x10/15MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.3% W -0.9%,2025 S -2.7% W -1.1%2026 S -1.9% W -1.4%2027 S -2.3% W -1.4
Load Category | Mixed Domestic
Localities | Supplies Dayboro, King Scrub, Laceys Creek, Rush Creek, Whiteside
|  |  |  | Latest Peak Compensated Load |  |  |  | 9.2 MVA on 13/02/2023 at 16:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 9.6 | 9.3 | 9.2 | 8.9 | 8.8 | 9.2 | 9.1 | 9.1 | 8.9 | 8.8
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.955 | 0.955 | 0.955 | 0.955 | 0.955 | 0.974 | 0.974 | 0.974 | 0.974 | 0.974
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 8.8 | 8.6 | 8.4 | 8.2 | 8.1 | 8 | 7.9 | 7.8 | 7.7 | 7.6
50 PoE Load > 95% (MVA) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Hours PA > 95% Peak Load | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
Raw LAR (MVA) | 8.8 | 8.6 | 8.4 | 8.2 | 8.1 | 8 | 7.9 | 7.8 | 7.7 | 7.6
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4
Mobile Plant Avail (MVA) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA) | SUMMER 2023/24: 0.4; SUMMER 2024/25: 0.2
LARc (MW) | SUMMER 2023/24: 0.4; SUMMER 2024/25: 0.2
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## WHO
Zone Summary Information and Peak Load Forecast
Substation | WHO - Wivenhoe (33/11kV) | [5 empty] | Supply | LRE - Lockrose BS
Description | Land area is 7221 sqm, Construction is pipework and shed class
Transformer size is 1x5/6.5MVA ONAN/ONAF;1x5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 4.0% W 1.1%, 2025 S -0.8% W 1.1%,2026 S -0.2% W 0.5%,2027 S -0.8% W 0.3%
Load Category | Domestic
Localities | Supplies Bryden, Dundas, England Creek, Fairney View, Fernvale, Lake Wivenhoe, Split Yard Creek, Vernor, Wivenhoe Pocket
|  |  |  | Latest Peak Compensated Load |  |  |  | 6.3 MVA on 12/02/2023 at 18:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Day | Night | Day | Day | Night
NCC Rating (MVA) | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 7.1 | 7 | 7 | 6.9 | 6.9 | 4.7 | 4.8 | 4.8 | 4.8 | 4.9
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.994 | 0.994 | 0.994 | 0.994 | 0.994 | 0.992 | 0.996 | 0.992 | 0.992 | 0.996
ECC Rating (MVA) | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
50 PoE Load (MVA) | 6.5 | 6.4 | 6.4 | 6.4 | 6.4 | 4.5 | 4.6 | 4.6 | 4.6 | 4.7
50 PoE Load > 95% (MVA) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hours PA > 95% Peak Load | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Raw LAR (MVA)
2HR Rating (MVA) | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 8 | 8 | 8 | 8 | 8
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8
Mobile Plant Avail (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
N-1 Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## WFD
Zone Summary Information and Peak Load Forecast
Substation | WFD - Woodford (33/11kV) | [5 empty] | Supply | BWH - Beerwah BS
Description | Land area is 14570 sqm, Construction is pipework and shed class
Transformer size is 1x15MVA ONAF;1x5/6.0MVA ONAN/ONAF(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.4% W -0.9%,2025 S -1.5% W -1.4%2026 S -0.8% W -0.4%2027 S -1.4% W -0.5
Load Category | Domestic
Localities | Supplies Bellthorpe, Booroobin, Bracalba, Campbells Pocket, Cedarton, Commissioners Flat, D'aguilar, Delaneys Creek, Mount Byron, Mount Delaney, Mount Mee, Mount Pleasant, Ocean View, Peachester, Rocksberg, Stanmore, Stony Creek, Wamuran, Wamuran Basin, Woodford
|  |  |  | Latest Peak Compensated Load |  |  |  | 10.4 MVA on 12/02/2023 at 17:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 11.1 | 10.9 | 10.8 | 10.6 | 10.6 | 9.2 | 9.1 | 9 | 8.9 | 8.9
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 10.6 | 10.4 | 10.4 | 10.2 | 10.2 | 8.4 | 8.4 | 8.3 | 8.2 | 8.2
50 PoE Load > 95% (MVA) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Hours PA > 95% Peak Load | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5
Raw LAR (MVA) | 10.6 | 10.4 | 10.4 | 10.2 | 10.2 | 8.4 | 8.4 | 8.3 | 8.2 | 8.2
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 15 | 15 | 15 | 15 | 15 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4
Mobile Plant Avail (MVA) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
N-1 Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## WRG
Zone Summary Information and Peak Load Forecast
Substation | WRG - Woodridge (33/11kV) | [5 empty] | Supply | LGL - Loganlea BS
Description | Land area is 8190 sqm, Construction is conventional indoor/outdoor class
Transformer size is 3x15/25MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.4% W 0.3%, 2025 S -1.8% W 0.3%,2026 S -1.1% W -0.3%2027 S -1.6% W -0.3
Load Category | Domestic
Localities | Supplies Daisy Hill, Karawatha, Kingston, Logan Central, Loganlea, Slacks Creek, Springwood, Woodridge
|  |  |  | Latest Peak Compensated Load |  |  |  | 34.8 MVA on 03/02/2023 at 13:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Day | Day | Day | Day
NCC Rating (MVA) | 85.4 | 85.4 | 85.4 | 85.4 | 85.4 | 89.6 | 89.6 | 89.6 | 89.6 | 89.6
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 36.1 | 35.5 | 35.1 | 34.5 | 34.4 | 30.4 | 30.5 | 30.6 | 30.5 | 30.4
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 1 | 1 | 1 | 1 | 1 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
ECC Rating (MVA) | 62 | 62 | 62 | 62 | 62 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5
50 PoE Load (MVA) | 33.2 | 32.6 | 32.3 | 32.2 | 32 | 27.1 | 27.2 | 27.3 | 27.2 | 27.1
50 PoE Load > 95% (MVA) | 1.7 | 1.6 | 1.6 | 1.6 | 1.6 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
Hours PA > 95% Peak Load | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
Raw LAR (MVA)
2HR Rating (MVA) | 67 | 67 | 67 | 67 | 67 | 74.4 | 74.4 | 74.4 | 74.4 | 74.4
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO
Capacity for Embedded Generation (MVA) | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
N-1 Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## WNM
Zone Summary Information and Peak Load Forecast
Substation | WNM - Wynnum (33/11kV) | [5 empty] | Supply | LBS - Lytton BS
Description | Land area is 1130 sqm, Construction is conventional all indoor class
Transformer size is 2x14.5/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.9% W 0.5%, 2025 S -0.9% W 0.6%,2026 S -0.2% W 0.0%,2027 S -1.0% W -0.3
Load Category | Domestic
Localities | Supplies Hemmant, Lytton, Manly, Port Of Brisbane, Wynnum, Wynnum West
|  |  |  | Latest Peak Compensated Load |  |  |  | 22.6 MVA on 03/02/2023 at 19:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 58.7 | 58.7 | 58.7 | 58.7 | 58.7 | 58.7 | 58.7 | 58.7 | 58.7 | 58.7
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 23.5 | 23.3 | 23.3 | 23.1 | 23 | 21.3 | 21.4 | 21.5 | 21.5 | 21.5
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.992 | 0.992 | 0.992 | 0.992 | 0.992 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
ECC Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
50 PoE Load (MVA) | 22.6 | 22.4 | 22.4 | 22.1 | 22.1 | 19.5 | 19.6 | 19.7 | 19.7 | 19.6
50 PoE Load > 95% (MVA) | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1 | 1 | 1 | 1 | 1
Hours PA > 95% Peak Load | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5
Raw LAR (MVA)
2HR Rating (MVA) | 33.8 | 33.8 | 33.8 | 33.8 | 33.8 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
N-1 Capacity for Embedded Generation (MVA) | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## YMT
Zone Summary Information and Peak Load Forecast
Substation | YMT - Yamanto (33/11kV) | [5 empty] | Supply | RVW - Raceview BS
Description | Construction is single modular class
Transformer size is 1x15/25MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 5.5% W 2.9%, 2025 S 0.9% W 2.7%, 2026 S 1.4% W 3.2%, 2027 S 0.5% W 2.6%
Load Category | Domestic
Localities | Supplies Deebing Heights, Purga, Yamanto
|  |  |  | Latest Peak Compensated Load |  |  |  | 13.6 MVA on 12/02/2023 at 17:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 15 | 15.8 | 16 | 16.1 | 16.3 | 9.4 | 10.2 | 10.5 | 10.8 | 11.1
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.996 | 0.996 | 0.996 | 0.996 | 0.996 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 13.5 | 14.3 | 14.5 | 14.6 | 14.8 | 9 | 9.8 | 10 | 10.3 | 10.6
50 PoE Load > 95% (MVA) | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hours PA > 95% Peak Load | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Raw LAR (MVA) | 13.5 | 14.3 | 14.5 | 14.6 | 14.8 | 9 | 9.8 | 10 | 10.3 | 10.6
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4
Manual Trans Avail (MVA) | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6
Mobile Plant Avail (MVA) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## YDA
Zone Summary Information and Peak Load Forecast
Substation | YDA - Yandina (33/11kV) | [5 empty] | Supply | NBR - Nambour BS
Description | Land area is 4040 sqm, Construction is single modular class
Transformer size is 1x15MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 3.4 MVA
Growth Rates | 2023 W 1.0%, 2024 S 4.2% W 1.0%, 2025 S -0.7% W 1.0%,2026 S 0.2% W 0.4%, 2027 S -0.9% W -0.3
Load Category | Mixed Industrial
Localities | Supplies Bridges, Cooloolabin, Eerwah Vale, Eumundi, Maroochy River, Ninderry, North Arm, Yandina
|  |  |  | Latest Peak Compensated Load |  |  |  | 10.5 MVA on 13/02/2023 at 18:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 11.1 | 11.5 | 11.6 | 11.5 | 11.5 | 10.2 | 10.7 | 10.8 | 10.9 | 10.8
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 9.9 | 10.3 | 10.4 | 10.3 | 10.3 | 9 | 9.5 | 9.6 | 9.6 | 9.6
50 PoE Load > 95% (MVA) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hours PA > 95% Peak Load | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Raw LAR (MVA) | 9.9 | 10.3 | 10.4 | 10.3 | 10.3 | 9 | 9.5 | 9.6 | 9.6 | 9.6
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
Mobile Plant Avail (MVA) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## YTA
Zone Summary Information and Peak Load Forecast
Substation | YTA - Yatala (110/11kV) | [5 empty] | Supply | LGH - LOGANLEA 110 CP
Description | Land area is 45120 sqm, Construction is a mixture of various construction classes
Transformer size is 2x15/25MVA ONAN/ONAF(Standby);1x30/60MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 2.1% W -0.7%,2025 S -3.0% W -0.1%2026 S -2.4% W -0.7%2027 S -1.9% W -0.8
Load Category | Mixed Industrial
Localities | Supplies Gilberton, Jacobs Well, Kingsholme, Luscombe, Mount Warren Park, Ormeau, Ormeau Hills, Pimpama, Stapylton, Willow Vale, Windaroo, Woongoolba, Yatala
|  |  |  | Latest Peak Compensated Load |  |  |  | 55.1 MVA on 15/03/2023 at 15:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Day | Day | Day | Day
NCC Rating (MVA) | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 63 | 61.2 | 59.7 | 58.7 | 58.3 | 47.9 | 49.9 | 49.9 | 49.5 | 49.1
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.997 | 0.996 | 0.996 | 0.996 | 0.996
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 58.4 | 56.8 | 55.5 | 54.5 | 54.1 | 46.5 | 48.5 | 48.4 | 48.1 | 47.7
50 PoE Load > 95% (MVA) | 2.9 | 2.8 | 2.8 | 2.7 | 2.7 | 2.3 | 2.4 | 2.4 | 2.4 | 2.4
Hours PA > 95% Peak Load | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Raw LAR (MVA) | 58.4 | 56.8 | 55.5 | 54.5 | 54.1 | 46.5 | 48.5 | 48.4 | 48.1 | 47.7
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 57.5 | 57.5 | 57.5 | 57.5 | 57.5 | 65 | 65 | 65 | 65 | 65
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
N-1 Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## ZMR
Zone Summary Information and Peak Load Forecast
Substation | ZMR - Zillmere (33/11kV) | [5 empty] | Supply | SGT - Sandgate BS
Description | Land area is 2030 sqm, Construction is conventional indoor/outdoor class
Transformer size is 2x15/18.75/25MVA ONAN/ODAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates | 2023 W 1.0%, 2024 S 3.4% W 0.1%, 2025 S -1.5% W 0.2%,2026 S -0.8% W -0.3%2027 S -1.2% W -0.3
Load Category | Domestic
Localities | Supplies Aspley, Boondall, Bridgeman Downs, Carseldine, Chermside, Fitzgibbon, Geebung, Zillmere
|  |  |  | Latest Peak Compensated Load |  |  |  | 37 MVA on 31/01/2023 at 14:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8 | 54.8
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 39.7 | 39.1 | 38.8 | 38.3 | 38.3 | 29.7 | 29.7 | 29.8 | 29.7 | 29.6
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
ECC Rating (MVA) | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5
50 PoE Load (MVA) | 36.1 | 35.6 | 35.3 | 34.9 | 34.9 | 28.3 | 28.4 | 28.4 | 28.3 | 28.3
50 PoE Load > 95% (MVA) | 1.8 | 1.8 | 1.8 | 1.7 | 1.7 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
Hours PA > 95% Peak Load | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
Raw LAR (MVA) | SUMMER 2023/24: 7.3; SUMMER 2024/25: 6.8; SUMMER 2025/26: 6.5; SUMMER 2026/27: 6.1; SUMMER 2027/28: 6.1
2HR Rating (MVA) | 31.3 | 31.3 | 31.3 | 31.3 | 31.3 | 35 | 35 | 35 | 35 | 35
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 24.5 | 24.5 | 24.5 | 24.5 | 24.5 | 24.5 | 24.5 | 24.5 | 24.5 | 24.5
N-1 Capacity for Embedded Generation (MVA) | 12.3 | 12.3 | 12.3 | 12.3 | 12.3 | 12.3 | 12.3 | 12.3 | 12.3 | 12.3
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index