## Notes
Sub-Transmission Feeders Forecasts (Energex Distribution Annual Planning Report 2023-24 to 2027-28)
This workbook provides 5 year forecast capacity and DER loading information for sub-transmission feeders in the Energex network.
Energex Distribution Annual Planning Report is prepared and made available solely for information purposes. While care was taken in the preparation of the information in this report, and it is provided in good faith, Energex accepts no responsibility or liability (including without limitation, liability to any person by reason of negligence or negligent mis-statement) for any loss or damage that may be incurred by any person acting in reliance on this information or assumptions drawn from it, except to the extent that liability under any applicable Queensland or Commonwealth of Australia statute cannot be excluded.
It contains assumptions regarding, among other things, economic growth and load forecasts which may or may not prove to be correct. The forecasts included in the document involve subjective judgements and analysis which are subject to significant uncertainties and contingencies, many of which are out of the control of Energex. Furthermore, forecasted data is subject to ongoing variation as new information becomes available. Energex makes no representation or warranty as to the accuracy, reliability, completeness or suitability for any particular purpose of the information in this document. All information should be independently investigated, reviewed, analysed and verified, and must not be relied upon in connection with any investment proposal or decision.
The following sections list the 33kV feeders, their forecast DER loads and power factor. The feeder loads are calculated from load flow results using forecast substation demands. For the transmission and sub-transmission feeders, load flow studies are conducted for system normal and single contingency situations.
The forecast and capacity accounts for committed projects, the project cut-off date for the winter season is 1 June of each year, and for the summer season is 1 December of each year. For example, 2024 winter forecast includes all committed projects with a proposed commissioning date up to 1 June 2024, and the 2023/24 summer forecast includes all committed projects with a proposed commissioning date up to 1 December 2023. The committed status of projects used in the forecast are taken as of 1 May 2023.
Assessment of 33kV feeders is performed at midday of the forecast minimum load day.
Feeder capacities are shown for ECC and NCC. These ratings have also been adjusted for known committed projects. All load transfers associated with contingent condition include acceptable feeder voltage profiles.
Although the conductor rating is generally the limiting factor for feeder capacity, there are other significant items of plant, such as the feeder circuit breaker, that can also restrict capacity. Furthermore, other factors such as voltage constraints and load sharing between parallel underground feeders can sometimes de‑rate the capacity of the feeders due to thermal characteristic constraints. Each of these factors has been taken into account in the production of the forecast tables.
Interconnected feeders that supply multiple customers are examined in the following tables. Feeders exclusively supplying a customer owned substation or dedicated to a customer are not included in these tables.
A definition of terms is shown in the table below.
Definition of Terms Feeder Capacity and Forecast Tables
Term | Definition
NCC Rating (A) | Normal Cyclic Capacity - the total capacity with all network components and equipment intact. This is the maximum permissible peak daily loading for a given load cycle that a feeder can supply each day of its life. For overhead feeders, the NCC is the conductor rating with an assumed 1m/s wind, orthogonal to the line. For underground cables, the NCC assumes that there are sufficient temperature and current operating margins from the thermal inertia of the cable and its surroundings.
DER Forecast under System Normal (A) | Forecast load at midday of the forecast minimum load day, including the impacts of distributed energy resources (DER), under System Normal conditions.
Power Factor | Lowest power factor along the feeder at the above condition. Where the Power Factor is 0, the feeder is a normally open feeder that does not have load under System Normal conditions.
ECC Rating (A) | Emergency Cyclic Capacity – the long term firm delivery capacity under single contingency conditions. Some underground cables are installed in close proximity to other circuits and are normally de‑rated to allow for the heat generated by the adjacent cables. ECC is the higher capacity available when any adjacent circuits have been unloaded. For overhead conductors which do not benefit from this phenomenon, the ECC is synonymous with the NCC.
DER Forecast under N-1 Contingency (A) | Forecast load at midday of the forecast minimum load day, including the impacts of distributed energy resources (DER), under N-1 contingency conditions.

## 33kV Feeders-DER Minimum Demand
Bulk Supply Name | Feeder | From Substation | To Substation | Attributes | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28
Abermain Bulk | 357-1 | Abermain BS | 357 Tee1 | NCC Rating (A) | 505 | 505 | 505 | 505 | 505
|  |  |  | DER Forecast under System Normal (A) | 54 | 67 | 78 | 88 | 97
|  |  |  | Power Factor | 0.99924 | 0.99996 | 0.99981 | 0.99937 | 0.9988
|  |  |  | ECC Rating (A) | 505 | 505 | 505 | 505 | 505
|  |  |  | DER Forecast under N-1 Contingency (A) | 125 | 156 | 182 | 205 | 227
Abermain Bulk | 357-2 | 357 Tee1 | Redbank | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under System Normal (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 3.128e-06 | 3.1282e-06 | 3.128e-06 | 3.1281e-06 | 3.1281e-06
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under N-1 Contingency (A) | 0 | 0 | 0 | 0 | 0
Abermain Bulk | 357-3 | 357 Tee1 | Moggill | NCC Rating (A) | 710 | 710 | 710 | 710 | 710
|  |  |  | DER Forecast under System Normal (A) | 54 | 67 | 78 | 88 | 98
|  |  |  | Power Factor | 0.99886 | 0.99854 | 0.99819 | 0.99783 | 0.99747
|  |  |  | ECC Rating (A) | 710 | 710 | 710 | 710 | 710
|  |  |  | DER Forecast under N-1 Contingency (A) | 125 | 156 | 182 | 205 | 227
Abermain Bulk | 358-1 | Abermain BS | Ebbw Vale | NCC Rating (A) | 473 | 473 | 473 | 473 | 473
|  |  |  | DER Forecast under System Normal (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 7.0417e-06 | 7.0412e-06 | 7.0412e-06 | 7.0414e-06 | 7.0416e-06
|  |  |  | ECC Rating (A) | 473 | 473 | 473 | 473 | 473
|  |  |  | DER Forecast under N-1 Contingency (A) | 1 | 1 | 1 | 1 | 1
Abermain Bulk | 364-1 | Marburg | Rosewood | NCC Rating (A) | 155 | 155 | 155 | 155 | 155
|  |  |  | DER Forecast under System Normal (A) | 20 | 12 | 3 | 7 | 20
|  |  |  | Power Factor | 0.97122 | 0.96933 | 0.96259 | 0.96959 | 0.96308
|  |  |  | ECC Rating (A) | 155 | 155 | 155 | 155 | 155
|  |  |  | DER Forecast under N-1 Contingency (A) | 42 | 69 | 98 | 131 | 169
Abermain Bulk | 365-1 | Abermain BS | 365 Tee1 | NCC Rating (A) | 746 | 746 | 746 | 746 | 746
|  |  |  | DER Forecast under System Normal (A) | 68 | 51 | 33 | 15 | 5
|  |  |  | Power Factor | 0.99986 | 0.99951 | 0.99897 | 0.99867 | 0.97183
|  |  |  | ECC Rating (A) | 746 | 746 | 746 | 746 | 746
|  |  |  | DER Forecast under N-1 Contingency (A) | 132 | 98 | 84 | 78 | 73
Abermain Bulk | 365-2 | 365 Tee1 | 366 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under System Normal (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 2.0188e-05 | 2.0191e-05 | 2.0193e-05 | 2.019e-05 | 2.019e-05
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under N-1 Contingency (A) | 0 | 0 | 0 | 0 | 0
Abermain Bulk | 365-3 | 365 Tee1 | Karrabin | NCC Rating (A) | 804 | 804 | 804 | 804 | 804
|  |  |  | DER Forecast under System Normal (A) | 68 | 51 | 33 | 15 | 5
|  |  |  | Power Factor | 0.99982 | 0.99963 | 0.99954 | 0.99937 | 0.88558
|  |  |  | ECC Rating (A) | 804 | 804 | 804 | 804 | 804
|  |  |  | DER Forecast under N-1 Contingency (A) | 132 | 98 | 84 | 78 | 73
Abermain Bulk | 366-1 | Abermain BS | 366 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under System Normal (A) | 74 | 55 | 36 | 17 | 5
|  |  |  | Power Factor | 0.99979 | 0.99952 | 0.99902 | 0.99882 | 0.94452
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under N-1 Contingency (A) | 133 | 99 | 92 | 86 | 79
Abermain Bulk | 366-2 | 366 Tee1 | Karrabin | NCC Rating (A) | 758 | 758 | 758 | 758 | 758
|  |  |  | DER Forecast under System Normal (A) | 74 | 55 | 36 | 17 | 5
|  |  |  | Power Factor | 0.99979 | 0.99958 | 0.99947 | 0.99994 | 0.92687
|  |  |  | ECC Rating (A) | 758 | 758 | 758 | 758 | 758
|  |  |  | DER Forecast under N-1 Contingency (A) | 133 | 99 | 92 | 86 | 79
Abermain Bulk | 366-3 | 366 Tee1 | 365 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under System Normal (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 9.0313e-06 | 9.0313e-06 | 9.0318e-06 | 9.0318e-06 | 9.0317e-06
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under N-1 Contingency (A) | 0 | 0 | 0 | 0 | 0
Abermain Bulk | 367-1 | Abermain BS | Mt Crosby West | NCC Rating (A) | 530 | 530 | 530 | 530 | 530
|  |  |  | DER Forecast under System Normal (A) | 47 | 59 | 45 | 35 | 26
|  |  |  | Power Factor | 0.99897 | 0.99897 | 0.99085 | 0.9815 | 0.95831
|  |  |  | ECC Rating (A) | 530 | 530 | 530 | 530 | 530
|  |  |  | DER Forecast under N-1 Contingency (A) | 80 | 99 | 117 | 133 | 149
Abermain Bulk | 368-1 | Abermain BS | Mt Crosby | NCC Rating (A) | 529 | 529 | 529 | 529 | 529
|  |  |  | DER Forecast under System Normal (A) | 0 | 0 | 62 | 56 | 50
|  |  |  | Power Factor | 0 | 0 | 0.98905 | 0.98492 | 0.9789
|  |  |  | ECC Rating (A) | 529 | 529 | 529 | 529 | 529
|  |  |  | DER Forecast under N-1 Contingency (A) | 0 | 0 | 225 | 225 | 225
Abermain Bulk | 369-1 | Abermain BS | Nth Ipswich | NCC Rating (A) | 499 | 499 | 499 | 499 | 499
|  |  |  | DER Forecast under System Normal (A) | 17 | 12 | 8 | 5 | 3
|  |  |  | Power Factor | 0.99821 | 0.99711 | 0.99462 | 0.98693 | 0.95062
|  |  |  | ECC Rating (A) | 499 | 499 | 499 | 499 | 499
|  |  |  | DER Forecast under N-1 Contingency (A) | 34 | 24 | 17 | 11 | 5
Abermain Bulk | 370-1 | Abermain BS | Nth Ipswich | NCC Rating (A) | 499 | 499 | 499 | 499 | 499
|  |  |  | DER Forecast under System Normal (A) | 17 | 12 | 9 | 5 | 3
|  |  |  | Power Factor | 0.99839 | 0.99731 | 0.99484 | 0.98711 | 0.95017
|  |  |  | ECC Rating (A) | 499 | 499 | 499 | 499 | 499
|  |  |  | DER Forecast under N-1 Contingency (A) | 34 | 24 | 17 | 11 | 5
Abermain Bulk | 387-1 | Abermain BS | Marburg | NCC Rating (A) | 290 | 290 | 290 | 290 | 290
|  |  |  | DER Forecast under System Normal (A) | 8 | 22 | 39 | 57 | 77
|  |  |  | Power Factor | 0.74251 | 0.99226 | 0.99984 | 0.99759 | 0.99401
|  |  |  | ECC Rating (A) | 290 | 290 | 290 | 290 | 290
|  |  |  | DER Forecast under N-1 Contingency (A) | 67 | 102 | 140 | 180 | 224
Abermain Bulk | 3901-1 | Karrabin | Amberley | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under System Normal (A) | 80 | 68 | 55 | 41 | 26
|  |  |  | Power Factor | 0.99996 | 0.99993 | 0.99996 | 0.99994 | 0.99624
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under N-1 Contingency (A) | 154 | 130 | 109 | 108 | 107
Abermain Bulk | 420-1 | Mt Crosby West | Mt Crosby | NCC Rating (A) | 349 | 349 | 349 | 349 | 349
|  |  |  | DER Forecast under System Normal (A) | 0 | 0 | 162 | 168 | 174
|  |  |  | Power Factor | 0 | 0 | 0.99982 | 0.99988 | 0.99993
|  |  |  | ECC Rating (A) | 349 | 349 | 349 | 349 | 349
|  |  |  | DER Forecast under N-1 Contingency (A) | 0 | 0 | 225 | 224 | 224
Abermain Bulk | 436-1 | Amberley | 436 Tee1 | NCC Rating (A) | 351 | 351 | 351 | 351 | 351
|  |  |  | DER Forecast under System Normal (A) | 63 | 83 | 106 | 131 | 160
|  |  |  | Power Factor | 0.99652 | 0.99799 | 0.9983 | 0.99809 | 0.99732
|  |  |  | ECC Rating (A) | 351 | 351 | 351 | 351 | 351
|  |  |  | DER Forecast under N-1 Contingency (A) | 74 | 105 | 144 | 186 | 234
Abermain Bulk | 436-4 | 436 Tee1 | Rosewood | NCC Rating (A) | 208 | 208 | 208 | 208 | 208
|  |  |  | DER Forecast under System Normal (A) | 63 | 83 | 106 | 131 | 160
|  |  |  | Power Factor | 0.99648 | 0.9983 | 0.99884 | 0.99891 | 0.99861
|  |  |  | ECC Rating (A) | 208 | 208 | 208 | 208 | 208
|  |  |  | DER Forecast under N-1 Contingency (A) | 74 | 105 | 144 | 186 | 234
Abermain Bulk | 445-1 | Abermain BS | Moggill | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under System Normal (A) | 73 | 91 | 106 | 120 | 132
|  |  |  | Power Factor | 0.99957 | 0.99993 | 0.99999 | 0.99988 | 0.9997
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under N-1 Contingency (A) | 126 | 157 | 183 | 207 | 228
Abermain Bulk | 475-1 | Karrabin | Amberley | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under System Normal (A) | 79 | 67 | 54 | 41 | 26
|  |  |  | Power Factor | 0.99993 | 0.99989 | 0.99993 | 0.99997 | 0.99646
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under N-1 Contingency (A) | 153 | 130 | 108 | 106 | 105
Abermain Bulk | 673-1 | Moggill | Kenmore | NCC Rating (A) | 636 | 636 | 636 | 636 | 636
|  |  |  | DER Forecast under System Normal (A) | 4 | 4 | 4 | 4 | 4
|  |  |  | Power Factor | 4.7649e-05 | 4.7649e-05 | 4.7649e-05 | 4.7649e-05 | 4.7649e-05
|  |  |  | ECC Rating (A) | 636 | 636 | 636 | 636 | 636
|  |  |  | DER Forecast under N-1 Contingency (A) | 4 | 4 | 4 | 4 | 4
Algester Bulk | 3400-1 | Algester BS | Calamvale | NCC Rating (A) | 694 | 694 | 694 | 694 | 694
|  |  |  | DER Forecast under System Normal (A) | 83 | 89 | 93 | 97 | 100
|  |  |  | Power Factor | 0.99911 | 0.99899 | 0.99888 | 0.99879 | 0.99872
|  |  |  | ECC Rating (A) | 694 | 694 | 694 | 694 | 694
|  |  |  | DER Forecast under N-1 Contingency (A) | 165 | 177 | 187 | 194 | 200
Algester Bulk | 3402-1 | Algester BS | Acacia Ridge | NCC Rating (A) | 687 | 687 | 687 | 687 | 687
|  |  |  | DER Forecast under System Normal (A) | 6 | 5 | 4 | 5 | 5
|  |  |  | Power Factor | 0.62364 | 0.34053 | 0.0059197 | 0.27869 | 0.44897
|  |  |  | ECC Rating (A) | 687 | 687 | 687 | 687 | 687
|  |  |  | DER Forecast under N-1 Contingency (A) | 8 | 5 | 4 | 5 | 6
Algester Bulk | 3403-1 | Algester BS | Acacia Ridge | NCC Rating (A) | 687 | 687 | 687 | 687 | 687
|  |  |  | DER Forecast under System Normal (A) | 6 | 5 | 4 | 5 | 5
|  |  |  | Power Factor | 0.62492 | 0.34154 | 0.0059436 | 0.27955 | 0.45017
|  |  |  | ECC Rating (A) | 687 | 687 | 687 | 687 | 687
|  |  |  | DER Forecast under N-1 Contingency (A) | 8 | 5 | 4 | 5 | 6
Algester Bulk | 3405-1 | Algester BS | Calamvale | NCC Rating (A) | 694 | 694 | 694 | 694 | 694
|  |  |  | DER Forecast under System Normal (A) | 83 | 89 | 93 | 97 | 100
|  |  |  | Power Factor | 0.99912 | 0.99899 | 0.99889 | 0.99879 | 0.99872
|  |  |  | ECC Rating (A) | 694 | 694 | 694 | 694 | 694
|  |  |  | DER Forecast under N-1 Contingency (A) | 165 | 177 | 187 | 194 | 200
Archerfield Bulk | 597-1 | Rocklea | Salisbury | NCC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | DER Forecast under System Normal (A) | 38 | 58 | 76 | 94 | 111
|  |  |  | Power Factor | 0.99744 | 0.99952 | 0.99928 | 0.9989 | 0.99846
|  |  |  | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | DER Forecast under N-1 Contingency (A) | 38 | 58 | 76 | 94 | 111
Archerfield Bulk | 635-1 | Archerfield BS | Coopers Plains | NCC Rating (A) | 523 | 523 | 523 | 523 | 523
|  |  |  | DER Forecast under System Normal (A) | 35 | 28 | 13 | 2 | 15
|  |  |  | Power Factor | 0.9999 | 0.99975 | 0.9978 | 0.9019 | 0.99856
|  |  |  | ECC Rating (A) | 523 | 523 | 523 | 523 | 523
|  |  |  | DER Forecast under N-1 Contingency (A) | 35 | 28 | 13 | 2 | 15
Archerfield Bulk | 650-1 | Archerfield BS | Rocklea | NCC Rating (A) | 650 | 650 | 650 | 650 | 650
|  |  |  | DER Forecast under System Normal (A) | 29 | 53 | 78 | 102 | 126
|  |  |  | Power Factor | 0.97217 | 0.99369 | 0.99806 | 0.99947 | 0.99958
|  |  |  | ECC Rating (A) | 650 | 650 | 650 | 650 | 650
|  |  |  | DER Forecast under N-1 Contingency (A) | 56 | 106 | 154 | 202 | 251
Archerfield Bulk | 651-1 | Archerfield BS | Rocklea | NCC Rating (A) | 650 | 650 | 650 | 650 | 650
|  |  |  | DER Forecast under System Normal (A) | 28 | 53 | 77 | 101 | 125
|  |  |  | Power Factor | 0.97168 | 0.99357 | 0.99801 | 0.99945 | 0.99957
|  |  |  | ECC Rating (A) | 650 | 650 | 650 | 650 | 650
|  |  |  | DER Forecast under N-1 Contingency (A) | 56 | 106 | 154 | 202 | 251
Ashgrove West Bulk | 432-1 | Ashgrove West BS | Toowong | NCC Rating (A) | 476 | 476 | 476 | 476 | 476
|  |  |  | DER Forecast under System Normal (A) | 14 | 14 | 14 | 14 | 14
|  |  |  | Power Factor | 4.2657e-05 | 4.2657e-05 | 4.2657e-05 | 4.2657e-05 | 4.2657e-05
|  |  |  | ECC Rating (A) | 476 | 476 | 476 | 476 | 476
|  |  |  | DER Forecast under N-1 Contingency (A) | 14 | 14 | 14 | 14 | 14
Ashgrove West Bulk | 552-1 | Ashgrove West BS | Ashgrove | NCC Rating (A) | 598 | 598 | 598 | 598 | 598
|  |  |  | DER Forecast under System Normal (A) | 33 | 45 | 58 | 70 | 81
|  |  |  | Power Factor | 0.74668 | 0.8883 | 0.94207 | 0.96683 | 0.98019
|  |  |  | ECC Rating (A) | 598 | 598 | 598 | 598 | 598
|  |  |  | DER Forecast under N-1 Contingency (A) | 50 | 70 | 90 | 109 | 128
Ashgrove West Bulk | 565-1 | Ashgrove West BS | Ashgrove | NCC Rating (A) | 851 | 851 | 851 | 851 | 851
|  |  |  | DER Forecast under System Normal (A) | 24 | 32 | 41 | 49 | 57
|  |  |  | Power Factor | 0.62989 | 0.80182 | 0.87631 | 0.91465 | 0.93766
|  |  |  | ECC Rating (A) | 851 | 851 | 851 | 851 | 851
|  |  |  | DER Forecast under N-1 Contingency (A) | 36 | 50 | 63 | 77 | 90
Ashgrove West Bulk | 570-1 | Ashgrove West BS | Ashgrove | NCC Rating (A) | 598 | 598 | 598 | 598 | 598
|  |  |  | DER Forecast under System Normal (A) | 32 | 44 | 56 | 68 | 80
|  |  |  | Power Factor | 0.7446 | 0.88705 | 0.94132 | 0.96634 | 0.97986
|  |  |  | ECC Rating (A) | 598 | 598 | 598 | 598 | 598
|  |  |  | DER Forecast under N-1 Contingency (A) | 50 | 69 | 89 | 108 | 127
Ashgrove West Bulk | 585-1 | Ashgrove West BS | The Gap | NCC Rating (A) | 622 | 622 | 622 | 622 | 622
|  |  |  | DER Forecast under System Normal (A) | 34 | 43 | 50 | 57 | 62
|  |  |  | Power Factor | 0.96765 | 0.98102 | 0.98731 | 0.9908 | 0.99299
|  |  |  | ECC Rating (A) | 622 | 622 | 622 | 622 | 622
|  |  |  | DER Forecast under N-1 Contingency (A) | 34 | 43 | 50 | 57 | 62
Ashgrove West Bulk | 586-1 | Ashgrove West BS | The Gap | NCC Rating (A) | 622 | 622 | 622 | 622 | 622
|  |  |  | DER Forecast under System Normal (A) | 35 | 43 | 50 | 57 | 62
|  |  |  | Power Factor | 0.96773 | 0.98118 | 0.98749 | 0.991 | 0.9932
|  |  |  | ECC Rating (A) | 622 | 622 | 622 | 622 | 622
|  |  |  | DER Forecast under N-1 Contingency (A) | 35 | 43 | 50 | 57 | 62
Ashgrove West Bulk | 590-1 | Ashgrove BS | Toowong | NCC Rating (A) | 705 | 705 | 705 | 705 | 705
|  |  |  | DER Forecast under System Normal (A) | 85 | 67 | 78 | 62 | 45
|  |  |  | Power Factor | 0.99423 | 0.99017 | 0.99294 | 0.98834 | 0.97903
|  |  |  | ECC Rating (A) | 705 | 705 | 705 | 705 | 705
|  |  |  | DER Forecast under N-1 Contingency (A) | 169 | 133 | 155 | 122 | 89
Ashgrove West Bulk | 591-1 | Ashgrove BS | Toowong | NCC Rating (A) | 705 | 705 | 705 | 705 | 705
|  |  |  | DER Forecast under System Normal (A) | 85 | 67 | 78 | 62 | 45
|  |  |  | Power Factor | 0.99425 | 0.9902 | 0.99297 | 0.98838 | 0.97907
|  |  |  | ECC Rating (A) | 705 | 705 | 705 | 705 | 705
|  |  |  | DER Forecast under N-1 Contingency (A) | 169 | 133 | 155 | 122 | 89
Ashgrove West Bulk | 675-1 | Ashgrove | Newmarket | NCC Rating (A) | 492 | 492 | 492 | 492 | 492
|  |  |  | DER Forecast under System Normal (A) | 17 | 17 | 17 | 17 | 17
|  |  |  | Power Factor | 3.5471e-05 | 3.5471e-05 | 3.5471e-05 | 3.5471e-05 | 3.5471e-05
|  |  |  | ECC Rating (A) | 492 | 492 | 492 | 492 | 492
|  |  |  | DER Forecast under N-1 Contingency (A) | 17 | 17 | 17 | 17 | 17
Ashgrove West Bulk | 676-1 | Ashgrove | Newmarket | NCC Rating (A) | 492 | 492 | 492 | 492 | 492
|  |  |  | DER Forecast under System Normal (A) | 17 | 17 | 17 | 17 | 17
|  |  |  | Power Factor | 3.4731e-05 | 3.4731e-05 | 3.4731e-05 | 3.4731e-05 | 3.4731e-05
|  |  |  | ECC Rating (A) | 492 | 492 | 492 | 492 | 492
|  |  |  | DER Forecast under N-1 Contingency (A) | 17 | 17 | 17 | 17 | 17
Beaudesert Bulk | 314-1 | Beaudesert BS | Jimboomba | NCC Rating (A) | 512 | 512 | 512 | 512 | 512
|  |  |  | DER Forecast under System Normal (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 1.6107e-05 | 1.6107e-05 | 1.6107e-05 | 1.6107e-05 | 1.6107e-05
|  |  |  | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
|  |  |  | DER Forecast under N-1 Contingency (A) | 1 | 1 | 1 | 1 | 1
Beaudesert Bulk | 404-1 | Beaudesert | Innisplain | NCC Rating (A) | 155 | 155 | 155 | 155 | 155
|  |  |  | DER Forecast under System Normal (A) | 9 | 11 | 12 | 14 | 15
|  |  |  | Power Factor | 0.98818 | 0.99269 | 0.99501 | 0.99633 | 0.99714
|  |  |  | ECC Rating (A) | 155 | 155 | 155 | 155 | 155
|  |  |  | DER Forecast under N-1 Contingency (A) | 9 | 11 | 12 | 14 | 15
Beaudesert Bulk | 466-1 | Beaudesert BS | Bromelton | NCC Rating (A) | 403 | 403 | 403 | 403 | 403
|  |  |  | DER Forecast under System Normal (A) | 15 | 11 | 7 | 4 | 1
|  |  |  | Power Factor | 0.9985 | 0.99867 | 0.99886 | 0.99917 | 0.9999
|  |  |  | ECC Rating (A) | 403 | 403 | 403 | 403 | 403
|  |  |  | DER Forecast under N-1 Contingency (A) | 25 | 18 | 12 | 7 | 2
Beaudesert Bulk | 467-1 | Beaudesert BS | Bromelton | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under System Normal (A) | 10 | 7 | 5 | 3 | 1
|  |  |  | Power Factor | 0.99237 | 0.98946 | 0.98358 | 0.96679 | 0.84727
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under N-1 Contingency (A) | 25 | 18 | 12 | 7 | 3
Beaudesert Bulk | 468-1 | Beaudesert BS | Beaudesert | NCC Rating (A) | 579 | 579 | 579 | 579 | 579
|  |  |  | DER Forecast under System Normal (A) | 54 | 88 | 122 | 158 | 197
|  |  |  | Power Factor | 0.99853 | 0.99979 | 0.99995 | 0.99927 | 0.99778
|  |  |  | ECC Rating (A) | 579 | 579 | 579 | 579 | 579
|  |  |  | DER Forecast under N-1 Contingency (A) | 72 | 126 | 182 | 243 | 310
Beaudesert Bulk | 469-1 | Beaudesert BS | 469 Tee1 | NCC Rating (A) | 537 | 537 | 537 | 537 | 537
|  |  |  | DER Forecast under System Normal (A) | 56 | 90 | 125 | 162 | 202
|  |  |  | Power Factor | 0.99873 | 0.99632 | 0.99329 | 0.98944 | 0.98481
|  |  |  | ECC Rating (A) | 537 | 537 | 537 | 537 | 537
|  |  |  | DER Forecast under N-1 Contingency (A) | 109 | 177 | 246 | 318 | 395
Beaudesert Bulk | 469-2 | 469 Tee1 | Beaudesert | NCC Rating (A) | 579 | 579 | 579 | 579 | 579
|  |  |  | DER Forecast under System Normal (A) | 19 | 39 | 61 | 86 | 114
|  |  |  | Power Factor | 0.98608 | 0.98536 | 0.98188 | 0.97661 | 0.97047
|  |  |  | ECC Rating (A) | 579 | 579 | 579 | 579 | 579
|  |  |  | DER Forecast under N-1 Contingency (A) | 72 | 125 | 181 | 242 | 308
Beaudesert Bulk | 469-3 | 469 Tee1 | Mt Tamborine Bus 2 | NCC Rating (A) | 512 | 512 | 512 | 512 | 512
|  |  |  | DER Forecast under System Normal (A) | 37 | 51 | 65 | 77 | 88
|  |  |  | Power Factor | 0.99999 | 0.99981 | 0.99932 | 0.99871 | 0.99802
|  |  |  | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
|  |  |  | DER Forecast under N-1 Contingency (A) | 37 | 52 | 65 | 77 | 88
Beenleigh Bulk | 3590-1 | Beenleigh BS | Loganholme | NCC Rating (A) | 766 | 766 | 766 | 766 | 766
|  |  |  | DER Forecast under System Normal (A) | 63 | 108 | 151 | 187 | 214
|  |  |  | Power Factor | 0.99977 | 0.99954 | 0.99923 | 0.99889 | 0.99858
|  |  |  | ECC Rating (A) | 766 | 766 | 766 | 766 | 766
|  |  |  | DER Forecast under N-1 Contingency (A) | 117 | 190 | 259 | 316 | 360
Beenleigh Bulk | 3591-1 | Cornubia | Loganholme | NCC Rating (A) | 807 | 807 | 807 | 807 | 807
|  |  |  | DER Forecast under System Normal (A) | 15 | 2 | 17 | 30 | 39
|  |  |  | Power Factor | 0.99306 | 0.2717 | 0.99479 | 0.99922 | 0.99985
|  |  |  | ECC Rating (A) | 807 | 807 | 807 | 807 | 807
|  |  |  | DER Forecast under N-1 Contingency (A) | 69 | 108 | 166 | 214 | 249
Beenleigh Bulk | 3601-1 | Yatala | Stapylton | NCC Rating (A) | 713 | 713 | 713 | 713 | 713
|  |  |  | DER Forecast under System Normal (A) | 11 | 10 | 10 | 10 | 9
|  |  |  | Power Factor | 0.99805 | 0.99767 | 0.99736 | 0.99711 | 0.99698
|  |  |  | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
|  |  |  | DER Forecast under N-1 Contingency (A) | 23 | 21 | 20 | 19 | 19
Beenleigh Bulk | 3620-1 | Beenleigh BS | Logan Village | NCC Rating (A) | 490 | 490 | 490 | 490 | 490
|  |  |  | DER Forecast under System Normal (A) | 2 | 2 | 2 | 2 | 2
|  |  |  | Power Factor | 0.00018079 | 0.00018079 | 0.00018079 | 0.00018079 | 0.00018079
|  |  |  | ECC Rating (A) | 490 | 490 | 490 | 490 | 490
|  |  |  | DER Forecast under N-1 Contingency (A) | 2 | 2 | 2 | 2 | 2
Beenleigh Bulk | 402-1 | Beenleigh BS | 402 Tee1 | NCC Rating (A) | 579 | 579 | 579 | 579 | 579
|  |  |  | DER Forecast under System Normal (A) | 73 | 90 | 105 | 118 | 131
|  |  |  | Power Factor | 0.99981 | 0.99935 | 0.99879 | 0.99812 | 0.99729
|  |  |  | ECC Rating (A) | 579 | 579 | 579 | 579 | 579
|  |  |  | DER Forecast under N-1 Contingency (A) | 73 | 90 | 105 | 118 | 131
Beenleigh Bulk | 402-2 | 402 Tee1 | Tamborine Village | NCC Rating (A) | 439 | 439 | 439 | 439 | 439
|  |  |  | DER Forecast under System Normal (A) | 28 | 29 | 30 | 31 | 32
|  |  |  | Power Factor | 0.99976 | 0.99974 | 0.99973 | 0.99971 | 0.99969
|  |  |  | ECC Rating (A) | 439 | 439 | 439 | 439 | 439
|  |  |  | DER Forecast under N-1 Contingency (A) | 28 | 29 | 30 | 31 | 32
Beenleigh Bulk | 402-3 | 402 Tee1 | Mt Tamborine Bus 1 | NCC Rating (A) | 812 | 812 | 812 | 812 | 812
|  |  |  | DER Forecast under System Normal (A) | 46 | 61 | 75 | 87 | 99
|  |  |  | Power Factor | 0.99975 | 0.99954 | 0.99916 | 0.99868 | 0.99808
|  |  |  | ECC Rating (A) | 812 | 812 | 812 | 812 | 812
|  |  |  | DER Forecast under N-1 Contingency (A) | 46 | 61 | 75 | 87 | 99
Beenleigh Bulk | 405-1 | Beenleigh BS | 405 Tee1 | NCC Rating (A) | 807 | 807 | 807 | 807 | 807
|  |  |  | DER Forecast under System Normal (A) | 54 | 82 | 109 | 131 | 148
|  |  |  | Power Factor | 0.99995 | 0.99998 | 0.99983 | 0.99958 | 0.99932
|  |  |  | ECC Rating (A) | 807 | 807 | 807 | 807 | 807
|  |  |  | DER Forecast under N-1 Contingency (A) | 117 | 189 | 258 | 315 | 358
Beenleigh Bulk | 405-3 | 405 Tee1 | Cornubia | NCC Rating (A) | 774 | 774 | 774 | 774 | 774
|  |  |  | DER Forecast under System Normal (A) | 54 | 82 | 109 | 131 | 148
|  |  |  | Power Factor | 0.99997 | 0.9999 | 0.99976 | 0.99958 | 0.99939
|  |  |  | ECC Rating (A) | 774 | 774 | 774 | 774 | 774
|  |  |  | DER Forecast under N-1 Contingency (A) | 117 | 189 | 258 | 315 | 358
Beenleigh Bulk | 419-1 | Loganholme | Tanah Merah | NCC Rating (A) | 713 | 713 | 713 | 713 | 713
|  |  |  | DER Forecast under System Normal (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 2.0559e-06 | 2.0559e-06 | 2.0558e-06 | 2.0556e-06 | 2.056e-06
|  |  |  | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
|  |  |  | DER Forecast under N-1 Contingency (A) | 1 | 1 | 1 | 1 | 1
Beenleigh Bulk | 426-1 | Beenleigh BS | Stapylton | NCC Rating (A) | 740 | 740 | 740 | 740 | 740
|  |  |  | DER Forecast under System Normal (A) | 12 | 11 | 11 | 10 | 10
|  |  |  | Power Factor | 0.99744 | 0.99702 | 0.9723 | 0.97024 | 0.96913
|  |  |  | ECC Rating (A) | 740 | 740 | 740 | 740 | 740
|  |  |  | DER Forecast under N-1 Contingency (A) | 23 | 21 | 20 | 20 | 19
Beenleigh Bulk | 427-1 | Beenleigh BS | Yatala | NCC Rating (A) | 740 | 740 | 740 | 740 | 740
|  |  |  | DER Forecast under System Normal (A) | 11 | 11 | 10 | 10 | 10
|  |  |  | Power Factor | 0.98098 | 0.97802 | 0.97554 | 0.97363 | 0.9726
|  |  |  | ECC Rating (A) | 740 | 740 | 740 | 740 | 740
|  |  |  | DER Forecast under N-1 Contingency (A) | 23 | 21 | 20 | 20 | 19
Beenleigh Bulk | 453-1 | Beenleigh BS | Beenleigh Nth | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under System Normal (A) | 215 | 338 | 465 | 597 | 738
|  |  |  | Power Factor | 0.99959 | 0.99849 | 0.99676 | 0.99445 | 0.99135
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under N-1 Contingency (A) | 215 | 338 | 465 | 597 | 738
Beenleigh Bulk | 496-1 | Beenleigh Nth | Bethania | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under System Normal (A) | 141 | 196 | 251 | 305 | 361
|  |  |  | Power Factor | 0.9991 | 0.99821 | 0.99691 | 0.99541 | 0.99352
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under N-1 Contingency (A) | 141 | 196 | 251 | 305 | 361
Beerwah Bulk | 3190-1 | Woodford | Kilcoy | NCC Rating (A) | 0 | 700 | 700 | 700 | 700
|  |  |  | DER Forecast under System Normal (A) | 0 | 29 | 36 | 41 | 44
|  |  |  | Power Factor | 0 | 0.9739 | 0.97946 | 0.98244 | 0.98424
|  |  |  | ECC Rating (A) | 0 | 700 | 700 | 700 | 700
|  |  |  | DER Forecast under N-1 Contingency (A) | 0 | 43 | 52 | 60 | 65
Beerwah Bulk | 324-1 | Woodford | Kilcoy | NCC Rating (A) | 348 | 348 | 348 | 348 | 348
|  |  |  | DER Forecast under System Normal (A) | 30 | 15 | 18 | 21 | 23
|  |  |  | Power Factor | 0.99704 | 0.94358 | 0.94287 | 0.94217 | 0.94159
|  |  |  | ECC Rating (A) | 348 | 348 | 348 | 348 | 348
|  |  |  | DER Forecast under N-1 Contingency (A) | 30 | 15 | 18 | 21 | 23
Beerwah Bulk | 428-1 | Beerwah BS | Woodford | NCC Rating (A) | 351 | 351 | 351 | 351 | 351
|  |  |  | DER Forecast under System Normal (A) | 30 | 43 | 52 | 59 | 64
|  |  |  | Power Factor | 0.99274 | 0.9954 | 0.99828 | 0.99934 | 0.99976
|  |  |  | ECC Rating (A) | 351 | 351 | 351 | 351 | 351
|  |  |  | DER Forecast under N-1 Contingency (A) | 30 | 43 | 52 | 59 | 64
Beerwah Bulk | 447-1 | Somerset Dam | Kilcoy | NCC Rating (A) | 155 | 704 | 704 | 704 | 704
|  |  |  | DER Forecast under System Normal (A) | 1 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0.00023397 | 1 | 1 | 1 | 1
|  |  |  | ECC Rating (A) | 155 | 0 | 0 | 0 | 0
|  |  |  | DER Forecast under N-1 Contingency (A) | 1 | 0 | 0 | 0 | 0
Beerwah Bulk | 477-1 | 477 Tee1 | Maleny | NCC Rating (A) | 155 | 155 | 155 | 155 | 155
|  |  |  | DER Forecast under System Normal (A) | 2 | 2 | 2 | 2 | 2
|  |  |  | Power Factor | 3.5253e-05 | 3.5253e-05 | 3.5253e-05 | 3.5253e-05 | 3.5252e-05
|  |  |  | ECC Rating (A) | 155 | 155 | 155 | 155 | 155
|  |  |  | DER Forecast under N-1 Contingency (A) | 2 | 2 | 2 | 2 | 2
Beerwah Bulk | 477-2 | 477 Tee1 | Woodford | NCC Rating (A) | 330 | 330 | 704 | 704 | 704
|  |  |  | DER Forecast under System Normal (A) | 47 | 65 | 83 | 99 | 114
|  |  |  | Power Factor | 0.99981 | 0.99942 | 0.99905 | 0.99869 | 0.99828
|  |  |  | ECC Rating (A) | 330 | 330 | 704 | 704 | 704
|  |  |  | DER Forecast under N-1 Contingency (A) | 47 | 65 | 83 | 99 | 114
Beerwah Bulk | 477-3 | Beerwah | 477 Tee1 | NCC Rating (A) | 711 | 711 | 711 | 711 | 711
|  |  |  | DER Forecast under System Normal (A) | 47 | 65 | 83 | 99 | 114
|  |  |  | Power Factor | 0.99957 | 0.99995 | 0.99936 | 0.99833 | 0.99702
|  |  |  | ECC Rating (A) | 711 | 711 | 711 | 711 | 711
|  |  |  | DER Forecast under N-1 Contingency (A) | 47 | 65 | 83 | 99 | 114
Beerwah Bulk | 608-1 | Beerwah BS | Landsborough | NCC Rating (A) | 412 | 412 | 412 | 412 | 412
|  |  |  | DER Forecast under System Normal (A) | 67 | 91 | 113 | 132 | 150
|  |  |  | Power Factor | 0.99981 | 0.99931 | 0.99869 | 0.9979 | 0.99712
|  |  |  | ECC Rating (A) | 412 | 412 | 412 | 412 | 412
|  |  |  | DER Forecast under N-1 Contingency (A) | 67 | 91 | 113 | 132 | 150
Belmont Bulk | 527-1 | Mt Gravatt | Upper Mt Gravatt | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under System Normal (A) | 29 | 29 | 29 | 29 | 30
|  |  |  | Power Factor | 0.99855 | 0.99939 | 0.9998 | 0.99995 | 1
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under N-1 Contingency (A) | 42 | 41 | 40 | 40 | 39
Belmont Bulk | 631-1 | Belmont BS | Mt Gravatt | NCC Rating (A) | 420 | 420 | 420 | 420 | 420
|  |  |  | DER Forecast under System Normal (A) | 27 | 26 | 26 | 27 | 28
|  |  |  | Power Factor | 0.16943 | 0.043419 | 0.21959 | 0.33588 | 0.41649
|  |  |  | ECC Rating (A) | 465 | 465 | 465 | 465 | 465
|  |  |  | DER Forecast under N-1 Contingency (A) | 29 | 30 | 32 | 35 | 36
Belmont Bulk | 632-1 | Belmont BS | Mt Gravatt | NCC Rating (A) | 420 | 420 | 420 | 420 | 420
|  |  |  | DER Forecast under System Normal (A) | 27 | 26 | 26 | 27 | 28
|  |  |  | Power Factor | 0.16844 | 0.04319 | 0.21837 | 0.33411 | 0.41443
|  |  |  | ECC Rating (A) | 452 | 452 | 452 | 452 | 452
|  |  |  | DER Forecast under N-1 Contingency (A) | 29 | 30 | 32 | 35 | 36
Belmont Bulk | 647-1 | Belmont BS | Eight Mile Plains Bus 2 | NCC Rating (A) | 479 | 479 | 479 | 479 | 479
|  |  |  | DER Forecast under System Normal (A) | 111 | 132 | 154 | 165 | 176
|  |  |  | Power Factor | 0.99827 | 0.99756 | 0.99668 | 0.99623 | 0.99571
|  |  |  | ECC Rating (A) | 479 | 479 | 479 | 479 | 479
|  |  |  | DER Forecast under N-1 Contingency (A) | 111 | 132 | 154 | 165 | 176
Belmont Bulk | 660-1 | Belmont BS | Scrub Road | NCC Rating (A) | 676 | 676 | 676 | 676 | 676
|  |  |  | DER Forecast under System Normal (A) | 5 | 7 | 16 | 24 | 31
|  |  |  | Power Factor | 0.99444 | 0.99702 | 0.99933 | 0.99955 | 0.9996
|  |  |  | ECC Rating (A) | 676 | 676 | 676 | 676 | 676
|  |  |  | DER Forecast under N-1 Contingency (A) | 10 | 13 | 33 | 49 | 62
Belmont Bulk | 661-1 | Belmont BS | Scrub Road | NCC Rating (A) | 676 | 676 | 676 | 676 | 676
|  |  |  | DER Forecast under System Normal (A) | 5 | 7 | 16 | 25 | 31
|  |  |  | Power Factor | 0.99444 | 0.99702 | 0.99933 | 0.99955 | 0.9996
|  |  |  | ECC Rating (A) | 676 | 676 | 676 | 676 | 676
|  |  |  | DER Forecast under N-1 Contingency (A) | 10 | 13 | 33 | 49 | 62
Belmont Bulk | 662-1 | Belmont BS | Upper Mt Gravatt | NCC Rating (A) | 656 | 656 | 656 | 656 | 656
|  |  |  | DER Forecast under System Normal (A) | 30 | 28 | 26 | 25 | 24
|  |  |  | Power Factor | 0.90746 | 0.88414 | 0.85942 | 0.83904 | 0.823
|  |  |  | ECC Rating (A) | 656 | 656 | 656 | 656 | 656
|  |  |  | DER Forecast under N-1 Contingency (A) | 43 | 41 | 39 | 37 | 36
Belmont Bulk | 663-1 | Belmont BS | Upper Mt Gravatt | NCC Rating (A) | 656 | 656 | 656 | 656 | 656
|  |  |  | DER Forecast under System Normal (A) | 30 | 28 | 26 | 25 | 24
|  |  |  | Power Factor | 0.90935 | 0.88636 | 0.86194 | 0.84179 | 0.82591
|  |  |  | ECC Rating (A) | 656 | 656 | 656 | 656 | 656
|  |  |  | DER Forecast under N-1 Contingency (A) | 43 | 41 | 39 | 38 | 37
Belmont Bulk | 692-1 | Belmont BS | Holland Pk East | NCC Rating (A) | 421 | 421 | 421 | 421 | 421
|  |  |  | DER Forecast under System Normal (A) | 25 | 26 | 29 | 33 | 37
|  |  |  | Power Factor | 0.090756 | 0.26242 | 0.50444 | 0.65017 | 0.73901
|  |  |  | ECC Rating (A) | 421 | 421 | 421 | 421 | 421
|  |  |  | DER Forecast under N-1 Contingency (A) | 26 | 29 | 39 | 50 | 60
Belmont Bulk | 693-1 | Belmont BS | Holland Pk East | NCC Rating (A) | 421 | 421 | 421 | 421 | 421
|  |  |  | DER Forecast under System Normal (A) | 25 | 26 | 29 | 33 | 37
|  |  |  | Power Factor | 0.091523 | 0.2645 | 0.50765 | 0.65339 | 0.7419
|  |  |  | ECC Rating (A) | 421 | 421 | 421 | 421 | 421
|  |  |  | DER Forecast under N-1 Contingency (A) | 26 | 29 | 39 | 50 | 60
Brendale Bulk | 303-1 | Brendale BS | Albany Ck | NCC Rating (A) | 725 | 725 | 725 | 725 | 725
|  |  |  | DER Forecast under System Normal (A) | 80 | 92 | 101 | 109 | 116
|  |  |  | Power Factor | 0.99914 | 0.99889 | 0.99865 | 0.99843 | 0.99823
|  |  |  | ECC Rating (A) | 725 | 725 | 725 | 725 | 725
|  |  |  | DER Forecast under N-1 Contingency (A) | 162 | 186 | 205 | 222 | 236
Brendale Bulk | 309-1 | Brendale BS | 309 Tee1 | NCC Rating (A) | 627 | 627 | 627 | 627 | 627
|  |  |  | DER Forecast under System Normal (A) | 73 | 84 | 93 | 101 | 109
|  |  |  | Power Factor | 0.9997 | 0.99946 | 0.99922 | 0.99897 | 0.99868
|  |  |  | ECC Rating (A) | 627 | 627 | 627 | 627 | 627
|  |  |  | DER Forecast under N-1 Contingency (A) | 138 | 156 | 173 | 187 | 200
Brendale Bulk | 309-2 | 309 Tee1 | Samford | NCC Rating (A) | 711 | 711 | 711 | 711 | 711
|  |  |  | DER Forecast under System Normal (A) | 53 | 63 | 71 | 80 | 89
|  |  |  | Power Factor | 0.99931 | 0.99903 | 0.99868 | 0.99828 | 0.99783
|  |  |  | ECC Rating (A) | 711 | 711 | 711 | 711 | 711
|  |  |  | DER Forecast under N-1 Contingency (A) | 122 | 141 | 159 | 177 | 195
Brendale Bulk | 309-3 | 309 Tee1 | Arana Hills | NCC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | DER Forecast under System Normal (A) | 20 | 21 | 22 | 22 | 20
|  |  |  | Power Factor | 0.99993 | 0.99998 | 1 | 0.99993 | 0.99957
|  |  |  | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | DER Forecast under N-1 Contingency (A) | 110 | 123 | 133 | 141 | 148
Brendale Bulk | 310-1 | Brendale BS | 310 Tee1 | NCC Rating (A) | 627 | 627 | 627 | 627 | 627
|  |  |  | DER Forecast under System Normal (A) | 90 | 102 | 112 | 121 | 129
|  |  |  | Power Factor | 0.9996 | 0.99937 | 0.99916 | 0.99895 | 0.99873
|  |  |  | ECC Rating (A) | 627 | 627 | 627 | 627 | 627
|  |  |  | DER Forecast under N-1 Contingency (A) | 118 | 134 | 148 | 160 | 171
Brendale Bulk | 310-2 | 310 Tee1 | Arana Hills | NCC Rating (A) | 792 | 792 | 792 | 792 | 792
|  |  |  | DER Forecast under System Normal (A) | 90 | 102 | 112 | 121 | 129
|  |  |  | Power Factor | 0.99962 | 0.99947 | 0.99932 | 0.99917 | 0.99902
|  |  |  | ECC Rating (A) | 792 | 792 | 792 | 792 | 792
|  |  |  | DER Forecast under N-1 Contingency (A) | 118 | 134 | 148 | 160 | 171
Brendale Bulk | 333-1 | Brendale BS | Lawnton | NCC Rating (A) | 732 | 732 | 732 | 732 | 732
|  |  |  | DER Forecast under System Normal (A) | 40 | 52 | 63 | 89 | 96
|  |  |  | Power Factor | 0.99978 | 0.99967 | 0.99956 | 0.99924 | 0.99912
|  |  |  | ECC Rating (A) | 732 | 732 | 732 | 732 | 732
|  |  |  | DER Forecast under N-1 Contingency (A) | 69 | 91 | 109 | 155 | 168
Brendale Bulk | 3340-1 | Brendale Bs | Strathpine | NCC Rating (A) | 512 | 512 | 512 | 512 | 512
|  |  |  | DER Forecast under System Normal (A) | 9 | 11 | 6 | 4 | 5
|  |  |  | Power Factor | 0.99539 | 0.99594 | 0.99369 | 0.40081 | 0.54343
|  |  |  | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
|  |  |  | DER Forecast under N-1 Contingency (A) | 14 | 17 | 9 | 4 | 4
Brendale Bulk | 334-1 | Lawnton | 334 Tee1 | NCC Rating (A) | 578 | 578 | 578 | 578 | 578
|  |  |  | DER Forecast under System Normal (A) | 15 | 14 | 12 | 18 | 16
|  |  |  | Power Factor | 0.99948 | 0.99883 | 0.9975 | 0.9996 | 0.99906
|  |  |  | ECC Rating (A) | 578 | 578 | 578 | 578 | 578
|  |  |  | DER Forecast under N-1 Contingency (A) | 28 | 31 | 32 | 47 | 48
Brendale Bulk | 334-2 | 334 Tee1 | Whiteside | NCC Rating (A) | 750 | 750 | 750 | 750 | 750
|  |  |  | DER Forecast under System Normal (A) | 25 | 30 | 35 | 38 | 42
|  |  |  | Power Factor | 0.99974 | 0.99997 | 0.99992 | 0.99983 | 0.99972
|  |  |  | ECC Rating (A) | 750 | 750 | 750 | 750 | 750
|  |  |  | DER Forecast under N-1 Contingency (A) | 52 | 63 | 72 | 80 | 88
Brendale Bulk | 334-3 | 334 Tee1 | Nth Pine Dam | NCC Rating (A) | 578 | 578 | 578 | 578 | 578
|  |  |  | DER Forecast under System Normal (A) | 40 | 44 | 47 | 56 | 58
|  |  |  | Power Factor | 0.99964 | 0.99978 | 0.99986 | 1 | 1
|  |  |  | ECC Rating (A) | 578 | 578 | 578 | 578 | 578
|  |  |  | DER Forecast under N-1 Contingency (A) | 52 | 60 | 66 | 83 | 87
Brendale Bulk | 335-1 | Brendale BS | 335 Tee1 | NCC Rating (A) | 485 | 485 | 485 | 485 | 485
|  |  |  | DER Forecast under System Normal (A) | 19 | 28 | 36 | 50 | 56
|  |  |  | Power Factor | 0.99941 | 0.99906 | 0.99875 | 0.99822 | 0.99795
|  |  |  | ECC Rating (A) | 485 | 485 | 485 | 485 | 485
|  |  |  | DER Forecast under N-1 Contingency (A) | 32 | 45 | 57 | 80 | 88
Brendale Bulk | 335-2 | 335 Tee | Whiteside | NCC Rating (A) | 750 | 750 | 750 | 750 | 750
|  |  |  | DER Forecast under System Normal (A) | 27 | 33 | 37 | 42 | 46
|  |  |  | Power Factor | 0.99984 | 0.99997 | 0.99989 | 0.99977 | 0.99965
|  |  |  | ECC Rating (A) | 750 | 750 | 750 | 750 | 750
|  |  |  | DER Forecast under N-1 Contingency (A) | 52 | 63 | 72 | 81 | 88
Brendale Bulk | 335-3 | 335 Tee | Nth Pine Dam | NCC Rating (A) | 485 | 485 | 485 | 485 | 485
|  |  |  | DER Forecast under System Normal (A) | 8 | 5 | 3 | 8 | 10
|  |  |  | Power Factor | 0.97943 | 0.92657 | 0.62054 | 0.95046 | 0.96323
|  |  |  | ECC Rating (A) | 485 | 485 | 485 | 485 | 485
|  |  |  | DER Forecast under N-1 Contingency (A) | 48 | 48 | 48 | 48 | 48
Brendale Bulk | 336-1 | Brendale BS | Strathpine | NCC Rating (A) | 455 | 455 | 455 | 455 | 455
|  |  |  | DER Forecast under System Normal (A) | 11 | 13 | 8 | 4 | 4
|  |  |  | Power Factor | 0.9351 | 0.95488 | 0.87707 | 0.4285 | 0.66482
|  |  |  | ECC Rating (A) | 455 | 455 | 455 | 455 | 455
|  |  |  | DER Forecast under N-1 Contingency (A) | 15 | 19 | 11 | 4 | 5
Brendale Bulk | 3364-1 | Brendale BS | Albany Ck | NCC Rating (A) | 725 | 725 | 725 | 725 | 725
|  |  |  | DER Forecast under System Normal (A) | 82 | 94 | 104 | 112 | 119
|  |  |  | Power Factor | 0.99918 | 0.99893 | 0.99869 | 0.99848 | 0.99828
|  |  |  | ECC Rating (A) | 725 | 725 | 725 | 725 | 725
|  |  |  | DER Forecast under N-1 Contingency (A) | 162 | 186 | 205 | 222 | 236
Brendale Bulk | 337-1 | Brendale BS | Strathpine | NCC Rating (A) | 490 | 490 | 490 | 490 | 490
|  |  |  | DER Forecast under System Normal (A) | 8 | 10 | 6 | 1 | 2
|  |  |  | Power Factor | 0.99847 | 0.99908 | 0.99641 | 0.94708 | 0.98293
|  |  |  | ECC Rating (A) | 490 | 490 | 490 | 490 | 490
|  |  |  | DER Forecast under N-1 Contingency (A) | 13 | 16 | 9 | 2 | 4
Brendale Bulk | 342-1 | Brendale BS | Bald Hills Bus 2 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under System Normal (A) | 33 | 42 | 50 | 59 | 68
|  |  |  | Power Factor | 0.99705 | 0.9986 | 0.99938 | 0.99978 | 0.99983
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under N-1 Contingency (A) | 33 | 42 | 50 | 59 | 68
Brendale Bulk | 349-1 | Brendale BS | Lawnton | NCC Rating (A) | 717 | 717 | 717 | 717 | 717
|  |  |  | DER Forecast under System Normal (A) | 43 | 56 | 68 | 96 | 104
|  |  |  | Power Factor | 0.99967 | 0.99955 | 0.99943 | 0.99909 | 0.99897
|  |  |  | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
|  |  |  | DER Forecast under N-1 Contingency (A) | 71 | 93 | 112 | 159 | 172
Brendale Bulk | 464-1 | Brendale BS | Samford | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under System Normal (A) | 69 | 80 | 89 | 98 | 107
|  |  |  | Power Factor | 0.99975 | 0.99946 | 0.99913 | 0.99877 | 0.99835
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under N-1 Contingency (A) | 122 | 141 | 159 | 177 | 195
Browns Plains Bulk | 406A-1 | Bethania | Kingston | NCC Rating (A) | 529 | 529 | 529 | 529 | 529
|  |  |  | DER Forecast under System Normal (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 6.3209e-06 | 6.3212e-06 | 6.3213e-06 | 6.3213e-06 | 6.3211e-06
|  |  |  | ECC Rating (A) | 529 | 529 | 529 | 529 | 529
|  |  |  | DER Forecast under N-1 Contingency (A) | 1 | 1 | 1 | 1 | 1
Browns Plains Bulk | 406B-1 | Crestmead | Kingston | NCC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | DER Forecast under System Normal (A) | 2 | 2 | 2 | 2 | 2
|  |  |  | Power Factor | 4.3754e-05 | 4.3755e-05 | 4.3755e-05 | 4.3755e-05 | 4.3754e-05
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | DER Forecast under N-1 Contingency (A) | 2 | 2 | 2 | 2 | 2
Browns Plains Bulk | 478-1 | Browns Plains BS | Nth Maclean | NCC Rating (A) | 813 | 813 | 813 | 813 | 813
|  |  |  | DER Forecast under System Normal (A) | 2 | 2 | 2 | 2 | 2
|  |  |  | Power Factor | 3.0986e-05 | 3.0986e-05 | 3.0986e-05 | 3.0986e-05 | 3.0986e-05
|  |  |  | ECC Rating (A) | 813 | 813 | 813 | 813 | 813
|  |  |  | DER Forecast under N-1 Contingency (A) | 2 | 2 | 2 | 2 | 2
Browns Plains Bulk | 481-1 | Browns Plains BS | Cresmead | NCC Rating (A) | 705 | 705 | 705 | 705 | 705
|  |  |  | DER Forecast under System Normal (A) | 55 | 101 | 155 | 217 | 293
|  |  |  | Power Factor | 0.9851 | 0.99839 | 0.99739 | 0.99452 | 0.98977
|  |  |  | ECC Rating (A) | 705 | 705 | 705 | 705 | 705
|  |  |  | DER Forecast under N-1 Contingency (A) | 109 | 202 | 310 | 436 | 586
Browns Plains Bulk | 482-1 | Browns Plains BS | Cresmead | NCC Rating (A) | 704 | 704 | 704 | 704 | 704
|  |  |  | DER Forecast under System Normal (A) | 56 | 101 | 156 | 219 | 294
|  |  |  | Power Factor | 0.98513 | 0.99916 | 0.99749 | 0.99465 | 0.98994
|  |  |  | ECC Rating (A) | 704 | 704 | 704 | 704 | 704
|  |  |  | DER Forecast under N-1 Contingency (A) | 109 | 202 | 310 | 436 | 586
Browns Plains Bulk | 542-1 | Browns Plains BS | Heathwood | NCC Rating (A) | 704 | 704 | 704 | 704 | 704
|  |  |  | DER Forecast under System Normal (A) | 13 | 47 | 80 | 113 | 145
|  |  |  | Power Factor | 0.97336 | 0.9988 | 0.9999 | 0.99955 | 0.99902
|  |  |  | ECC Rating (A) | 704 | 704 | 704 | 704 | 704
|  |  |  | DER Forecast under N-1 Contingency (A) | 13 | 47 | 80 | 113 | 145
Burleigh Heads Bulk | 3751-1 | Burleigh Hds BS | Currumbin | NCC Rating (A) | 606 | 606 | 606 | 606 | 606
|  |  |  | DER Forecast under System Normal (A) | 249 | 233 | 219 | 207 | 195
|  |  |  | Power Factor | 0.99872 | 0.99877 | 0.99871 | 0.99863 | 0.99854
|  |  |  | ECC Rating (A) | 695 | 695 | 695 | 695 | 695
|  |  |  | DER Forecast under N-1 Contingency (A) | 411 | 385 | 362 | 341 | 322
Burleigh Heads Bulk | 3755-1 | Burleigh Hds BS | Currumbin | NCC Rating (A) | 606 | 606 | 606 | 606 | 606
|  |  |  | DER Forecast under System Normal (A) | 248 | 233 | 219 | 207 | 195
|  |  |  | Power Factor | 0.99873 | 0.99877 | 0.99871 | 0.99863 | 0.99854
|  |  |  | ECC Rating (A) | 695 | 695 | 695 | 695 | 695
|  |  |  | DER Forecast under N-1 Contingency (A) | 410 | 385 | 362 | 341 | 322
Burleigh Heads Bulk | 3756-1 | Burleigh Hds BS | 3756 Tee1 | NCC Rating (A) | 715 | 715 | 715 | 715 | 715
|  |  |  | DER Forecast under System Normal (A) | 63 | 58 | 53 | 49 | 46
|  |  |  | Power Factor | 0.9995 | 0.99929 | 0.99924 | 0.99919 | 0.99915
|  |  |  | ECC Rating (A) | 715 | 715 | 715 | 715 | 715
|  |  |  | DER Forecast under N-1 Contingency (A) | 105 | 98 | 91 | 84 | 79
Burleigh Heads Bulk | 3756-2 | 3756 Tee1 | Palm Beach | NCC Rating (A) | 532 | 532 | 532 | 532 | 532
|  |  |  | DER Forecast under System Normal (A) | 89 | 95 | 100 | 104 | 107
|  |  |  | Power Factor | 0.9991 | 0.9996 | 0.9996 | 0.9996 | 0.99959
|  |  |  | ECC Rating (A) | 532 | 532 | 532 | 532 | 532
|  |  |  | DER Forecast under N-1 Contingency (A) | 135 | 139 | 141 | 143 | 144
Burleigh Heads Bulk | 3756-3 | 3756 Tee1 | 3756 Tee2 | NCC Rating (A) | 636 | 636 | 636 | 636 | 636
|  |  |  | DER Forecast under System Normal (A) | 152 | 153 | 154 | 154 | 153
|  |  |  | Power Factor | 0.99921 | 0.99944 | 0.99944 | 0.99944 | 0.99943
|  |  |  | ECC Rating (A) | 636 | 636 | 636 | 636 | 636
|  |  |  | DER Forecast under N-1 Contingency (A) | 240 | 236 | 232 | 227 | 222
Burleigh Heads Bulk | 3756-4 | 3756 Tee2 | Currumbin | NCC Rating (A) | 717 | 717 | 717 | 717 | 717
|  |  |  | DER Forecast under System Normal (A) | 152 | 153 | 154 | 154 | 153
|  |  |  | Power Factor | 0.99921 | 0.99944 | 0.99944 | 0.99944 | 0.99943
|  |  |  | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
|  |  |  | DER Forecast under N-1 Contingency (A) | 240 | 236 | 232 | 227 | 222
Burleigh Heads Bulk | 393-1 | Currumbin | Kirra | NCC Rating (A) | 403 | 403 | 445 | 445 | 445
|  |  |  | DER Forecast under System Normal (A) | 144 | 134 | 124 | 113 | 102
|  |  |  | Power Factor | 0.99825 | 0.99846 | 0.99905 | 0.99915 | 0.99922
|  |  |  | ECC Rating (A) | 403 | 403 | 445 | 445 | 445
|  |  |  | DER Forecast under N-1 Contingency (A) | 144 | 134 | 124 | 113 | 102
Burleigh Heads Bulk | 395-1 | Burleigh Hds BS | Miami | NCC Rating (A) | 654 | 654 | 654 | 654 | 654
|  |  |  | DER Forecast under System Normal (A) | 10 | 10 | 28 | 42 | 54
|  |  |  | Power Factor | 0.98915 | 0.98908 | 0.99824 | 0.99905 | 0.99929
|  |  |  | ECC Rating (A) | 654 | 654 | 654 | 654 | 654
|  |  |  | DER Forecast under N-1 Contingency (A) | 10 | 10 | 28 | 42 | 54
Burleigh Heads Bulk | 396-1 | Burleigh Hds BS | Palm Beach | NCC Rating (A) | 806 | 806 | 806 | 806 | 806
|  |  |  | DER Forecast under System Normal (A) | 68 | 62 | 57 | 53 | 48
|  |  |  | Power Factor | 0.9995 | 0.99923 | 0.99914 | 0.99903 | 0.99892
|  |  |  | ECC Rating (A) | 806 | 806 | 806 | 806 | 806
|  |  |  | DER Forecast under N-1 Contingency (A) | 114 | 106 | 98 | 91 | 84
Burleigh Heads Bulk | 397-1 | Burleigh Hds BS | 397 Tee1 | NCC Rating (A) | 602 | 602 | 602 | 602 | 602
|  |  |  | DER Forecast under System Normal (A) | 3 | 3 | 3 | 3 | 3
|  |  |  | Power Factor | 1.8279e-05 | 1.8279e-05 | 1.8279e-05 | 1.8279e-05 | 1.8279e-05
|  |  |  | ECC Rating (A) | 602 | 602 | 602 | 602 | 602
|  |  |  | DER Forecast under N-1 Contingency (A) | 3 | 3 | 3 | 3 | 3
Burleigh Heads Bulk | 397-2 | 397 Tee1 | 396 Tee | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under System Normal (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 4.76e-05 | 4.76e-05 | 4.76e-05 | 4.7615e-05 | 4.7615e-05
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under N-1 Contingency (A) | 0 | 0 | 0 | 0 | 0
Burleigh Heads Bulk | 397-3 | 397 Tee1 | 397 Tee2 | NCC Rating (A) | 529 | 529 | 529 | 529 | 529
|  |  |  | DER Forecast under System Normal (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 8.555e-06 | 8.555e-06 | 8.555e-06 | 8.5548e-06 | 8.5546e-06
|  |  |  | ECC Rating (A) | 529 | 529 | 529 | 529 | 529
|  |  |  | DER Forecast under N-1 Contingency (A) | 1 | 1 | 1 | 1 | 1
Burleigh Heads Bulk | 397-4 | 397 Tee2 | 3700 Tee1 | NCC Rating (A) | 362 | 362 | 362 | 362 | 362
|  |  |  | DER Forecast under System Normal (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 8.645e-07 | 8.645e-07 | 8.645e-07 | 8.646e-07 | 8.6437e-07
|  |  |  | ECC Rating (A) | 362 | 362 | 362 | 362 | 362
|  |  |  | DER Forecast under N-1 Contingency (A) | 0 | 0 | 0 | 0 | 0
Burleigh Heads Bulk | 397-5 | 397 Tee2 | Mudgeeraba BS | NCC Rating (A) | 703 | 703 | 703 | 703 | 703
|  |  |  | DER Forecast under System Normal (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 2.5247e-06 | 2.5247e-06 | 2.5247e-06 | 2.5239e-06 | 2.5233e-06
|  |  |  | ECC Rating (A) | 703 | 703 | 703 | 703 | 703
|  |  |  | DER Forecast under N-1 Contingency (A) | 0 | 0 | 0 | 0 | 0
Caboolture Bulk | 321-1 | Caboolture BS | Caboolture West | NCC Rating (A) | 509 | 509 | 509 | 509 | 509
|  |  |  | DER Forecast under System Normal (A) | 103 | 157 | 214 | 274 | 339
|  |  |  | Power Factor | 0.99843 | 0.99622 | 0.99305 | 0.98873 | 0.9829
|  |  |  | ECC Rating (A) | 509 | 509 | 509 | 509 | 509
|  |  |  | DER Forecast under N-1 Contingency (A) | 161 | 245 | 333 | 427 | 529
Caboolture Bulk | 322-1 | Caboolture BS | Caboolture West | NCC Rating (A) | 509 | 509 | 509 | 509 | 509
|  |  |  | DER Forecast under System Normal (A) | 109 | 165 | 225 | 288 | 356
|  |  |  | Power Factor | 0.99972 | 0.99854 | 0.9964 | 0.99316 | 0.9885
|  |  |  | ECC Rating (A) | 509 | 509 | 509 | 509 | 509
|  |  |  | DER Forecast under N-1 Contingency (A) | 165 | 251 | 341 | 437 | 542
Caboolture Bulk | 323-1 | Caboolture West | 323 Tee1 | NCC Rating (A) | 250 | 250 | 250 | 250 | 250
|  |  |  | DER Forecast under System Normal (A) | 34 | 39 | 44 | 47 | 51
|  |  |  | Power Factor | 0.99962 | 0.9999 | 0.99999 | 1 | 0.99997
|  |  |  | ECC Rating (A) | 250 | 250 | 250 | 250 | 250
|  |  |  | DER Forecast under N-1 Contingency (A) | 34 | 39 | 44 | 47 | 51
Caboolture Bulk | 323-2 | 323 Tee1 | Wamuran | NCC Rating (A) | 457 | 457 | 457 | 457 | 457
|  |  |  | DER Forecast under System Normal (A) | 34 | 39 | 44 | 47 | 51
|  |  |  | Power Factor | 0.99969 | 0.99957 | 0.99947 | 0.99939 | 0.99931
|  |  |  | ECC Rating (A) | 457 | 457 | 457 | 457 | 457
|  |  |  | DER Forecast under N-1 Contingency (A) | 34 | 39 | 44 | 47 | 51
Caboolture Bulk | 323-3 | 323 Tee1 | Woodford | NCC Rating (A) | 251 | 251 | 251 | 251 | 251
|  |  |  | DER Forecast under System Normal (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 1.5119e-05 | 1.5118e-05 | 1.5118e-05 | 1.5119e-05 | 1.5118e-05
|  |  |  | ECC Rating (A) | 251 | 251 | 251 | 251 | 251
|  |  |  | DER Forecast under N-1 Contingency (A) | 1 | 1 | 1 | 1 | 1
Caboolture Bulk | 350-1 | Caboolture BS | Ningi | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under System Normal (A) | 170 | 214 | 253 | 290 | 325
|  |  |  | Power Factor | 0.99758 | 0.99552 | 0.9933 | 0.9908 | 0.98822
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under N-1 Contingency (A) | 309 | 389 | 462 | 529 | 594
Caboolture Bulk | 412-1 | Caboolture BS | Toorbul Pt | NCC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | DER Forecast under System Normal (A) | 144 | 182 | 216 | 248 | 279
|  |  |  | Power Factor | 0.99974 | 0.99898 | 0.99796 | 0.99667 | 0.99526
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | DER Forecast under N-1 Contingency (A) | 309 | 389 | 463 | 531 | 598
Caboolture Bulk | 417-1 | Ningi | Toorbul Pt | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under System Normal (A) | 102 | 130 | 156 | 180 | 204
|  |  |  | Power Factor | 0.9985 | 0.99718 | 0.99577 | 0.99414 | 0.99254
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under N-1 Contingency (A) | 242 | 306 | 365 | 420 | 474
Caboolture Bulk | 431-1 | Toorbul Point | Bribie Is | NCC Rating (A) | 396 | 396 | 396 | 396 | 396
|  |  |  | DER Forecast under System Normal (A) | 85 | 108 | 130 | 149 | 168
|  |  |  | Power Factor | 0.99967 | 0.99922 | 0.99868 | 0.99798 | 0.99729
|  |  |  | ECC Rating (A) | 443 | 443 | 443 | 443 | 443
|  |  |  | DER Forecast under N-1 Contingency (A) | 169 | 216 | 258 | 298 | 335
Caboolture Bulk | 448-1 | Morayfield Nth | 448 Tee1 | NCC Rating (A) | 776 | 776 | 776 | 776 | 776
|  |  |  | DER Forecast under System Normal (A) | 236 | 345 | 462 | 587 | 725
|  |  |  | Power Factor | 0.99827 | 0.99576 | 0.99184 | 0.98623 | 0.97856
|  |  |  | ECC Rating (A) | 776 | 776 | 776 | 776 | 776
|  |  |  | DER Forecast under N-1 Contingency (A) | 286 | 420 | 565 | 719 | 889
Caboolture Bulk | 448-2 | 448 Tee1 | Morayfield | NCC Rating (A) | 698 | 698 | 698 | 698 | 698
|  |  |  | DER Forecast under System Normal (A) | 203 | 303 | 410 | 525 | 651
|  |  |  | Power Factor | 0.99878 | 0.99722 | 0.99486 | 0.99153 | 0.98723
|  |  |  | ECC Rating (A) | 698 | 698 | 698 | 698 | 698
|  |  |  | DER Forecast under N-1 Contingency (A) | 203 | 303 | 410 | 525 | 651
Caboolture Bulk | 448-3 | 448 Tee1 | Caboolture West | NCC Rating (A) | 485 | 485 | 485 | 485 | 485
|  |  |  | DER Forecast under System Normal (A) | 33 | 42 | 51 | 62 | 75
|  |  |  | Power Factor | 0.99911 | 0.9986 | 0.99757 | 0.99577 | 0.99228
|  |  |  | ECC Rating (A) | 485 | 485 | 485 | 485 | 485
|  |  |  | DER Forecast under N-1 Contingency (A) | 83 | 118 | 155 | 195 | 239
Caboolture Bulk | 457-1 | Toorbul Pt | Bribie Island | NCC Rating (A) | 402 | 402 | 402 | 402 | 402
|  |  |  | DER Forecast under System Normal (A) | 84 | 108 | 129 | 148 | 167
|  |  |  | Power Factor | 0.9991 | 0.99845 | 0.99775 | 0.99687 | 0.99603
|  |  |  | ECC Rating (A) | 402 | 402 | 402 | 402 | 402
|  |  |  | DER Forecast under N-1 Contingency (A) | 169 | 216 | 259 | 298 | 335
Caboolture Bulk | 461-1 | Caboolture BS | Morayfield Nth | NCC Rating (A) | 676 | 676 | 676 | 676 | 676
|  |  |  | DER Forecast under System Normal (A) | 137 | 231 | 331 | 434 | 545
|  |  |  | Power Factor | 0.9987 | 0.99715 | 0.99463 | 0.99098 | 0.986
|  |  |  | ECC Rating (A) | 758 | 758 | 758 | 758 | 758
|  |  |  | DER Forecast under N-1 Contingency (A) | 247 | 418 | 597 | 783 | 982
Caboolture Bulk | 499-1 | Caboolture BS | Morayfield Nth | NCC Rating (A) | 676 | 676 | 676 | 676 | 676
|  |  |  | DER Forecast under System Normal (A) | 138 | 233 | 333 | 437 | 548
|  |  |  | Power Factor | 0.99872 | 0.99718 | 0.99465 | 0.991 | 0.98603
|  |  |  | ECC Rating (A) | 758 | 758 | 758 | 758 | 758
|  |  |  | DER Forecast under N-1 Contingency (A) | 248 | 418 | 598 | 784 | 983
Cleveland Bulk | 3550-1 | Cleveland BS | Victoria Pt | NCC Rating (A) | 746 | 746 | 746 | 746 | 746
|  |  |  | DER Forecast under System Normal (A) | 128 | 169 | 205 | 236 | 266
|  |  |  | Power Factor | 0.99884 | 0.99971 | 0.99963 | 0.99942 | 0.99919
|  |  |  | ECC Rating (A) | 746 | 746 | 746 | 746 | 746
|  |  |  | DER Forecast under N-1 Contingency (A) | 179 | 236 | 285 | 330 | 371
Cleveland Bulk | 3570-1 | Capalaba South | Capalaba | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under System Normal (A) | 24 | 26 | 29 | 33 | 36
|  |  |  | Power Factor | 0.99896 | 0.99959 | 0.99995 | 0.99995 | 0.99958
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under N-1 Contingency (A) | 79 | 101 | 122 | 143 | 164
Cleveland Bulk | 3580-1 | Redland Bay | 3580 Tee1 | NCC Rating (A) | 717 | 717 | 717 | 717 | 717
|  |  |  | DER Forecast under System Normal (A) | 39 | 48 | 56 | 64 | 70
|  |  |  | Power Factor | 0.99818 | 0.99725 | 0.99636 | 0.9955 | 0.99466
|  |  |  | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
|  |  |  | DER Forecast under N-1 Contingency (A) | 150 | 189 | 223 | 253 | 281
Cleveland Bulk | 3580-2 | 3580 Tee1 | Mt Cotton | NCC Rating (A) | 527 | 527 | 527 | 527 | 527
|  |  |  | DER Forecast under System Normal (A) | 39 | 48 | 56 | 63 | 70
|  |  |  | Power Factor | 0.99929 | 0.99835 | 0.99735 | 0.99637 | 0.99539
|  |  |  | ECC Rating (A) | 527 | 527 | 527 | 527 | 527
|  |  |  | DER Forecast under N-1 Contingency (A) | 150 | 189 | 223 | 253 | 280
Cleveland Bulk | 3580-3 | 3580 Tee1 | Cornubia | NCC Rating (A) | 717 | 717 | 717 | 717 | 717
|  |  |  | DER Forecast under System Normal (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 2.2668e-06 | 2.2668e-06 | 2.2666e-06 | 2.2669e-06 | 2.2666e-06
|  |  |  | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
|  |  |  | DER Forecast under N-1 Contingency (A) | 1 | 1 | 1 | 1 | 1
Cleveland Bulk | 371-1 | Cleveland BS | Birkdale | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under System Normal (A) | 87 | 107 | 125 | 141 | 156
|  |  |  | Power Factor | 0.99968 | 0.99942 | 0.99915 | 0.99888 | 0.99861
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under N-1 Contingency (A) | 156 | 180 | 199 | 216 | 231
Cleveland Bulk | 372-1 | Cleveland BS | Raby Bay | NCC Rating (A) | 611 | 611 | 611 | 611 | 611
|  |  |  | DER Forecast under System Normal (A) | 45 | 66 | 85 | 102 | 119
|  |  |  | Power Factor | 0.99517 | 0.9987 | 0.99913 | 0.99892 | 0.9987
|  |  |  | ECC Rating (A) | 611 | 611 | 611 | 611 | 611
|  |  |  | DER Forecast under N-1 Contingency (A) | 87 | 128 | 164 | 198 | 230
Cleveland Bulk | 373-1 | Raby Bay | Capalaba | NCC Rating (A) | 715 | 715 | 715 | 715 | 715
|  |  |  | DER Forecast under System Normal (A) | 44 | 60 | 75 | 89 | 103
|  |  |  | Power Factor | 0.99857 | 0.99826 | 0.99799 | 0.99774 | 0.9975
|  |  |  | ECC Rating (A) | 715 | 715 | 715 | 715 | 715
|  |  |  | DER Forecast under N-1 Contingency (A) | 88 | 114 | 138 | 160 | 182
Cleveland Bulk | 374-1 | Cleveland BS | Capalaba South | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under System Normal (A) | 55 | 75 | 93 | 111 | 128
|  |  |  | Power Factor | 1 | 0.99995 | 0.99981 | 0.99963 | 0.99943
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under N-1 Contingency (A) | 97 | 126 | 153 | 178 | 203
Cleveland Bulk | 375-1 | Cleveland BS | 375 Tee1 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under System Normal (A) | 45 | 60 | 73 | 84 | 94
|  |  |  | Power Factor | 0.9995 | 0.99877 | 0.998 | 0.99724 | 0.99648
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under N-1 Contingency (A) | 156 | 201 | 239 | 273 | 304
Cleveland Bulk | 375-2 | 375 Tee1 | Mt Cotton | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under System Normal (A) | 45 | 60 | 73 | 84 | 94
|  |  |  | Power Factor | 0.99936 | 0.99878 | 0.99812 | 0.99748 | 0.99685
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under N-1 Contingency (A) | 156 | 201 | 239 | 273 | 304
Cleveland Bulk | 375-3 | 375 Tee1 | 425 Tee1 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under System Normal (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0.00030557 | 0.00030497 | 0.00030444 | 0.00030517 | 0.00030475
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under N-1 Contingency (A) | 0 | 0 | 0 | 0 | 0
Cleveland Bulk | 413-1 | Cleveland BS | Raby Bay | NCC Rating (A) | 611 | 611 | 611 | 611 | 611
|  |  |  | DER Forecast under System Normal (A) | 46 | 67 | 86 | 104 | 120
|  |  |  | Power Factor | 0.99532 | 0.99875 | 0.99916 | 0.99895 | 0.99873
|  |  |  | ECC Rating (A) | 611 | 611 | 611 | 611 | 611
|  |  |  | DER Forecast under N-1 Contingency (A) | 87 | 128 | 165 | 198 | 230
Cleveland Bulk | 425-1 | Cleveland BS | Victoria Pt | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under System Normal (A) | 57 | 75 | 91 | 105 | 118
|  |  |  | Power Factor | 0.99921 | 0.99841 | 0.99765 | 0.99693 | 0.99623
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under N-1 Contingency (A) | 157 | 207 | 250 | 289 | 325
Cleveland Bulk | 465-1 | Victoria Pt | Redland Bay | NCC Rating (A) | 508 | 508 | 508 | 508 | 508
|  |  |  | DER Forecast under System Normal (A) | 113 | 143 | 170 | 193 | 215
|  |  |  | Power Factor | 0.99961 | 0.99933 | 0.99903 | 0.9987 | 0.99836
|  |  |  | ECC Rating (A) | 508 | 508 | 508 | 508 | 508
|  |  |  | DER Forecast under N-1 Contingency (A) | 158 | 203 | 242 | 277 | 308
Cleveland Bulk | 484-1 | Capalaba | Birkdale | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under System Normal (A) | 70 | 74 | 75 | 76 | 75
|  |  |  | Power Factor | 0.99863 | 0.99795 | 0.99724 | 0.99648 | 0.99567
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under N-1 Contingency (A) | 156 | 180 | 199 | 215 | 230
Coomera Bulk | 3640-1 | Coomera BS | Hope Is | NCC Rating (A) | 716 | 716 | 716 | 716 | 716
|  |  |  | DER Forecast under System Normal (A) | 92 | 139 | 184 | 229 | 273
|  |  |  | Power Factor | 0.99631 | 0.99983 | 0.99965 | 0.99471 | 0.99225
|  |  |  | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
|  |  |  | DER Forecast under N-1 Contingency (A) | 185 | 280 | 373 | 461 | 550
Coomera Bulk | 3641-1 | Coomera BS | Pimpama East | NCC Rating (A) | 713 | 713 | 713 | 713 | 713
|  |  |  | DER Forecast under System Normal (A) | 158 | 249 | 364 | 492 | 569
|  |  |  | Power Factor | 0.9957 | 0.98918 | 0.97639 | 0.95796 | 0.94572
|  |  |  | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
|  |  |  | DER Forecast under N-1 Contingency (A) | 315 | 498 | 727 | 985 | 1142
Coomera Bulk | 3642-1 | Coomera BS | Pimpama East | NCC Rating (A) | 713 | 713 | 713 | 713 | 713
|  |  |  | DER Forecast under System Normal (A) | 159 | 251 | 367 | 496 | 573
|  |  |  | Power Factor | 0.99573 | 0.98923 | 0.97647 | 0.95806 | 0.94584
|  |  |  | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
|  |  |  | DER Forecast under N-1 Contingency (A) | 315 | 498 | 728 | 985 | 1142
Coomera Bulk | 394-1 | Coomera BS | Hope Is | NCC Rating (A) | 716 | 716 | 716 | 716 | 716
|  |  |  | DER Forecast under System Normal (A) | 94 | 143 | 189 | 235 | 280
|  |  |  | Power Factor | 0.99858 | 0.99728 | 0.99519 | 0.99269 | 0.98972
|  |  |  | ECC Rating (A) | 716 | 716 | 716 | 716 | 716
|  |  |  | DER Forecast under N-1 Contingency (A) | 185 | 281 | 373 | 462 | 551
Coorparoo Bulk | 3429-1 | Coorparoo BS | Holland Park | NCC Rating (A) | 735 | 735 | 735 | 735 | 735
|  |  |  | DER Forecast under System Normal (A) | 6 | 6 | 16 | 25 | 34
|  |  |  | Power Factor | 0.99831 | 0.99788 | 0.99956 | 0.99965 | 0.99963
|  |  |  | ECC Rating (A) | 735 | 735 | 735 | 735 | 735
|  |  |  | DER Forecast under N-1 Contingency (A) | 12 | 11 | 31 | 50 | 66
Coorparoo Bulk | 3430-1 | Coorparoo BS | Holland Park | NCC Rating (A) | 735 | 735 | 735 | 735 | 735
|  |  |  | DER Forecast under System Normal (A) | 6 | 5 | 16 | 25 | 33
|  |  |  | Power Factor | 0.99819 | 0.99774 | 0.99954 | 0.99964 | 0.99962
|  |  |  | ECC Rating (A) | 735 | 735 | 735 | 735 | 735
|  |  |  | DER Forecast under N-1 Contingency (A) | 12 | 11 | 31 | 50 | 66
Coorparoo Bulk | 584-4 | 584 Tee2 | Coorparoo BS | NCC Rating (A) | 721 | 721 | 721 | 721 | 721
|  |  |  | DER Forecast under System Normal (A) | 2 | 2 | 2 | 2 | 2
|  |  |  | Power Factor | 7.9103e-07 | 7.9103e-07 | 7.9103e-07 | 7.9103e-07 | 7.9103e-07
|  |  |  | ECC Rating (A) | 721 | 721 | 721 | 721 | 721
|  |  |  | DER Forecast under N-1 Contingency (A) | 2 | 2 | 2 | 2 | 2
Coorparoo Bulk | 612-1 | Coorparoo BS | Camp Hill | NCC Rating (A) | 766 | 766 | 766 | 766 | 766
|  |  |  | DER Forecast under System Normal (A) | 67 | 103 | 137 | 171 | 205
|  |  |  | Power Factor | 0.99959 | 0.99883 | 0.99779 | 0.99649 | 0.99489
|  |  |  | ECC Rating (A) | 766 | 766 | 766 | 766 | 766
|  |  |  | DER Forecast under N-1 Contingency (A) | 133 | 206 | 275 | 342 | 409
Coorparoo Bulk | 613-1 | Coorparoo BS | Camp Hill | NCC Rating (A) | 766 | 766 | 766 | 766 | 766
|  |  |  | DER Forecast under System Normal (A) | 67 | 103 | 137 | 171 | 205
|  |  |  | Power Factor | 0.99959 | 0.99883 | 0.99779 | 0.99649 | 0.99489
|  |  |  | ECC Rating (A) | 766 | 766 | 766 | 766 | 766
|  |  |  | DER Forecast under N-1 Contingency (A) | 133 | 206 | 275 | 342 | 409
Coorparoo Bulk | 648-1 | Scrub Rd | 648 Tee1 | NCC Rating (A) | 597 | 597 | 597 | 597 | 597
|  |  |  | DER Forecast under System Normal (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 1.2324e-06 | 1.2316e-06 | 1.2324e-06 | 1.2328e-06 | 1.2328e-06
|  |  |  | ECC Rating (A) | 597 | 597 | 597 | 597 | 597
|  |  |  | DER Forecast under N-1 Contingency (A) | 1 | 1 | 1 | 1 | 1
Coorparoo Bulk | 648-2 | 648 Tee1 | 584 Tee1 | NCC Rating (A) | 348 | 348 | 348 | 348 | 348
|  |  |  | DER Forecast under System Normal (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 1.5487e-05 | 1.5489e-05 | 1.5486e-05 | 1.5488e-05 | 1.5489e-05
|  |  |  | ECC Rating (A) | 348 | 348 | 348 | 348 | 348
|  |  |  | DER Forecast under N-1 Contingency (A) | 0 | 0 | 0 | 0 | 0
Coorparoo Bulk | 648-3 | 648 Tee1 | Camp Hill | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under System Normal (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 2.117e-05 | 2.117e-05 | 2.1171e-05 | 2.1171e-05 | 2.1171e-05
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under N-1 Contingency (A) | 1 | 1 | 1 | 1 | 1
Doboy Bulk | 3426-1 | Queensport | Bulimba | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under System Normal (A) | 17 | 44 | 70 | 94 | 117
|  |  |  | Power Factor | 0.99086 | 0.99917 | 0.99995 | 0.99996 | 0.99971
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under N-1 Contingency (A) | 28 | 75 | 119 | 160 | 199
Doboy Bulk | 414-1 | Doboy BS | Tingalpa | NCC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | DER Forecast under System Normal (A) | 26 | 34 | 41 | 48 | 53
|  |  |  | Power Factor | 0.99997 | 0.9999 | 0.99982 | 0.99975 | 0.99968
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | DER Forecast under N-1 Contingency (A) | 64 | 82 | 98 | 112 | 124
Doboy Bulk | 416-1 | Doboy BS | Murarrie | NCC Rating (A) | 355 | 355 | 355 | 355 | 355
|  |  |  | DER Forecast under System Normal (A) | 38 | 29 | 18 | 7 | 11
|  |  |  | Power Factor | 0.99335 | 0.987 | 0.96491 | 0.71425 | 0.90007
|  |  |  | ECC Rating (A) | 355 | 355 | 355 | 355 | 355
|  |  |  | DER Forecast under N-1 Contingency (A) | 73 | 55 | 34 | 11 | 19
Doboy Bulk | 443-1 | Queensport | Bulimba | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under System Normal (A) | 12 | 31 | 49 | 66 | 83
|  |  |  | Power Factor | 0.99576 | 0.99996 | 0.9998 | 0.99932 | 0.99868
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under N-1 Contingency (A) | 28 | 75 | 119 | 160 | 199
Doboy Bulk | 446-11 | Doboy BS | Wellington Rd | NCC Rating (A) | 468 | 468 | 468 | 468 | 468
|  |  |  | DER Forecast under System Normal (A) | 73 | 68 | 63 | 59 | 54
|  |  |  | Power Factor | 0.99981 | 0.99968 | 0.9994 | 0.99888 | 0.99781
|  |  |  | ECC Rating (A) | 468 | 468 | 468 | 468 | 468
|  |  |  | DER Forecast under N-1 Contingency (A) | 179 | 179 | 179 | 179 | 179
Doboy Bulk | 446-12 | Wellington Rd | Queensport | NCC Rating (A) | 731 | 731 | 731 | 731 | 731
|  |  |  | DER Forecast under System Normal (A) | 105 | 110 | 114 | 119 | 124
|  |  |  | Power Factor | 0.99875 | 0.99901 | 0.99927 | 0.9995 | 0.99972
|  |  |  | ECC Rating (A) | 731 | 731 | 731 | 731 | 731
|  |  |  | DER Forecast under N-1 Contingency (A) | 178 | 178 | 178 | 178 | 178
Doboy Bulk | 558-1 | Hemmant | Tingalpa | NCC Rating (A) | 680 | 680 | 680 | 680 | 680
|  |  |  | DER Forecast under System Normal (A) | 38 | 48 | 57 | 64 | 71
|  |  |  | Power Factor | 0.99992 | 0.99984 | 0.99973 | 0.99962 | 0.99949
|  |  |  | ECC Rating (A) | 680 | 680 | 680 | 680 | 680
|  |  |  | DER Forecast under N-1 Contingency (A) | 64 | 82 | 98 | 112 | 124
Doboy Bulk | 563-1 | Doboy BS | Hemmant | NCC Rating (A) | 371 | 371 | 371 | 371 | 371
|  |  |  | DER Forecast under System Normal (A) | 16 | 26 | 37 | 49 | 61
|  |  |  | Power Factor | 0.8526 | 0.95257 | 0.97902 | 0.98937 | 0.99437
|  |  |  | ECC Rating (A) | 429 | 429 | 429 | 429 | 429
|  |  |  | DER Forecast under N-1 Contingency (A) | 28 | 47 | 69 | 91 | 116
Doboy Bulk | 564-1 | Doboy BS | Hemmant | NCC Rating (A) | 371 | 371 | 371 | 371 | 371
|  |  |  | DER Forecast under System Normal (A) | 15 | 25 | 36 | 47 | 59
|  |  |  | Power Factor | 0.83645 | 0.9439 | 0.97369 | 0.98579 | 0.99185
|  |  |  | ECC Rating (A) | 429 | 429 | 429 | 429 | 429
|  |  |  | DER Forecast under N-1 Contingency (A) | 27 | 47 | 68 | 91 | 115
Doboy Bulk | 575C-1 | Doboy BS | Murarrie | NCC Rating (A) | 355 | 355 | 355 | 355 | 355
|  |  |  | DER Forecast under System Normal (A) | 36 | 27 | 17 | 7 | 11
|  |  |  | Power Factor | 0.9924 | 0.98465 | 0.95731 | 0.66749 | 0.87008
|  |  |  | ECC Rating (A) | 475 | 475 | 475 | 475 | 475
|  |  |  | DER Forecast under N-1 Contingency (A) | 73 | 55 | 34 | 11 | 19
Doboy Bulk | 581-1 | Doboy BS | Queensport | NCC Rating (A) | 661 | 661 | 661 | 661 | 661
|  |  |  | DER Forecast under System Normal (A) | 67 | 18 | 32 | 81 | 134
|  |  |  | Power Factor | 0.99645 | 0.95097 | 0.99104 | 0.99794 | 0.99751
|  |  |  | ECC Rating (A) | 785 | 785 | 785 | 785 | 785
|  |  |  | DER Forecast under N-1 Contingency (A) | 127 | 52 | 89 | 155 | 255
Doboy Bulk | 645-1 | Doboy BS | Gibson Island | NCC Rating (A) | 433 | 433 | 433 | 433 | 433
|  |  |  | DER Forecast under System Normal (A) | 5 | 5 | 5 | 5 | 5
|  |  |  | Power Factor | 1.3174e-06 | 1.3174e-06 | 1.3174e-06 | 1.3174e-06 | 1.3174e-06
|  |  |  | ECC Rating (A) | 433 | 433 | 433 | 433 | 433
|  |  |  | DER Forecast under N-1 Contingency (A) | 5 | 5 | 5 | 5 | 5
Doboy Bulk | 677-1 | Doboy BS | Queensport | NCC Rating (A) | 661 | 661 | 661 | 661 | 661
|  |  |  | DER Forecast under System Normal (A) | 67 | 18 | 32 | 81 | 133
|  |  |  | Power Factor | 0.99642 | 0.95066 | 0.99096 | 0.99792 | 0.9975
|  |  |  | ECC Rating (A) | 785 | 785 | 785 | 785 | 785
|  |  |  | DER Forecast under N-1 Contingency (A) | 127 | 52 | 89 | 155 | 255
Gatton Bulk | 377-1 | Gatton BS | 377 Tee1 | NCC Rating (A) | 821 | 821 | 821 | 821 | 821
|  |  |  | DER Forecast under System Normal (A) | 6 | 14 | 22 | 29 | 35
|  |  |  | Power Factor | 0.84904 | 0.9758 | 0.99056 | 0.99506 | 0.99704
|  |  |  | ECC Rating (A) | 821 | 821 | 821 | 821 | 821
|  |  |  | DER Forecast under N-1 Contingency (A) | 26 | 41 | 55 | 67 | 78
Gatton Bulk | 377-2 | 377 Tee1 | 487 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under System Normal (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 4.5117e-05 | 4.5133e-05 | 4.5116e-05 | 4.5117e-05 | 4.5116e-05
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under N-1 Contingency (A) | 0 | 0 | 0 | 0 | 0
Gatton Bulk | 377-3 | 377 Tee1 | 377 Tee2 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under System Normal (A) | 6 | 14 | 22 | 29 | 35
|  |  |  | Power Factor | 0.87778 | 0.98134 | 0.99285 | 0.99632 | 0.99784
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under N-1 Contingency (A) | 26 | 41 | 55 | 67 | 78
Gatton Bulk | 377-4 | 377 Tee2 | Gatton | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under System Normal (A) | 6 | 14 | 22 | 29 | 35
|  |  |  | Power Factor | 0.93684 | 0.99124 | 0.99675 | 0.99838 | 0.99909
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under N-1 Contingency (A) | 26 | 41 | 55 | 67 | 78
Gatton Bulk | 377-5 | 377 Tee2 | Glenmore Grove | NCC Rating (A) | 355 | 355 | 355 | 355 | 355
|  |  |  | DER Forecast under System Normal (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 2.1626e-05 | 2.1626e-05 | 2.1626e-05 | 2.1626e-05 | 2.1626e-05
|  |  |  | ECC Rating (A) | 355 | 355 | 355 | 355 | 355
|  |  |  | DER Forecast under N-1 Contingency (A) | 1 | 1 | 1 | 1 | 1
Gatton Bulk | 3859-1 | Gatton BS | Springfield Central | NCC Rating (A) | 764 | 764 | 764 | 764 | 764
|  |  |  | DER Forecast under System Normal (A) | 3 | 4 | 7 | 8 | 10
|  |  |  | Power Factor | 0.36271 | 0.81591 | 0.92021 | 0.95509 | 0.97102
|  |  |  | ECC Rating (A) | 764 | 764 | 764 | 764 | 764
|  |  |  | DER Forecast under N-1 Contingency (A) | 3 | 8 | 12 | 16 | 20
Gatton Bulk | 3860-1 | Gatton BS | Springfield Central | NCC Rating (A) | 764 | 764 | 764 | 764 | 764
|  |  |  | DER Forecast under System Normal (A) | 3 | 4 | 7 | 8 | 10
|  |  |  | Power Factor | 0.36493 | 0.81778 | 0.92118 | 0.95568 | 0.97141
|  |  |  | ECC Rating (A) | 764 | 764 | 764 | 764 | 764
|  |  |  | DER Forecast under N-1 Contingency (A) | 3 | 8 | 12 | 16 | 20
Gatton Bulk | 487-1 | Gatton BS | 487 Tee1 | NCC Rating (A) | 821 | 821 | 821 | 821 | 821
|  |  |  | DER Forecast under System Normal (A) | 10 | 4 | 8 | 14 | 19
|  |  |  | Power Factor | 0.88223 | 0.066152 | 0.84532 | 0.9526 | 0.97755
|  |  |  | ECC Rating (A) | 821 | 821 | 821 | 821 | 821
|  |  |  | DER Forecast under N-1 Contingency (A) | 17 | 15 | 29 | 42 | 54
Gatton Bulk | 487-2 | 487 Tee1 | 377 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under System Normal (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 4.3534e-05 | 4.3561e-05 | 4.3569e-05 | 4.356e-05 | 4.3562e-05
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under N-1 Contingency (A) | 0 | 0 | 0 | 0 | 0
Gatton Bulk | 487-3 | 487 Tee1 | 487 Tee2 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under System Normal (A) | 9 | 4 | 8 | 14 | 19
|  |  |  | Power Factor | 0.89786 | 0.07206 | 0.86556 | 0.96006 | 0.98133
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under N-1 Contingency (A) | 17 | 15 | 29 | 42 | 54
Gatton Bulk | 487-6 | 487 Tee3 | 3844 Tee1 | NCC Rating (A) | 251 | 251 | 251 | 251 | 251
|  |  |  | DER Forecast under System Normal (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 3.3837e-05 | 3.3834e-05 | 3.3844e-05 | 3.3833e-05 | 3.384e-05
|  |  |  | ECC Rating (A) | 251 | 251 | 251 | 251 | 251
|  |  |  | DER Forecast under N-1 Contingency (A) | 0 | 0 | 0 | 0 | 0
Gatton Bulk | 487-8 | 487 Tee4 | 3844 Tee2 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under System Normal (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0.00046813 | 0.0004621 | 0.00046541 | 0.00046651 | 0.00046402
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under N-1 Contingency (A) | 0 | 0 | 0 | 0 | 0
Gatton Bulk | 487-9 | 487 Tee2 | Gatton | NCC Rating (A) | 713 | 713 | 713 | 713 | 713
|  |  |  | DER Forecast under System Normal (A) | 21 | 27 | 33 | 38 | 43
|  |  |  | Power Factor | 0.99928 | 0.99974 | 0.99991 | 0.99998 | 1
|  |  |  | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
|  |  |  | DER Forecast under N-1 Contingency (A) | 26 | 41 | 55 | 67 | 78
Gatton Bulk | 531-1 | Gatton | Tenthill | NCC Rating (A) | 154 | 154 | 154 | 154 | 154
|  |  |  | DER Forecast under System Normal (A) | 17 | 21 | 24 | 27 | 29
|  |  |  | Power Factor | 0.99898 | 0.99946 | 0.9997 | 0.99983 | 0.99991
|  |  |  | ECC Rating (A) | 154 | 154 | 154 | 154 | 154
|  |  |  | DER Forecast under N-1 Contingency (A) | 17 | 21 | 24 | 27 | 29
Gatton Bulk | 532-1 | Tenthill | 532 Tee1 | NCC Rating (A) | 208 | 208 | 208 | 208 | 208
|  |  |  | DER Forecast under System Normal (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 8.2565e-05 | 8.2568e-05 | 8.2634e-05 | 8.2537e-05 | 8.2567e-05
|  |  |  | ECC Rating (A) | 208 | 208 | 208 | 208 | 208
|  |  |  | DER Forecast under N-1 Contingency (A) | 0 | 0 | 0 | 0 | 0
Gatton Bulk | 533-1 | Tenthill | Mt Sylvia | NCC Rating (A) | 78 | 78 | 78 | 78 | 78
|  |  |  | DER Forecast under System Normal (A) | 3 | 4 | 4 | 5 | 6
|  |  |  | Power Factor | 0.99722 | 0.99845 | 0.99895 | 0.9992 | 0.99934
|  |  |  | ECC Rating (A) | 78 | 78 | 78 | 78 | 78
|  |  |  | DER Forecast under N-1 Contingency (A) | 3 | 4 | 4 | 5 | 6
Goodna Bulk | 3800-1 | Goodna BS | Cooneana | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under System Normal (A) | 57 | 41 | 73 | 108 | 149
|  |  |  | Power Factor | 0.99857 | 0.99933 | 0.99725 | 0.99297 | 0.9857
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under N-1 Contingency (A) | 120 | 88 | 155 | 229 | 316
Goodna Bulk | 3801-1 | Goodna BS | Carol Pk Central | NCC Rating (A) | 720 | 720 | 720 | 720 | 720
|  |  |  | DER Forecast under System Normal (A) | 14 | 24 | 9 | 21 | 42
|  |  |  | Power Factor | 0.38857 | 0.89414 | 0.15551 | 0.93589 | 0.96168
|  |  |  | ECC Rating (A) | 720 | 720 | 720 | 720 | 720
|  |  |  | DER Forecast under N-1 Contingency (A) | 29 | 54 | 43 | 73 | 109
Goodna Bulk | 3802-1 | Goodna BS | Springfield | NCC Rating (A) | 592 | 592 | 592 | 592 | 592
|  |  |  | DER Forecast under System Normal (A) | 102 | 165 | 249 | 339 | 441
|  |  |  | Power Factor | 0.99159 | 0.99906 | 0.99667 | 0.99307 | 0.98791
|  |  |  | ECC Rating (A) | 675 | 675 | 675 | 675 | 675
|  |  |  | DER Forecast under N-1 Contingency (A) | 198 | 323 | 487 | 663 | 862
Goodna Bulk | 3803-1 | Goodna BS | Carol Park | NCC Rating (A) | 502 | 502 | 502 | 502 | 502
|  |  |  | DER Forecast under System Normal (A) | 49 | 67 | 99 | 132 | 166
|  |  |  | Power Factor | 0.99559 | 0.99975 | 0.99852 | 0.99364 | 0.98615
|  |  |  | ECC Rating (A) | 502 | 502 | 502 | 502 | 502
|  |  |  | DER Forecast under N-1 Contingency (A) | 106 | 143 | 208 | 278 | 354
Goodna Bulk | 3805-1 | Goodna BS | Carol Park | NCC Rating (A) | 502 | 502 | 502 | 502 | 502
|  |  |  | DER Forecast under System Normal (A) | 45 | 61 | 91 | 121 | 152
|  |  |  | Power Factor | 0.99433 | 0.99938 | 0.99915 | 0.99503 | 0.98825
|  |  |  | ECC Rating (A) | 502 | 502 | 502 | 502 | 502
|  |  |  | DER Forecast under N-1 Contingency (A) | 97 | 131 | 190 | 254 | 324
Goodna Bulk | 3806-1 | Goodna BS | Springfield | NCC Rating (A) | 592 | 592 | 592 | 592 | 592
|  |  |  | DER Forecast under System Normal (A) | 101 | 164 | 248 | 338 | 439
|  |  |  | Power Factor | 0.99149 | 0.99905 | 0.99666 | 0.99307 | 0.98791
|  |  |  | ECC Rating (A) | 675 | 675 | 675 | 675 | 675
|  |  |  | DER Forecast under N-1 Contingency (A) | 198 | 323 | 487 | 663 | 862
Goodna Bulk | 3807-1 | Goodna BS | Redbank | NCC Rating (A) | 748 | 748 | 748 | 748 | 748
|  |  |  | DER Forecast under System Normal (A) | 91 | 99 | 96 | 94 | 92
|  |  |  | Power Factor | 0.99951 | 0.99947 | 0.99949 | 0.9995 | 0.9995
|  |  |  | ECC Rating (A) | 748 | 748 | 748 | 748 | 748
|  |  |  | DER Forecast under N-1 Contingency (A) | 91 | 99 | 96 | 94 | 92
Goodna Bulk | 3808-1 | Goodna BS | Carol Pk Central | NCC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | DER Forecast under System Normal (A) | 14 | 24 | 9 | 21 | 42
|  |  |  | Power Factor | 0.38792 | 0.89384 | 0.15478 | 0.93607 | 0.96163
|  |  |  | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | DER Forecast under N-1 Contingency (A) | 29 | 54 | 43 | 73 | 109
Goodna Bulk | 3809-1 | Goodna BS | Cooneana | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under System Normal (A) | 64 | 47 | 82 | 122 | 169
|  |  |  | Power Factor | 0.99833 | 0.99928 | 0.99695 | 0.99274 | 0.98573
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under N-1 Contingency (A) | 120 | 88 | 155 | 229 | 317
Goodna Bulk | 3880-1 | Carol Park | Springfield Central | NCC Rating (A) | 742 | 742 | 742 | 742 | 742
|  |  |  | DER Forecast under System Normal (A) | 139 | 185 | 257 | 333 | 413
|  |  |  | Power Factor | 0.99671 | 0.99506 | 0.99125 | 0.98602 | 0.97897
|  |  |  | ECC Rating (A) | 742 | 742 | 742 | 742 | 742
|  |  |  | DER Forecast under N-1 Contingency (A) | 290 | 385 | 543 | 717 | 910
Goodna Bulk | 3881-1 | Springfield | Springfield Central | NCC Rating (A) | 742 | 742 | 742 | 742 | 742
|  |  |  | DER Forecast under System Normal (A) | 150 | 197 | 274 | 353 | 438
|  |  |  | Power Factor | 0.99857 | 0.99672 | 0.99262 | 0.98683 | 0.97891
|  |  |  | ECC Rating (A) | 742 | 742 | 742 | 742 | 742
|  |  |  | DER Forecast under N-1 Contingency (A) | 290 | 386 | 543 | 713 | 902
Goodna Bulk | 456-1 | Wacol Sth | 456 Tee1 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under System Normal (A) | 42 | 62 | 81 | 100 | 120
|  |  |  | Power Factor | 0.99981 | 0.99965 | 0.99648 | 0.99055 | 0.98159
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under N-1 Contingency (A) | 81 | 114 | 155 | 200 | 249
Goodna Bulk | 456-2 | 456 Tee1 | Carol Pk Central | NCC Rating (A) | 441 | 441 | 441 | 441 | 441
|  |  |  | DER Forecast under System Normal (A) | 42 | 62 | 81 | 100 | 120
|  |  |  | Power Factor | 0.99932 | 0.99965 | 0.99644 | 0.99043 | 0.98135
|  |  |  | ECC Rating (A) | 441 | 441 | 441 | 441 | 441
|  |  |  | DER Forecast under N-1 Contingency (A) | 81 | 114 | 155 | 200 | 249
Goodna Bulk | 456-3 | 456 Tee1 | Carol Pk | NCC Rating (A) | 441 | 441 | 441 | 441 | 441
|  |  |  | DER Forecast under System Normal (A) | 42 | 62 | 81 | 100 | 120
|  |  |  | Power Factor | 0.99994 | 0.99908 | 0.9954 | 0.98926 | 0.98023
|  |  |  | ECC Rating (A) | 441 | 441 | 441 | 441 | 441
|  |  |  | DER Forecast under N-1 Contingency (A) | 81 | 115 | 156 | 200 | 250
Griffin Bulk | 312-1 | Kallangur | Narangba | NCC Rating (A) | 422 | 422 | 422 | 422 | 422
|  |  |  | DER Forecast under System Normal (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 1.4388e-05 | 1.4388e-05 | 1.4388e-05 | 1.4388e-05 | 1.4388e-05
|  |  |  | ECC Rating (A) | 422 | 422 | 422 | 422 | 422
|  |  |  | DER Forecast under N-1 Contingency (A) | 1 | 1 | 1 | 1 | 1
Griffin Bulk | 320-1 | Griffin BS | 320 Tee1 | NCC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | DER Forecast under System Normal (A) | 33 | 65 | 94 | 99 | 131
|  |  |  | Power Factor | 0.99409 | 0.99764 | 0.99661 | 0.99064 | 0.98915
|  |  |  | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | DER Forecast under N-1 Contingency (A) | 55 | 100 | 139 | 158 | 210
Griffin Bulk | 320-2 | 320 Tee1 | Mango Hill Bus 2 | NCC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | DER Forecast under System Normal (A) | 4 | 36 | 72 | 119 | 160
|  |  |  | Power Factor | 0.97002 | 0.99547 | 0.99136 | 0.98913 | 0.98505
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | DER Forecast under N-1 Contingency (A) | 20 | 82 | 146 | 215 | 288
Griffin Bulk | 320-3 | 320 Tee1 | Kalangur | NCC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | DER Forecast under System Normal (A) | 29 | 29 | 22 | 21 | 30
|  |  |  | Power Factor | 0.99615 | 0.99919 | 0.99689 | 0.97988 | 0.95823
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | DER Forecast under N-1 Contingency (A) | 59 | 75 | 81 | 58 | 79
Griffin Bulk | 3329-1 | Griffin BS | 3329 Tee1 | NCC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | DER Forecast under System Normal (A) | 52 | 80 | 101 | 73 | 95
|  |  |  | Power Factor | 0.98963 | 0.99793 | 0.99975 | 0.98781 | 0.98607
|  |  |  | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | DER Forecast under N-1 Contingency (A) | 86 | 123 | 150 | 184 | 211
Griffin Bulk | 3329-2 | 3329 Tee1 | 3330 Tee1 | NCC Rating (A) | 748 | 748 | 748 | 748 | 748
|  |  |  | DER Forecast under System Normal (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 6.7995e-06 | 6.8e-06 | 6.7991e-06 | 6.7992e-06 | 6.7993e-06
|  |  |  | ECC Rating (A) | 748 | 748 | 748 | 748 | 748
|  |  |  | DER Forecast under N-1 Contingency (A) | 0 | 0 | 0 | 0 | 0
Griffin Bulk | 3329-3 | 3329 Tee1 | Kallangur | NCC Rating (A) | 711 | 711 | 711 | 711 | 711
|  |  |  | DER Forecast under System Normal (A) | 52 | 80 | 101 | 74 | 96
|  |  |  | Power Factor | 0.99866 | 0.99998 | 0.99971 | 0.97895 | 0.97933
|  |  |  | ECC Rating (A) | 711 | 711 | 711 | 711 | 711
|  |  |  | DER Forecast under N-1 Contingency (A) | 86 | 123 | 150 | 184 | 211
Griffin Bulk | 3330-1 | Griffin BS | 3330 Tee1 | NCC Rating (A) | 717 | 717 | 717 | 717 | 717
|  |  |  | DER Forecast under System Normal (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0.00011645 | 0.00011657 | 0.00011661 | 0.00011649 | 0.00011649
|  |  |  | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
|  |  |  | DER Forecast under N-1 Contingency (A) | 0 | 0 | 0 | 0 | 0
Griffin Bulk | 3330-2 | 3330 Tee1 | 3329 Tee1 | NCC Rating (A) | 523 | 523 | 523 | 523 | 523
|  |  |  | DER Forecast under System Normal (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 2.7955e-05 | 2.7959e-05 | 2.796e-05 | 2.7959e-05 | 2.7968e-05
|  |  |  | ECC Rating (A) | 523 | 523 | 523 | 523 | 523
|  |  |  | DER Forecast under N-1 Contingency (A) | 0 | 0 | 0 | 0 | 0
Griffin Bulk | 3330-3 | 3330 Tee1 | APM | NCC Rating (A) | 717 | 717 | 717 | 717 | 717
|  |  |  | DER Forecast under System Normal (A) | 21 | 35 | 45 | 42 | 35
|  |  |  | Power Factor | 0.99824 | 0.99937 | 0.99765 | 0.94782 | 0.89229
|  |  |  | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
|  |  |  | DER Forecast under N-1 Contingency (A) | 42 | 68 | 87 | 47 | 41
Griffin Bulk | 3331-1 | 3331 Tee1 | Kallangur | NCC Rating (A) | 717 | 717 | 717 | 717 | 717
|  |  |  | DER Forecast under System Normal (A) | 58 | 72 | 83 | 189 | 198
|  |  |  | Power Factor | 0.9984 | 0.99759 | 0.99655 | 1 | 0.99996
|  |  |  | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
|  |  |  | DER Forecast under N-1 Contingency (A) | 79 | 106 | 125 | 216 | 233
Griffin Bulk | 3331-3 | APM | 3331 Tee1 | NCC Rating (A) | 717 | 717 | 717 | 717 | 717
|  |  |  | DER Forecast under System Normal (A) | 21 | 35 | 45 | 151 | 160
|  |  |  | Power Factor | 0.99969 | 0.99932 | 0.9976 | 0.99965 | 0.99994
|  |  |  | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
|  |  |  | DER Forecast under N-1 Contingency (A) | 42 | 68 | 87 | 179 | 196
Griffin Bulk | 3359-1 | 3359 Tee1 | Hays Inlet | NCC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | DER Forecast under System Normal (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 1.0514e-06 | 1.0528e-06 | 1.0519e-06 | 1.0527e-06 | 1.0521e-06
|  |  |  | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | DER Forecast under N-1 Contingency (A) | 0 | 0 | 0 | 0 | 0
Griffin Bulk | 3359-2 | 3359 Tee1 | 3359 Tee2 | NCC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | DER Forecast under System Normal (A) | 17 | 46 | 76 | 98 | 131
|  |  |  | Power Factor | 0.99668 | 0.99632 | 0.99676 | 0.99713 | 0.99832
|  |  |  | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | DER Forecast under N-1 Contingency (A) | 24 | 82 | 147 | 216 | 289
Griffin Bulk | 3359-3 | 3359 Tee2 | 3359 Tee3 | NCC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | DER Forecast under System Normal (A) | 17 | 46 | 76 | 98 | 131
|  |  |  | Power Factor | 0.99719 | 0.9965 | 0.99686 | 0.9972 | 0.99835
|  |  |  | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | DER Forecast under N-1 Contingency (A) | 24 | 82 | 147 | 216 | 289
Griffin Bulk | 3359-4 | 3359 Tee3 | Mango Hill Bus 2 | NCC Rating (A) | 762 | 762 | 762 | 762 | 762
|  |  |  | DER Forecast under System Normal (A) | 17 | 46 | 76 | 98 | 131
|  |  |  | Power Factor | 0.99901 | 0.9976 | 0.99742 | 0.99754 | 0.99846
|  |  |  | ECC Rating (A) | 762 | 762 | 762 | 762 | 762
|  |  |  | DER Forecast under N-1 Contingency (A) | 24 | 82 | 147 | 216 | 289
Griffin Bulk | 3359-5 | 3359 Tee2 | P51001-D | NCC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | DER Forecast under System Normal (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 6.7086e-06 | 6.7087e-06 | 6.7087e-06 | 6.7087e-06 | 6.7088e-06
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | DER Forecast under N-1 Contingency (A) | 0 | 0 | 0 | 0 | 0
Griffin Bulk | 3359-6 | 3359 Tee3 | X18574-E | NCC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | DER Forecast under System Normal (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 3.3931e-06 | 3.3931e-06 | 3.3931e-06 | 3.3931e-06 | 3.3931e-06
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | DER Forecast under N-1 Contingency (A) | 0 | 0 | 0 | 0 | 0
Griffin Bulk | 3359-7 | Griffin BS | 3359 Tee1 | NCC Rating (A) | 703 | 703 | 703 | 703 | 703
|  |  |  | DER Forecast under System Normal (A) | 17 | 46 | 76 | 98 | 132
|  |  |  | Power Factor | 0.99457 | 0.99583 | 0.99675 | 0.99734 | 0.99866
|  |  |  | ECC Rating (A) | 703 | 703 | 703 | 703 | 703
|  |  |  | DER Forecast under N-1 Contingency (A) | 24 | 82 | 147 | 216 | 289
Griffin Bulk | 338-1 | Griffin BS | Strathpine | NCC Rating (A) | 348 | 348 | 348 | 348 | 348
|  |  |  | DER Forecast under System Normal (A) | 2 | 2 | 2 | 2 | 2
|  |  |  | Power Factor | 0.00011716 | 0.00011716 | 0.00011716 | 0.00011716 | 0.00011716
|  |  |  | ECC Rating (A) | 348 | 348 | 348 | 348 | 348
|  |  |  | DER Forecast under N-1 Contingency (A) | 2 | 2 | 2 | 2 | 2
Gympie Bulk | 3004-1 | Coondoo Ck Reg | Tin Can Bay | NCC Rating (A) | 127 | 127 | 127 | 127 | 127
|  |  |  | DER Forecast under System Normal (A) | 24 | 29 | 34 | 38 | 42
|  |  |  | Power Factor | 1 | 0.99993 | 0.99983 | 0.99969 | 0.99957
|  |  |  | ECC Rating (A) | 127 | 127 | 127 | 127 | 127
|  |  |  | DER Forecast under N-1 Contingency (A) | 24 | 29 | 34 | 38 | 42
Gympie Bulk | 3005-1 | Coondoo Ck Reg | Tin Can Bay | NCC Rating (A) | 582 | 582 | 582 | 582 | 582
|  |  |  | DER Forecast under System Normal (A) | 24 | 30 | 34 | 39 | 43
|  |  |  | Power Factor | 0.99965 | 0.99958 | 0.99948 | 0.9994 | 0.99931
|  |  |  | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
|  |  |  | DER Forecast under N-1 Contingency (A) | 24 | 30 | 34 | 39 | 43
Gympie Bulk | 3009-1 | Gympie BS | Gympie Nth | NCC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | DER Forecast under System Normal (A) | 31 | 42 | 53 | 64 | 73
|  |  |  | Power Factor | 0.9251 | 0.9647 | 0.98006 | 0.98758 | 0.99191
|  |  |  | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | DER Forecast under N-1 Contingency (A) | 58 | 83 | 105 | 126 | 146
Gympie Bulk | 3011-1 | Gympie BS | Gympie Nth | NCC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | DER Forecast under System Normal (A) | 31 | 42 | 54 | 64 | 73
|  |  |  | Power Factor | 0.92519 | 0.96474 | 0.98009 | 0.9876 | 0.99193
|  |  |  | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | DER Forecast under N-1 Contingency (A) | 58 | 83 | 105 | 126 | 146
Gympie Bulk | 339/2-1 | Amamoor | 339 Tee1 | NCC Rating (A) | 155 | 155 | 403 | 403 | 403
|  |  |  | DER Forecast under System Normal (A) | 6 | 3 | 1 | 2 | 3
|  |  |  | Power Factor | 0.99308 | 0.97732 | 0.66545 | 0.92969 | 0.98704
|  |  |  | ECC Rating (A) | 155 | 155 | 403 | 403 | 403
|  |  |  | DER Forecast under N-1 Contingency (A) | 6 | 3 | 1 | 2 | 3
Gympie Bulk | 339/2-2 | 339 Tee1 | Imbil | NCC Rating (A) | 200 | 200 | 200 | 200 | 200
|  |  |  | DER Forecast under System Normal (A) | 6 | 9 | 11 | 13 | 15
|  |  |  | Power Factor | 0.99981 | 0.99986 | 0.99986 | 0.99985 | 0.99984
|  |  |  | ECC Rating (A) | 200 | 200 | 200 | 200 | 200
|  |  |  | DER Forecast under N-1 Contingency (A) | 6 | 9 | 11 | 13 | 15
Gympie Bulk | 339/2-5 | 339 Tee2 | 340 Tee2 | NCC Rating (A) | 155 | 155 | 403 | 403 | 403
|  |  |  | DER Forecast under System Normal (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 3.5511e-06 | 3.5511e-06 | 2.4497e-06 | 2.4497e-06 | 2.4497e-06
|  |  |  | ECC Rating (A) | 155 | 155 | 403 | 403 | 403
|  |  |  | DER Forecast under N-1 Contingency (A) | 0 | 0 | 0 | 0 | 0
Gympie Bulk | 339-1 | Gympie BS | 339 Tee1 | NCC Rating (A) | 210 | 210 | 210 | 210 | 210
|  |  |  | DER Forecast under System Normal (A) | 14 | 26 | 38 | 50 | 61
|  |  |  | Power Factor | 0.99353 | 0.99933 | 0.99999 | 0.99974 | 0.9992
|  |  |  | ECC Rating (A) | 210 | 210 | 210 | 210 | 210
|  |  |  | DER Forecast under N-1 Contingency (A) | 14 | 26 | 38 | 50 | 61
Gympie Bulk | 339-2 | 339 Tee1 | Amamoor | NCC Rating (A) | 210 | 210 | 210 | 210 | 210
|  |  |  | DER Forecast under System Normal (A) | 14 | 26 | 38 | 50 | 61
|  |  |  | Power Factor | 0.99573 | 0.99966 | 0.9999 | 0.99969 | 0.99921
|  |  |  | ECC Rating (A) | 210 | 210 | 210 | 210 | 210
|  |  |  | DER Forecast under N-1 Contingency (A) | 14 | 26 | 38 | 50 | 61
Gympie Bulk | 339-3 | 339 Tee1 | 340 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under System Normal (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0.00059009 | 0.00059174 | 0.00059377 | 0.00059177 | 0.00059854
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under N-1 Contingency (A) | 0 | 0 | 0 | 0 | 0
Gympie Bulk | 340-1 | Gympie BS | 340 Tee1 | NCC Rating (A) | 349 | 349 | 349 | 349 | 349
|  |  |  | DER Forecast under System Normal (A) | 5 | 4 | 3 | 2 | 2
|  |  |  | Power Factor | 0.90808 | 0.89648 | 0.73839 | 0.28849 | 0.36631
|  |  |  | ECC Rating (A) | 349 | 349 | 349 | 349 | 349
|  |  |  | DER Forecast under N-1 Contingency (A) | 10 | 9 | 6 | 4 | 4
Gympie Bulk | 340-2 | 340 Tee1 | 339 Tee1 | NCC Rating (A) | 349 | 349 | 349 | 349 | 349
|  |  |  | DER Forecast under System Normal (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0.00010582 | 0.0001059 | 0.00010574 | 0.00010566 | 0.00010571
|  |  |  | ECC Rating (A) | 349 | 349 | 349 | 349 | 349
|  |  |  | DER Forecast under N-1 Contingency (A) | 0 | 0 | 0 | 0 | 0
Gympie Bulk | 340-4 | 340 Tee1 | 340 Tee2 | NCC Rating (A) | 349 | 349 | 349 | 349 | 349
|  |  |  | DER Forecast under System Normal (A) | 5 | 4 | 3 | 2 | 2
|  |  |  | Power Factor | 0.90835 | 0.89677 | 0.73896 | 0.28894 | 0.36686
|  |  |  | ECC Rating (A) | 349 | 349 | 349 | 349 | 349
|  |  |  | DER Forecast under N-1 Contingency (A) | 10 | 9 | 6 | 4 | 4
Gympie Bulk | 340-5 | 340 Tee2 | 340 Tee3 | NCC Rating (A) | 328 | 328 | 328 | 328 | 328
|  |  |  | DER Forecast under System Normal (A) | 3 | 3 | 3 | 3 | 3
|  |  |  | Power Factor | 0.00072412 | 0.00072412 | 0.00072412 | 0.00072412 | 0.00072412
|  |  |  | ECC Rating (A) | 328 | 328 | 328 | 328 | 328
|  |  |  | DER Forecast under N-1 Contingency (A) | 3 | 3 | 3 | 3 | 3
Gympie Bulk | 340-6 | 340 Tee3 | 339 Tee2 | NCC Rating (A) | 208 | 208 | 208 | 208 | 208
|  |  |  | DER Forecast under System Normal (A) | 2 | 2 | 2 | 2 | 2
|  |  |  | Power Factor | 0.00013902 | 0.00013902 | 0.00013902 | 0.00013902 | 0.00013902
|  |  |  | ECC Rating (A) | 208 | 208 | 208 | 208 | 208
|  |  |  | DER Forecast under N-1 Contingency (A) | 2 | 2 | 2 | 2 | 2
Gympie Bulk | 340-7 | 339 Tee2 | Kenilworth | NCC Rating (A) | 208 | 208 | 208 | 208 | 208
|  |  |  | DER Forecast under System Normal (A) | 2 | 2 | 2 | 2 | 2
|  |  |  | Power Factor | 0.00013861 | 0.00013861 | 0.00013861 | 0.00013861 | 0.00013861
|  |  |  | ECC Rating (A) | 208 | 208 | 208 | 208 | 208
|  |  |  | DER Forecast under N-1 Contingency (A) | 2 | 2 | 2 | 2 | 2
Gympie Bulk | 340-8 | 340 Tee3 | Black Mountain | NCC Rating (A) | 328 | 328 | 328 | 328 | 328
|  |  |  | DER Forecast under System Normal (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 1.7204e-05 | 1.7204e-05 | 1.7204e-05 | 1.7204e-05 | 1.7204e-05
|  |  |  | ECC Rating (A) | 328 | 328 | 328 | 328 | 328
|  |  |  | DER Forecast under N-1 Contingency (A) | 1 | 1 | 1 | 1 | 1
Gympie Bulk | 340-9 | 340 Tee2 | Gympie South | NCC Rating (A) | 403 | 403 | 403 | 403 | 403
|  |  |  | DER Forecast under System Normal (A) | 5 | 4 | 3 | 2 | 2
|  |  |  | Power Factor | 0.91567 | 0.91444 | 0.77379 | 0.31578 | 0.39799
|  |  |  | ECC Rating (A) | 403 | 403 | 403 | 403 | 403
|  |  |  | DER Forecast under N-1 Contingency (A) | 9 | 9 | 5 | 2 | 2
Gympie Bulk | 341-1 | Gympie BS | 341 Tee1 | NCC Rating (A) | 211 | 211 | 211 | 211 | 211
|  |  |  | DER Forecast under System Normal (A) | 8 | 14 | 18 | 22 | 26
|  |  |  | Power Factor | 0.99097 | 0.99413 | 0.99126 | 0.98918 | 0.98761
|  |  |  | ECC Rating (A) | 211 | 211 | 211 | 211 | 211
|  |  |  | DER Forecast under N-1 Contingency (A) | 8 | 18 | 28 | 36 | 43
Gympie Bulk | 341-3 | 341 Tee1 | Coondoo Ck Reg | NCC Rating (A) | 210 | 210 | 210 | 210 | 210
|  |  |  | DER Forecast under System Normal (A) | 48 | 59 | 68 | 77 | 84
|  |  |  | Power Factor | 0.9998 | 0.99999 | 0.99998 | 0.99988 | 0.99974
|  |  |  | ECC Rating (A) | 210 | 210 | 210 | 210 | 210
|  |  |  | DER Forecast under N-1 Contingency (A) | 48 | 59 | 68 | 77 | 84
Gympie Bulk | 341-4 | Coondoo Ck Reg | 341 Tee2 | NCC Rating (A) | 717 | 717 | 717 | 717 | 717
|  |  |  | DER Forecast under System Normal (A) | 48 | 59 | 68 | 77 | 84
|  |  |  | Power Factor | 0.99981 | 0.99999 | 0.99998 | 0.99989 | 0.99976
|  |  |  | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
|  |  |  | DER Forecast under N-1 Contingency (A) | 48 | 59 | 68 | 77 | 84
Gympie Bulk | 351-1 | Gympie BS | Gympie Sth | NCC Rating (A) | 355 | 355 | 355 | 355 | 355
|  |  |  | DER Forecast under System Normal (A) | 5 | 5 | 3 | 2 | 2
|  |  |  | Power Factor | 0.92989 | 0.9306 | 0.80655 | 0.35921 | 0.41342
|  |  |  | ECC Rating (A) | 355 | 355 | 355 | 355 | 355
|  |  |  | DER Forecast under N-1 Contingency (A) | 9 | 9 | 5 | 2 | 2
Gympie Bulk | 429-1 | Gympie BS | 429 Tee1 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under System Normal (A) | 17 | 25 | 31 | 37 | 42
|  |  |  | Power Factor | 0.97516 | 0.98672 | 0.9914 | 0.99393 | 0.99549
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under N-1 Contingency (A) | 23 | 25 | 31 | 37 | 42
Gympie Bulk | 429-2 | 429 Tee1 | Goomboorian | NCC Rating (A) | 461 | 461 | 461 | 461 | 461
|  |  |  | DER Forecast under System Normal (A) | 18 | 20 | 21 | 23 | 24
|  |  |  | Power Factor | 0.99987 | 0.99985 | 0.99984 | 0.99982 | 0.99981
|  |  |  | ECC Rating (A) | 461 | 461 | 461 | 461 | 461
|  |  |  | DER Forecast under N-1 Contingency (A) | 18 | 20 | 21 | 23 | 24
Hays Inlet Bulk | 305-1 | Hays Inlet BS | Deception Bay | NCC Rating (A) | 759 | 759 | 759 | 759 | 759
|  |  |  | DER Forecast under System Normal (A) | 167 | 207 | 241 | 271 | 297
|  |  |  | Power Factor | 0.99967 | 0.99999 | 0.9999 | 0.99968 | 0.9994
|  |  |  | ECC Rating (A) | 759 | 759 | 759 | 759 | 759
|  |  |  | DER Forecast under N-1 Contingency (A) | 275 | 339 | 393 | 440 | 483
Hays Inlet Bulk | 311-1 | Hays Inlet BS | Deception Bay | NCC Rating (A) | 623 | 623 | 623 | 623 | 623
|  |  |  | DER Forecast under System Normal (A) | 55 | 68 | 80 | 90 | 98
|  |  |  | Power Factor | 0.99853 | 0.99754 | 0.99659 | 0.99573 | 0.99489
|  |  |  | ECC Rating (A) | 623 | 623 | 623 | 623 | 623
|  |  |  | DER Forecast under N-1 Contingency (A) | 184 | 227 | 265 | 297 | 327
Hays Inlet Bulk | 3250-1 | Deception Bay | Burpengary | NCC Rating (A) | 713 | 713 | 713 | 713 | 713
|  |  |  | DER Forecast under System Normal (A) | 128 | 155 | 178 | 197 | 215
|  |  |  | Power Factor | 0.99915 | 0.99858 | 0.99802 | 0.99748 | 0.99694
|  |  |  | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
|  |  |  | DER Forecast under N-1 Contingency (A) | 272 | 330 | 380 | 423 | 463
Hays Inlet Bulk | 325-1 | Hays Inlet BS | Scarborough | NCC Rating (A) | 529 | 529 | 529 | 529 | 529
|  |  |  | DER Forecast under System Normal (A) | 32 | 65 | 97 | 113 | 131
|  |  |  | Power Factor | 0.99622 | 0.99667 | 0.99587 | 0.99309 | 0.98911
|  |  |  | ECC Rating (A) | 529 | 529 | 529 | 529 | 529
|  |  |  | DER Forecast under N-1 Contingency (A) | 112 | 173 | 235 | 299 | 368
Hays Inlet Bulk | 3251-1 | Burpengary | Morayfield | NCC Rating (A) | 464 | 464 | 464 | 464 | 464
|  |  |  | DER Forecast under System Normal (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 1.0517e-05 | 1.0517e-05 | 1.0517e-05 | 1.0517e-05 | 1.0517e-05
|  |  |  | ECC Rating (A) | 464 | 464 | 464 | 464 | 464
|  |  |  | DER Forecast under N-1 Contingency (A) | 1 | 1 | 1 | 1 | 1
Hays Inlet Bulk | 326-1 | Redcliffe | Scarborough | NCC Rating (A) | 322 | 322 | 322 | 322 | 322
|  |  |  | DER Forecast under System Normal (A) | 80 | 109 | 139 | 188 | 241
|  |  |  | Power Factor | 0.99999 | 0.99999 | 0.99992 | 0.99979 | 0.99962
|  |  |  | ECC Rating (A) | 322 | 322 | 322 | 322 | 322
|  |  |  | DER Forecast under N-1 Contingency (A) | 112 | 173 | 236 | 300 | 370
Hays Inlet Bulk | 327-1 | Hays Inlet BS | Mango Hill Bus 1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under System Normal (A) | 203 | 272 | 347 | 427 | 513
|  |  |  | Power Factor | 0.99461 | 0.99016 | 0.98396 | 0.97552 | 0.96602
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under N-1 Contingency (A) | 203 | 272 | 347 | 427 | 513
Hays Inlet Bulk | 329-1 | Redcliffe | Duffield Rd | NCC Rating (A) | 578 | 578 | 578 | 578 | 578
|  |  |  | DER Forecast under System Normal (A) | 17 | 2 | 14 | 10 | 9
|  |  |  | Power Factor | 0.99942 | 0.90585 | 0.99298 | 0.91962 | 0.60527
|  |  |  | ECC Rating (A) | 578 | 578 | 578 | 578 | 578
|  |  |  | DER Forecast under N-1 Contingency (A) | 58 | 57 | 63 | 85 | 115
Hays Inlet Bulk | 330-1 | Hays Inlet BS | Duffield Rd | NCC Rating (A) | 543 | 543 | 543 | 543 | 543
|  |  |  | DER Forecast under System Normal (A) | 19 | 35 | 50 | 53 | 56
|  |  |  | Power Factor | 0.99894 | 0.99916 | 0.99902 | 0.99769 | 0.99511
|  |  |  | ECC Rating (A) | 543 | 543 | 543 | 543 | 543
|  |  |  | DER Forecast under N-1 Contingency (A) | 30 | 55 | 79 | 84 | 89
Hays Inlet Bulk | 331-1 | Hays Inlet BS | Duffield Rd | NCC Rating (A) | 543 | 543 | 543 | 543 | 543
|  |  |  | DER Forecast under System Normal (A) | 19 | 35 | 50 | 54 | 57
|  |  |  | Power Factor | 0.99961 | 0.99972 | 0.99963 | 0.99871 | 0.99665
|  |  |  | ECC Rating (A) | 543 | 543 | 543 | 543 | 543
|  |  |  | DER Forecast under N-1 Contingency (A) | 30 | 56 | 79 | 84 | 89
Hays Inlet Bulk | 332-1 | Hays Inlet BS | Redcliffe | NCC Rating (A) | 524 | 524 | 524 | 524 | 524
|  |  |  | DER Forecast under System Normal (A) | 6 | 28 | 50 | 50 | 51
|  |  |  | Power Factor | 1 | 1 | 0.99995 | 0.99832 | 0.99203
|  |  |  | ECC Rating (A) | 524 | 524 | 524 | 524 | 524
|  |  |  | DER Forecast under N-1 Contingency (A) | 34 | 61 | 99 | 106 | 116
Hays Inlet Bulk | 451-1 | Narangba | Burpengary | NCC Rating (A) | 422 | 422 | 422 | 422 | 422
|  |  |  | DER Forecast under System Normal (A) | 11 | 15 | 18 | 22 | 26
|  |  |  | Power Factor | 0.95787 | 0.96115 | 0.96194 | 0.96158 | 0.96162
|  |  |  | ECC Rating (A) | 422 | 422 | 422 | 422 | 422
|  |  |  | DER Forecast under N-1 Contingency (A) | 155 | 191 | 222 | 249 | 275
Hays Inlet Bulk | 497-1 | Hays Inlet BS | Narangba | NCC Rating (A) | 713 | 713 | 713 | 713 | 713
|  |  |  | DER Forecast under System Normal (A) | 146 | 179 | 207 | 231 | 253
|  |  |  | Power Factor | 0.99953 | 0.99904 | 0.99851 | 0.99798 | 0.99741
|  |  |  | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
|  |  |  | DER Forecast under N-1 Contingency (A) | 273 | 331 | 382 | 425 | 464
Jimboomba Bulk | 470-1 | Jimboomba BS | Logan Village | NCC Rating (A) | 512 | 512 | 512 | 512 | 512
|  |  |  | DER Forecast under System Normal (A) | 144 | 235 | 328 | 424 | 519
|  |  |  | Power Factor | 0.99746 | 0.99316 | 0.98661 | 0.97863 | 0.96909
|  |  |  | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
|  |  |  | DER Forecast under N-1 Contingency (A) | 144 | 235 | 328 | 424 | 519
Jimboomba Bulk | 479-1 | Jimboomba BS | Nth Maclean | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under System Normal (A) | 425 | 572 | 735 | 911 | 1114
|  |  |  | Power Factor | 0.99312 | 0.98803 | 0.98005 | 0.97012 | 0.95796
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under N-1 Contingency (A) | 425 | 572 | 735 | 911 | 1114
Lockrose Bulk | 378-1 | Lockrose BS | 378 Tee1 | NCC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | DER Forecast under System Normal (A) | 32 | 41 | 35 | 44 | 52
|  |  |  | Power Factor | 0.99615 | 0.99752 | 0.99737 | 0.99831 | 0.99888
|  |  |  | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | DER Forecast under N-1 Contingency (A) | 53 | 69 | 54 | 68 | 80
Lockrose Bulk | 378-2 | 378 Tee1 | Glenmore Grove | NCC Rating (A) | 442 | 442 | 442 | 442 | 442
|  |  |  | DER Forecast under System Normal (A) | 12 | 14 | 18 | 21 | 25
|  |  |  | Power Factor | 0.99994 | 0.99993 | 0.9999 | 0.99986 | 0.99982
|  |  |  | ECC Rating (A) | 442 | 442 | 442 | 442 | 442
|  |  |  | DER Forecast under N-1 Contingency (A) | 12 | 14 | 18 | 21 | 25
Lockrose Bulk | 378-3 | 378 Tee1 | 378 Tee2 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under System Normal (A) | 20 | 27 | 18 | 22 | 27
|  |  |  | Power Factor | 0.99166 | 0.99454 | 0.98965 | 0.99277 | 0.99451
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under N-1 Contingency (A) | 42 | 55 | 36 | 46 | 55
Lockrose Bulk | 378-4 | 378 Tee2 | 532 Tee1 | NCC Rating (A) | 200 | 200 | 200 | 200 | 200
|  |  |  | DER Forecast under System Normal (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 6.0726e-05 | 6.0726e-05 | 6.0726e-05 | 6.0726e-05 | 6.0726e-05
|  |  |  | ECC Rating (A) | 200 | 200 | 200 | 200 | 200
|  |  |  | DER Forecast under N-1 Contingency (A) | 1 | 1 | 1 | 1 | 1
Lockrose Bulk | 378-5 | 378 Tee2 | Laidley | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under System Normal (A) | 20 | 27 | 17 | 22 | 27
|  |  |  | Power Factor | 0.99945 | 0.99941 | 0.99952 | 0.99943 | 0.99941
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under N-1 Contingency (A) | 42 | 55 | 36 | 46 | 55
Lockrose Bulk | 380-1 | Murrumba | 380 Tee1 | NCC Rating (A) | 200 | 200 | 200 | 200 | 200
|  |  |  | DER Forecast under System Normal (A) | 10 | 11 | 12 | 12 | 13
|  |  |  | Power Factor | 0.99131 | 0.99435 | 0.99599 | 0.99726 | 0.99696
|  |  |  | ECC Rating (A) | 200 | 200 | 200 | 200 | 200
|  |  |  | DER Forecast under N-1 Contingency (A) | 34 | 39 | 44 | 48 | 52
Lockrose Bulk | 380-2 | 380 Tee1 | Somerset Dam | NCC Rating (A) | 160 | 160 | 160 | 160 | 160
|  |  |  | DER Forecast under System Normal (A) | 1 | 2 | 2 | 2 | 3
|  |  |  | Power Factor | 0.99909 | 0.99955 | 0.99972 | 0.99981 | 0.99986
|  |  |  | ECC Rating (A) | 160 | 160 | 160 | 160 | 160
|  |  |  | DER Forecast under N-1 Contingency (A) | 1 | 2 | 2 | 2 | 3
Lockrose Bulk | 380-3 | 380 Tee1 | Toogoolahwah | NCC Rating (A) | 200 | 200 | 200 | 200 | 200
|  |  |  | DER Forecast under System Normal (A) | 9 | 10 | 10 | 10 | 11
|  |  |  | Power Factor | 0.99554 | 0.99534 | 0.99526 | 0.97357 | 0.97356
|  |  |  | ECC Rating (A) | 200 | 200 | 200 | 200 | 200
|  |  |  | DER Forecast under N-1 Contingency (A) | 33 | 38 | 42 | 46 | 49
Lockrose Bulk | 381-1 | Lockrose BS | 381 Tee1 | NCC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | DER Forecast under System Normal (A) | 10 | 15 | 19 | 23 | 26
|  |  |  | Power Factor | 0.93387 | 0.9722 | 0.98405 | 0.98884 | 0.99191
|  |  |  | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | DER Forecast under N-1 Contingency (A) | 25 | 34 | 42 | 49 | 54
Lockrose Bulk | 381-2 | 381 Tee1 | 382 Tee1 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under System Normal (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 3.3472e-05 | 3.348e-05 | 3.3488e-05 | 3.348e-05 | 3.3491e-05
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under N-1 Contingency (A) | 0 | 0 | 0 | 0 | 0
Lockrose Bulk | 381-3 | 381 Tee1 | 381 Tee2 | NCC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | DER Forecast under System Normal (A) | 10 | 15 | 19 | 23 | 26
|  |  |  | Power Factor | 0.93565 | 0.97298 | 0.9845 | 0.98914 | 0.99213
|  |  |  | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | DER Forecast under N-1 Contingency (A) | 25 | 34 | 42 | 49 | 54
Lockrose Bulk | 381-4 | 381 Tee2 | 383 Tee1 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under System Normal (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 3.3881e-05 | 3.3875e-05 | 3.3863e-05 | 3.3863e-05 | 3.3863e-05
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under N-1 Contingency (A) | 0 | 0 | 0 | 0 | 0
Lockrose Bulk | 381-5 | 381 Tee2 | 381 Tee3 | NCC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | DER Forecast under System Normal (A) | 10 | 15 | 19 | 23 | 26
|  |  |  | Power Factor | 0.94962 | 0.97902 | 0.98794 | 0.99146 | 0.99378
|  |  |  | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | DER Forecast under N-1 Contingency (A) | 25 | 34 | 42 | 49 | 54
Lockrose Bulk | 381-6 | 381 Tee3 | Coominya TR2 | NCC Rating (A) | 403 | 403 | 403 | 403 | 403
|  |  |  | DER Forecast under System Normal (A) | 4 | 2 | 1 | 0 | 1
|  |  |  | Power Factor | 0.99869 | 0.99639 | 0.97653 | 0.86714 | 0.99024
|  |  |  | ECC Rating (A) | 403 | 403 | 403 | 403 | 403
|  |  |  | DER Forecast under N-1 Contingency (A) | 4 | 2 | 1 | 0 | 1
Lockrose Bulk | 381-7 | 381 Tee3 | 381 Tee4 | NCC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | DER Forecast under System Normal (A) | 14 | 17 | 20 | 22 | 24
|  |  |  | Power Factor | 0.98221 | 0.98877 | 0.99194 | 0.99336 | 0.99464
|  |  |  | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | DER Forecast under N-1 Contingency (A) | 29 | 37 | 43 | 48 | 53
Lockrose Bulk | 381-8 | 381 Tee4 | Coominya TR1 | NCC Rating (A) | 403 | 403 | 403 | 403 | 403
|  |  |  | DER Forecast under System Normal (A) | 4 | 3 | 1 | 1 | 2
|  |  |  | Power Factor | 0.99452 | 0.98439 | 0.90758 | 0.6139 | 0.95708
|  |  |  | ECC Rating (A) | 403 | 403 | 403 | 403 | 403
|  |  |  | DER Forecast under N-1 Contingency (A) | 4 | 3 | 1 | 1 | 2
Lockrose Bulk | 381-9 | 381 Tee4 | Paddys Gully | NCC Rating (A) | 155 | 155 | 155 | 155 | 155
|  |  |  | DER Forecast under System Normal (A) | 18 | 19 | 21 | 22 | 23
|  |  |  | Power Factor | 0.98607 | 0.98849 | 0.99012 | 0.99083 | 0.99183
|  |  |  | ECC Rating (A) | 155 | 155 | 155 | 155 | 155
|  |  |  | DER Forecast under N-1 Contingency (A) | 33 | 39 | 44 | 48 | 52
Lockrose Bulk | 382-1 | Lockrose BS | 382 Tee1 | NCC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | DER Forecast under System Normal (A) | 16 | 20 | 24 | 27 | 30
|  |  |  | Power Factor | 0.97373 | 0.98574 | 0.99106 | 0.99351 | 0.99534
|  |  |  | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | DER Forecast under N-1 Contingency (A) | 34 | 39 | 44 | 48 | 52
Lockrose Bulk | 382-2 | 382 Tee1 | 381 Tee1 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under System Normal (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 1.9422e-05 | 1.942e-05 | 1.9426e-05 | 1.9424e-05 | 1.9422e-05
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under N-1 Contingency (A) | 0 | 0 | 0 | 0 | 0
Lockrose Bulk | 382-3 | 382 Tee1 | Paddys Gully | NCC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | DER Forecast under System Normal (A) | 16 | 20 | 24 | 27 | 30
|  |  |  | Power Factor | 0.97429 | 0.98606 | 0.99127 | 0.99365 | 0.99545
|  |  |  | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | DER Forecast under N-1 Contingency (A) | 34 | 39 | 44 | 48 | 52
Lockrose Bulk | 3828-1 | Paddy's Gully | Esk | NCC Rating (A) | 154 | 154 | 154 | 154 | 154
|  |  |  | DER Forecast under System Normal (A) | 25 | 29 | 33 | 37 | 40
|  |  |  | Power Factor | 0.99616 | 0.99748 | 0.99818 | 0.99605 | 0.9967
|  |  |  | ECC Rating (A) | 154 | 154 | 154 | 154 | 154
|  |  |  | DER Forecast under N-1 Contingency (A) | 33 | 39 | 44 | 48 | 52
Lockrose Bulk | 3829-1 | Paddy's Gully | Murrumba | NCC Rating (A) | 155 | 155 | 155 | 155 | 155
|  |  |  | DER Forecast under System Normal (A) | 9 | 10 | 11 | 11 | 12
|  |  |  | Power Factor | 0.98723 | 0.99175 | 0.99416 | 0.99971 | 0.99949
|  |  |  | ECC Rating (A) | 155 | 155 | 155 | 155 | 155
|  |  |  | DER Forecast under N-1 Contingency (A) | 33 | 39 | 43 | 47 | 51
Lockrose Bulk | 3831-1 | Lockrose BS | Tarampa | NCC Rating (A) | 355 | 355 | 355 | 355 | 355
|  |  |  | DER Forecast under System Normal (A) | 50 | 62 | 72 | 83 | 93
|  |  |  | Power Factor | 0.99943 | 0.99931 | 0.99907 | 0.99881 | 0.99849
|  |  |  | ECC Rating (A) | 355 | 355 | 355 | 355 | 355
|  |  |  | DER Forecast under N-1 Contingency (A) | 50 | 62 | 72 | 83 | 93
Lockrose Bulk | 3832-1 | Tarampa | 3832 Tee1 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under System Normal (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 3.7175e-05 | 3.7172e-05 | 3.7172e-05 | 3.7186e-05 | 3.7174e-05
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under N-1 Contingency (A) | 0 | 0 | 0 | 0 | 0
Lockrose Bulk | 3832-3 | 3832 Tee1 | Lowood | NCC Rating (A) | 434 | 434 | 434 | 434 | 434
|  |  |  | DER Forecast under System Normal (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 5.5524e-06 | 5.5522e-06 | 5.5524e-06 | 5.5524e-06 | 5.5524e-06
|  |  |  | ECC Rating (A) | 434 | 434 | 434 | 434 | 434
|  |  |  | DER Forecast under N-1 Contingency (A) | 1 | 1 | 1 | 1 | 1
Lockrose Bulk | 3840-1 | Esk | Toogoolawah | NCC Rating (A) | 155 | 155 | 155 | 713 | 713
|  |  |  | DER Forecast under System Normal (A) | 6 | 6 | 6 | 8 | 8
|  |  |  | Power Factor | 0.99303 | 0.99229 | 0.99144 | 0.955 | 0.95345
|  |  |  | ECC Rating (A) | 155 | 155 | 155 | 713 | 713
|  |  |  | DER Forecast under N-1 Contingency (A) | 18 | 23 | 26 | 29 | 32
Lockrose Bulk | 384-1 | Lockrose BS | 384 Tee1 | NCC Rating (A) | 451 | 451 | 451 | 451 | 451
|  |  |  | DER Forecast under System Normal (A) | 33 | 42 | 37 | 46 | 54
|  |  |  | Power Factor | 0.99989 | 0.9995 | 0.99996 | 0.99977 | 0.99952
|  |  |  | ECC Rating (A) | 451 | 451 | 451 | 451 | 451
|  |  |  | DER Forecast under N-1 Contingency (A) | 53 | 69 | 54 | 67 | 80
Lockrose Bulk | 384-2 | 384 Tee1 | Glenmore Grove | NCC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | DER Forecast under System Normal (A) | 12 | 14 | 18 | 21 | 25
|  |  |  | Power Factor | 0.99997 | 0.99998 | 0.99996 | 0.99992 | 0.99988
|  |  |  | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | DER Forecast under N-1 Contingency (A) | 12 | 14 | 18 | 21 | 25
Lockrose Bulk | 384-3 | 384 Tee1 | Laidley1 | NCC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | DER Forecast under System Normal (A) | 22 | 28 | 19 | 24 | 29
|  |  |  | Power Factor | 0.99817 | 0.99748 | 0.99855 | 0.99799 | 0.99755
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | DER Forecast under N-1 Contingency (A) | 42 | 55 | 36 | 46 | 55
Lockrose Bulk | 3870-1 | Lockrose BS | Lowood | NCC Rating (A) | 703 | 703 | 703 | 703 | 703
|  |  |  | DER Forecast under System Normal (A) | 55 | 82 | 108 | 131 | 153
|  |  |  | Power Factor | 0.99992 | 0.99986 | 0.99946 | 0.99887 | 0.99819
|  |  |  | ECC Rating (A) | 703 | 703 | 703 | 703 | 703
|  |  |  | DER Forecast under N-1 Contingency (A) | 55 | 82 | 108 | 131 | 153
Lockrose Bulk | 3871-1 | Lowood | Wivenhoe | NCC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | DER Forecast under System Normal (A) | 46 | 64 | 82 | 99 | 117
|  |  |  | Power Factor | 0.99966 | 0.99947 | 0.99911 | 0.99858 | 0.99803
|  |  |  | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | DER Forecast under N-1 Contingency (A) | 47 | 64 | 82 | 99 | 117
Loganlea Bulk | 407-1 | Loganlea BS | Woodridge | NCC Rating (A) | 777 | 777 | 777 | 777 | 777
|  |  |  | DER Forecast under System Normal (A) | 43 | 36 | 30 | 24 | 20
|  |  |  | Power Factor | 0.99984 | 0.99958 | 0.99911 | 0.99833 | 0.99704
|  |  |  | ECC Rating (A) | 777 | 777 | 777 | 777 | 777
|  |  |  | DER Forecast under N-1 Contingency (A) | 82 | 68 | 56 | 46 | 37
Loganlea Bulk | 408-1 | Loganlea BS | Kingston | NCC Rating (A) | 529 | 529 | 529 | 529 | 529
|  |  |  | DER Forecast under System Normal (A) | 101 | 173 | 250 | 331 | 418
|  |  |  | Power Factor | 0.99962 | 0.9978 | 0.9946 | 0.98977 | 0.98291
|  |  |  | ECC Rating (A) | 529 | 529 | 529 | 529 | 529
|  |  |  | DER Forecast under N-1 Contingency (A) | 182 | 314 | 451 | 598 | 756
Loganlea Bulk | 409-1 | Loganlea BS | Woodridge | NCC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | DER Forecast under System Normal (A) | 39 | 32 | 26 | 22 | 17
|  |  |  | Power Factor | 0.99999 | 0.99995 | 0.99986 | 0.9997 | 0.99944
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | DER Forecast under N-1 Contingency (A) | 82 | 68 | 56 | 46 | 37
Loganlea Bulk | 418-1 | Loganlea BS | Tanah Merah | NCC Rating (A) | 631 | 631 | 631 | 631 | 631
|  |  |  | DER Forecast under System Normal (A) | 55 | 68 | 79 | 88 | 95
|  |  |  | Power Factor | 0.99993 | 0.99988 | 0.99984 | 0.99979 | 0.99975
|  |  |  | ECC Rating (A) | 631 | 631 | 631 | 631 | 631
|  |  |  | DER Forecast under N-1 Contingency (A) | 55 | 68 | 79 | 88 | 95
Loganlea Bulk | 452-1 | Loganlea BS | Kingston | NCC Rating (A) | 510 | 510 | 510 | 510 | 510
|  |  |  | DER Forecast under System Normal (A) | 82 | 141 | 203 | 269 | 340
|  |  |  | Power Factor | 0.99906 | 0.99682 | 0.99338 | 0.98847 | 0.98171
|  |  |  | ECC Rating (A) | 510 | 510 | 510 | 510 | 510
|  |  |  | DER Forecast under N-1 Contingency (A) | 182 | 313 | 451 | 597 | 755
Lytton Bulk | 3302-1 | Lytton BS | Fisherman Is B | NCC Rating (A) | 650 | 650 | 650 | 650 | 650
|  |  |  | DER Forecast under System Normal (A) | 122 | 176 | 194 | 203 | 203
|  |  |  | Power Factor | 0.99942 | 0.99913 | 0.99891 | 0.99878 | 0.99878
|  |  |  | ECC Rating (A) | 650 | 650 | 650 | 650 | 650
|  |  |  | DER Forecast under N-1 Contingency (A) | 245 | 355 | 392 | 410 | 409
Lytton Bulk | 3303-1 | Lytton BS | Fisherman Is B | NCC Rating (A) | 600 | 600 | 600 | 600 | 600
|  |  |  | DER Forecast under System Normal (A) | 122 | 176 | 194 | 203 | 203
|  |  |  | Power Factor | 0.99942 | 0.99913 | 0.9989 | 0.99877 | 0.99877
|  |  |  | ECC Rating (A) | 600 | 600 | 600 | 600 | 600
|  |  |  | DER Forecast under N-1 Contingency (A) | 245 | 355 | 392 | 410 | 409
Lytton Bulk | 490-1 | Lytton BS | Gibson Island | NCC Rating (A) | 628 | 628 | 628 | 628 | 628
|  |  |  | DER Forecast under System Normal (A) | 7 | 31 | 31 | 31 | 31
|  |  |  | Power Factor | 0.47004 | 0.99133 | 0.99133 | 0.99133 | 0.99133
|  |  |  | ECC Rating (A) | 628 | 628 | 628 | 628 | 628
|  |  |  | DER Forecast under N-1 Contingency (A) | 8 | 59 | 59 | 59 | 59
Lytton Bulk | 491-1 | Lytton BS | Lytton | NCC Rating (A) | 450 | 450 | 450 | 450 | 450
|  |  |  | DER Forecast under System Normal (A) | 129 | 144 | 167 | 166 | 166
|  |  |  | Power Factor | 0.99548 | 0.99642 | 0.9976 | 0.99756 | 0.99754
|  |  |  | ECC Rating (A) | 450 | 450 | 450 | 450 | 450
|  |  |  | DER Forecast under N-1 Contingency (A) | 258 | 287 | 334 | 332 | 331
Lytton Bulk | 492-1 | Lytton BS | Gibson Island | NCC Rating (A) | 463 | 463 | 463 | 463 | 463
|  |  |  | DER Forecast under System Normal (A) | 7 | 30 | 30 | 30 | 30
|  |  |  | Power Factor | 0.39157 | 0.96186 | 0.96186 | 0.96186 | 0.96186
|  |  |  | ECC Rating (A) | 463 | 463 | 463 | 463 | 463
|  |  |  | DER Forecast under N-1 Contingency (A) | 10 | 60 | 60 | 60 | 60
Lytton Bulk | 493-1 | Lytton BS | Lytton | NCC Rating (A) | 536 | 536 | 536 | 536 | 536
|  |  |  | DER Forecast under System Normal (A) | 129 | 144 | 167 | 167 | 166
|  |  |  | Power Factor | 0.99277 | 0.99214 | 0.991 | 0.99104 | 0.99107
|  |  |  | ECC Rating (A) | 536 | 536 | 536 | 536 | 536
|  |  |  | DER Forecast under N-1 Contingency (A) | 258 | 287 | 333 | 332 | 331
Lytton Bulk | 494-1 | Fisherman Is B | Fishermans Is | NCC Rating (A) | 488 | 488 | 488 | 488 | 488
|  |  |  | DER Forecast under System Normal (A) | 40 | 88 | 106 | 115 | 115
|  |  |  | Power Factor | 0.99399 | 0.99731 | 0.99803 | 0.99833 | 0.99833
|  |  |  | ECC Rating (A) | 488 | 488 | 488 | 488 | 488
|  |  |  | DER Forecast under N-1 Contingency (A) | 80 | 178 | 214 | 232 | 232
Lytton Bulk | 495-1 | Fisherman Is B | Fisherman Is | NCC Rating (A) | 600 | 600 | 600 | 600 | 600
|  |  |  | DER Forecast under System Normal (A) | 40 | 90 | 108 | 118 | 117
|  |  |  | Power Factor | 0.99796 | 0.99272 | 0.99102 | 0.99018 | 0.99021
|  |  |  | ECC Rating (A) | 600 | 600 | 600 | 600 | 600
|  |  |  | DER Forecast under N-1 Contingency (A) | 80 | 178 | 214 | 232 | 231
Lytton Bulk | 560-1 | Lytton BS | 560 Tee1 | NCC Rating (A) | 527 | 527 | 527 | 527 | 527
|  |  |  | DER Forecast under System Normal (A) | 44 | 53 | 61 | 68 | 74
|  |  |  | Power Factor | 0.99978 | 0.99892 | 0.99794 | 0.99696 | 0.99603
|  |  |  | ECC Rating (A) | 527 | 527 | 527 | 527 | 527
|  |  |  | DER Forecast under N-1 Contingency (A) | 134 | 162 | 185 | 205 | 223
Lytton Bulk | 560-2 | 560 Tee1 | Tingalpa | NCC Rating (A) | 600 | 600 | 600 | 600 | 600
|  |  |  | DER Forecast under System Normal (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 1.94e-06 | 1.9397e-06 | 1.9408e-06 | 1.9407e-06 | 1.94e-06
|  |  |  | ECC Rating (A) | 600 | 600 | 600 | 600 | 600
|  |  |  | DER Forecast under N-1 Contingency (A) | 0 | 0 | 0 | 0 | 0
Lytton Bulk | 560-3 | 560 Tee1 | 560 Tee2 | NCC Rating (A) | 600 | 600 | 600 | 600 | 600
|  |  |  | DER Forecast under System Normal (A) | 44 | 54 | 61 | 68 | 74
|  |  |  | Power Factor | 0.99914 | 0.99807 | 0.9971 | 0.99621 | 0.99541
|  |  |  | ECC Rating (A) | 600 | 600 | 600 | 600 | 600
|  |  |  | DER Forecast under N-1 Contingency (A) | 134 | 162 | 185 | 205 | 223
Lytton Bulk | 560-5 | Lota | 560 Tee2 | NCC Rating (A) | 704 | 704 | 704 | 704 | 704
|  |  |  | DER Forecast under System Normal (A) | 26 | 31 | 36 | 40 | 44
|  |  |  | Power Factor | 0.99941 | 0.99843 | 0.99749 | 0.99662 | 0.99583
|  |  |  | ECC Rating (A) | 704 | 704 | 704 | 704 | 704
|  |  |  | DER Forecast under N-1 Contingency (A) | 79 | 95 | 109 | 121 | 131
Lytton Bulk | 569-1 | Lytton BS | Lota | NCC Rating (A) | 582 | 582 | 582 | 582 | 582
|  |  |  | DER Forecast under System Normal (A) | 91 | 110 | 126 | 140 | 153
|  |  |  | Power Factor | 0.99698 | 0.99852 | 0.99926 | 0.99966 | 0.99987
|  |  |  | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
|  |  |  | DER Forecast under N-1 Contingency (A) | 135 | 164 | 188 | 208 | 227
Lytton Bulk | 599-1 | Hemmant | Lindum | NCC Rating (A) | 443 | 443 | 443 | 443 | 443
|  |  |  | DER Forecast under System Normal (A) | 2 | 2 | 2 | 2 | 2
|  |  |  | Power Factor | 2.5275e-05 | 2.5274e-05 | 2.5275e-05 | 2.5275e-05 | 2.5275e-05
|  |  |  | ECC Rating (A) | 443 | 443 | 443 | 443 | 443
|  |  |  | DER Forecast under N-1 Contingency (A) | 2 | 2 | 2 | 2 | 2
Lytton Bulk | 681-1 | Lindum | Wynnum | NCC Rating (A) | 661 | 661 | 661 | 661 | 661
|  |  |  | DER Forecast under System Normal (A) | 32 | 44 | 55 | 65 | 74
|  |  |  | Power Factor | 0.98891 | 0.99533 | 0.99771 | 0.99884 | 0.99933
|  |  |  | ECC Rating (A) | 661 | 661 | 661 | 661 | 661
|  |  |  | DER Forecast under N-1 Contingency (A) | 62 | 86 | 107 | 127 | 145
Lytton Bulk | 682-1 | Lindum | Wynnum | NCC Rating (A) | 661 | 661 | 661 | 661 | 661
|  |  |  | DER Forecast under System Normal (A) | 30 | 42 | 53 | 62 | 71
|  |  |  | Power Factor | 0.98818 | 0.99495 | 0.99748 | 0.99869 | 0.99933
|  |  |  | ECC Rating (A) | 661 | 661 | 661 | 661 | 661
|  |  |  | DER Forecast under N-1 Contingency (A) | 62 | 86 | 107 | 127 | 145
Lytton Bulk | 687-1 | Lytton BS | 687 Tee1 | NCC Rating (A) | 758 | 758 | 758 | 758 | 758
|  |  |  | DER Forecast under System Normal (A) | 23 | 32 | 40 | 47 | 53
|  |  |  | Power Factor | 0.97178 | 0.9899 | 0.99596 | 0.99845 | 0.99951
|  |  |  | ECC Rating (A) | 758 | 758 | 758 | 758 | 758
|  |  |  | DER Forecast under N-1 Contingency (A) | 63 | 87 | 108 | 127 | 145
Lytton Bulk | 687-2 | 687 Tee1 | Lytton | NCC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | DER Forecast under System Normal (A) | 2 | 2 | 2 | 2 | 2
|  |  |  | Power Factor | 1.3245e-06 | 1.3248e-06 | 1.3252e-06 | 1.3256e-06 | 1.3252e-06
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | DER Forecast under N-1 Contingency (A) | 2 | 2 | 2 | 2 | 2
Lytton Bulk | 687-3 | 687 Tee1 | Lindum | NCC Rating (A) | 636 | 636 | 636 | 636 | 636
|  |  |  | DER Forecast under System Normal (A) | 23 | 32 | 39 | 46 | 53
|  |  |  | Power Factor | 0.99493 | 0.99915 | 0.99996 | 0.99991 | 0.99957
|  |  |  | ECC Rating (A) | 636 | 636 | 636 | 636 | 636
|  |  |  | DER Forecast under N-1 Contingency (A) | 62 | 86 | 108 | 127 | 145
Lytton Bulk | 688-1 | Lytton BS | Lindum | NCC Rating (A) | 636 | 636 | 636 | 636 | 636
|  |  |  | DER Forecast under System Normal (A) | 40 | 55 | 69 | 81 | 92
|  |  |  | Power Factor | 0.97473 | 0.98663 | 0.99158 | 0.99424 | 0.99588
|  |  |  | ECC Rating (A) | 636 | 636 | 636 | 636 | 636
|  |  |  | DER Forecast under N-1 Contingency (A) | 62 | 86 | 108 | 127 | 145
Meeandah Bulk | 3374-1 | Whinstanes | Hamilton Lands | NCC Rating (A) | 476 | 476 | 476 | 476 | 476
|  |  |  | DER Forecast under System Normal (A) | 2 | 2 | 1 | 2 | 4
|  |  |  | Power Factor | 0.81124 | 0.82489 | 0.091225 | 0.85958 | 0.95475
|  |  |  | ECC Rating (A) | 476 | 476 | 476 | 476 | 476
|  |  |  | DER Forecast under N-1 Contingency (A) | 17 | 17 | 17 | 17 | 17
Meeandah Bulk | 506-1 | Meeandah BS | Hamilton Lands | NCC Rating (A) | 720 | 720 | 720 | 720 | 720
|  |  |  | DER Forecast under System Normal (A) | 36 | 36 | 31 | 26 | 22
|  |  |  | Power Factor | 0.98169 | 0.9817 | 0.97501 | 0.96432 | 0.94666
|  |  |  | ECC Rating (A) | 720 | 720 | 720 | 720 | 720
|  |  |  | DER Forecast under N-1 Contingency (A) | 61 | 62 | 53 | 44 | 36
Meeandah Bulk | 513-1 | Meeandah BS | Hamilton Lands | NCC Rating (A) | 720 | 720 | 720 | 720 | 720
|  |  |  | DER Forecast under System Normal (A) | 36 | 36 | 31 | 26 | 21
|  |  |  | Power Factor | 0.98142 | 0.98144 | 0.97466 | 0.96383 | 0.94594
|  |  |  | ECC Rating (A) | 720 | 720 | 720 | 720 | 720
|  |  |  | DER Forecast under N-1 Contingency (A) | 61 | 61 | 53 | 44 | 36
Meeandah Bulk | 556-1 | Meeandah BS | Whinstanes | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under System Normal (A) | 19 | 19 | 17 | 15 | 13
|  |  |  | Power Factor | 0.98978 | 0.98974 | 0.98741 | 0.98431 | 0.98025
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under N-1 Contingency (A) | 28 | 28 | 25 | 22 | 19
Meeandah Bulk | 609-1 | Meeandah BS | Myrtletown | NCC Rating (A) | 813 | 813 | 813 | 813 | 813
|  |  |  | DER Forecast under System Normal (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 2.9588e-06 | 2.9586e-06 | 2.9585e-06 | 2.9588e-06 | 2.9585e-06
|  |  |  | ECC Rating (A) | 813 | 813 | 813 | 813 | 813
|  |  |  | DER Forecast under N-1 Contingency (A) | 1 | 1 | 1 | 1 | 1
Meeandah Bulk | 610-1 | Meeandah BS | Myrtletown | NCC Rating (A) | 748 | 748 | 748 | 748 | 748
|  |  |  | DER Forecast under System Normal (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 8.8416e-06 | 8.8416e-06 | 8.8416e-06 | 8.8389e-06 | 8.8391e-06
|  |  |  | ECC Rating (A) | 748 | 748 | 748 | 748 | 748
|  |  |  | DER Forecast under N-1 Contingency (A) | 1 | 1 | 1 | 1 | 1
Molendinar Bulk | 3670-1 | Molendinar BS | Parkwood | NCC Rating (A) | 710 | 710 | 710 | 710 | 710
|  |  |  | DER Forecast under System Normal (A) | 75 | 77 | 73 | 63 | 55
|  |  |  | Power Factor | 0.99907 | 0.99975 | 0.99968 | 0.99952 | 0.99916
|  |  |  | ECC Rating (A) | 710 | 710 | 710 | 710 | 710
|  |  |  | DER Forecast under N-1 Contingency (A) | 113 | 116 | 119 | 117 | 116
Molendinar Bulk | 3671-1 | Molendinar BS | Parkwood | NCC Rating (A) | 708 | 708 | 708 | 708 | 708
|  |  |  | DER Forecast under System Normal (A) | 60 | 61 | 58 | 50 | 43
|  |  |  | Power Factor | 0.99864 | 0.99949 | 0.99981 | 0.99989 | 0.99998
|  |  |  | ECC Rating (A) | 708 | 708 | 708 | 708 | 708
|  |  |  | DER Forecast under N-1 Contingency (A) | 104 | 106 | 101 | 93 | 92
Molendinar Bulk | 389-1 | Parkwood | 389 Tee1 | NCC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | DER Forecast under System Normal (A) | 36 | 62 | 82 | 96 | 110
|  |  |  | Power Factor | 0.98339 | 0.99445 | 0.99719 | 0.99847 | 0.9992
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | DER Forecast under N-1 Contingency (A) | 67 | 94 | 113 | 126 | 148
Molendinar Bulk | 389-2 | F389 Tee1 | Labrador | NCC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | DER Forecast under System Normal (A) | 55 | 45 | 37 | 31 | 26
|  |  |  | Power Factor | 0.99875 | 0.99906 | 0.99941 | 0.99974 | 0.99997
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | DER Forecast under N-1 Contingency (A) | 75 | 59 | 44 | 41 | 39
Molendinar Bulk | 389-3 | F389 Tee1 | Hollywell | NCC Rating (A) | 631 | 631 | 631 | 631 | 631
|  |  |  | DER Forecast under System Normal (A) | 91 | 107 | 119 | 127 | 137
|  |  |  | Power Factor | 0.99485 | 0.99689 | 0.99808 | 0.9989 | 0.99945
|  |  |  | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
|  |  |  | DER Forecast under N-1 Contingency (A) | 115 | 131 | 143 | 166 | 187
Molendinar Bulk | 390-1 | Molendinar BS | F390 Tee1 | NCC Rating (A) | 637 | 637 | 637 | 637 | 637
|  |  |  | DER Forecast under System Normal (A) | 24 | 32 | 27 | 20 | 14
|  |  |  | Power Factor | 0.97787 | 0.98828 | 0.98224 | 0.96957 | 0.93247
|  |  |  | ECC Rating (A) | 637 | 637 | 637 | 637 | 637
|  |  |  | DER Forecast under N-1 Contingency (A) | 53 | 71 | 59 | 45 | 29
Molendinar Bulk | 390-2 | F390 Tee | Bundall | NCC Rating (A) | 653 | 653 | 653 | 653 | 653
|  |  |  | DER Forecast under System Normal (A) | 23 | 32 | 26 | 20 | 13
|  |  |  | Power Factor | 0.99533 | 0.99753 | 0.99625 | 0.99361 | 0.98581
|  |  |  | ECC Rating (A) | 653 | 653 | 653 | 653 | 653
|  |  |  | DER Forecast under N-1 Contingency (A) | 53 | 72 | 59 | 45 | 29
Molendinar Bulk | 390-3 | F390 Tee | Miami | NCC Rating (A) | 529 | 529 | 529 | 529 | 529
|  |  |  | DER Forecast under System Normal (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 7.1419e-06 | 7.142e-06 | 7.1424e-06 | 7.1415e-06 | 7.1423e-06
|  |  |  | ECC Rating (A) | 529 | 529 | 529 | 529 | 529
|  |  |  | DER Forecast under N-1 Contingency (A) | 0 | 0 | 0 | 0 | 0
Molendinar Bulk | 391-1 | Molendinar BS | Bundall | NCC Rating (A) | 623 | 623 | 623 | 623 | 623
|  |  |  | DER Forecast under System Normal (A) | 29 | 39 | 32 | 25 | 16
|  |  |  | Power Factor | 0.99634 | 0.99894 | 0.99751 | 0.99392 | 0.98136
|  |  |  | ECC Rating (A) | 623 | 623 | 623 | 623 | 623
|  |  |  | DER Forecast under N-1 Contingency (A) | 53 | 71 | 59 | 45 | 29
Molendinar Bulk | 392-1 | Molendinar BS | Gaven | NCC Rating (A) | 708 | 708 | 708 | 708 | 708
|  |  |  | DER Forecast under System Normal (A) | 68 | 106 | 142 | 177 | 212
|  |  |  | Power Factor | 0.99983 | 0.99891 | 0.99756 | 0.99584 | 0.99366
|  |  |  | ECC Rating (A) | 708 | 708 | 708 | 708 | 708
|  |  |  | DER Forecast under N-1 Contingency (A) | 136 | 212 | 283 | 352 | 424
Molendinar Bulk | 421-1 | Molendinar BS | Arundel | NCC Rating (A) | 673 | 673 | 673 | 673 | 673
|  |  |  | DER Forecast under System Normal (A) | 21 | 19 | 39 | 63 | 90
|  |  |  | Power Factor | 0.66383 | 0.55961 | 0.92304 | 0.97578 | 0.99053
|  |  |  | ECC Rating (A) | 712 | 712 | 712 | 712 | 712
|  |  |  | DER Forecast under N-1 Contingency (A) | 35 | 65 | 96 | 126 | 160
Molendinar Bulk | 458-1 | Molendinar BS | Labrador | NCC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | DER Forecast under System Normal (A) | 20 | 14 | 8 | 3 | 5
|  |  |  | Power Factor | 0.98737 | 0.97823 | 0.94553 | 0.48192 | 0.91517
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | DER Forecast under N-1 Contingency (A) | 75 | 59 | 44 | 33 | 22
Molendinar Bulk | 473-1 | Molendinar BS | Gaven | NCC Rating (A) | 717 | 717 | 717 | 717 | 717
|  |  |  | DER Forecast under System Normal (A) | 68 | 106 | 142 | 177 | 213
|  |  |  | Power Factor | 0.99948 | 0.99863 | 0.99749 | 0.99606 | 0.99427
|  |  |  | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
|  |  |  | DER Forecast under N-1 Contingency (A) | 136 | 212 | 283 | 353 | 424
Molendinar Bulk | 474A-1 | Arundel | Hollywell | NCC Rating (A) | 631 | 631 | 631 | 631 | 631
|  |  |  | DER Forecast under System Normal (A) | 14 | 15 | 27 | 40 | 52
|  |  |  | Power Factor | 0.45711 | 0.61582 | 0.91001 | 0.96528 | 0.98114
|  |  |  | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
|  |  |  | DER Forecast under N-1 Contingency (A) | 85 | 116 | 143 | 166 | 187
Molendinar Bulk | 474B-1 | Hope Is | Hollywell | NCC Rating (A) | 786 | 786 | 786 | 786 | 786
|  |  |  | DER Forecast under System Normal (A) | 4 | 4 | 4 | 4 | 4
|  |  |  | Power Factor | 4.5529e-06 | 4.5529e-06 | 4.5529e-06 | 4.5529e-06 | 4.5529e-06
|  |  |  | ECC Rating (A) | 786 | 786 | 786 | 786 | 786
|  |  |  | DER Forecast under N-1 Contingency (A) | 4 | 4 | 4 | 4 | 4
Molendinar Bulk | 486-1 | Molendinar BS | Arundel | NCC Rating (A) | 673 | 673 | 673 | 673 | 673
|  |  |  | DER Forecast under System Normal (A) | 21 | 19 | 39 | 63 | 90
|  |  |  | Power Factor | 0.66361 | 0.55916 | 0.92285 | 0.9757 | 0.99049
|  |  |  | ECC Rating (A) | 721 | 721 | 721 | 721 | 721
|  |  |  | DER Forecast under N-1 Contingency (A) | 35 | 65 | 96 | 126 | 160
Mudgeeraba Bulk | 3700-1 | Mudgeeraba BS | 3700 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under System Normal (A) | 64 | 80 | 95 | 108 | 119
|  |  |  | Power Factor | 0.99904 | 0.99829 | 0.99756 | 0.99684 | 0.99612
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under N-1 Contingency (A) | 132 | 167 | 197 | 223 | 248
Mudgeeraba Bulk | 3700-2 | 3700 Tee1 | 3701 Tee1 | NCC Rating (A) | 723 | 723 | 723 | 723 | 723
|  |  |  | DER Forecast under System Normal (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 6.6074e-05 | 6.6077e-05 | 6.6126e-05 | 6.6119e-05 | 6.6144e-05
|  |  |  | ECC Rating (A) | 723 | 723 | 723 | 723 | 723
|  |  |  | DER Forecast under N-1 Contingency (A) | 0 | 0 | 0 | 0 | 0
Mudgeeraba Bulk | 3700-3 | 3700 Tee1 | 3700 Tee2 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under System Normal (A) | 64 | 80 | 95 | 108 | 119
|  |  |  | Power Factor | 0.99904 | 0.99836 | 0.99769 | 0.99704 | 0.99639
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under N-1 Contingency (A) | 132 | 167 | 197 | 223 | 248
Mudgeeraba Bulk | 3700-4 | 3700 Tee2 | 3702 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under System Normal (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 8.6876e-06 | 8.688e-06 | 8.6891e-06 | 8.6875e-06 | 8.6882e-06
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under N-1 Contingency (A) | 0 | 0 | 0 | 0 | 0
Mudgeeraba Bulk | 3700-5 | 3700 Tee2 | Mudgeeraba Pkg | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under System Normal (A) | 64 | 80 | 95 | 108 | 119
|  |  |  | Power Factor | 0.99895 | 0.99831 | 0.99769 | 0.99708 | 0.99647
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under N-1 Contingency (A) | 132 | 167 | 197 | 223 | 248
Mudgeeraba Bulk | 3701-1 | Mudgeeraba | Mudgeeraba Pkg | NCC Rating (A) | 529 | 529 | 529 | 529 | 529
|  |  |  | DER Forecast under System Normal (A) | 69 | 87 | 103 | 116 | 129
|  |  |  | Power Factor | 0.99982 | 0.99944 | 0.999 | 0.99853 | 0.99803
|  |  |  | ECC Rating (A) | 529 | 529 | 529 | 529 | 529
|  |  |  | DER Forecast under N-1 Contingency (A) | 132 | 167 | 197 | 224 | 248
Nambour Bulk | 307-1 | Nambour BS | 307 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under System Normal (A) | 41 | 50 | 65 | 80 | 95
|  |  |  | Power Factor | 0.98171 | 0.98532 | 0.98975 | 0.99277 | 0.99506
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under N-1 Contingency (A) | 76 | 93 | 121 | 150 | 178
Nambour Bulk | 307-2 | 307 Tee1 | Yandina | NCC Rating (A) | 755 | 755 | 755 | 755 | 755
|  |  |  | DER Forecast under System Normal (A) | 40 | 49 | 65 | 80 | 95
|  |  |  | Power Factor | 0.99002 | 0.99114 | 0.99296 | 0.99459 | 0.996
|  |  |  | ECC Rating (A) | 755 | 755 | 755 | 755 | 755
|  |  |  | DER Forecast under N-1 Contingency (A) | 76 | 93 | 121 | 150 | 178
Nambour Bulk | 344-1 | Nambour BS | Maleny | NCC Rating (A) | 155 | 200 | 200 | 200 | 200
|  |  |  | DER Forecast under System Normal (A) | 44 | 49 | 53 | 56 | 58
|  |  |  | Power Factor | 0.99986 | 0.99995 | 0.99989 | 0.99983 | 0.99977
|  |  |  | ECC Rating (A) | 155 | 200 | 200 | 200 | 200
|  |  |  | DER Forecast under N-1 Contingency (A) | 44 | 49 | 53 | 56 | 58
Nambour Bulk | 345-1 | Nambour BS | Kenilworth | NCC Rating (A) | 208 | 208 | 208 | 208 | 208
|  |  |  | DER Forecast under System Normal (A) | 9 | 14 | 19 | 24 | 28
|  |  |  | Power Factor | 0.99146 | 0.99767 | 0.9992 | 0.99967 | 0.99962
|  |  |  | ECC Rating (A) | 208 | 208 | 208 | 208 | 208
|  |  |  | DER Forecast under N-1 Contingency (A) | 9 | 14 | 19 | 24 | 28
Nambour Bulk | 347-1 | Nambour BS | 347 Tee1 | NCC Rating (A) | 412 | 412 | 412 | 412 | 412
|  |  |  | DER Forecast under System Normal (A) | 59 | 79 | 97 | 114 | 130
|  |  |  | Power Factor | 0.99928 | 0.99833 | 0.99726 | 0.99597 | 0.99468
|  |  |  | ECC Rating (A) | 412 | 412 | 412 | 412 | 412
|  |  |  | DER Forecast under N-1 Contingency (A) | 132 | 176 | 217 | 253 | 289
Nambour Bulk | 347-2 | 347 Tee1 | Palmwoods Central | NCC Rating (A) | 357 | 357 | 357 | 357 | 357
|  |  |  | DER Forecast under System Normal (A) | 59 | 79 | 97 | 114 | 130
|  |  |  | Power Factor | 0.99776 | 0.99701 | 0.99615 | 0.99505 | 0.99399
|  |  |  | ECC Rating (A) | 357 | 357 | 357 | 357 | 357
|  |  |  | DER Forecast under N-1 Contingency (A) | 132 | 177 | 217 | 253 | 289
Nambour Bulk | 347-3 | 347 Tee1 | Landsborough | NCC Rating (A) | 412 | 412 | 412 | 412 | 412
|  |  |  | DER Forecast under System Normal (A) | 2 | 2 | 2 | 2 | 2
|  |  |  | Power Factor | 7.6423e-05 | 7.6423e-05 | 7.6423e-05 | 7.6423e-05 | 7.6423e-05
|  |  |  | ECC Rating (A) | 412 | 412 | 412 | 412 | 412
|  |  |  | DER Forecast under N-1 Contingency (A) | 2 | 2 | 2 | 2 | 2
Nambour Bulk | 348-1 | Nambour BS | Palmwoods Central | NCC Rating (A) | 403 | 403 | 403 | 403 | 403
|  |  |  | DER Forecast under System Normal (A) | 75 | 100 | 124 | 145 | 166
|  |  |  | Power Factor | 0.99985 | 0.99928 | 0.99847 | 0.9974 | 0.99625
|  |  |  | ECC Rating (A) | 403 | 403 | 403 | 403 | 403
|  |  |  | DER Forecast under N-1 Contingency (A) | 133 | 178 | 218 | 256 | 292
Nambour Bulk | 489-1 | Nambour BS | Yandina | NCC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | DER Forecast under System Normal (A) | 37 | 45 | 59 | 73 | 87
|  |  |  | Power Factor | 0.97644 | 0.97342 | 0.96758 | 0.96181 | 0.95603
|  |  |  | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | DER Forecast under N-1 Contingency (A) | 76 | 92 | 120 | 148 | 175
Nudgee Bulk | 3280-1 | Hendra | Clayfield | NCC Rating (A) | 725 | 725 | 725 | 725 | 725
|  |  |  | DER Forecast under System Normal (A) | 15 | 6 | 11 | 21 | 31
|  |  |  | Power Factor | 0.92015 | 0.30493 | 0.84684 | 0.96202 | 0.98491
|  |  |  | ECC Rating (A) | 725 | 725 | 725 | 725 | 725
|  |  |  | DER Forecast under N-1 Contingency (A) | 28 | 7 | 19 | 40 | 61
Nudgee Bulk | 540-1 | Hendra | Nundah | NCC Rating (A) | 814 | 814 | 814 | 814 | 814
|  |  |  | DER Forecast under System Normal (A) | 26 | 15 | 15 | 16 | 26
|  |  |  | Power Factor | 0.82706 | 0.44851 | 0.48218 | 0.64656 | 0.89952
|  |  |  | ECC Rating (A) | 814 | 814 | 814 | 814 | 814
|  |  |  | DER Forecast under N-1 Contingency (A) | 40 | 20 | 24 | 38 | 51
Nudgee Bulk | 593-1 | Nudgee BS | Nundah | NCC Rating (A) | 696 | 696 | 696 | 696 | 696
|  |  |  | DER Forecast under System Normal (A) | 41 | 19 | 34 | 50 | 75
|  |  |  | Power Factor | 0.87798 | 0.11112 | 0.85064 | 0.93984 | 0.97766
|  |  |  | ECC Rating (A) | 696 | 696 | 696 | 696 | 696
|  |  |  | DER Forecast under N-1 Contingency (A) | 55 | 23 | 42 | 63 | 98
Nudgee Bulk | 604-1 | Nudgee BS | Geebung | NCC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | DER Forecast under System Normal (A) | 28 | 27 | 28 | 32 | 37
|  |  |  | Power Factor | 0.23047 | 0.11971 | 0.27221 | 0.55295 | 0.71683
|  |  |  | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | DER Forecast under N-1 Contingency (A) | 33 | 32 | 34 | 41 | 50
Nudgee Bulk | 605-1 | Nudgee BS | Geebung | NCC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | DER Forecast under System Normal (A) | 28 | 27 | 28 | 32 | 37
|  |  |  | Power Factor | 0.23066 | 0.11981 | 0.27243 | 0.55328 | 0.71713
|  |  |  | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | DER Forecast under N-1 Contingency (A) | 33 | 32 | 34 | 41 | 50
Nudgee Bulk | 622-1 | Nudgee BS | Hendra | NCC Rating (A) | 738 | 738 | 738 | 738 | 738
|  |  |  | DER Forecast under System Normal (A) | 37 | 21 | 26 | 34 | 53
|  |  |  | Power Factor | 0.85995 | 0.33254 | 0.63964 | 0.79937 | 0.92203
|  |  |  | ECC Rating (A) | 738 | 738 | 738 | 738 | 738
|  |  |  | DER Forecast under N-1 Contingency (A) | 57 | 28 | 41 | 57 | 89
Nudgee Bulk | 623-1 | Nudgee BS | Hendra | NCC Rating (A) | 738 | 738 | 738 | 738 | 738
|  |  |  | DER Forecast under System Normal (A) | 37 | 21 | 26 | 34 | 53
|  |  |  | Power Factor | 0.85995 | 0.33254 | 0.63964 | 0.79937 | 0.92203
|  |  |  | ECC Rating (A) | 738 | 738 | 738 | 738 | 738
|  |  |  | DER Forecast under N-1 Contingency (A) | 57 | 28 | 41 | 57 | 89
Nudgee Bulk | 636-1 | Hendra | Clayfield | NCC Rating (A) | 725 | 725 | 725 | 725 | 725
|  |  |  | DER Forecast under System Normal (A) | 15 | 6 | 11 | 21 | 31
|  |  |  | Power Factor | 0.91958 | 0.30503 | 0.84649 | 0.96206 | 0.98498
|  |  |  | ECC Rating (A) | 725 | 725 | 725 | 725 | 725
|  |  |  | DER Forecast under N-1 Contingency (A) | 28 | 7 | 19 | 40 | 61
Nudgee Bulk | 643-1 | Hendra | Hamilton | NCC Rating (A) | 711 | 711 | 711 | 711 | 711
|  |  |  | DER Forecast under System Normal (A) | 29 | 20 | 11 | 5 | 6
|  |  |  | Power Factor | 0.99328 | 0.98327 | 0.94211 | 0.53927 | 0.80423
|  |  |  | ECC Rating (A) | 711 | 711 | 711 | 711 | 711
|  |  |  | DER Forecast under N-1 Contingency (A) | 58 | 39 | 21 | 6 | 11
Sandgate Bulk | 664-1 | Geebung | Zillmere | NCC Rating (A) | 410 | 410 | 410 | 410 | 410
|  |  |  | DER Forecast under System Normal (A) | 25 | 25 | 25 | 25 | 25
|  |  |  | Power Factor | 7.3809e-05 | 7.3809e-05 | 7.3809e-05 | 7.3809e-05 | 7.3809e-05
|  |  |  | ECC Rating (A) | 410 | 410 | 410 | 410 | 410
|  |  |  | DER Forecast under N-1 Contingency (A) | 25 | 25 | 25 | 25 | 25
Nudgee Bulk | 674-1 | Hendra | Hamilton | NCC Rating (A) | 711 | 711 | 711 | 711 | 711
|  |  |  | DER Forecast under System Normal (A) | 29 | 20 | 11 | 5 | 6
|  |  |  | Power Factor | 0.99327 | 0.98324 | 0.94199 | 0.53878 | 0.80376
|  |  |  | ECC Rating (A) | 711 | 711 | 711 | 711 | 711
|  |  |  | DER Forecast under N-1 Contingency (A) | 58 | 39 | 21 | 6 | 11
Nudgee Bulk | 683-1 | Nudgee BS | Geebung | NCC Rating (A) | 478 | 478 | 478 | 478 | 478
|  |  |  | DER Forecast under System Normal (A) | 29 | 28 | 29 | 33 | 38
|  |  |  | Power Factor | 0.23513 | 0.13013 | 0.23629 | 0.50377 | 0.66769
|  |  |  | ECC Rating (A) | 478 | 478 | 478 | 478 | 478
|  |  |  | DER Forecast under N-1 Contingency (A) | 33 | 32 | 34 | 41 | 50
Postmans Ridge Bulk | 376-1 | Postmans Ridge BS | Helidon | NCC Rating (A) | 290 | 582 | 582 | 582 | 582
|  |  |  | DER Forecast under System Normal (A) | 10 | 13 | 16 | 18 | 20
|  |  |  | Power Factor | 0.99799 | 0.99887 | 0.99939 | 0.99965 | 0.9998
|  |  |  | ECC Rating (A) | 290 | 582 | 582 | 582 | 582
|  |  |  | DER Forecast under N-1 Contingency (A) | 10 | 13 | 16 | 18 | 20
Postmans Ridge Bulk | 379-1 | Postmans Ridge BS | Carpendale | NCC Rating (A) | 200 | 200 | 200 | 200 | 200
|  |  |  | DER Forecast under System Normal (A) | 6 | 7 | 7 | 8 | 8
|  |  |  | Power Factor | 0.97922 | 0.98423 | 0.98718 | 0.98907 | 0.99036
|  |  |  | ECC Rating (A) | 200 | 200 | 200 | 200 | 200
|  |  |  | DER Forecast under N-1 Contingency (A) | 6 | 7 | 7 | 8 | 8
Postmans Ridge Bulk | 379-2 | Carpendale | Tenthill | NCC Rating (A) | 154 | 154 | 154 | 154 | 154
|  |  |  | DER Forecast under System Normal (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 1.8786e-05 | 1.8787e-05 | 1.8786e-05 | 1.8785e-05 | 1.8788e-05
|  |  |  | ECC Rating (A) | 154 | 154 | 154 | 154 | 154
|  |  |  | DER Forecast under N-1 Contingency (A) | 0 | 0 | 0 | 0 | 0
Raceview Bulk | 354-1 | Raceview BS | Roderick St | NCC Rating (A) | 497 | 497 | 497 | 497 | 497
|  |  |  | DER Forecast under System Normal (A) | 60 | 55 | 52 | 49 | 47
|  |  |  | Power Factor | 0.99866 | 0.99843 | 0.99819 | 0.99794 | 0.99768
|  |  |  | ECC Rating (A) | 497 | 497 | 497 | 497 | 497
|  |  |  | DER Forecast under N-1 Contingency (A) | 114 | 109 | 104 | 101 | 99
Raceview Bulk | 355-1 | Roderick St | Booval | NCC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | DER Forecast under System Normal (A) | 54 | 53 | 53 | 52 | 52
|  |  |  | Power Factor | 1 | 0.99998 | 0.99995 | 0.99991 | 0.99988
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | DER Forecast under N-1 Contingency (A) | 114 | 109 | 105 | 101 | 99
Raceview Bulk | 361-1 | Raceview BS | Booval | NCC Rating (A) | 631 | 631 | 631 | 631 | 631
|  |  |  | DER Forecast under System Normal (A) | 11 | 3 | 6 | 12 | 17
|  |  |  | Power Factor | 0.99822 | 0.6923 | 0.99787 | 0.99965 | 0.99986
|  |  |  | ECC Rating (A) | 631 | 631 | 631 | 631 | 631
|  |  |  | DER Forecast under N-1 Contingency (A) | 44 | 32 | 34 | 40 | 45
Raceview Bulk | 362-1 | Raceview BS | 362 Tee1 | NCC Rating (A) | 357 | 357 | 357 | 357 | 357
|  |  |  | DER Forecast under System Normal (A) | 12 | 8 | 7 | 7 | 11
|  |  |  | Power Factor | 0.93002 | 0.75017 | 0.49629 | 0.27339 | 0.66513
|  |  |  | ECC Rating (A) | 357 | 357 | 357 | 357 | 357
|  |  |  | DER Forecast under N-1 Contingency (A) | 22 | 35 | 61 | 92 | 124
Raceview Bulk | 362-2 | 362 Tee1 | Flinders | NCC Rating (A) | 708 | 708 | 708 | 708 | 708
|  |  |  | DER Forecast under System Normal (A) | 24 | 25 | 28 | 29 | 31
|  |  |  | Power Factor | 0.86054 | 0.84303 | 0.85703 | 0.83669 | 0.81648
|  |  |  | ECC Rating (A) | 708 | 708 | 708 | 708 | 708
|  |  |  | DER Forecast under N-1 Contingency (A) | 37 | 40 | 47 | 74 | 102
Raceview Bulk | 362-3 | 362 Tee1 | Kalbar | NCC Rating (A) | 708 | 708 | 708 | 708 | 708
|  |  |  | DER Forecast under System Normal (A) | 12 | 17 | 23 | 28 | 33
|  |  |  | Power Factor | 0.79176 | 0.88804 | 0.92818 | 0.94851 | 0.96112
|  |  |  | ECC Rating (A) | 708 | 708 | 708 | 708 | 708
|  |  |  | DER Forecast under N-1 Contingency (A) | 20 | 30 | 39 | 49 | 59
Raceview Bulk | 363-1 | Raceview BS | 363 Tee1 | NCC Rating (A) | 351 | 351 | 351 | 351 | 351
|  |  |  | DER Forecast under System Normal (A) | 11 | 7 | 6 | 7 | 11
|  |  |  | Power Factor | 0.92599 | 0.69528 | 0.35904 | 0.40002 | 0.70712
|  |  |  | ECC Rating (A) | 351 | 351 | 351 | 351 | 351
|  |  |  | DER Forecast under N-1 Contingency (A) | 21 | 33 | 57 | 86 | 116
Raceview Bulk | 363-2 | 363 Tee1 | Flinders | NCC Rating (A) | 403 | 403 | 403 | 403 | 403
|  |  |  | DER Forecast under System Normal (A) | 19 | 19 | 21 | 20 | 20
|  |  |  | Power Factor | 0.9166 | 0.91132 | 0.92711 | 0.91703 | 0.90527
|  |  |  | ECC Rating (A) | 403 | 403 | 403 | 403 | 403
|  |  |  | DER Forecast under N-1 Contingency (A) | 36 | 39 | 45 | 64 | 89
Raceview Bulk | 363-3 | 363 Tee1 | Kalbar | NCC Rating (A) | 374 | 374 | 374 | 374 | 374
|  |  |  | DER Forecast under System Normal (A) | 9 | 13 | 17 | 22 | 26
|  |  |  | Power Factor | 0.90793 | 0.97464 | 0.99224 | 0.99805 | 0.99982
|  |  |  | ECC Rating (A) | 374 | 374 | 374 | 374 | 374
|  |  |  | DER Forecast under N-1 Contingency (A) | 20 | 30 | 39 | 49 | 58
Raceview Bulk | 3960-1 | Ipswich Sth | Yamanto | NCC Rating (A) | 711 | 711 | 711 | 711 | 711
|  |  |  | DER Forecast under System Normal (A) | 40 | 76 | 122 | 175 | 230
|  |  |  | Power Factor | 0.95878 | 0.98534 | 0.98918 | 0.98959 | 0.98806
|  |  |  | ECC Rating (A) | 711 | 711 | 711 | 711 | 711
|  |  |  | DER Forecast under N-1 Contingency (A) | 74 | 108 | 156 | 207 | 261
Raceview Bulk | 3972-1 | Yamanto | Flinders | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under System Normal (A) | 103 | 103 | 103 | 103 | 103
|  |  |  | Power Factor | 0.94813 | 0.94814 | 0.94814 | 0.94815 | 0.94816
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under N-1 Contingency (A) | 103 | 103 | 153 | 201 | 252
Raceview Bulk | 3980-1 | Kalbar | Boonah | NCC Rating (A) | 713 | 713 | 713 | 713 | 713
|  |  |  | DER Forecast under System Normal (A) | 5 | 5 | 6 | 6 | 7
|  |  |  | Power Factor | 0.64555 | 0.74469 | 0.80139 | 0.83576 | 0.85663
|  |  |  | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
|  |  |  | DER Forecast under N-1 Contingency (A) | 8 | 9 | 11 | 12 | 13
Raceview Bulk | 401-1 | Kalbar | Boonah | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under System Normal (A) | 4 | 5 | 6 | 6 | 7
|  |  |  | Power Factor | 0.66404 | 0.76284 | 0.81812 | 0.85119 | 0.87124
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under N-1 Contingency (A) | 6 | 8 | 9 | 11 | 12
Raceview Bulk | 411-1 | Raceview BS | Booval | NCC Rating (A) | 558 | 558 | 558 | 558 | 558
|  |  |  | DER Forecast under System Normal (A) | 9 | 2 | 5 | 10 | 14
|  |  |  | Power Factor | 0.99988 | 0.99475 | 0.99743 | 0.99862 | 0.99882
|  |  |  | ECC Rating (A) | 558 | 558 | 558 | 558 | 558
|  |  |  | DER Forecast under N-1 Contingency (A) | 37 | 27 | 29 | 34 | 38
Raceview Bulk | 509A-1 | Raceview BS | Ipswich Sth | NCC Rating (A) | 721 | 721 | 721 | 721 | 721
|  |  |  | DER Forecast under System Normal (A) | 57 | 86 | 120 | 155 | 192
|  |  |  | Power Factor | 0.99839 | 0.99907 | 0.99833 | 0.99733 | 0.99585
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | DER Forecast under N-1 Contingency (A) | 112 | 170 | 235 | 305 | 376
Raceview Bulk | 509B-1 | Raceview BS | Cooneana | NCC Rating (A) | 455 | 455 | 455 | 455 | 455
|  |  |  | DER Forecast under System Normal (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 8.6763e-06 | 8.6756e-06 | 8.6751e-06 | 8.6761e-06 | 8.6756e-06
|  |  |  | ECC Rating (A) | 455 | 455 | 455 | 455 | 455
|  |  |  | DER Forecast under N-1 Contingency (A) | 0 | 0 | 0 | 0 | 0
Raceview Bulk | 510A-1 | Raceview BS | Ipswich Sth | NCC Rating (A) | 721 | 721 | 721 | 721 | 721
|  |  |  | DER Forecast under System Normal (A) | 57 | 86 | 118 | 154 | 190
|  |  |  | Power Factor | 0.99833 | 0.99904 | 0.9983 | 0.9973 | 0.99583
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | DER Forecast under N-1 Contingency (A) | 112 | 170 | 235 | 305 | 376
Raceview Bulk | 510B-1 | Raceview BS | Cooneana | NCC Rating (A) | 426 | 426 | 426 | 426 | 426
|  |  |  | DER Forecast under System Normal (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 1.6338e-05 | 1.6338e-05 | 1.6339e-05 | 1.6338e-05 | 1.6339e-05
|  |  |  | ECC Rating (A) | 426 | 426 | 426 | 426 | 426
|  |  |  | DER Forecast under N-1 Contingency (A) | 1 | 1 | 1 | 1 | 1
Richlands Bulk | 3818-1 | Richlands BS | Wacol | NCC Rating (A) | 750 | 750 | 750 | 750 | 750
|  |  |  | DER Forecast under System Normal (A) | 33 | 54 | 51 | 46 | 41
|  |  |  | Power Factor | 0.96214 | 0.98873 | 0.98635 | 0.98278 | 0.97687
|  |  |  | ECC Rating (A) | 750 | 750 | 750 | 750 | 750
|  |  |  | DER Forecast under N-1 Contingency (A) | 65 | 109 | 101 | 92 | 81
Richlands Bulk | 454-1 | Richlands BS | Wacol Sth | NCC Rating (A) | 430 | 430 | 430 | 430 | 430
|  |  |  | DER Forecast under System Normal (A) | 7 | 11 | 7 | 5 | 3
|  |  |  | Power Factor | 0.96527 | 0.98835 | 0.97166 | 0.92373 | 0.7722
|  |  |  | ECC Rating (A) | 430 | 430 | 430 | 430 | 430
|  |  |  | DER Forecast under N-1 Contingency (A) | 13 | 22 | 14 | 9 | 5
Richlands Bulk | 455-1 | Richlands BS | Wacol Sth | NCC Rating (A) | 430 | 430 | 430 | 430 | 430
|  |  |  | DER Forecast under System Normal (A) | 7 | 11 | 7 | 5 | 3
|  |  |  | Power Factor | 0.96427 | 0.98799 | 0.97083 | 0.92173 | 0.76769
|  |  |  | ECC Rating (A) | 430 | 430 | 430 | 430 | 430
|  |  |  | DER Forecast under N-1 Contingency (A) | 13 | 22 | 14 | 9 | 5
Richlands Bulk | 543-1 | Inala | 543 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under System Normal (A) | 3 | 3 | 3 | 3 | 3
|  |  |  | Power Factor | 0.00012567 | 0.00012567 | 0.00012567 | 0.00012567 | 0.00012567
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under N-1 Contingency (A) | 3 | 3 | 3 | 3 | 3
Richlands Bulk | 543-2 | 543 Tee1 | Coopers Plains | NCC Rating (A) | 348 | 348 | 348 | 348 | 348
|  |  |  | DER Forecast under System Normal (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 5.5492e-06 | 5.5492e-06 | 5.5492e-06 | 5.5492e-06 | 5.5492e-06
|  |  |  | ECC Rating (A) | 348 | 348 | 348 | 348 | 348
|  |  |  | DER Forecast under N-1 Contingency (A) | 0 | 0 | 0 | 0 | 0
Richlands Bulk | 543-3 | 543 Tee1 | Heathwood | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under System Normal (A) | 2 | 2 | 2 | 2 | 2
|  |  |  | Power Factor | 8.8129e-05 | 8.8129e-05 | 8.8129e-05 | 8.8129e-05 | 8.8129e-05
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under N-1 Contingency (A) | 2 | 2 | 2 | 2 | 2
Richlands Bulk | 616-1 | Richlands BS | Darra | NCC Rating (A) | 407 | 407 | 407 | 407 | 407
|  |  |  | DER Forecast under System Normal (A) | 143 | 143 | 143 | 143 | 143
|  |  |  | Power Factor | 0.019427 | 0.031961 | 0.032301 | 0.001091 | 0.027543
|  |  |  | ECC Rating (A) | 440 | 440 | 440 | 440 | 440
|  |  |  | DER Forecast under N-1 Contingency (A) | 222 | 223 | 223 | 222 | 222
Richlands Bulk | 617-1 | Richlands BS | Darra | NCC Rating (A) | 407 | 407 | 407 | 407 | 407
|  |  |  | DER Forecast under System Normal (A) | 148 | 148 | 148 | 148 | 148
|  |  |  | Power Factor | 0.019453 | 0.032005 | 0.032345 | 0.0010925 | 0.027581
|  |  |  | ECC Rating (A) | 440 | 440 | 440 | 440 | 440
|  |  |  | DER Forecast under N-1 Contingency (A) | 225 | 226 | 226 | 225 | 225
Richlands Bulk | 618-1 | Richlands BS | Inala | NCC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under System Normal (A) | 19 | 26 | 32 | 36 | 40
|  |  |  | Power Factor | 0.99205 | 0.99644 | 0.99796 | 0.99862 | 0.99897
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | DER Forecast under N-1 Contingency (A) | 31 | 43 | 53 | 60 | 65
Richlands Bulk | 619-1 | Richlands BS | Inala | NCC Rating (A) | 550 | 550 | 550 | 550 | 550
|  |  |  | DER Forecast under System Normal (A) | 12 | 17 | 21 | 24 | 26
|  |  |  | Power Factor | 0.99392 | 0.99734 | 0.99851 | 0.99901 | 0.99928
|  |  |  | ECC Rating (A) | 550 | 550 | 550 | 550 | 550
|  |  |  | DER Forecast under N-1 Contingency (A) | 31 | 43 | 53 | 60 | 65
Richlands Bulk | 620-1 | Richlands BS | Oxley | NCC Rating (A) | 324 | 324 | 324 | 324 | 324
|  |  |  | DER Forecast under System Normal (A) | 22 | 43 | 35 | 28 | 25
|  |  |  | Power Factor | 0.71652 | 0.99981 | 0.99955 | 0.99903 | 0.79762
|  |  |  | ECC Rating (A) | 359 | 359 | 359 | 359 | 359
|  |  |  | DER Forecast under N-1 Contingency (A) | 30 | 84 | 69 | 54 | 39
Richlands Bulk | 621-1 | Richlands BS | Oxley | NCC Rating (A) | 324 | 324 | 324 | 324 | 324
|  |  |  | DER Forecast under System Normal (A) | 21 | 41 | 34 | 26 | 24
|  |  |  | Power Factor | 0.7055 | 0.99952 | 0.99962 | 0.99961 | 0.78988
|  |  |  | ECC Rating (A) | 359 | 359 | 359 | 359 | 359
|  |  |  | DER Forecast under N-1 Contingency (A) | 30 | 84 | 69 | 54 | 39
Richlands Bulk | 641-1 | Darra | Jindalee | NCC Rating (A) | 703 | 703 | 703 | 703 | 703
|  |  |  | DER Forecast under System Normal (A) | 12 | 12 | 12 | 12 | 13
|  |  |  | Power Factor | 0.33812 | 0.087024 | 0.14043 | 0.31876 | 0.44535
|  |  |  | ECC Rating (A) | 703 | 703 | 703 | 703 | 703
|  |  |  | DER Forecast under N-1 Contingency (A) | 14 | 12 | 12 | 13 | 16
Richlands Bulk | 642-1 | Darra | Jindalee | NCC Rating (A) | 703 | 703 | 703 | 703 | 703
|  |  |  | DER Forecast under System Normal (A) | 12 | 12 | 12 | 12 | 13
|  |  |  | Power Factor | 0.33682 | 0.087326 | 0.13817 | 0.31503 | 0.44081
|  |  |  | ECC Rating (A) | 703 | 703 | 703 | 703 | 703
|  |  |  | DER Forecast under N-1 Contingency (A) | 14 | 12 | 12 | 13 | 16
Richlands Bulk | 679-1 | Richlands BS | Wacol | NCC Rating (A) | 605 | 605 | 605 | 605 | 605
|  |  |  | DER Forecast under System Normal (A) | 33 | 55 | 51 | 47 | 41
|  |  |  | Power Factor | 0.98086 | 0.99484 | 0.99362 | 0.99177 | 0.98868
|  |  |  | ECC Rating (A) | 605 | 605 | 605 | 605 | 605
|  |  |  | DER Forecast under N-1 Contingency (A) | 65 | 109 | 101 | 92 | 81
Richlands Bulk | 680-1 | Richlands BS | Wacol | NCC Rating (A) | 750 | 750 | 750 | 750 | 750
|  |  |  | DER Forecast under System Normal (A) | 65 | 108 | 101 | 92 | 81
|  |  |  | Power Factor | 0.99361 | 0.99855 | 0.99875 | 0.99842 | 0.99716
|  |  |  | ECC Rating (A) | 750 | 750 | 750 | 750 | 750
|  |  |  | DER Forecast under N-1 Contingency (A) | 65 | 108 | 101 | 92 | 81
Richlands Bulk | 700-1 | Richlands BS | Darra | NCC Rating (A) | 517 | 517 | 517 | 517 | 517
|  |  |  | DER Forecast under System Normal (A) | 113 | 114 | 114 | 113 | 113
|  |  |  | Power Factor | 0.059917 | 0.11102 | 0.11136 | 0.078174 | 0.051828
|  |  |  | ECC Rating (A) | 517 | 517 | 517 | 517 | 517
|  |  |  | DER Forecast under N-1 Contingency (A) | 176 | 176 | 176 | 176 | 176
Runcorn Bulk | 3440-1 | Runcorn BS | Sunnybank | NCC Rating (A) | 544 | 544 | 544 | 544 | 544
|  |  |  | DER Forecast under System Normal (A) | 104 | 101 | 99 | 97 | 110
|  |  |  | Power Factor | 0.9998 | 0.99978 | 0.99976 | 0.99975 | 0.99983
|  |  |  | ECC Rating (A) | 544 | 544 | 544 | 544 | 544
|  |  |  | DER Forecast under N-1 Contingency (A) | 126 | 123 | 120 | 117 | 133
Runcorn Bulk | 433-1 | Runcorn BS | Calamvale | NCC Rating (A) | 406 | 406 | 406 | 406 | 406
|  |  |  | DER Forecast under System Normal (A) | 2 | 2 | 2 | 2 | 2
|  |  |  | Power Factor | 1.7626e-05 | 1.7626e-05 | 1.7626e-05 | 1.7626e-05 | 1.7626e-05
|  |  |  | ECC Rating (A) | 406 | 406 | 406 | 406 | 406
|  |  |  | DER Forecast under N-1 Contingency (A) | 2 | 2 | 2 | 2 | 2
Runcorn Bulk | 434-1 | Runcorn | Calamvale | NCC Rating (A) | 406 | 406 | 406 | 406 | 406
|  |  |  | DER Forecast under System Normal (A) | 2 | 2 | 2 | 2 | 2
|  |  |  | Power Factor | 5.1614e-05 | 5.1614e-05 | 5.1614e-05 | 5.1614e-05 | 5.1614e-05
|  |  |  | ECC Rating (A) | 406 | 406 | 406 | 406 | 406
|  |  |  | DER Forecast under N-1 Contingency (A) | 2 | 2 | 2 | 2 | 2
Runcorn Bulk | 459A-1 | Upper Mt Gravatt | Sunnybank | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under System Normal (A) | 22 | 22 | 21 | 21 | 24
|  |  |  | Power Factor | 0.96223 | 0.96173 | 0.9613 | 0.96091 | 0.96309
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under N-1 Contingency (A) | 127 | 123 | 120 | 118 | 133
Runcorn Bulk | 459B-1 | Runcorn BS | Upper Mt Gravatt | NCC Rating (A) | 801 | 801 | 801 | 801 | 801
|  |  |  | DER Forecast under System Normal (A) | 22 | 22 | 21 | 21 | 23
|  |  |  | Power Factor | 0.96978 | 0.96667 | 0.964 | 0.96148 | 0.97498
|  |  |  | ECC Rating (A) | 801 | 801 | 801 | 801 | 801
|  |  |  | DER Forecast under N-1 Contingency (A) | 127 | 123 | 120 | 118 | 133
Runcorn Bulk | 667-1 | Runcorn BS | Acacia Ridge | NCC Rating (A) | 426 | 426 | 426 | 426 | 426
|  |  |  | DER Forecast under System Normal (A) | 28 | 28 | 28 | 28 | 28
|  |  |  | Power Factor | 9.2863e-05 | 9.2863e-05 | 9.2863e-05 | 9.2863e-05 | 9.2863e-05
|  |  |  | ECC Rating (A) | 426 | 426 | 426 | 426 | 426
|  |  |  | DER Forecast under N-1 Contingency (A) | 28 | 28 | 28 | 28 | 28
Runcorn Bulk | 668-1 | Runcorn BS | Acacia Ridge | NCC Rating (A) | 426 | 426 | 426 | 426 | 426
|  |  |  | DER Forecast under System Normal (A) | 28 | 28 | 28 | 28 | 28
|  |  |  | Power Factor | 9.3774e-05 | 9.3774e-05 | 9.3774e-05 | 9.3774e-05 | 9.3774e-05
|  |  |  | ECC Rating (A) | 426 | 426 | 426 | 426 | 426
|  |  |  | DER Forecast under N-1 Contingency (A) | 28 | 28 | 28 | 28 | 28
Runcorn Bulk | 690-1 | Runcorn BS | Runcorn | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under System Normal (A) | 57 | 77 | 97 | 115 | 128
|  |  |  | Power Factor | 1 | 0.99985 | 0.99953 | 0.99914 | 0.99879
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under N-1 Contingency (A) | 102 | 137 | 173 | 205 | 229
Runcorn Bulk | 691-1 | Runcorn BS | Runcorn | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under System Normal (A) | 45 | 61 | 77 | 91 | 101
|  |  |  | Power Factor | 0.99999 | 0.99982 | 0.99946 | 0.99904 | 0.99867
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under N-1 Contingency (A) | 102 | 137 | 173 | 205 | 229
Runcorn Bulk | 694-1 | Runcorn BS | Eight Mile Plains Bus 1 | NCC Rating (A) | 531 | 531 | 531 | 531 | 531
|  |  |  | DER Forecast under System Normal (A) | 46 | 81 | 120 | 147 | 178
|  |  |  | Power Factor | 0.87298 | 0.96792 | 0.99016 | 0.99598 | 0.99678
|  |  |  | ECC Rating (A) | 531 | 531 | 531 | 531 | 531
|  |  |  | DER Forecast under N-1 Contingency (A) | 46 | 81 | 120 | 147 | 178
Sandgate Bulk | 3290-1 | Sandgate BS | Bald Hills Bus 1 | NCC Rating (A) | 853 | 853 | 853 | 853 | 853
|  |  |  | DER Forecast under System Normal (A) | 34 | 42 | 51 | 59 | 68
|  |  |  | Power Factor | 0.97637 | 0.98627 | 0.99169 | 0.99492 | 0.99695
|  |  |  | ECC Rating (A) | 853 | 853 | 853 | 853 | 853
|  |  |  | DER Forecast under N-1 Contingency (A) | 34 | 42 | 51 | 59 | 68
Sandgate Bulk | 505-1 | Sandgate BS | Zilmere | NCC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | DER Forecast under System Normal (A) | 11 | 19 | 28 | 37 | 46
|  |  |  | Power Factor | 0.1657 | 0.78976 | 0.91234 | 0.95036 | 0.96743
|  |  |  | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | DER Forecast under N-1 Contingency (A) | 14 | 25 | 38 | 51 | 63
Sandgate Bulk | 524-1 | Sandgate BS | Geebung | NCC Rating (A) | 453 | 453 | 453 | 453 | 453
|  |  |  | DER Forecast under System Normal (A) | 9 | 13 | 19 | 25 | 31
|  |  |  | Power Factor | 0.1298 | 0.73827 | 0.89344 | 0.94327 | 0.9652
|  |  |  | ECC Rating (A) | 453 | 453 | 453 | 453 | 453
|  |  |  | DER Forecast under N-1 Contingency (A) | 15 | 23 | 34 | 45 | 55
Sandgate Bulk | 524-2 | Geebung | Zillmere | NCC Rating (A) | 410 | 410 | 410 | 410 | 410
|  |  |  | DER Forecast under System Normal (A) | 16 | 19 | 24 | 29 | 34
|  |  |  | Power Factor | 0.073606 | 0.51175 | 0.71799 | 0.81225 | 0.86181
|  |  |  | ECC Rating (A) | 410 | 410 | 410 | 410 | 410
|  |  |  | DER Forecast under N-1 Contingency (A) | 16 | 23 | 34 | 45 | 55
Sandgate Bulk | 561-1 | Sandgate BS | Brighton TR1 | NCC Rating (A) | 786 | 786 | 786 | 786 | 786
|  |  |  | DER Forecast under System Normal (A) | 26 | 31 | 35 | 39 | 42
|  |  |  | Power Factor | 0.99699 | 0.99785 | 0.99833 | 0.99865 | 0.99887
|  |  |  | ECC Rating (A) | 786 | 786 | 786 | 786 | 786
|  |  |  | DER Forecast under N-1 Contingency (A) | 50 | 60 | 68 | 76 | 82
Sandgate Bulk | 656-1 | Sandgate BS | Brighton TR2 | NCC Rating (A) | 270 | 270 | 270 | 270 | 270
|  |  |  | DER Forecast under System Normal (A) | 25 | 29 | 34 | 37 | 40
|  |  |  | Power Factor | 0.99864 | 0.99852 | 0.99841 | 0.99831 | 0.99823
|  |  |  | ECC Rating (A) | 270 | 270 | 270 | 270 | 270
|  |  |  | DER Forecast under N-1 Contingency (A) | 50 | 60 | 68 | 75 | 81
Sandgate Bulk | 671-1 | Sandagate BS | Zillmere | NCC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | DER Forecast under System Normal (A) | 15 | 10 | 16 | 22 | 26
|  |  |  | Power Factor | 0.094306 | 0.88628 | 0.96527 | 0.98502 | 0.99257
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | DER Forecast under N-1 Contingency (A) | 20 | 19 | 29 | 39 | 48
Brendale Bulk | 310-3 | 310 Tee1 | 569 Tee1 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under System Normal (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 2.0848e-06 | 2.0848e-06 | 2.0848e-06 | 2.0848e-06 | 2.0849e-06
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | DER Forecast under N-1 Contingency (A) | 0 | 0 | 0 | 0 | 0
Stafford Bulk | 548-1 | Stafford BS | Enoggera | NCC Rating (A) | 836 | 836 | 836 | 836 | 836
|  |  |  | DER Forecast under System Normal (A) | 81 | 40 | 18 | 51 | 93
|  |  |  | Power Factor | 0.96888 | 0.88471 | 0.42251 | 0.97015 | 0.99673
|  |  |  | ECC Rating (A) | 963 | 963 | 963 | 963 | 963
|  |  |  | DER Forecast under N-1 Contingency (A) | 160 | 76 | 74 | 115 | 184
Stafford Bulk | 550-1 | Stafford BS | Chermside | NCC Rating (A) | 668 | 668 | 668 | 668 | 668
|  |  |  | DER Forecast under System Normal (A) | 91 | 85 | 79 | 74 | 70
|  |  |  | Power Factor | 0.9984 | 0.99782 | 0.99717 | 0.99649 | 0.99577
|  |  |  | ECC Rating (A) | 789 | 789 | 789 | 789 | 789
|  |  |  | DER Forecast under N-1 Contingency (A) | 182 | 169 | 158 | 148 | 140
Stafford Bulk | 551-1 | Stafford BS | Chermside | NCC Rating (A) | 668 | 668 | 668 | 668 | 668
|  |  |  | DER Forecast under System Normal (A) | 91 | 85 | 79 | 74 | 70
|  |  |  | Power Factor | 0.99839 | 0.9978 | 0.99716 | 0.99647 | 0.99575
|  |  |  | ECC Rating (A) | 789 | 789 | 789 | 789 | 789
|  |  |  | DER Forecast under N-1 Contingency (A) | 182 | 169 | 158 | 148 | 140
Stafford Bulk | 567-1 | Stafford BS | Kedron | NCC Rating (A) | 576 | 576 | 576 | 576 | 576
|  |  |  | DER Forecast under System Normal (A) | 16 | 31 | 48 | 66 | 83
|  |  |  | Power Factor | 0.34836 | 0.86958 | 0.95438 | 0.97859 | 0.98916
|  |  |  | ECC Rating (A) | 576 | 576 | 576 | 576 | 576
|  |  |  | DER Forecast under N-1 Contingency (A) | 19 | 55 | 93 | 129 | 166
Stafford Bulk | 568-1 | Stafford BS | Kedron | NCC Rating (A) | 576 | 576 | 576 | 576 | 576
|  |  |  | DER Forecast under System Normal (A) | 16 | 31 | 48 | 66 | 84
|  |  |  | Power Factor | 0.35028 | 0.87069 | 0.95463 | 0.97962 | 0.98977
|  |  |  | ECC Rating (A) | 576 | 576 | 576 | 576 | 576
|  |  |  | DER Forecast under N-1 Contingency (A) | 19 | 55 | 93 | 129 | 166
Stafford Bulk | 594-1 | Stafford BS | Enoggera | NCC Rating (A) | 836 | 836 | 836 | 836 | 836
|  |  |  | DER Forecast under System Normal (A) | 81 | 39 | 18 | 51 | 92
|  |  |  | Power Factor | 0.96873 | 0.88417 | 0.42139 | 0.96991 | 0.99668
|  |  |  | ECC Rating (A) | 963 | 963 | 963 | 963 | 963
|  |  |  | DER Forecast under N-1 Contingency (A) | 160 | 76 | 74 | 114 | 184
Stafford Bulk | 595-1 | Enoggera | Grovely | NCC Rating (A) | 720 | 720 | 720 | 720 | 720
|  |  |  | DER Forecast under System Normal (A) | 34 | 58 | 83 | 108 | 135
|  |  |  | Power Factor | 0.97631 | 0.99433 | 0.99861 | 0.99858 | 0.99779
|  |  |  | ECC Rating (A) | 720 | 720 | 720 | 720 | 720
|  |  |  | DER Forecast under N-1 Contingency (A) | 67 | 117 | 167 | 218 | 273
Stafford Bulk | 596-1 | Enoggera | Grovely | NCC Rating (A) | 720 | 720 | 720 | 720 | 720
|  |  |  | DER Forecast under System Normal (A) | 34 | 59 | 84 | 109 | 136
|  |  |  | Power Factor | 0.9769 | 0.99451 | 0.99868 | 0.99857 | 0.99778
|  |  |  | ECC Rating (A) | 720 | 720 | 720 | 720 | 720
|  |  |  | DER Forecast under N-1 Contingency (A) | 67 | 117 | 167 | 218 | 272
Stafford Bulk | 607-1 | Chermside | Zillmere | NCC Rating (A) | 416 | 416 | 416 | 416 | 416
|  |  |  | DER Forecast under System Normal (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 1.1685e-05 | 1.1685e-05 | 1.1685e-05 | 1.1685e-05 | 1.1685e-05
|  |  |  | ECC Rating (A) | 416 | 416 | 416 | 416 | 416
|  |  |  | DER Forecast under N-1 Contingency (A) | 1 | 1 | 1 | 1 | 1
Sunrise Hills Bulk | 308-1 | Perigian | 308 Tee1 | NCC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | DER Forecast under System Normal (A) | 91 | 157 | 219 | 278 | 335
|  |  |  | Power Factor | 0.99945 | 0.99854 | 0.99728 | 0.99571 | 0.99382
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | DER Forecast under N-1 Contingency (A) | 91 | 157 | 219 | 278 | 335
Sunrise Hills Bulk | 308-2 | 308 Tee1 | Coolum | NCC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | DER Forecast under System Normal (A) | 91 | 157 | 219 | 278 | 335
|  |  |  | Power Factor | 0.99954 | 0.99891 | 0.99805 | 0.99696 | 0.99567
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | DER Forecast under N-1 Contingency (A) | 91 | 157 | 219 | 278 | 335
Sunrise Hills Bulk | 308-3 | 308 Tee1 | 307 Tee2 | NCC Rating (A) | 529 | 529 | 529 | 529 | 529
|  |  |  | DER Forecast under System Normal (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 2.6222e-05 | 2.6219e-05 | 2.6219e-05 | 2.6217e-05 | 2.6219e-05
|  |  |  | ECC Rating (A) | 529 | 529 | 529 | 529 | 529
|  |  |  | DER Forecast under N-1 Contingency (A) | 0 | 0 | 0 | 0 | 0
Sunrise Hills Bulk | 3100-1 | Sunrise Hills BS | 3100 Tee1 | NCC Rating (A) | 793 | 793 | 793 | 793 | 793
|  |  |  | DER Forecast under System Normal (A) | 183 | 284 | 381 | 475 | 568
|  |  |  | Power Factor | 0.999 | 0.99586 | 0.9914 | 0.98571 | 0.97882
|  |  |  | ECC Rating (A) | 793 | 793 | 793 | 793 | 793
|  |  |  | DER Forecast under N-1 Contingency (A) | 183 | 284 | 381 | 475 | 568
Sunrise Hills Bulk | 3100-2 | 3100 Tee1 | Peregian | NCC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | DER Forecast under System Normal (A) | 183 | 284 | 381 | 475 | 568
|  |  |  | Power Factor | 0.99979 | 0.99875 | 0.99722 | 0.99526 | 0.99289
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | DER Forecast under N-1 Contingency (A) | 183 | 284 | 381 | 475 | 568
Sunrise Hills Bulk | 343-1 | Sunrise Hills BS | 343 Tee1 | NCC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | DER Forecast under System Normal (A) | 150 | 213 | 279 | 346 | 418
|  |  |  | Power Factor | 0.99956 | 0.99846 | 0.99686 | 0.99468 | 0.99189
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | DER Forecast under N-1 Contingency (A) | 247 | 357 | 470 | 589 | 715
Sunrise Hills Bulk | 343-2 | 343 Tee1 | Tewantin | NCC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | DER Forecast under System Normal (A) | 43 | 71 | 101 | 135 | 173
|  |  |  | Power Factor | 0.99848 | 0.99774 | 0.99628 | 0.9941 | 0.99085
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | DER Forecast under N-1 Contingency (A) | 141 | 215 | 294 | 378 | 471
Sunrise Hills Bulk | 343-3 | 343 Tee1 | Cooroy | NCC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | DER Forecast under System Normal (A) | 106 | 142 | 177 | 211 | 245
|  |  |  | Power Factor | 0.99997 | 0.99989 | 0.9996 | 0.99918 | 0.99874
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | DER Forecast under N-1 Contingency (A) | 106 | 142 | 177 | 211 | 245
Sunrise Hills Bulk | 346-1 | Sunrise Hills BS | 346 Tee1 | NCC Rating (A) | 976 | 976 | 976 | 976 | 976
|  |  |  | DER Forecast under System Normal (A) | 98 | 145 | 193 | 244 | 300
|  |  |  | Power Factor | 0.99948 | 0.99842 | 0.99683 | 0.99461 | 0.99161
|  |  |  | ECC Rating (A) | 976 | 976 | 976 | 976 | 976
|  |  |  | DER Forecast under N-1 Contingency (A) | 142 | 215 | 294 | 379 | 472
Sunrise Hills Bulk | 346-2 | 346 Tee1 | Tewantin | NCC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | DER Forecast under System Normal (A) | 98 | 145 | 193 | 244 | 300
|  |  |  | Power Factor | 0.99948 | 0.99842 | 0.99683 | 0.99461 | 0.99161
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | DER Forecast under N-1 Contingency (A) | 142 | 215 | 294 | 379 | 472
Sunrise Hills Bulk | 346-3 | 346 Tee1 | 3100 Tee1 | NCC Rating (A) | 529 | 529 | 529 | 529 | 529
|  |  |  | DER Forecast under System Normal (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0.00030689 | 0.00030659 | 0.00030614 | 0.00030635 | 0.00030656
|  |  |  | ECC Rating (A) | 529 | 529 | 529 | 529 | 529
|  |  |  | DER Forecast under N-1 Contingency (A) | 0 | 0 | 0 | 0 | 0
Sunrise Hills Bulk | 488-1 | Cooroy | 488 Tee1 | NCC Rating (A) | 582 | 582 | 582 | 582 | 582
|  |  |  | DER Forecast under System Normal (A) | 54 | 73 | 90 | 106 | 122
|  |  |  | Power Factor | 0.99993 | 0.99998 | 0.99981 | 0.99953 | 0.99919
|  |  |  | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
|  |  |  | DER Forecast under N-1 Contingency (A) | 54 | 73 | 90 | 106 | 122
Sunrise Hills Bulk | 488-3 | 488 Tee1 | 488 Tee2 | NCC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | DER Forecast under System Normal (A) | 54 | 73 | 90 | 106 | 122
|  |  |  | Power Factor | 0.99993 | 0.99999 | 0.99983 | 0.99958 | 0.99928
|  |  |  | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | DER Forecast under N-1 Contingency (A) | 54 | 73 | 90 | 106 | 122
Sunrise Hills Bulk | 488-4 | 488 Tee2 | Black Mtn | NCC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | DER Forecast under System Normal (A) | 30 | 39 | 48 | 56 | 64
|  |  |  | Power Factor | 0.99977 | 0.99959 | 0.9994 | 0.99913 | 0.9989
|  |  |  | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | DER Forecast under N-1 Contingency (A) | 30 | 39 | 48 | 56 | 64
Sunrise Hills Bulk | 488-5 | 488 Tee2 | 488 Tee3 | NCC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | DER Forecast under System Normal (A) | 24 | 33 | 42 | 51 | 58
|  |  |  | Power Factor | 0.999 | 0.99984 | 0.99999 | 0.99989 | 0.9997
|  |  |  | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | DER Forecast under N-1 Contingency (A) | 24 | 33 | 42 | 51 | 58
Sunrise Hills Bulk | 488-6 | 488 Tee3 | Eumundi | NCC Rating (A) | 438 | 438 | 438 | 438 | 438
|  |  |  | DER Forecast under System Normal (A) | 24 | 33 | 42 | 51 | 58
|  |  |  | Power Factor | 0.9998 | 0.99966 | 0.99946 | 0.99925 | 0.99897
|  |  |  | ECC Rating (A) | 438 | 438 | 438 | 438 | 438
|  |  |  | DER Forecast under N-1 Contingency (A) | 24 | 33 | 42 | 51 | 58
Sunrise Hills Bulk | 488-7 | 488 Tee3 | Yandina | NCC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | DER Forecast under System Normal (A) | 1 | 1 | 1 | 1 | 1
|  |  |  | Power Factor | 3.6886e-05 | 3.6886e-05 | 3.6886e-05 | 3.6886e-05 | 3.6886e-05
|  |  |  | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | DER Forecast under N-1 Contingency (A) | 1 | 1 | 1 | 1 | 1
Tennyson Bulk | 3390-1 | Taringa | Indooroopilly | NCC Rating (A) | 728 | 728 | 728 | 728 | 728
|  |  |  | DER Forecast under System Normal (A) | 7 | 9 | 14 | 18 | 23
|  |  |  | Power Factor | 0.034992 | 0.56248 | 0.80725 | 0.8832 | 0.91485
|  |  |  | ECC Rating (A) | 728 | 728 | 728 | 728 | 728
|  |  |  | DER Forecast under N-1 Contingency (A) | 13 | 14 | 20 | 26 | 33
Tennyson Bulk | 3393-1 | Tennyson BS | St Lucia TR1 | NCC Rating (A) | 610 | 610 | 610 | 610 | 610
|  |  |  | DER Forecast under System Normal (A) | 50 | 49 | 47 | 46 | 46
|  |  |  | Power Factor | 0.99975 | 0.99981 | 0.99985 | 0.99989 | 0.99991
|  |  |  | ECC Rating (A) | 610 | 610 | 610 | 610 | 610
|  |  |  | DER Forecast under N-1 Contingency (A) | 105 | 103 | 102 | 100 | 99
Tennyson Bulk | 3394-1 | Tennyson BS | St Lucia TR2 | NCC Rating (A) | 610 | 610 | 610 | 610 | 610
|  |  |  | DER Forecast under System Normal (A) | 105 | 103 | 101 | 100 | 99
|  |  |  | Power Factor | 0.99829 | 0.99834 | 0.99839 | 0.99842 | 0.99845
|  |  |  | ECC Rating (A) | 610 | 610 | 610 | 610 | 610
|  |  |  | DER Forecast under N-1 Contingency (A) | 105 | 103 | 101 | 100 | 99
Tennyson Bulk | 3460-1 | Annerley | Buranda | NCC Rating (A) | 802 | 802 | 802 | 802 | 802
|  |  |  | DER Forecast under System Normal (A) | 51 | 105 | 104 | 103 | 102
|  |  |  | Power Factor | 0.99839 | 0.99868 | 0.99872 | 0.99874 | 0.99875
|  |  |  | ECC Rating (A) | 802 | 802 | 802 | 802 | 802
|  |  |  | DER Forecast under N-1 Contingency (A) | 101 | 211 | 208 | 206 | 205
Tennyson Bulk | 3461-1 | Annerley | Buranda | NCC Rating (A) | 802 | 802 | 802 | 802 | 802
|  |  |  | DER Forecast under System Normal (A) | 51 | 105 | 104 | 103 | 102
|  |  |  | Power Factor | 0.9984 | 0.99869 | 0.99873 | 0.99875 | 0.99876
|  |  |  | ECC Rating (A) | 802 | 802 | 802 | 802 | 802
|  |  |  | DER Forecast under N-1 Contingency (A) | 101 | 211 | 208 | 206 | 205
Tennyson Bulk | 410-1 | Sherwood | Indooroopilly | NCC Rating (A) | 400 | 400 | 400 | 400 | 400
|  |  |  | DER Forecast under System Normal (A) | 62 | 52 | 45 | 39 | 33
|  |  |  | Power Factor | 0.94301 | 0.91749 | 0.88451 | 0.8389 | 0.77521
|  |  |  | ECC Rating (A) | 400 | 400 | 400 | 400 | 400
|  |  |  | DER Forecast under N-1 Contingency (A) | 100 | 89 | 89 | 89 | 88
Tennyson Bulk | 460-1 | Tennyson BS | Sherwood | NCC Rating (A) | 762 | 762 | 762 | 762 | 762
|  |  |  | DER Forecast under System Normal (A) | 20 | 28 | 45 | 63 | 80
|  |  |  | Power Factor | 0.10708 | 0.70766 | 0.91009 | 0.96043 | 0.9794
|  |  |  | ECC Rating (A) | 762 | 762 | 762 | 762 | 762
|  |  |  | DER Forecast under N-1 Contingency (A) | 26 | 38 | 63 | 89 | 114
Tennyson Bulk | 480-1 | Taringa | St Lucia | NCC Rating (A) | 610 | 610 | 610 | 610 | 610
|  |  |  | DER Forecast under System Normal (A) | 55 | 54 | 54 | 54 | 53
|  |  |  | Power Factor | 0.99783 | 0.99786 | 0.9979 | 0.99794 | 0.99799
|  |  |  | ECC Rating (A) | 610 | 610 | 610 | 610 | 610
|  |  |  | DER Forecast under N-1 Contingency (A) | 105 | 103 | 101 | 100 | 99
Tennyson Bulk | 504-1 | Tennyson BS | Taringa | NCC Rating (A) | 601 | 601 | 601 | 601 | 601
|  |  |  | DER Forecast under System Normal (A) | 39 | 27 | 17 | 18 | 26
|  |  |  | Power Factor | 0.89505 | 0.75935 | 0.29251 | 0.47608 | 0.81847
|  |  |  | ECC Rating (A) | 601 | 601 | 601 | 601 | 601
|  |  |  | DER Forecast under N-1 Contingency (A) | 58 | 40 | 27 | 31 | 43
Tennyson Bulk | 507A-1 | Toowong | Indooroopilly | NCC Rating (A) | 735 | 735 | 735 | 735 | 735
|  |  |  | DER Forecast under System Normal (A) | 7 | 9 | 14 | 19 | 23
|  |  |  | Power Factor | 0.046902 | 0.5783 | 0.81274 | 0.88456 | 0.91453
|  |  |  | ECC Rating (A) | 735 | 735 | 735 | 735 | 735
|  |  |  | DER Forecast under N-1 Contingency (A) | 13 | 15 | 20 | 26 | 33
Tennyson Bulk | 507B-1 | Toowong | Taringa | NCC Rating (A) | 727 | 727 | 727 | 727 | 727
|  |  |  | DER Forecast under System Normal (A) | 6 | 8 | 12 | 17 | 22
|  |  |  | Power Factor | 0.06197 | 0.71041 | 0.9249 | 0.97231 | 0.98825
|  |  |  | ECC Rating (A) | 727 | 727 | 727 | 727 | 727
|  |  |  | DER Forecast under N-1 Contingency (A) | 10 | 14 | 19 | 25 | 32
Tennyson Bulk | 511-1 | Tennyson BS | Moorooka | NCC Rating (A) | 739 | 739 | 739 | 739 | 739
|  |  |  | DER Forecast under System Normal (A) | 9 | 18 | 25 | 32 | 38
|  |  |  | Power Factor | 0.94157 | 0.98528 | 0.99349 | 0.99652 | 0.99793
|  |  |  | ECC Rating (A) | 739 | 739 | 739 | 739 | 739
|  |  |  | DER Forecast under N-1 Contingency (A) | 9 | 18 | 25 | 32 | 38
Tennyson Bulk | 514-1 | Tennyson BS | Moorooka | NCC Rating (A) | 739 | 739 | 739 | 739 | 739
|  |  |  | DER Forecast under System Normal (A) | 9 | 18 | 25 | 32 | 38
|  |  |  | Power Factor | 0.94443 | 0.98607 | 0.99385 | 0.99671 | 0.99805
|  |  |  | ECC Rating (A) | 739 | 739 | 739 | 739 | 739
|  |  |  | DER Forecast under N-1 Contingency (A) | 9 | 18 | 25 | 32 | 38
Tennyson Bulk | 515-1 | Tennyson BS | Sherwood | NCC Rating (A) | 740 | 740 | 740 | 740 | 740
|  |  |  | DER Forecast under System Normal (A) | 22 | 29 | 46 | 66 | 84
|  |  |  | Power Factor | 0.1246 | 0.72178 | 0.94684 | 0.97933 | 0.99059
|  |  |  | ECC Rating (A) | 740 | 740 | 740 | 740 | 740
|  |  |  | DER Forecast under N-1 Contingency (A) | 27 | 40 | 66 | 93 | 120
Tennyson Bulk | 523A-1 | Tennyson BS | Rocklea | NCC Rating (A) | 650 | 650 | 650 | 650 | 650
|  |  |  | DER Forecast under System Normal (A) | 8 | 8 | 8 | 8 | 8
|  |  |  | Power Factor | 8.7628e-06 | 8.7628e-06 | 8.7628e-06 | 8.7628e-06 | 8.7628e-06
|  |  |  | ECC Rating (A) | 650 | 650 | 650 | 650 | 650
|  |  |  | DER Forecast under N-1 Contingency (A) | 8 | 8 | 8 | 8 | 8
Tennyson Bulk | 539-1 | Sherwood | Kenmore | NCC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | DER Forecast under System Normal (A) | 41 | 57 | 71 | 83 | 93
|  |  |  | Power Factor | 0.99988 | 0.99925 | 0.99847 | 0.99771 | 0.99699
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | DER Forecast under N-1 Contingency (A) | 115 | 152 | 183 | 211 | 236
Tennyson Bulk | 554-1 | Tennyson BS | Sherwood | NCC Rating (A) | 716 | 716 | 716 | 716 | 716
|  |  |  | DER Forecast under System Normal (A) | 22 | 31 | 51 | 71 | 90
|  |  |  | Power Factor | 0.11636 | 0.72163 | 0.9172 | 0.96452 | 0.98205
|  |  |  | ECC Rating (A) | 716 | 716 | 716 | 716 | 716
|  |  |  | DER Forecast under N-1 Contingency (A) | 28 | 41 | 69 | 98 | 125
Tennyson Bulk | 571-1 | Indooroopilly | Kenmore | NCC Rating (A) | 527 | 527 | 527 | 527 | 527
|  |  |  | DER Forecast under System Normal (A) | 75 | 96 | 114 | 130 | 145
|  |  |  | Power Factor | 0.9999 | 1 | 0.99994 | 0.99979 | 0.9996
|  |  |  | ECC Rating (A) | 527 | 527 | 527 | 527 | 527
|  |  |  | DER Forecast under N-1 Contingency (A) | 116 | 152 | 184 | 213 | 237
Tennyson Bulk | 606-1 | Tennyson BS | Taringa | NCC Rating (A) | 601 | 601 | 601 | 601 | 601
|  |  |  | DER Forecast under System Normal (A) | 39 | 27 | 17 | 18 | 26
|  |  |  | Power Factor | 0.89555 | 0.76026 | 0.2933 | 0.47722 | 0.81935
|  |  |  | ECC Rating (A) | 601 | 601 | 601 | 601 | 601
|  |  |  | DER Forecast under N-1 Contingency (A) | 58 | 41 | 27 | 31 | 43
Tennyson Bulk | 637-1 | Tennyson BS | Annerley | NCC Rating (A) | 716 | 716 | 716 | 716 | 716
|  |  |  | DER Forecast under System Normal (A) | 58 | 101 | 89 | 79 | 70
|  |  |  | Power Factor | 0.98365 | 0.99821 | 0.99765 | 0.99705 | 0.99643
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | DER Forecast under N-1 Contingency (A) | 114 | 201 | 179 | 158 | 139
Tennyson Bulk | 638-1 | Tennyson BS | Annerley | NCC Rating (A) | 716 | 716 | 716 | 716 | 716
|  |  |  | DER Forecast under System Normal (A) | 58 | 101 | 90 | 79 | 70
|  |  |  | Power Factor | 0.98373 | 0.99822 | 0.99767 | 0.99708 | 0.99646
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | DER Forecast under N-1 Contingency (A) | 114 | 201 | 179 | 158 | 139
Tennyson Bulk | F703-1 | Sherwood | Indooroopilly | NCC Rating (A) | 400 | 400 | 400 | 400 | 400
|  |  |  | DER Forecast under System Normal (A) | 62 | 52 | 45 | 39 | 34
|  |  |  | Power Factor | 0.94363 | 0.91844 | 0.88584 | 0.8407 | 0.77754
|  |  |  | ECC Rating (A) | 400 | 400 | 400 | 400 | 400
|  |  |  | DER Forecast under N-1 Contingency (A) | 100 | 90 | 90 | 90 | 89
Victoria Park Bulk | 627-1 | Victoria Pk BS | Astor Tce | NCC Rating (A) | 415 | 415 | 415 | 415 | 415
|  |  |  | DER Forecast under System Normal (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0.96802 | 0.96802 | 0.96802 | 0.96802 | 0.96802
|  |  |  | ECC Rating (A) | 415 | 415 | 415 | 415 | 415
|  |  |  | DER Forecast under N-1 Contingency (A) | 0 | 0 | 0 | 0 | 0
Victoria Park Bulk | 628-1 | Victoria Pk BS | Astor Tce | NCC Rating (A) | 415 | 415 | 415 | 415 | 415
|  |  |  | DER Forecast under System Normal (A) | 117 | 116 | 115 | 114 | 113
|  |  |  | Power Factor | 0.99832 | 0.99835 | 0.99838 | 0.99841 | 0.99843
|  |  |  | ECC Rating (A) | 415 | 415 | 415 | 415 | 415
|  |  |  | DER Forecast under N-1 Contingency (A) | 237 | 235 | 233 | 230 | 228
Victoria Park Bulk | 639-1 | Victoria Pk BS | Newmarket | NCC Rating (A) | 503 | 503 | 503 | 503 | 503
|  |  |  | DER Forecast under System Normal (A) | 24 | 38 | 52 | 65 | 78
|  |  |  | Power Factor | 0.70795 | 0.89951 | 0.95221 | 0.97304 | 0.98348
|  |  |  | ECC Rating (A) | 503 | 503 | 503 | 503 | 503
|  |  |  | DER Forecast under N-1 Contingency (A) | 38 | 69 | 100 | 127 | 153
Victoria Park Bulk | 649-1 | Victoria Pk BS | Astor Tce | NCC Rating (A) | 415 | 415 | 415 | 415 | 415
|  |  |  | DER Forecast under System Normal (A) | 118 | 117 | 116 | 115 | 114
|  |  |  | Power Factor | 0.9984 | 0.99843 | 0.99845 | 0.99848 | 0.99851
|  |  |  | ECC Rating (A) | 415 | 415 | 415 | 415 | 415
|  |  |  | DER Forecast under N-1 Contingency (A) | 237 | 235 | 233 | 230 | 228
Victoria Park Bulk | 653-1 | Victoria Pk BS | Newmarket | NCC Rating (A) | 503 | 503 | 503 | 503 | 503
|  |  |  | DER Forecast under System Normal (A) | 24 | 38 | 52 | 65 | 78
|  |  |  | Power Factor | 0.70795 | 0.89951 | 0.95221 | 0.97304 | 0.98348
|  |  |  | ECC Rating (A) | 503 | 503 | 503 | 503 | 503
|  |  |  | DER Forecast under N-1 Contingency (A) | 38 | 69 | 100 | 127 | 153
Victoria Park Bulk | 689-1 | Victoria Pk BS | Astor Tce | NCC Rating (A) | 538 | 538 | 538 | 538 | 538
|  |  |  | DER Forecast under System Normal (A) | 9 | 9 | 9 | 9 | 9
|  |  |  | Power Factor | 1.0298e-05 | 1.0298e-05 | 1.0298e-05 | 1.0298e-05 | 1.0298e-05
|  |  |  | ECC Rating (A) | 538 | 538 | 538 | 538 | 538
|  |  |  | DER Forecast under N-1 Contingency (A) | 9 | 9 | 9 | 9 | 9