## Index
Index
Notes
AFD - Archerfield BS (110/33kV)
BDS - Beaudesert BS (110/33kV)
BLH - Beenleigh BS (110/33kV)
BWH - Beerwah BS (132/33kV)
BRD - Brendale BS (110/33kV)
BPN - Browns Plains BS (110/33kV)
BHD - Burleigh Heads BS (110/33kV)
CBT - Caboolture BS (110/33kV)
CVL - Cleveland BS (110/33kV)
CMA - Coomera BS (110/33kV)
CPR - Coorparoo BS (110/33kV)
DBS - Doboy BS (110/33kV)
GBS - Gatton BS (110/33kV)
GFN - Griffin BS (110/33kV)
GYM - Gympie BS (132/33kV)
HIL - Hays Inlet BS (110/33kV)
IBS - Ibis BS (110/33kV)
JBB - Jimboomba BS (110/33kV)
LRE - Lockrose BS (110/33kV)
LBS - Lytton BS (110/33kV)
MDH - Meeandah BS (110/33kV)
MTN - Myrtletown BS (110/33kV)
NBR - Nambour BS (132/33kV)
NGE - Nudgee BS (110/33kV)
PRG - Postmans Ridge BS (110/33kV)
RVW - Raceview BS (110/33kV)
SGT - Sandgate BS (110/33kV)
SFD - Stafford BS (110/33kV)
SIS - Stradbroke Is BS (110/33kV)
SRH - Sunrise Hills BS (132/33kV)
VPK - Victoria Park BS (110/33kV)

## Notes
Bulk Supply Substation Forecasts (Energex Distribution Annual Planning Report (2023-24 to 2027-28)
This workbook provides 5 year forecast capacity and loading information for Bulk Supply Substations in the Energex network.
Energex Distribution Annual Planning Report is prepared and made available solely for information purposes. While care was taken in the preparation of the information in this report, and it is provided in good faith, Energex accepts no responsibility or liability (including without limitation, liability to any person by reason of negligence or negligent mis-statement) for any loss or damage that may be incurred by any person acting in reliance on this information or assumptions drawn from it, except to the extent that liability under any applicable Queensland or Commonwealth of Australia statute cannot be excluded.
It contains assumptions regarding, among other things, economic growth and load forecasts which may or may not prove to be correct. The forecasts included in the document involve subjective judgements and analysis which are subject to significant uncertainties and contingencies, many of which are out of the control of Energex. Furthermore, forecasted data is subject to ongoing variation as new information becomes available. Energex makes no representation or warranty as to the accuracy, reliability, completeness or suitability for any particular purpose of the information in this document. All information should be independently investigated, reviewed, analysed and verified, and must not be relied upon in connection with any investment proposal or decision.
Each summary sheet contains a brief description of the substation, including its location, land area, construction type, installed transformers and capacity of known embedded generation connected to the substation. Localities give a general view of the areas serviced by the substation. Load categories indicate the type of loads supplied. Growth rates for the Jointly Owned Substations provide a projection of the expected growth rates for the next five years for planning purposes.
With respect to growth rates:
· Large individual or block loads (existing and new) are treated on an individual basis and not listed in these substation summaries, but these are factored into load forecasts.
The next section includes a summary of performance and capability.
The latest compensated peak demand is displayed along with the typical daily compensated load profile. In addition, the compensated descriptor refers to the slightly reduced transformer load experienced when available capacitors are in service. Entries in the major loads section indicate there are significant or large customers connected to the substation. Both summer and winter profiles are presented where available. Where a substation has less than 12 months of metering data available, such as small substations and newly established substations, the graphs and the information against these fields is either blank or not applicable (N/A).
The forecast and capacity accounts for committed projects, the project cut-off date for the winter season is 1 June of each year, and for the summer season is 1 December of each year. For example, 2024 winter forecast includes all committed projects with a proposed commissioning date up to 1 June 2024, and the 2023/24 summer forecast includes all committed projects with a proposed commissioning date up to 1 December 2023. The committed status of projects used in the forecast are taken as of 1 May 2023.
Term | Definition
Peak Risk Period | The time period over which the load is highest (Day/Night).
NCC Rating (MVA) | Normal Cyclic Capacity – the total capacity with all network components and equipment in service.
The maximum permissible peak daily loading for a given load cycle that plant can supply each day of its life. Taking impedance mismatch into consideration, it is considered the maximum rating for a transformer to be loaded under normal load conditions.
Contracted non-network (MVA) | The amount of embedded generation and contracted curtailed demand management capacity available within the supply area of a substation during peak times. The impacts of these have been incorporated into the load forecasts. Solar PV connections are not included in the reported figure.
10 PoE Load (MVA) | Peak load forecast with 10% probability of being exceeded (one in every 10 years will be exceeded). Based on normal expected growth rates & weather corrected starting loads.
LARn (MVA) | Security standard load at risk under system normal condition, expressed in MVA.
LARn (MW) | Security standard load at risk under system normal condition, expressed in MW.
Power Factor at Peak Load | Compensated power factor at 50 PoE Load. Capacitive compensation is switched according to the size of the capacitor banks installed at the substation, compensation is generally limited to prevent a substation from going into leading power factor.
ECC Rating (MVA) | Emergency Cyclic Capacity – the long term `.
The maximum permissible peak emergency loading for a given load cycle that an item of plant can supply for an extended period of time without unacceptable damage. For substations with multiple transformers, the ECC is the minimum emergency cyclic capacity of all transformer combinations taking impedance mismatches into consideration, with one transformer off line.
50 PoE Load (MVA) | Peak load forecast with 50% probability of being exceeded (one in every two years will be exceeded). Based on normal expected growth rates and weather corrected starting loads.
50 PoE Load > 95% (MVA) | The amount of load greater than 95% 50 PoE Load.
(50 PoE Load – 0.95 x 50 PoE Load)
Hours PA > 95% Peak Load | The number of hours per annum (maximum over the last 3 years) where the load exceeded 95% of the peak 50 PoE demand.
Raw LAR (MVA) | The amount of load exceeding ECC rating.
(50 PoE Load – ECC Rating)
2-Hour Rating (MVA) | Two-Hour Emergency Capacity (2HEC) – the short term or firm delivery capacity under a single contingent condition.
The maximum permissible peak emergency loading for a given load cycle that an item of plant can supply up to two hours without causing unacceptable damage. For substations with multiple transformers, the 2HEC is the minimum two hour emergency rating of all transformer combinations taking impedance mismatches into consideration, with one transformer off line.
Auto Trans Avail (MVA) | SCADA or automatically controlled load transfers that can be implemented within one minute.
Remote Trans Avail (MVA) | Load transfers that can be implemented through SCADA switching procedures by the network control officer. It is assumed that this can generally be achieved within 30 minutes excluding complex or prolonged restoration procedures.
Manual Trans Avail (MVA) | Load transfers can also be deployed via manually controlled switchgear locally by field staff. It is assumed that the implementation of manual switching procedures to isolate the faulted portion of the network to restore supply to healthy parts of the network can be fully implemented within three hours (urban) or four hours (rural).
Manual transfers are obtained from load flow studies performed on each 11 kV distribution feeder, with the sum of all available 11 kV transfers at a substation is multiplied by a 0.75 factor to account for diversity and to provide a margin of error to avoid voltage collapse. The same approach applies throughout the forward planning period.
Mobile Plant Avail (MVA) | The capacity of mobile substation or mobile generation that can be deployed within the timeframe prescribed by the security standard.
The maximum allowable mobile generator capacity is limited to 4 MVA for urban and 10 MVA for rural. The maximum mobile substation capacity is 15 MVA.
POPS | Plant Overload Protection Scheme consists of several applications which continuously monitor specific items of plant for overload conditions. If overload conditions are detected and validated, POPS will initiate predefined actions in order to relieve the overload condition.
Bus Configuration | An indication of the electrical configuration of the substation 11 kV bus (e.g. split bus or solid bus)
Capacity for Embedded Generation (MVA) | The total capacity for embedded generation to transfer power from lower voltage network to higher voltage network with all network components and equipment in service.
N-1 Capacity for Embedded Generation (MVA) | The firm capacity for embedded generation to transfer power from lower voltage network to higher voltage network under a single contingent condition.
LARc (MVA) | Security standard load at risk for single contingent conditions.
LARc (MW) | Estimated generation / load reduction required to defer the forecast system limitation. This is the security standard load at risk for a single contingency, expressed in MW.
Customer Category | For security standard application, the general type of customer a substation or feeder supplying the area.
The load at risk is evaluated for both normal (LARn) and contingent (LARc) conditions. Under normal conditions, the loadings on a substation are not to exceed the normal cyclic capacity (NCC) of a major network component such as a zone substation transformer. Under contingent conditions, the loadings of a substation are not to exceed the available emergency supply under contingency whilst taking into consideration the security of supply standards of the substation. It should be noted that for Jointly Owned substations, Energex typically only owns the switchgear at the connection point, and as such the Energex ratings will not reflect the rating of upstream equipment not owned by Energex.
Load at risk is the shortfall between the forecast load (either 10 PoE or 50 PoE) and the available supply. The general equations for LAR are as follows:
· LARn = 10 PoE – NCC where NCC is the normal cyclic capacity
· LARc = 50 PoE – available capacity – available supply (within security standard timeframe)
Network security standards are not being met if LARn or LARc is greater than 0.
Generally, there are two available capacities and five available sources of supply that can be deployed upon loss of a major network component such as a transformer.
Types of available capacity:
· Emergency Cyclic Capacity (ECC) – The maximum permissible peak emergency loading for a given load cycle that a plant can supply for an extended period of time without doing unacceptable damage. For substations with multiple transformers, the ECC is the minimum emergency cyclic capacity of all transformer combinations taking impedance mismatches into consideration, with one transformer off line.
· Two Hour Emergency Capacity (2HEC) – The maximum permissible peak emergency loading for a given load cycle that a plant can supply up to two hours without doing unacceptable damage. For substations with multiple transformer, the 2HEC is the minimum 2 hour emergency rating of all transformer combinations taking impedance mismatches into consideration, with one transformer off line. By the end of the 2 hours, the transformer load must be reduced to or below ECC.
Types of available supply:
· Automatic Transfers (AT) – SCADA or automatically controlled load transfers that can be implemented within 1 minute. Examples include auto changeover switching capacity from adjacent bus sections, standby transformers or via dedicated tie feeders from other substations. Such capacity has been considered at a number of substations where it is available.
· Remote Transfers (RT) – Load transfer capacity can be deployed via remotely controlled switchgear. The implementation of a series of SCADA controlled switching procedures to isolate the faulted portion of the network whilst restoring supply to fault free portions can be fully implemented within 30 minutes and is available for extended periods. At present, only remote transfers to other substations or standby transformers, using SCADA control of substation circuit breakers, have been considered.
· Manual Transfers (MT) – Load transfer capacity can be deployed via manually controlled switchgear. The implementation of a series of manual switching procedures to isolate the faulted portion of the network whilst restoring supply to fault free portions can be fully implemented within 3 hours (urban) or 4 hours (rural) and is available for extended periods. Some manual transfers are likely to be implemented within 2 hours but this has not been quantified at this time. Analysis done to identify the available 11 kV transfer capability in the systems for every substation. To accommodate future 11 kV network changes and system coincidence peak, a 75% factor is applied to ensure the transfers are practical and achievable throughout the analysis period. The manual switching of standby transformers, which do not have automatic switching, has also been included where available.
· Mobile Generation (MG) – Alternate supply from mobile generators can be sourced within 8 hours (urban) or 12 hours (rural). These are generally smaller 500 kVA units that do not require transport permits or police escorts and can be rapidly deployed. Up to 4 MVA (urban) or 10 MVA (rural) of mobile generation may be committed to a single contingency event.
· Mobile Substation (MS) – Alternate supply provided through deployment of a mobile substation within 8 hours (urban and non-urban) – only applies to 33/11 kV zone substation contingencies. These mobile substations generally do not require transport permits or police escorts and can be rapidly deployed. The standard size of the mobile substation transformer is 18 MVA however a capacity of 15 MVA is used in the assessment of zone substation security standard compliance. Use of the mobile substation may be committed to a single contingency event.
Back to Index

## AFD
Bulk Supply Summary Information and Peak Load Forecast
Substation | AFD - Archerfield BS (110/33kV) | [5 empty] | Supply | RLA - ROCKLEA 110 CP
Description | Land area is 12540 sqm, Construction is conventional outdoor bulk class
Transformer size is 1x48/60/64/80MVA ODAF;1x80MVA ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 2.2 MVA
Growth Rates
Load Category | Industrial
Localities | Supplies Archerfield, Coopers Plains, Rocklea, Salisbury
|  |  |  | Latest Peak Compensated Load |  |  |  | 62.3 MVA on 13/02/2023 at 13:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Day | Day | Day | Day
NCC Rating (MVA) | 175.5 | 175.5 | 175.5 | 175.5 | 175.5 | 175.5 | 175.5 | 175.5 | 175.5 | 175.5
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 67.4 | 66.4 | 65.4 | 64.2 | 63.7 | 57.5 | 57.2 | 57.3 | 56.8 | 56.3
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.966 | 0.966 | 0.966 | 0.966 | 0.966
ECC Rating (MVA) | 92 | 92 | 92 | 92 | 92 | 102.9 | 102.9 | 102.9 | 102.9 | 102.9
50 PoE Load (MVA) | 64.1 | 63.3 | 62.3 | 61.1 | 60.6 | 53.8 | 53.6 | 53.7 | 53.2 | 52.7
50 PoE Load > 95% (MVA) | 3.2 | 3.2 | 3.1 | 3.1 | 3 | 2.7 | 2.7 | 2.7 | 2.7 | 2.6
Hours PA > 95% Peak Load | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
Raw LAR (MVA)
2HR Rating (MVA) | 100 | 100 | 100 | 100 | 100 | 112 | 112 | 112 | 112 | 112
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 10 | 10.1 | 9.9 | 9.7 | 9.6 | 8.7 | 8.7 | 8.9 | 8.9 | 8.8
Manual Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mobile Plant Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
N-1 Capacity for Embedded Generation (MVA) | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## BDS
Bulk Supply Summary Information and Peak Load Forecast
Substation | BDS - Beaudesert BS (110/33kV) | [5 empty] | Supply | LGH - LOGANLEA 110 CP
Description | Land area is 20140 sqm, Construction is a mixture of various construction classes
Transformer size is 1x30/60MVA ONAN/ODAF;1x45/60/80MVA ONAN/ODAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 31.4 MVA
Growth Rates
Load Category | Domestic
Localities | Supplies Beaudesert, Bromelton, Innisplain, Jimboomba, Mt Tamborine
|  |  |  | Latest Peak Compensated Load |  |  |  | 38.5 MVA on 12/02/2023 at 17:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 145.1 | 145.1 | 145.1 | 145.1 | 145.1 | 145.1 | 145.1 | 145.1 | 145.1 | 145.1
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 41.1 | 41 | 41.3 | 41.3 | 41.7 | 36.8 | 37.3 | 37.8 | 38.1 | 38.3
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.964 | 0.964 | 0.964 | 0.964 | 0.964 | 0.978 | 0.978 | 0.978 | 0.978 | 0.978
ECC Rating (MVA) | 75 | 75 | 75 | 75 | 75 | 84 | 84 | 84 | 84 | 84
50 PoE Load (MVA) | 39 | 39 | 39.3 | 39.3 | 39.7 | 35.4 | 35.9 | 36.4 | 36.6 | 36.8
50 PoE Load > 95% (MVA) | 2 | 2 | 2 | 2 | 2 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8
Hours PA > 95% Peak Load | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Raw LAR (MVA)
2HR Rating (MVA) | 81 | 81 | 81 | 81 | 81 | 90 | 90 | 90 | 90 | 90
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 7.8 | 7.7 | 7.7 | 7.6 | 7.6 | 9.8 | 9.8 | 9.8 | 9.7 | 9.7
Manual Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mobile Plant Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 58.5 | 58.5 | 58.5 | 58.5 | 58.5 | 58.5 | 58.5 | 58.5 | 58.5 | 58.5
N-1 Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## BLH
Bulk Supply Summary Information and Peak Load Forecast
Substation | BLH - Beenleigh BS (110/33kV) | [5 empty] | Supply | LGH - LOGANLEA 110 CP
Description | Land area is 32220 sqm, Construction is conventional outdoor bulk class
Transformer size is 3x80MVA ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 2.8 MVA
Growth Rates
Load Category | Mixed Domestic
Localities | Supplies Beenleigh, Bethania, Logan Village, Loganholme, Yatala
|  |  |  | Latest Peak Compensated Load |  |  |  | 129.8 MVA on 17/03/2023 at 16:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 259.6 | 259.6 | 259.6 | 259.6 | 259.6 | 259.6 | 259.6 | 259.6 | 259.6 | 259.6
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 139.1 | 162.4 | 161.1 | 159.3 | 158.8 | 116.5 | 116.7 | 137.5 | 136.9 | 136.4
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.991 | 1 | 1 | 1 | 1 | 0.995 | 0.995 | 0.995 | 0.995 | 0.995
ECC Rating (MVA) | 181.2 | 181.2 | 181.2 | 181.2 | 181.2 | 204.9 | 204.9 | 204.9 | 204.9 | 204.9
50 PoE Load (MVA) | 128.4 | 151.8 | 150.6 | 149 | 148.5 | 108.5 | 108.7 | 129.6 | 129 | 128.5
50 PoE Load > 95% (MVA) | 6.4 | 7.6 | 7.5 | 7.5 | 7.4 | 5.4 | 5.4 | 6.5 | 6.5 | 6.4
Hours PA > 95% Peak Load | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
Raw LAR (MVA)
2HR Rating (MVA) | 197 | 197 | 197 | 197 | 197 | 220.6 | 220.6 | 220.6 | 220.6 | 220.6
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 39.2 | 38.8 | 38.6 | 38.2 | 38.2 | 36.5 | 36.6 | 36.7 | 36.6 | 36.5
Manual Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mobile Plant Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 143.4 | 143.4 | 143.4 | 143.4 | 143.4 | 143.4 | 143.4 | 143.4 | 143.4 | 143.4
N-1 Capacity for Embedded Generation (MVA) | 95.4 | 95.4 | 95.4 | 95.4 | 95.4 | 95.4 | 95.4 | 95.4 | 95.4 | 95.4
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## BWH
Bulk Supply Summary Information and Peak Load Forecast
Substation | BWH - Beerwah BS (132/33kV) | [5 empty] | Supply | PWD - PALMWOODS 132 CP
Description | Land area is 4050 sqm, Construction is conventional outdoor bulk class
Transformer size is 1x30/35/60MVA ODAF;1x30/60MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates
Load Category | Domestic
Localities | Supplies Beerwah, Kilcoy, Landsborough, Woodford
|  |  |  | Latest Peak Compensated Load |  |  |  | 55.8 MVA on 12/02/2023 at 17:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Day | Day | Day | Day | Day
NCC Rating (MVA) | 143.5 | 143.5 | 143.5 | 143.5 | 143.5 | 143.5 | 143.5 | 143.5 | 143.5 | 143.5
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 61.1 | 60.4 | 60.2 | 59.4 | 59.3 | 48.7 | 48.6 | 48.5 | 48.3 | 48
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.982 | 0.982 | 0.982 | 0.982 | 0.982 | 0.994 | 0.994 | 0.994 | 0.994 | 0.994
ECC Rating (MVA) | 75 | 75 | 75 | 75 | 75 | 84 | 84 | 84 | 84 | 84
50 PoE Load (MVA) | 56.6 | 56 | 55.7 | 55.1 | 55 | 45.1 | 45 | 44.9 | 44.8 | 44.5
50 PoE Load > 95% (MVA) | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.3 | 2.3 | 2.2 | 2.2 | 2.2
Hours PA > 95% Peak Load | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Raw LAR (MVA)
2HR Rating (MVA) | 81 | 81 | 81 | 81 | 81 | 90 | 90 | 90 | 90 | 90
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 18.7 | 18.5 | 18.5 | 18.3 | 18.4 | 15.8 | 15.8 | 15.9 | 15.7 | 15.7
Manual Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mobile Plant Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8
N-1 Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## BRD
Bulk Supply Summary Information and Peak Load Forecast
Substation | BRD - Brendale BS (110/33kV) | [5 empty] | Supply | SPN - SOUTH PINE 110 CP
Description | Land area is 314650 sqm, Construction is conventional outdoor bulk class
Transformer size is 1x45/60/80MVA ONAN/ODAN/ODAF;2x80MVA ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 1.5 MVA
Growth Rates
Load Category | Domestic
Localities | Supplies Albany Creek, Arana Hills, Brendale, Lawnton, Nth Pine Dam, Samford, Strathpine
|  |  |  | Latest Peak Compensated Load |  |  |  | 183.6 MVA on 17/03/2023 at 16:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 273.2 | 273.2 | 273.2 | 273.2 | 273.2 | 273.2 | 273.2 | 273.2 | 273.2 | 273.2
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 197.6 | 195.5 | 193.9 | 191.3 | 190.9 | 155.1 | 156.3 | 157 | 157.1 | 157
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 1 | 1 | 1 | 1 | 1
ECC Rating (MVA) | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182
50 PoE Load (MVA) | 184.5 | 182.7 | 181.2 | 178.8 | 178.4 | 143.8 | 145.1 | 145.7 | 145.8 | 145.7
50 PoE Load > 95% (MVA) | 9.2 | 9.1 | 9.1 | 8.9 | 8.9 | 7.2 | 7.3 | 7.3 | 7.3 | 7.3
Hours PA > 95% Peak Load | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
Raw LAR (MVA) | SUMMER 2023/24: 2.5; SUMMER 2024/25: 0.7
2HR Rating (MVA) | 200.2 | 200.2 | 200.2 | 200.2 | 200.2 | 200.2 | 200.2 | 200.2 | 200.2 | 200.2
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 25.2 | 25.1 | 24.7 | 24.1 | 24 | 15.8 | 16.1 | 16.1 | 16 | 15.9
Manual Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 143.4 | 143.4 | 143.4 | 143.4 | 143.4 | 143.4 | 143.4 | 143.4 | 143.4 | 143.4
N-1 Capacity for Embedded Generation (MVA) | 95.5 | 95.5 | 95.5 | 95.5 | 95.5 | 95.5 | 95.5 | 95.5 | 95.5 | 95.5
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## BPN
Bulk Supply Summary Information and Peak Load Forecast
Substation | BPN - Browns Plains BS (110/33kV) | [5 empty] | Supply | LGH - LOGANLEA 110 CP
Description | Land area is 7242 sqm, Construction is conventional outdoor bulk class
Transformer size is 1x120MVA ODAF;1x48/80MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 4.5 MVA
Growth Rates
Load Category | Mixed Domestic
Localities | Supplies Browns Plains, Heathwood, North Maclean
|  |  |  | Latest Peak Compensated Load |  |  |  | 136.9 MVA on 17/03/2023 at 17:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 196.4 | 196.4 | 196.4 | 196.4 | 196.4 | 196.4 | 196.4 | 196.4 | 196.4 | 196.4
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 110.3 | 108 | 106.3 | 104.5 | 103.7 | 127.1 | 97.3 | 97.9 | 97.6 | 97.5
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.955 | 0.955 | 0.955 | 0.955 | 0.955 | 0.985 | 0.985 | 0.985 | 0.985 | 0.985
ECC Rating (MVA) | 92 | 92 | 92 | 92 | 92 | 104 | 104 | 104 | 104 | 104
50 PoE Load (MVA) | 103.6 | 101.5 | 99.9 | 98.2 | 97.5 | 120.4 | 93.3 | 93.9 | 93.6 | 93.5
50 PoE Load > 95% (MVA) | 5.2 | 5.1 | 5 | 4.9 | 4.9 | 6 | 4.7 | 4.7 | 4.7 | 4.7
Hours PA > 95% Peak Load | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
Raw LAR (MVA) | 11.6 | 9.5 | 7.9 | 6.2 | 5.5 | 16.4
2HR Rating (MVA) | 100 | 100 | 100 | 100 | 100 | 112 | 112 | 112 | 112 | 112
Auto Trans Avail (MVA) | 29.9 | 29.4 | 29 | 28.5 | 28.3 | 25.2 | 25.1 | 25.1 | 24.9 | 24.8
Remote Trans Avail (MVA) | 14.4 | 14.5 | 14.3 | 13.9 | 13.9 | 13.6 | 13.3 | 13.5 | 13.4 | 13.4
Manual Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 107.1 | 107.1 | 107.1 | 107.1 | 107.1 | 107.1 | 107.1 | 107.1 | 107.1 | 107.1
N-1 Capacity for Embedded Generation (MVA) | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## BHD
Bulk Supply Summary Information and Peak Load Forecast
Substation | BHD - Burleigh Heads BS (110/33kV) | [5 empty] | Supply | MGB - MUDGEERABA 110 CP
Description | Land area is 25760 sqm, Construction is conventional outdoor bulk class
Transformer size is 2x50/60/75MVA ONAN/ODAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 2.2 MVA
Growth Rates
Load Category | Domestic
Localities | Supplies Currumbin, Kirra, Little Nerang Creek, Miami, Mudgeeraba, Palm Beach, Tugun
|  |  |  | Latest Peak Compensated Load |  |  |  | 98 MVA on 04/07/2022 at 17:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 164.9 | 164.9 | 164.9 | 164.9 | 164.9 | 164.9 | 164.9 | 164.9 | 164.9 | 164.9
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 101.6 | 101.3 | 101.5 | 101.3 | 101.8 | 114.1 | 115 | 115.9 | 116.4 | 116.9
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.991 | 0.991 | 0.991 | 0.991 | 0.991 | 0.995 | 0.995 | 0.995 | 0.995 | 0.995
ECC Rating (MVA) | 86.3 | 86.3 | 86.3 | 86.3 | 86.3 | 90 | 90 | 90 | 90 | 90
50 PoE Load (MVA) | 97 | 96.7 | 96.8 | 96.6 | 97.1 | 109.8 | 110.6 | 111.5 | 112 | 112.5
50 PoE Load > 95% (MVA) | 4.9 | 4.8 | 4.8 | 4.8 | 4.9 | 5.5 | 5.5 | 5.6 | 5.6 | 5.6
Hours PA > 95% Peak Load | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
Raw LAR (MVA) | 10.7 | 10.4 | 10.5 | 10.3 | 10.8 | 19.8 | 20.6 | 21.5 | 22 | 22.5
2HR Rating (MVA) | 93.8 | 93.8 | 93.8 | 93.8 | 93.8 | 96 | 96 | 96 | 96 | 96
Auto Trans Avail (MVA) | 23.6 | 23.7 | 24 | 24.2 | 24.7 | 23.2 | 23.7 | 24.1 | 24.5 | 24.9
Remote Trans Avail (MVA) | 18.6 | 18.5 | 18.6 | 18.5 | 18.6 | 14.5 | 14.7 | 14.8 | 14.9 | 15
Manual Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mobile Plant Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9
N-1 Capacity for Embedded Generation (MVA) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## CBT
Bulk Supply Summary Information and Peak Load Forecast
Substation | CBT - Caboolture BS (110/33kV) | [5 empty] | Supply | SPN - SOUTH PINE 110 CP
Description | Land area is 47630 sqm, Construction is conventional outdoor bulk class
Transformer size is 1x48/60/64/80MVA ONAN/ODAN/ONAF/ODAF;1x48/80MVA ONAN/ODAF;1x60/80MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 3.9 MVA
Growth Rates
Load Category | Domestic
Localities | Supplies Bribie Island, Caboolture West, Morayfield, Morayfield North, Ningi, Toorbul Point
|  |  |  | Latest Peak Compensated Load |  |  |  | 152.8 MVA on 17/03/2023 at 17:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 269.5 | 269.5 | 269.5 | 269.5 | 269.5 | 282.9 | 282.9 | 282.9 | 282.9 | 282.9
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 165.7 | 162.7 | 161.4 | 159.7 | 159.3 | 137 | 137 | 137.2 | 137 | 137.4
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 1 | 1 | 1 | 1 | 1 | 0.994 | 0.994 | 0.994 | 0.994 | 0.994
ECC Rating (MVA) | 180.4 | 180.4 | 180.4 | 180.4 | 180.4 | 189.4 | 189.4 | 189.4 | 189.4 | 189.4
50 PoE Load (MVA) | 155.7 | 152.9 | 151.6 | 150 | 149.7 | 126 | 126 | 126.2 | 126 | 126.4
50 PoE Load > 95% (MVA) | 7.8 | 7.6 | 7.6 | 7.5 | 7.5 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3
Hours PA > 95% Peak Load | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Raw LAR (MVA)
2HR Rating (MVA) | 198.4 | 198.4 | 198.4 | 198.4 | 198.4 | 207.5 | 207.5 | 207.5 | 207.5 | 207.5
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 16.9 | 16.7 | 16.6 | 16.5 | 16.5 | 12.4 | 12.4 | 12.5 | 12.6 | 12.9
Manual Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mobile Plant Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 141.5 | 141.5 | 141.5 | 141.5 | 141.5 | 141.5 | 141.5 | 141.5 | 141.5 | 141.5
N-1 Capacity for Embedded Generation (MVA) | 94.7 | 94.7 | 94.7 | 94.7 | 94.7 | 94.7 | 94.7 | 94.7 | 94.7 | 94.7
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## CVL
Bulk Supply Summary Information and Peak Load Forecast
Substation | CVL - Cleveland BS (110/33kV) | [5 empty] | Supply | BMH - BELMONT 110 CP
Description | Land area is 40420 sqm, Construction is conventional outdoor bulk class
Transformer size is 1x120MVA ODAF;1x72/120MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 1.0 MVA
Growth Rates
Load Category | Domestic
Localities | Supplies Birkdale, Capalaba, Cleveland, Mt Cotton, Raby Bay, Redland Bay, Victoria Point
|  |  |  | Latest Peak Compensated Load |  |  |  | 167.3 MVA on 17/03/2023 at 17:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5 | 286.5
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 181 | 178.2 | 176.9 | 174.5 | 173.9 | 153 | 153.1 | 153.4 | 152.9 | 152.2
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.995 | 0.995 | 0.995 | 0.995 | 0.995
ECC Rating (MVA) | 150 | 150 | 150 | 150 | 150 | 168 | 168 | 168 | 168 | 168
50 PoE Load (MVA) | 169.7 | 167.1 | 165.9 | 163.7 | 163 | 141.5 | 141.7 | 141.9 | 141.5 | 140.8
50 PoE Load > 95% (MVA) | 8.5 | 8.4 | 8.3 | 8.2 | 8.2 | 7.1 | 7.1 | 7.1 | 7.1 | 7
Hours PA > 95% Peak Load | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
Raw LAR (MVA) | SUMMER 2023/24: 19.7; SUMMER 2024/25: 17.1; SUMMER 2025/26: 15.9; SUMMER 2026/27: 13.7; SUMMER 2027/28: 13
2HR Rating (MVA) | 162 | 162 | 162 | 162 | 162 | 180 | 180 | 180 | 180 | 180
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 27.6 | 27.2 | 27.1 | 26.8 | 26.8 | 23.7 | 23.8 | 23.8 | 23.8 | 23.7
Manual Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 143.3 | 143.3 | 143.3 | 143.3 | 143.3 | 143.3 | 143.3 | 143.3 | 143.3 | 143.3
N-1 Capacity for Embedded Generation (MVA) | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## CMA
Bulk Supply Summary Information and Peak Load Forecast
Substation | CMA - Coomera BS (110/33kV) | [5 empty] | Supply | MAR - MOLENDINAR 110 CP
Description | Land area is 16100 sqm, Construction is a mixture of various construction classes
Transformer size is 1x48/60/80MVA ONAN/ONAF/ODAF;1x48/80MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 2.2 MVA
Growth Rates
Load Category | Domestic
Localities | Supplies Coomera, Gaven, Hope Island
|  |  |  | Latest Peak Compensated Load |  |  |  | 124.4 MVA on 03/02/2023 at 17:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 189.6 | 189.6 | 189.6 | 189.6 | 189.6 | 189.6 | 189.6 | 189.6 | 189.6 | 189.6
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 131 | 129.5 | 129.6 | 132.2 | 136 | 98.9 | 100.7 | 102.3 | 103.7 | 107.2
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.978 | 0.978 | 0.978 | 0.978 | 0.978 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
ECC Rating (MVA) | 100 | 100 | 100 | 100 | 100 | 112 | 112 | 112 | 112 | 112
50 PoE Load (MVA) | 121.8 | 120.4 | 120.5 | 123.1 | 126.9 | 90.4 | 91.9 | 93.4 | 94.7 | 98.1
50 PoE Load > 95% (MVA) | 6.1 | 6 | 6 | 6.2 | 6.3 | 4.5 | 4.6 | 4.7 | 4.7 | 4.9
Hours PA > 95% Peak Load | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Raw LAR (MVA) | SUMMER 2023/24: 21.8; SUMMER 2024/25: 20.4; SUMMER 2025/26: 20.5; SUMMER 2026/27: 23.1; SUMMER 2027/28: 26.9
2HR Rating (MVA) | 108 | 108 | 108 | 108 | 108 | 120 | 120 | 120 | 120 | 120
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Manual Trans Avail (MVA) | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8
Mobile Plant Avail (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8
N-1 Capacity for Embedded Generation (MVA) | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## CPR
Bulk Supply Summary Information and Peak Load Forecast
Substation | CPR - Coorparoo BS (110/33kV) | [5 empty] | Supply | BMH - BELMONT 110 CP
Description | Land area is 3860 sqm, Construction is conventional all indoor class
Transformer size is 2x48/80MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates
Load Category | Domestic
Localities | Supplies Annerley, Camp Hill, Cannon Hill, Carina Heights, Carindale, Coorparoo, East Brisbane, Greenslopes, Holland Park, Holland Park West, Morningside, Norman Park, Tarragindi
|  |  |  | Latest Peak Compensated Load |  |  |  | 81.1 MVA on 03/02/2023 at 19:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 178.6 | 178.6 | 178.6 | 178.6 | 178.6 | 191.1 | 191.1 | 191.1 | 191.1 | 191.1
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 86.3 | 85 | 84.6 | 83.7 | 83.7 | 70.5 | 70.8 | 71.2 | 71.2 | 71.2
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.985 | 0.985 | 0.985 | 0.985 | 0.985 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
ECC Rating (MVA) | 98.4 | 98.4 | 98.4 | 98.4 | 98.4 | 104 | 104 | 104 | 104 | 104
50 PoE Load (MVA) | 81.9 | 80.7 | 80.2 | 79.4 | 79.4 | 65.9 | 66.2 | 66.6 | 66.6 | 66.7
50 PoE Load > 95% (MVA) | 4.1 | 4 | 4 | 4 | 4 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3
Hours PA > 95% Peak Load | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
Raw LAR (MVA)
2HR Rating (MVA) | 108 | 108 | 108 | 108 | 108 | 120 | 120 | 120 | 120 | 120
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 18.1 | 18 | 17.9 | 17.8 | 17.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8
Manual Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mobile Plant Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 95.8 | 95.8 | 95.8 | 95.8 | 95.8 | 95.8 | 95.8 | 95.8 | 95.8 | 95.8
N-1 Capacity for Embedded Generation (MVA) | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## DBS
Bulk Supply Summary Information and Peak Load Forecast
Substation | DBS - Doboy BS (110/33kV) | [5 empty] | Supply | MRE - MURARRIE 110 CP
Description | Land area is 18760 sqm, Construction is conventional outdoor bulk class
Transformer size is 3x48/80MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates
Load Category | Mixed Industrial
Localities | Supplies Bulimba, Hemmant, Lota, Murarrie, Queensport, Tingalpa, Visypaper, Wynnum
|  |  |  | Latest Peak Compensated Load |  |  |  | 123 MVA on 01/02/2023 at 16:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 262.9 | 262.9 | 262.9 | 262.9 | 262.9 | 262.9 | 262.9 | 262.9 | 262.9 | 262.9
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 141.5 | 144.6 | 167.6 | 190.1 | 189.4 | 104.2 | 106.4 | 108.4 | 127.1 | 143.2
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 1 | 1 | 0.999 | 0.998 | 0.998 | 0.983 | 0.983 | 0.983 | 0.983 | 1
ECC Rating (MVA) | 183.1 | 183.1 | 183.1 | 183.1 | 183.1 | 207 | 207 | 207 | 207 | 207
50 PoE Load (MVA) | 135.5 | 138.6 | 161.8 | 184.2 | 183.6 | 100.6 | 102.8 | 104.8 | 123.5 | 139.7
50 PoE Load > 95% (MVA) | 6.8 | 6.9 | 8.1 | 9.2 | 9.2 | 5 | 5.1 | 5.2 | 6.2 | 7
Hours PA > 95% Peak Load | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
Raw LAR (MVA) | SUMMER 2026/27: 1.1; SUMMER 2027/28: 0.5
2HR Rating (MVA) | 199 | 199 | 199 | 199 | 199 | 222.9 | 222.9 | 222.9 | 222.9 | 222.9
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
Manual Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mobile Plant Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 143.4 | 143.4 | 143.4 | 143.4 | 143.4 | 143.4 | 143.4 | 143.4 | 143.4 | 143.4
N-1 Capacity for Embedded Generation (MVA) | 95.5 | 95.5 | 95.5 | 95.5 | 95.5 | 95.5 | 95.5 | 95.5 | 95.5 | 95.5
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## GBS
Bulk Supply Summary Information and Peak Load Forecast
Substation | GBS - Gatton BS (110/33kV) | [5 empty] | Supply | MRG - MIDDLE RIDGE 110 CP
Description | Land area is 43446 sqm, Construction is a mixture of various construction classes
Transformer size is 1x30/60MVA ONAN/ODAF;1x36/60MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 6.1 MVA
Growth Rates
Load Category | Domestic
Localities | Supplies Gatton, Mt Sylvia, Tenthill
|  |  |  | Latest Peak Compensated Load |  |  |  | 30.2 MVA on 03/02/2023 at 15:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Day | Day | Day | Day
NCC Rating (MVA) | 143.2 | 143.2 | 143.2 | 143.2 | 143.2 | 143.2 | 143.2 | 143.2 | 143.2 | 143.2
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 35.3 | 34.8 | 34.5 | 34 | 33.8 | 24.4 | 25.2 | 25.2 | 25.1 | 25
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.967 | 0.967 | 0.967 | 0.967 | 0.967 | 0.978 | 0.978 | 0.978 | 0.978 | 0.978
ECC Rating (MVA) | 75 | 75 | 75 | 75 | 75 | 84 | 84 | 84 | 84 | 84
50 PoE Load (MVA) | 33.1 | 32.5 | 32.2 | 31.8 | 31.6 | 22.8 | 23.6 | 23.6 | 23.5 | 23.4
50 PoE Load > 95% (MVA) | 1.7 | 1.6 | 1.6 | 1.6 | 1.6 | 1.1 | 1.2 | 1.2 | 1.2 | 1.2
Hours PA > 95% Peak Load | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Raw LAR (MVA)
2HR Rating (MVA) | 81 | 81 | 81 | 81 | 81 | 90 | 90 | 90 | 90 | 90
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 10.3 | 10.1 | 10.1 | 10 | 9.8 | 7.7 | 8.4 | 8.4 | 8.4 | 8.2
Manual Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mobile Plant Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 59.7 | 59.7 | 59.7 | 59.7 | 59.7 | 59.7 | 59.7 | 59.7 | 59.7 | 59.7
N-1 Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## GFN
Bulk Supply Summary Information and Peak Load Forecast
Substation | GFN - Griffin BS (110/33kV) | [5 empty] | Supply | SPN - SOUTH PINE 110 CP
Description | Land area is 23140 sqm, Construction is a mixture of various construction classes
Transformer size is 2x48/80MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 1.5 MVA
Growth Rates
Load Category | Domestic
Localities | Supplies Dakabin, Kallangur, Mango Hill, Murrumba Downs, North Lakes
|  |  |  | Latest Peak Compensated Load |  |  |  | 71.4 MVA on 17/03/2023 at 17:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 189.1 | 189.1 | 189.1 | 189.1 | 189.1 | 191.3 | 191.3 | 191.3 | 191.3 | 191.3
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 78.9 | 77.1 | 77 | 77.3 | 77.3 | 55.3 | 55.6 | 56.8 | 58.3 | 59
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.989 | 0.989 | 0.989 | 0.989 | 0.989 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
ECC Rating (MVA) | 100 | 100 | 100 | 100 | 100 | 108.7 | 108.7 | 108.7 | 108.7 | 108.7
50 PoE Load (MVA) | 73.6 | 72 | 72 | 72.4 | 72.4 | 52 | 52.2 | 53.3 | 54.9 | 55.6
50 PoE Load > 95% (MVA) | 3.7 | 3.6 | 3.6 | 3.6 | 3.6 | 2.6 | 2.6 | 2.7 | 2.7 | 2.8
Hours PA > 95% Peak Load | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Raw LAR (MVA)
2HR Rating (MVA) | 108 | 108 | 108 | 108 | 108 | 120 | 120 | 120 | 120 | 120
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 34.3 | 33.4 | 32.6 | 31.5 | 30.7 | 23.3 | 23.5 | 23.6 | 23.7 | 23.5
Manual Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mobile Plant Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 95.6 | 95.6 | 95.6 | 95.6 | 95.6 | 95.6 | 95.6 | 95.6 | 95.6 | 95.6
N-1 Capacity for Embedded Generation (MVA) | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## GYM
Bulk Supply Summary Information and Peak Load Forecast
Substation | GYM - Gympie BS (132/33kV) | [5 empty] | Supply | WLG - WOOLOOGA 132 CP
Description | Land area is 21870 sqm, Construction is conventional outdoor bulk class
Transformer size is 1x50/61/69MVA ONAN/ONAF/ODAF;1x60/80MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates
Load Category | Mixed Domestic
Localities | Supplies Amamoor, Gympie South, Imbil, Mary River Pumping, Tin Can Bay, Toolara Forest
|  |  |  | Latest Peak Compensated Load |  |  |  | 53.3 MVA on 13/02/2023 at 18:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 55.2 | 55.5 | 55.2 | 54.6 | 54.3 | 53 | 54.1 | 54.1 | 53.8 | 53.5
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.988 | 0.988 | 0.988 | 0.988 | 0.988 | 0.994 | 0.994 | 0.994 | 0.994 | 0.994
ECC Rating (MVA) | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 85 | 85 | 85 | 85 | 85
50 PoE Load (MVA) | 50.8 | 51.3 | 50.9 | 50.4 | 50.2 | 50.7 | 51.7 | 51.7 | 51.5 | 51.2
50 PoE Load > 95% (MVA) | 2.5 | 2.6 | 2.5 | 2.5 | 2.5 | 2.5 | 2.6 | 2.6 | 2.6 | 2.6
Hours PA > 95% Peak Load | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
Raw LAR (MVA)
2HR Rating (MVA) | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 85 | 85 | 85 | 85 | 85
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mobile Plant Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 79.1 | 79.1 | 79.1 | 79.1 | 79.1 | 79.1 | 79.1 | 79.1 | 79.1 | 79.1
N-1 Capacity for Embedded Generation (MVA) | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## HIL
Bulk Supply Summary Information and Peak Load Forecast
Substation | HIL - Hays Inlet BS (110/33kV) | [5 empty] | Supply | SPN - SOUTH PINE 110 CP
Description | Land area is 26040 sqm, Construction is conventional outdoor bulk class
Transformer size is 2x50/60/75MVA ONAN/ODAN/ODAF;1x80MVA ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 4.8 MVA
Growth Rates
Load Category | Domestic
Localities | Supplies Deception Bay, Duffield Road, Kallangur, Mango Hill, Narangba, Redcliffe, Scarborough
|  |  |  | Latest Peak Compensated Load |  |  |  | 168.9 MVA on 01/02/2023 at 17:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 267.9 | 267.9 | 267.9 | 267.9 | 267.9 | 267.9 | 267.9 | 267.9 | 267.9 | 267.9
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 175.1 | 173.6 | 173.4 | 176.1 | 180.5 | 142.8 | 144 | 145.2 | 145.7 | 148.5
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 1 | 1 | 1 | 1 | 1 | 0.995 | 0.995 | 0.995 | 0.995 | 0.995
ECC Rating (MVA) | 181.2 | 181.2 | 181.2 | 181.2 | 181.2 | 199.3 | 199.3 | 199.3 | 199.3 | 199.3
50 PoE Load (MVA) | 164.9 | 163.5 | 163.4 | 166.1 | 170.4 | 132.9 | 134 | 135.1 | 135.6 | 138.3
50 PoE Load > 95% (MVA) | 8.2 | 8.2 | 8.2 | 8.3 | 8.5 | 6.6 | 6.7 | 6.8 | 6.8 | 6.9
Hours PA > 95% Peak Load | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Raw LAR (MVA)
2HR Rating (MVA) | 199.3 | 199.3 | 199.3 | 199.3 | 199.3 | 217.4 | 217.4 | 217.4 | 217.4 | 217.4
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 35 | 34.8 | 34.8 | 34.8 | 35.2 | 24.7 | 25.1 | 25.6 | 25.9 | 26.2
Manual Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mobile Plant Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 143.6 | 143.6 | 143.6 | 143.6 | 143.6 | 143.6 | 143.6 | 143.6 | 143.6 | 143.6
N-1 Capacity for Embedded Generation (MVA) | 95.3 | 95.3 | 95.3 | 95.3 | 95.3 | 95.3 | 95.3 | 95.3 | 95.3 | 95.3
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## IBS
Bulk Supply Summary Information and Peak Load Forecast
Substation | IBS - Ibis BS (110/33kV) | [5 empty] | Supply | LGH - LOGANLEA 110 CP
Description | Land area is 14800 sqm, Construction is conventional outdoor bulk class
Transformer size is 1x48/60MVA ONAN/OFDAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates
Load Category | Continuous
Localities | Supplies Herring Lagoon, Ibis
|  |  |  | Latest Peak Compensated Load |  |  |  | 2.3 MVA on 05/07/2022 at 10:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Day | Day | Day | Day
NCC Rating (MVA) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 2 | 1.9 | 1.9 | 1.9 | 1.9 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.918 | 0.918 | 0.918 | 0.918 | 0.918 | 0.948 | 0.948 | 0.948 | 0.948 | 0.948
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 1.9 | 1.9 | 1.9 | 1.8 | 1.8 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3
50 PoE Load > 95% (MVA) | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Hours PA > 95% Peak Load | 398.5 | 398.5 | 398.5 | 398.5 | 398.5 | 398.5 | 398.5 | 398.5 | 398.5 | 398.5
Raw LAR (MVA) | 1.9 | 1.9 | 1.9 | 1.8 | 1.8 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 1.9 | 1.9 | 1.9 | 1.8 | 1.8 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3
Manual Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mobile Plant Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## JBB
Bulk Supply Summary Information and Peak Load Forecast
Substation | JBB - Jimboomba BS (110/33kV) | [5 empty] | Supply | LGH - LOGANLEA 110 CP
Description | Land area is 40470 sqm, Construction is a mixture of various construction classes
Transformer size is 1x80MVA ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates
Load Category | Domestic
Localities | Supplies Jimboomba, Maclean, North Maclean, South Maclean, Stockleigh
|  |  |  | Latest Peak Compensated Load |  |  |  | 81.7 MVA on 04/07/2022 at 17:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 104.4 | 104.2 | 106.8 | 108.6 | 111.6 | 77.5 | 84.1 | 85.8 | 89.2 | 94.1
LARn (MVA) | 16.4 | 16.2 | 18.8 | 20.6 | 23.6 |  |  |  | 1.2 | 6.1
LARn (MW) | 16 | 15.8 | 18.4 | 20.2 | 23.1 |  |  |  | 1.2 | 6.1
Power Factor at Peak Load | 0.978 | 0.978 | 0.978 | 0.978 | 0.978 | 0.993 | 0.993 | 0.993 | 0.993 | 0.993
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 93.7 | 93.4 | 96 | 97.8 | 100.6 | 72.13 | 78.3 | 79.8 | 83.2 | 88
50 PoE Load > 95% (MVA) | 4.7 | 4.7 | 4.8 | 4.9 | 5 | 3.6 | 3.9 | 4 | 4.2 | 4.4
Hours PA > 95% Peak Load | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Raw LAR (MVA) | 93.7 | 93.4 | 96 | 97.8 | 100.6 | 72.1 | 78.3 | 79.8 | 83.2 | 88
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 71.2 | 71 | 75.8 | 76.8 | 78.6 | 56.3 | 61.2 | 65.3 | 67.3 | 70.3
Remote Trans Avail (MVA) | 2 | 2 | 2 | 2 | 2 | 6 | 6 | 6 | 6 | 6
Manual Trans Avail (MVA) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Mobile Plant Avail (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA) | SUMMER 2023/24: 8.5; SUMMER 2024/25: 8.4; SUMMER 2025/26: 6.2; SUMMER 2026/27: 7; SUMMER 2027/28: 8
LARc (MW) | SUMMER 2023/24: 8.313; SUMMER 2024/25: 8.2152; SUMMER 2025/26: 6.0636; SUMMER 2026/27: 6.846; SUMMER 2027/28: 7.824
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | No | No | No | No | No | Yes | Yes | Yes | No | No
Back to Index

## LRE
Bulk Supply Summary Information and Peak Load Forecast
Substation | LRE - Lockrose BS (110/33kV) | [5 empty] | Supply | ABR - ABERMAIN 110 CP
Description | Land area is 38445 sqm, Construction is conventional outdoor bulk class
Transformer size is 2x30/60MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 5.2 MVA
Growth Rates
Load Category | Domestic
Localities | Supplies Coominya, Glenore Grove, Laidley, Lowood, Murrumba, Somerset Dam, Tarampa, Toogoolawah, Wivenhoe
|  |  |  | Latest Peak Compensated Load |  |  |  | 62.4 MVA on 12/02/2023 at 18:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 143.9 | 143.9 | 143.9 | 143.9 | 143.9 | 143.9 | 143.9 | 143.9 | 143.9 | 143.9
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 69 | 68.6 | 70.9 | 70.1 | 70 | 49.8 | 50.2 | 52.9 | 52.8 | 52.6
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 1 | 1 | 1 | 1 | 1 | 0.992 | 0.992 | 0.992 | 0.992 | 0.992
ECC Rating (MVA) | 75 | 75 | 75 | 75 | 75 | 84 | 84 | 84 | 84 | 84
50 PoE Load (MVA) | 64.9 | 64.5 | 65.8 | 65.1 | 65 | 47 | 47.4 | 50.1 | 50 | 49.8
50 PoE Load > 95% (MVA) | 3.2 | 3.2 | 3.3 | 3.3 | 3.3 | 2.4 | 2.4 | 2.5 | 2.5 | 2.5
Hours PA > 95% Peak Load | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Raw LAR (MVA)
2HR Rating (MVA) | 81 | 81 | 81 | 81 | 81 | 90 | 90 | 90 | 90 | 90
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0.4 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | bar: SUMMER 2023/24 to WINTER 2027
Mobile Plant Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
N-1 Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## LBS
Bulk Supply Summary Information and Peak Load Forecast
Substation | LBS - Lytton BS (110/33kV) | [5 empty] | Supply | MRE - MURARRIE 110 CP
Description | Land area is 30170 sqm, Construction is a mixture of various construction classes
Transformer size is 3x48/80MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 2.2 MVA
Growth Rates
Load Category | Continuous
Localities | Supplies Fisherman Is, Gibson Island, Lytton, Lytton Bulk Supply
|  |  |  | Latest Peak Compensated Load |  |  |  | 114.4 MVA on 05/07/2022 at 17:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 238.3 | 238.3 | 238.3 | 238.3 | 238.3 | 238.7 | 238.7 | 238.7 | 238.7 | 238.7
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 114.7 | 128.1 | 133.4 | 133.3 | 132.8 | 116.9 | 129.8 | 136.1 | 138.3 | 138.8
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.991 | 0.991 | 0.991 | 0.991 | 0.991 | 0.996 | 0.996 | 0.996 | 0.996 | 0.996
ECC Rating (MVA) | 170.9 | 170.9 | 170.9 | 170.9 | 170.9 | 179.2 | 179.2 | 179.2 | 179.2 | 179.2
50 PoE Load (MVA) | 111.5 | 124.9 | 130.3 | 130.2 | 129.7 | 112 | 124.8 | 131.1 | 133.3 | 133.9
50 PoE Load > 95% (MVA) | 5.6 | 6.2 | 6.5 | 6.5 | 6.5 | 5.6 | 6.2 | 6.6 | 6.7 | 6.7
Hours PA > 95% Peak Load | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Raw LAR (MVA)
2HR Rating (MVA) | 180.8 | 180.8 | 180.8 | 180.8 | 180.8 | 180.8 | 180.8 | 180.8 | 180.8 | 180.8
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mobile Plant Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO | Split w ACO
Capacity for Embedded Generation (MVA) | 141.4 | 141.4 | 141.4 | 141.4 | 141.4 | 141.4 | 141.4 | 141.4 | 141.4 | 141.4
N-1 Capacity for Embedded Generation (MVA) | 94.3 | 94.3 | 94.3 | 94.3 | 94.3 | 94.3 | 94.3 | 94.3 | 94.3 | 94.3
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## MDH
Bulk Supply Summary Information and Peak Load Forecast
Substation | MDH - Meeandah BS (110/33kV) | [5 empty] | Supply | SPN - SOUTH PINE 110 CP
Description | Land area is 3720 sqm, Construction is conventional outdoor bulk class
Transformer size is 2x80MVA ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates
Load Category | Industrial
Localities | Supplies Hamilton Lands, Meeandah, Myrtletown
|  |  |  | Latest Peak Compensated Load |  |  |  | 45.2 MVA on 01/02/2023 at 12:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Day | Day | Day | Day
NCC Rating (MVA) | 167.8 | 167.8 | 167.8 | 167.8 | 167.8 | 167.8 | 167.8 | 167.8 | 167.8 | 167.8
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 49.3 | 54.7 | 54.8 | 54.6 | 54.9 | 37.7 | 42.3 | 42.8 | 43 | 43.3
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.922 | 0.922 | 0.922 | 0.922 | 0.922 | 0.938 | 0.938 | 0.938 | 0.938 | 0.938
ECC Rating (MVA) | 91.5 | 91.5 | 91.5 | 91.5 | 91.5 | 96 | 96 | 96 | 96 | 96
50 PoE Load (MVA) | 47.9 | 53.3 | 53.5 | 53.3 | 53.6 | 36.6 | 41.2 | 41.6 | 41.9 | 42.1
50 PoE Load > 95% (MVA) | 2.4 | 2.7 | 2.7 | 2.7 | 2.7 | 1.8 | 2.1 | 2.1 | 2.1 | 2.1
Hours PA > 95% Peak Load | 36.5 | 36.5 | 36.5 | 36.5 | 36.5 | 36.5 | 36.5 | 36.5 | 36.5 | 36.5
Raw LAR (MVA)
2HR Rating (MVA) | 100 | 100 | 100 | 100 | 100 | 105.2 | 105.2 | 105.2 | 105.2 | 105.2
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mobile Plant Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 95.9 | 95.9 | 95.9 | 95.9 | 95.9 | 95.9 | 95.9 | 95.9 | 95.9 | 95.9
N-1 Capacity for Embedded Generation (MVA) | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## MTN
Bulk Supply Summary Information and Peak Load Forecast
Substation | MTN - Myrtletown BS (110/33kV) | [5 empty] | Supply | SPN - SOUTH PINE 110 CP
Description | Land area is 12550 sqm, Construction is a mixture of various construction classes
Transformer size is 2x120MVA ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 1.4 MVA
Growth Rates
Load Category | Continuous
Localities | Supplies Pinkenba
|  |  |  | Latest Peak Compensated Load |  |  |  | 35 MVA on 24/03/2023 at 17:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Day | Day | Day | Day | Day
NCC Rating (MVA) | 239.6 | 239.6 | 239.6 | 239.6 | 239.6 | 239.6 | 239.6 | 239.6 | 239.6 | 239.6
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 44.1 | 44 | 44 | 60.6 | 77.3 | 43 | 42.9 | 43 | 57.6 | 72.1
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.993 | 0.993 | 0.993 | 0.993 | 0.993 | 0.988 | 0.988 | 0.988 | 0.988 | 0.988
ECC Rating (MVA) | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138
50 PoE Load (MVA) | 43 | 42.9 | 42.9 | 59.5 | 76.2 | 42.2 | 42.2 | 42.3 | 56.8 | 71.4
50 PoE Load > 95% (MVA) | 2.2 | 2.1 | 2.1 | 3 | 3.8 | 2.1 | 2.1 | 2.1 | 2.8 | 3.6
Hours PA > 95% Peak Load | 34.5 | 34.5 | 34.5 | 34.5 | 34.5 | 34.5 | 34.5 | 34.5 | 34.5 | 34.5
Raw LAR (MVA)
2HR Rating (MVA) | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manual Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mobile Plant Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 143.7 | 143.7 | 143.7 | 143.7 | 143.7 | 143.7 | 143.7 | 143.7 | 143.7 | 143.7
N-1 Capacity for Embedded Generation (MVA) | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
LARc (MVA)
LARc (MW)
Customer Category | HighSec | HighSec | HighSec | HighSec | HighSec | HighSec | HighSec | HighSec | HighSec | HighSec
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## NBR
Bulk Supply Summary Information and Peak Load Forecast
Substation | NBR - Nambour BS (132/33kV) | [5 empty] | Supply | PWD - PALMWOODS 132 CP
Description | Land area is 20000 sqm, Construction is conventional outdoor bulk class
Transformer size is 2x48/60MVA ONAN/ODAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 19.2 MVA
Growth Rates
Load Category | Mixed Domestic
Localities | Supplies Kenilworth, Maleny, Nambour, Palmwoods Central, Yandina
|  |  |  | Latest Peak Compensated Load |  |  |  | 81.1 MVA on 04/07/2022 at 17:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 143.8 | 143.8 | 143.8 | 143.8 | 143.8 | 143.8 | 143.8 | 143.8 | 143.8 | 143.8
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 87 | 86.6 | 86.3 | 85.4 | 85.4 | 82.7 | 84.6 | 84.9 | 84.9 | 84.7
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.994 | 0.994 | 0.994 | 0.994 | 0.994 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 80 | 80 | 80 | 80 | 80 | 90 | 90 | 90 | 90 | 90
50 PoE Load (MVA) | 80.6 | 80.3 | 80 | 79.1 | 79.1 | 76.6 | 78.5 | 78.8 | 78.7 | 78.6
50 PoE Load > 95% (MVA) | 4 | 4 | 4 | 4 | 4 | 3.8 | 3.9 | 3.9 | 3.9 | 3.9
Hours PA > 95% Peak Load | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5
Raw LAR (MVA) | SUMMER 2023/24: 0.6; SUMMER 2024/25: 0.3
2HR Rating (MVA) | 91 | 91 | 91 | 91 | 91 | 96 | 96 | 96 | 96 | 96
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 7.5 | 7.4 | 7.4 | 7.3 | 7.3 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7
Manual Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mobile Plant Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
N-1 Capacity for Embedded Generation (MVA) | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## NGE
Bulk Supply Summary Information and Peak Load Forecast
Substation | NGE - Nudgee BS (110/33kV) | [5 empty] | Supply | SPN - SOUTH PINE 110 CP
Description | Land area is 20450 sqm, Construction is conventional outdoor bulk class
Transformer size is 2x48/80MVA ONAN/ODAF;1x80MVA ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 3.1 MVA
Growth Rates
Load Category | Industrial
Localities | Supplies Eagle Farm, Geebung, Hamilton, Hendra, Nudgee, Nundah, Zillmere
|  |  |  | Latest Peak Compensated Load |  |  |  | 155.2 MVA on 01/02/2023 at 16:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 249.5 | 249.5 | 249.5 | 249.5 | 249.5 | 249.5 | 249.5 | 249.5 | 249.5 | 249.5
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 180.3 | 183.3 | 181.9 | 182 | 181.7 | 139.3 | 144.5 | 148.2 | 149.3 | 149
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | bar: SUMMER 2023/24 to WINTER 2027
ECC Rating (MVA) | 181.7 | 181.7 | 181.7 | 181.7 | 181.7 | 205.4 | 205.4 | 205.4 | 205.4 | 205.4
50 PoE Load (MVA) | 170.9 | 174 | 172.7 | 172.9 | 172.6 | 133.5 | 138.6 | 142.2 | 143.3 | 143
50 PoE Load > 95% (MVA) | 8.5 | 8.7 | 8.6 | 8.6 | 8.6 | 6.7 | 6.9 | 7.1 | 7.2 | 7.2
Hours PA > 95% Peak Load | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Raw LAR (MVA)
2HR Rating (MVA) | 197.5 | 197.5 | 197.5 | 197.5 | 197.5 | 221.2 | 221.2 | 221.2 | 221.2 | 221.2
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 34.6 | 35.2 | 34.5 | 33.9 | 33.7 | 26.5 | 27.7 | 27.4 | 27.1 | 26.8
Manual Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mobile Plant Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5 | 142.5
N-1 Capacity for Embedded Generation (MVA) | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## PRG
Bulk Supply Summary Information and Peak Load Forecast
Substation | PRG - Postmans Ridge BS (110/33kV) | [5 empty] | Supply | MRG - MIDDLE RIDGE 110 CP
Description | Land area is 37223 sqm, Construction is conventional outdoor bulk class
Transformer size is 1x48/60MVA ONAN/ONAF;1x60MVA
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates
Load Category | Mixed Industrial
Localities | Supplies Carpendale, Grantham, Helidon, Postmans Ridge
|  |  |  | Latest Peak Compensated Load |  |  |  | 20.4 MVA on 09/06/2022 at 07:00
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 127.3 | 127.3 | 127.3 | 127.3 | 127.3 | 127.3 | 127.3 | 127.3 | 127.3 | 127.3
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 33.4 | 33.2 | 33.2 | 33 | 33 | 31 | 31.1 | 31.1 | 31.1 | 31.1
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.991 | 0.991 | 0.991 | 0.991 | 0.991 | 0.996 | 0.996 | 0.996 | 0.996 | 0.996
ECC Rating (MVA) | 69 | 69 | 69 | 69 | 69 | 78 | 78 | 78 | 78 | 78
50 PoE Load (MVA) | 30.9 | 30.7 | 30.6 | 30.5 | 30.5 | 29.9 | 29.9 | 29.9 | 29.9 | 29.9
50 PoE Load > 95% (MVA) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
Hours PA > 95% Peak Load | 279 | 279 | 279 | 279 | 279 | 279 | 279 | 279 | 279 | 279
Raw LAR (MVA)
2HR Rating (MVA) | 75 | 75 | 75 | 75 | 75 | 84 | 84 | 84 | 84 | 84
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6
Manual Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mobile Plant Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 61.8 | 61.8 | 61.8 | 61.8 | 61.8 | 61.8 | 61.8 | 61.8 | 61.8 | 61.8
N-1 Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## RVW
Bulk Supply Summary Information and Peak Load Forecast
Substation | RVW - Raceview BS (110/33kV) | [5 empty] | Supply | BKS - BLACKSTONE 110 CP
Description | Land area is 76972 sqm, Construction is conventional outdoor bulk class
Transformer size is 2x37/48/60MVA ONAN/ONAF/OFAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 1.4 MVA
Growth Rates
Load Category | Mixed Industrial
Localities | Supplies Boonah, Booval, Cooneana, Flinders, Ipswich South, Kalbar, Roderick St
|  |  |  | Latest Peak Compensated Load |  |  |  | 99.4 MVA on 17/03/2023 at 17:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 114.7 | 115.1 | 116.5 | 116.4 | 117.4 | 83.9 | 85.9 | 88 | 89.2 | 90.1
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.988 | 0.988 | 0.988 | 0.988 | 0.988 | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
ECC Rating (MVA) | 84 | 84 | 84 | 84 | 84 | 90 | 90 | 90 | 90 | 90
50 PoE Load (MVA) | 106.7 | 107.2 | 108.5 | 108.4 | 109.3 | 80.6 | 82.6 | 84.6 | 85.7 | 86.6
50 PoE Load > 95% (MVA) | 5.3 | 5.4 | 5.4 | 5.4 | 5.5 | 4 | 4.1 | 4.2 | 4.3 | 4.3
Hours PA > 95% Peak Load | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
Raw LAR (MVA) | SUMMER 2023/24: 22.7; SUMMER 2024/25: 23.2; SUMMER 2025/26: 24.5; SUMMER 2026/27: 24.4; SUMMER 2027/28: 25.3
2HR Rating (MVA) | 90 | 90 | 90 | 90 | 90 | 96 | 96 | 96 | 96 | 96
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 35.9 | 36.8 | 37.3 | 37.5 | 38.1 | 24.7 | 26 | 26.7 | 27.4 | 28
Manual Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mobile Plant Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 54.4 | 54.4 | 54.4 | 54.4 | 54.4 | 54.4 | 54.4 | 54.4 | 54.4 | 54.4
N-1 Capacity for Embedded Generation (MVA) | 27.2 | 27.2 | 27.2 | 27.2 | 27.2 | 27.2 | 27.2 | 27.2 | 27.2 | 27.2
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## SGT
Bulk Supply Summary Information and Peak Load Forecast
Substation | SGT - Sandgate BS (110/33kV) | [5 empty] | Supply | SPN - SOUTH PINE 110 CP
Description | Land area is 7910 sqm, Construction is conventional outdoor bulk class
Transformer size is 1x45/60/80MVA ONAN/ODAN/ODAF;1x48/64/80MVA ONAN/ONAF/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 2.3 MVA
Growth Rates
Load Category | Domestic
Localities | Supplies Bald Hills, Brighton, Sandgate
|  |  |  | Latest Peak Compensated Load |  |  |  | 89 MVA on 17/03/2023 at 17:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 191.4 | 191.4 | 191.4 | 191.4 | 191.4 | 191.4 | 191.4 | 191.4 | 191.4 | 191.4
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 93.6 | 92 | 91.2 | 89.8 | 89.5 | 77.2 | 77.3 | 77.4 | 77.2 | 76.9
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.997 | 0.997 | 0.997 | 0.997 | 0.997 | 0.998 | 0.998 | 0.998 | 0.998 | 0.998
ECC Rating (MVA) | 100 | 100 | 100 | 100 | 100 | 112 | 112 | 112 | 112 | 112
50 PoE Load (MVA) | 86.2 | 84.8 | 84 | 82.8 | 82.5 | 72.9 | 73 | 73.2 | 73 | 72.7
50 PoE Load > 95% (MVA) | 4.3 | 4.2 | 4.2 | 4.1 | 4.1 | 3.6 | 3.7 | 3.7 | 3.7 | 3.6
Hours PA > 95% Peak Load | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
Raw LAR (MVA)
2HR Rating (MVA) | 108 | 108 | 108 | 108 | 108 | 120 | 120 | 120 | 120 | 120
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 9.4 | 9.2 | 9.1 | 8.9 | 8.9 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8
Manual Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mobile Plant Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
N-1 Capacity for Embedded Generation (MVA) | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## SFD
Bulk Supply Summary Information and Peak Load Forecast
Substation | SFD - Stafford BS (110/33kV) | [5 empty] | Supply | SPN - SOUTH PINE 110 CP
Description | Land area is 9770 sqm, Construction is conventional outdoor bulk class
Transformer size is 1x45/60/80MVA ONAN/ODAN/ODAF;2x80MVA ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 7.7 MVA
Growth Rates
Load Category | Mixed Domestic
Localities | Supplies Chermside, Clayfield, Enoggera, Grovely, Kedron, Stafford
|  |  |  | Latest Peak Compensated Load |  |  |  | 150.6 MVA on 17/03/2023 at 16:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Night | Night | Night | Night | Night
NCC Rating (MVA) | 262.3 | 262.3 | 262.3 | 262.3 | 262.3 | 262.3 | 262.3 | 262.3 | 262.3 | 262.3
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 175.4 | 173 | 171.8 | 169.7 | 169 | 140.2 | 140.4 | 140.6 | 140.3 | 139.8
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.996 | 0.996 | 0.996 | 0.996 | 0.996
ECC Rating (MVA) | 182.2 | 182.2 | 182.2 | 182.2 | 182.2 | 206 | 206 | 206 | 206 | 206
50 PoE Load (MVA) | 164.6 | 162.5 | 161.3 | 159.3 | 158.7 | 133.4 | 133.6 | 133.8 | 133.4 | 133
50 PoE Load > 95% (MVA) | 8.2 | 8.1 | 8.1 | 8 | 7.9 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7
Hours PA > 95% Peak Load | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Raw LAR (MVA)
2HR Rating (MVA) | 198.1 | 198.1 | 198.1 | 198.1 | 198.1 | 221.9 | 221.9 | 221.9 | 221.9 | 221.9
Auto Trans Avail (MVA) | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2
Remote Trans Avail (MVA) | 43.8 | 43.2 | 42.7 | 42.1 | 42 | 34.9 | 34.9 | 35 | 34.9 | 34.8
Manual Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mobile Plant Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 143.1 | 143.1 | 143.1 | 143.1 | 143.1 | 143.1 | 143.1 | 143.1 | 143.1 | 143.1
N-1 Capacity for Embedded Generation (MVA) | 95.1 | 95.1 | 95.1 | 95.1 | 95.1 | 95.1 | 95.1 | 95.1 | 95.1 | 95.1
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## SIS
Bulk Supply Summary Information and Peak Load Forecast
Substation | SIS - Stradbroke Is BS (110/33kV) | [5 empty] | Supply | LGH - LOGANLEA 110 CP
Description | Land area is 19020 sqm, Construction is conventional outdoor bulk class
Transformer size is 1x48/60MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates
Load Category | Domestic
Localities | Supplies Stradbroke Is
|  |  |  | Latest Peak Compensated Load |  |  |  | 4.3 MVA on 04/01/2023 at 18:00
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 4.9 | 4.9 | 4.8 | 4.8 | 4.8 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.972 | 0.972 | 0.972 | 0.972 | 0.972 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
ECC Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 PoE Load (MVA) | 4.8 | 4.7 | 4.7 | 4.6 | 4.6 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9
50 PoE Load > 95% (MVA) | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hours PA > 95% Peak Load | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5
Raw LAR (MVA) | 4.8 | 4.7 | 4.7 | 4.6 | 4.6 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9
2HR Rating (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 4.8 | 4.7 | 4.7 | 4.6 | 4.6 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9
Manual Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mobile Plant Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POPS | bar: SUMMER 2023/24 to WINTER 2027
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
N-1 Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## SRH
Bulk Supply Summary Information and Peak Load Forecast
Substation | SRH - Sunrise Hills BS (132/33kV) | [5 empty] | Supply | WLG - WOOLOOGA 132 CP
Description | Land area is 5990 sqm, Construction is a mixture of various construction classes
Transformer size is 1x30/48/60MVA ONAN/ODAN/ODAF;1x48/60/64/80MVA ONAN/ODAN/ONAF/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates
Load Category | Domestic
Localities | Supplies Black Mountain, Coolum, Cooroy, Peregian, Tewantin
|  |  |  | Latest Peak Compensated Load |  |  |  | 81 MVA on 03/02/2023 at 18:30
Major Loads
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Night | Night | Night | Night | Night | Night | Night | Night | Night | Night
NCC Rating (MVA) | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 90.8 | 89.9 | 89.6 | 88.5 | 88.3 | 80.4 | 80.3 | 80.3 | 79.9 | 79.2
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.979 | 0.979 | 0.979 | 0.979 | 0.979 | 0.987 | 0.987 | 0.987 | 0.987 | 0.987
ECC Rating (MVA) | 75 | 75 | 75 | 75 | 75 | 84 | 84 | 84 | 84 | 84
50 PoE Load (MVA) | 83.1 | 82.3 | 82 | 81 | 80.8 | 75.6 | 75.6 | 75.6 | 75.2 | 74.5
50 PoE Load > 95% (MVA) | 4.2 | 4.1 | 4.1 | 4.1 | 4 | 3.8 | 3.8 | 3.8 | 3.8 | 3.7
Hours PA > 95% Peak Load | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Raw LAR (MVA) | SUMMER 2023/24: 8.1; SUMMER 2024/25: 7.3; SUMMER 2025/26: 7; SUMMER 2026/27: 6; SUMMER 2027/28: 5.8
2HR Rating (MVA) | 81 | 81 | 81 | 81 | 81 | 90 | 90 | 90 | 90 | 90
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 31.3 | 30.9 | 30.8 | 30.4 | 30.3 | 29.5 | 29.5 | 29.5 | 29.5 | 29.3
Manual Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mobile Plant Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6
N-1 Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
LARc (MVA)
LARc (MW)
Customer Category | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural | Rural
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index

## VPK
Bulk Supply Summary Information and Peak Load Forecast
Substation | VPK - Victoria Park BS (110/33kV) | [5 empty] | Supply | MRE - MURARRIE 110 CP
Description | Land area is 10200 sqm, Construction is a mixture of various construction classes
Transformer size is 2x66/80/96/120MVA ONAN/OFAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates
Load Category | Industrial
Localities | Supplies Astor Terrace, New Farm, Newmarket, Victoria Park
|  |  |  | Latest Peak Compensated Load |  |  |  | 49.3 MVA on 03/02/2023 at 14:30
|  |  |  | Major Loads |  |  |  | Yes
PEAK LOAD FORECAST AND CAPACITY | SUMMER |  |  |  |  | WINTER
| 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Peak Risk Period | Day | Day | Day | Day | Day | Day | Day | Day | Day | Day
NCC Rating (MVA) | 251.4 | 251.4 | 251.4 | 251.4 | 251.4 | 251.4 | 251.4 | 251.4 | 251.4 | 251.4
Contracted non-network (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 PoE Load (MVA) | 66.5 | 65.8 | 65.4 | 64.7 | 64.5 | 45.8 | 45.9 | 46.1 | 46.1 | 46
LARn (MVA)
LARn (MW)
Power Factor at Peak Load | 0.988 | 0.988 | 0.988 | 0.988 | 0.988 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
ECC Rating (MVA) | 138 | 138 | 138 | 138 | 138 | 156 | 156 | 156 | 156 | 156
50 PoE Load (MVA) | 64 | 63.3 | 62.9 | 62.2 | 62.1 | 44.5 | 44.6 | 44.8 | 44.8 | 44.7
50 PoE Load > 95% (MVA) | 3.2 | 3.2 | 3.1 | 3.1 | 3.1 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2
Hours PA > 95% Peak Load | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Raw LAR (MVA)
2HR Rating (MVA) | 150 | 150 | 150 | 150 | 150 | 168 | 168 | 168 | 168 | 168
Auto Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remote Trans Avail (MVA) | 23.2 | 22.8 | 22.6 | 22.2 | 22.1 | 15.9 | 16 | 16.1 | 16.1 | 16.1
Manual Trans Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mobile Plant Avail (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POPS | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Bus Configuration | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid | Solid
Capacity for Embedded Generation (MVA) | 131.7 | 131.7 | 131.7 | 131.7 | 131.7 | 131.7 | 131.7 | 131.7 | 131.7 | 131.7
N-1 Capacity for Embedded Generation (MVA) | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66
LARc (MVA)
LARc (MW)
Customer Category | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban | Urban
Meets Security Standard | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Back to Index