## Compendium Guide
1. Version Control |  |  | 4.2. Fault Calculation Methodology
Version | Description | Date | Based on the IEC60909 standard, the fault calculation performed in the Power Factory assumes:
1 | First 2025 report version release | 2025-06-26 | • Transformers being set to nominal taps,
2 |  |  | • Conductor temperature of
o Maximum Fault: 20°C
o Minimum Fault: Individual Annealing Temperature
2. Known Limitations |  |  | • Voltage factor value set as Cmax = 1.1 under Max Fault Levels and Cmin = 1.0 under Min Fault Levels, for voltages above 1kV.
This section outlines any report shortfalls that users should be aware of. |  |  | 4.3. Study Cases Modelled
No known limitations in version 1. |  |  |  | Scenario | Voltage factor (C) | Generation1 | Switch Status2 | Model Version | Study Case | Study Case Date
3. Disclaimer |  |  | SEQ | Max (Max Fault Normal Config) | 1.1 | Max Dispatch | System Normal | V-3-3-88 Transmission_2025 | Transmission_2025_Max_FL | 2026-01-01 17:00
The Energex Fault Level Report is prepared and made available solely for information purposes. Whilst care was taken in the preparation of the information in this report, and it is provided with the best intentions and good faith, Energex accepts no responsibility or liability (including without limitation, liability to any person by reason of negligence or negligent mis-statement) for any loss or damage that may be incurred by any person acting in reliance on this information or assumptions drawn from it, except to the extent that liability under any applicable Queensland or Commonwealth of Australia statute cannot be excluded.
Energex makes no representation or warranty as to the accuracy, reliability, completeness or suitability for any particular purpose of the information in this document. All information should be independently investigated, reviewed, analysed, and verified, and must not be relied upon in connection with any investment proposal or decision. The information contained in this report is subject to annual review. Energex is obligated to publish future editions of this report on an annual basis in accordance with the National Electricity Rules. |  |  | 1Generation scenario considered for each study is clarified the next section. 2Switch status attempts to reflect the 'system normal’ conditions of the network where network elements being ‘intact’ and normally open switches, circuit breakers and isolators remain per their normal state when performing the fault level study. This report assumes that all existing and known commissioned and de-commissioned plants have been taken into consideration with normal network operating conditions applied within the model. Due to the dynamic nature of the network, and the model being a snapshot at a given point of time, it is possible that further deviation of network could occur as compared to what was modelled. All reasonable efforts have also been placed to identify the system normal state of all network switches and generation connections. No future projects or network models have been included in the sub-transmission models.
This work is copyright. Material contained in this document may be reproduced for personal, in-house or non-commercial use, without formal permission or charge, provided there is due acknowledgement of Energex as the source. Request and enquiries concerning reproduction and rights for a purpose other than personal, in-house or non-commercial use, should be addressed to the Group Manager Renewables and Distributed Energy. |  |  | 4.4. Generation Generation considered for both Powerlink and Energex networks (transmission, subtransmission and distribution) are as follows:
Users of the Report must acknowledge and accept that:
• The information obtained from the Report is intended as general in nature, may be based on assumptions that change with time and may not necessarily be complete. Information contained in, or obtained from, the Report should not be relied upon, and use of the information contained in the Report is at your own risk. |  |  | Generation Scenario |  | Powerlink (Transmission) |  |  |  | Energex (Subtransmission and Distribution)
• Energex makes no representation or warranty as to the quality, accuracy, completeness, merchantability, suitability or fitness for purpose of any information contained in the Report. The Report is not a substitute for independent advice and research. The information contained in this report is subject to annual review. |  |  | Max Dispatch |  | All modelled generating units in service |  |  |  | All modelled embedded generation in service
• Energex does not accept any responsibility or liability for any loss or damage, however caused, which any person or entity may suffer in connection with the information contained in, or obtained from, the Report. |  |  | · Fault Level contributions of Non-Synchronous generators (e.g. PV and BESS elements) have been modelled as per the prescribed levels in their respective Generator Performance Standards (GPS) information.
Use of the Report constitutes acceptance of the terms of this Disclaimer. |  |  | · Distribution Embedded Generators are modelled at the upstream supplying subtransmission substation to account for their impact on Fault Levels.
4. Introduction and Methodology
This Fault Level Summary Report is prepared to provide a reference for designers, asset managers, planners, customer representatives and network operators. Engineers should carry out their own due diligence on the information provided by this report prior to applying it to engineering activities. Whenever possible, these activities should be undertaken with an awareness of fault levels and actions to manage fault levels.
The fault levels contained in this Report are indicative values under certain network configurations as per the methodology described below. Most Fault levels reported are under normal network conditions. Changes to Network Configuration can result in fault levels above or below the levels reported. Note that Only Terminals associated with an alternate configuration are reported. Any other variations of fault level studies would require the user to source or modify the data to meet their specific requirements.
In preparing the Report:
• The sub-transmission network model was developed and prepared using Power Factory 2024 SP5. This network modelling software program was used to produce the Fault Level Summary Report.
• A transmission network model was obtained from Powerlink in PSSE V32 format. This model was then converted to PowerFactory and merged with the sub-transmission model at all of Energex’s respective common coupling points.
• Conversion of the transmission network from PSSE to PowerFactory was done using PowerFactory 2024 to leverage off the newer version updates and features.
• Using Python automation, the following fault level results were obtained at different nodes and buses across the entire network:
o 3-Phase fault levels (kA and MVA);
o 2-Phase - G fault levels (kA and MVA);
o 1-Phase - G fault levels (kA and MVA);
o Positive sequence resistance and reactance (ohms);
o Zero sequence resistance and reactance (ohms); and
o Negative sequence resistance and reactance (ohms)
4.1. Fault Calculation Data
The following data has been used to prepare the Fault Level Summary:
· Powerlink’s PSS/E data model source impedances;
· Network topology and connectivity from Energex’s SCADA and GIS systems; and
· Where applicable and available:
o Connection agreements for generator data;
o Transformer test certificates; and
o Nameplate information.

## Max Fault Level Report
Sub Code | Substation | BSP | Reported on Bus in PowerFactory | Voltage (kV) | 2025 3-Ph Fault Level (kA) | 2025 3-Ph Fault Level (MVA) | 2025 1-Ph-G Fault Level (kA) | 2025 1-Ph-G Fault Level (MVA) | 2025 3*I0 Fault Level (kA) | 2025 B 2-Ph-G Fault Level (kA) | 2025 B 2-Ph-G Fault Level (MVA) | 2025 C 2-Ph-G Fault Level (kA) | 2025 C 2-Ph-G Fault Level (MVA) | R1 (Ohms) | X1 (Ohms) | R0 (Ohms) | X0 (Ohms) | R2 (Ohms) | X2 (Ohms)
935 | QR Victoria Park | Victoria Park Bulk Supply | 93533kVB1_Term | 33 | 20.6108 | 1178.0659 | 2.3074 | 43.9625 | 1.1634 | 18.3969 | 350.5075 | 17.2381 | 328.43 | 0.04978 | 1.0162 | 27.0372 | 0.57991 | 0.05026 | 1.0198
ABM | Abermain Bulk | Abermain Bulk Supply | ABM33kVB1_Term | 33 | 24.4614 | 1398.1565 | 1.1642 | 22.1807 | 0.58422 | 21.4215 | 408.1353 | 20.8377 | 397.0105 | 0.05788 | 0.85508 | 53.9037 | -2.3038 | 0.05832 | 0.85949
ACR | Albany Creek | Brendale Bulk Supply | ACR33kVB1_Term | 33 | 17.2668 | 986.9327 | 3.1427 | 59.8769 | 1.7335 | 14.9292 | 284.4397 | 14.9552 | 284.9345 | 0.15174 | 1.2045 | 1.902 | 17.4733 | 0.15086 | 1.2108
ACR | Albany Creek | Brendale Bulk Supply | ACR33kVB2_Term | 33 | 17.2079 | 983.5614 | 3.1401 | 59.8272 | 1.7325 | 14.8789 | 283.4819 | 14.9039 | 283.9578 | 0.15303 | 1.2085 | 1.9242 | 17.4792 | 0.15215 | 1.2148
ACR | Acacia Ridge | Brendale Bulk Supply | ACR11kVB1_Term | 11 | 10.8888 | 207.4596 | 1.9441 | 12.3464 | 1.0678 | 9.4176 | 59.81 | 9.4626 | 60.0957 | 0.02937 | 0.64104 | 0.01853 | 9.4998 | 0.02928 | 0.64174
ACR | Acacia Ridge | Brendale Bulk Supply | ACR11kVB2_Term | 11 | 10.8888 | 207.4596 | 1.9441 | 12.3464 | 1.0678 | 9.4176 | 59.81 | 9.4626 | 60.0957 | 0.02937 | 0.64104 | 0.01853 | 9.4998 | 0.02928 | 0.64174
AFD | Archerfield Bulk | Archerfield Bulk Supply | 43041 ARCFLD1D | 110 | 21.9918 | 4190.0016 | 23.5955 | 1498.5161 | 25.6581 | 22.9687 | 1458.7106 | 22.8857 | 1453.4369 | 0.48875 | 3.1399 | 0.40253 | 2.4734 | 0.49403 | 3.1632
AFD | Archerfield Bulk | Archerfield Bulk Supply | 43042 ARCFLD2D | 110 | 21.9919 | 4190.0115 | 23.6408 | 1501.3949 | 25.7651 | 22.9907 | 1460.1065 | 22.924 | 1455.8677 | 0.48875 | 3.1399 | 0.3967 | 2.4571 | 0.49402 | 3.1632
AFD | Archerfield Bulk | Archerfield Bulk Supply | AFD33kVB2_Term | 33 | 17.8248 | 1018.8234 | 2.2643 | 43.1399 | 1.2103 | 15.3965 | 293.3426 | 15.4647 | 294.6413 | 0.06869 | 1.1742 | 0.02225 | 25.4255 | 0.06902 | 1.1769
AFD | Archerfield | Archerfield Bulk Supply | AFD11kVB2_Term | 11 | 11.0705 | 210.9217 | 1.9525 | 12.4002 | 1.0709 | 9.5799 | 60.8404 | 9.6201 | 61.0957 | 0.0257 | 0.63073 | 0.01807 | 9.4753 | 0.02574 | 0.63104
AFD | Archerfield | Archerfield Bulk Supply | AFD11kVB3_Term | 11 | 11.0705 | 210.9217 | 1.9525 | 12.4002 | 1.0709 | 9.5799 | 60.8404 | 9.6201 | 61.0957 | 0.0257 | 0.63073 | 0.01807 | 9.4753 | 0.02574 | 0.63104
AGE | Ashgrove | Ashgrove West Bulk Supply | AGE33kVB1_Term | 33 | 17.018 | 972.7082 | 2.1397 | 40.7671 | 1.1425 | 14.6966 | 280.0074 | 14.7766 | 281.5321 | 0.11549 | 1.2265 | 0.60276 | 26.9263 | 0.116 | 1.2286
AGE | Ashgrove | Ashgrove West Bulk Supply | AGE11kVB1_Term | 11 | 10.5095 | 200.2336 | 1.9357 | 12.2932 | 1.0661 | 9.0926 | 57.7458 | 9.1385 | 58.0372 | 0.03089 | 0.66421 | 0.01806 | 9.5015 | 0.03095 | 0.66445
AGE | Ashgrove | Ashgrove West Bulk Supply | AGE11kVB2_Term | 11 | 10.5095 | 200.2336 | 1.9357 | 12.2932 | 1.0661 | 9.0926 | 57.7458 | 9.1385 | 58.0372 | 0.03089 | 0.66421 | 0.01806 | 9.5015 | 0.03095 | 0.66445
AGT | Algester Bulk | Algester Bulk Supply | AGT33kVB1_Term | 33 | 19.7644 | 1129.687 | 2.3104 | 44.0196 | 1.23 | 17.0434 | 324.7196 | 17.1273 | 326.3183 | 0.07523 | 1.0582 | 0.00943 | 25.1036 | 0.07472 | 1.0636
AGT | Algester | Algester Bulk Supply | AGT11kVB2_Term | 11 | 11.4244 | 217.6631 | 1.9546 | 12.4136 | 1.0773 | 9.8166 | 62.3439 | 9.8599 | 62.619 | 0.03074 | 0.61101 | 0.01784 | 9.4955 | 0.02699 | 0.62024
AGT | Algester | Algester Bulk Supply | AGT11kVB3_Term | 11 | 11.4244 | 217.6631 | 1.9546 | 12.4136 | 1.0773 | 9.8166 | 62.3439 | 9.8599 | 62.619 | 0.03074 | 0.61101 | 0.01784 | 9.4955 | 0.02699 | 0.62024
AGW | Ashgrove West Bulk | Ashgrove West Bulk Supply | AGW33kVB2_Term | 33 | 18.9267 | 1081.8074 | 2.1831 | 41.5933 | 1.1594 | 16.3456 | 311.4247 | 16.4262 | 312.961 | 0.07895 | 1.1048 | 0.01493 | 26.597 | 0.07946 | 1.1069
AHD | Alexander Headlands | Palmwood Bulk Supply | 43000 ALEXHD1D | 132 | 9.984 | 2282.6415 | 10.5166 | 801.471 | 11.1765 | 10.3555 | 789.1934 | 10.2078 | 777.9371 | 1.4385 | 8.274 | 1.3617 | 6.9427 | 1.4168 | 8.3269
AHD | Alexander Headlands | Palmwood Bulk Supply | AHD11kVB1_Term | 11 | 9.8302 | 187.2906 | 2.3999 | 15.2414 | 1.3668 | 8.5821 | 54.5036 | 8.4947 | 53.9489 | 0.02355 | 0.7104 | 0.7315 | 7.2784 | 0.0234 | 0.71076
AHD | Alexander Headlands | Palmwood Bulk Supply | AHD11kVB2_Term | 11 | 10.0543 | 191.561 | 2.4086 | 15.2967 | 1.3683 | 8.7751 | 55.7296 | 8.6886 | 55.1801 | 0.02356 | 0.69454 | 0.7315 | 7.2784 | 0.02341 | 0.69491
AHD | Alexander Headlands | Palmwood Bulk Supply | AHD11kVB3_Term | 11 | 9.8302 | 187.2906 | 2.3999 | 15.2414 | 1.3668 | 8.5821 | 54.5036 | 8.4947 | 53.9489 | 0.02355 | 0.7104 | 0.7315 | 7.2784 | 0.0234 | 0.71076
AHD | Alexander Headlands | Palmwood Bulk Supply | AHD11kVB4_Term | 11 | 10.0543 | 191.561 | 2.4086 | 15.2967 | 1.3683 | 8.7751 | 55.7296 | 8.6886 | 55.1801 | 0.02356 | 0.69454 | 0.7315 | 7.2784 | 0.02341 | 0.69491
AHL | Arana Hills | Brendale Bulk Supply | AHL33kVB1_Term | 33 | 8.0416 | 459.6414 | 2.122 | 40.4291 | 1.2283 | 6.8303 | 130.1345 | 7.0654 | 134.6133 | 0.69285 | 2.513 | 1.5684 | 24.4284 | 0.69869 | 2.5465
AHL | Arana Hills | Brendale Bulk Supply | AHL11kVB1_Term | 11 | 9.39 | 178.9025 | 1.9049 | 12.0975 | 1.0791 | 7.9574 | 50.5366 | 8.08 | 51.3152 | 0.09545 | 0.73798 | 0.01794 | 9.5006 | 0.0926 | 0.76395
ALY | Annerley | Tennyson Bulk Supply | ALY33kVB1_Term | 33 | 19.9137 | 1138.2227 | 3.0174 | 57.4888 | 1.6379 | 17.1593 | 326.9278 | 17.2619 | 328.8838 | 0.12654 | 1.0451 | 1.0541 | 18.7058 | 0.12776 | 1.0519
ALY | Annerley | Tennyson Bulk Supply | ALY11kVB1_Term | 11 | 10.5783 | 201.5429 | 1.9345 | 12.2858 | 1.0652 | 9.1463 | 58.087 | 9.1965 | 58.4053 | 0.03346 | 0.65977 | 0.01942 | 9.5166 | 0.0336 | 0.66053
ALY | Annerley | Tennyson Bulk Supply | ALY11kVB2_Term | 11 | 10.5783 | 201.5429 | 1.9345 | 12.2858 | 1.0652 | 9.1463 | 58.087 | 9.1965 | 58.4053 | 0.03346 | 0.65977 | 0.01942 | 9.5166 | 0.0336 | 0.66053
AMR | Amamoor | Gympie Bulk Supply | AMR33kVB1_Term | 33 | 1.6985 | 97.0846 | 0.7954 | 15.1545 | 0.50533 | 1.3717 | 26.134 | 1.6046 | 30.5715 | 8.2632 | 9.1654 | 11.1603 | 55.7204 | 8.258 | 9.1663
AMR | Amamoor | Gympie Bulk Supply | AMR11kVB1_Term | 11 | 2.4441 | 46.5665 | 0.83861 | 5.3259 | 0.50122 | 2.0473 | 13.0019 | 2.2125 | 14.0513 | 1.029 | 2.667 | 0.11088 | 19.5662 | 1.0284 | 2.6671
AMR | Amamoor | Gympie Bulk Supply | AMR11kVB2_Term | 11 | 2.4441 | 46.5665 | 0.83861 | 5.3259 | 0.50122 | 2.0473 | 13.0019 | 2.2125 | 14.0513 | 1.029 | 2.667 | 0.11088 | 19.5662 | 1.0284 | 2.6671
APB | Brisbane Airport | Nudgee Bulk Supply | APB33kVB1_Term | 33 | 15.3311 | 876.2882 | 2.9657 | 56.5049 | 1.6465 | 13.259 | 252.618 | 13.2778 | 252.9766 | 0.22818 | 1.3481 | 2.8437 | 18.2424 | 0.22785 | 1.3556
APB | Brisbane Airport | Nudgee Bulk Supply | APB33kVB2_Term | 33 | 15.3469 | 877.1909 | 2.9667 | 56.5236 | 1.6469 | 13.2727 | 252.8782 | 13.2914 | 253.2344 | 0.22813 | 1.3467 | 2.847 | 18.2376 | 0.2278 | 1.3542
APB | Brisbane Airport | Nudgee Bulk Supply | APB11kVB2_Term | 11 | 10.6162 | 202.2658 | 1.9388 | 12.313 | 1.0674 | 9.1772 | 58.2833 | 9.2303 | 58.6201 | 0.03522 | 0.65724 | 0.01807 | 9.4964 | 0.03518 | 0.65808
ARG | Acacia Ridge | Algester Bulk Supply | ARG33kVB1_Term | 33 | 17.1946 | 982.8053 | 2.2625 | 43.106 | 1.2135 | 14.8289 | 282.5282 | 14.9145 | 284.1584 | 0.12714 | 1.2128 | 0.79266 | 25.3523 | 0.12664 | 1.2182
ARG | Acacia RIdge | Algester Bulk Supply | ARG11kVB1_Term | 11 | 10.9169 | 207.9948 | 2.2618 | 14.3642 | 1.1552 | 10.0215 | 63.6452 | 8.8791 | 56.3897 | 0.03891 | 0.63904 | 9.0248 | 0.47841 | 0.03886 | 0.63964
ARG | Acacia RIdge | Algester Bulk Supply | ARG11kVB2_Term | 11 | 10.9169 | 207.9948 | 2.2618 | 14.3642 | 1.1552 | 10.0215 | 63.6452 | 8.8791 | 56.3897 | 0.03891 | 0.63904 | 9.0248 | 0.47841 | 0.03886 | 0.63964
ARL | Arundel | Molendinar Bulk Supply | ARL33kVB1_Term | 33 | 19.1925 | 1096.9963 | 3.1589 | 60.1857 | 1.7249 | 16.5642 | 315.5908 | 16.6541 | 317.3032 | 0.13087 | 1.0847 | 1.1604 | 17.6893 | 0.13062 | 1.0894
ARL | Arundel | Molendinar Bulk Supply | ARL11kVB1_Term | 11 | 10.4962 | 199.9785 | 1.9329 | 12.2753 | 1.0648 | 9.0768 | 57.6457 | 9.1272 | 57.9656 | 0.03409 | 0.66506 | 0.01953 | 9.5178 | 0.03406 | 0.66559
ARL | Arundel | Molendinar Bulk Supply | ARL11kVB2_Term | 11 | 10.4962 | 199.9785 | 1.9329 | 12.2753 | 1.0648 | 9.0768 | 57.6457 | 9.1272 | 57.9656 | 0.03409 | 0.66506 | 0.01953 | 9.5178 | 0.03406 | 0.66559
AST | Ann St | Belmont Bulk Supply | 43020 ANNST1D | 110 | 23.3386 | 4446.5964 | 28.3547 | 1800.7673 | 36.7109 | 28.1321 | 1786.6297 | 26.3463 | 1673.215 | 0.31956 | 2.9778 | 0.3345 | 1.3335 | 0.32504 | 3.0189
AST | Ann St | Belmont Bulk Supply | AST11kVB1_Term | 11 | 13.4159 | 255.6067 | 5.0213 | 31.8895 | 3.0915 | 11.8136 | 75.0267 | 11.6035 | 73.6921 | 0.01342 | 0.52083 | 0.3135 | 3.1193 | 0.01349 | 0.52199
AST | Ann St | Belmont Bulk Supply | AST11kVB2_Term | 11 | 13.4159 | 255.6069 | 5.0213 | 31.8895 | 3.0915 | 11.8137 | 75.0267 | 11.6035 | 73.6921 | 0.01342 | 0.52083 | 0.3135 | 3.1193 | 0.01349 | 0.52199
AST | Ann St | Belmont Bulk Supply | AST11kVB3_Term | 11 | 13.4159 | 255.6067 | 5.0213 | 31.8895 | 3.0915 | 11.8136 | 75.0267 | 11.6035 | 73.6921 | 0.01342 | 0.52083 | 0.3135 | 3.1193 | 0.01349 | 0.52199
AST | Ann St | Belmont Bulk Supply | AST11kVB4_Term | 11 | 14.2648 | 271.7819 | 5.0851 | 32.2948 | 3.1334 | 12.4379 | 78.9912 | 12.2218 | 77.6188 | 0.01233 | 0.48983 | 0.3135 | 3.1193 | 0.01253 | 0.5005
AST | Ann St | Belmont Bulk Supply | AST11kVB5_Term | 11 | 14.2649 | 271.7821 | 5.0851 | 32.2948 | 3.1334 | 12.4379 | 78.9912 | 12.2218 | 77.6188 | 0.01233 | 0.48983 | 0.3135 | 3.1193 | 0.01253 | 0.5005
AST | Ann St | Belmont Bulk Supply | AST11kVB6_Term | 11 | 14.2648 | 271.7819 | 5.0851 | 32.2948 | 3.1334 | 12.4379 | 78.9912 | 12.2218 | 77.6188 | 0.01233 | 0.48983 | 0.3135 | 3.1193 | 0.01253 | 0.5005
ATC | Astor Terrace | Victoria Park Bulk Supply | ATC33kVB1_Term | 33 | 18.4133 | 1052.4606 | 2.2831 | 43.4991 | 1.1574 | 16.4918 | 314.2107 | 15.3502 | 292.4602 | 0.13492 | 1.1308 | 27.1237 | 0.69568 | 0.1354 | 1.1344
ATC | Astor Terrace | Victoria Park Bulk Supply | ATC33kVB3_Term | 33 | 18.3734 | 1050.1786 | 2.2825 | 43.4882 | 1.1573 | 16.4571 | 313.5495 | 15.316 | 291.8084 | 0.13735 | 1.133 | 27.125 | 0.69753 | 0.13783 | 1.1366
ATC | Astor Terrace | Victoria Park Bulk Supply | ATC33kVB2_Term | 33 | 18.3985 | 1051.6147 | 2.2829 | 43.4957 | 1.1573 | 16.4789 | 313.966 | 15.3375 | 292.2181 | 0.13554 | 1.1316 | 27.1243 | 0.69653 | 0.13603 | 1.1353
ATC | Astor Terrace | Victoria Park Bulk Supply | ATC11kVB1_Term | 11 | 11.0161 | 209.8842 | 1.9493 | 12.3796 | 1.0696 | 9.531 | 60.53 | 9.5734 | 60.799 | 0.0271 | 0.63393 | 0.01676 | 9.4889 | 0.02715 | 0.63433
ATC | Astor Terrace | Victoria Park Bulk Supply | ATC11kVB2_Term | 11 | 11.0161 | 209.8842 | 1.9493 | 12.3796 | 1.0696 | 9.531 | 60.53 | 9.5734 | 60.799 | 0.0271 | 0.63393 | 0.01676 | 9.4889 | 0.02715 | 0.63433
ATC | Astor Terrace | Victoria Park Bulk Supply | ATC11kVB3_Term | 11 | 11.0161 | 209.8842 | 1.9493 | 12.3796 | 1.0696 | 9.531 | 60.53 | 9.5734 | 60.799 | 0.0271 | 0.63393 | 0.01676 | 9.4889 | 0.02715 | 0.63433
BBH | Broadbeach | Mudgeeraba Bulk Supply | 43060 BRDBCH1D | 110 | 17.2775 | 3291.8125 | 20.9118 | 1328.0794 | 26.3963 | 21.2358 | 1348.6571 | 18.5686 | 1179.2628 | 0.45358 | 4.02 | 0.74591 | 1.8429 | 0.45393 | 4.0273
BBH | Broadbeach | Mudgeeraba Bulk Supply | 43061 BRDBCH2D | 110 | 17.2775 | 3291.8125 | 20.9117 | 1328.0698 | 26.3957 | 21.236 | 1348.666 | 18.568 | 1179.2272 | 0.45358 | 4.02 | 0.74607 | 1.8429 | 0.45393 | 4.0273
BBH | Broadbeach | Mudgeeraba Bulk Supply | BBH11kVB1_Term | 11 | 10.6095 | 202.1376 | 2.4299 | 15.4319 | 1.3718 | 9.2622 | 58.8227 | 9.1639 | 58.1984 | 0.01647 | 0.65861 | 0.7315 | 7.2784 | 0.01648 | 0.65868
BBH | Broadbeach | Mudgeeraba Bulk Supply | BBH11kVB2_Term | 11 | 10.7054 | 203.9659 | 2.4332 | 15.453 | 1.3723 | 9.3449 | 59.3484 | 9.2469 | 58.7256 | 0.01649 | 0.6527 | 0.7315 | 7.2784 | 0.01649 | 0.65278
BBH | Broadbeach | Mudgeeraba Bulk Supply | BBH11kVB3_Term | 11 | 10.7054 | 203.9659 | 2.4332 | 15.453 | 1.3723 | 9.3449 | 59.3484 | 9.2469 | 58.7256 | 0.01649 | 0.6527 | 0.7315 | 7.2784 | 0.01649 | 0.65278
BBH | Broadbeach | Mudgeeraba Bulk Supply | BBH11kVB4_Term | 11 | 10.6095 | 202.1376 | 2.4299 | 15.4319 | 1.3718 | 9.2622 | 58.8227 | 9.1639 | 58.1984 | 0.01647 | 0.65861 | 0.7315 | 7.2784 | 0.01648 | 0.65868
BBS | Belmont Bulk | Belmont Bulk Supply | BBS33kVB1_Term | 33 | 27.7841 | 1588.0767 | 1.1685 | 22.2624 | 0.58698 | 24.2401 | 461.8365 | 23.6532 | 450.6542 | 0.04113 | 0.75362 | 53.699 | -4.028 | 0.04006 | 0.76093
BBS | Belmont | Belmont Bulk Supply | BBS11kVB1_Term | 11 | 12.791 | 243.7018 | 1.9735 | 12.5331 | 1.0896 | 10.8751 | 69.0659 | 10.9278 | 69.4006 | 0.03571 | 0.54527 | 0.02085 | 9.5143 | 0.02946 | 0.5653
BDA | Buranda | Tennyson Bulk Supply | BDA33kVB1_Term | 33 | 17.6773 | 1010.3915 | 2.9157 | 55.5509 | 1.5947 | 15.2361 | 290.2874 | 15.3202 | 291.889 | 0.15985 | 1.1751 | 1.5564 | 19.1308 | 0.16148 | 1.1833
BDA | Buranda | Tennyson Bulk Supply | BDA11kVB1_Term | 11 | 12.4093 | 236.4294 | 1.9722 | 12.525 | 1.088 | 10.584 | 67.2175 | 10.6348 | 67.5399 | 0.0285 | 0.5624 | 0.01701 | 9.4883 | 0.02894 | 0.57898
BDA | Buranda | Tennyson Bulk Supply | BDA11kVB2_Term | 11 | 12.4093 | 236.4294 | 1.9722 | 12.525 | 1.088 | 10.584 | 67.2175 | 10.6348 | 67.5399 | 0.0285 | 0.5624 | 0.01701 | 9.4883 | 0.02894 | 0.57898
BDA | Buranda | Tennyson Bulk Supply | BDA11kVB3_Term | 11 | 12.4093 | 236.4294 | 1.9722 | 12.525 | 1.088 | 10.584 | 67.2175 | 10.6348 | 67.5399 | 0.0285 | 0.5624 | 0.01701 | 9.4883 | 0.02894 | 0.57898
BDB | Bundamba | Bundamba Bulk Supply | BDB11kVB1_Term | 11 | 9.1184 | 173.7296 | 3.3638 | 21.3627 | 2.0617 | 8.0306 | 51.0015 | 7.8947 | 50.1382 | 0.02157 | 0.76608 | 0.47025 | 4.679 | 0.02162 | 0.76625
BDB | Bundamba | Bundamba Bulk Supply | BDB11kVB2_Term | 11 | 9.2061 | 175.399 | 3.3716 | 21.4128 | 2.0632 | 8.1063 | 51.4819 | 7.9697 | 50.6145 | 0.02119 | 0.75879 | 0.47025 | 4.679 | 0.02124 | 0.75896
BDB | Bundamba | Bundamba Bulk Supply | BDB11kVB3_Term | 11 | 9.2061 | 175.399 | 3.3716 | 21.4128 | 2.0632 | 8.1063 | 51.4819 | 7.9697 | 50.6145 | 0.02119 | 0.75879 | 0.47025 | 4.679 | 0.02124 | 0.75896
BDB | Bundamba | Bundamba Bulk Supply | BDB11kVB6_Term | 11 | 9.1184 | 173.7296 | 3.3638 | 21.3627 | 2.0617 | 8.0306 | 51.0015 | 7.8947 | 50.1382 | 0.02157 | 0.76608 | 0.47025 | 4.679 | 0.02162 | 0.76625
BDL | Bundall | Molendinar Bulk Supply | BDL33kVB1_Term | 33 | 4.0439 | 231.1421 | 1.2997 | 24.7625 | 0.77352 | 3.4709 | 66.1295 | 3.5728 | 68.0707 | 1.4922 | 4.966 | 5.6832 | 37.6835 | 1.4919 | 4.9703
BDL | Bundall | Molendinar Bulk Supply | BDL33kVB2_Term | 33 | 7.6813 | 439.0452 | 2.0695 | 39.4294 | 1.1945 | 6.5724 | 125.2217 | 6.7748 | 129.0782 | 0.75069 | 2.6247 | 2.4413 | 24.8872 | 0.75036 | 2.6289
BDL | Bundall | Molendinar Bulk Supply | BDL11kVB1_Term | 11 | 8.0897 | 154.13 | 1.8543 | 11.7767 | 1.0465 | 6.9555 | 44.1732 | 7.0912 | 45.0349 | 0.12163 | 0.85543 | 0.0468 | 9.5931 | 0.12159 | 0.8559
BDL | Bundall | Molendinar Bulk Supply | BDL11kVB2_Term | 11 | 8.0897 | 154.13 | 1.8543 | 11.7767 | 1.0465 | 6.9555 | 44.1732 | 7.0912 | 45.0349 | 0.12163 | 0.85543 | 0.0468 | 9.5931 | 0.12159 | 0.8559
BDS | Beaudesert Bulk | Beaudesert Bulk Supply | 43080 BEAUDS1D | 110 | 4.4568 | 849.1428 | 5.8764 | 373.202 | 8.5798 | 5.5516 | 352.5751 | 5.9838 | 380.0232 | 3.776 | 15.2251 | 0.14844 | 4.4341 | 3.7497 | 15.1971
BDS | Beaudesert Bulk | Beaudesert Bulk Supply | BDS33kVB1_Term | 33 | 10.2177 | 584.0223 | 2.9115 | 55.471 | 1.6902 | 8.7856 | 167.3887 | 9.0314 | 172.0711 | 0.33915 | 2.0243 | 0.17185 | 17.5541 | 0.33522 | 2.0149
BDT | Beaudesert | Beaudesert Bulk Supply | BDT33kVB1_Term | 33 | 7.7125 | 440.8279 | 2.4691 | 47.0418 | 1.4622 | 6.5907 | 125.5704 | 6.8678 | 130.8498 | 0.65471 | 2.6393 | 0.76551 | 20.1287 | 0.65078 | 2.6298
BDT | Beaudesert | Beaudesert Bulk Supply | BDT11kVB1_Term | 11 | 5.2979 | 100.9381 | 0.97088 | 6.1659 | 0.53403 | 4.5774 | 29.0705 | 4.6178 | 29.3272 | 0.10616 | 1.3153 | 0.0333 | 18.9704 | 0.10572 | 1.3142
BGY | Burpengary | Hays Inlet Bulk Supply | BGY33kVB1_Term | 33 | 8.1812 | 467.6172 | 1.2879 | 24.5385 | 0.69754 | 7.2047 | 137.2681 | 6.9151 | 131.7502 | 0.65405 | 2.4774 | 28.3598 | 33.799 | 0.6582 | 2.5012
BGY | Burpengary | Hays Inlet Bulk Supply | BGY11kVB1_Term | 11 | 8.7591 | 166.8841 | 1.8917 | 12.0137 | 1.0617 | 7.5355 | 47.8571 | 7.648 | 48.5716 | 0.08954 | 0.79269 | 0.01687 | 9.4916 | 0.09 | 0.79534
BGY | Burpengary | Hays Inlet Bulk Supply | BGY11kVB2_Term | 11 | 8.7591 | 166.8841 | 1.8917 | 12.0137 | 1.0617 | 7.5355 | 47.8571 | 7.648 | 48.5716 | 0.08954 | 0.79269 | 0.01687 | 9.4916 | 0.09 | 0.79534
BHD | Burleigh Heads Bulk | Burleigh Head Bulk Supply | 43140 BURLEE1D | 110 | 13.7177 | 2613.575 | 14.1189 | 896.673 | 14.5419 | 14.1223 | 896.8863 | 13.731 | 872.0384 | 0.62406 | 5.0569 | 0.79516 | 4.596 | 0.62287 | 5.0575
BHD | Burleigh Heads Bulk | Burleigh Head Bulk Supply | 43141 BURLEE2D | 110 | 13.7177 | 2613.575 | 14.1201 | 896.7449 | 14.5443 | 14.1228 | 896.9203 | 13.7318 | 872.0842 | 0.62406 | 5.0569 | 0.79484 | 4.5948 | 0.62287 | 5.0575
BHD | Burleigh Heads Bulk | Burleigh Head Bulk Supply | BHD33kVB1_Term | 33 | 15.888 | 908.1192 | 1.1692 | 22.2754 | 0.5846 | 14.0514 | 267.7148 | 13.4669 | 256.5786 | 0.08907 | 1.3168 | 53.5624 | -5.259 | 0.08897 | 1.3168
BHD | Burleigh Heads | Mudgeeraba Bulk Supply | BHD11kVB1_Term | 11 | 9.5278 | 181.5285 | 1.9258 | 12.2304 | 1.0709 | 8.306 | 52.75 | 8.2311 | 52.2745 | 0.02006 | 0.73332 | 0.94253 | 9.3772 | 0.02005 | 0.73333
BHD | Burleigh Heads | Mudgeeraba Bulk Supply | BHD11kVB3_Term | 11 | 9.5278 | 181.5285 | 1.9258 | 12.2304 | 1.0709 | 8.306 | 52.75 | 8.2311 | 52.2745 | 0.02006 | 0.73332 | 0.94253 | 9.3772 | 0.02005 | 0.73333
BHD | Burleigh Heads | Mudgeeraba Bulk Supply | BHD11kVB2_Term | 11 | 9.593 | 182.7704 | 1.9276 | 12.2416 | 1.0712 | 8.3621 | 53.1064 | 8.2877 | 52.6337 | 0.02026 | 0.72833 | 0.94253 | 9.3772 | 0.02025 | 0.72834
BHD | Burleigh Heads | Mudgeeraba Bulk Supply | BHD11kVB4_Term | 11 | 9.593 | 182.7704 | 1.9276 | 12.2416 | 1.0712 | 8.3621 | 53.1064 | 8.2877 | 52.6337 | 0.02026 | 0.72833 | 0.94253 | 9.3772 | 0.02025 | 0.72834
BHD | Burleigh Heads | Mudgeeraba Bulk Supply | TR6_11kV_Term | 11 | 9.614 | 183.172 | 1.9313 | 12.2657 | 1.0732 | 8.3806 | 53.2242 | 8.3057 | 52.7482 | 0.01995 | 0.72674 | 0.94074 | 9.3592 | 0.01994 | 0.72675
BHD | Burleigh Heads | Mudgeeraba Bulk Supply | TR2_11kV_Term | 11 | 9.5486 | 181.9246 | 1.9296 | 12.2545 | 1.073 | 8.3243 | 52.8662 | 8.2489 | 52.3874 | 0.01975 | 0.73173 | 0.94074 | 9.3592 | 0.01974 | 0.73174
BHL | Bald Hills | Brendale Bulk Supply | BHL33kVB2_Term | 33 | 11.4746 | 655.8584 | 1.9624 | 37.3885 | 1.0749 | 9.9122 | 188.8521 | 9.9579 | 189.7228 | 0.18738 | 1.8172 | 1.6546 | 28.3411 | 0.18718 | 1.8236
BHL | Bald Hills | Brendale Bulk Supply | BHL33kVB3_Term | 33 | 8.2372 | 470.8223 | 2.2035 | 41.9819 | 1.2711 | 7.0469 | 134.2625 | 7.2599 | 138.3198 | 0.67714 | 2.4531 | 2.1186 | 23.4155 | 0.67626 | 2.4594
BHL | Bald Hills | Brendale Bulk Supply | BHL11kVB1_Term | 11 | 5.1468 | 98.06 | 0.96142 | 6.1058 | 0.53026 | 4.4451 | 28.2304 | 4.4828 | 28.4699 | 0.10629 | 1.3535 | 0.08547 | 19.094 | 0.10627 | 1.3542
BHL | Bald Hills | Brendale Bulk Supply | BHL11kVB2_Term | 11 | 5.4548 | 103.9275 | 0.97458 | 6.1894 | 0.5351 | 4.7095 | 29.9094 | 4.751 | 30.1731 | 0.10506 | 1.2767 | 0.02982 | 18.9539 | 0.10496 | 1.2774
BHT | Bowen Hills Tunnel | Victoria Park Bulk Supply | BHT22kVB1_Term | 22 | 5.1159 | 194.9417 | 0.11003 | 1.3976 | 0.05505 | 4.4567 | 56.6076 | 4.4017 | 55.9086 | 0.03298 | 2.7324 | 381 | 2.1206 | 0.0332 | 2.734
BIS | Bribie Island | Caboolture Bulk Supply | BIS33kVB1_Term | 33 | 4.1629 | 237.9416 | 1.5695 | 29.9036 | 0.96327 | 3.5853 | 68.3093 | 3.7017 | 70.5261 | 1.414 | 4.8328 | 4.3902 | 29.7625 | 1.38 | 4.8216
BIS | Bribie Island | Caboolture Bulk Supply | BIS11kVB1_Term | 11 | 6.6774 | 127.2216 | 1.8145 | 11.5236 | 1.0412 | 5.7554 | 36.552 | 5.9182 | 37.586 | 0.18216 | 1.0304 | 0.02947 | 9.4957 | 0.1743 | 1.0198
BIS | Bribie Island | Caboolture Bulk Supply | BIS11kVB2_Term | 11 | 6.6774 | 127.2216 | 1.8145 | 11.5236 | 1.0412 | 5.7554 | 36.552 | 5.9182 | 37.586 | 0.18216 | 1.0304 | 0.02947 | 9.4957 | 0.1743 | 1.0198
BIS | Bribie Island | Caboolture Bulk Supply | BISBESS11kVB1_Term | 11 | 6.6774 | 127.2216 | 1.8145 | 11.5236 | 1.0412 | 5.7554 | 36.552 | 5.9182 | 37.586 | 0.18216 | 1.0304 | 0.02947 | 9.4957 | 0.1743 | 1.0198
BKD | Birkdale | Cleveland Bulk Supply | BKD33kVB1_Term | 33 | 8.3114 | 475.0608 | 1.7154 | 32.6837 | 0.95819 | 7.1051 | 135.3696 | 7.2775 | 138.6556 | 0.59448 | 2.452 | 1.5446 | 31.6502 | 0.59706 | 2.468
BKD | Birkdale | Cleveland Bulk Supply | BKD11kVB1_Term | 11 | 9.0768 | 172.9367 | 1.898 | 12.0542 | 1.07 | 7.7593 | 49.2782 | 7.8627 | 49.935 | 0.08169 | 0.76573 | 0.01794 | 9.5008 | 0.08056 | 0.77991
BKD | Birkdale | Cleveland Bulk Supply | BKD11kVB2_Term | 11 | 9.0768 | 172.9367 | 1.898 | 12.0542 | 1.07 | 7.7593 | 49.2782 | 7.8627 | 49.935 | 0.08169 | 0.76573 | 0.01794 | 9.5008 | 0.08056 | 0.77991
BLB | Bulimba | Doboy Bulk Supply | BLB33kVB1_Term | 33 | 14.9775 | 856.0779 | 2.8854 | 54.974 | 1.5997 | 12.894 | 245.6639 | 13.0413 | 248.4693 | 0.24232 | 1.3789 | 1.4677 | 18.9501 | 0.24215 | 1.3852
BLB | Bulimba | Doboy Bulk Supply | BLB11kVB1_Term | 11 | 10.4427 | 198.9595 | 1.9369 | 12.3013 | 1.0679 | 9.022 | 57.2976 | 9.0874 | 57.7129 | 0.04376 | 0.6679 | 0.01676 | 9.4887 | 0.04374 | 0.66861
BLB | Bulimba | Doboy Bulk Supply | BLB11kVB2_Term | 11 | 10.4427 | 198.9595 | 1.9369 | 12.3013 | 1.0679 | 9.022 | 57.2976 | 9.0874 | 57.7129 | 0.04376 | 0.6679 | 0.01676 | 9.4887 | 0.04374 | 0.66861
BLH | Beenleigh Bulk | Beenleigh Bulk Supply (Including Bay Islands) | 41080 BEENLH1D | 110 | 18.4099 | 3507.5608 | 21.2177 | 1347.5046 | 25.2689 | 20.1443 | 1279.334 | 20.4862 | 1301.0478 | 0.65371 | 3.7432 | 0.31551 | 2.2401 | 0.65489 | 3.7736
BLH | Beenleigh Bulk | Beenleigh Bulk Supply (Including Bay Islands) | BLH33kVB1_Term | 33 | 22.0875 | 1262.4689 | 3.2724 | 62.3479 | 1.769 | 19.0572 | 363.0894 | 19.1961 | 365.7341 | 0.07906 | 0.94924 | 0.02899 | 17.3858 | 0.07864 | 0.95153
BLH | Beenleigh | Beenleigh Bulk Supply (Including Bay Islands) | BLH11kVB3_Term | 11 | 11.9292 | 227.2816 | 1.9724 | 12.5267 | 1.0794 | 10.2864 | 65.3274 | 10.3287 | 65.5963 | 0.02617 | 0.5872 | 0.02701 | 9.4855 | 0.02567 | 0.59165
BLH | Beenleigh | Beenleigh Bulk Supply (Including Bay Islands) | BLH11kVB4_Term | 11 | 11.9292 | 227.2816 | 1.9724 | 12.5267 | 1.0794 | 10.2864 | 65.3274 | 10.3287 | 65.5963 | 0.02617 | 0.5872 | 0.02701 | 9.4855 | 0.02567 | 0.59165
BLN | Beenleigh North | Beenleigh Bulk Supply (Including Bay Islands) | BLN33kVB1_Term | 33 | 11.7074 | 669.1694 | 2.6016 | 49.5675 | 1.4605 | 10.0538 | 191.5501 | 10.2853 | 195.961 | 0.38661 | 1.7614 | 0.99494 | 20.7591 | 0.38323 | 1.7602
BLN | Beenleigh North | Beenleigh Bulk Supply (Including Bay Islands) | BLN11kVB1_Term | 11 | 10.0303 | 191.1024 | 1.9693 | 12.5065 | 1.0859 | 8.7007 | 55.2569 | 8.783 | 55.7797 | 0.0596 | 0.71268 | 0.01793 | 9.5081 | 0.05715 | 0.7063
BLN | Beenleigh North | Beenleigh Bulk Supply (Including Bay Islands) | BLN11kVB2_Term | 11 | 10.0303 | 191.1024 | 1.9693 | 12.5065 | 1.0859 | 8.7007 | 55.2569 | 8.783 | 55.7797 | 0.0596 | 0.71268 | 0.01793 | 9.5081 | 0.05715 | 0.7063
BLN | Beenleigh North | Beenleigh Bulk Supply (Including Bay Islands) | BLNBESS11kVB1_Term | 11 | 10.0303 | 191.1024 | 1.9693 | 12.5065 | 1.0859 | 8.7007 | 55.2569 | 8.783 | 55.7797 | 0.0596 | 0.71268 | 0.01793 | 9.5081 | 0.05715 | 0.7063
BMT | Black Mountain | Sunrise Hills Bulk Supply | BMT33kVB1_Term | 33 | 1.7805 | 101.7671 | 0.77894 | 14.8408 | 0.49052 | 1.4671 | 27.9526 | 1.6501 | 31.4388 | 6.5606 | 9.7755 | 9.7174 | 57.8796 | 6.5579 | 9.7775
BMT | Black Mountain | Sunrise Hills Bulk Supply | BMT11kVB1_Term | 11 | 2.5204 | 48.021 | 0.84446 | 5.3631 | 0.50383 | 2.126 | 13.502 | 2.2662 | 14.3922 | 0.84576 | 2.64 | 0.1225 | 19.4753 | 0.84546 | 2.6402
BMT | Black Mountain | Sunrise Hills Bulk Supply | BMT11kVB2_Term | 11 | 2.5202 | 48.017 | 0.84444 | 5.3629 | 0.50382 | 2.1258 | 13.5009 | 2.266 | 14.391 | 0.84594 | 2.6402 | 0.12368 | 19.4754 | 0.84564 | 2.6404
BMT | Black Mountain | Sunrise Hills Bulk Supply | BMT11kVB3_Term | 11 | 2.5201 | 48.0149 | 0.84443 | 5.3629 | 0.50382 | 2.1258 | 13.5003 | 2.2659 | 14.3904 | 0.84602 | 2.6403 | 0.12426 | 19.4754 | 0.84573 | 2.6405
BNH | Boonah | Raceview Bulk Supply | BNH33kVB1_Term | 33 | 2.0173 | 115.3067 | 0.75132 | 14.3146 | 0.45877 | 1.7019 | 32.4246 | 1.8198 | 34.6726 | 4.2443 | 9.4861 | 8.6895 | 62.9548 | 4.2446 | 9.4892
BNH | Boonah | Raceview Bulk Supply | BNH11kVB1_Term | 11 | 2.5608 | 48.7888 | 3.0029 | 19.0707 | 3.624 | 2.7557 | 17.5012 | 2.9678 | 18.8482 | 0.58256 | 2.6661 | 0.11098 | 1.5315 | 0.58261 | 2.6664
BNH | Boonah | Raceview Bulk Supply | BNH11kVB2_Term | 11 | 3.3209 | 63.2719 | 0.91003 | 5.7794 | 0.52531 | 2.8259 | 17.9471 | 2.9482 | 18.7239 | 0.52411 | 2.038 | 0.05252 | 18.9348 | 0.52415 | 2.0383
BPN | Browns Plains Bulk | Browns Plains Bulk Supply | 43130 BROWNS1D | 110 | 10.5409 | 2008.3185 | 10.9271 | 693.9654 | 11.3805 | 10.3721 | 658.7141 | 11.1063 | 705.3456 | 1.6696 | 6.4194 | 0.79893 | 5.8737 | 1.6746 | 6.4501
BPN | Browns Plains Bulk | Browns Plains Bulk Supply | 43131 BROWNS2D | 110 | 10.5503 | 2010.1123 | 11.2622 | 715.2481 | 12.1185 | 10.5258 | 668.4799 | 11.3621 | 721.5906 | 1.6666 | 6.4141 | 0.64104 | 5.3339 | 1.6722 | 6.4462
BPN | Browns Plains Bulk | Browns Plains Bulk Supply | BPN33kVB1_Term | 33 | 17.1457 | 980.0088 | 2.2224 | 42.3429 | 1.1928 | 14.7466 | 280.9607 | 14.8612 | 283.1439 | 0.12211 | 1.2172 | 0.02553 | 25.8684 | 0.12256 | 1.2268
BPN | Browns Plains | Browns Plains Bulk Supply | BPN11kVB1_Term | 11 | 6.2689 | 119.4393 | 0.99132 | 6.2957 | 0.53844 | 5.4201 | 34.4224 | 5.4463 | 34.5885 | 0.05851 | 1.1138 | 0.04494 | 18.9296 | 0.05856 | 1.1148
BPN | Browns Plains | Browns Plains Bulk Supply | BPN11kVB2_Term | 11 | 10.8671 | 207.0458 | 1.9477 | 12.3697 | 1.0706 | 9.3928 | 59.6523 | 9.4448 | 59.9827 | 0.03374 | 0.6425 | 0.02 | 9.4826 | 0.03379 | 0.64356
BPN | Browns Plains | Browns Plains Bulk Supply | BPN11kVB3_Term | 11 | 10.8671 | 207.0458 | 1.9477 | 12.3697 | 1.0706 | 9.3928 | 59.6523 | 9.4448 | 59.9827 | 0.03374 | 0.6425 | 0.02 | 9.4826 | 0.03379 | 0.64356
BRD | Brendale Bulk | Brendale Bulk Supply | 43120 BRENDL1D | 110 | 25.1922 | 4799.7584 | 32.1425 | 2041.3234 | 45.0266 | 31.521 | 2001.8542 | 31.1147 | 1976.0481 | 0.19455 | 2.7668 | 0.0957 | 0.94123 | 0.19355 | 2.7957
BRD | Brendale Bulk | Brendale Bulk Supply | 43121 BRENDL2D | 110 | 25.1922 | 4799.7589 | 32.1426 | 2041.3281 | 45.0268 | 31.5211 | 2001.8588 | 31.1148 | 1976.0568 | 0.19455 | 2.7668 | 0.0957 | 0.94121 | 0.19355 | 2.7957
BRD | Brendale Bulk | Brendale Bulk Supply | 43122 BRENDL3D | 110 | 25.1922 | 4799.7568 | 32.144 | 2041.4174 | 45.0324 | 31.5225 | 2001.9451 | 31.1175 | 1976.2235 | 0.19455 | 2.7668 | 0.09558 | 0.94093 | 0.19355 | 2.7957
BRD | Brendale Bulk | Brendale Bulk Supply | BRD33kVB1_Term | 33 | 24.4215 | 1395.8746 | 3.3611 | 64.0384 | 1.8117 | 21.0556 | 401.1626 | 21.1327 | 402.6318 | 0.0389 | 0.85748 | 0.00486 | 16.9886 | 0.03802 | 0.86378
BRD | Brendale | Brendale Bulk Supply | BRD11kVB1_Term | 11 | 11.465 | 218.438 | 1.9578 | 12.4334 | 1.0709 | 9.9215 | 63.0098 | 9.9544 | 63.2188 | 0.02053 | 0.60911 | 0.01626 | 9.4883 | 0.02043 | 0.60981
BRD | Brendale | Brendale Bulk Supply | BRD11kVB2_Term | 11 | 11.465 | 218.438 | 1.9578 | 12.4334 | 1.0709 | 9.9215 | 63.0098 | 9.9544 | 63.2188 | 0.02053 | 0.60911 | 0.01626 | 9.4883 | 0.02043 | 0.60981
BRT | Brighton | Sandgate Bulk Supply | BRT33kVB1_Term | 33 | 7.9912 | 456.7584 | 1.7027 | 32.4404 | 0.95321 | 6.8507 | 130.5233 | 7.0019 | 133.4032 | 0.5508 | 2.5647 | 1.4232 | 31.7101 | 0.55125 | 2.573
BRT | Brighton | Sandgate Bulk Supply | BRT33kVB2_Term | 33 | 6.6022 | 377.369 | 1.6363 | 31.1766 | 0.92892 | 5.575 | 106.2188 | 5.8793 | 112.0149 | 1.3164 | 2.8893 | 2.4619 | 32.3047 | 1.3181 | 2.898
BRT | Brighton | Sandgate Bulk Supply | BRT11kVB1_Term | 11 | 9.5309 | 181.5878 | 1.9089 | 12.1235 | 1.0637 | 8.1875 | 51.9979 | 8.3048 | 52.7428 | 0.08675 | 0.72799 | 0.02874 | 9.5186 | 0.08687 | 0.73259
BRT | Brighton | Sandgate Bulk Supply | BRT11kVB2_Term | 11 | 9.5309 | 181.5878 | 1.9089 | 12.1235 | 1.0637 | 8.1875 | 51.9979 | 8.3048 | 52.7428 | 0.08675 | 0.72799 | 0.02874 | 9.5186 | 0.08687 | 0.73259
BTA | Bethania | Beenleigh Bulk Supply (Including Bay Islands) | BTA33kVB1_Term | 33 | 6.6743 | 381.4885 | 1.9561 | 37.268 | 1.1431 | 5.7133 | 108.8531 | 5.9052 | 112.51 | 0.85281 | 3.046 | 2.41 | 26.0261 | 0.84944 | 3.0449
BTA | Bethania | Beenleigh Bulk Supply (Including Bay Islands) | BTA11kVB1_Term | 11 | 8.1488 | 155.2551 | 1.884 | 11.965 | 1.064 | 7.0108 | 44.5249 | 7.1441 | 45.3708 | 0.11552 | 0.85584 | 0.02074 | 9.4915 | 0.11514 | 0.85571
BTA | Bethania | Beenleigh Bulk Supply (Including Bay Islands) | BTA11kVB2_Term | 11 | 8.1488 | 155.2551 | 1.884 | 11.965 | 1.064 | 7.0108 | 44.5249 | 7.1441 | 45.3708 | 0.11552 | 0.85584 | 0.02074 | 9.4915 | 0.11514 | 0.85571
BTN | Bromelton | Beaudesert Bulk Supply | BTN33kVB1_Term | 33 | 7.2101 | 412.1119 | 2.4831 | 47.3091 | 1.4874 | 6.197 | 118.0678 | 6.4352 | 122.6063 | 0.59938 | 2.846 | 0.58811 | 19.6075 | 0.58273 | 2.82
BTN | Bromelton | Beaudesert Bulk Supply | BTN11kVB1_Term | 11 | 8.2752 | 157.6641 | 1.8764 | 11.9168 | 1.0554 | 7.1456 | 45.3808 | 7.2509 | 46.0492 | 0.09195 | 0.83967 | 0.02535 | 9.4973 | 0.0901 | 0.83679
BTY | Birtinya | Palmwood Bulk Supply | 43050 BIRTYA1D | 132 | 8.1597 | 1865.5669 | 8.8478 | 674.2958 | 9.7399 | 8.4768 | 646.0184 | 8.6606 | 660.0283 | 2.1759 | 10.0426 | 1.3381 | 7.6907 | 2.1621 | 10.1236
BTY | Birtinya | Palmwood Bulk Supply | BTY11kVB1_Term | 11 | 11.0102 | 209.7724 | 1.96 | 12.4478 | 1.0936 | 9.4357 | 59.9245 | 9.3839 | 59.5958 | 0.0369 | 0.63352 | 0.94051 | 9.358 | 0.03341 | 0.65327
BTY | Birtinya | Palmwood Bulk Supply | BTY11kVB2_Term | 11 | 10.9992 | 209.5634 | 1.9598 | 12.4463 | 1.0936 | 9.4263 | 59.8652 | 9.3745 | 59.5363 | 0.03693 | 0.63416 | 0.94051 | 9.358 | 0.03342 | 0.65393
BVL | Boovall | Raceview Bulk Supply | BVL33kVB1_Term | 33 | 13.833 | 790.6636 | 2.0195 | 38.4764 | 1.0903 | 11.9207 | 227.1207 | 12.0332 | 229.2639 | 0.19432 | 1.503 | 0.62912 | 28.117 | 0.19489 | 1.5069
BVL | Boovall | Raceview Bulk Supply | BVL11kVB1_Term | 11 | 13.0821 | 249.2482 | 2.4357 | 15.4688 | 1.2931 | 11.8395 | 75.1911 | 10.7734 | 68.4201 | 0.04195 | 0.53253 | 7.0217 | 3.7896 | 0.04188 | 0.53532
BVL | Boovall | Raceview Bulk Supply | BVL11kVB2_Term | 11 | 13.0821 | 249.2482 | 2.4357 | 15.4688 | 1.2931 | 11.8395 | 75.1911 | 10.7734 | 68.4201 | 0.04195 | 0.53253 | 7.0217 | 3.7896 | 0.04188 | 0.53532
BWH | Beewah Bulk | Beerwah Bulk Supply | 43110 BEERWH1D | 110 | 7.1494 | 1362.1371 | 7.9285 | 503.5297 | 8.9567 | 7.4069 | 470.4014 | 7.8499 | 498.5385 | 1.8547 | 9.5957 | 0.57539 | 6.8299 | 1.8485 | 9.6644
BWH | Beewah Bulk | Beerwah Bulk Supply | 43111 BEERWH2D | 110 | 7.1485 | 1361.9721 | 7.1279 | 452.68 | 7.1523 | 7.0086 | 445.1082 | 7.264 | 461.3262 | 1.8537 | 9.5971 | 1.2413 | 9.7272 | 1.8477 | 9.6657
BWH | Beewah Bulk | Beerwah Bulk Supply | BWH33kVB2_Term | 33 | 13.3231 | 761.5185 | 2.1936 | 41.793 | 1.2007 | 11.4422 | 218.004 | 11.5612 | 220.2706 | 0.16728 | 1.5644 | 0.03564 | 25.5219 | 0.16464 | 1.5795
BWH | Beerwah | Beerwah Bulk Supply | BWH11kVB1_Term | 11 | 10.1195 | 192.8028 | 1.9282 | 12.2458 | 1.0669 | 8.7447 | 55.536 | 8.795 | 55.856 | 0.03547 | 0.68956 | 0.01687 | 9.4899 | 0.03517 | 0.69123
BWH | Beerwah | Beerwah Bulk Supply | BWH11kVB2_Term | 11 | 10.1195 | 192.8028 | 1.9282 | 12.2458 | 1.0669 | 8.7447 | 55.536 | 8.795 | 55.856 | 0.03547 | 0.68956 | 0.01687 | 9.4899 | 0.03517 | 0.69123
BWI | Bulwer Island | Myrtletown Bulk Supply | BWI33kVB2_Term | 33 | 16.5017 | 943.1961 | 2.2533 | 42.9309 | 1.2101 | 14.2451 | 271.4063 | 14.3376 | 273.1683 | 0.10972 | 1.2656 | 0.12987 | 25.373 | 0.10626 | 1.2681
BWI | Bulwer Island | Myrtletown Bulk Supply | BWI11kVB1_Term | 11 | 10.5219 | 200.4697 | 2.261 | 14.3595 | 1.1549 | 9.6823 | 61.4912 | 8.5391 | 54.2308 | 0.03419 | 0.6632 | 9.022 | 0.49645 | 0.03381 | 0.66348
CBT | Caboolture Bulk | Caboolture Bulk Supply | 40110 CABLTR1D | 110 | 9.4217 | 1795.0846 | 10.9986 | 698.5084 | 13.3843 | 10.121 | 642.7686 | 10.9284 | 694.0497 | 1.4751 | 7.268 | 0.20677 | 4.1651 | 1.4777 | 7.3618
CBT | Caboolture Bulk | Caboolture Bulk Supply | CBT33kVB1_Term | 33 | 17.1283 | 979.0158 | 3.1762 | 60.5148 | 1.7674 | 14.625 | 278.6443 | 14.8268 | 282.4888 | 0.15032 | 1.2146 | 0.01502 | 17.344 | 0.14878 | 1.238
CBT | Caboolture | Caboolture Bulk Supply | CBT11kVB1_Term | 11 | 11.6428 | 221.8249 | 1.9593 | 12.4432 | 1.0832 | 9.952 | 63.2039 | 10.015 | 63.6039 | 0.04703 | 0.59829 | 0.01676 | 9.4866 | 0.03802 | 0.6132
CBT | Caboolture | Caboolture Bulk Supply | CBT11kVB2_Term | 11 | 11.6428 | 221.8249 | 1.9593 | 12.4432 | 1.0832 | 9.952 | 63.2039 | 10.015 | 63.6039 | 0.04703 | 0.59829 | 0.01676 | 9.4866 | 0.03802 | 0.6132
CBW | Caboolture West | Caboolture Bulk Supply | CBW33kVB1_Term | 33 | 11.9484 | 682.9448 | 2.7301 | 52.0148 | 1.5542 | 10.1735 | 193.8311 | 10.4071 | 198.2825 | 0.33839 | 1.7214 | 0.65663 | 19.5219 | 0.34036 | 1.7524
CBW | Caboolture West | Caboolture Bulk Supply | CBW11kVB1_Term | 11 | 10.462 | 199.3278 | 1.9259 | 12.2311 | 1.0781 | 8.9045 | 56.5514 | 8.9822 | 57.0443 | 0.0516 | 0.66587 | 0.02122 | 9.5311 | 0.05298 | 0.68647
CBW | Caboolture West | Caboolture Bulk Supply | CBW11kVB2_Term | 11 | 10.462 | 199.3278 | 1.9259 | 12.2311 | 1.0781 | 8.9045 | 56.5514 | 8.9822 | 57.0443 | 0.0516 | 0.66587 | 0.02122 | 9.5311 | 0.05298 | 0.68647
CCY | Cades County | Molendinar Bulk Supply | 40810 CADCTY1D | 110 | 15.4644 | 2946.3712 | 15.8988 | 1009.7085 | 16.3996 | 15.9306 | 1011.7285 | 15.4524 | 981.3569 | 0.80061 | 4.4491 | 0.94682 | 4.0319 | 0.80143 | 4.4616
CCY | Cades County | Molendinar Bulk Supply | CCY11kVB1_Term | 11 | 8.9263 | 170.0696 | 3.3469 | 21.2559 | 2.059 | 7.8638 | 49.9416 | 7.7319 | 49.1043 | 0.0236 | 0.78281 | 0.47025 | 4.679 | 0.02361 | 0.78293
CCY | Cades County | Molendinar Bulk Supply | CCY11kVB2_Term | 11 | 8.9263 | 170.0696 | 3.3469 | 21.2559 | 2.059 | 7.8638 | 49.9416 | 7.7319 | 49.1043 | 0.0236 | 0.78281 | 0.47025 | 4.679 | 0.02361 | 0.78293
CCY | Cades County | Molendinar Bulk Supply | CCY11kVB3_Term | 11 | 9.0325 | 172.0917 | 3.3568 | 21.3185 | 2.0608 | 7.9551 | 50.5219 | 7.823 | 49.6828 | 0.02332 | 0.77361 | 0.47025 | 4.679 | 0.02332 | 0.77374
CCY | Cades County | Molendinar Bulk Supply | CCY11kVB4_Term | 11 | 9.0325 | 172.0917 | 3.3568 | 21.3185 | 2.0608 | 7.9551 | 50.5219 | 7.823 | 49.6828 | 0.02332 | 0.77361 | 0.47025 | 4.679 | 0.02332 | 0.77374
CDC | Coondoo Creek | Coondoo Creek Bulk Supply | CDC-X219022_Term | 33 | 2.6807 | 153.2229 | 0.96296 | 18.3468 | 0.58312 | 2.2626 | 43.1076 | 2.4149 | 46.01 | 3.0187 | 7.2129 | 5.4513 | 49.8566 | 3.0135 | 7.2138
CFD | Clayfield | Nudgee Bulk Supply | CFD33kVB1_Term | 33 | 12.8507 | 734.517 | 2.354 | 44.8491 | 1.2989 | 11.0797 | 211.0973 | 11.164 | 212.702 | 0.1999 | 1.6189 | 1.2861 | 23.4162 | 0.1997 | 1.6269
CFD | Clayfield | Nudgee Bulk Supply | CFD33kVB2_Term | 33 | 12.866 | 735.3932 | 2.3567 | 44.9008 | 1.3004 | 11.093 | 211.3493 | 11.1772 | 212.9543 | 0.19949 | 1.617 | 1.2834 | 23.3894 | 0.19928 | 1.625
CFD | Clayfield | Nudgee Bulk Supply | CFD11kVB1_Term | 11 | 10.2943 | 196.1327 | 1.9285 | 12.2479 | 1.0646 | 8.8993 | 56.5179 | 8.9514 | 56.8491 | 0.03593 | 0.67782 | 0.01921 | 9.5126 | 0.03591 | 0.67871
CFD | Clayfield | Nudgee Bulk Supply | CFD11kVB2_Term | 11 | 10.2943 | 196.1327 | 1.9285 | 12.2479 | 1.0646 | 8.8993 | 56.5179 | 8.9514 | 56.8491 | 0.03593 | 0.67782 | 0.01921 | 9.5126 | 0.03591 | 0.67871
CHL | Camp Hill | Coorparoo Bulk Supply | CHL33kVB1_Term | 33 | 14.9536 | 854.7151 | 2.1918 | 41.7596 | 1.1841 | 12.9115 | 245.9977 | 12.983 | 247.359 | 0.11439 | 1.3976 | 0.51045 | 25.893 | 0.11487 | 1.4013
CHL | Camp Hill | Coorparoo Bulk Supply | CHL11kVB1_Term | 11 | 6.1279 | 116.753 | 0.98637 | 6.2643 | 0.53641 | 5.3009 | 33.6651 | 5.3247 | 33.8165 | 0.05226 | 1.1394 | 0 | 18.9796 | 0.05231 | 1.1399
CHL | Camp Hill | Coorparoo Bulk Supply | CHL11kVB2_Term | 11 | 6.0946 | 116.1183 | 0.98585 | 6.261 | 0.53636 | 5.2726 | 33.4853 | 5.2954 | 33.6305 | 0.05281 | 1.1457 | 0.0401 | 18.9781 | 0.05286 | 1.1461
CLD | Caloundra | Palmwood Bulk Supply | 43180 CLNDRA1D | 132 | 7.8396 | 1792.371 | 8.2897 | 631.7622 | 8.8529 | 8.0506 | 613.5402 | 8.1367 | 620.1003 | 2.2221 | 10.4618 | 1.6583 | 8.7312 | 2.205 | 10.5339
CLD | Caloundra | Palmwood Bulk Supply | CLD11kVB1_Term | 11 | 9.2245 | 175.7511 | 1.9199 | 12.1931 | 1.0716 | 8.0362 | 51.037 | 7.9719 | 50.6283 | 0.02856 | 0.75692 | 0.9405 | 9.358 | 0.02844 | 0.75742
CLD | Caloundra | Palmwood Bulk Supply | CLD11kVB2_Term | 11 | 9.1705 | 174.7219 | 1.9183 | 12.1831 | 1.0714 | 7.9896 | 50.7405 | 7.9253 | 50.3322 | 0.02874 | 0.76137 | 0.9405 | 9.358 | 0.02862 | 0.76187
CLD | Caloundra | Palmwood Bulk Supply | CLD11kVB3_Term | 11 | 9.2245 | 175.7511 | 1.9199 | 12.1931 | 1.0716 | 8.0362 | 51.037 | 7.9719 | 50.6283 | 0.02856 | 0.75692 | 0.9405 | 9.358 | 0.02844 | 0.75742
CLD | Caloundra | Palmwood Bulk Supply | CLD11kVB4_Term | 11 | 9.1705 | 174.7219 | 1.9183 | 12.1831 | 1.0714 | 7.9896 | 50.7405 | 7.9253 | 50.3322 | 0.02874 | 0.76137 | 0.9405 | 9.358 | 0.02862 | 0.76187
CLM | Coolum | Nambour Bulk Supply | CLM33kVB1_Term | 33 | 2.8745 | 164.3014 | 1.0037 | 19.1226 | 0.60589 | 2.4468 | 46.6171 | 2.567 | 48.9082 | 2.2978 | 6.9206 | 5.0087 | 48.0699 | 2.2951 | 6.9226
CLM | Coolum | Nambour Bulk Supply | CLM33kVB3_Term | 33 | 2.6559 | 151.807 | 0.9044 | 17.2311 | 0.54387 | 2.2666 | 43.1844 | 2.3623 | 45.0085 | 2.3467 | 7.5352 | 5.7695 | 53.655 | 2.3219 | 7.5523
CLM | Coolum | Nambour Bulk Supply | CLM11kVB1_Term | 11 | 5.2203 | 99.4601 | 2.0822 | 13.2238 | 1.1356 | 5.0606 | 32.1392 | 3.9883 | 25.3292 | 0.27398 | 1.3101 | 9.0187 | 0.51409 | 0.27368 | 1.3103
CLM | Coolum | Nambour Bulk Supply | CLM11kVB2_Term | 11 | 5.2203 | 99.4601 | 2.0822 | 13.2238 | 1.1356 | 5.0606 | 32.1392 | 3.9883 | 25.3292 | 0.27398 | 1.3101 | 9.0187 | 0.51409 | 0.27368 | 1.3103
CMA | Coomera Bulk | Coomera Bulk Supply | 43230 COOMRA1D | 110 | 13.1869 | 2512.4486 | 14.1353 | 897.7139 | 15.2777 | 13.5728 | 861.9911 | 13.8869 | 881.934 | 1.2333 | 5.1569 | 0.81315 | 4.1425 | 1.2339 | 5.1732
CMA | Coomera | Coomera Bulk Supply | CMA33kVB1_Term | 33 | 15.1015 | 863.1695 | 2.1117 | 40.2332 | 1.1355 | 13.0289 | 248.2337 | 13.1387 | 250.3265 | 0.14151 | 1.3818 | 0.06793 | 27.0331 | 0.14156 | 1.3833
CMA | Coomera | Coomera Bulk Supply | CMA11kVB2_Term | 11 | 10.2531 | 195.348 | 1.9308 | 12.2622 | 1.0658 | 8.87 | 56.3321 | 8.9187 | 56.6416 | 0.03364 | 0.68112 | 0.01794 | 9.5013 | 0.03365 | 0.68128
CMA | Coomera | Coomera Bulk Supply | CMA11kVB3_Term | 11 | 10.2531 | 195.348 | 1.9308 | 12.2622 | 1.0658 | 8.87 | 56.3321 | 8.9187 | 56.6416 | 0.03364 | 0.68112 | 0.01794 | 9.5013 | 0.03365 | 0.68128
CMD | Currimundi | Palmwood Bulk Supply | 43250 CRRMND1D | 132 | 7.9702 | 1822.2296 | 8.6284 | 657.5729 | 9.4754 | 8.2663 | 629.9755 | 8.4527 | 644.1851 | 2.2404 | 10.2786 | 1.3771 | 7.925 | 2.2255 | 10.3571
CMD | Currimundi | Palmwood Bulk Supply | CMD11kVB1_Term | 11 | 9.7702 | 186.1471 | 1.9347 | 12.2867 | 1.074 | 8.4983 | 53.9714 | 8.452 | 53.6776 | 0.03969 | 0.71405 | 0.9405 | 9.358 | 0.03959 | 0.71459
CMD | Currimundi | Palmwood Bulk Supply | CMD11kVB2_Term | 11 | 9.7337 | 185.4512 | 1.9337 | 12.2807 | 1.0738 | 8.4669 | 53.7717 | 8.4204 | 53.4766 | 0.03969 | 0.71674 | 0.9405 | 9.358 | 0.03958 | 0.71728
CMV | Calamvale | Algester Bulk Supply | CMV33kVB1_Term | 33 | 16.809 | 960.7618 | 2.2536 | 42.9374 | 1.2103 | 14.4967 | 276.2 | 14.5819 | 277.8232 | 0.13636 | 1.24 | 0.92541 | 25.4012 | 0.13585 | 1.2453
CMV | Calamvale | Algester Bulk Supply | CMV11kVB2_Term | 11 | 10.5479 | 200.9635 | 2.2626 | 14.3697 | 1.156 | 9.7031 | 61.6228 | 8.5588 | 54.356 | 0.03379 | 0.66177 | 9.0186 | 0.49779 | 0.03374 | 0.66237
CMV | Calamvale | Algester Bulk Supply | CMV11kVB3_Term | 11 | 10.5479 | 200.9635 | 2.2626 | 14.3697 | 1.156 | 9.7031 | 61.6228 | 8.5588 | 54.356 | 0.03379 | 0.66177 | 9.0186 | 0.49779 | 0.03374 | 0.66237
CMY | Coominya | Lockrose Bulk Supply | CMY33kVB1_Term | 33 | 2.8752 | 164.3386 | 1.1901 | 22.6736 | 0.74321 | 2.4101 | 45.9176 | 2.6229 | 49.9727 | 3.3813 | 6.4593 | 6.2432 | 38.3073 | 3.3774 | 6.453
CMY | Coominya | Lockrose Bulk Supply | CMY33kVB2_Term | 33 | 2.8747 | 164.3089 | 1.1899 | 22.6714 | 0.74315 | 2.4096 | 45.9091 | 2.6224 | 49.9641 | 3.3821 | 6.4604 | 6.2437 | 38.31 | 3.3782 | 6.454
CMY | Coominya | Lockrose Bulk Supply | CMY11kVB1_Term | 11 | 3.0088 | 57.3244 | 3.4316 | 21.7937 | 3.9859 | 3.1704 | 20.135 | 3.3872 | 21.5119 | 0.54138 | 2.2584 | 0.16568 | 1.4637 | 0.54094 | 2.2577
CMY | Coominya | Lockrose Bulk Supply | CMY11kVB2_Term | 11 | 2.8468 | 54.2385 | 3.2251 | 20.4819 | 3.7134 | 2.9875 | 18.9731 | 3.1824 | 20.2111 | 0.55307 | 2.3914 | 0.17728 | 1.5899 | 0.55263 | 2.3907
CNA | Cooneana | Goodna Bulk Supply | CNA33kVB1_Term | 33 | 8.8085 | 503.472 | 1.6501 | 31.4393 | 0.9121 | 7.527 | 143.4076 | 7.7057 | 146.813 | 0.57092 | 2.3106 | 1.2141 | 33.4038 | 0.57184 | 2.3272
CNA | Cooneana | Goodna Bulk Supply | CNA11kVB1_Term | 11 | 5.4132 | 103.1355 | 0.97254 | 6.1765 | 0.53456 | 4.6733 | 29.6792 | 4.7114 | 29.9212 | 0.09765 | 1.2873 | 0.03421 | 18.979 | 0.09775 | 1.2891
CNB | Cornubia | Beenleigh Bulk Supply (Including Bay Islands) | CNB33kVB1_Term | 33 | 8.0645 | 460.9473 | 2.1518 | 40.9976 | 1.2393 | 6.8951 | 131.369 | 7.1208 | 135.6685 | 0.66866 | 2.5217 | 1.5749 | 24.1412 | 0.66825 | 2.524
CNB | Cornubia | Beenleigh Bulk Supply (Including Bay Islands) | CNB11kVB1_Term | 11 | 5.3202 | 101.3628 | 0.97352 | 6.1827 | 0.53569 | 4.5941 | 29.1764 | 4.6353 | 29.4383 | 0.10756 | 1.3138 | 0.03327 | 18.9819 | 0.10752 | 1.314
CNB | Cornubia | Beenleigh Bulk Supply (Including Bay Islands) | CNB11kVB2_Term | 11 | 5.3202 | 101.3628 | 0.97352 | 6.1827 | 0.53569 | 4.5941 | 29.1764 | 4.6353 | 29.4383 | 0.10756 | 1.3138 | 0.03327 | 18.9819 | 0.10752 | 1.314
COR | Coran | Direct Transformation Substations | 43780 COORAN1D | 132 | 7.1448 | 1633.5312 | 6.5545 | 499.5241 | 6.0585 | 6.7783 | 516.5771 | 6.9943 | 533.0406 | 3.1839 | 11.2948 | 3.174 | 14.5652 | 3.1328 | 11.3232
COR | Coran | Direct Transformation Substations | COR11kVB2_Term | 11 | 7.0102 | 133.5627 | 1.8393 | 11.6808 | 1.0584 | 6.119 | 38.861 | 6.0679 | 38.5365 | 0.0493 | 0.99547 | 0.9405 | 9.358 | 0.04895 | 0.99567
CPB | Capalaba | Cleveland Bulk Supply | CPB33kVB1_Term | 33 | 9.5845 | 547.8253 | 1.8009 | 34.311 | 0.99438 | 8.2129 | 156.476 | 8.3869 | 159.792 | 0.4862 | 2.1332 | 1.2496 | 30.5876 | 0.48645 | 2.1415
CPB | Capalaba | Cleveland Bulk Supply | CPB11kVB1_Term | 11 | 8.8042 | 167.7424 | 1.886 | 11.9775 | 1.0563 | 7.5878 | 48.1891 | 7.6892 | 48.833 | 0.08215 | 0.78967 | 0.03037 | 9.5369 | 0.08217 | 0.7906
CPB | Capalaba | Cleveland Bulk Supply | CPB11kVB2_Term | 11 | 8.8042 | 167.7424 | 1.886 | 11.9775 | 1.0563 | 7.5878 | 48.1891 | 7.6892 | 48.833 | 0.08215 | 0.78967 | 0.03037 | 9.5369 | 0.08217 | 0.7906
CPB | Capalaba | Cleveland Bulk Supply | CPB11kVB3_Term | 11 | 8.8042 | 167.7424 | 1.886 | 11.9775 | 1.0563 | 7.5878 | 48.1891 | 7.6892 | 48.833 | 0.08215 | 0.78967 | 0.03037 | 9.5369 | 0.08217 | 0.7906
CPC | Carole Park Central | Goodna Bulk Supply | CPC33kVB1_Term | 33 | 16.1684 | 924.1477 | 2.0192 | 38.4709 | 1.0854 | 13.8737 | 264.3299 | 13.9456 | 265.6995 | 0.15986 | 1.2868 | 1.5785 | 28.4969 | 0.16175 | 1.3063
CPC | Carole Park Central | Goodna Bulk Supply | CPC11kVB1_Term | 11 | 10.151 | 193.4022 | 1.9214 | 12.2023 | 1.0628 | 8.7671 | 55.6787 | 8.8201 | 56.0149 | 0.03698 | 0.68743 | 0.02049 | 9.5339 | 0.03719 | 0.68961
CPD | Carpendale | Postmans Ridge Bulk Supply | CPD33kVB2_Term | 33 | 3.3919 | 193.8731 | 1.1741 | 22.3691 | 0.70181 | 2.8335 | 53.9846 | 3.0796 | 58.6744 | 2.9202 | 5.4463 | 4.424 | 41.6788 | 2.9201 | 5.4425
CPD | Carpendale | Postmans Ridge Bulk Supply | CPD11kVB1_Term | 11 | 3.1367 | 59.7617 | 3.5223 | 22.3698 | 4.0095 | 3.2597 | 20.7021 | 3.4889 | 22.1572 | 0.43249 | 2.1852 | 0.10803 | 1.501 | 0.43249 | 2.1847
CPK | Carole Park | Goodna Bulk Supply | CPK33kVB1_Term | 33 | 13.4834 | 770.6774 | 1.8967 | 36.1369 | 1.0339 | 11.4693 | 218.5187 | 11.6071 | 221.1458 | 0.25767 | 1.5333 | 0.96795 | 30.019 | 0.26956 | 1.5735
CPK | Carole Park | Goodna Bulk Supply | CPK11kVB2_Term | 11 | 12.4368 | 236.9536 | 1.9627 | 12.4646 | 1.1301 | 10.1719 | 64.6004 | 10.2423 | 65.0473 | 0.03539 | 0.56075 | 0.02049 | 9.4935 | 0.0418 | 0.62643
CPK | Carole Park | Goodna Bulk Supply | CPK11kVB3_Term | 11 | 12.4368 | 236.9536 | 1.9627 | 12.4646 | 1.1301 | 10.1719 | 64.6004 | 10.2423 | 65.0473 | 0.03539 | 0.56075 | 0.02049 | 9.4935 | 0.0418 | 0.62643
CPL | Coopers Plain | Archerfield Bulk Supply | CPL33kVB1_Term | 33 | 7.622 | 435.656 | 1.6708 | 31.8322 | 0.93676 | 6.5225 | 124.2694 | 6.7048 | 127.7435 | 0.68147 | 2.6648 | 1.4665 | 32.2054 | 0.68179 | 2.6676
CPL | Coopers Plain | Archerfield Bulk Supply | CPL11kVB1_Term | 11 | 5.2878 | 100.7459 | 0.97033 | 6.1624 | 0.5341 | 4.5658 | 28.9965 | 4.6074 | 29.2608 | 0.10902 | 1.3171 | 0.0333 | 18.9699 | 0.10906 | 1.3174
CPL | Coopers Plain | Archerfield Bulk Supply | CPL11kVB2_Term | 11 | 5.2195 | 99.4441 | 0.96804 | 6.1479 | 0.53341 | 4.5069 | 28.6227 | 4.5481 | 28.8842 | 0.10953 | 1.3344 | 0.03381 | 18.9864 | 0.10957 | 1.3347
CPR | Coorparoo Bulk | Coorparoo Bulk Supply | 43210 COORPA1D | 110 | 21.3084 | 4059.7989 | 25.5077 | 1619.9573 | 31.9402 | 26.4586 | 1680.3447 | 22.0647 | 1401.2932 | 0.35891 | 3.2606 | 0.77265 | 1.5219 | 0.36423 | 3.301
CPR | Coorparoo Bulk | Coorparoo Bulk Supply | 43211 COORPA2D | 110 | 21.3084 | 4059.7989 | 25.5077 | 1619.9573 | 31.9402 | 26.4586 | 1680.3448 | 22.0646 | 1401.2929 | 0.35891 | 3.2606 | 0.77265 | 1.5219 | 0.36423 | 3.301
CPR | Coorparoo Bulk | Coorparoo Bulk Supply | CPR33kVB1_Term | 33 | 17.622 | 1007.2347 | 2.2915 | 43.6584 | 1.2273 | 15.2213 | 290.0052 | 15.2798 | 291.1194 | 0.05972 | 1.1885 | 0.04051 | 25.0721 | 0.0602 | 1.1921
CPR | Coorparoo | Coorparoo Bulk Supply | CPR11kVB2_Term | 11 | 10.8531 | 206.7799 | 1.9463 | 12.3608 | 1.0693 | 9.3935 | 59.6569 | 9.4293 | 59.884 | 0.0234 | 0.64361 | 0.01676 | 9.486 | 0.02345 | 0.64401
CPR | Coorparoo | Coorparoo Bulk Supply | CPR11kVB3_Term | 11 | 10.8531 | 206.7799 | 1.9463 | 12.3608 | 1.0693 | 9.3935 | 59.6569 | 9.4293 | 59.884 | 0.0234 | 0.64361 | 0.01676 | 9.486 | 0.02345 | 0.64401
CPS | Capalaba South | Cleveland Bulk Supply | CPS33kVB1_Term | 33 | 9.2749 | 530.134 | 1.7731 | 33.7822 | 0.98062 | 7.9497 | 151.4631 | 8.1185 | 154.679 | 0.50712 | 2.2033 | 1.4227 | 30.9819 | 0.50718 | 2.2109
CPS | Capalaba South | Cleveland Bulk Supply | CPS11kVB1_Term | 11 | 9.1077 | 173.5252 | 1.9023 | 12.0814 | 1.0623 | 7.8535 | 49.8764 | 7.9486 | 50.4807 | 0.07309 | 0.76399 | 0.01675 | 9.4932 | 0.0731 | 0.76484
CPS | Capalaba South | Cleveland Bulk Supply | CPS11kVB2_Term | 11 | 9.1077 | 173.5252 | 1.9023 | 12.0814 | 1.0623 | 7.8535 | 49.8764 | 7.9486 | 50.4807 | 0.07309 | 0.76399 | 0.01675 | 9.4932 | 0.0731 | 0.76484
CRB | Curumbin | Burleigh Head Bulk Supply | CRB33kVB1_Term | 33 | 12.7272 | 727.458 | 1.131 | 21.5489 | 0.56742 | 11.3053 | 215.3943 | 10.7386 | 204.5988 | 0.19991 | 1.6354 | 55.2027 | -4.6086 | 0.1998 | 1.6354
CRB | Curumbin | Burleigh Head Bulk Supply | CRB11kVB1_Term | 11 | 9.6538 | 183.929 | 1.9132 | 12.1503 | 1.0616 | 8.3473 | 53.0124 | 8.407 | 53.3919 | 0.04407 | 0.72268 | 0.02201 | 9.5142 | 0.04406 | 0.72269
CRB | Curumbin | Burleigh Head Bulk Supply | CRB11kVB2_Term | 11 | 9.6538 | 183.929 | 1.9132 | 12.1503 | 1.0616 | 8.3473 | 53.0124 | 8.407 | 53.3919 | 0.04407 | 0.72268 | 0.02201 | 9.5142 | 0.04406 | 0.72269
CRM | Crestmead | Browns Plains Bulk Supply | CRM33kVB1_Term | 33 | 13.8222 | 790.0435 | 2.1355 | 40.6866 | 1.1622 | 11.8855 | 226.4487 | 11.984 | 228.325 | 0.21798 | 1.5017 | 1.4898 | 26.3866 | 0.21932 | 1.5147
CRM | Crestmead | Browns Plains Bulk Supply | CRM11kVB1_Term | 11 | 10.9303 | 208.2505 | 1.9433 | 12.3418 | 1.0823 | 9.3252 | 59.223 | 9.3877 | 59.6202 | 0.04175 | 0.63826 | 0.01795 | 9.4979 | 0.04059 | 0.6561
CRM | Crestmead | Browns Plains Bulk Supply | CRM11kVB2_Term | 11 | 10.9303 | 208.2505 | 1.9433 | 12.3418 | 1.0823 | 9.3252 | 59.223 | 9.3877 | 59.6202 | 0.04175 | 0.63826 | 0.01795 | 9.4979 | 0.04059 | 0.6561
CRY | Cooroy | Sunrise Hills Bulk Supply | CRY33kVB1_Term | 33 | 2.8099 | 160.607 | 1.0475 | 19.9574 | 0.63699 | 2.347 | 44.716 | 2.5568 | 48.713 | 3.4669 | 6.6052 | 5.3822 | 45.5436 | 3.4642 | 6.6073
CRY | Cooroy | Sunrise Hills Bulk Supply | CRY11kVB1_Term | 11 | 3.8032 | 72.461 | 0.92767 | 5.8915 | 0.52675 | 3.2466 | 20.6189 | 3.3605 | 21.3421 | 0.42086 | 1.7883 | 0.03565 | 19.0017 | 0.42056 | 1.7885
CSE | Chermside | Stafford Bulk Supply | CSE33kVB1_Term | 33 | 16.6024 | 948.9521 | 2.9959 | 57.08 | 1.6511 | 14.3079 | 272.602 | 14.42 | 274.7389 | 0.16596 | 1.2517 | 1.1408 | 18.4301 | 0.16741 | 1.2585
CSE | Chermside | Stafford Bulk Supply | CSE11kVB1_Term | 11 | 5.9818 | 113.9689 | 0.98366 | 6.2471 | 0.53604 | 5.1746 | 32.8629 | 5.1968 | 33.0043 | 0.05204 | 1.167 | 0.0336 | 18.9765 | 0.0522 | 1.1678
CSE | Chermside | Stafford Bulk Supply | CSE11kVB2_Term | 11 | 5.9818 | 113.9689 | 0.98366 | 6.2471 | 0.53604 | 5.1746 | 32.8629 | 5.1968 | 33.0043 | 0.05204 | 1.167 | 0.0336 | 18.9765 | 0.0522 | 1.1678
CSE | Chermside | Stafford Bulk Supply | CSE11kVB3_Term | 11 | 11.6092 | 221.1855 | 1.9582 | 12.4364 | 1.0815 | 9.9371 | 63.1088 | 9.9953 | 63.4786 | 0.03478 | 0.60091 | 0.02142 | 9.4902 | 0.0356 | 0.61366
CSE | Chermside | Stafford Bulk Supply | CSE11kVB4_Term | 11 | 11.6092 | 221.1855 | 1.9582 | 12.4364 | 1.0815 | 9.9371 | 63.1088 | 9.9953 | 63.4786 | 0.03478 | 0.60091 | 0.02142 | 9.4902 | 0.0356 | 0.61366
CST | Charlotte St | Belmont Bulk Supply | 43200 CHRLOT1D | 110 | 23.5024 | 4477.8068 | 28.5541 | 1813.4322 | 36.973 | 28.3447 | 1800.1319 | 26.5174 | 1684.0836 | 0.31564 | 2.9573 | 0.33436 | 1.3236 | 0.32112 | 2.9984
CST | Charlotte St | Belmont Bulk Supply | 43201 CHRLOT2D | 110 | 19.9787 | 3806.4589 | 21.0038 | 1333.9199 | 22.236 | 21.5336 | 1367.5663 | 19.4825 | 1237.3031 | 0.68009 | 3.431 | 1.0832 | 2.7897 | 0.68613 | 3.4554
CST | Charlotte St | Belmont Bulk Supply | CST11kVB1_Term | 11 | 14.7204 | 280.4622 | 5.1245 | 32.5447 | 3.1372 | 12.838 | 81.5325 | 12.6237 | 80.171 | 0.01239 | 0.47466 | 0.3135 | 3.1193 | 0.01255 | 0.48389
CST | Charlotte St | Belmont Bulk Supply | CST11kVB2_Term | 11 | 14.7205 | 280.4624 | 5.1245 | 32.5447 | 3.1372 | 12.8381 | 81.5326 | 12.6237 | 80.171 | 0.01239 | 0.47466 | 0.3135 | 3.1193 | 0.01255 | 0.48388
CST | Charlotte St | Belmont Bulk Supply | CST11kVB3_Term | 11 | 14.7204 | 280.4621 | 5.1245 | 32.5447 | 3.1372 | 12.838 | 81.5325 | 12.6237 | 80.171 | 0.01239 | 0.47466 | 0.3135 | 3.1193 | 0.01255 | 0.48389
CST | Charlotte St | Belmont Bulk Supply | CST11kVB4_Term | 11 | 14.7915 | 281.8165 | 5.1293 | 32.5755 | 3.1404 | 12.8899 | 81.8621 | 12.6755 | 80.5003 | 0.01242 | 0.47238 | 0.3135 | 3.1193 | 0.01255 | 0.48228
CST | Charlotte St | Belmont Bulk Supply | CST11kVB5_Term | 11 | 14.7915 | 281.8167 | 5.1293 | 32.5755 | 3.1404 | 12.8899 | 81.8621 | 12.6755 | 80.5004 | 0.01242 | 0.47238 | 0.3135 | 3.1193 | 0.01255 | 0.48228
CST | Charlotte St | Belmont Bulk Supply | CST11kVB6_Term | 11 | 14.7915 | 281.8166 | 5.1293 | 32.5755 | 3.1404 | 12.8899 | 81.8621 | 12.6755 | 80.5003 | 0.01242 | 0.47238 | 0.3135 | 3.1193 | 0.01255 | 0.48228
CVL | Cleveland Bulk | Cleveland Bulk Supply | 43220 CLVLND1D | 110 | 10.3061 | 1963.5839 | 9.2979 | 590.4926 | 8.5045 | 9.7814 | 621.1995 | 9.9635 | 632.769 | 1.0615 | 6.6988 | 1.1086 | 8.8911 | 1.0641 | 6.7307
CVL | Cleveland Bulk | Cleveland Bulk Supply | 43221 CLVLND2D | 110 | 10.1713 | 1937.8998 | 10.7169 | 680.6134 | 11.3745 | 10.2704 | 652.2603 | 10.6744 | 677.9135 | 1.0576 | 6.7904 | 0.50238 | 5.7784 | 1.0603 | 6.8223
CVL | Cleveland Bulk | Cleveland Bulk Supply | CVL33kVB1_Term | 33 | 18.116 | 1035.4669 | 2.1819 | 41.5705 | 1.1627 | 15.6347 | 297.8819 | 15.7154 | 299.4179 | 0.08539 | 1.1544 | 0.05148 | 26.5194 | 0.08458 | 1.1582
CVL | Cleveland | Cleveland Bulk Supply | CVL11kVB1_Term | 11 | 5.9367 | 113.1098 | 0.98221 | 6.2379 | 0.53547 | 5.1379 | 32.63 | 5.157 | 32.7511 | 0.04562 | 1.1765 | 0.03614 | 18.9959 | 0.04553 | 1.1769
CVL | Cleveland | Cleveland Bulk Supply | CVL11kVB2_Term | 11 | 10.3679 | 197.5352 | 1.93 | 12.2569 | 1.0643 | 8.9666 | 56.9458 | 9.0172 | 57.267 | 0.03517 | 0.67328 | 0.02576 | 9.5181 | 0.03508 | 0.6737
DBS | Doboy Bulk | Doboy Bulk Supply | 40730 DOBOY1D | 110 | 26.0389 | 4961.0751 | 29.8577 | 1896.2187 | 35.5061 | 29.0876 | 1847.3104 | 28.1826 | 1789.8331 | 0.26214 | 2.6715 | 0.25507 | 1.6021 | 0.26648 | 2.7055
DBS | Doboy Bulk | Doboy Bulk Supply | 40731 DOBOY2D | 110 | 26.0482 | 4962.8512 | 29.8508 | 1895.7804 | 35.4704 | 29.0657 | 1845.9171 | 28.1954 | 1790.6466 | 0.26455 | 2.6703 | 0.25335 | 1.6058 | 0.2689 | 2.7043
DBS | Doboy Bulk | Doboy Bulk Supply | 40732 DOBOY3D | 110 | 26.0366 | 4960.6372 | 29.8689 | 1896.9282 | 35.5424 | 29.0854 | 1847.1689 | 28.2047 | 1791.2372 | 0.26454 | 2.6715 | 0.25343 | 1.5991 | 0.26889 | 2.7055
DBS | Doboy Bulk | Doboy Bulk Supply | DBS33kVB1_Term | 33 | 25.2926 | 1445.6681 | 3.3555 | 63.93 | 1.8041 | 21.7973 | 415.2949 | 21.8853 | 416.9717 | 0.04289 | 0.82794 | 0.01933 | 17.085 | 0.04273 | 0.83429
DBS | Doboy | Doboy Bulk Supply | DBS11kVB1_Term | 11 | 11.466 | 218.456 | 1.9578 | 12.4334 | 1.0709 | 9.9213 | 63.0085 | 9.9561 | 63.2298 | 0.02163 | 0.60921 | 0.01687 | 9.4914 | 0.02162 | 0.60992
DBY | Deception Bay | Hays Inlet Bulk Supply | DBY33kVB1_Term | 33 | 14.6485 | 837.2758 | 1.4878 | 28.346 | 0.77993 | 12.8617 | 245.0482 | 12.4241 | 236.7117 | 0.23121 | 1.4122 | 27.6676 | 28.7144 | 0.23094 | 1.4232
DBY | Deception Bay | Hays Inlet Bulk Supply | DBY11kVB1_Term | 11 | 5.9488 | 113.3398 | 0.98353 | 6.2463 | 0.53634 | 5.1436 | 32.6663 | 5.1688 | 32.826 | 0.059 | 1.1731 | 0.03331 | 18.9654 | 0.05897 | 1.1743
DBY | Deception Bay | Hays Inlet Bulk Supply | DBY11kVB2_Term | 11 | 5.9356 | 113.0886 | 0.98317 | 6.244 | 0.53623 | 5.1322 | 32.5941 | 5.1573 | 32.7534 | 0.059 | 1.1757 | 0.03331 | 18.9679 | 0.05897 | 1.1769
DRA | Darra | Richlands Bulk Supply | DRA33kVB1_Term | 33 | 24.1198 | 1378.631 | 3.356 | 63.9397 | 1.8146 | 20.6943 | 394.279 | 20.8747 | 397.7165 | 0.09039 | 0.86455 | 0.03234 | 17.0018 | 0.09149 | 0.8751
DRA | Darra | Richlands Bulk Supply | DRA11kVB1_Term | 11 | 12.1102 | 230.7309 | 2.2789 | 14.4731 | 1.1589 | 11.0526 | 70.1932 | 9.9022 | 62.8876 | 0.02265 | 0.57666 | 9.0126 | 0.45657 | 0.02277 | 0.57783
DRA | Darra | Richlands Bulk Supply | DRA11kVB2_Term | 11 | 12.1102 | 230.7309 | 2.2789 | 14.4731 | 1.1589 | 11.0526 | 70.1932 | 9.9022 | 62.8876 | 0.02265 | 0.57666 | 9.0126 | 0.45657 | 0.02277 | 0.57783
DRD | Duffield Road | Hays Inlet Bulk Supply | DRD33kVB1_Term | 33 | 11.93 | 681.8901 | 1.4402 | 27.4388 | 0.7628 | 10.4941 | 199.9391 | 10.1193 | 192.7981 | 0.35472 | 1.7209 | 26.953 | 30.3347 | 0.35429 | 1.7318
DRD | Duffield Road | Hays Inlet Bulk Supply | DRD11kVB1_Term | 11 | 9.6882 | 184.5851 | 1.9159 | 12.1676 | 1.0637 | 8.3606 | 53.0971 | 8.44 | 53.6011 | 0.05747 | 0.71894 | 0.01806 | 9.5013 | 0.05742 | 0.72014
DRD | Duffield Road | Hays Inlet Bulk Supply | DRD11kVB2_Term | 11 | 9.6882 | 184.5851 | 1.9159 | 12.1676 | 1.0637 | 8.3606 | 53.0971 | 8.44 | 53.6011 | 0.05747 | 0.71894 | 0.01806 | 9.5013 | 0.05742 | 0.72014
EAN | Enoggera Army Camp (North) | Stafford Bulk Supply | EAN33kVB1_Term | 33 | 13.6961 | 782.8379 | 2.8389 | 54.0889 | 1.5863 | 11.8272 | 225.3394 | 11.91 | 226.9156 | 0.25424 | 1.5094 | 2.1419 | 18.9699 | 0.25502 | 1.5144
EAS | Enoggera Army Camp (South) | Stafford Bulk Supply | EAS33kVB1_Term | 33 | 12.3508 | 705.9435 | 2.7502 | 52.3989 | 1.5499 | 10.6847 | 203.5705 | 10.7328 | 204.4876 | 0.30842 | 1.6691 | 2.912 | 19.2502 | 0.30921 | 1.6741
EMD | Eumundi | Sunrise Hills Bulk Supply | EMD33kVB1_Term | 33 | 1.9497 | 111.4427 | 0.79511 | 15.1488 | 0.49462 | 1.6307 | 31.0687 | 1.7791 | 33.8963 | 4.92 | 9.5589 | 8.1225 | 57.9019 | 4.9173 | 9.561
EMD | Eumundi | Sunrise Hills Bulk Supply | EMD11kVB1_Term | 11 | 2.5739 | 49.04 | 3.0339 | 19.2678 | 3.6856 | 2.7633 | 17.5491 | 3.0156 | 19.1516 | 0.6608 | 2.6329 | 0.11414 | 1.4923 | 0.6605 | 2.6331
EMP | Eight Mile Plains | Belmont Bulk Supply | EMP11kVB1_Term | 11 | 6.3149 | 120.3149 | 0.99382 | 6.3116 | 0.53936 | 5.4587 | 34.6674 | 5.4908 | 34.8713 | 0.06975 | 1.1046 | 0.03226 | 18.8888 | 0.06979 | 1.1049
EMP | Eight Mile Plains | Belmont Bulk Supply | EMP11kVB3_Term | 11 | 5.757 | 109.6859 | 0.9775 | 6.208 | 0.54351 | 4.8692 | 30.9237 | 4.9524 | 31.452 | 0.2088 | 1.196 | 0.03891 | 19.0098 | 0.20136 | 1.24
EMP | Eight Mile Plains | Runcorn Bulk Supply | EMP33kVB1_Term | 33 | 13.4551 | 769.0612 | 2.2405 | 42.6878 | 1.2211 | 11.5357 | 219.785 | 11.78 | 224.4385 | 0.33736 | 1.5215 | 0.25502 | 25.0155 | 0.33779 | 1.5242
EMP | Eight Mile Plains | Runcorn Bulk Supply | EMP33kVB2_Term | 33 | 5.6695 | 324.0545 | 1.0235 | 19.501 | 0.54333 | 5.1129 | 97.4133 | 4.6606 | 88.7956 | 1.5513 | 3.3576 | 56.7246 | 7.2703 | 1.5644 | 3.3948
ENG | Ennogera | Stafford Bulk Supply | ENG33kVB1_Term | 33 | 16.5199 | 944.238 | 2.9821 | 56.8163 | 1.6421 | 14.2365 | 271.2426 | 14.368 | 273.7461 | 0.16887 | 1.2577 | 0.93772 | 18.5304 | 0.16965 | 1.2628
ENG | Ennogera | Stafford Bulk Supply | ENG11kVB1_Term | 11 | 10.4676 | 199.434 | 1.9349 | 12.2882 | 1.0663 | 9.0491 | 57.4693 | 9.1051 | 57.8253 | 0.03765 | 0.66651 | 0.01888 | 9.5005 | 0.03774 | 0.66707
ENG | Ennogera | Stafford Bulk Supply | ENG11kVB2_Term | 11 | 10.4676 | 199.434 | 1.9349 | 12.2882 | 1.0663 | 9.0491 | 57.4693 | 9.1051 | 57.8253 | 0.03765 | 0.66651 | 0.01888 | 9.5005 | 0.03774 | 0.66707
ESK | Esk | Lockrose Bulk Supply | ESK33kVB1_Term | 33 | 2.0341 | 116.2653 | 0.88617 | 16.8839 | 0.5633 | 1.7202 | 32.7734 | 1.8456 | 35.1638 | 4.6478 | 9.1977 | 10.9567 | 49.6173 | 4.6447 | 9.199
ESK | Esk | Lockrose Bulk Supply | ESK11kVB1_Term | 11 | 2.6296 | 50.1014 | 3.0897 | 19.622 | 3.7368 | 2.8195 | 17.9064 | 3.0667 | 19.476 | 0.6321 | 2.5809 | 0.11568 | 1.481 | 0.63176 | 2.581
FBS | Fishermans Island Bulk | Lytton Bulk Supply | FBS33kVB1_Term | 33 | 8.9203 | 509.8643 | 1.8953 | 36.1104 | 1.0602 | 7.6717 | 146.165 | 7.8048 | 148.7015 | 0.37888 | 2.32 | 0.86796 | 28.5081 | 0.37927 | 2.323
FBS | Fishermans Island Bulk | Lytton Bulk Supply | FBS11kVB1_Term | 11 | 5.4234 | 103.3294 | 0.97296 | 6.1791 | 0.53442 | 4.6891 | 29.7799 | 4.7184 | 29.9659 | 0.07538 | 1.2866 | 0.03328 | 18.9774 | 0.07542 | 1.2869
FDS | Flinders | Raceview Bulk Supply | FDS33kVB1_Term | 33 | 5.0078 | 286.2358 | 1.3499 | 25.72 | 0.7761 | 4.2412 | 80.8055 | 4.4615 | 85.0031 | 1.5777 | 3.8777 | 3.1485 | 38.4031 | 1.5781 | 3.8809
FDS | Flinders | Raceview Bulk Supply | FDS11kVB1_Term | 11 | 5.5987 | 106.6703 | 1.7176 | 10.9083 | 1.0117 | 4.7776 | 30.3419 | 4.9692 | 31.5585 | 0.26356 | 1.22 | 0.08824 | 9.7498 | 0.2636 | 1.2204
FIS | Fishermans Island | Lytton Bulk Supply | FIS11kVB2_Term | 11 | 8.8186 | 168.0167 | 1.8935 | 12.0254 | 1.0605 | 7.6094 | 48.326 | 7.6982 | 48.8903 | 0.0713 | 0.78939 | 0.02381 | 9.4937 | 0.07135 | 0.78973
GAP | The Gap | Ashgrove West Bulk Supply | GAP33kVB1_Term | 33 | 12.7575 | 729.1881 | 2.0349 | 38.7699 | 1.1062 | 11.0205 | 209.9684 | 11.0897 | 211.2876 | 0.25487 | 1.6234 | 2.5176 | 27.5098 | 0.25538 | 1.6255
GAP | The Gap | Ashgrove West Bulk Supply | GAP11kVB1_Term | 11 | 5.7963 | 110.434 | 0.98062 | 6.2278 | 0.53559 | 5.01 | 31.818 | 5.0427 | 32.0254 | 0.07912 | 1.203 | 0.0508 | 18.9715 | 0.07918 | 1.2033
GAP | The Gap | Ashgrove West Bulk Supply | GAP11kVB2_Term | 11 | 5.4622 | 104.0696 | 0.97074 | 6.165 | 0.53268 | 4.722 | 29.9887 | 4.753 | 30.1855 | 0.08048 | 1.2768 | 0.05207 | 19.0414 | 0.08054 | 1.2771
GBG | Geebung | Nudgee Bulk Supply | GBG33kVB1_Term | 33 | 17.5387 | 1002.4684 | 3.0526 | 58.1589 | 1.6764 | 15.0682 | 287.0886 | 15.2647 | 290.8322 | 0.15475 | 1.1851 | 0.13174 | 18.2189 | 0.15442 | 1.1926
GBG | Geebung | Nudgee Bulk Supply | GBG11kVB1_Term | 11 | 10.6538 | 202.9823 | 1.9395 | 12.3174 | 1.0675 | 9.2101 | 58.492 | 9.2624 | 58.8239 | 0.03455 | 0.65495 | 0.01737 | 9.4971 | 0.03452 | 0.65578
GBG | Geebung | Nudgee Bulk Supply | GBG11kVB2_Term | 11 | 10.6538 | 202.9823 | 1.9395 | 12.3174 | 1.0675 | 9.2101 | 58.492 | 9.2624 | 58.8239 | 0.03455 | 0.65495 | 0.01737 | 9.4971 | 0.03452 | 0.65578
GBG | Geebung | Nudgee Bulk Supply | GBG11kVB3_Term | 11 | 5.9663 | 113.6738 | 0.98286 | 6.242 | 0.53571 | 5.1614 | 32.7795 | 5.1829 | 32.9155 | 0.05045 | 1.1701 | 0.03326 | 18.9865 | 0.05041 | 1.1709
GBN | Goomboorian | Gympie Bulk Supply | GBN33kVB1_Term | 33 | 3.6245 | 207.169 | 1.1533 | 21.9737 | 0.68289 | 3.0802 | 58.6847 | 3.2333 | 61.6031 | 1.8418 | 5.4819 | 3.4811 | 43.0857 | 1.8366 | 5.4828
GBN | Goomboorian | Gympie Bulk Supply | GBN11kVB1_Term | 11 | 3.1877 | 60.7335 | 3.5727 | 22.6899 | 4.0618 | 3.3621 | 21.3524 | 3.491 | 22.1711 | 0.32032 | 2.1683 | 0.11568 | 1.4812 | 0.31974 | 2.1684
GBS | Gatton Bulk | Gatton Bulk Supply | 43280 GATOBS1D | 110 | 6.5903 | 1255.6173 | 7.8517 | 498.6492 | 9.6246 | 6.9698 | 442.6433 | 7.9364 | 504.0288 | 3.627 | 9.9629 | 0.54134 | 5.6421 | 3.6204 | 9.9312
GBS | Gatton Bulk | Gatton Bulk Supply | GBS33kVB1_Term | 33 | 11.0478 | 631.4665 | 2.1393 | 40.7599 | 1.1813 | 9.4823 | 180.6624 | 9.7024 | 184.8548 | 0.36967 | 1.861 | 0.03772 | 25.6657 | 0.36908 | 1.8582
GFN | Gatton Bulk | Griffin Bulk Supply | 43820 GRIFIN1D | 110 | 15.8654 | 3022.7731 | 15.1731 | 963.6245 | 14.6166 | 16.0095 | 1016.7388 | 15.0419 | 955.2884 | 0.43699 | 4.3825 | 1.0257 | 4.8884 | 0.43601 | 4.4135
GFN | Griffin Bulk | Griffin Bulk Supply | GFN33kVB1_Term | 33 | 16.0473 | 917.2269 | 2.1957 | 41.8336 | 1.1797 | 13.8669 | 264.1999 | 13.924 | 265.288 | 0.06918 | 1.3045 | 0.08101 | 26.0287 | 0.0691 | 1.3073
GGR | Glenore Grove | Lockrose Bulk Supply | GGR33kVB2_Term | 33 | 4.8238 | 275.7152 | 1.7857 | 34.0231 | 1.0852 | 4.0585 | 77.3253 | 4.3713 | 83.2853 | 1.8491 | 3.9327 | 3.2541 | 26.67 | 1.8443 | 3.9219
GGR | Glenore Grove | Lockrose Bulk Supply | GGR33kVB1_Term | 33 | 4.3807 | 250.3902 | 1.6546 | 31.525 | 1.0112 | 3.6932 | 70.3639 | 3.9653 | 75.5494 | 1.9545 | 4.3679 | 3.5419 | 28.5458 | 1.9498 | 4.3571
GGR | Glenore Grove | Lockrose Bulk Supply | GGR11kVB1_Term | 11 | 3.374 | 64.2841 | 0.88706 | 5.6336 | 0.50974 | 2.8963 | 18.394 | 2.9711 | 18.8691 | 0.33431 | 2.0438 | 0.12368 | 19.5321 | 0.33378 | 2.0426
GGR | Glenore Grove | Lockrose Bulk Supply | GGR11kVB2_Term | 11 | 3.467 | 66.0548 | 0.89339 | 5.6738 | 0.51187 | 2.9768 | 18.9053 | 3.0513 | 19.3782 | 0.32312 | 1.9894 | 0.13211 | 19.4737 | 0.32259 | 1.9882
GHM | Grantham | Postmans Ridge Bulk Supply | GHM33kVB1_Term | 33 | 2.6533 | 151.6572 | 1.0569 | 20.1374 | 0.64938 | 2.1918 | 41.7589 | 2.4434 | 46.5537 | 4.3477 | 6.5964 | 6.5587 | 44.3201 | 4.3471 | 6.5935
GIS | Gibson Island | Lytton Bulk Supply | GIS33kVB1_Term | 33 | 14.7584 | 843.5567 | 2.1725 | 41.3917 | 1.1738 | 12.7487 | 242.896 | 12.8135 | 244.1294 | 0.13467 | 1.4144 | 0.99879 | 26.0963 | 0.13506 | 1.4175
GIS | Gibson Island | Lytton Bulk Supply | GIS11kVB1_Term | 11 | 10.402 | 198.1843 | 1.9359 | 12.2949 | 1.0675 | 8.9986 | 57.1489 | 9.0453 | 57.4451 | 0.03161 | 0.67121 | 0.01664 | 9.4884 | 0.03165 | 0.67155
GIS | Gibson Island | Lytton Bulk Supply | GIS11kVB2_Term | 11 | 10.402 | 198.1843 | 1.9359 | 12.2949 | 1.0675 | 8.9986 | 57.1489 | 9.0453 | 57.4451 | 0.03161 | 0.67121 | 0.01664 | 9.4884 | 0.03165 | 0.67155
GLY | Grovely | Stafford Bulk Supply | GLY33kVB1_Term | 33 | 11.1559 | 637.6456 | 2.5066 | 47.7569 | 1.414 | 9.655 | 183.953 | 9.6941 | 184.6975 | 0.28407 | 1.8576 | 2.6129 | 21.1675 | 0.28485 | 1.8626
GLY | Grovely | Stafford Bulk Supply | GLY33kVB2_Term | 33 | 11.1739 | 638.6735 | 2.5087 | 47.7964 | 1.415 | 9.6704 | 184.245 | 9.7098 | 184.9972 | 0.28351 | 1.8546 | 2.6042 | 21.1537 | 0.2843 | 1.8596
GLY | Grovely | Stafford Bulk Supply | GLY11kVB1_Term | 11 | 10.098 | 192.392 | 1.928 | 12.2444 | 1.066 | 8.7272 | 55.4255 | 8.7884 | 55.8138 | 0.04239 | 0.69071 | 0.01687 | 9.4909 | 0.04248 | 0.69127
GLY | Grovely | Stafford Bulk Supply | GLY11kVB2_Term | 11 | 10.098 | 192.392 | 1.928 | 12.2444 | 1.066 | 8.7272 | 55.4255 | 8.7884 | 55.8138 | 0.04239 | 0.69071 | 0.01687 | 9.4909 | 0.04248 | 0.69127
GNA | Goodna Bulk | Goodna Bulk Supply | GNA33kVB1_Term | 33 | 21.7926 | 1245.613 | 2.1258 | 40.5017 | 1.1274 | 18.6953 | 356.1924 | 18.7495 | 357.2269 | 0.04744 | 0.96084 | 0.01048 | 27.6477 | 0.04836 | 0.97745
GNA | Goodna | Goodna Bulk Supply | GNA11kVB1_Term | 11 | 6.18 | 117.7445 | 0.98515 | 6.2565 | 0.53569 | 5.3458 | 33.9502 | 5.3632 | 34.0607 | 0.0401 | 1.1301 | 0.03828 | 19.0184 | 0.0402 | 1.1319
GNA | Goodna | Goodna Bulk Supply | GNA11kVB2_Term | 11 | 6.18 | 117.7445 | 0.98515 | 6.2565 | 0.53569 | 5.3458 | 33.9502 | 5.3632 | 34.0607 | 0.0401 | 1.1301 | 0.03828 | 19.0184 | 0.0402 | 1.1319
GTN | Gatton | Gatton Bulk Supply | GTN33kVB1_Term | 33 | 5.7622 | 329.3551 | 1.5732 | 29.9733 | 0.90747 | 4.912 | 93.5856 | 5.1114 | 97.3859 | 1.0218 | 3.4914 | 1.6447 | 32.8232 | 1.0212 | 3.4886
GTN | Gatton | Gatton Bulk Supply | GTN11kVB1_Term | 11 | 7.5965 | 144.7334 | 1.8518 | 11.7602 | 1.053 | 6.5297 | 41.4693 | 6.6714 | 42.3689 | 0.13184 | 0.91031 | 0.01831 | 9.4963 | 0.13177 | 0.90999
GTN | Gatton | Gatton Bulk Supply | GTN11kVB2_Term | 11 | 7.5965 | 144.7334 | 1.8518 | 11.7602 | 1.053 | 6.5297 | 41.4693 | 6.6714 | 42.3689 | 0.13184 | 0.91031 | 0.01831 | 9.4963 | 0.13177 | 0.90999
GVN | Gavin | Molendinar Bulk Supply | GVN33kVB1_Term | 33 | 14.4533 | 826.1158 | 2.6087 | 49.703 | 1.4346 | 12.4161 | 236.5578 | 12.624 | 240.5199 | 0.27083 | 1.4253 | 0.77135 | 21.2237 | 0.27049 | 1.4296
GVN | Gavin | Molendinar Bulk Supply | GVN11kVB1_Term | 11 | 10.3013 | 196.2653 | 1.9331 | 12.2771 | 1.0668 | 8.8987 | 56.5142 | 8.9695 | 56.9637 | 0.04806 | 0.67683 | 0.01797 | 9.4925 | 0.04803 | 0.6773
GYM | Gympie | Gympie Bulk Supply | 40080 GYMPIE1D | 132 | 6.8473 | 1565.4931 | 6.638 | 505.8806 | 6.4281 | 6.5438 | 498.7054 | 6.9436 | 529.1733 | 3.2383 | 11.8087 | 2.1146 | 13.2941 | 3.1532 | 11.8224
GYM | Gympie | Gympie Bulk Supply | 40081 GYMPIE2D | 132 | 7.2105 | 1648.5357 | 6.7489 | 514.339 | 6.3334 | 6.8203 | 519.7747 | 7.1809 | 547.2582 | 3.0652 | 11.2166 | 2.3709 | 13.8566 | 2.9845 | 11.2323
GYM | Gympie | Gympie Bulk Supply | GYM33kVB1_Term | 33 | 12.7284 | 727.5278 | 2.0894 | 39.8089 | 1.1378 | 10.981 | 209.217 | 11.0922 | 211.3348 | 0.17722 | 1.6372 | 0.09757 | 26.8167 | 0.17201 | 1.6381
GYM | Gympie | Gympie Bulk Supply | GYM11kVB1_Term | 11 | 8.1717 | 155.6921 | 1.886 | 11.9775 | 1.0659 | 7.1171 | 45.2 | 7.0762 | 44.9401 | 0.05178 | 0.85344 | 0.9405 | 9.358 | 0.05119 | 0.85353
GYM | Gympie | Gympie Bulk Supply | GYM11kVB2_Term | 11 | 8.2119 | 156.4567 | 1.8874 | 11.9865 | 1.0662 | 7.1523 | 45.4233 | 7.1103 | 45.1562 | 0.05058 | 0.84933 | 0.9405 | 9.358 | 0.05002 | 0.84944
GYN | Gympie North | Gympie Bulk Supply | GYN33kVB1_Term | 33 | 10.4599 | 597.8622 | 1.936 | 36.885 | 1.0664 | 9.0308 | 172.0608 | 9.1164 | 173.69 | 0.25335 | 1.9878 | 1.1646 | 28.4617 | 0.24814 | 1.9887
GYN | Gympie North | Gympie Bulk Supply | GYN11kVB1_Term | 11 | 9.5615 | 182.1716 | 1.9156 | 12.1654 | 1.0643 | 8.2672 | 52.5035 | 8.3273 | 52.8852 | 0.04481 | 0.72935 | 0.01666 | 9.4831 | 0.04423 | 0.72945
GYN | Gympie North | Gympie Bulk Supply | GYN11kVB2_Term | 11 | 9.5615 | 182.1716 | 1.9156 | 12.1654 | 1.0643 | 8.2672 | 52.5035 | 8.3273 | 52.8852 | 0.04481 | 0.72935 | 0.01666 | 9.4831 | 0.04423 | 0.72945
GYS | Gympie South | Gympie Bulk Supply | GYS33kVB1_Term | 33 | 8.9044 | 508.9531 | 1.8532 | 35.3089 | 1.0316 | 7.6176 | 145.134 | 7.8397 | 149.3659 | 0.59804 | 2.2767 | 0.83539 | 29.316 | 0.59283 | 2.2776
GYS | Gympie South | Gympie Bulk Supply | GYS11kVB1_Term | 11 | 5.3548 | 102.0229 | 0.97062 | 6.1642 | 0.53352 | 4.6226 | 29.3575 | 4.6673 | 29.6411 | 0.11716 | 1.2995 | 0.05071 | 18.9942 | 0.11658 | 1.2996
HDA | Hendra | Nudgee Bulk Supply | HDA33kVB1_Term | 33 | 15.8521 | 906.0661 | 2.8731 | 54.74 | 1.5847 | 13.6693 | 260.4358 | 13.7533 | 262.0348 | 0.13284 | 1.3157 | 0.86468 | 19.2196 | 0.13263 | 1.3237
HDA | Hendra | Nudgee Bulk Supply | HDA11kVB1_Term | 11 | 10.4011 | 198.1671 | 1.931 | 12.2635 | 1.065 | 8.9937 | 57.1176 | 9.0414 | 57.4206 | 0.03261 | 0.67101 | 0.01881 | 9.5124 | 0.03258 | 0.6719
HDA | Hendra | Nudgee Bulk Supply | HDA11kVB2_Term | 11 | 10.4011 | 198.1671 | 1.931 | 12.2635 | 1.065 | 8.9937 | 57.1176 | 9.0414 | 57.4206 | 0.03261 | 0.67101 | 0.01881 | 9.5124 | 0.03258 | 0.6719
HDN | Helidon | Postmans Ridge Bulk Supply | HDN33kVB1_Term | 33 | 5.1658 | 295.2663 | 1.4427 | 27.4879 | 0.83526 | 4.4045 | 83.9163 | 4.5839 | 87.3356 | 1.1561 | 3.8895 | 2.1184 | 35.5855 | 1.1561 | 3.8857
HDN | Helidon | Postmans Ridge Bulk Supply | HDN11kVB1_Term | 11 | 3.3639 | 64.0901 | 3.6734 | 23.3293 | 4.0441 | 3.5022 | 22.2417 | 3.5899 | 22.799 | 0.23939 | 2.0633 | 0.11093 | 1.5495 | 0.23938 | 2.0628
HIL | Hays Inlet Bulk | Hays Inlet Bulk Supply | 43300 HAYSIN1D | 110 | 8.3191 | 1584.9927 | 6.6849 | 424.5509 | 5.6083 | 7.6933 | 488.5895 | 7.7453 | 491.89 | 1.7289 | 8.2195 | 2.7942 | 14.2505 | 1.7295 | 8.258
HIL | Hays Inlet Bulk | Hays Inlet Bulk Supply | 43301 HAYSIN2D | 110 | 8.3289 | 1586.8683 | 6.6292 | 421.0079 | 5.5259 | 7.6666 | 486.8936 | 7.7577 | 492.6806 | 1.729 | 8.2093 | 2.7092 | 14.5569 | 1.7296 | 8.248
HIL | Hays Inlet Bulk | Hays Inlet Bulk Supply | 43302 HAYSIN3D | 110 | 10.4643 | 1993.7217 | 9.2559 | 587.831 | 8.3305 | 10.1763 | 646.2847 | 9.7346 | 618.2274 | 0.74103 | 6.6362 | 1.7518 | 9.1079 | 0.74017 | 6.6715
HIL | Hays Inlet Bulk | Hays Inlet Bulk Supply | HIL33kVB1_Term | 33 | 20.7374 | 1185.3006 | 1.5906 | 30.3057 | 0.82401 | 18.1383 | 345.5815 | 17.6279 | 335.8565 | 0.09087 | 1.0068 | 26.2707 | 27.3608 | 0.09022 | 1.0159
HIS | Hope Island | Coomera Bulk Supply | HIS33kVB1_Term | 33 | 9.8762 | 564.5008 | 1.8657 | 35.5466 | 1.0304 | 8.5361 | 162.634 | 8.5953 | 163.7617 | 0.33034 | 2.0981 | 2.8389 | 29.3495 | 0.33039 | 2.0995
HIS | Hope Island | Coomera Bulk Supply | HIS11kVB1_Term | 11 | 5.6302 | 107.2703 | 0.97853 | 6.2145 | 0.53579 | 4.868 | 30.916 | 4.8979 | 31.1057 | 0.07404 | 1.2397 | 0.03734 | 18.9562 | 0.07405 | 1.2398
HIS | Hope Island | Coomera Bulk Supply | HIS11kVB2_Term | 11 | 5.3625 | 102.1693 | 0.97023 | 6.1618 | 0.53334 | 4.6374 | 29.4512 | 4.6655 | 29.6297 | 0.07372 | 1.3018 | 0.03702 | 19.0153 | 0.07373 | 1.302
HLG | Herring Lagoon | Beenleigh Bulk Supply (Including Bay Islands) | HLG33kVB1_Term | 33 | 3.6853 | 210.6432 | 1.0016 | 19.0834 | 0.54032 | 3.4289 | 65.3283 | 2.9555 | 56.3092 | 1.4158 | 5.5155 | 55.7703 | 11.685 | 1.4169 | 5.523
HMT | Hemmant | Doboy Bulk Supply | HMT33kVB1_Term | 33 | 22.2773 | 1273.317 | 3.2961 | 62.7987 | 1.7855 | 19.1692 | 365.2219 | 19.3324 | 368.3321 | 0.11405 | 0.93433 | 0.45253 | 17.1981 | 0.11388 | 0.94068
HMT | Hemmant | Doboy Bulk Supply | HMT11kVB1_Term | 11 | 11.2522 | 214.3831 | 1.9496 | 12.3815 | 1.0678 | 9.7267 | 61.7728 | 9.7812 | 62.1188 | 0.03436 | 0.62023 | 0.02349 | 9.514 | 0.03434 | 0.62093
HMT | Hemmant | Doboy Bulk Supply | HMT11kVB2_Term | 11 | 11.2522 | 214.3831 | 1.9496 | 12.3815 | 1.0678 | 9.7267 | 61.7728 | 9.7812 | 62.1188 | 0.03436 | 0.62023 | 0.02349 | 9.514 | 0.03434 | 0.62093
HPE | Holland Park East | Belmont Bulk Supply | HPE33kVB1_Term | 33 | 22.3497 | 1277.4545 | 1.1602 | 22.1054 | 0.58435 | 19.5735 | 372.9246 | 18.9935 | 361.8754 | 0.17577 | 0.92165 | 53.8336 | -3.8599 | 0.1747 | 0.92896
HPE | Holland Park East | Belmont Bulk Supply | HPE11kVB1_Term | 11 | 11.1114 | 211.7009 | 1.9495 | 12.3811 | 1.0691 | 9.6019 | 60.98 | 9.6614 | 61.358 | 0.03759 | 0.62795 | 0.01806 | 9.4993 | 0.03748 | 0.62876
HPE | Holland Park East | Belmont Bulk Supply | HPE11kVB2_Term | 11 | 11.1114 | 211.7009 | 1.9495 | 12.3811 | 1.0691 | 9.6019 | 60.98 | 9.6614 | 61.358 | 0.03759 | 0.62795 | 0.01806 | 9.4993 | 0.03748 | 0.62876
HPK | Holland Park | Coorparoo Bulk Supply | HPK33kVB1_Term | 33 | 12.4301 | 710.4751 | 2.0544 | 39.142 | 1.1208 | 10.7294 | 204.4236 | 10.8064 | 205.8905 | 0.18532 | 1.6768 | 1.0664 | 27.2298 | 0.1858 | 1.6804
HPK | Holland Park | Coorparoo Bulk Supply | HPK33kVB2_Term | 33 | 12.5035 | 714.6694 | 2.0424 | 38.9135 | 1.1132 | 10.7976 | 205.7226 | 10.8645 | 206.9976 | 0.18768 | 1.6665 | 1.3749 | 27.414 | 0.18815 | 1.6702
HPK | Holland Park | Coorparoo Bulk Supply | HPK11kVB1_Term | 11 | 10.4692 | 199.4658 | 1.9387 | 12.3125 | 1.0685 | 9.0539 | 57.4999 | 9.1054 | 57.8273 | 0.03483 | 0.66674 | 0.02072 | 9.4818 | 0.03488 | 0.66714
HPK | Holland Park | Coorparoo Bulk Supply | HPK11kVB2_Term | 11 | 10.4692 | 199.4658 | 1.9387 | 12.3125 | 1.0685 | 9.0539 | 57.4999 | 9.1054 | 57.8273 | 0.03483 | 0.66674 | 0.02072 | 9.4818 | 0.03488 | 0.66714
HTL | Hamilton Lands | Meeandah Bulk Supply | HTL33kVB1_Term | 33 | 13.1264 | 750.2735 | 2.1616 | 41.1831 | 1.1788 | 11.3308 | 215.8816 | 11.4124 | 217.4353 | 0.15785 | 1.5891 | 0.70254 | 25.8941 | 0.15752 | 1.5925
HTL | Hamilton Lands | Meeandah Bulk Supply | HTL11kVB1_Term | 11 | 10.0527 | 191.5291 | 1.9243 | 12.2209 | 1.0642 | 8.6952 | 55.2222 | 8.7445 | 55.5348 | 0.03476 | 0.69421 | 0.01813 | 9.5044 | 0.03472 | 0.69459
HTL | Hamilton Lands | Meeandah Bulk Supply | HTL11kVB2_Term | 11 | 10.0527 | 191.5291 | 1.9243 | 12.2209 | 1.0642 | 8.6952 | 55.2222 | 8.7445 | 55.5348 | 0.03476 | 0.69421 | 0.01813 | 9.5044 | 0.03472 | 0.69459
HTN | Hamilton | Nudgee Bulk Supply | HTN33kVB1_Term | 33 | 13.311 | 760.8235 | 2.7484 | 52.3646 | 1.5367 | 11.5048 | 219.1951 | 11.5461 | 219.9834 | 0.21384 | 1.5602 | 2.1128 | 19.6111 | 0.21364 | 1.5682
HTN | Hamilton | Nudgee Bulk Supply | HTN33kVB2_Term | 33 | 13.3085 | 760.6811 | 2.7483 | 52.3621 | 1.5366 | 11.5026 | 219.155 | 11.544 | 219.9418 | 0.21393 | 1.5605 | 2.1145 | 19.6114 | 0.21373 | 1.5685
HTN | Hamilton | Nudgee Bulk Supply | HTN11kVB1_Term | 11 | 10.3652 | 197.4843 | 1.9347 | 12.2867 | 1.0675 | 8.9601 | 56.9045 | 9.0132 | 57.2416 | 0.03602 | 0.67316 | 0.01664 | 9.4876 | 0.036 | 0.67405
HTN | Hamilton | Nudgee Bulk Supply | HTN11kVB2_Term | 11 | 10.3652 | 197.4843 | 1.9347 | 12.2867 | 1.0675 | 8.9601 | 56.9045 | 9.0132 | 57.2416 | 0.03602 | 0.67316 | 0.01664 | 9.4876 | 0.036 | 0.67405
HWD | Heathwood | Browns Plains Bulk Supply | HWD33kVB1_Term | 33 | 6.016 | 343.8582 | 1.5225 | 29.0082 | 0.87245 | 5.1325 | 97.7871 | 5.2945 | 100.8744 | 0.97493 | 3.3474 | 2.9823 | 34.3189 | 0.98121 | 3.3663
HWD | Heathwood | Browns Plains Bulk Supply | HWD11kVB1_Term | 11 | 8.0504 | 153.3814 | 1.8684 | 11.866 | 1.0614 | 6.8914 | 43.7665 | 7.0297 | 44.6444 | 0.11977 | 0.86016 | 0.01808 | 9.4944 | 0.12139 | 0.86819
HWD | Heathwood | Browns Plains Bulk Supply | HWD11kVB2_Term | 11 | 8.0504 | 153.3814 | 1.8684 | 11.866 | 1.0614 | 6.8914 | 43.7665 | 7.0297 | 44.6444 | 0.11977 | 0.86016 | 0.01808 | 9.4944 | 0.12139 | 0.86819
HWL | Hollywell | Molendinar Bulk Supply | HWL33kVB1_Term | 33 | 14.6547 | 837.6312 | 2.8643 | 54.5715 | 1.5907 | 12.6517 | 241.0474 | 12.7298 | 242.5349 | 0.24743 | 1.4093 | 2.3245 | 18.9566 | 0.24742 | 1.4154
HWL | Hollywell | Molendinar Bulk Supply | HWL11kVB1_Term | 11 | 10.3094 | 196.4197 | 1.933 | 12.2763 | 1.0669 | 8.9058 | 56.5594 | 8.9737 | 56.9908 | 0.04616 | 0.67643 | 0.01867 | 9.4939 | 0.04616 | 0.6771
HWL | Hollywell | Molendinar Bulk Supply | HWL11kVB2_Term | 11 | 10.3094 | 196.4197 | 1.933 | 12.2763 | 1.0669 | 8.9058 | 56.5594 | 8.9737 | 56.9908 | 0.04616 | 0.67643 | 0.01867 | 9.4939 | 0.04616 | 0.6771
HZD | Hinze Dam | Mudgeeraba Bulk Supply | HZD3.3kVB1_Term | 3.3 | 9.6499 | 55.1566 | 11.1281 | 21.2019 | 13.1263 | 10.2987 | 19.6217 | 10.9438 | 20.8508 | 0.05449 | 0.21035 | 0.01823 | 0.13009 | 0.05449 | 0.21035
IBL | Imbil | Gympie Bulk Supply | IBL33kVB1_Term | 33 | 1.0773 | 61.5733 | 0.54918 | 10.4633 | 0.36267 | 0.88642 | 16.8887 | 1.0104 | 19.2511 | 12.0706 | 15.2609 | 20.7421 | 74.8177 | 12.0654 | 15.2618
IBL | Imbil | Gympie Bulk Supply | IBL11kVB1_Term | 11 | 1.9272 | 36.7189 | 2.4021 | 15.2552 | 3.1628 | 2.1122 | 13.4145 | 2.4722 | 15.7005 | 1.4506 | 3.3225 | 0.10941 | 1.5455 | 1.45 | 3.3226
IBL | Imbil | Gympie Bulk Supply | IBL11kVB2_Term | 11 | 1.9272 | 36.7189 | 2.4021 | 15.2552 | 3.1628 | 2.1122 | 13.4145 | 2.4722 | 15.7005 | 1.4506 | 3.3225 | 0.10941 | 1.5455 | 1.45 | 3.3226
IBS | Ibis Bulk | Beenleigh Bulk Supply (Including Bay Islands) | 43320 IBIS1D | 110 | 4.1026 | 781.6464 | 4.8809 | 309.9797 | 6.0249 | 4.3248 | 274.665 | 4.9629 | 315.188 | 5.3397 | 16.1929 | 0.42983 | 9.0626 | 5.3517 | 16.2761
IBS | Ibis | Beenleigh Bulk Supply (Including Bay Islands) | IBS33kVB1_Term | 33 | 5.9992 | 342.9022 | 1.1254 | 21.4417 | 0.57857 | 5.4714 | 104.2446 | 4.9093 | 93.5351 | 0.57547 | 3.4504 | 54.0304 | 2.2748 | 0.57655 | 3.4578
IBS | Ibis | Beenleigh Bulk Supply (Including Bay Islands) | IBS11kVB1_Term | 11 | 3.5019 | 66.7209 | 3.7976 | 24.1183 | 4.1497 | 3.6583 | 23.2336 | 3.6902 | 23.4356 | 0.1734 | 1.99 | 0.10946 | 1.5263 | 0.17352 | 1.9908
IDY | Indooroopilly | Tennyson Bulk Supply | IDY33kVB1_Term | 33 | 19.7444 | 1128.5438 | 2.9745 | 56.6728 | 1.612 | 17.0001 | 323.8958 | 17.1569 | 326.8833 | 0.14231 | 1.0522 | 0.64833 | 19.014 | 0.1429 | 1.0572
IDY | Indooroopilly | Tennyson Bulk Supply | IDY11kVB1_Term | 11 | 10.7124 | 204.099 | 1.9391 | 12.3148 | 1.0664 | 9.2626 | 58.8252 | 9.3148 | 59.1566 | 0.03431 | 0.65145 | 0.01851 | 9.5079 | 0.03438 | 0.652
IDY | Indooroopilly | Tennyson Bulk Supply | IDY11kVB2_Term | 11 | 10.7124 | 204.099 | 1.9391 | 12.3148 | 1.0664 | 9.2626 | 58.8252 | 9.3148 | 59.1566 | 0.03431 | 0.65145 | 0.01851 | 9.5079 | 0.03438 | 0.652
INA | Inala | Richlands Bulk Supply | INA33kVB1_Term | 33 | 14.9774 | 856.0735 | 2.8501 | 54.3021 | 1.5793 | 12.8158 | 244.1736 | 13.0787 | 249.1826 | 0.27696 | 1.3722 | 0.47841 | 19.2899 | 0.27805 | 1.3827
INA | Inala | Richlands Bulk Supply | INA11kVB1_Term | 11 | 10.26 | 195.4802 | 1.9266 | 12.2358 | 1.0639 | 8.8576 | 56.2536 | 8.9302 | 56.7141 | 0.04959 | 0.67936 | 0.02035 | 9.5219 | 0.04971 | 0.68054
INA | Inala | Richlands Bulk Supply | INA11kVB2_Term | 11 | 10.26 | 195.4802 | 1.9266 | 12.2358 | 1.0639 | 8.8576 | 56.2536 | 8.9302 | 56.7141 | 0.04959 | 0.67936 | 0.02035 | 9.5219 | 0.04971 | 0.68054
IPL | Innisplain | Beaudesert Bulk Supply | IPL33kVB1_Term | 33 | 1.1791 | 67.3954 | 0.66489 | 12.6678 | 0.45088 | 0.94909 | 18.0826 | 1.1346 | 21.6169 | 12.1904 | 12.9519 | 15.9956 | 59.6889 | 12.1864 | 12.9425
IPL | Innisplain | Beaudesert Bulk Supply | IPL11kVB1_Term | 11 | 2.0846 | 39.7162 | 2.5827 | 16.4021 | 3.359 | 2.2378 | 14.2117 | 2.6745 | 16.9853 | 1.4701 | 3.0142 | 0.11563 | 1.4963 | 1.4697 | 3.0131
IPS | Ipswich | Raceview Bulk Supply | IPS33kVB1_Term | 33 | 14.9274 | 853.2124 | 2.0805 | 39.6384 | 1.1193 | 12.8837 | 245.4679 | 12.967 | 247.0536 | 0.1534 | 1.3961 | 0.90674 | 27.411 | 0.15379 | 1.3992
IPS | Ipswich | Raceview Bulk Supply | IPS11kVB1_Term | 11 | 5.6389 | 107.4357 | 0.97483 | 6.191 | 0.53358 | 4.8794 | 30.9883 | 4.9007 | 31.1237 | 0.05356 | 1.2381 | 0.03651 | 19.0289 | 0.0536 | 1.2385
IPS | Ipswich | Raceview Bulk Supply | IPS11kVB2_Term | 11 | 5.8163 | 110.8146 | 0.97377 | 6.1843 | 0.53142 | 5.0325 | 31.9607 | 5.0541 | 32.0979 | 0.05272 | 1.2003 | 0.03621 | 19.1279 | 0.05276 | 1.2007
JBB | Jimboomba Bulk | Jimboomba Bulk Supply | 43840 JIMBBA1D | 110 | 9.6105 | 1831.0362 | 10.5972 | 673.014 | 11.8162 | 9.9502 | 631.9196 | 10.4525 | 663.8224 | 1.4263 | 7.1338 | 0.56608 | 5.2188 | 1.421 | 7.1435
JBB | Jimboomba Bulk | Jimboomba Bulk Supply | JBB33kVB1_Term | 33 | 8.5283 | 487.4565 | 1.1374 | 21.6703 | 0.60808 | 7.3827 | 140.6592 | 7.4265 | 141.4935 | 0.18636 | 2.4523 | 0.04245 | 50.4248 | 0.18299 | 2.444
JBB | Jimboomba Bulk | Jimboomba Bulk Supply | JBB33kVB2_Term | 33 | 8.5283 | 487.4565 | 1.1374 | 21.6703 | 0.60808 | 7.3827 | 140.6592 | 7.4265 | 141.4935 | 0.18636 | 2.4523 | 0.04245 | 50.4248 | 0.18299 | 2.444
JBB | Jimboomba | Jimboomba Bulk Supply | JBB11kVB1_Term | 11 | 5.5939 | 106.5787 | 0.97911 | 6.2182 | 0.53622 | 4.8397 | 30.7363 | 4.8676 | 30.9135 | 0.07091 | 1.2478 | 0.0502 | 18.9266 | 0.07054 | 1.2469
JBB | Jimboomba | Jimboomba Bulk Supply | JBB11kVB2_Term | 11 | 5.2853 | 100.6977 | 0.96927 | 6.1557 | 0.53331 | 4.5761 | 29.062 | 4.5969 | 29.1943 | 0.05637 | 1.3216 | 0.03566 | 18.9967 | 0.056 | 1.3207
JDL | Jindalee | Richlands Bulk Supply | JDL33kVB1_Term | 33 | 12.3786 | 707.5303 | 2.6725 | 50.9173 | 1.5031 | 10.6985 | 203.8332 | 10.7305 | 204.444 | 0.27739 | 1.6709 | 2.847 | 19.9365 | 0.27848 | 1.6815
JDL | Jindalee | Richlands Bulk Supply | JDL33kVB2_Term | 33 | 12.3732 | 707.2223 | 2.6721 | 50.9103 | 1.503 | 10.6939 | 203.7465 | 10.7258 | 204.3542 | 0.27762 | 1.6716 | 2.8507 | 19.9378 | 0.27871 | 1.6822
JDL | Jindalee | Richlands Bulk Supply | JDL11kVB1_Term | 11 | 9.7786 | 186.307 | 1.9112 | 12.1376 | 1.0599 | 8.4471 | 53.6465 | 8.5095 | 54.0424 | 0.04546 | 0.71326 | 0.02426 | 9.5422 | 0.04558 | 0.71443
JDL | Jindalee | Richlands Bulk Supply | JDL11kVB2_Term | 11 | 9.7786 | 186.307 | 1.9112 | 12.1376 | 1.0599 | 8.4471 | 53.6465 | 8.5095 | 54.0424 | 0.04546 | 0.71326 | 0.02426 | 9.5422 | 0.04558 | 0.71443
KBN | Karrabin | Abermain Bulk Supply | KBN33kVB1_Term | 33 | 8.1752 | 467.2727 | 1.089 | 20.7484 | 0.56239 | 7.3072 | 139.2205 | 6.7864 | 129.2981 | 0.70228 | 2.4663 | 55.5064 | 4.8016 | 0.71298 | 2.4893
KBN | Karrabin | Abermain Bulk Supply | KBN11kVB1_Term | 11 | 8.9359 | 170.2525 | 1.9001 | 12.0674 | 1.0643 | 7.6792 | 48.7696 | 7.8089 | 49.593 | 0.10038 | 0.77555 | 0.02201 | 9.4771 | 0.10157 | 0.77809
KBN | Karrabin | Abermain Bulk Supply | KBN11kVB2_Term | 11 | 8.9359 | 170.2525 | 1.9001 | 12.0674 | 1.0643 | 7.6792 | 48.7696 | 7.8089 | 49.593 | 0.10038 | 0.77555 | 0.02201 | 9.4771 | 0.10157 | 0.77809
KBR | Kalbar | Raceview Bulk Supply | KBR33kVB1A_Term | 33 | 2.5442 | 145.4205 | 0.89713 | 17.0926 | 0.54076 | 2.142 | 40.8102 | 2.2944 | 43.7141 | 3.464 | 7.4768 | 6.7286 | 53.8062 | 3.4643 | 7.4799
KBR | Kalbar | Raceview Bulk Supply | KBR33kVB4_Term | 33 | 2.5433 | 145.3701 | 0.8971 | 17.0921 | 0.54077 | 2.1412 | 40.7948 | 2.2937 | 43.7007 | 3.4675 | 7.4783 | 6.7337 | 53.8032 | 3.4679 | 7.4814
KBR | Kalbar | Raceview Bulk Supply | KBR11kVB2_Term | 11 | 3.7537 | 71.5168 | 0.92892 | 5.8994 | 0.52848 | 3.2024 | 20.3382 | 3.3189 | 21.078 | 0.43625 | 1.8099 | 0.05097 | 18.93 | 0.43629 | 1.8102
KCY | Kilcoy | Beerwah Bulk Supply | KCY33kVB1_Term | 33 | 1.6618 | 94.9834 | 0.61218 | 11.6636 | 0.39551 | 1.3528 | 25.7749 | 1.4301 | 27.2474 | 4.9432 | 11.6045 | 16.0247 | 74.9955 | 5.7271 | 12.5889
KCY | Kilcoy | Beerwah Bulk Supply | KCY11kVB2_Term | 11 | 4.2718 | 81.3892 | 4.5855 | 29.122 | 6.0245 | 4.3867 | 27.8593 | 4.8806 | 30.9958 | 0.38248 | 1.5902 | 0.03965 | 1.0097 | 0.48157 | 1.8809
KLG | Kalangur | Griffin Bulk Supply | KLG33kVB1_Term | 33 | 11.6509 | 665.9365 | 1.9782 | 37.6888 | 1.0811 | 10.0358 | 191.2086 | 10.1577 | 193.5305 | 0.25763 | 1.7807 | 0.75293 | 28.2015 | 0.25755 | 1.7835
KLG | Kalangur | Griffin Bulk Supply | KLG11kVB1_Term | 11 | 12.0692 | 229.9488 | 2.789 | 17.7127 | 1.5766 | 10.4174 | 66.1591 | 10.5408 | 66.943 | 0.04951 | 0.57683 | 0.02159 | 6.3611 | 0.0495 | 0.57714
KLG | Kalangur | Griffin Bulk Supply | KLG11kVB2_Term | 11 | 12.0692 | 229.9488 | 2.789 | 17.7127 | 1.5766 | 10.4174 | 66.1591 | 10.5408 | 66.943 | 0.04951 | 0.57683 | 0.02159 | 6.3611 | 0.0495 | 0.57714
KLG | Kalangur | Griffin Bulk Supply | KLG11kVB3_Term | 11 | 12.0692 | 229.9488 | 2.789 | 17.7127 | 1.5766 | 10.4174 | 66.1591 | 10.5408 | 66.943 | 0.04951 | 0.57683 | 0.02159 | 6.3611 | 0.0495 | 0.57714
KMR | Kenmore | Tennyson Bulk Supply | KMR33kVB1_Term | 33 | 10.5793 | 604.6864 | 2.3777 | 45.3006 | 1.3371 | 9.0198 | 171.8511 | 9.3283 | 177.7275 | 0.61337 | 1.8844 | 1.5945 | 22.5274 | 0.61397 | 1.8894
KMR | Kenmore | Tennyson Bulk Supply | KMR11kVB3_Term | 11 | 9.4618 | 180.2715 | 1.9116 | 12.1403 | 1.063 | 8.1493 | 51.755 | 8.267 | 52.5028 | 0.08658 | 0.73348 | 0.01842 | 9.4979 | 0.08664 | 0.73404
KMR | Kenmore | Tennyson Bulk Supply | KMR11kVB4_Term | 11 | 9.4618 | 180.2715 | 1.9116 | 12.1403 | 1.063 | 8.1493 | 51.755 | 8.267 | 52.5028 | 0.08658 | 0.73348 | 0.01842 | 9.4979 | 0.08664 | 0.73404
KRA | Kirra | Burleigh Head Bulk Supply | KRA33kVB1_Term | 33 | 4.7623 | 272.2028 | 1.0005 | 19.0629 | 0.52443 | 4.3665 | 83.1928 | 3.8847 | 74.0126 | 1.2587 | 4.2193 | 58.9487 | 4.783 | 1.2586 | 4.2193
KRA | Kirra | Burleigh Head Bulk Supply | KRA11kVB1_Term | 11 | 6.4858 | 123.5704 | 1.7928 | 11.3858 | 1.0385 | 5.5605 | 35.3139 | 5.7199 | 36.3265 | 0.17986 | 1.0626 | 0.04 | 9.5641 | 0.17984 | 1.0626
KRA | Kirra | Burleigh Head Bulk Supply | KRA11kVB2_Term | 11 | 6.4858 | 123.5704 | 1.7928 | 11.3858 | 1.0385 | 5.5605 | 35.3139 | 5.7199 | 36.3265 | 0.17986 | 1.0626 | 0.04 | 9.5641 | 0.17984 | 1.0626
KRN | Kedron | Stafford Bulk Supply | KRN33kVB1_Term | 33 | 17.4662 | 998.3278 | 3.0468 | 58.0498 | 1.6714 | 14.9997 | 285.7829 | 15.2356 | 290.2781 | 0.18763 | 1.1855 | 0.19075 | 18.2576 | 0.18842 | 1.1905
KRN | Kedron | Stafford Bulk Supply | KRN11kVB1_Term | 11 | 11.1836 | 213.0757 | 2.2603 | 14.3549 | 1.1547 | 10.2515 | 65.106 | 9.1111 | 57.8635 | 0.04319 | 0.62334 | 9.0245 | 0.48739 | 0.04328 | 0.6239
KRN | Kedron | Stafford Bulk Supply | KRN11kVB2_Term | 11 | 11.1836 | 213.0757 | 2.2603 | 14.3549 | 1.1547 | 10.2515 | 65.106 | 9.1111 | 57.8635 | 0.04319 | 0.62334 | 9.0245 | 0.48739 | 0.04328 | 0.6239
KSN | Kingston | Loganlea Bulk Supply | KSN33kVB1_Term | 33 | 15.7377 | 899.5296 | 2.958 | 56.3573 | 1.6325 | 13.5331 | 257.8403 | 13.7514 | 261.9991 | 0.23256 | 1.3124 | 0.67253 | 18.6158 | 0.23278 | 1.3146
KSN | Kingston | Loganlea Bulk Supply | KSN11kVB1_Term | 11 | 10.5721 | 201.426 | 1.9405 | 12.324 | 1.0683 | 9.1372 | 58.029 | 9.202 | 58.4403 | 0.04272 | 0.65996 | 0.01688 | 9.4885 | 0.04274 | 0.66021
KSN | Kingston | Loganlea Bulk Supply | KSN11kVB2_Term | 11 | 10.5721 | 201.426 | 1.9405 | 12.324 | 1.0683 | 9.1372 | 58.029 | 9.202 | 58.4403 | 0.04272 | 0.65996 | 0.01688 | 9.4885 | 0.04274 | 0.66021
KVG | Kelvin Grove | Ashgrove West Bulk Supply | 43350 KELVGR1D | 110 | 19.4136 | 3698.7958 | 20.0282 | 1271.9631 | 20.7282 | 20.8819 | 1326.1762 | 18.4838 | 1173.8757 | 0.69037 | 3.5328 | 1.2956 | 3.0287 | 0.69624 | 3.5565
KVG | Kelvin Grove | Ashgrove West Bulk Supply | KVG11kVB1_Term | 11 | 8.9545 | 170.6068 | 3.3487 | 21.2669 | 2.0589 | 7.8896 | 50.1056 | 7.7534 | 49.2409 | 0.02169 | 0.7801 | 0.47025 | 4.679 | 0.02175 | 0.78034
KVG | Kelvin Grove | Ashgrove West Bulk Supply | KVG11kVB2_Term | 11 | 8.9545 | 170.6068 | 3.3487 | 21.2669 | 2.0589 | 7.8896 | 50.1056 | 7.7534 | 49.2409 | 0.02169 | 0.7801 | 0.47025 | 4.679 | 0.02175 | 0.78034
KVG | Kelvin Grove | Ashgrove West Bulk Supply | KVG11kVB4_Term | 11 | 9.0385 | 172.2058 | 3.3564 | 21.3161 | 2.0604 | 7.9616 | 50.5627 | 7.8257 | 49.7 | 0.02171 | 0.77285 | 0.47025 | 4.679 | 0.02177 | 0.77309
KVG | Kelvin Grove | Ashgrove West Bulk Supply | KVG11kVB5_Term | 11 | 9.0385 | 172.2058 | 3.3564 | 21.3161 | 2.0604 | 7.9616 | 50.5627 | 7.8257 | 49.7 | 0.02171 | 0.77285 | 0.47025 | 4.679 | 0.02177 | 0.77309
KWA | Kawana | Palmwood Bulk Supply | 43340 KAWANA1D | 132 | 8.7247 | 1994.735 | 9.3551 | 712.9503 | 10.1581 | 9.0549 | 690.079 | 9.1272 | 695.5894 | 1.9676 | 9.4066 | 1.4279 | 7.467 | 1.9507 | 9.4775
KWA | Kawana | Palmwood Bulk Supply | KWA11kVB1_Term | 11 | 9.9032 | 188.6805 | 1.9381 | 12.3087 | 1.0745 | 8.6145 | 54.7093 | 8.5662 | 54.4025 | 0.0378 | 0.70454 | 0.9405 | 9.358 | 0.03768 | 0.70503
KWA | Kawana | Palmwood Bulk Supply | KWA11kVB2_Term | 11 | 9.8495 | 187.6584 | 1.9367 | 12.3 | 1.0743 | 8.568 | 54.4141 | 8.52 | 54.1091 | 0.0382 | 0.70836 | 0.9405 | 9.358 | 0.03808 | 0.70886
KWH | Kenilworth | Nambour Bulk Supply | KWH33kVB1_Term | 33 | 1.6892 | 96.5532 | 0.73299 | 13.9653 | 0.46211 | 1.4012 | 26.6963 | 1.5565 | 29.6548 | 6.4954 | 10.5729 | 10.5265 | 61.3536 | 6.4922 | 10.5793
KWH | Kenilworth | Nambour Bulk Supply | KWH11kVB1_Term | 11 | 2.3937 | 45.6069 | 0.83338 | 5.2927 | 0.50108 | 2.0173 | 12.8114 | 2.1563 | 13.6943 | 0.90206 | 2.776 | 0.1957 | 19.5198 | 0.90171 | 2.7767
LBH | Landsborough | Beerwah Bulk Supply | LBH33kVB1_Term | 33 | 4.1546 | 237.467 | 1.3294 | 25.3291 | 0.78594 | 3.4893 | 66.4792 | 3.737 | 71.2002 | 2.1311 | 4.5733 | 3.4049 | 37.5156 | 2.1284 | 4.5884
LBH | Landsborough | Beerwah Bulk Supply | LBH11kVB1_Term | 11 | 4.4161 | 84.1374 | 0.94745 | 6.0171 | 0.53018 | 3.7883 | 24.0592 | 3.8747 | 24.6076 | 0.27244 | 1.5586 | 0.03566 | 18.9979 | 0.27215 | 1.5603
LBS | Lyton Bulk | Lytton Bulk Supply | 43390 LYTTBS1D | 110 | 19.2352 | 3664.7995 | 20.7337 | 1316.7649 | 22.7165 | 20.0916 | 1275.9846 | 20.1539 | 1279.9463 | 0.43152 | 3.6081 | 0.31875 | 2.7935 | 0.43587 | 3.6421
LBS | Lyton Bulk | Lytton Bulk Supply | LBS33kVB1_Term | 33 | 16.6262 | 950.3141 | 2.2194 | 42.2852 | 1.1905 | 14.3618 | 273.6298 | 14.4258 | 274.8489 | 0.07035 | 1.2592 | 0.02197 | 25.8221 | 0.07074 | 1.2623
LBS | Lyton Bulk | Lytton Bulk Supply | LBS33kVB3_Term | 33 | 9.7663 | 558.2176 | 1.0856 | 20.6843 | 0.57517 | 8.444 | 160.8791 | 8.4696 | 161.3676 | 0.09854 | 2.1448 | 0.02792 | 53.6513 | 0.09894 | 2.1479
LBS | Lyton Bulk | Lytton Bulk Supply | LBS11kVB1_Term | 11 | 10.6836 | 203.5507 | 1.9422 | 12.3349 | 1.0685 | 9.247 | 58.7262 | 9.2838 | 58.9598 | 0.02446 | 0.65378 | 0.01664 | 9.4882 | 0.0245 | 0.65412
LBS | Lyton Bulk | Lytton Bulk Supply | LBS11kVB2_Term | 11 | 10.6836 | 203.5507 | 1.9422 | 12.3349 | 1.0685 | 9.247 | 58.7262 | 9.2838 | 58.9598 | 0.02446 | 0.65378 | 0.01664 | 9.4882 | 0.0245 | 0.65412
LDM | Lindum | Lytton Bulk Supply | LDM33kVB1_Term | 33 | 9.2341 | 527.8028 | 1.0708 | 20.4018 | 0.56872 | 7.9809 | 152.0563 | 8.0126 | 152.6605 | 0.13984 | 2.2665 | 0.25504 | 54.2081 | 0.14023 | 2.2696
LDR | Ladbrador | Molendinar Bulk Supply | LDR33kVB1_Term | 33 | 12.0958 | 691.3692 | 2.5745 | 49.0506 | 1.4423 | 10.3894 | 197.9452 | 10.5723 | 201.4293 | 0.37583 | 1.6924 | 1.7832 | 20.9118 | 0.37594 | 1.699
LDR | Ladbrador | Molendinar Bulk Supply | LDR11kVB1_Term | 11 | 9.9801 | 190.1467 | 1.9237 | 12.217 | 1.0647 | 8.6126 | 54.6972 | 8.6973 | 55.2352 | 0.05932 | 0.69785 | 0.01897 | 9.5033 | 0.05934 | 0.69859
LDR | Ladbrador | Molendinar Bulk Supply | LDR11kVB2_Term | 11 | 9.9801 | 190.1467 | 1.9237 | 12.217 | 1.0647 | 8.6126 | 54.6972 | 8.6973 | 55.2352 | 0.05932 | 0.69785 | 0.01897 | 9.5033 | 0.05934 | 0.69859
LGL | Loganlea Bulk | Loganlea Bulk Supply | LGL33kVB1_Term | 33 | 25.3216 | 1447.3224 | 3.4245 | 65.2446 | 1.8389 | 21.8682 | 416.6461 | 21.9708 | 418.6004 | 0.04775 | 0.82698 | 0.00896 | 16.719 | 0.04797 | 0.82921
LGL | Loganlea | Loganlea Bulk Supply | LGL11kVB1_Term | 11 | 11.3438 | 216.1292 | 1.9548 | 12.4147 | 1.0697 | 9.818 | 62.3529 | 9.8553 | 62.5897 | 0.02337 | 0.61591 | 0.01807 | 9.4978 | 0.0234 | 0.61615
LGL | Loganlea | Loganlea Bulk Supply | LGL11kVB2_Term | 11 | 11.3438 | 216.1292 | 1.9548 | 12.4147 | 1.0697 | 9.818 | 62.3529 | 9.8553 | 62.5897 | 0.02337 | 0.61591 | 0.01807 | 9.4978 | 0.0234 | 0.61615
LGV | Logan Village | Jimboomba Bulk Supply | LGV33kVB1_Term | 33 | 3.6401 | 208.0567 | 0.8773 | 16.7147 | 0.4952 | 3.1319 | 59.6711 | 3.2193 | 61.3349 | 1.3444 | 5.6031 | 2.7239 | 60.3612 | 1.3087 | 5.5576
LGV | Logan Village | Jimboomba Bulk Supply | LGV11kVB1_Term | 11 | 4.3521 | 82.9179 | 0.9461 | 6.0086 | 0.52404 | 3.7914 | 24.0787 | 3.8427 | 24.4044 | 0.17758 | 1.5966 | 0.03657 | 19.0052 | 0.16358 | 1.5636
LGV | Logan Village | Jimboomba Bulk Supply | LGVBESS11kVB1_Term | 11 | 4.3521 | 82.9179 | 0.9461 | 6.0086 | 0.52404 | 3.7914 | 24.0787 | 3.8427 | 24.4044 | 0.17758 | 1.5966 | 0.03657 | 19.0052 | 0.16358 | 1.5636
LHM | Loganholme | Beenleigh Bulk Supply (Including Bay Islands) | LHM33kVB1_Term | 33 | 8.5042 | 486.0811 | 2.2143 | 42.1889 | 1.2707 | 7.2714 | 138.538 | 7.5053 | 142.9951 | 0.63381 | 2.3914 | 1.4918 | 23.5847 | 0.6334 | 2.3937
LHM | Loganholme | Beenleigh Bulk Supply (Including Bay Islands) | LHM11kVB1_Term | 11 | 10.8153 | 206.0599 | 2.7517 | 17.4755 | 1.575 | 9.295 | 59.0315 | 9.4993 | 60.3286 | 0.09087 | 0.64203 | 0.02129 | 6.3588 | 0.09083 | 0.64228
LHM | Loganholme | Beenleigh Bulk Supply (Including Bay Islands) | LHM11kVB2_Term | 11 | 10.8153 | 206.0599 | 2.7517 | 17.4755 | 1.575 | 9.295 | 59.0315 | 9.4993 | 60.3286 | 0.09087 | 0.64203 | 0.02129 | 6.3588 | 0.09083 | 0.64228
LHM | Loganholme | Beenleigh Bulk Supply (Including Bay Islands) | LHM11kVB3_Term | 11 | 10.8153 | 206.0599 | 2.7517 | 17.4755 | 1.575 | 9.295 | 59.0315 | 9.4993 | 60.3286 | 0.09087 | 0.64203 | 0.02129 | 6.3588 | 0.09083 | 0.64228
LLY | Laidley | Lockrose Bulk Supply | LLY33kVB1_Term | 33 | 3.1935 | 182.5313 | 1.302 | 24.8065 | 0.81048 | 2.6858 | 51.1721 | 2.9047 | 55.3426 | 2.8201 | 5.9276 | 5.0683 | 35.2559 | 2.8153 | 5.9168
LLY | Laidley | Lockrose Bulk Supply | LLY11kVB1_Term | 11 | 3.0838 | 58.7551 | 3.4846 | 22.1305 | 3.9979 | 3.2321 | 20.5265 | 3.4373 | 21.83 | 0.429 | 2.2249 | 0.11566 | 1.488 | 0.42847 | 2.2237
LLY | Laidley | Lockrose Bulk Supply | LLY11kVB2_Term | 11 | 3.1156 | 59.3598 | 3.5247 | 22.3851 | 4.0502 | 3.268 | 20.7543 | 3.4767 | 22.0801 | 0.42907 | 2.2014 | 0.11573 | 1.4656 | 0.42854 | 2.2002
LMD | Lomandra Drive | Nudgee Bulk Supply | LMD33kVB1_Term | 33 | 14.3158 | 818.2599 | 2.8862 | 54.9894 | 1.6092 | 12.3571 | 235.434 | 12.4309 | 236.8402 | 0.19996 | 1.4506 | 1.6629 | 18.7825 | 0.19964 | 1.4581
LMD | Lomandra Drive | Nudgee Bulk Supply | LMD11kVB1_Term | 11 | 10.6634 | 203.1643 | 1.9412 | 12.3286 | 1.0685 | 9.22 | 58.555 | 9.269 | 58.8661 | 0.03237 | 0.65448 | 0.0168 | 9.4883 | 0.03233 | 0.65531
LMD | Lomandra Drive | Nudgee Bulk Supply | LMD11kVB2_Term | 11 | 10.6634 | 203.1643 | 1.9412 | 12.3286 | 1.0685 | 9.22 | 58.555 | 9.269 | 58.8661 | 0.03237 | 0.65448 | 0.0168 | 9.4883 | 0.03233 | 0.65531
LRE | Lockrose Bulk | Lockrose Bulk Supply | 40780 LOCROS1D | 110 | 6.2849 | 1197.4407 | 7.8467 | 498.3335 | 10.3354 | 6.9688 | 442.5788 | 8.0115 | 508.801 | 3.9598 | 10.389 | 0.27937 | 4.6842 | 3.9389 | 10.3598
LRE | Lockrose Bulk | Lockrose Bulk Supply | LRE33kVB1_Term | 33 | 11.1981 | 640.059 | 2.8941 | 55.1398 | 1.6535 | 9.64 | 183.667 | 9.8818 | 188.2732 | 0.38969 | 1.831 | 0.96579 | 18.009 | 0.38491 | 1.8201
LRE | Lockrose | Lockrose Bulk Supply | LRE11kVB1_Term | 11 | 5.1414 | 97.9564 | 0.96148 | 6.1062 | 0.52996 | 4.4458 | 28.2343 | 4.479 | 28.4453 | 0.09224 | 1.3559 | 0.04808 | 19.0907 | 0.09171 | 1.3547
LTA | Lota | Lytton Bulk Supply | LTA33kVB1_Term | 33 | 5.9596 | 340.6395 | 0.94875 | 18.0762 | 0.51516 | 5.1257 | 97.6573 | 5.2049 | 99.1664 | 0.65229 | 3.4575 | 1.6198 | 59.3222 | 0.65268 | 3.4606
LTA | Lota | Lytton Bulk Supply | LTA11kVB1_Term | 11 | 7.5285 | 143.4365 | 1.8455 | 11.7204 | 1.0513 | 6.4904 | 41.2194 | 6.589 | 41.8455 | 0.09364 | 0.9237 | 0.02127 | 9.5127 | 0.09369 | 0.92404
LTA | Lota | Lytton Bulk Supply | LTA11kVB2_Term | 11 | 7.5285 | 143.4365 | 1.8455 | 11.7204 | 1.0513 | 6.4904 | 41.2194 | 6.589 | 41.8455 | 0.09364 | 0.9237 | 0.02127 | 9.5127 | 0.09369 | 0.92404
LTN | Lawnton | Brendale Bulk Supply | LTN33kVB1_Term | 33 | 11.6064 | 663.3971 | 2.5704 | 48.973 | 1.4473 | 9.9354 | 189.2939 | 10.1689 | 193.7433 | 0.39098 | 1.7633 | 0.99969 | 20.8648 | 0.39155 | 1.7727
LTN | Lawnton | Brendale Bulk Supply | LTN11kVB1_Term | 11 | 12.5389 | 238.8991 | 2.4196 | 15.3669 | 1.2923 | 11.346 | 72.0566 | 10.3028 | 65.4314 | 0.06094 | 0.55392 | 7.0313 | 3.7746 | 0.0613 | 0.55826
LWD | Lowood | Lockrose Bulk Supply | LWD33kVB1_Term | 33 | 2.6349 | 150.6076 | 1.7796 | 33.9068 | 1.3087 | 2.3176 | 44.1552 | 2.4843 | 47.3327 | 2.5161 | 7.5471 | 2.9793 | 19.5595 | 2.3515 | 7.3479
LWD | Lowood | Lockrose Bulk Supply | LWD11kVB1_Term | 11 | 2.8644 | 54.5737 | 3.3036 | 20.9808 | 3.8531 | 3.0777 | 19.5458 | 3.2139 | 20.4111 | 0.38913 | 2.4082 | 0.10956 | 1.4911 | 0.37084 | 2.3861
LYT | Lytton | Lytton Bulk Supply | LYT33kVB1_Term | 33 | 15.1499 | 865.9354 | 2.1717 | 41.377 | 1.171 | 13.0879 | 249.359 | 13.1501 | 250.5435 | 0.11465 | 1.3793 | 0.74534 | 26.1882 | 0.11504 | 1.3824
LYT | Lytton | Lytton Bulk Supply | LYT11kVB1_Term | 11 | 6.2515 | 119.1074 | 0.99058 | 6.291 | 0.53791 | 5.403 | 34.3136 | 5.4367 | 34.5274 | 0.07796 | 1.1154 | 0.09926 | 18.9359 | 0.078 | 1.1157
LYT | Lytton | Lytton Bulk Supply | LYT11kVB2_Term | 11 | 10.2811 | 195.8808 | 1.9276 | 12.2416 | 1.0637 | 8.8949 | 56.49 | 8.9398 | 56.7756 | 0.03122 | 0.67914 | 0.01998 | 9.5196 | 0.03127 | 0.67948
MAI | Miami | Burleigh Head Bulk Supply | MAI33kVB1_Term | 33 | 5.9471 | 339.9223 | 1.0786 | 20.5493 | 0.55941 | 5.4125 | 103.1218 | 4.8901 | 93.1687 | 0.95469 | 3.3941 | 55.5142 | 3.4215 | 0.95458 | 3.3942
MAI | Miami | Burleigh Head Bulk Supply | MAI11kVB1_Term | 11 | 8.972 | 170.9389 | 2.2104 | 14.038 | 1.149 | 8.3272 | 52.8849 | 7.2153 | 45.8236 | 0.13296 | 0.76761 | 9.0269 | 0.37096 | 0.13295 | 0.76762
MBG | Marburg | Abermain Bulk Supply | MBG33kVB1_Term | 33 | 3.2337 | 184.8295 | 0.87461 | 16.6635 | 0.49135 | 2.9571 | 56.3411 | 2.6404 | 50.3062 | 3.4331 | 5.4994 | 59.4186 | 16.7922 | 3.4574 | 5.5299
MBG | Marburg | Abermain Bulk Supply | MBG11kVB1_Term | 11 | 3.0333 | 57.7916 | 3.4062 | 21.6323 | 3.885 | 3.1458 | 19.9786 | 3.382 | 21.4785 | 0.55652 | 2.2356 | 0.17506 | 1.5433 | 0.55922 | 2.2389
MCN | Mt Cotton | Cleveland Bulk Supply | MCN33kVB1_Term | 33 | 6.8655 | 392.4176 | 1.6046 | 30.5718 | 0.90746 | 5.8815 | 112.0568 | 6.0372 | 115.0233 | 0.77373 | 2.9548 | 2.4756 | 33.0856 | 0.77292 | 2.9585
MCN | Mt Cotton | Cleveland Bulk Supply | MCN11kVB1_Term | 11 | 3.5311 | 67.2755 | 3.7979 | 24.12 | 4.1092 | 3.6635 | 23.2662 | 3.7043 | 23.5253 | 0.26342 | 1.962 | 0.17745 | 1.552 | 0.26333 | 1.9624
MCN | Mt Cotton | Cleveland Bulk Supply | MCN11kVB2_Term | 11 | 3.5734 | 68.082 | 3.8454 | 24.4217 | 4.1629 | 3.6987 | 23.4897 | 3.7598 | 23.8777 | 0.1954 | 1.9463 | 0.10943 | 1.5371 | 0.19531 | 1.9468
MDH | Meeandah Bulk | Meeandah Bulk Supply | 43440 MEANDH1D | 110 | 11.3637 | 2165.0799 | 13.9278 | 884.5362 | 18.1153 | 13.6132 | 864.553 | 13.1121 | 832.733 | 1.0159 | 6.0644 | 0.65993 | 2.6427 | 1.0122 | 6.1016
MDH | Meeandah Bulk | Meeandah Bulk Supply | 43441 MEANDH2D | 110 | 11.3676 | 2165.8255 | 13.9321 | 884.8042 | 18.1194 | 13.6228 | 865.1661 | 13.11 | 832.5943 | 1.0042 | 6.0642 | 0.65992 | 2.6427 | 1.0005 | 6.1014
MDH | Meeandah Bulk | Meeandah Bulk Supply | MDH33kVB1_Term | 33 | 14.5083 | 829.2629 | 2.2127 | 42.1567 | 1.1989 | 12.5222 | 238.5808 | 12.6074 | 240.2036 | 0.10735 | 1.4409 | 0.01949 | 25.5355 | 0.10702 | 1.4442
MDH | Meeandah | Meeandah Bulk Supply | MDH11kVB1_Term | 11 | 10.3137 | 196.5021 | 1.9328 | 12.2752 | 1.0666 | 8.9247 | 56.6795 | 8.9662 | 56.9428 | 0.02856 | 0.67689 | 0.01663 | 9.491 | 0.02852 | 0.67726
MDH | Meeandah | Meeandah Bulk Supply | MDH11kVB2_Term | 11 | 10.3137 | 196.5021 | 1.9328 | 12.2752 | 1.0666 | 8.9247 | 56.6795 | 8.9662 | 56.9428 | 0.02856 | 0.67689 | 0.01663 | 9.491 | 0.02852 | 0.67726
MDH | Meeandah | Meeandah Bulk Supply | MDH11kVB3_Term | 11 | 10.3137 | 196.5021 | 1.9328 | 12.2752 | 1.0666 | 8.9247 | 56.6795 | 8.9662 | 56.9428 | 0.02856 | 0.67689 | 0.01663 | 9.491 | 0.02852 | 0.67726
MDR | Molendinar Bulk | Molendinar Bulk Supply | MDR33kVB1_Term | 33 | 25.0908 | 1434.1314 | 3.3455 | 63.741 | 1.7969 | 21.6487 | 412.4623 | 21.7407 | 414.2168 | 0.04473 | 0.83454 | 0.00514 | 17.13 | 0.04439 | 0.83876
MDR | Molendinar | Molendinar Bulk Supply | MDR11kVB1_Term | 11 | 7.4881 | 142.6681 | 4.1951 | 26.6421 | 2.9121 | 6.74 | 42.8048 | 6.5508 | 41.6031 | 0.02203 | 0.93319 | 0.3135 | 3.1193 | 0.02204 | 0.93329
MDR | Molendinar | Molendinar Bulk Supply | MDR11kVB2_Term | 11 | 7.4881 | 142.6681 | 4.1951 | 26.6421 | 2.9121 | 6.74 | 42.8048 | 6.5508 | 41.6031 | 0.02203 | 0.93319 | 0.3135 | 3.1193 | 0.02204 | 0.93329
MDR | Molendinar | Molendinar Bulk Supply | MDR11kVB3_Term | 11 | 7.4881 | 142.6681 | 4.1951 | 26.6421 | 2.9121 | 6.74 | 42.8048 | 6.5508 | 41.6031 | 0.02203 | 0.93319 | 0.3135 | 3.1193 | 0.02204 | 0.93329
MDR | Molendinar | Molendinar Bulk Supply | MDR11kVB4_Term | 11 | 7.4881 | 142.6681 | 4.1951 | 26.6421 | 2.9121 | 6.74 | 42.8048 | 6.5508 | 41.6031 | 0.02203 | 0.93319 | 0.3135 | 3.1193 | 0.02204 | 0.93329
MFD | Morayfield | Caboolture Bulk Supply | MFD33kVB1_Term | 33 | 6.6395 | 379.4964 | 2.0083 | 38.2641 | 1.1847 | 5.6743 | 108.1094 | 5.8557 | 111.5659 | 0.8442 | 3.0422 | 2.5585 | 24.9192 | 0.83637 | 3.0624
MFD | Morayfield | Caboolture Bulk Supply | MFD11kVB1_Term | 11 | 8.2971 | 158.0808 | 1.8786 | 11.9307 | 1.0539 | 7.1664 | 45.5129 | 7.2933 | 46.3189 | 0.11222 | 0.83462 | 0.03158 | 9.4918 | 0.1081 | 0.82893
MFD | Morayfield | Caboolture Bulk Supply | MFD11kVB2_Term | 11 | 8.2971 | 158.0808 | 1.8786 | 11.9307 | 1.0539 | 7.1664 | 45.5129 | 7.2933 | 46.3189 | 0.11222 | 0.83462 | 0.03158 | 9.4918 | 0.1081 | 0.82893
MFD | Morayfield | Caboolture Bulk Supply | MFDBESS11kVB1_Term | 11 | 8.2971 | 158.0808 | 1.8786 | 11.9307 | 1.0539 | 7.1664 | 45.5129 | 7.2933 | 46.3189 | 0.11222 | 0.83462 | 0.03158 | 9.4918 | 0.1081 | 0.82893
MFN | Morayfield Nth | Caboolture Bulk Supply | MFN33kVB1_Term | 33 | 14.2846 | 816.4756 | 3.0029 | 57.2129 | 1.6956 | 12.2136 | 232.7011 | 12.3538 | 235.3708 | 0.22901 | 1.4495 | 1.2198 | 17.9461 | 0.2299 | 1.4787
MFN | Morayfield Nth | Caboolture Bulk Supply | MFN11kVB1_Term | 11 | 11.5705 | 220.4479 | 1.9541 | 12.4103 | 1.1019 | 9.7151 | 61.699 | 9.779 | 62.105 | 0.03689 | 0.60275 | 0.01806 | 9.484 | 0.03971 | 0.6397
MFN | Morayfield Nth | Caboolture Bulk Supply | MFN11kVB2_Term | 11 | 11.5705 | 220.4479 | 1.9541 | 12.4103 | 1.1019 | 9.7151 | 61.699 | 9.779 | 62.105 | 0.03689 | 0.60275 | 0.01806 | 9.484 | 0.03971 | 0.6397
MGB | Mudgeeraba Bulk | Mudgeeraba Bulk Supply | MGB33kVB1_Term | 33 | 10.7287 | 613.2248 | 1.1817 | 22.5151 | 0.62529 | 9.2845 | 176.8932 | 9.3084 | 177.3481 | 0.07642 | 1.953 | 0.00395 | 49.3255 | 0.07631 | 1.953
MGL | Moggill | Abermain Bulk Supply | MGL33kVB1_Term | 33 | 5.6456 | 322.6923 | 1.0262 | 19.5524 | 0.53836 | 5.125 | 97.6451 | 4.6512 | 88.6171 | 1.0986 | 3.5471 | 56.8014 | 9.4833 | 1.0991 | 3.5515
MGL | Moggill | Abermain Bulk Supply | MGL11kVB1_Term | 11 | 7.6912 | 146.5366 | 1.8588 | 11.805 | 1.056 | 6.6006 | 41.9197 | 6.7583 | 42.9209 | 0.14462 | 0.897 | 0.02209 | 9.4796 | 0.14467 | 0.89749
MGL | Moggill | Abermain Bulk Supply | MGL11kVB2_Term | 11 | 7.6912 | 146.5366 | 1.8588 | 11.805 | 1.056 | 6.6006 | 41.9197 | 6.7583 | 42.9209 | 0.14462 | 0.897 | 0.02209 | 9.4796 | 0.14467 | 0.89749
MGP | Mudgeeraba Package | Mudgeeraba Bulk Supply | MGP33kVB1_Term | 33 | 7.4058 | 423.2954 | 1.0756 | 20.492 | 0.57958 | 6.385 | 121.6513 | 6.4549 | 122.9825 | 0.40557 | 2.8022 | 1.0304 | 52.8537 | 0.40546 | 2.8023
MGP | Mudgeeraba Package | Mudgeeraba Bulk Supply | MGP11kVB1_Term | 11 | 4.6694 | 88.9647 | 0.94855 | 6.0241 | 0.52772 | 4.0315 | 25.6035 | 4.0733 | 25.8687 | 0.12993 | 1.4912 | 0.08487 | 19.1209 | 0.12992 | 1.4912
MGP | Mudgeeraba Package | Mudgeeraba Bulk Supply | MGP11kVB2_Term | 11 | 5.1931 | 98.9409 | 0.96768 | 6.1456 | 0.53348 | 4.4908 | 28.5201 | 4.5196 | 28.7034 | 0.07788 | 1.3437 | 0.0328 | 18.9807 | 0.07787 | 1.3437
MHL | Mango Hill | Griffin Bulk Supply | MHL33kVB1_Term | 33 | 9.5824 | 547.707 | 1.3649 | 26.0045 | 0.73115 | 8.4478 | 160.9517 | 8.1303 | 154.9026 | 0.52611 | 2.1234 | 27.2065 | 32.1365 | 0.52546 | 2.1325
MHL | Mango Hill | Griffin Bulk Supply | MHL33kVB2_Term | 33 | 9.5529 | 546.0226 | 1.8759 | 35.7412 | 1.0395 | 8.2029 | 156.2859 | 8.3652 | 159.3792 | 0.4309 | 2.1516 | 1.0021 | 29.1654 | 0.43081 | 2.1544
MHL | Mango Hill | Griffin Bulk Supply | MHL11kVB1_Term | 11 | 5.615 | 106.98 | 0.97777 | 6.2097 | 0.53563 | 4.8494 | 30.7981 | 4.8869 | 31.0359 | 0.09235 | 1.241 | 0.0339 | 18.9548 | 0.09228 | 1.242
MHL | Mango Hill | Griffin Bulk Supply | MHL11kVB2_Term | 11 | 9.1659 | 174.6339 | 1.9031 | 12.0863 | 1.0617 | 7.9116 | 50.2457 | 7.9963 | 50.7834 | 0.06476 | 0.75958 | 0.01688 | 9.4945 | 0.06475 | 0.75989
MHL | Mango Hill | Griffin Bulk Supply | MHL11kVB3_Term | 11 | 9.1659 | 174.6339 | 1.9031 | 12.0863 | 1.0617 | 7.9116 | 50.2457 | 7.9963 | 50.7834 | 0.06476 | 0.75958 | 0.01688 | 9.4945 | 0.06475 | 0.75989
MLB | Mooloolaba | Palmwood Bulk Supply | 43480 MOOLBA1D | 132 | 11.0205 | 2519.6202 | 12.3559 | 941.6421 | 14.1669 | 11.972 | 912.3925 | 11.7682 | 896.8592 | 1.1754 | 7.5169 | 0.92469 | 5.0069 | 1.1538 | 7.5723
MLB | Mooloolaba | Palmwood Bulk Supply | MLB11kVB1_Term | 11 | 9.1722 | 174.7544 | 1.9934 | 12.6599 | 1.1119 | 8.0193 | 50.9292 | 7.982 | 50.6922 | 0.05176 | 0.76001 | 0.90001 | 8.955 | 0.04908 | 0.75263
MLB | Mooloolaba | Palmwood Bulk Supply | MLB11kVB2_Term | 11 | 10.0723 | 191.903 | 1.9425 | 12.3364 | 1.0751 | 8.7649 | 55.6647 | 8.7092 | 55.3111 | 0.0323 | 0.69295 | 0.9405 | 9.358 | 0.03215 | 0.69333
MLS | McLachlan St | Belmont Bulk Supply | 43430 MCLACS1D | 110 | 22.8615 | 4355.691 | 27.7133 | 1760.0298 | 35.7381 | 27.4628 | 1744.1193 | 25.756 | 1635.7282 | 0.33104 | 3.0395 | 0.34261 | 1.3792 | 0.33645 | 3.0801
MLS | McLachlan St | Belmont Bulk Supply | MLS11kVB1_Term | 11 | 9.6726 | 184.2885 | 3.407 | 21.6373 | 2.0841 | 8.4608 | 53.7335 | 8.3145 | 52.804 | 0.01742 | 0.7224 | 0.47025 | 4.679 | 0.01745 | 0.73246
MLS | McLachlan St | Belmont Bulk Supply | MLS11kVB2_Term | 11 | 9.6726 | 184.2885 | 3.407 | 21.6373 | 2.0841 | 8.4608 | 53.7335 | 8.3145 | 52.804 | 0.01742 | 0.7224 | 0.47025 | 4.679 | 0.01745 | 0.73246
MLS | McLachlan St | Belmont Bulk Supply | MLS11kVB3_Term | 11 | 9.225 | 175.7605 | 3.3735 | 21.4249 | 2.0651 | 8.1216 | 51.5793 | 7.9785 | 50.67 | 0.01858 | 0.75746 | 0.47025 | 4.679 | 0.01864 | 0.75853
MLS | McLachlan St | Belmont Bulk Supply | MLS11kVB4_Term | 11 | 9.225 | 175.7605 | 3.3735 | 21.4249 | 2.0651 | 8.1216 | 51.5793 | 7.9785 | 50.67 | 0.01858 | 0.75746 | 0.47025 | 4.679 | 0.01864 | 0.75853
MLT | Milton | Ashgrove West Bulk Supply | 43461 MILTON1D | 110 | 20.0239 | 3815.0754 | 20.9973 | 1333.5083 | 22.1762 | 21.4593 | 1362.8484 | 19.6 | 1244.7682 | 0.67026 | 3.4249 | 1.0349 | 2.8224 | 0.6762 | 3.4489
MLT | Milton | Ashgrove West Bulk Supply | MLT11kVB1_Term | 11 | 9.3235 | 177.6368 | 3.3949 | 21.5602 | 2.0346 | 8.3233 | 52.8598 | 8.1877 | 51.9988 | 0.02132 | 0.74921 | 0.47025 | 4.679 | 0.02017 | 0.72589
MLT | Milton | Ashgrove West Bulk Supply | MLT11kVB2_Term | 11 | 9.3235 | 177.6368 | 3.3949 | 21.5602 | 2.0346 | 8.3233 | 52.8598 | 8.1877 | 51.9988 | 0.02132 | 0.74921 | 0.47025 | 4.679 | 0.02017 | 0.72589
MLT | Milton | Ashgrove West Bulk Supply | MLT11kVB3_Term | 11 | 9.3184 | 177.5402 | 3.3824 | 21.4812 | 2.063 | 8.2103 | 52.1424 | 8.0743 | 51.2788 | 0.0213 | 0.74962 | 0.47025 | 4.679 | 0.02124 | 0.74823
MLT | Milton | Ashgrove West Bulk Supply | MLT11kVB4_Term | 11 | 9.3184 | 177.5402 | 3.3824 | 21.4812 | 2.063 | 8.2103 | 52.1424 | 8.0743 | 51.2788 | 0.0213 | 0.74962 | 0.47025 | 4.679 | 0.02124 | 0.74823
MLY | Maleny | Nambour Bulk Supply | MLY33kVB1_Term | 33 | 2.1799 | 124.5968 | 0.82436 | 15.7061 | 0.50582 | 1.8453 | 35.1569 | 1.9615 | 37.3718 | 3.5238 | 8.9469 | 6.9618 | 57.0854 | 3.5206 | 8.9533
MLY | Maleny | Nambour Bulk Supply | MLY11kVB1_Term | 11 | 3.7436 | 71.3246 | 4.6563 | 29.5715 | 6.1507 | 4.3087 | 27.3641 | 4.6227 | 29.358 | 0.4672 | 1.807 | 0.07566 | 0.77228 | 0.46684 | 1.8077
MMC | Merrimac | Mudgeeraba Bulk Supply | 43450 MERRIM1D | 110 | 17.4811 | 3330.5937 | 21.1198 | 1341.2905 | 26.5816 | 21.4337 | 1361.2222 | 18.7589 | 1191.3509 | 0.42839 | 3.9754 | 0.72922 | 1.8437 | 0.42861 | 3.9819
MMC | Merrimac | Mudgeeraba Bulk Supply | MMC11kVB1_Term | 11 | 9.8692 | 188.0332 | 1.9381 | 12.3088 | 1.0744 | 8.596 | 54.5923 | 8.5307 | 54.1774 | 0.02614 | 0.70775 | 0.9405 | 9.358 | 0.02615 | 0.70782
MMC | Merrimac | Mudgeeraba Bulk Supply | MMC11kVB2_Term | 11 | 9.8867 | 188.3665 | 1.9386 | 12.3117 | 1.0745 | 8.6116 | 54.6912 | 8.5454 | 54.2706 | 0.02548 | 0.70652 | 0.9405 | 9.358 | 0.02549 | 0.70659
MRB | Murrumba | Lockrose Bulk Supply | MRB33kVB1_Term | 33 | 2.2986 | 131.3848 | 0.98282 | 18.7252 | 0.62031 | 1.9312 | 36.7935 | 2.0945 | 39.9056 | 4.4201 | 7.9766 | 9.6526 | 45.2993 | 4.4188 | 7.9799
MRB | Murrumba | Lockrose Bulk Supply | MRB11kVB1_Term | 11 | 2.7841 | 53.0433 | 3.2349 | 20.5444 | 3.8516 | 2.9481 | 18.7228 | 3.2174 | 20.4335 | 0.60692 | 2.4353 | 0.11571 | 1.4712 | 0.60677 | 2.4357
MRE | Murrarie | Doboy Bulk Supply | MRE33kVB1_Term | 33 | 20.7627 | 1186.747 | 3.2601 | 62.1142 | 1.7748 | 17.921 | 341.4405 | 17.9769 | 342.5065 | 0.14023 | 1.0002 | 1.8235 | 17.1739 | 0.14007 | 1.0065
MRE | Murrarie | Doboy Bulk Supply | MRE33kVB2_Term | 33 | 20.7227 | 1184.4632 | 3.259 | 62.092 | 1.7744 | 17.8869 | 340.792 | 17.9423 | 341.8459 | 0.14125 | 1.002 | 1.8427 | 17.1749 | 0.14109 | 1.0083
MRE | Murrarie | Doboy Bulk Supply | MRE11kVB1_Term | 11 | 11.431 | 217.7899 | 2.2695 | 14.4131 | 1.1567 | 10.4671 | 66.475 | 9.3213 | 59.1979 | 0.03034 | 0.61071 | 9.02 | 0.48357 | 0.03032 | 0.61141
MRE | Murrarie | Doboy Bulk Supply | MRE11kVB2_Term | 11 | 11.431 | 217.7899 | 2.2695 | 14.4131 | 1.1567 | 10.4671 | 66.475 | 9.3213 | 59.1979 | 0.03034 | 0.61071 | 9.02 | 0.48357 | 0.03032 | 0.61141
MRK | Moorooka | Tennyson Bulk Supply | MRK33kVB1_Term | 33 | 20.4876 | 1171.0211 | 3.0388 | 57.8971 | 1.6452 | 17.6635 | 336.534 | 17.775 | 338.6596 | 0.11759 | 1.0165 | 0.84587 | 18.6307 | 0.11818 | 1.0215
MRK | Moorooka | Tennyson Bulk Supply | MRK33kVB2_Term | 33 | 20.4665 | 1169.8163 | 3.0382 | 57.8856 | 1.645 | 17.6453 | 336.1889 | 17.7568 | 338.3131 | 0.11793 | 1.0175 | 0.85077 | 18.6324 | 0.11853 | 1.0226
MRK | Moorooka | Tennyson Bulk Supply | MRK11kVB1_Term | 11 | 6.1726 | 117.6032 | 0.98749 | 6.2714 | 0.53678 | 5.3403 | 33.9155 | 5.3618 | 34.0519 | 0.04881 | 1.1311 | 0.03575 | 18.9672 | 0.04888 | 1.1317
MRK | Moorooka | Tennyson Bulk Supply | MRK11kVB2_Term | 11 | 6.0348 | 114.9788 | 0.98395 | 6.2489 | 0.53575 | 5.2219 | 33.1633 | 5.242 | 33.2912 | 0.0469 | 1.157 | 0.0338 | 18.9918 | 0.04697 | 1.1576
MRR | Mary River Pumping | Gympie Bulk Supply | MRR33kVB1_Term | 33 | 1.4414 | 82.385 | 0.70132 | 13.3619 | 0.45269 | 1.17 | 22.2918 | 1.3603 | 25.9171 | 9.5445 | 10.9717 | 14.1279 | 61.3407 | 9.5393 | 10.9726
MST | Makerston Street | Ashgrove West Bulk Supply | 43400 MAKERS1D | 110 | 19.7218 | 3757.5037 | 20.6748 | 1313.0249 | 21.8111 | 21.2523 | 1349.7019 | 19.1581 | 1216.7056 | 0.6951 | 3.4745 | 1.1311 | 2.8467 | 0.70116 | 3.4988
MST | Makerston Street | Ashgrove West Bulk Supply | 43401 MAKERS2D | 110 | 19.7888 | 3770.2699 | 20.7351 | 1316.8554 | 21.8664 | 21.3051 | 1353.0534 | 19.2335 | 1221.4935 | 0.68965 | 3.4634 | 1.119 | 2.8444 | 0.69576 | 3.4878
MST | Makerston Street | Ashgrove West Bulk Supply | MST11kVB1_Term | 11 | 14.0853 | 268.3605 | 5.5408 | 35.189 | 3.512 | 12.2613 | 77.87 | 12.0555 | 76.5626 | 0.01523 | 0.49588 | 0.26366 | 2.7653 | 0.01551 | 0.5109
MST | Makerston Street | Ashgrove West Bulk Supply | MST11kVB2_Term | 11 | 14.0853 | 268.3606 | 5.5408 | 35.189 | 3.512 | 12.2614 | 77.87 | 12.0555 | 76.5626 | 0.01523 | 0.49588 | 0.26366 | 2.7653 | 0.01551 | 0.5109
MST | Makerston Street | Ashgrove West Bulk Supply | MST11kVB3_Term | 11 | 14.0853 | 268.3604 | 5.5408 | 35.189 | 3.512 | 12.2613 | 77.8699 | 12.0555 | 76.5626 | 0.01523 | 0.49588 | 0.26366 | 2.7653 | 0.01551 | 0.5109
MST | Makerston Street | Ashgrove West Bulk Supply | MST11kVB4_Term | 11 | 13.5279 | 257.7407 | 5.4804 | 34.8051 | 3.4786 | 11.8372 | 75.1766 | 11.6363 | 73.9002 | 0.016 | 0.51632 | 0.26367 | 2.7707 | 0.01628 | 0.52682
MST | Makerston Street | Ashgrove West Bulk Supply | MST11kVB5_Term | 11 | 13.5279 | 257.7408 | 5.4804 | 34.8051 | 3.4786 | 11.8372 | 75.1766 | 11.6363 | 73.9002 | 0.016 | 0.51632 | 0.26367 | 2.7707 | 0.01628 | 0.52682
MST | Makerston Street | Ashgrove West Bulk Supply | MST11kVB6_Term | 11 | 13.5279 | 257.7406 | 5.4804 | 34.8051 | 3.4786 | 11.8372 | 75.1766 | 11.6363 | 73.9002 | 0.016 | 0.51632 | 0.26367 | 2.7707 | 0.01628 | 0.52682
MSV | Mount Silvia | Gatton Bulk Supply | MSV33kVB1_Term | 33 | 1.6737 | 95.6672 | 0.71096 | 13.5457 | 0.44691 | 1.3992 | 26.6579 | 1.5314 | 29.1767 | 5.8322 | 11.0832 | 9.735 | 63.6611 | 5.8316 | 11.0804
MSV | Mount Silvia | Gatton Bulk Supply | MSV11kVB2_Term | 11 | 2.4531 | 46.7378 | 2.9177 | 18.5296 | 3.5896 | 2.6518 | 16.841 | 2.9048 | 18.4481 | 0.81387 | 2.7296 | 0.16585 | 1.4982 | 0.81381 | 2.7293
MTB | Mt Tamborine | Beaudesert Bulk Supply | MTB33kVB1_Term | 33 | 1.3535 | 77.3645 | 0.62244 | 11.859 | 0.40249 | 1.1511 | 21.9309 | 1.2263 | 23.3639 | 6.0664 | 14.311 | 13.3277 | 69.5299 | 6.066 | 14.3133
MTB | Mt Tamborine | Beaudesert Bulk Supply | MTB33kVB2_Term | 33 | 1.5574 | 89.0142 | 0.71151 | 13.5562 | 0.45741 | 1.3097 | 24.9542 | 1.4246 | 27.1433 | 5.7663 | 12.1697 | 9.774 | 61.4921 | 5.7623 | 12.1602
MTB | Mt Tamborine | Beaudesert Bulk Supply | MTB11kVB1_Term | 11 | 2.6006 | 49.5471 | 0.8686 | 5.5164 | 0.51866 | 2.2018 | 13.9832 | 2.3303 | 14.7991 | 0.72566 | 2.5972 | 0.05313 | 18.9799 | 0.72561 | 2.5975
MTB | Mt Tamborine | Beaudesert Bulk Supply | MTB11kVB2_Term | 11 | 2.7984 | 53.3159 | 0.87901 | 5.5825 | 0.51848 | 2.3702 | 15.0531 | 2.5035 | 15.8994 | 0.69324 | 2.4 | 0.05389 | 19.0163 | 0.69281 | 2.399
MTG | Mt Gravatt | Belmont Bulk Supply | MTG33kVB1_Term | 33 | 23.2285 | 1327.6885 | 1.1621 | 22.1399 | 0.58471 | 20.3292 | 387.3234 | 19.7465 | 376.2217 | 0.13413 | 0.89274 | 53.8292 | -3.8817 | 0.13306 | 0.90005
MTG | Mt Gravatt | Belmont Bulk Supply | MTG11kVB1_Term | 11 | 11.2329 | 214.0161 | 1.9525 | 12.3998 | 1.0698 | 9.7108 | 61.6717 | 9.7624 | 61.9995 | 0.03235 | 0.62143 | 0.01746 | 9.4962 | 0.03224 | 0.62224
MTG | Mt Gravatt | Belmont Bulk Supply | MTG11kVB2_Term | 11 | 11.2329 | 214.0161 | 1.9525 | 12.3998 | 1.0698 | 9.7108 | 61.6717 | 9.7624 | 61.9995 | 0.03235 | 0.62143 | 0.01746 | 9.4962 | 0.03224 | 0.62224
MTN | Myrtletown Bulk | Myrtletown Bulk Supply | 43510 MYRTTN1D | 110 | 11.3867 | 2169.4522 | 14.5073 | 921.3346 | 20.1134 | 14.5831 | 926.15 | 13.5502 | 860.55 | 0.73202 | 6.0927 | 0.63296 | 2.0747 | 0.72758 | 6.1299
MTN | Myrtletown Bulk | Myrtletown Bulk Supply | 43511 MYRTTN2D | 110 | 11.3865 | 2169.4298 | 14.5071 | 921.3269 | 20.1133 | 14.583 | 926.1419 | 13.5501 | 860.5447 | 0.73203 | 6.0928 | 0.63295 | 2.0747 | 0.7276 | 6.1299
MTN | Myrtletown Bulk | Myrtletown Bulk Supply | MTN33kVB1_Term | 33 | 17.6637 | 1009.6173 | 2.2984 | 43.7899 | 1.2306 | 15.2546 | 290.64 | 15.329 | 292.0567 | 0.07726 | 1.1842 | 0.01596 | 24.9894 | 0.0744 | 1.1872
MTN | Myrtletown | Myrtletown Bulk Supply | MTN11kVB1_Term | 11 | 12.0868 | 230.2845 | 3.1055 | 19.7227 | 1.797 | 10.5398 | 66.9365 | 10.3024 | 65.4289 | 0.02925 | 0.57735 | 1.0473 | 5.4942 | 0.02846 | 0.5873
NBR | Nambour | Nambour Bulk Supply | 40160 NAMBOR1D | 132 | 8.7704 | 2005.1743 | 7.5377 | 574.4469 | 6.6312 | 8.3173 | 633.8674 | 8.2371 | 627.7525 | 2.0395 | 9.34 | 3.2235 | 13.8439 | 2.0111 | 9.3843
NBR | Nambour | Nambour Bulk Supply | 40161 NAMBOR2D | 132 | 8.7709 | 2005.2914 | 7.5403 | 574.6497 | 6.635 | 8.3203 | 634.0888 | 8.2365 | 627.7074 | 2.0382 | 9.3397 | 3.23 | 13.8315 | 2.0098 | 9.384
NBR | Nambour Bulk | Nambour Bulk Supply | NBR33kVB1_Term | 33 | 15.7751 | 901.6685 | 2.2094 | 42.0949 | 1.1905 | 13.5912 | 258.9463 | 13.6969 | 260.9614 | 0.13299 | 1.3221 | 0.15557 | 25.8081 | 0.12977 | 1.3285
NBR | Nambour | Nambour Bulk Supply | NBR11kVB1_Term | 11 | 10.4449 | 199.0028 | 1.935 | 12.2891 | 1.0668 | 9.0328 | 57.3658 | 9.0807 | 57.6699 | 0.0328 | 0.66814 | 0.01805 | 9.4953 | 0.03245 | 0.66886
NBR | Nambour | Nambour Bulk Supply | NBR11kVB2_Term | 11 | 10.4449 | 199.0028 | 1.935 | 12.2891 | 1.0668 | 9.0328 | 57.3658 | 9.0807 | 57.6699 | 0.0328 | 0.66814 | 0.01805 | 9.4953 | 0.03245 | 0.66886
NDH | Nundah Bulk | Nudgee Bulk Supply | NDH33kVB1_Term | 33 | 16.2558 | 929.1454 | 2.9571 | 56.3402 | 1.6324 | 14.0145 | 267.0119 | 14.0955 | 268.5554 | 0.14071 | 1.2818 | 1.0669 | 18.6511 | 0.14073 | 1.2907
NDH | Nundah | Nudgee Bulk Supply | NDH11kVB1_Term | 11 | 11.3849 | 216.9105 | 1.954 | 12.4099 | 1.0792 | 9.7596 | 61.9815 | 9.816 | 62.3402 | 0.03574 | 0.6127 | 0.0217 | 9.4904 | 0.03526 | 0.62398
NDH | Nundah | Nudgee Bulk Supply | NDH11kVB2_Term | 11 | 11.3849 | 216.9105 | 1.954 | 12.4099 | 1.0792 | 9.7596 | 61.9815 | 9.816 | 62.3402 | 0.03574 | 0.6127 | 0.0217 | 9.4904 | 0.03526 | 0.62398
NGE | Nudgee Bulk | Nudgee Bulk Supply | 43540 NUDGEE1D | 110 | 12.862 | 2450.5452 | 16.5284 | 1049.692 | 23.3352 | 16.0074 | 1016.6094 | 16.2334 | 1030.956 | 0.64063 | 5.3947 | 0.14447 | 1.7761 | 0.63692 | 5.4319
NGE | Nudgee Bulk | Nudgee Bulk Supply | NGE33kVB1_Term | 33 | 19.48 | 1113.4311 | 3.1067 | 59.1915 | 1.694 | 16.778 | 319.6634 | 16.8918 | 321.8318 | 0.07619 | 1.0734 | 0.01337 | 18.0871 | 0.07587 | 1.0809
NGE | Nudgee | Nudgee Bulk Supply | NGE11kVB1_Term | 11 | 11.5909 | 220.8363 | 2.1201 | 13.4647 | 1.1738 | 9.9806 | 63.3852 | 10.0225 | 63.6514 | 0.02384 | 0.60236 | 0.01951 | 8.6754 | 0.02394 | 0.60907
NGE | Nudgee | Nudgee Bulk Supply | NGE11kVB2_Term | 11 | 11.5909 | 220.8363 | 2.1201 | 13.4647 | 1.1738 | 9.9806 | 63.3852 | 10.0225 | 63.6514 | 0.02384 | 0.60236 | 0.01951 | 8.6754 | 0.02394 | 0.60907
NGE | Nudgee | Nudgee Bulk Supply | NGE11kVB3_Term | 11 | 11.5909 | 220.8363 | 2.1201 | 13.4647 | 1.1738 | 9.9806 | 63.3852 | 10.0225 | 63.6514 | 0.02384 | 0.60236 | 0.01951 | 8.6754 | 0.02394 | 0.60907
NGI | Ningi | Caboolture Bulk Supply | NGI33kVB1_Term | 33 | 4.8456 | 276.9644 | 1.6671 | 31.7624 | 1.0044 | 4.1342 | 78.7679 | 4.3134 | 82.1818 | 1.2189 | 4.1506 | 2.5628 | 29.0811 | 1.2042 | 4.1589
NGI | Ningi | Caboolture Bulk Supply | NGI11kVB1_Term | 11 | 4.6291 | 88.1969 | 0.95353 | 6.0557 | 0.53127 | 3.986 | 25.3148 | 4.0474 | 25.7047 | 0.18864 | 1.4976 | 0.06606 | 18.9829 | 0.18701 | 1.4985
NIP | Nth Ipswich | Abermain Bulk Supply | NIP33kVB1_Term | 33 | 11.2408 | 642.4988 | 1.1239 | 21.4135 | 0.57123 | 9.9981 | 190.4892 | 9.4494 | 180.0345 | 0.42548 | 1.8158 | 54.8293 | 1.9345 | 0.42593 | 1.8202
NIP | Nth Ipswich | Abermain Bulk Supply | NIP33kVB2_Term | 33 | 10.6671 | 609.7049 | 1.1213 | 21.3635 | 0.57059 | 9.5014 | 181.0256 | 8.9547 | 170.6092 | 0.44526 | 1.9142 | 54.8453 | 2.454 | 0.4457 | 1.9186
NIP | Nth Ipswich | Abermain Bulk Supply | NIP11kVB1_Term | 11 | 10.242 | 195.1369 | 2.252 | 14.3023 | 1.1542 | 9.4363 | 59.9287 | 8.2981 | 52.6999 | 0.05018 | 0.68045 | 9.0206 | 0.50027 | 0.05023 | 0.68094
NIP | Nth Ipswich | Abermain Bulk Supply | NIP11kVB2_Term | 11 | 10.242 | 195.1369 | 2.252 | 14.3023 | 1.1542 | 9.4363 | 59.9287 | 8.2981 | 52.6999 | 0.05018 | 0.68045 | 9.0206 | 0.50027 | 0.05023 | 0.68094
NMC | North Maclean | Jimboomba Bulk Supply | NMC33kVB1_Term | 33 | 3.79 | 216.6249 | 1.1642 | 22.18 | 0.68595 | 3.2242 | 61.4299 | 3.3692 | 64.1916 | 1.6939 | 5.2688 | 3.5796 | 43.0544 | 1.6944 | 5.2783
NMC | North Maclean | Jimboomba Bulk Supply | NMC33kVB2_Term | 33 | 3.1587 | 180.5428 | 0.78222 | 14.9032 | 0.44491 | 2.7014 | 51.4683 | 2.7905 | 53.1656 | 1.7243 | 6.4125 | 3.3969 | 67.3346 | 1.7209 | 6.4041
NMC | North Maclean | Jimboomba Bulk Supply | NMC11kVB1_Term | 11 | 4.2052 | 80.12 | 0.94019 | 5.971 | 0.52896 | 3.6162 | 22.9659 | 3.6841 | 23.3971 | 0.22666 | 1.6471 | 0.03844 | 19.0086 | 0.22671 | 1.6482
NMC | North Maclean | Jimboomba Bulk Supply | NMC11kVB2_Term | 11 | 3.9285 | 74.8475 | 0.93077 | 5.9112 | 0.52731 | 3.3815 | 21.4756 | 3.4447 | 21.8766 | 0.22724 | 1.7651 | 0.03566 | 19 | 0.22687 | 1.7642
NMK | Newmarket | Victoria Park Bulk Supply | NMK33kVB1_Term | 33 | 18.6864 | 1068.0737 | 2.2853 | 43.5412 | 1.158 | 16.7283 | 318.7174 | 15.5852 | 296.9377 | 0.12816 | 1.1148 | 27.1156 | 0.67854 | 0.12864 | 1.1185
NMK | Newmarket | Victoria Park Bulk Supply | NMK11kVB1_Term | 11 | 10.8544 | 206.8032 | 1.9423 | 12.3351 | 1.0668 | 9.3883 | 59.6236 | 9.4364 | 59.9294 | 0.03129 | 0.6432 | 0.01826 | 9.5091 | 0.03135 | 0.6436
NMK | Newmarket | Victoria Park Bulk Supply | NMK11kVB2_Term | 11 | 10.8544 | 206.8032 | 1.9423 | 12.3351 | 1.0668 | 9.3883 | 59.6236 | 9.4364 | 59.9294 | 0.03129 | 0.6432 | 0.01826 | 9.5091 | 0.03135 | 0.6436
NPD | Nth Pine Dam | Brendale Bulk Supply | NPD33kVB1_Term | 33 | 8.3559 | 477.6019 | 2.1894 | 41.7129 | 1.2589 | 7.1313 | 135.8687 | 7.3729 | 140.4723 | 0.65324 | 2.4222 | 1.3909 | 23.7446 | 0.65315 | 2.4303
NPD | Nth Pine Dam | Brendale Bulk Supply | NPD11kVB1_Term | 11 | 3.9184 | 74.6562 | 4.1925 | 26.6257 | 4.51 | 4.0526 | 25.7377 | 4.0951 | 26.0076 | 0.23599 | 1.7675 | 0.16341 | 1.4235 | 0.23598 | 1.7685
NPD | Nth Pine Dam | Brendale Bulk Supply | NPD6.6kVB1_Term | 6.6 | 12.7429 | 145.6704 | 1.3726 | 5.2304 | 0.69478 | 11.3714 | 43.331 | 10.6895 | 40.7324 | 0.04931 | 0.32529 | 9.0232 | 0.21698 | 0.04931 | 0.32561
NRA | Narangba | Hays Inlet Bulk Supply | NRA33kVB1_Term | 33 | 8.2654 | 472.4307 | 1.2915 | 24.6074 | 0.70064 | 7.2649 | 138.4146 | 6.9652 | 132.7042 | 0.62544 | 2.4578 | 28.5156 | 33.5744 | 0.63424 | 2.4934
NRA | Narangba | Hays Inlet Bulk Supply | NRA11kVB1_Term | 11 | 9.7305 | 185.3905 | 1.9136 | 12.1531 | 1.0833 | 8.2296 | 52.2649 | 8.346 | 53.0045 | 0.08498 | 0.71304 | 0.02149 | 9.4979 | 0.08522 | 0.74146
NRA | Narangba | Hays Inlet Bulk Supply | NRA11kVB2_Term | 11 | 9.7305 | 185.3905 | 1.9136 | 12.1531 | 1.0833 | 8.2296 | 52.2649 | 8.346 | 53.0045 | 0.08498 | 0.71304 | 0.02149 | 9.4979 | 0.08522 | 0.74146
NRG | Nerang | Molendinar Bulk Supply | 40750 NERANG1D | 110 | 15.6864 | 2988.6529 | 16.757 | 1064.2127 | 18.0129 | 16.5495 | 1051.0351 | 16.0324 | 1018.1913 | 0.50485 | 4.4272 | 0.60622 | 3.5465 | 0.50543 | 4.4351
NRG | Nerang | Molendinar Bulk Supply | NRG11kVB1_Term | 11 | 9.6872 | 184.5651 | 1.9336 | 12.2798 | 1.0738 | 8.4443 | 53.6287 | 8.3676 | 53.1413 | 0.01857 | 0.72131 | 0.9405 | 9.358 | 0.01857 | 0.72139
NRG | Nerang | Molendinar Bulk Supply | NRG11kVB2_Term | 11 | 9.6687 | 184.2142 | 1.9331 | 12.2767 | 1.0737 | 8.4286 | 53.5286 | 8.3515 | 53.0392 | 0.01838 | 0.72269 | 0.9405 | 9.358 | 0.01838 | 0.72277
NRG | Nerang | Molendinar Bulk Supply | NRG11kVB3_Term | 11 | 9.6872 | 184.5651 | 1.9336 | 12.2798 | 1.0738 | 8.4443 | 53.6287 | 8.3676 | 53.1413 | 0.01857 | 0.72131 | 0.9405 | 9.358 | 0.01857 | 0.72139
NRG | Nerang | Molendinar Bulk Supply | NRG11kVB4_Term | 11 | 9.6687 | 184.2142 | 1.9331 | 12.2767 | 1.0737 | 8.4286 | 53.5286 | 8.3515 | 53.0392 | 0.01838 | 0.72269 | 0.9405 | 9.358 | 0.01838 | 0.72277
NSD | Newstead | CBD East Bulk Supply | 43500 NEWSTD1D | 110 | 22.6776 | 4320.6553 | 27.3887 | 1739.4147 | 35.0873 | 27.2784 | 1732.411 | 25.2578 | 1604.086 | 0.33514 | 3.064 | 0.38963 | 1.4134 | 0.34049 | 3.1043
NSD | Newstead | CBD East Bulk Supply | NSD11kVB1_Term | 11 | 9.0857 | 173.1066 | 3.3614 | 21.3476 | 2.0619 | 8.0047 | 50.8367 | 7.8623 | 49.9325 | 0.01901 | 0.76907 | 0.47025 | 4.679 | 0.01906 | 0.76948
NSD | Newstead | CBD East Bulk Supply | NSD11kVB2_Term | 11 | 9.0857 | 173.1066 | 3.3614 | 21.3476 | 2.0619 | 8.0047 | 50.8367 | 7.8623 | 49.9325 | 0.01901 | 0.76907 | 0.47025 | 4.679 | 0.01906 | 0.76948
NSD | Newstead | CBD East Bulk Supply | NSD11kVB3_Term | 11 | 9.2571 | 176.3715 | 3.3768 | 21.4455 | 2.0648 | 8.1525 | 51.7752 | 8.0091 | 50.8647 | 0.01844 | 0.75484 | 0.47025 | 4.679 | 0.01849 | 0.75525
NSD | Newstead | CBD East Bulk Supply | NSD11kVB4_Term | 11 | 9.2571 | 176.3715 | 3.3768 | 21.4455 | 2.0648 | 8.1525 | 51.7752 | 8.0091 | 50.8647 | 0.01844 | 0.75484 | 0.47025 | 4.679 | 0.01849 | 0.75525
NSW | North Springwood | Loganlea Bulk Supply | 43601 SPGWDN2D | 110 | 13.1695 | 2509.1189 | 12.4516 | 790.7801 | 11.8594 | 12.8084 | 813.4443 | 12.8679 | 817.223 | 1.4369 | 5.1109 | 1.6256 | 5.9863 | 1.4393 | 5.1357
NSW | North Springwood | Loganlea Bulk Supply | 43600 SPGWDN1D | 110 | 13.2346 | 2521.5375 | 12.1569 | 772.0663 | 11.2994 | 12.8144 | 813.8243 | 12.7009 | 806.6183 | 1.4215 | 5.0881 | 1.8882 | 6.3855 | 1.4264 | 5.1174
NSW | North Springwood | Loganlea Bulk Supply | NSW11kVB1_Term | 11 | 9.8088 | 186.8834 | 2.3999 | 15.2414 | 1.3674 | 8.5455 | 54.2711 | 8.496 | 53.9566 | 0.0442 | 0.71143 | 0.7315 | 7.2784 | 0.04422 | 0.71168
NSW | North Springwood | Loganlea Bulk Supply | NSW11kVB2_Term | 11 | 4.681 | 89.1852 | 1.6928 | 10.7505 | 1.0345 | 4.1153 | 26.1358 | 4.0477 | 25.7065 | 0.04379 | 1.4929 | 0.9405 | 9.358 | 0.04344 | 1.497
NSW | North Springwood | Loganlea Bulk Supply | NSW11kVB3_Term | 11 | 5.7845 | 110.2102 | 1.766 | 11.2154 | 1.0706 | 4.9624 | 31.5158 | 4.8964 | 31.0964 | 0.04871 | 1.2075 | 0.9405 | 9.358 | 0.04291 | 1.2652
NSW | North Springwood | Loganlea Bulk Supply | NSW11kVB4_Term | 11 | 9.778 | 186.2956 | 2.3987 | 15.2336 | 1.3672 | 8.519 | 54.1028 | 8.4692 | 53.7867 | 0.04419 | 0.71369 | 0.7315 | 7.2784 | 0.04422 | 0.71393
NVL | Noosaville | Sunrise Hills Bulk Supply | 43520 NOOSVL1D | 132 | 6.7212 | 1536.6758 | 7.5924 | 578.6208 | 8.7219 | 6.9793 | 531.8945 | 7.5522 | 575.556 | 3.5517 | 11.9583 | 1.1498 | 8.1462 | 3.5088 | 11.9916
NVL | Noosaville | Sunrise Hills Bulk Supply | 43521 NOOSVL2D | 132 | 6.7212 | 1536.6758 | 7.5129 | 572.5609 | 8.5164 | 6.938 | 528.747 | 7.4725 | 569.4803 | 3.5517 | 11.9583 | 1.2824 | 8.4742 | 3.5088 | 11.9916
NVL | Noosaville | Sunrise Hills Bulk Supply | NVL11kVB1_Term | 11 | 4.5001 | 85.7387 | 1.6761 | 10.6448 | 1.0296 | 3.9613 | 25.1578 | 3.9 | 24.7687 | 0.05486 | 1.5517 | 0.9405 | 9.358 | 0.05456 | 1.5519
NVL | Noosaville | Sunrise Hills Bulk Supply | NVL11kVB2_Term | 11 | 6.9738 | 132.869 | 1.8375 | 11.67 | 1.0582 | 6.0863 | 38.6534 | 6.0376 | 38.344 | 0.05186 | 1.0006 | 0.9405 | 9.358 | 0.05156 | 1.0008
NVL | Noosaville | Sunrise Hills Bulk Supply | NVL11kVB3_Term | 11 | 6.9614 | 132.6323 | 1.837 | 11.6663 | 1.0581 | 6.0757 | 38.5856 | 6.0268 | 38.2756 | 0.05185 | 1.0024 | 0.9405 | 9.358 | 0.05155 | 1.0026
NVL | Noosaville | Sunrise Hills Bulk Supply | NVL11kVB4_Term | 11 | 4.4327 | 84.4545 | 1.6698 | 10.6049 | 1.0284 | 3.9035 | 24.7904 | 3.842 | 24.4003 | 0.05518 | 1.5753 | 0.9405 | 9.358 | 0.05488 | 1.5755
OXL | Oxley | Richlands Bulk Supply | OXL33kVB1_Term | 33 | 18.9497 | 1083.1215 | 3.2422 | 61.7722 | 1.7795 | 16.1728 | 308.1327 | 16.533 | 314.9953 | 0.24434 | 1.0791 | 0.19177 | 17.2187 | 0.24593 | 1.0904
OXL | Oxley | Richlands Bulk Supply | OXL33kVB2_Term | 33 | 18.9434 | 1082.7607 | 3.242 | 61.7685 | 1.7795 | 16.1669 | 308.0204 | 16.5273 | 314.8878 | 0.24462 | 1.0794 | 0.19211 | 17.2192 | 0.24622 | 1.0908
OXL | Oxley | Richlands Bulk Supply | OXL11kVB1_Term | 11 | 11.995 | 228.5354 | 1.9675 | 12.4951 | 1.0834 | 10.2678 | 65.2095 | 10.3316 | 65.6146 | 0.03792 | 0.5814 | 0.02098 | 9.4812 | 0.03748 | 0.59343
OXL | Oxley | Richlands Bulk Supply | OXL11kVB2_Term | 11 | 11.995 | 228.5354 | 1.9675 | 12.4951 | 1.0834 | 10.2678 | 65.2095 | 10.3316 | 65.6146 | 0.03792 | 0.5814 | 0.02098 | 9.4812 | 0.03748 | 0.59343
PAV | Pandanus Avenue | Myrtletown Bulk Supply | PAV33kVB1_Term | 33 | 15.5041 | 886.1798 | 2.2135 | 42.1736 | 1.193 | 13.3926 | 255.1641 | 13.4609 | 256.4639 | 0.10708 | 1.3478 | 0.46835 | 25.7032 | 0.10422 | 1.3508
PAV | Pandanus Avenue | Myrtletown Bulk Supply | PAV33kVB2_Term | 33 | 15.5074 | 886.3652 | 2.2137 | 42.1764 | 1.1931 | 13.3954 | 255.2172 | 13.4637 | 256.5175 | 0.10704 | 1.3475 | 0.46752 | 25.7019 | 0.10418 | 1.3505
PAV | Pandanus Avenue | Myrtletown Bulk Supply | PAV11kVB2_Term | 11 | 10.66 | 203.0998 | 1.9412 | 12.328 | 1.068 | 9.225 | 58.5869 | 9.265 | 58.8408 | 0.02691 | 0.65493 | 0.01664 | 9.4884 | 0.02659 | 0.65526
PBH | Palm Beach | Burleigh Head Bulk Supply | PBH33kVB1_Term | 33 | 11.6467 | 665.696 | 1.1288 | 21.5062 | 0.56783 | 10.3687 | 197.5504 | 9.8038 | 186.7868 | 0.27612 | 1.7791 | 55.1763 | -3.8292 | 0.27602 | 1.7792
PBH | Palm Beach | Burleigh Head Bulk Supply | PBH11kVB1_Term | 11 | 9.7571 | 185.898 | 1.92 | 12.1934 | 1.0645 | 8.4335 | 53.5601 | 8.4996 | 53.9797 | 0.04751 | 0.71478 | 0.01683 | 9.4913 | 0.0475 | 0.71478
PBH | Palm Beach | Burleigh Head Bulk Supply | PBH11kVB2_Term | 11 | 9.7571 | 185.898 | 1.92 | 12.1934 | 1.0645 | 8.4335 | 53.5601 | 8.4996 | 53.9797 | 0.04751 | 0.71478 | 0.01683 | 9.4913 | 0.0475 | 0.71478
PGN | Perigian | Sunrise Hills Bulk Supply | PGN33kVB1_Term | 33 | 4.3125 | 246.4939 | 1.3145 | 25.044 | 0.77247 | 3.6667 | 69.8599 | 3.8399 | 73.1591 | 1.4841 | 4.6284 | 2.6088 | 38.2547 | 1.4814 | 4.6305
PGN | Perigian | Sunrise Hills Bulk Supply | PGN11kVB1_Term | 11 | 4.4109 | 84.0387 | 0.94628 | 6.0097 | 0.52961 | 3.7971 | 24.1148 | 3.8604 | 24.517 | 0.20101 | 1.5712 | 0.03611 | 19.0041 | 0.20071 | 1.5715
PGY | Paddys Gully | Lockrose Bulk Supply | PGY33kVB1_Term | 33 | 2.734 | 156.2671 | 1.1061 | 21.0742 | 0.68801 | 2.2991 | 43.8029 | 2.483 | 47.3072 | 3.4796 | 6.8323 | 7.2242 | 41.3929 | 3.4767 | 6.8319
PGY | Paddys Gully | Lockrose Bulk Supply | PGY33kVB2_Term | 33 | 2.7288 | 155.975 | 1.1043 | 21.0402 | 0.687 | 2.2952 | 43.7293 | 2.478 | 47.2115 | 3.4792 | 6.8487 | 7.2524 | 41.4481 | 3.4762 | 6.8483
PKW | Parkwood | Molendinar Bulk Supply | PKW33kVB1_Term | 33 | 16.5053 | 943.4052 | 2.9144 | 55.5266 | 1.604 | 14.1789 | 270.145 | 14.351 | 273.4226 | 0.19215 | 1.2558 | 0.76484 | 19.0334 | 0.19304 | 1.2653
PKW | Parkwood | Molendinar Bulk Supply | PKW11kVB1_Term | 11 | 11.9139 | 226.9911 | 1.9636 | 12.4706 | 1.0901 | 10.1316 | 64.3442 | 10.1876 | 64.7001 | 0.03547 | 0.58559 | 0.01666 | 9.4861 | 0.03334 | 0.60637
PKW | Parkwood | Molendinar Bulk Supply | PKW11kVB2_Term | 11 | 11.9139 | 226.9911 | 1.9636 | 12.4706 | 1.0901 | 10.1316 | 64.3442 | 10.1876 | 64.7001 | 0.03547 | 0.58559 | 0.01666 | 9.4861 | 0.03334 | 0.60637
PPE | Pimpama East | Coomera Bulk Supply | PPE33kVB1_Term | 33 | 7.7192 | 441.2103 | 1.6109 | 30.6919 | 0.89871 | 6.6381 | 126.4726 | 6.7582 | 128.7602 | 0.63742 | 2.6416 | 3.2599 | 33.5154 | 0.63747 | 2.6431
PPE | Pimpama East | Coomera Bulk Supply | PPE11kVB1_Term | 11 | 8.5704 | 163.288 | 1.887 | 11.9844 | 1.0598 | 7.3867 | 46.912 | 7.4936 | 47.5909 | 0.08746 | 0.81114 | 0.01663 | 9.4918 | 0.08746 | 0.8113
PPE | Pimpama East | Coomera Bulk Supply | PPE11kVB2_Term | 11 | 8.5704 | 163.288 | 1.887 | 11.9844 | 1.0598 | 7.3867 | 46.912 | 7.4936 | 47.5909 | 0.08746 | 0.81114 | 0.01663 | 9.4918 | 0.08746 | 0.8113
PRG | Postmans Ridge Bulk | Postmans Ridge Bulk Supply | 40290 POSTRG1D | 110 | 11.4062 | 2173.1795 | 12.2378 | 777.2052 | 13.0942 | 11.582 | 735.5539 | 12.1474 | 771.4664 | 1.2709 | 5.9924 | 0.62298 | 4.8913 | 1.2707 | 5.9498
PRG | Postmans Ridge Bulk | Postmans Ridge Bulk Supply | PRG33kVB1_Term | 33 | 14.065 | 803.9212 | 2.2173 | 42.2457 | 1.2013 | 12.1483 | 231.4558 | 12.2726 | 233.8236 | 0.16134 | 1.4816 | 0.04959 | 25.3986 | 0.16132 | 1.4777
PRG | Postmans Ridge | Postmans Ridge Bulk Supply | PRG11kVB1_Term | 11 | 3.8879 | 74.0743 | 4.0743 | 25.8755 | 4.2785 | 3.9949 | 25.371 | 3.9838 | 25.3005 | 0.1857 | 1.7875 | 0.16778 | 1.5418 | 0.1857 | 1.7871
PWC | Palmwoods Central | Nambour Bulk Supply | PWC33kVB1_Term | 33 | 5.431 | 310.4252 | 1.4803 | 28.2032 | 0.85106 | 4.5792 | 87.2459 | 4.8568 | 92.5347 | 1.5994 | 3.5126 | 2.6099 | 35.0508 | 1.5961 | 3.519
PWC | Palmwoods Central | Nambour Bulk Supply | PWC11kVB1_Term | 11 | 7.2621 | 138.3618 | 1.8368 | 11.665 | 1.0491 | 6.2043 | 39.4028 | 6.4121 | 40.7225 | 0.20374 | 0.94031 | 0.02603 | 9.5226 | 0.20338 | 0.94103
PWC | Palmwoods Central | Nambour Bulk Supply | PWC11kVB2_Term | 11 | 7.2621 | 138.3618 | 1.8368 | 11.665 | 1.0491 | 6.2043 | 39.4028 | 6.4121 | 40.7225 | 0.20374 | 0.94031 | 0.02603 | 9.5226 | 0.20338 | 0.94103
PWC | Palmwoods Central | Nambour Bulk Supply | PWC11kVB3_Term | 11 | 7.2621 | 138.3618 | 1.8368 | 11.665 | 1.0491 | 6.2043 | 39.4028 | 6.4121 | 40.7225 | 0.20374 | 0.94031 | 0.02603 | 9.5226 | 0.20338 | 0.94103
QPT | Queensport | Doboy Bulk Supply | QPT33kVB1_Term | 33 | 20.6451 | 1180.0248 | 3.2239 | 61.4229 | 1.7541 | 17.8032 | 339.1964 | 17.8908 | 340.8658 | 0.10543 | 1.0102 | 0.903 | 17.4542 | 0.10526 | 1.0165
QPT | Queensport | Doboy Bulk Supply | QPT11kVB1_Term | 11 | 10.9945 | 209.474 | 1.9474 | 12.3675 | 1.0689 | 9.5084 | 60.3867 | 9.5544 | 60.6786 | 0.02954 | 0.63505 | 0.01782 | 9.4967 | 0.02952 | 0.63575
QPT | Queensport | Doboy Bulk Supply | QPT11kVB2_Term | 11 | 10.9945 | 209.474 | 1.9474 | 12.3675 | 1.0689 | 9.5084 | 60.3867 | 9.5544 | 60.6786 | 0.02954 | 0.63505 | 0.01782 | 9.4967 | 0.02952 | 0.63575
RBA | Robina | Mudgeeraba Bulk Supply | 41280 ROBINA1D | 110 | 14.997 | 2857.303 | 16.136 | 1024.7752 | 17.4687 | 15.8791 | 1008.4587 | 15.4166 | 979.0875 | 0.51687 | 4.6319 | 0.59659 | 3.6257 | 0.51624 | 4.6348
RBA | Robina | Mudgeeraba Bulk Supply | RBA11kVB1_Term | 11 | 9.0823 | 173.0416 | 3.3611 | 21.3461 | 2.0613 | 8.0019 | 50.8186 | 7.8628 | 49.9355 | 0.02041 | 0.76931 | 0.47025 | 4.679 | 0.0204 | 0.76934
RBA | Robina | Mudgeeraba Bulk Supply | RBA11kVB2_Term | 11 | 9.0823 | 173.0416 | 3.3611 | 21.3461 | 2.0613 | 8.0019 | 50.8186 | 7.8628 | 49.9355 | 0.02041 | 0.76931 | 0.47025 | 4.679 | 0.0204 | 0.76934
RBA | Robina | Mudgeeraba Bulk Supply | RBA11kVB3_Term | 11 | 8.9141 | 169.8368 | 3.3456 | 21.2473 | 2.0584 | 7.8568 | 49.8975 | 7.7186 | 49.0199 | 0.02098 | 0.78382 | 0.47025 | 4.679 | 0.02097 | 0.78385
RBA | Robina | Mudgeeraba Bulk Supply | RBA11kVB4_Term | 11 | 8.9141 | 169.8368 | 3.3456 | 21.2473 | 2.0584 | 7.8568 | 49.8975 | 7.7186 | 49.0199 | 0.02098 | 0.78382 | 0.47025 | 4.679 | 0.02097 | 0.78385
RBK | Redbank | Goodna Bulk Supply | RBK33kVB1_Term | 33 | 11.53 | 659.04 | 1.8009 | 34.3118 | 0.981 | 9.885 | 188.3344 | 10.018 | 190.87 | 0.3221 | 1.7895 | 1.1372 | 31.2815 | 0.32283 | 1.8068
RBK | Redbank | Goodna Bulk Supply | RBK11kVB1_Term | 11 | 6.8358 | 130.2403 | 0.99748 | 6.3349 | 0.53941 | 5.8988 | 37.4624 | 5.9245 | 37.6257 | 0.05323 | 1.0209 | 0.0333 | 18.9691 | 0.05218 | 1.0261
RBK | Redbank | Goodna Bulk Supply | RBK11kVB2_Term | 11 | 9.8549 | 187.7608 | 1.9095 | 12.1271 | 1.0595 | 8.487 | 53.9 | 8.577 | 54.4713 | 0.06647 | 0.70596 | 0.04458 | 9.5619 | 0.06615 | 0.70927
RBK | Redbank | Goodna Bulk Supply | RBK11kVB3_Term | 11 | 9.8549 | 187.7608 | 1.9095 | 12.1271 | 1.0595 | 8.487 | 53.9 | 8.577 | 54.4713 | 0.06647 | 0.70596 | 0.04458 | 9.5619 | 0.06615 | 0.70927
RBS | Runcorn Bulk | Runcorn Bulk Supply | RBS33kVB1_Term | 33 | 17.2731 | 987.289 | 2.3187 | 44.1779 | 1.2441 | 14.9112 | 284.0964 | 14.9994 | 285.7776 | 0.08837 | 1.2107 | 0.00602 | 24.7047 | 0.08879 | 1.2135
RBY | Raby Bay | Cleveland Bulk Supply | RBY33kVB1_Term | 33 | 15.9358 | 910.8506 | 2.1345 | 40.6685 | 1.1452 | 13.7545 | 262.0583 | 13.8368 | 263.6272 | 0.13822 | 1.3086 | 0.8126 | 26.8314 | 0.13705 | 1.3121
RBY | Raby Bay | Cleveland Bulk Supply | RBY11kVB1_Term | 11 | 5.3356 | 101.6567 | 0.96365 | 6.12 | 0.5245 | 4.6528 | 29.5495 | 4.6815 | 29.7318 | 0.08524 | 1.3073 | 0.07389 | 19.1669 | 0.0779 | 1.285
RBY | Raby Bay | Cleveland Bulk Supply | RBY11kVB2_Term | 11 | 10.0106 | 190.7276 | 1.9202 | 12.1949 | 1.0621 | 8.6506 | 54.9386 | 8.7162 | 55.3553 | 0.04735 | 0.69665 | 0.03274 | 9.5262 | 0.04722 | 0.69703
RBY | Raby Bay | Cleveland Bulk Supply | RBY11kVB3_Term | 11 | 10.0106 | 190.7276 | 1.9202 | 12.1949 | 1.0621 | 8.6506 | 54.9386 | 8.7162 | 55.3553 | 0.04735 | 0.69665 | 0.03274 | 9.5262 | 0.04722 | 0.69703
RBY | Raby Bay | Cleveland Bulk Supply | RBYBESS11kVB1_Term | 11 | 5.3356 | 101.6567 | 0.96365 | 6.12 | 0.5245 | 4.6528 | 29.5495 | 4.6815 | 29.7318 | 0.08524 | 1.3073 | 0.07389 | 19.1669 | 0.0779 | 1.285
RCF | Redcliffe | Hays Inlet Bulk Supply | RCF33kVB1_Term | 33 | 11.1569 | 637.7046 | 1.4153 | 26.9643 | 0.7526 | 9.8138 | 186.9779 | 9.4523 | 180.0911 | 0.38708 | 1.8386 | 27.0556 | 30.9494 | 0.38715 | 1.8527
RCF | Redcliffe | Hays Inlet Bulk Supply | RCF11kVB1_Term | 11 | 10.4452 | 199.0081 | 1.9384 | 12.3102 | 1.0758 | 8.9575 | 56.8877 | 9.0495 | 57.4721 | 0.06329 | 0.66596 | 0.02215 | 9.4724 | 0.06174 | 0.67514
RCF | Redcliffe | Hays Inlet Bulk Supply | RCF11kVB2_Term | 11 | 10.4452 | 199.0081 | 1.9384 | 12.3102 | 1.0758 | 8.9575 | 56.8877 | 9.0495 | 57.4721 | 0.06329 | 0.66596 | 0.02215 | 9.4724 | 0.06174 | 0.67514
RCN | Runcorn | Runcorn Bulk Supply | RCN33kVB1_Term | 33 | 12.9372 | 739.4574 | 2.1251 | 40.488 | 1.1579 | 11.1334 | 212.1208 | 11.2853 | 215.0137 | 0.24014 | 1.6029 | 0.34278 | 26.3819 | 0.24057 | 1.6057
RCN | Runcorn | Runcorn Bulk Supply | RCN11kVB1_Term | 11 | 9.9923 | 190.3792 | 1.9207 | 12.1978 | 1.0625 | 8.6369 | 54.8518 | 8.6991 | 55.2468 | 0.04391 | 0.69812 | 0.01926 | 9.5204 | 0.04396 | 0.69842
RCN | Runcorn | Runcorn Bulk Supply | RCN11kVB2_Term | 11 | 9.9923 | 190.3792 | 1.9207 | 12.1978 | 1.0625 | 8.6369 | 54.8518 | 8.6991 | 55.2468 | 0.04391 | 0.69812 | 0.01926 | 9.5204 | 0.04396 | 0.69842
RIS | Russell Island | Loganlea Bulk Supply | 43710 RUSLIS1D | 110 | 4.3932 | 837.0072 | 4.5396 | 288.305 | 4.6723 | 4.1285 | 262.1962 | 4.7739 | 303.1825 | 8.208 | 13.6453 | 4.1983 | 14.0578 | 8.2092 | 13.6757
RIS | Russell Island | Loganlea Bulk Supply | RIS11kVB1_Term | 11 | 7.893 | 150.3818 | 1.8776 | 11.9242 | 1.0657 | 6.8423 | 43.4542 | 6.868 | 43.6179 | 0.11103 | 0.87932 | 0.9405 | 9.358 | 0.11104 | 0.87962
RLA | Rocklea | Archerfield Bulk Supply | RLA33kVB1_Term | 33 | 15.8558 | 906.2801 | 2.2194 | 42.2846 | 1.1945 | 13.6942 | 260.9087 | 13.7643 | 262.2443 | 0.11727 | 1.317 | 0.73413 | 25.6853 | 0.11761 | 1.32
RLA | Rocklea | Archerfield Bulk Supply | RLA11kVB1_Term | 11 | 10.5385 | 200.7857 | 1.9356 | 12.2928 | 1.0658 | 9.1136 | 57.8792 | 9.1662 | 58.2133 | 0.03548 | 0.66217 | 0.02251 | 9.506 | 0.03552 | 0.6625
RLA | Rocklea | Archerfield Bulk Supply | RLA11kVB2_Term | 11 | 10.5385 | 200.7857 | 1.9356 | 12.2928 | 1.0658 | 9.1136 | 57.8792 | 9.1662 | 58.2133 | 0.03548 | 0.66217 | 0.02251 | 9.506 | 0.03552 | 0.6625
RLB | Redland Bay | Cleveland Bulk Supply | RLB33kVB1_Term | 33 | 8.5473 | 488.5442 | 1.7675 | 33.6757 | 0.98557 | 7.3484 | 140.0065 | 7.478 | 142.4746 | 0.52719 | 2.3961 | 2.4107 | 30.6273 | 0.52639 | 2.3999
RLB | Redland Bay | Cleveland Bulk Supply | RLB11kVB1_Term | 11 | 8.9263 | 170.0683 | 1.8981 | 12.0543 | 1.0618 | 7.6985 | 48.892 | 7.7945 | 49.5018 | 0.07542 | 0.77944 | 0.01684 | 9.4876 | 0.07533 | 0.77986
RLD | Richlands Bulk | Richlands Bulk Supply | RLD33kVB1_Term | 33 | 25.2539 | 1443.4559 | 3.3763 | 64.327 | 1.821 | 21.6848 | 413.1509 | 21.8234 | 415.7907 | 0.0648 | 0.8277 | 0.00566 | 16.9633 | 0.06589 | 0.83824
RPN | Redbank Plains | Redbank Plains Bulk Supply | RPN11kVB1_Term | 11 | 9.3702 | 178.5264 | 1.9234 | 12.2152 | 1.0756 | 8.1357 | 51.6684 | 8.0763 | 51.2911 | 0.03534 | 0.74495 | 0.9405 | 9.358 | 0.03196 | 0.75022
RPN | Redbank Plains | Redbank Plains Bulk Supply | RPN11kVB2_Term | 11 | 8.8277 | 168.1906 | 1.9083 | 12.1192 | 1.0698 | 7.6925 | 48.8542 | 7.6327 | 48.474 | 0.03293 | 0.79095 | 0.9405 | 9.358 | 0.03299 | 0.79117
RPT | Rocky Point | Beenleigh Bulk Supply (Including Bay Islands) | 43800 ROCKPT1D | 110 | 7.8004 | 1486.1861 | 7.2123 | 458.0404 | 6.7671 | 7.3354 | 465.8611 | 7.7246 | 490.5754 | 2.4314 | 8.6316 | 2.0154 | 10.9092 | 2.447 | 8.7273
RPT | Rocky Point Sugar Mill Substation | Loganlea Bulk Supply | RPT11kVB1_Term | 11 | 19.9121 | 379.3761 | 19.7645 | 125.5214 | 21.7629 | 19.7124 | 125.1907 | 20.1411 | 127.9132 | 0.02478 | 0.3502 | 0 | 0.32199 | 0.01464 | 0.38817
RST | Roderick St | Raceview Bulk Supply | RST33kVB1_Term | 33 | 10.4518 | 597.4029 | 1.8477 | 35.2032 | 1.013 | 8.9696 | 170.8945 | 9.1457 | 174.2486 | 0.41855 | 1.9617 | 0.88191 | 30.0691 | 0.41901 | 1.9652
RST | Roderick St | Raceview Bulk Supply | RST11kVB1_Term | 11 | 11.2475 | 214.2945 | 2.2522 | 14.3033 | 1.1539 | 10.3047 | 65.4438 | 9.1717 | 58.2484 | 0.07061 | 0.61729 | 9.0252 | 0.38573 | 0.07066 | 0.61767
RST | Roderick St | Raceview Bulk Supply | RST11kVB2_Term | 11 | 11.2475 | 214.2945 | 2.2522 | 14.3033 | 1.1539 | 10.3047 | 65.4438 | 9.1717 | 58.2484 | 0.07061 | 0.61729 | 9.0252 | 0.38573 | 0.07066 | 0.61767
RST | Roderick St | Raceview Bulk Supply | RST11kVB3_Term | 11 | 11.2475 | 214.2945 | 2.2522 | 14.3033 | 1.1539 | 10.3047 | 65.4438 | 9.1717 | 58.2484 | 0.07061 | 0.61729 | 9.0252 | 0.38573 | 0.07066 | 0.61767
RVW | Raceview Bulk | Raceview Bulk Supply | 40860 RACEVW1D | 110 | 16.7222 | 3186.0132 | 13.5066 | 857.7826 | 11.3733 | 15.5998 | 990.7216 | 15.4669 | 982.2806 | 0.76349 | 4.1087 | 1.4216 | 7.0015 | 0.76857 | 4.1281
RVW | Raceview Bulk | Raceview Bulk Supply | 40861 RACEVW2D | 110 | 16.7742 | 3195.9162 | 13.5628 | 861.3558 | 11.429 | 15.6534 | 994.1228 | 15.5172 | 985.477 | 0.75924 | 4.0963 | 1.4131 | 6.964 | 0.76432 | 4.1157
RVW | Raceview Bulk | Raceview Bulk Supply | RVW33kVB1_Term | 33 | 16.8693 | 964.2082 | 2.1253 | 40.4927 | 1.1354 | 14.5599 | 277.4023 | 14.6443 | 279.0107 | 0.09974 | 1.2388 | 0.11547 | 27.1105 | 0.10012 | 1.2419
RWD | Rosewood | Abermain Bulk Supply | RWD33kVB1_Term | 33 | 3.4563 | 197.5528 | 0.89374 | 17.028 | 0.49831 | 3.1527 | 60.0675 | 2.8047 | 53.4368 | 2.7959 | 5.3826 | 59.0415 | 16.8609 | 2.8545 | 5.4476
RWD | Rosewood | Abermain Bulk Supply | RWD11kVB1_Term | 11 | 4.8466 | 92.3407 | 1.6693 | 10.6018 | 1.0064 | 4.0873 | 25.9581 | 4.3399 | 27.562 | 0.3989 | 1.3855 | 0.08825 | 9.7481 | 0.40541 | 1.3927
SBH | Scarborough | Hays Inlet Bulk Supply | SBH33kVB1_Term | 33 | 10.0311 | 573.3565 | 1.3783 | 26.2596 | 0.73678 | 8.8354 | 168.336 | 8.5018 | 161.9811 | 0.47289 | 2.0355 | 27.2413 | 31.7963 | 0.47277 | 2.0481
SBH | Scarborough | Hays Inlet Bulk Supply | SBH11kVB1_Term | 11 | 12.0978 | 230.4946 | 2.8026 | 17.7992 | 1.5859 | 10.4052 | 66.0818 | 10.5841 | 67.218 | 0.07008 | 0.57331 | 0.01754 | 6.3298 | 0.07007 | 0.57471
SBH | Scarborough | Hays Inlet Bulk Supply | SBH11kVB2_Term | 11 | 12.0978 | 230.4946 | 2.8026 | 17.7992 | 1.5859 | 10.4052 | 66.0818 | 10.5841 | 67.218 | 0.07008 | 0.57331 | 0.01754 | 6.3298 | 0.07007 | 0.57471
SBH | Scarborough | Hays Inlet Bulk Supply | SBH11kVB3_Term | 11 | 12.0978 | 230.4946 | 2.8026 | 17.7992 | 1.5859 | 10.4052 | 66.0818 | 10.5841 | 67.218 | 0.07008 | 0.57331 | 0.01754 | 6.3298 | 0.07007 | 0.57471
SBK | Sunnybank | Runcorn Bulk Supply | SBK33kVB1_Term | 33 | 13.505 | 771.9161 | 2.1827 | 41.5852 | 1.1882 | 11.6575 | 222.1052 | 11.7438 | 223.7496 | 0.27025 | 1.529 | 2.5656 | 25.5924 | 0.27067 | 1.5317
SBK | Sunnybank | Runcorn Bulk Supply | SBK11kVB1_Term | 11 | 12.9376 | 246.4943 | 2.823 | 17.9284 | 1.5843 | 11.166 | 70.9138 | 11.2921 | 71.7143 | 0.04627 | 0.53827 | 0.01619 | 6.3502 | 0.04632 | 0.53857
SBK | Sunnybank | Runcorn Bulk Supply | SBK11kVB2_Term | 11 | 12.9376 | 246.4943 | 2.823 | 17.9284 | 1.5843 | 11.166 | 70.9138 | 11.2921 | 71.7143 | 0.04627 | 0.53827 | 0.01619 | 6.3502 | 0.04632 | 0.53857
SBK | Sunnybank | Runcorn Bulk Supply | SBK11kVB3_Term | 11 | 12.9376 | 246.4943 | 2.823 | 17.9284 | 1.5843 | 11.166 | 70.9138 | 11.2921 | 71.7143 | 0.04627 | 0.53827 | 0.01619 | 6.3502 | 0.04632 | 0.53857
SBY | Salisbury | Archerfield Bulk Supply | SBY33kVB2_Term | 33 | 13.8651 | 792.4998 | 2.1306 | 40.5927 | 1.1552 | 11.975 | 228.1542 | 12.0422 | 229.4356 | 0.15952 | 1.5036 | 1.2106 | 26.4698 | 0.15986 | 1.5069
SBY | Salisbury | Archerfield Bulk Supply | SBY11kVB1_Term | 11 | 6.3027 | 120.082 | 0.98782 | 6.2735 | 0.53776 | 5.4303 | 34.4868 | 5.4642 | 34.7023 | 0.07749 | 1.106 | 0.06238 | 19.0019 | 0.07623 | 1.1136
SBY | Salisbury | Archerfield Bulk Supply | SBY11kVB2_Term | 11 | 6.3027 | 120.082 | 0.98782 | 6.2735 | 0.53776 | 5.4303 | 34.4868 | 5.4642 | 34.7023 | 0.07749 | 1.106 | 0.06238 | 19.0019 | 0.07623 | 1.1136
SDM | Somerset Dam | Lockrose Bulk Supply | SDM33kVB1_Term | 33 | 1.597 | 91.2787 | 0.67123 | 12.7887 | 0.42364 | 1.3558 | 25.8323 | 1.4389 | 27.4143 | 5.7748 | 11.7875 | 15.8776 | 65.98 | 5.7778 | 11.8134
SDM | Somerset Dam | Lockrose Bulk Supply | SDM11kVB1_Term | 11 | 2.3596 | 44.9558 | 0.82996 | 5.2709 | 0.5014 | 1.9991 | 12.6961 | 2.115 | 13.4318 | 0.75734 | 2.8628 | 0.1157 | 19.4754 | 0.75768 | 2.8656
SFC | Springfield Central | Goodna Bulk Supply | SFC33kVB1_Term | 33 | 11.6018 | 663.1297 | 1.8335 | 34.9324 | 1.0005 | 9.9958 | 190.4462 | 10.0308 | 191.1116 | 0.26785 | 1.7871 | 3.4322 | 30.4813 | 0.26925 | 1.8044
SFC | Springfield Central | Goodna Bulk Supply | SFC33kVB2_Term | 33 | 7.7622 | 443.6709 | 1.5028 | 28.6315 | 0.83859 | 6.6712 | 127.1031 | 6.7049 | 127.7452 | 0.47451 | 2.6588 | 4.9435 | 36.0774 | 0.48519 | 2.6973
SFC | Springfield Central | Goodna Bulk Supply | SFC11kVB1_Term | 11 | 10.0994 | 192.4197 | 1.9287 | 12.2487 | 1.0685 | 8.7138 | 55.34 | 8.7748 | 55.7273 | 0.04184 | 0.69068 | 0.01688 | 9.4852 | 0.04243 | 0.69366
SFC | Springfield Central | Goodna Bulk Supply | SFC11kVB2_Term | 11 | 10.0994 | 192.4197 | 1.9287 | 12.2487 | 1.0685 | 8.7138 | 55.34 | 8.7748 | 55.7273 | 0.04184 | 0.69068 | 0.01688 | 9.4852 | 0.04243 | 0.69366
SFD | Stafford Bulk | Stafford Bulk Supply | 43620 STAFRD1D | 110 | 14.2403 | 2713.1387 | 14.4942 | 920.5027 | 14.8245 | 14.0792 | 894.1482 | 14.6577 | 930.8891 | 0.81654 | 4.8387 | 0.45219 | 4.6103 | 0.82252 | 4.8625
SFD | Stafford Bulk | Stafford Bulk Supply | SFD33kVB1_Term | 33 | 20.2455 | 1157.1842 | 3.1294 | 59.6235 | 1.6998 | 17.4398 | 332.2724 | 17.5835 | 335.0115 | 0.09202 | 1.0314 | 0.03744 | 18.0276 | 0.0928 | 1.0364
SFD | Stafford | Stafford Bulk Supply | SFD11kVB1_Term | 11 | 6.1358 | 116.9032 | 2.1558 | 13.6912 | 1.1386 | 5.8694 | 37.2759 | 4.7585 | 30.2204 | 0.05876 | 1.1373 | 9.0485 | 0.97161 | 0.05885 | 1.1379
SFD | Stafford | Stafford Bulk Supply | SFD11kVB2_Term | 11 | 6.0203 | 114.7019 | 2.1561 | 13.693 | 1.1395 | 5.7703 | 36.6466 | 4.6575 | 29.5791 | 0.04402 | 1.1599 | 9.0338 | 1.0453 | 0.04411 | 1.1604
SGT | Sangate Bulk | Sandgate Bulk Supply | 43610 SANDGT1D | 110 | 17.3706 | 3309.5343 | 18.1172 | 1150.6 | 19.0806 | 17.7293 | 1125.9588 | 17.837 | 1132.8005 | 0.45215 | 3.9971 | 0.35257 | 3.4772 | 0.45145 | 4.0278
SGT | Sangate Bulk | Sandgate Bulk Supply | SGT33kVB1_Term | 33 | 16.4202 | 938.5388 | 2.2149 | 42.1998 | 1.1906 | 14.1662 | 269.9034 | 14.2298 | 271.1139 | 0.07202 | 1.2746 | 0.0322 | 25.8364 | 0.07182 | 1.281
SGT | Sangate | Sandgate Bulk Supply | SGT11kVB1_Term | 11 | 10.9827 | 209.2483 | 1.9383 | 12.3098 | 1.069 | 9.459 | 60.0725 | 9.4967 | 60.3122 | 0.02515 | 0.63572 | 0.02108 | 9.5364 | 0.02492 | 0.64248
SGT | Sangate | Sandgate Bulk Supply | SGT11kVB2_Term | 11 | 10.9827 | 209.2483 | 1.9383 | 12.3098 | 1.069 | 9.459 | 60.0725 | 9.4967 | 60.3122 | 0.02515 | 0.63572 | 0.02108 | 9.5364 | 0.02492 | 0.64248
SHW | Sherwood | Tennyson Bulk Supply | SHW33kVB1_Term | 33 | 21.4708 | 1227.2208 | 3.0154 | 57.4519 | 1.6259 | 18.5119 | 352.6988 | 18.6186 | 354.7314 | 0.09108 | 0.97217 | 0.49355 | 18.897 | 0.09168 | 0.97719
SHW | Sherwood | Tennyson Bulk Supply | SHW11kVB1_Term | 11 | 10.9665 | 208.9389 | 1.9455 | 12.3555 | 1.0678 | 9.4857 | 60.2422 | 9.5306 | 60.5277 | 0.029 | 0.63658 | 0.01888 | 9.5021 | 0.02906 | 0.63714
SHW | Sherwood | Tennyson Bulk Supply | SHW11kVB2_Term | 11 | 10.9665 | 208.9389 | 1.9455 | 12.3555 | 1.0678 | 9.4857 | 60.2422 | 9.5306 | 60.5277 | 0.029 | 0.63658 | 0.01888 | 9.5021 | 0.02906 | 0.63714
SIS | Stradboke Island Bulk | Beenleigh Bulk Supply (Including Bay Islands) | 43640 STRDBK1D | 110 | 2.6021 | 495.768 | 3.353 | 212.9444 | 4.647 | 2.8638 | 181.8768 | 3.5705 | 226.7595 | 14.8926 | 22.3823 | 0.67516 | 9.8829 | 14.8938 | 22.4127
SIS | Stradboke Island | Beenleigh Bulk Supply (Including Bay Islands) | SIS33kVB1_Term | 33 | 5.1088 | 292.0052 | 1.0838 | 20.6491 | 0.6027 | 4.3313 | 82.522 | 4.5329 | 86.3632 | 1.434 | 3.8495 | 0.04358 | 50.3173 | 1.4341 | 3.8523
SIS | Stradboke Island | Beenleigh Bulk Supply (Including Bay Islands) | SIS11kVB1_Term | 11 | 3.3872 | 64.5352 | 0.88763 | 5.6372 | 0.51031 | 2.914 | 18.5064 | 2.9743 | 18.8892 | 0.26925 | 2.0476 | 0.10991 | 19.5389 | 0.26926 | 2.048
SIS | Stradboke Island | Beenleigh Bulk Supply (Including Bay Islands) | SIS11kVB2_Term | 11 | 3.3872 | 64.5352 | 0.88763 | 5.6372 | 0.51031 | 2.914 | 18.5064 | 2.9743 | 18.8892 | 0.26925 | 2.0476 | 0.10991 | 19.5389 | 0.26926 | 2.048
SIS | Stradboke Island | Beenleigh Bulk Supply (Including Bay Islands) | SIS11kVB3_Term | 11 | 3.3872 | 64.5352 | 0.88763 | 5.6372 | 0.51031 | 2.914 | 18.5064 | 2.9743 | 18.8892 | 0.26925 | 2.0476 | 0.10991 | 19.5389 | 0.26926 | 2.048
SMF | Samford | Brendale Bulk Supply | SMF33kVB1_Term | 33 | 5.9738 | 341.4487 | 1.7976 | 34.2487 | 1.0569 | 5.0828 | 96.8407 | 5.2977 | 100.9343 | 1.0288 | 3.3548 | 2.1869 | 28.0023 | 1.0291 | 3.3685
SMF | Samford | Brendale Bulk Supply | SMF11kVB1_Term | 11 | 7.6964 | 146.6354 | 1.8495 | 11.7455 | 1.0508 | 6.6086 | 41.9702 | 6.752 | 42.8808 | 0.13225 | 0.89821 | 0.02054 | 9.5329 | 0.13228 | 0.89972
SMF | Samford | Brendale Bulk Supply | SMF11kVB2_Term | 11 | 7.697 | 146.6481 | 1.8495 | 11.7458 | 1.0508 | 6.6092 | 41.9739 | 6.7526 | 42.8845 | 0.13223 | 0.89813 | 0.02053 | 9.5328 | 0.13226 | 0.89965
SMR | Sumner | Sumner Bulk Supply | SMR11kVB1_Term | 11 | 9.1298 | 173.9463 | 3.3648 | 21.3695 | 2.062 | 8.0405 | 51.0644 | 7.9038 | 50.1957 | 0.02121 | 0.76515 | 0.47025 | 4.679 | 0.02127 | 0.76539
SMR | Sumner | Sumner Bulk Supply | SMR11kVB2_Term | 11 | 9.2701 | 176.6189 | 3.3774 | 21.4493 | 2.0644 | 8.1616 | 51.8334 | 8.0239 | 50.9584 | 0.02063 | 0.75358 | 0.47025 | 4.679 | 0.02069 | 0.75382
SPC | Spring Creek | Gatton Bulk Supply | SPC33kVB1_Term | 33 | 5.7219 | 327.0494 | 1.3888 | 26.46 | 0.78779 | 4.8891 | 93.1505 | 5.0551 | 96.312 | 1.0149 | 3.5201 | 2.1994 | 38.046 | 1.0143 | 3.5173
SPC | Spring Creek | Gatton Bulk Supply | SPC11kVB1_Term | 11 | 4.781 | 91.0911 | 0.9565 | 6.0746 | 0.53105 | 4.1213 | 26.1736 | 4.1774 | 26.5303 | 0.1648 | 1.4522 | 0.05203 | 19.008 | 0.16473 | 1.4518
SPD | Surfers Paradise | Molendinar Bulk Supply | 43660 SURFPD1D | 110 | 17.8934 | 3409.1438 | 22.0523 | 1400.5058 | 28.7154 | 22.1511 | 1406.7827 | 20.0356 | 1272.4298 | 0.40476 | 3.8853 | 0.53906 | 1.6342 | 0.40544 | 3.8931
SPD | Surfers Paradise | Molendinar Bulk Supply | SPD11kVB1_Term | 11 | 10.1155 | 192.7269 | 1.9425 | 12.3367 | 1.0836 | 8.7501 | 55.5709 | 8.6705 | 55.0651 | 0.01663 | 0.69077 | 0.9405 | 9.358 | 0.01664 | 0.70178
SPD | Surfers Paradise | Molendinar Bulk Supply | SPD11kVB2_Term | 11 | 10.2665 | 195.6037 | 1.9481 | 12.3722 | 1.076 | 8.9436 | 56.7996 | 8.8699 | 56.3316 | 0.01975 | 0.68054 | 0.9405 | 9.358 | 0.01976 | 0.68062
SPD | Surfers Paradise | Molendinar Bulk Supply | SPD11kVB3_Term | 11 | 10.1155 | 192.7269 | 1.9425 | 12.3367 | 1.0836 | 8.7501 | 55.5709 | 8.6705 | 55.0651 | 0.01663 | 0.69077 | 0.9405 | 9.358 | 0.01664 | 0.70178
SPD | Surfers Paradise | Molendinar Bulk Supply | SPD11kVB4_Term | 11 | 9.7701 | 186.1462 | 1.9358 | 12.2938 | 1.0741 | 8.5167 | 54.0882 | 8.4387 | 53.5928 | 0.01757 | 0.7152 | 0.9405 | 9.358 | 0.01758 | 0.71528
SPD | Surfers Paradise | Molendinar Bulk Supply | SPD11kVB5_Term | 11 | 10.2665 | 195.6037 | 1.9481 | 12.3722 | 1.076 | 8.9436 | 56.7996 | 8.8699 | 56.3316 | 0.01975 | 0.68054 | 0.9405 | 9.358 | 0.01976 | 0.68062
SPD | Surfers Paradise | Molendinar Bulk Supply | SPD11kVB6_Term | 11 | 9.7701 | 186.1462 | 1.9358 | 12.2938 | 1.0741 | 8.5167 | 54.0882 | 8.4387 | 53.5928 | 0.01757 | 0.7152 | 0.9405 | 9.358 | 0.01758 | 0.71528
SPE | Samford | Brendale Bulk Supply | SPE33kVB1_Term | 33 | 17.618 | 1007.0024 | 3.0393 | 57.9058 | 1.6669 | 15.153 | 288.7036 | 15.3315 | 292.1046 | 0.16436 | 1.1784 | 0.47941 | 18.3127 | 0.16348 | 1.1847
SPE | Samford | Brendale Bulk Supply | SPE11kVB1_Term | 11 | 10.6323 | 202.5728 | 1.9386 | 12.3116 | 1.067 | 9.191 | 58.3704 | 9.2462 | 58.7212 | 0.03666 | 0.65617 | 0.01839 | 9.4999 | 0.03656 | 0.65687
SPE | Samford | Brendale Bulk Supply | SPE11kVB2_Term | 11 | 10.6323 | 202.5728 | 1.9386 | 12.3116 | 1.067 | 9.191 | 58.3704 | 9.2462 | 58.7212 | 0.03666 | 0.65617 | 0.01839 | 9.4999 | 0.03656 | 0.65687
SPF | Springfield | Goodna Bulk Supply | SPF33kVB1_Term | 33 | 15.2603 | 872.2434 | 2.0133 | 38.3585 | 1.0847 | 13.1171 | 249.9152 | 13.1786 | 251.0856 | 0.1808 | 1.3619 | 2.0805 | 28.403 | 0.18196 | 1.3788
SPF | Springfield | Goodna Bulk Supply | SPF11kVB1_Term | 11 | 10.1043 | 192.5128 | 1.9241 | 12.2199 | 1.0648 | 8.7279 | 55.4293 | 8.7826 | 55.7771 | 0.03823 | 0.69055 | 0.01814 | 9.5123 | 0.03836 | 0.69243
SPF | Springfield | Goodna Bulk Supply | SPF11kVB2_Term | 11 | 10.1043 | 192.5128 | 1.9241 | 12.2199 | 1.0648 | 8.7279 | 55.4293 | 8.7826 | 55.7771 | 0.03823 | 0.69055 | 0.01814 | 9.5123 | 0.03836 | 0.69243
SPO | Southport | Molendinar Bulk Supply | 43580 STHPRT1D | 110 | 15.6859 | 2988.5579 | 17.6564 | 1121.3293 | 20.2192 | 17.4581 | 1108.7389 | 16.3775 | 1040.1111 | 0.57597 | 4.4187 | 0.72405 | 2.8798 | 0.57701 | 4.4286
SPO | Southport | Molendinar Bulk Supply | SPO11kVB1_Term | 11 | 10.8476 | 206.674 | 1.9609 | 12.4533 | 1.0777 | 9.4471 | 59.9973 | 9.3707 | 59.5123 | 0.01834 | 0.6441 | 0.95763 | 9.3592 | 0.01836 | 0.6442
SPO | Southport | Molendinar Bulk Supply | SPO11kVB2_Term | 11 | 9.6668 | 184.1763 | 1.9325 | 12.273 | 1.0734 | 8.4261 | 53.513 | 8.3503 | 53.0314 | 0.02051 | 0.72279 | 0.95763 | 9.3592 | 0.02052 | 0.72289
SPO | Southport | Molendinar Bulk Supply | SPO11kVB3_Term | 11 | 10.6372 | 202.6655 | 1.9562 | 12.4234 | 1.077 | 9.2632 | 58.8292 | 9.1909 | 58.3702 | 0.02124 | 0.65677 | 0.95763 | 9.3592 | 0.02125 | 0.65687
SPO | Southport | Molendinar Bulk Supply | SPO11kVB4_Term | 11 | 9.6668 | 184.1763 | 1.9325 | 12.273 | 1.0734 | 8.4261 | 53.513 | 8.3503 | 53.0314 | 0.02051 | 0.72279 | 0.95763 | 9.3592 | 0.02052 | 0.72289
SPO | Southport | Molendinar Bulk Supply | SPO11kVB5_Term | 11 | 10.8476 | 206.674 | 1.9609 | 12.4533 | 1.0777 | 9.4471 | 59.9973 | 9.3707 | 59.5123 | 0.01834 | 0.6441 | 0.95763 | 9.3592 | 0.01836 | 0.6442
SPO | Southport | Molendinar Bulk Supply | SPO11kVB6_Term | 11 | 10.6372 | 202.6655 | 1.9562 | 12.4234 | 1.077 | 9.2632 | 58.8292 | 9.1909 | 58.3702 | 0.02124 | 0.65677 | 0.95763 | 9.3592 | 0.02125 | 0.65687
SRD | Scrub Rd | Belmont Bulk Supply | SRD33kVB1_Term | 33 | 21.6018 | 1234.7096 | 1.1244 | 21.4221 | 0.5661 | 18.9187 | 360.4491 | 18.3559 | 349.7266 | 0.16645 | 0.95636 | 55.5829 | -3.928 | 0.16554 | 0.96396
SRD | Scrub Rd | Belmont Bulk Supply | SRD11kVB1_Term | 11 | 10.2356 | 195.0153 | 1.9222 | 12.2074 | 1.0612 | 8.8378 | 56.1273 | 8.9121 | 56.5992 | 0.05218 | 0.6809 | 0.03368 | 9.5459 | 0.05208 | 0.68175
SRD | Scrub Rd | Belmont Bulk Supply | SRD11kVB2_Term | 11 | 6.4203 | 122.3228 | 0.99079 | 6.2923 | 0.53945 | 5.5268 | 35.0998 | 5.5564 | 35.2876 | 0.06547 | 1.0867 | 0.04921 | 18.9798 | 0.06492 | 1.0969
SRD | Scrub Rd | Belmont Bulk Supply | SRD11kVB3_Term | 11 | 10.2356 | 195.0153 | 1.9222 | 12.2074 | 1.0612 | 8.8378 | 56.1273 | 8.9121 | 56.5992 | 0.05218 | 0.6809 | 0.03368 | 9.5459 | 0.05208 | 0.68175
SRH | Sunrise Hills Bulk | Sunrise Hills Bulk Supply | 43651 SNRHLL1D | 132 | 7.3743 | 1685.9966 | 8.8544 | 674.7973 | 11.0621 | 7.9801 | 608.1633 | 8.8894 | 677.4654 | 3.1518 | 10.9242 | 0.34532 | 5.7473 | 3.109 | 10.9574
SRH | Sunrise Hills Bulk | Sunrise Hills Bulk Supply | SRH33kVB1_Term | 33 | 12.6599 | 723.6121 | 2.1943 | 41.807 | 1.2009 | 10.8932 | 207.5435 | 11.0561 | 210.6462 | 0.23609 | 1.6388 | 0.01629 | 25.3739 | 0.23341 | 1.6409
STL | St Lucia | Tennyson Bulk Supply | STL33kVB1_Term | 33 | 13.838 | 790.9455 | 2.5944 | 49.4301 | 1.4339 | 11.9586 | 227.841 | 12.0138 | 228.8943 | 0.18799 | 1.5033 | 1.7872 | 21.1338 | 0.18858 | 1.5083
STL | St Lucia | Tennyson Bulk Supply | STL33kVB2_Term | 33 | 14.0312 | 801.9905 | 2.5985 | 49.5089 | 1.4344 | 12.1271 | 231.053 | 12.1783 | 232.0277 | 0.18101 | 1.4831 | 1.7889 | 21.1365 | 0.1816 | 1.4882
STL | St Lucia | Tennyson Bulk Supply | STL33kVB3_Term | 33 | 14.0342 | 802.1635 | 2.6404 | 50.3074 | 1.46 | 12.1309 | 231.1238 | 12.1814 | 232.086 | 0.20986 | 1.479 | 2.1822 | 20.7138 | 0.21045 | 1.484
STL | St Lucia | Tennyson Bulk Supply | STL11kVB1_Term | 11 | 5.2926 | 100.8367 | 2.104 | 13.362 | 1.1302 | 5.1312 | 32.5876 | 4.0384 | 25.6472 | 0.08711 | 1.3175 | 9.0662 | 1.093 | 0.08718 | 1.3181
STL | St Lucia | Tennyson Bulk Supply | STL11kVB2_Term | 11 | 10.4532 | 199.1593 | 2.257 | 14.3336 | 1.1544 | 9.6199 | 61.0945 | 8.4788 | 53.8478 | 0.03947 | 0.66736 | 9.0247 | 0.51025 | 0.03954 | 0.66792
STT | Stapylton | Beenleigh Bulk Supply (Including Bay Islands) | STT33kVB1_Term | 33 | 8.6854 | 496.4357 | 2.2123 | 42.1493 | 1.2657 | 7.4333 | 141.6238 | 7.6555 | 145.857 | 0.63041 | 2.3389 | 1.8226 | 23.6832 | 0.63 | 2.3412
STT | Stapylton | Beenleigh Bulk Supply (Including Bay Islands) | STT11kVB1_Term | 11 | 8.9119 | 169.7943 | 1.8993 | 12.0622 | 1.0625 | 7.6792 | 48.7693 | 7.7905 | 49.476 | 0.08813 | 0.78197 | 0.02488 | 9.5111 | 0.08808 | 0.78222
STT | Stapylton | Beenleigh Bulk Supply (Including Bay Islands) | STT11kVB2_Term | 11 | 8.9124 | 169.8033 | 1.8993 | 12.0623 | 1.0625 | 7.6796 | 48.772 | 7.7909 | 49.4786 | 0.08811 | 0.78193 | 0.02487 | 9.5111 | 0.08807 | 0.78218
T70 | SST70 Cooroy 132kV Bulk Supply | Cooroy Bulk Supply | 40700 COOROY1D | 132 | 9.2168 | 2107.2387 | 9.5556 | 728.2331 | 9.9424 | 9.2682 | 706.332 | 9.5269 | 726.0451 | 2.2004 | 8.8268 | 1.5404 | 7.967 | 2.1576 | 8.86
TBV | Tamborine Village | Beenleigh Bulk Supply (Including Bay Islands) | TBV33kVB1_Term | 33 | 1.9313 | 110.3896 | 0.8754 | 16.6786 | 0.56374 | 1.6429 | 31.302 | 1.7475 | 33.2944 | 4.2606 | 10.0258 | 9.681 | 49.7112 | 4.2602 | 10.0281
TBV | Tamborine Village | Beenleigh Bulk Supply (Including Bay Islands) | TBV11kVB1_Term | 11 | 2.5894 | 49.3347 | 3.0654 | 19.4679 | 3.7504 | 2.8171 | 17.8911 | 3.0255 | 19.2145 | 0.58916 | 2.6435 | 0.11576 | 1.453 | 0.58911 | 2.6437
TCB | Tin Can Bay | Gympie Bulk Supply | TCB33kVB2_Term | 33 | 1.4001 | 80.025 | 0.46593 | 8.8772 | 0.27777 | 1.1831 | 22.5412 | 1.2567 | 23.9441 | 5.7457 | 13.8246 | 11.0836 | 105.4087 | 5.7405 | 13.8255
TCB | Tin Can Bay | Gympie Bulk Supply | TCB33kVB3_Term | 33 | 1.4012 | 80.0882 | 0.46607 | 8.8798 | 0.27784 | 1.1842 | 22.5613 | 1.2576 | 23.9605 | 5.7253 | 13.8203 | 11.0496 | 105.3907 | 5.7201 | 13.8212
TCB | Tin Can Bay | Gympie Bulk Supply | TCB11kVB2_Term | 11 | 2.1365 | 40.7056 | 2.5889 | 16.4415 | 3.2781 | 2.3735 | 15.0737 | 2.5664 | 16.2988 | 0.74929 | 3.1833 | 0.11087 | 1.5684 | 0.74871 | 3.1834
TCB | Tin Can Bay | Gympie Bulk Supply | TCB11kVB3_Term | 11 | 2.1279 | 40.5429 | 2.5791 | 16.3797 | 3.2686 | 2.3798 | 15.1137 | 2.5438 | 16.1553 | 0.81354 | 3.181 | 0.1774 | 1.5622 | 0.81297 | 3.1811
TGP | Tingalpa | Doboy Bulk Supply | TGP33kVB1_Term | 33 | 12.8677 | 735.4861 | 2.683 | 51.1173 | 1.4974 | 10.9952 | 209.487 | 11.3006 | 215.306 | 0.42575 | 1.573 | 0.9938 | 20.2216 | 0.42558 | 1.5793
TGP | Tingalpa | Doboy Bulk Supply | TGP11kVB1_Term | 11 | 9.7885 | 186.4951 | 1.9116 | 12.1406 | 1.0594 | 8.443 | 53.6206 | 8.5359 | 54.2101 | 0.06676 | 0.71094 | 0.02217 | 9.5453 | 0.06674 | 0.71164
TGP | Tingalpa | Doboy Bulk Supply | TGP11kVB2_Term | 11 | 9.7885 | 186.4951 | 1.9116 | 12.1406 | 1.0594 | 8.443 | 53.6206 | 8.5359 | 54.2101 | 0.06676 | 0.71094 | 0.02217 | 9.5453 | 0.06674 | 0.71164
TGW | Toogoolawah | Lockrose Bulk Supply | TGW33kVB1_Term | 33 | 1.451 | 82.9365 | 0.66997 | 12.7646 | 0.43185 | 1.2152 | 23.1531 | 1.3317 | 25.3713 | 7.476 | 12.3617 | 15.4617 | 64.0688 | 7.4751 | 12.3704
TGW | Toogoolawah | Lockrose Bulk Supply | TGW11kVB1_Term | 11 | 2.1979 | 41.8764 | 2.6503 | 16.8319 | 3.3251 | 2.3788 | 15.1076 | 2.6673 | 16.9398 | 0.93997 | 3.0369 | 0.10931 | 1.5802 | 0.93988 | 3.0379
THL | Tenthill | Gatton Bulk Supply | THL33kVB1_Term | 33 | 2.7334 | 156.2348 | 0.99002 | 18.8624 | 0.6012 | 2.3145 | 44.0971 | 2.4566 | 46.8047 | 2.7264 | 7.1678 | 5.0551 | 48.3121 | 2.7258 | 7.165
THL | Tenthill | Gatton Bulk Supply | THL11kVB1_Term | 11 | 2.9103 | 55.4479 | 3.3326 | 21.165 | 3.8945 | 3.1004 | 19.6904 | 3.2675 | 20.7511 | 0.41859 | 2.3642 | 0.11565 | 1.4894 | 0.41853 | 2.3638
TLF | Toolara Forest | Gympie Bulk Supply | TLF33kVB1_Term | 33 | 2.8168 | 160.9992 | 0.99528 | 18.9626 | 0.60063 | 2.3786 | 45.3177 | 2.5349 | 48.2969 | 2.8397 | 6.8783 | 5.1383 | 48.4908 | 2.8345 | 6.8792
TLF | Toolara Forest | Gympie Bulk Supply | TLF11kVB2_Term | 11 | 5.2689 | 100.3864 | 1.736 | 11.0248 | 1.0342 | 4.4681 | 28.3763 | 4.7133 | 29.9333 | 0.34177 | 1.2813 | 0.02625 | 9.491 | 0.3412 | 1.2814
TMH | Tanah Merah | Loganlea Bulk Supply | TMH33kVB1_Term | 33 | 8.7314 | 499.0686 | 2.2948 | 43.7218 | 1.3204 | 7.5073 | 143.0331 | 7.6661 | 146.059 | 0.55426 | 2.3375 | 2.3794 | 22.5212 | 0.55447 | 2.3397
TMH | Tanah Merah | Loganlea Bulk Supply | TMH11kVB1_Term | 11 | 8.8737 | 169.0668 | 1.8956 | 12.0386 | 1.0607 | 7.6466 | 48.5624 | 7.7569 | 49.2632 | 0.08771 | 0.78302 | 0.02613 | 9.4972 | 0.08774 | 0.78327
TMH | Tanah Merah | Loganlea Bulk Supply | TMH11kVB2_Term | 11 | 8.8737 | 169.0668 | 1.8956 | 12.0386 | 1.0607 | 7.6466 | 48.5624 | 7.7569 | 49.2632 | 0.08771 | 0.78302 | 0.02613 | 9.4972 | 0.08774 | 0.78327
TPT | Toorbal Point | Caboolture Bulk Supply | TPT33kVB1_Term | 33 | 4.3062 | 246.1323 | 1.5984 | 30.4538 | 0.97694 | 3.6915 | 70.3334 | 3.8416 | 73.1929 | 1.3582 | 4.6745 | 3.2296 | 29.5552 | 1.3265 | 4.6657
TPT | Toorbal Point | Caboolture Bulk Supply | TPT11kVB1_Term | 11 | 5.3932 | 102.7551 | 2.0779 | 13.1962 | 1.1266 | 5.2101 | 33.0886 | 4.1431 | 26.3123 | 0.2332 | 1.2744 | 9.0823 | 0.71726 | 0.22968 | 1.2734
TRG | Taringa | Tennyson Bulk Supply | TRG33kVB1_Term | 33 | 19.9774 | 1141.859 | 3.0095 | 57.3391 | 1.6313 | 17.2231 | 328.1448 | 17.3362 | 330.2982 | 0.12772 | 1.0416 | 0.9514 | 18.7752 | 0.12832 | 1.0466
TRG | Taringa | Tennyson Bulk Supply | TRG11kVB1_Term | 11 | 11.3415 | 216.0855 | 1.9582 | 12.4364 | 1.072 | 9.8033 | 62.2592 | 9.8614 | 62.6281 | 0.03588 | 0.61512 | 0.0214 | 9.4748 | 0.03594 | 0.61568
TRG | Taringa | Tennyson Bulk Supply | TRG11kVB2_Term | 11 | 11.3415 | 216.0855 | 1.9582 | 12.4364 | 1.072 | 9.8033 | 62.2592 | 9.8614 | 62.6281 | 0.03588 | 0.61512 | 0.0214 | 9.4748 | 0.03594 | 0.61568
TRP | Tarampa | Lockrose Bulk Supply | TRP33kVB1_Term | 33 | 3.0673 | 175.3174 | 1.2927 | 24.6286 | 0.80949 | 2.5615 | 48.8041 | 2.8108 | 53.5526 | 3.278 | 5.9969 | 5.465 | 35.1596 | 3.2732 | 5.9861
TRP | Tarampa | Lockrose Bulk Supply | TRP11kVB1_Term | 11 | 3.1164 | 59.3748 | 3.5404 | 22.4844 | 4.0896 | 3.2709 | 20.773 | 3.498 | 22.2152 | 0.53002 | 2.1787 | 0.16579 | 1.4367 | 0.52948 | 2.1775
TRP | Tarampa | Lockrose Bulk Supply | TRP11kVB2_Term | 11 | 2.989 | 56.9481 | 3.379 | 21.4594 | 3.8786 | 3.129 | 19.8716 | 3.3372 | 21.1939 | 0.54179 | 2.2741 | 0.17757 | 1.5274 | 0.54126 | 2.2729
TSN | Tennyson Bulk | Tennyson Bulk Supply | TSN33kVB1_Term | 33 | 24.8611 | 1421.005 | 3.1427 | 59.8768 | 1.6825 | 21.4275 | 408.2486 | 21.5405 | 410.4017 | 0.05814 | 0.84127 | 0.00851 | 18.3248 | 0.05873 | 0.84628
TSN | Tennyson | Tennyson Bulk Supply | TSN11kVB1_Term | 11 | 11.4517 | 218.184 | 1.9573 | 12.4307 | 1.0706 | 9.9087 | 62.929 | 9.9462 | 63.1669 | 0.0231 | 0.6098 | 0.01664 | 9.4905 | 0.02316 | 0.61036
TSN | Tennyson | Tennyson Bulk Supply | TSN11kVB2_Term | 11 | 11.4517 | 218.184 | 1.9573 | 12.4307 | 1.0706 | 9.9087 | 62.929 | 9.9462 | 63.1669 | 0.0231 | 0.6098 | 0.01664 | 9.4905 | 0.02316 | 0.61036
TUG | Tugun Desal | Burleigh Head Bulk Supply | TUG33kVB1_Term | 33 | 10.0966 | 577.0952 | 1.0837 | 20.6478 | 0.54585 | 9.0151 | 171.7612 | 8.4726 | 161.4238 | 0.33179 | 2.0501 | 57.3821 | -3.9552 | 0.33169 | 2.0502
TUG | Tugun Desal | Burleigh Head Bulk Supply | TUG33kVB2_Term | 33 | 10.101 | 577.3504 | 1.0838 | 20.6497 | 0.54589 | 9.019 | 171.8354 | 8.4764 | 161.4969 | 0.33153 | 2.0492 | 57.3774 | -3.9567 | 0.33142 | 2.0493
TWG | Toowong | Ashgrove West Bulk Supply | TWG33kVB1_Term | 33 | 15.2494 | 871.6186 | 2.1084 | 40.1706 | 1.1333 | 13.1687 | 250.8967 | 13.2482 | 252.4127 | 0.16542 | 1.3648 | 1.3182 | 27.0524 | 0.16594 | 1.3669
TWG | Toowong | Ashgrove West Bulk Supply | TWG11kVB1_Term | 11 | 10.2859 | 195.9725 | 1.926 | 12.2316 | 1.0625 | 8.8945 | 56.4878 | 8.9498 | 56.8386 | 0.03815 | 0.67832 | 0.02164 | 9.5278 | 0.0382 | 0.67855
TWG | Toowong | Ashgrove West Bulk Supply | TWG11kVB2_Term | 11 | 10.2859 | 195.9725 | 1.926 | 12.2316 | 1.0625 | 8.8945 | 56.4878 | 8.9498 | 56.8386 | 0.03815 | 0.67832 | 0.02164 | 9.5278 | 0.0382 | 0.67855
TWT | Tewantin | Sunrise Hills Bulk Supply | TWT33kVB1_Term | 33 | 9.5287 | 544.6403 | 1.9691 | 37.5172 | 1.0966 | 8.1683 | 155.6272 | 8.3659 | 159.3917 | 0.45302 | 2.1526 | 0.47683 | 27.5972 | 0.45035 | 2.1547
TWT | Tewantin | Sunrise Hills Bulk Supply | TWT11kVB1_Term | 11 | 8.9917 | 171.3143 | 1.8956 | 12.0388 | 1.0593 | 7.7604 | 49.2852 | 7.8474 | 49.8378 | 0.06837 | 0.77404 | 0.01804 | 9.5083 | 0.06808 | 0.77428
TWT | Tewantin | Sunrise Hills Bulk Supply | TWT11kVB2_Term | 11 | 8.9917 | 171.3143 | 1.8956 | 12.0388 | 1.0593 | 7.7604 | 49.2852 | 7.8474 | 49.8378 | 0.06837 | 0.77404 | 0.01804 | 9.5083 | 0.06808 | 0.77428
UMG | Upper Mt Gravatt | Belmont Bulk Supply | UMG33kVB1_Term | 33 | 21.0437 | 1202.8094 | 1.1459 | 21.8324 | 0.57639 | 18.4469 | 351.4601 | 17.8721 | 340.5087 | 0.12952 | 0.98803 | 54.6214 | -3.4609 | 0.12844 | 0.99535
UMG | Upper Mt Gravatt | Belmont Bulk Supply | UMG11kVB1_Term | 11 | 6.2322 | 118.7388 | 0.98905 | 6.2813 | 0.53732 | 5.3909 | 34.2365 | 5.4132 | 34.3782 | 0.05026 | 1.1205 | 0.0357 | 18.9599 | 0.05014 | 1.1213
UMG | Upper Mt Gravatt | Belmont Bulk Supply | UMG11kVB2_Term | 11 | 11.1074 | 211.6244 | 1.9483 | 12.3731 | 1.0684 | 9.603 | 60.9874 | 9.6532 | 61.3064 | 0.03265 | 0.62846 | 0.02837 | 9.5052 | 0.03253 | 0.62927
UMG | Upper Mt Gravatt | Belmont Bulk Supply | UMG11kVB3_Term | 11 | 11.1084 | 211.6437 | 1.9483 | 12.3733 | 1.0684 | 9.6039 | 60.993 | 9.6541 | 61.3118 | 0.03262 | 0.6284 | 0.02835 | 9.5052 | 0.0325 | 0.62921
VGA | Virginia | Nudgee Bulk Supply | VGA33kVB1_Term | 33 | 17.3687 | 992.7562 | 3.0463 | 58.039 | 1.674 | 14.9198 | 284.261 | 15.121 | 288.093 | 0.16192 | 1.196 | 0.16137 | 18.2388 | 0.1616 | 1.2035
VPK | Victoria Park Bulk | Victoria Park Bulk Supply | 43680 VICPRK1D | 110 | 22.4052 | 4268.7623 | 27.1537 | 1724.4902 | 34.986 | 26.9434 | 1711.1332 | 25.1863 | 1599.5421 | 0.34544 | 3.1005 | 0.36334 | 1.4078 | 0.35084 | 3.1411
VPK | Victoria Park | Victoria Park Bulk Supply | VPK33kVB1_Term | 33 | 20.6108 | 1178.0659 | 2.3074 | 43.9625 | 1.1634 | 18.3969 | 350.5075 | 17.2381 | 328.43 | 0.04978 | 1.0162 | 27.0372 | 0.57991 | 0.05026 | 1.0198
VPK | Victoria Park | Victoria Park Bulk Supply | VPK11kVB1_Term | 11 | 11.0821 | 211.1423 | 3.5125 | 22.3075 | 2.1025 | 9.6739 | 61.4375 | 9.5171 | 60.4415 | 0.01368 | 0.63051 | 0.47029 | 4.6791 | 0.01275 | 0.63891
VPK | Victoria Park | Victoria Park Bulk Supply | VPK11kVB2_Term | 11 | 11.0821 | 211.1423 | 3.5125 | 22.3075 | 2.1025 | 9.6739 | 61.4375 | 9.5171 | 60.4415 | 0.01368 | 0.63051 | 0.47029 | 4.6791 | 0.01275 | 0.63891
VPK | Victoria Park | Victoria Park Bulk Supply | VPK11kVB3_Term | 11 | 11.0821 | 211.1423 | 3.5125 | 22.3075 | 2.1025 | 9.6739 | 61.4375 | 9.5171 | 60.4415 | 0.01368 | 0.63051 | 0.47029 | 4.6791 | 0.01275 | 0.63891
VPK | Victoria Park | Victoria Park Bulk Supply | VPK11kVB4_Term | 11 | 9.2262 | 175.7826 | 3.3736 | 21.4253 | 2.0647 | 8.1237 | 51.5923 | 7.9803 | 50.6817 | 0.01856 | 0.75735 | 0.47029 | 4.6792 | 0.01855 | 0.75823
VPK | Victoria Park | Victoria Park Bulk Supply | VPK11kVB5_Term | 11 | 9.2262 | 175.7826 | 3.3736 | 21.4253 | 2.0647 | 8.1237 | 51.5923 | 7.9803 | 50.6817 | 0.01856 | 0.75735 | 0.47029 | 4.6792 | 0.01855 | 0.75823
VPK | Victoria Park | Victoria Park Bulk Supply | VPK11kVB6_Term | 11 | 9.2262 | 175.7826 | 3.3736 | 21.4253 | 2.0647 | 8.1237 | 51.5923 | 7.9803 | 50.6817 | 0.01856 | 0.75735 | 0.47029 | 4.6792 | 0.01855 | 0.75823
VPT | Victoria Point | Cleveland Bulk Supply | VPT33kVB1_Term | 33 | 12.2509 | 700.2328 | 1.9755 | 37.6385 | 1.0753 | 10.5672 | 201.3322 | 10.6573 | 203.0484 | 0.25055 | 1.6933 | 1.6937 | 28.3789 | 0.24974 | 1.697
VPT | Victoria Point | Cleveland Bulk Supply | VPT33kVB2_Term | 33 | 12.2363 | 699.3964 | 1.9748 | 37.6257 | 1.075 | 10.5545 | 201.0908 | 10.6447 | 202.8084 | 0.25132 | 1.6952 | 1.6992 | 28.3853 | 0.25051 | 1.699
VPT | Victoria Point | Cleveland Bulk Supply | VPT11kVB1_Term | 11 | 9.7555 | 185.8683 | 1.9155 | 12.1647 | 1.0621 | 8.4314 | 53.5463 | 8.4943 | 53.946 | 0.04642 | 0.71501 | 0.02882 | 9.5167 | 0.04633 | 0.71543
VPT | Victoria Point | Cleveland Bulk Supply | VPT11kVB2_Term | 11 | 9.7562 | 185.8808 | 1.9155 | 12.1648 | 1.0621 | 8.432 | 53.5501 | 8.4948 | 53.9496 | 0.0464 | 0.71496 | 0.02881 | 9.5167 | 0.04631 | 0.71538
VSF | Valdora Solar Farm | Nambour Bulk Supply | VSFPV33kVB1_Term | 33 | 4.289 | 245.1495 | 1.2249 | 23.3367 | 0.71336 | 3.6605 | 69.7426 | 3.7947 | 72.2992 | 1.3948 | 4.6839 | 3.4337 | 41.5785 | 1.37 | 4.701
VSL | Varsity Lakes | Mudgeeraba Bulk Supply | 43690 VARSIT1D | 110 | 16.5531 | 3153.7806 | 19.2897 | 1225.0592 | 22.8257 | 20.0778 | 1275.1138 | 16.3816 | 1040.3703 | 0.45733 | 4.1977 | 1.1979 | 2.2674 | 0.45614 | 4.1983
VSL | Varsity Lakes | Mudgeeraba Bulk Supply | 43691 VARSIT2D | 110 | 16.5531 | 3153.7806 | 19.2897 | 1225.0604 | 22.8258 | 20.0777 | 1275.1037 | 16.3819 | 1040.3883 | 0.45733 | 4.1977 | 1.1978 | 2.2675 | 0.45614 | 4.1983
VSL | Varsity Lakes | Mudgeeraba Bulk Supply | VSL11kVB1_Term | 11 | 9.0276 | 171.9995 | 3.3562 | 21.3146 | 2.0603 | 7.9559 | 50.527 | 7.8148 | 49.631 | 0.01964 | 0.77399 | 0.47025 | 4.679 | 0.01963 | 0.774
VSL | Varsity Lakes | Mudgeeraba Bulk Supply | VSL11kVB2_Term | 11 | 9.0276 | 171.9995 | 3.3562 | 21.3146 | 2.0603 | 7.9559 | 50.527 | 7.8148 | 49.631 | 0.01964 | 0.77399 | 0.47025 | 4.679 | 0.01963 | 0.774
VSP | Visy Paper | Doboy Bulk Supply | VSP33kVB1_Term | 33 | 21.7632 | 1243.9369 | 3.2497 | 61.9157 | 1.7634 | 18.7582 | 357.392 | 18.8329 | 358.8139 | 0.09406 | 0.95889 | 0.93237 | 17.3995 | 0.09415 | 0.96659
WCL | Wacol | Richlands Bulk Supply | WCL33kVB1_Term | 33 | 15.2993 | 874.4717 | 2.828 | 53.8799 | 1.5644 | 13.1843 | 251.194 | 13.2625 | 252.6841 | 0.18431 | 1.358 | 1.612 | 19.4271 | 0.1854 | 1.3685
WCL | Wacol | Richlands Bulk Supply | WCL33kVB2_Term | 33 | 15.4123 | 880.9282 | 2.8207 | 53.7424 | 1.5619 | 13.2625 | 252.6838 | 13.3335 | 254.0368 | 0.17852 | 1.3486 | 1.6564 | 19.4952 | 0.18097 | 1.3638
WCL | Wacol | Richlands Bulk Supply | WCL33kVB3_Term | 33 | 16.9162 | 966.8919 | 3.0746 | 58.5798 | 1.7014 | 14.5539 | 277.2892 | 14.6347 | 278.8283 | 0.18615 | 1.2254 | 1.8249 | 17.8742 | 0.18855 | 1.2393
WCL | Wacol | Richlands Bulk Supply | WCL11kVB1_Term | 11 | 5.8664 | 111.7692 | 0.98116 | 6.2312 | 0.5356 | 5.0738 | 32.2228 | 5.0963 | 32.3658 | 0.05373 | 1.1901 | 0.03325 | 18.9873 | 0.05385 | 1.1913
WCL | Wacol | Richlands Bulk Supply | WCL11kVB2_Term | 11 | 5.8664 | 111.7692 | 0.98116 | 6.2312 | 0.5356 | 5.0738 | 32.2228 | 5.0963 | 32.3658 | 0.05373 | 1.1901 | 0.03325 | 18.9873 | 0.05385 | 1.1913
WCL | Wacol | Richlands Bulk Supply | WCL11kVB3_Term | 11 | 12.2229 | 232.8779 | 1.9659 | 12.4853 | 1.1013 | 10.2906 | 65.3538 | 10.339 | 65.6616 | 0.02657 | 0.57114 | 0.01725 | 9.4895 | 0.02858 | 0.60376
WCL | Wacol | Richlands Bulk Supply | WCL11kVB4_Term | 11 | 12.2229 | 232.8779 | 1.9659 | 12.4853 | 1.1013 | 10.2906 | 65.3538 | 10.339 | 65.6616 | 0.02657 | 0.57114 | 0.01725 | 9.4895 | 0.02858 | 0.60376
WED | West End | CBD Bulk Supply | 43720 WSTEND1D | 110 | 19.9717 | 3805.1284 | 21 | 1333.6777 | 22.2192 | 21.6228 | 1373.2314 | 19.3637 | 1229.7573 | 0.69275 | 3.4298 | 1.1447 | 2.772 | 0.69866 | 3.4539
WED | West End | CBD Bulk Supply | WED11kVB3_Term | 11 | 9.715 | 185.0953 | 1.9279 | 12.2436 | 1.0701 | 8.4653 | 53.7618 | 8.3927 | 53.3006 | 0.02119 | 0.71901 | 0.9439 | 9.3913 | 0.02124 | 0.71925
WED | West End | CBD Bulk Supply | WED11kVB4_Term | 11 | 10.7121 | 204.0931 | 1.9521 | 12.3974 | 1.0739 | 9.3272 | 59.2356 | 9.2543 | 58.7728 | 0.01938 | 0.65207 | 0.94381 | 9.3902 | 0.01943 | 0.65231
WED | West End | CBD Bulk Supply | WED11kVB5_Term | 11 | 10.7121 | 204.0932 | 1.9521 | 12.3974 | 1.0739 | 9.3272 | 59.2357 | 9.2543 | 58.7728 | 0.01938 | 0.65207 | 0.94381 | 9.3902 | 0.01943 | 0.65231
WED | West End | CBD Bulk Supply | WED11kVB6_Term | 11 | 9.6645 | 184.134 | 1.919 | 12.1874 | 1.0652 | 8.4209 | 53.4801 | 8.3495 | 53.0266 | 0.02191 | 0.72274 | 0.94811 | 9.4337 | 0.02197 | 0.72298
WFD | Wooford | Beerwah Bulk Supply | WFD33kVB2_Term | 33 | 1.8863 | 107.8148 | 0.79077 | 15.0661 | 0.50007 | 1.6264 | 30.9865 | 1.6767 | 31.9447 | 3.745 | 10.4628 | 13.1542 | 55.8583 | 3.7424 | 10.4778
WFD | Wooford | Beerwah Bulk Supply | WFD33kVB1_Term | 33 | 2.2818 | 130.422 | 0.81696 | 15.5651 | 0.51046 | 1.8685 | 35.5991 | 2.014 | 38.3715 | 4.0416 | 8.2494 | 8.8431 | 58.0998 | 4.3615 | 8.6669
WFD | Wooford | Beerwah Bulk Supply | WFD11kVB1_Term | 11 | 3.8705 | 73.7437 | 5.4458 | 34.5855 | 9.6516 | 6.0715 | 38.5594 | 5.6643 | 35.9734 | 0.53426 | 1.7243 | 0.13482 | 0.1492 | 0.5698 | 1.7707
WFD | Wooford | Beerwah Bulk Supply | WFD11kVB2_Term | 11 | 3.0768 | 58.6213 | 0.89301 | 5.6714 | 0.5211 | 2.6261 | 16.6781 | 2.7258 | 17.3114 | 0.46895 | 2.222 | 0.05284 | 19.0065 | 0.46866 | 2.2237
WGT | Wooloongabba Tunnel | Doboy Bulk Supply | WGT22kVB1_Term | 22 | 4.5575 | 173.6642 | 0.10993 | 1.3962 | 0.05504 | 3.9726 | 50.4581 | 3.9177 | 49.7611 | 0.2089 | 3.0602 | 381 | 2.1206 | 0.20883 | 3.063
WMD | West Maroochydore | Palmwood Bulk Supply | 43741 WMAROO1D | 132 | 10.9259 | 2497.9863 | 11.7336 | 894.2174 | 12.7541 | 11.4706 | 874.174 | 11.3202 | 862.7152 | 1.2159 | 7.5772 | 1.0736 | 5.947 | 1.1942 | 7.6284
WMD | West Maroochydore | Palmwood Bulk Supply | WMD11kVB1_Term | 11 | 10.0052 | 190.625 | 1.9408 | 12.3258 | 1.0748 | 8.7071 | 55.2974 | 8.6515 | 54.9445 | 0.03257 | 0.69759 | 0.9405 | 9.358 | 0.03242 | 0.69795
WMD | West Maroochydore | Palmwood Bulk Supply | WMD11kVB2_Term | 11 | 9.4692 | 180.4119 | 1.927 | 12.2378 | 1.0727 | 8.2526 | 52.4109 | 8.1796 | 51.9476 | 0.02176 | 0.73757 | 0.9405 | 9.358 | 0.02161 | 0.73792
WMR | Wamuran | Caboolture Bulk Supply | WMR33kVB1_Term | 33 | 3.6918 | 211.0159 | 1.37 | 26.1013 | 0.84038 | 3.1303 | 59.6413 | 3.3015 | 62.9012 | 1.8989 | 5.351 | 4.0159 | 34.5 | 1.9008 | 5.382
WMR | Wamuran | Caboolture Bulk Supply | WMR11kVB1_Term | 11 | 3.2275 | 61.4926 | 3.6121 | 22.9399 | 4.1061 | 3.3968 | 21.5724 | 3.536 | 22.4563 | 0.32519 | 2.1403 | 0.11421 | 1.4685 | 0.32541 | 2.1438
WNM | Wynnum | Lytton Bulk Supply | WNM33kVB1_Term | 33 | 8.1673 | 466.8263 | 1.0505 | 20.015 | 0.56166 | 7.0576 | 134.4655 | 7.0915 | 135.1102 | 0.23673 | 2.5565 | 1.6769 | 54.7272 | 0.23712 | 2.5596
WNM | Wynnum | Lytton Bulk Supply | WNM33kVB2_Term | 33 | 8.1801 | 467.5539 | 1.0508 | 20.0203 | 0.56175 | 7.0686 | 134.6752 | 7.1025 | 135.32 | 0.23545 | 2.5526 | 1.6573 | 54.7201 | 0.23584 | 2.5556
WNM | Wynnum | Lytton Bulk Supply | WNM11kVB1_Term | 11 | 8.9413 | 170.3553 | 2.2484 | 14.279 | 1.1548 | 8.3133 | 52.7964 | 7.1712 | 45.543 | 0.03985 | 0.78071 | 9.0188 | 0.487 | 0.03989 | 0.78105
WNM | Wynnum | Lytton Bulk Supply | WNM11kVB2_Term | 11 | 8.9413 | 170.3553 | 2.2484 | 14.279 | 1.1548 | 8.3133 | 52.7964 | 7.1712 | 45.543 | 0.03985 | 0.78071 | 9.0188 | 0.487 | 0.03989 | 0.78105
WRD | Wellington Rd | Doboy Bulk Supply | 43760 WELGRD1D | 110 | 24.2006 | 4610.832 | 29.3303 | 1862.7229 | 37.8309 | 29.1825 | 1853.3406 | 27.1399 | 1723.6182 | 0.30394 | 2.8722 | 0.3431 | 1.3002 | 0.30926 | 2.9127
WRD | Wellington Rd | Doboy Bulk Supply | WRD33kVB1_Term | 33 | 11.3453 | 648.4689 | 2.5398 | 48.3896 | 1.4302 | 9.7122 | 185.0433 | 9.9578 | 189.7211 | 0.44646 | 1.7935 | 1.3196 | 21.0759 | 0.44629 | 1.7999
WRD | Wellington Rd | Doboy Bulk Supply | WRD11kVB1_Term | 11 | 12.3014 | 234.373 | 3.5492 | 22.5408 | 2.219 | 10.2068 | 64.8222 | 10.0416 | 63.7724 | 0.01993 | 0.56779 | 0.47025 | 4.679 | 0.01282 | 0.6391
WRD | Wellington Rd | Doboy Bulk Supply | WRD11kVB2_Term | 11 | 12.3014 | 234.373 | 3.5492 | 22.5408 | 2.219 | 10.2068 | 64.8222 | 10.0416 | 63.7724 | 0.01993 | 0.56779 | 0.47025 | 4.679 | 0.01282 | 0.6391
WRD | Wellington Rd | Doboy Bulk Supply | WRD11kVB3_Term | 11 | 9.3027 | 177.2399 | 3.3781 | 21.4536 | 2.0717 | 8.1686 | 51.8773 | 8.0241 | 50.9596 | 0.01871 | 0.75112 | 0.47025 | 4.679 | 0.01826 | 0.75643
WRD | Wellington Rd | Doboy Bulk Supply | WRD11kVB4_Term | 11 | 9.3027 | 177.2399 | 3.3781 | 21.4536 | 2.0717 | 8.1686 | 51.8773 | 8.0241 | 50.9596 | 0.01871 | 0.75112 | 0.47025 | 4.679 | 0.01826 | 0.75643
WRG | Woodridge | Loganlea Bulk Supply | WRG33kVB1_Term | 33 | 12.2252 | 698.7664 | 2.7452 | 52.3026 | 1.5455 | 10.4967 | 199.9897 | 10.7201 | 204.2447 | 0.3586 | 1.6779 | 1.1441 | 19.4888 | 0.35881 | 1.6801
WRG | Woodridge | Loganlea Bulk Supply | WRG11kVB1_Term | 11 | 5.7883 | 110.2825 | 0.98104 | 6.2305 | 0.53592 | 5.0041 | 31.7805 | 5.0348 | 31.9754 | 0.07362 | 1.2057 | 0.03377 | 18.9683 | 0.07364 | 1.2059
WRG | Woodridge | Loganlea Bulk Supply | WRG11kVB2_Term | 11 | 9.9457 | 189.4916 | 1.9259 | 12.2313 | 1.0661 | 8.5877 | 54.5391 | 8.6687 | 55.0534 | 0.05672 | 0.7007 | 0.01688 | 9.4886 | 0.05674 | 0.70095
WRG | Woodridge | Loganlea Bulk Supply | WRG11kVB3_Term | 11 | 9.9457 | 189.4916 | 1.9259 | 12.2313 | 1.0661 | 8.5877 | 54.5391 | 8.6687 | 55.0534 | 0.05672 | 0.7007 | 0.01688 | 9.4886 | 0.05674 | 0.70095
WSE | Whiteside | Brendale Bulk Supply | WSE33kVB1_Term | 33 | 5.4944 | 314.0493 | 1.6995 | 32.3802 | 1.0031 | 4.676 | 89.0896 | 4.8822 | 93.0183 | 1.148 | 3.6384 | 2.4595 | 29.4112 | 1.1479 | 3.6465
WSE | Whiteside | Brendale Bulk Supply | WSE11kVB1_Term | 11 | 4.8484 | 92.3742 | 0.9599 | 6.0962 | 0.5325 | 4.1746 | 26.5126 | 4.2371 | 26.9095 | 0.17994 | 1.4299 | 0.05209 | 18.9736 | 0.17993 | 1.4308
WSO | Wacol South | Richlands Bulk Supply | WSO33kVB1_Term | 33 | 12.4572 | 712.0224 | 2.3915 | 45.5638 | 1.3253 | 10.6609 | 203.118 | 10.8903 | 207.4881 | 0.39099 | 1.637 | 1.2163 | 22.9408 | 0.39208 | 1.6476
WSO | Wacol South | Richlands Bulk Supply | WSO11kVB1_Term | 11 | 10.1482 | 193.3498 | 1.9318 | 12.2688 | 1.0682 | 8.7537 | 55.5935 | 8.8413 | 56.1497 | 0.05978 | 0.68608 | 0.01634 | 9.479 | 0.0599 | 0.68725
WSO | Wacol South | Richlands Bulk Supply | WSO11kVB2_Term | 11 | 10.1482 | 193.3498 | 1.9318 | 12.2688 | 1.0682 | 8.7537 | 55.5935 | 8.8413 | 56.1497 | 0.05978 | 0.68608 | 0.01634 | 9.479 | 0.0599 | 0.68725
WSS | Whinstanes | Meeandah Bulk Supply | WSS33kVB1_Term | 33 | 12.0287 | 687.5313 | 2.0971 | 39.9559 | 1.1495 | 10.3721 | 197.6152 | 10.4747 | 199.5691 | 0.20751 | 1.7303 | 0.70324 | 26.5023 | 0.20718 | 1.7336
WSS | Whinstanes | Meeandah Bulk Supply | WSS11kVB1_Term | 11 | 9.8769 | 188.1797 | 1.9228 | 12.2116 | 1.0653 | 8.5401 | 54.2369 | 8.5959 | 54.5913 | 0.03982 | 0.70634 | 0.01676 | 9.4884 | 0.03978 | 0.70671
WSS | Whinstanes | Meeandah Bulk Supply | WSS11kVB2_Term | 11 | 9.8769 | 188.1797 | 1.9228 | 12.2116 | 1.0653 | 8.5401 | 54.2369 | 8.5959 | 54.5913 | 0.03982 | 0.70634 | 0.01676 | 9.4884 | 0.03978 | 0.70671
YDA | Yandina | Nambour Bulk Supply | YDA33kVB1_Term | 33 | 6.2764 | 358.7422 | 1.5667 | 29.8495 | 0.89562 | 5.3006 | 100.9907 | 5.5524 | 105.7873 | 1.2023 | 3.1158 | 2.3039 | 33.5964 | 1.215 | 3.147
YDA | Yandina | Nambour Bulk Supply | YDA11kVB1_Term | 11 | 5.9743 | 113.8264 | 0.97951 | 6.2207 | 0.54669 | 5.034 | 31.9703 | 5.0964 | 32.3664 | 0.14141 | 1.1609 | 0.05294 | 19.0195 | 0.1478 | 1.2159
YMT | Yamanto | Raceview Bulk Supply | YMT33kVB1_Term | 33 | 10.9031 | 623.1977 | 1.8696 | 35.6201 | 1.0232 | 9.4185 | 179.4469 | 9.4788 | 180.5964 | 0.26042 | 1.9051 | 2.2279 | 29.7151 | 0.2608 | 1.9082
YMT | Yamanto | Raceview Bulk Supply | YMT11kVB1_Term | 11 | 5.6204 | 107.0841 | 0.97678 | 6.2034 | 0.5349 | 4.8616 | 30.8755 | 4.8866 | 31.0341 | 0.06221 | 1.2418 | 0.03328 | 18.9786 | 0.06226 | 1.2422
YTA | Yatala | Beenleigh Bulk Supply | 43850 YATALA1D | 110 | 14.8599 | 2831.1987 | 14.3919 | 914.0093 | 13.9916 | 15.2065 | 965.7405 | 14.0243 | 890.662 | 1.0686 | 4.5841 | 1.8617 | 4.8278 | 1.0686 | 4.6092
YTA | Yatala | Beenleigh Bulk Supply (Including Bay Islands) | YTA33kVB1_Term | 33 | 9.614 | 549.5145 | 2.3897 | 45.5307 | 1.362 | 8.2184 | 156.5808 | 8.4795 | 161.5569 | 0.55037 | 2.118 | 1.1198 | 22.0797 | 0.54996 | 2.1203
YTA | Yatala | Beenleigh Bulk Supply (Including Bay Islands) | YTA33kVB2_Term | 33 | 9.5685 | 546.9122 | 2.3996 | 45.719 | 1.3695 | 8.1804 | 155.8569 | 8.4396 | 160.7966 | 0.5447 | 2.1302 | 1.0826 | 21.9501 | 0.54429 | 2.1325
YTA | Yatala | Beenleigh Bulk Supply (Including Bay Islands) | YTA11kVB2_Term | 11 | 7.6183 | 145.1485 | 3.2164 | 20.4269 | 2.0215 | 6.7803 | 43.0605 | 6.6422 | 42.1834 | 0.02483 | 0.91776 | 0.47025 | 4.679 | 0.02208 | 0.90648
YTA | Yatala | Beenleigh Bulk Supply (Including Bay Islands) | YTA11kVB3_Term | 11 | 7.6183 | 145.1487 | 3.2164 | 20.4269 | 2.0215 | 6.7803 | 43.0605 | 6.6422 | 42.1834 | 0.02483 | 0.91776 | 0.47025 | 4.679 | 0.02208 | 0.90647
YTA | Yatala | Beenleigh Bulk Supply (Including Bay Islands) | YTA11kVB4_Term | 11 | 7.6183 | 145.1487 | 3.2164 | 20.4269 | 2.0215 | 6.7803 | 43.0605 | 6.6422 | 42.1834 | 0.02483 | 0.91776 | 0.47025 | 4.679 | 0.02208 | 0.90647
YTA | Yatala | Beenleigh Bulk Supply (Including Bay Islands) | YTA11kVTR1_Term | 11 | 5.5266 | 105.2963 | 0.97815 | 6.2121 | 0.53649 | 4.7736 | 30.3163 | 4.8128 | 30.5657 | 0.09869 | 1.2651 | 0.03728 | 18.977 | 0.09864 | 1.2653
YTA | Yatala | Beenleigh Bulk Supply (Including Bay Islands) | YTA11kVTR2_Term | 11 | 5.6173 | 107.023 | 0.98091 | 6.2296 | 0.53731 | 4.852 | 30.8144 | 4.8912 | 31.063 | 0.0965 | 1.2447 | 0.03577 | 18.9572 | 0.09646 | 1.245
YTA | Yatala | Beenleigh Bulk Supply (Including Bay Islands) | YTABESS11kVB1_Term | 11 | 7.6183 | 145.1485 | 3.2164 | 20.4269 | 2.0215 | 6.7803 | 43.0605 | 6.6422 | 42.1834 | 0.02483 | 0.91776 | 0.47025 | 4.679 | 0.02208 | 0.90648
ZMR | Zillmere | Sandgate Bulk Supply | ZMR33kVB1_Term | 33 | 10.4765 | 598.8122 | 1.9191 | 36.5643 | 1.057 | 8.9924 | 171.3289 | 9.1561 | 174.4462 | 0.38365 | 1.9638 | 0.89681 | 28.7924 | 0.38345 | 1.9702
ZMR | Zillmere | Sandgate Bulk Supply | ZMR11kVB1_Term | 11 | 9.739 | 185.5536 | 2.2415 | 14.2355 | 1.1529 | 8.9975 | 57.1419 | 7.864 | 49.9431 | 0.06466 | 0.71455 | 9.024 | 0.48759 | 0.06464 | 0.71526
ZMR | Zillmere | Sandgate Bulk Supply | ZMR11kVB2_Term | 11 | 9.739 | 185.5536 | 2.2415 | 14.2355 | 1.1529 | 8.9975 | 57.1419 | 7.864 | 49.9431 | 0.06466 | 0.71455 | 9.024 | 0.48759 | 0.06464 | 0.71526