## Notes
Transmission Feeders Forecasts (Energex Distribution Annual Planning Report 2021-22 to 2025-26)
This workbook provides 5 year forecast capacity and loading information for sub-transmission feeders in the Energex network.
This workbook forms part of the Energex Distribution Annual Planning Report 2021-22 to 2025-26 (DAPR) and should be read in conjunction with the report document.
Energex Distribution Annual Planning Report is prepared and made available solely for information purposes. While care was taken in the preparation of the information in this report, and it is provided in good faith, Energex accepts no responsibility or liability (including without limitation, liability to any person by reason of negligence or negligent mis-statement) for any loss or damage that may be incurred by any person acting in reliance on this information or assumptions drawn from it, except to the extent that liability under any applicable Queensland or Commonwealth of Australia statute cannot be excluded.
It contains assumptions regarding, among other things, economic growth and load forecasts which may or may not prove to be correct. The forecasts included in the document involve subjective judgements and analysis which are subject to significant uncertainties and contingencies, many of which are out of the control of Energex. Furthermore, forecasted data is subject to ongoing variation due to COVID 19 impacts. Energex makes no representation or warranty as to the accuracy, reliability, completeness or suitability for any particular purpose of the information in this document. All information should be independently investigated, reviewed, analysed and verified, and must not be relied upon in connection with any investment proposal or decision.
The following sections list the 110kV and 132kV feeders, their forecast loads, power factor, customer category and available load transfers. The feeder loads are calculated from load flow results using forecast substation demands. For the transmission and sub-transmission feeders, load flow studies are conducted for system normal and single contingency situations.
The forecast and capacity cut-off date for the winter season is 1 June of each year, and for the summer season is 1 December of each year. For example, 2022 winter forecast includes all committed projects with a proposed commissioning date up to 1 June 2022, and the 2021/22 summer forecast includes all committed projects with a proposed commissioning date up to 1 December 2021.
Assessment of 110kV & 132kV feeders is performed under four possible risk periods: winter day, winter night, summer day and summer night. For the summer table, the worst case (highest) load between summer day and summer night has been represented in the table.
Peak, reconciled, compensated load forecasts have been used in the 110kV & 132kV feeder analyses, with 50 PoE forecast load used for single contingency studies, and 10 PoE forecast load used for system normal studies.
Feeder capacities are shown for ECC and NCC. These ratings have also been adjusted for known committed projects. All load transfers associated with contingent condition include acceptable feeder voltage profiles.
Although the conductor rating is generally the limiting factor for feeder capacity, there are other significant items of plant, such as the feeder circuit breaker, that can also restrict capacity. Furthermore, other factors such as voltage constraints and load sharing between parallel underground feeders can sometimes de‑rate the capacity of the feeders due to thermal characteristic constraints. Each of these factors has been taken into account in the production of the forecast tables.
Interconnected feeders that supply multiple customers are examined in the following tables. Feeders exclusively supplying a customer owned substation or dedicated to a customer are not included in these tables.
A definition of terms is shown in the table below.
Definition of Terms Feeder Capacity and Forecast Tables
Term | Definition
NCC Rating (A) | Normal Cyclic Capacity - the total capacity with all network components and equipment intact. This is the maximum permissible peak daily loading for a given load cycle that a feeder can supply each day of its life. For overhead feeders, the NCC is the conductor rating with an assumed 1m/s wind, orthogonal to the line. For underground cables, the NCC assumes that there are sufficient temperature and current operating margins from the thermal inertia of the cable and its surroundings.
10 PoE Load (A) | Peak load forecast with 10% probability of being exceeded (one in every 10 years will be exceeded). Based on normal expected growth rates and weather corrected starting loads.
Power Factor (System Normal) | Lowest power factor along the feeder at 10 PoE Peak Load. Where the Power Factor is 0 the feeder is a normally open feeder that does not have load under System Normal conditions.
ECC Rating (A) | Emergency Cyclic Capacity – the long term firm delivery capacity under single contingency conditions. Some underground cables are installed in close proximity to other circuits and are normally de‑rated to allow for the heat generated by the adjacent cables. ECC is the higher capacity available when any adjacent circuits have been unloaded. For overhead conductors which do not benefit from this phenomenon, the ECC is synonymous with the NCC.
50 PoE Load (A) | Peak load forecast with 50% probability of being exceeded (one in every two years will be exceeded). Based on normal expected growth rates & weather corrected starting loads. This is the worst case (highest) load forecast beween summer day and summer night.
Security Standard | For security standard application, the general type of customer a sub-transmission, or transmission feeder is supplying.
Transfers | This is the total amount of load transfers that are available following the worst case network contingency. This includes automatic transfers that are controlled automatically through SCADA and are generally implemented within a minute, load transfers that can be implemented through screen switching by a network controller, manual transfers that are deployed via manually controlled switchgear locally by field staff, and mobile generation which can be deployed by field staff by moving generation to specific sites. It should be noted under the Safety Net in the Distribution Authority, it is generally assumed that 4MVA (21A @ 110kV) of generation is available for Urban feeders to meet this criteria and 10MVA (52A) is available for Rural feeders. These values have been used as a default in the forecast tables where these are sufficient to reduce the 50PoE load below the ECC rating. Where the load is still above the ECC rating, specific load transfers have been calculated for the feeder to determine whether the Safety Net criteria is met.
Hours PA > 95% Peak Load | The forecast number of hours per annum where the load exceeded 95% of the peak 50 PoE demand. This information is not readily available for every feeder without significant analysis being undertaken. As such, this has only been provided where a feeder does not meet the Safety Net criteria or is otherwise in the Limitations and Proposed Solutions table.

## 110kV & 132kV Feeders - Winter
Connection Point | Feeder | From Substation | To Substation | Attributes | 2021 | 2022 | 2023 | 2024 | 2025 | Security Standard | Transfers | Hours above 95% | Voltage (kV)
Abermain | F7259/1 | Abermain | Wulkuraka Tee | NCC Rating (A) | 613 | 613 | 613 | 613 | 613 | Rural | 150 | NA | 110
|  |  |  | 10 POE Load (A) | 270 | 268 | 269 | 275 | 302 |  |  |  | 110
|  |  |  | Power Factor | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 |  |  |  | 110
|  |  |  | ECC Rating (A) | 613 | 613 | 613 | 613 | 613 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 378 | 385 | 386 | 390 | 419 |  |  |  | 110
Abermain | F7259/2 | Wulkuraka Tee | Lockrose | NCC Rating (A) | 613 | 613 | 613 | 613 | 613 | Rural | 52 | NA | 110
|  |  |  | 10 POE Load (A) | 239 | 237 | 238 | 244 | 271 |  |  |  | 110
|  |  |  | Power Factor | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 |  |  |  | 110
|  |  |  | ECC Rating (A) | 613 | 613 | 613 | 613 | 613 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 347 | 354 | 355 | 359 | 388 |  |  |  | 110
Abermain | F7289 | Lockrose | Gatton | NCC Rating (A) | 690 | 690 | 690 | 690 | 690 | Rural | 52 | NA | 110
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0 |  |  |  | 110
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0 |  |  |  | 110
|  |  |  | ECC Rating (A) | 690 | 690 | 690 | 690 | 690 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 232 | 230 | 231 | 236 | 263 |  |  |  | 110
Belmont | F750 | Belmont | Beenleigh | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Rural | 52 | NA | 110
|  |  |  | 10 POE Load (A) | 182 | 172 | 175 | 173 | 186 |  |  |  | 110
|  |  |  | Power Factor | 0.96 | 0.95 | 0.91 | 0.91 | 0.92 |  |  |  | 110
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 274 | 269 | 271 | 268 | 269 |  |  |  | 110
Belmont | F766 | Belmont | Cleveland | NCC Rating (A) | 1600 | 1600 | 1600 | 1600 | 1600 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 360 | 349 | 349 | 349 | 352 |  |  |  | 110
|  |  |  | Power Factor | 0.96 | 0.97 | 0.97 | 0.97 | 0.97 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1600 | 1600 | 1600 | 1600 | 1600 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 699 | 692 | 696 | 690 | 697 |  |  |  | 110
Belmont | F767 | Belmont | Cleveland | NCC Rating (A) | 1600 | 1600 | 1600 | 1600 | 1600 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 345 | 349 | 349 | 349 | 352 |  |  |  | 110
|  |  |  | Power Factor | 0.98 | 0.97 | 0.97 | 0.97 | 0.97 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1600 | 1600 | 1600 | 1600 | 1600 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 699 | 692 | 696 | 690 | 697 |  |  |  | 110
Blackstone | F713 | Blackstone | Raceview | NCC Rating (A) | 1131 | 1131 | 1131 | 1131 | 1131 | Rural | 52 | NA | 110
|  |  |  | 10 POE Load (A) | 184 | 185 | 188 | 190 | 194 |  |  |  | 110
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1131 | 1131 | 1131 | 1131 | 1131 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 353 | 356 | 362 | 365 | 375 |  |  |  | 110
Blackstone | F714 | Blackstone | Raceview | NCC Rating (A) | 1131 | 1131 | 1131 | 1131 | 1131 | Rural | 52 | NA | 110
|  |  |  | 10 POE Load (A) | 183 | 185 | 188 | 190 | 194 |  |  |  | 110
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1131 | 1131 | 1131 | 1131 | 1131 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 353 | 356 | 362 | 365 | 375 |  |  |  | 110
CBD East | F7231 | Wellington Road | Charlotte St | NCC Rating (A) | 1283 | 1283 | 1283 | 1283 | 1283 | CBD | NA | NA | 110
|  |  |  | 10 POE Load (A) | 240 | 288 | 299 | 310 | 319 |  |  |  | 110
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1283 | 1283 | 1283 | 1283 | 1283 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 455 | 548 | 570 | 588 | 603 |  |  |  | 110
CBD East | F7232 | Wellington Road | Charlotte St | NCC Rating (A) | 1283 | 1283 | 1283 | 1283 | 1283 | CBD | NA | NA | 110
|  |  |  | 10 POE Load (A) | 240 | 288 | 299 | 310 | 319 |  |  |  | 110
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1283 | 1283 | 1283 | 1283 | 1283 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 455 | 548 | 570 | 588 | 603 |  |  |  | 110
CBD East | F7287/3 | Tingalpa Tee | Wellington Road | NCC Rating (A) | 1197 | 1197 | 1197 | 1197 | 1197 | CBD | NA | NA | 110
|  |  |  | 10 POE Load (A) | 503 | 552 | 560 | 571 | 582 |  |  |  | 110
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1197 | 1197 | 1197 | 1197 | 1197 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 806 | 893 | 907 | 917 | 934 |  |  |  | 110
CBD East | F7288/3 | Tingalpa Tee | Wellington Road | NCC Rating (A) | 1197 | 1197 | 1197 | 1197 | 1197 | CBD | NA | NA | 110
|  |  |  | 10 POE Load (A) | 506 | 555 | 563 | 572 | 583 |  |  |  | 110
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1197 | 1197 | 1197 | 1197 | 1197 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 809 | 895 | 909 | 919 | 936 |  |  |  | 110
CBD East | F7230 | Wellington Road | Coorparoo | NCC Rating (A) | 1300 | 1300 | 1300 | 1300 | 1300 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 163 | 164 | 165 | 165 | 166 |  |  |  | 110
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1300 | 1300 | 1300 | 1300 | 1300 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 311 | 313 | 315 | 312 | 316 |  |  |  | 110
CBD East | F7362 | Wellington Road | Coorparoo | NCC Rating (A) | 1300 | 1300 | 1300 | 1300 | 1300 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 163 | 164 | 165 | 165 | 166 |  |  |  | 110
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1300 | 1300 | 1300 | 1300 | 1300 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 311 | 313 | 315 | 312 | 316 |  |  |  | 110
CBD East | F752 | Murarrie | Newstead | NCC Rating (A) | 1456 | 1456 | 1456 | 1456 | 1456 | CBD | NA | NA | 110
|  |  |  | 10 POE Load (A) | 256 | 275 | 280 | 287 | 293 |  |  |  | 110
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1456 | 1456 | 1456 | 1456 | 1456 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 338 | 364 | 373 | 380 | 387 |  |  |  | 110
CBD East | F753 | Murarrie | Newstead | NCC Rating (A) | 1456 | 1456 | 1456 | 1456 | 1456 | CBD | NA | NA | 110
|  |  |  | 10 POE Load (A) | 256 | 275 | 280 | 287 | 293 |  |  |  | 110
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1456 | 1456 | 1456 | 1456 | 1456 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 338 | 364 | 373 | 380 | 387 |  |  |  | 110
CBD East | F809 | Newstead | Victoria Park | NCC Rating (A) | 704 | 704 | 704 | 704 | 704 | CBD | NA | NA | 110
|  |  |  | 10 POE Load (A) | 86 | 90 | 92 | 97 | 101 |  |  |  | 110
|  |  |  | Power Factor | 0.98 | 0.98 | 0.98 | 0.99 | 0.99 |  |  |  | 110
|  |  |  | ECC Rating (A) | 704 | 704 | 704 | 704 | 704 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 168 | 175 | 184 | 193 | 205 |  |  |  | 110
CBD East | F810 | Newstead | Victoria Park | NCC Rating (A) | 704 | 704 | 704 | 704 | 704 | CBD | NA | NA | 110
|  |  |  | 10 POE Load (A) | 86 | 90 | 92 | 97 | 101 |  |  |  | 110
|  |  |  | Power Factor | 0.98 | 0.98 | 0.98 | 0.99 | 0.99 |  |  |  | 110
|  |  |  | ECC Rating (A) | 704 | 704 | 704 | 704 | 704 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 168 | 175 | 184 | 193 | 205 |  |  |  | 110
CBD East | F829 | Charlotte St | Ann St | NCC Rating (A) | 963 | 963 | 963 | 963 | 963 | CBD | NA | NA | 110
|  |  |  | 10 POE Load (A) | 127 | 144 | 150 | 157 | 164 |  |  |  | 110
|  |  |  | Power Factor | 1 | 1 | 1 | 0.99 | 0.99 |  |  |  | 110
|  |  |  | ECC Rating (A) | 963 | 963 | 963 | 963 | 963 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 253 | 286 | 300 | 308 | 322 |  |  |  | 110
CBD East | F833 | Charlotte St | Ann St | NCC Rating (A) | 963 | 963 | 963 | 963 | 963 | CBD | NA | NA | 110
|  |  |  | 10 POE Load (A) | 127 | 144 | 150 | 157 | 164 |  |  |  | 110
|  |  |  | Power Factor | 1 | 1 | 1 | 0.99 | 0.99 |  |  |  | 110
|  |  |  | ECC Rating (A) | 963 | 963 | 963 | 963 | 963 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 253 | 286 | 300 | 308 | 322 |  |  |  | 110
CBD East | F834 | McLachlan St | Ann St | NCC Rating (A) | 967 | 967 | 967 | 967 | 967 | CBD | NA | NA | 110
|  |  |  | 10 POE Load (A) | 147 | 162 | 172 | 188 | 200 |  |  |  | 110
|  |  |  | Power Factor | 0.98 | 0.99 | 1 | 0.98 | 0.98 |  |  |  | 110
|  |  |  | ECC Rating (A) | 967 | 967 | 967 | 967 | 967 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 318 | 347 | 363 | 376 | 393 |  |  |  | 110
CBD East | F835 | McLachlan St | Victoria Park | NCC Rating (A) | 967 | 967 | 967 | 967 | 967 | CBD | NA | NA | 110
|  |  |  | 10 POE Load (A) | 174 | 181 | 192 | 204 | 220 |  |  |  | 110
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1 |  |  |  | 110
|  |  |  | ECC Rating (A) | 967 | 967 | 967 | 967 | 967 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 227 | 238 | 251 | 264 | 283 |  |  |  | 110
CBD East | F914 | Newstead | McLachlan St | NCC Rating (A) | 1305 | 1305 | 1305 | 1305 | 1305 | CBD | NA | NA | 110
|  |  |  | 10 POE Load (A) | 87 | 91 | 91 | 95 | 96 |  |  |  | 110
|  |  |  | Power Factor | 0.98 | 0.98 | 0.99 | 0.96 | 0.96 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1305 | 1305 | 1305 | 1305 | 1305 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 149 | 159 | 161 | 164 | 166 |  |  |  | 110
CBD East | F915 | Newstead | McLachlan St | NCC Rating (A) | 1305 | 1305 | 1305 | 1305 | 1305 | CBD | NA | NA | 110
|  |  |  | 10 POE Load (A) | 87 | 91 | 91 | 95 | 96 |  |  |  | 110
|  |  |  | Power Factor | 0.98 | 0.98 | 0.99 | 0.96 | 0.96 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1305 | 1305 | 1305 | 1305 | 1305 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 149 | 159 | 161 | 164 | 166 |  |  |  | 110
CBD South | F830 | West End | Charlotte St | NCC Rating (A) | 690 | 690 | 690 | 690 | 690 | CBD | NA | NA | 110
|  |  |  | 10 POE Load (A) | 233 | 232 | 239 | 243 | 239 |  |  |  | 110
|  |  |  | Power Factor | 0.23 | 0.28 | 0.32 | 0.34 | 0.36 |  |  |  | 110
|  |  |  | ECC Rating (A) | 690 | 690 | 690 | 690 | 690 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 386 | 389 | 401 | 402 | 404 |  |  |  | 110
CBD South | F905 | Rocklea | West End | NCC Rating (A) | 693 | 693 | 693 | 693 | 693 | CBD | NA | NA | 110
|  |  |  | 10 POE Load (A) | 315 | 322 | 335 | 342 | 344 |  |  |  | 110
|  |  |  | Power Factor | 0.77 | 0.79 | 0.81 | 0.81 | 0.83 |  |  |  | 110
|  |  |  | ECC Rating (A) | 693 | 693 | 693 | 693 | 693 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 495 | 502 | 519 | 523 | 529 |  |  |  | 110
CBD West | F7266 | Milton | Customer | NCC Rating (A) | 966 | 966 | 966 | 966 | 966 | CBD | NA | NA | 110
|  |  |  | 10 POE Load (A) | 154 | 156 | 156 | 158 | 155 |  |  |  | 110
|  |  |  | Power Factor | 0.59 | 0.6 | 0.62 | 0.62 | 0.62 |  |  |  | 110
|  |  |  | ECC Rating (A) | 966 | 966 | 966 | 966 | 966 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 309 | 319 | 323 | 321 | 329 |  |  |  | 110
CBD West | F7267 | Milton | Makerston St | NCC Rating (A) | 966 | 966 | 966 | 966 | 966 | CBD | NA | NA | 110
|  |  |  | 10 POE Load (A) | 159 | 166 | 167 | 175 | 177 |  |  |  | 110
|  |  |  | Power Factor | 0.6 | 0.62 | 0.66 | 0.67 | 0.68 |  |  |  | 110
|  |  |  | ECC Rating (A) | 966 | 966 | 966 | 966 | 966 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 313 | 323 | 327 | 326 | 333 |  |  |  | 110
CBD West | F7321 | Customer | Makerston St | NCC Rating (A) | 966 | 966 | 966 | 966 | 966 | CBD | NA | NA | 110
|  |  |  | 10 POE Load (A) | 98 | 101 | 99 | 104 | 105 |  |  |  | 110
|  |  |  | Power Factor | 0.26 | 0.29 | 0.33 | 0.36 | 0.39 |  |  |  | 110
|  |  |  | ECC Rating (A) | 966 | 966 | 966 | 966 | 966 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 249 | 259 | 261 | 264 | 275 |  |  |  | 110
CBD West | F7365 | Kelvin Grove | Milton | NCC Rating (A) | 973 | 973 | 973 | 973 | 973 | CBD | NA | NA | 110
|  |  |  | 10 POE Load (A) | 160 | 164 | 168 | 172 | 172 |  |  |  | 110
|  |  |  | Power Factor | 0.67 | 0.68 | 0.71 | 0.71 | 0.72 |  |  |  | 110
|  |  |  | ECC Rating (A) | 973 | 973 | 973 | 973 | 973 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 374 | 384 | 397 | 395 | 403 |  |  |  | 110
CBD West | F781 | Ashgrove West | Kelvin Grove | NCC Rating (A) | 913 | 913 | 913 | 913 | 913 | CBD | NA | NA | 110
|  |  |  | 10 POE Load (A) | 205 | 209 | 215 | 219 | 219 |  |  |  | 110
|  |  |  | Power Factor | 0.81 | 0.82 | 0.83 | 0.83 | 0.84 |  |  |  | 110
|  |  |  | ECC Rating (A) | 913 | 913 | 913 | 913 | 913 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 417 | 428 | 442 | 441 | 449 |  |  |  | 110
CBD West | F782 | Ashgrove West | Milton | NCC Rating (A) | 913 | 913 | 913 | 913 | 913 | CBD | NA | NA | 110
|  |  |  | 10 POE Load (A) | 237 | 242 | 249 | 254 | 254 |  |  |  | 110
|  |  |  | Power Factor | 0.78 | 0.79 | 0.81 | 0.81 | 0.81 |  |  |  | 110
|  |  |  | ECC Rating (A) | 913 | 913 | 913 | 913 | 913 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 425 | 435 | 450 | 449 | 457 |  |  |  | 110
CBD West | F807 | Makerston St | Charlotte St | NCC Rating (A) | 629 | 629 | 629 | 629 | 629 | CBD | NA | NA | 110
|  |  |  | 10 POE Load (A) | 103 | 103 | 105 | 107 | 105 |  |  |  | 110
|  |  |  | Power Factor | 0.35 | 0.39 | 0.42 | 0.43 | 0.44 |  |  |  | 110
|  |  |  | ECC Rating (A) | 629 | 629 | 629 | 629 | 629 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 229 | 232 | 232 | 229 | 235 |  |  |  | 110
CBD West | F808 | Makerston St | Charlotte St | NCC Rating (A) | 629 | 629 | 629 | 629 | 629 | CBD | NA | NA | 110
|  |  |  | 10 POE Load (A) | 124 | 124 | 128 | 130 | 128 |  |  |  | 110
|  |  |  | Power Factor | 0.18 | 0.25 | 0.31 | 0.35 | 0.39 |  |  |  | 110
|  |  |  | ECC Rating (A) | 629 | 629 | 629 | 629 | 629 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 257 | 255 | 256 | 245 | 247 |  |  |  | 110
Loganlea | F704 | Beenleigh | Yatala | NCC Rating (A) | 1088 | 1088 | 1088 | 1088 | 1088 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 262 | 249 | 267 | 257 | 292 |  |  |  | 110
|  |  |  | Power Factor | 0.91 | 0.91 | 0.88 | 0.89 | 0.94 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1088 | 1088 | 1088 | 1088 | 1088 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 643 | 652 | 654 | 657 | 662 |  |  |  | 110
Loganlea | F7351 | Jimboomba | Beaudesert | NCC Rating (A) | 865 | 865 | 865 | 865 | 865 | Rural | 52 | NA | 110
|  |  |  | 10 POE Load (A) | 179 | 182 | 190 | 198 | 205 |  |  |  | 110
|  |  |  | Power Factor | 0.97 | 0.97 | 0.97 | 0.96 | 0.96 |  |  |  | 110
|  |  |  | ECC Rating (A) | 865 | 865 | 865 | 865 | 865 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 175 | 179 | 189 | 197 | 202 |  |  |  | 110
Loganlea | F7354 | Loganlea | Jimboomba | NCC Rating (A) | 952 | 952 | 952 | 952 | 952 | Rural | 52 | NA | 110
|  |  |  | 10 POE Load (A) | 292 | 297 | 306 | 316 | 328 |  |  |  | 110
|  |  |  | Power Factor | 0.96 | 0.96 | 0.95 | 0.95 | 0.95 |  |  |  | 110
|  |  |  | ECC Rating (A) | 952 | 952 | 952 | 952 | 952 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 469 | 476 | 496 | 511 | 526 |  |  |  | 110
Loganlea | F7377 | Yatala | Coomera | NCC Rating (A) | 1088 | 1088 | 1088 | 1088 | 1088 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 13 | 14 | 45 | 34 | 59 |  |  |  | 110
|  |  |  | Power Factor | 0.6 | 0.39 | 0.32 | 0.31 | 0.99 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1088 | 1088 | 1088 | 1088 | 1088 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 403 | 422 | 426 | 432 | 439 |  |  |  | 110
Loganlea | F787 | Loganlea | Beenleigh | NCC Rating (A) | 1200 | 1200 | 1200 | 1200 | 1200 | Rural | 52 | NA | 110
|  |  |  | 10 POE Load (A) | 363 | 359 | 373 | 368 | 382 |  |  |  | 110
|  |  |  | Power Factor | 0.91 | 0.92 | 0.9 | 0.9 | 0.92 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1200 | 1200 | 1200 | 1200 | 1200 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 560 | 553 | 554 | 547 | 597 |  |  |  | 110
Loganlea | F788/1 | Beenleigh | Russell Island Tee | NCC Rating (A) | 325 | 325 | 325 | 325 | 325 | Rural | 52 | NA | 110
|  |  |  | 10 POE Load (A) | 59 | 59 | 60 | 61 | 63 |  |  |  | 110
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1 |  |  |  | 110
|  |  |  | ECC Rating (A) | 325 | 325 | 325 | 325 | 325 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 69 | 70 | 71 | 71 | 72 |  |  |  | 110
Loganlea | F788/2 | Russell Island Tee | Stradbroke Island | NCC Rating (A) | 441 | 441 | 441 | 441 | 441 | Rural | 52 | NA | 110
|  |  |  | 10 POE Load (A) | 25 | 25 | 25 | 26 | 26 |  |  |  | 110
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1 |  |  |  | 110
|  |  |  | ECC Rating (A) | 441 | 441 | 441 | 441 | 441 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 38 | 38 | 38 | 38 | 38 |  |  |  | 110
Loganlea | F788/3 | Russell Island Tee | Russell Island | NCC Rating (A) | 902 | 902 | 902 | 902 | 902 | Rural | 52 | NA | 110
|  |  |  | 10 POE Load (A) | 34 | 35 | 35 | 36 | 37 |  |  |  | 110
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 |  |  |  | 110
|  |  |  | ECC Rating (A) | 902 | 902 | 902 | 902 | 902 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 33 | 34 | 35 | 35 | 36 |  |  |  | 110
Loganlea | F793 | Loganlea | North Springwood | NCC Rating (A) | 872 | 872 | 872 | 872 | 872 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 44 | 41 | 42 | 42 | 41 |  |  |  | 110
|  |  |  | Power Factor | 0.98 | 1 | 0.96 | 0.96 | 0.96 |  |  |  | 110
|  |  |  | ECC Rating (A) | 872 | 872 | 872 | 872 | 872 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 154 | 151 | 148 | 145 | 142 |  |  |  | 110
Loganlea | F799 | Loganlea | North Springwood | NCC Rating (A) | 872 | 872 | 872 | 872 | 872 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 113 | 108 | 106 | 104 | 103 |  |  |  | 110
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1 |  |  |  | 110
|  |  |  | ECC Rating (A) | 872 | 872 | 872 | 872 | 872 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 151 | 146 | 144 | 140 | 138 |  |  |  | 110
Loganlea | F820 | Loganlea | Jimboomba | NCC Rating (A) | 962 | 962 | 962 | 962 | 962 | Rural | 52 | NA | 110
|  |  |  | 10 POE Load (A) | 202 | 205 | 211 | 218 | 227 |  |  |  | 110
|  |  |  | Power Factor | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 |  |  |  | 110
|  |  |  | ECC Rating (A) | 962 | 962 | 962 | 962 | 962 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 478 | 487 | 507 | 523 | 539 |  |  |  | 110
Loganlea | F837 | Loganlea | Beenleigh | NCC Rating (A) | 1200 | 1200 | 1200 | 1200 | 1200 | Rural | 52 | NA | 110
|  |  |  | 10 POE Load (A) | 363 | 359 | 373 | 368 | 382 |  |  |  | 110
|  |  |  | Power Factor | 0.91 | 0.92 | 0.9 | 0.9 | 0.92 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1200 | 1200 | 1200 | 1200 | 1200 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 560 | 553 | 554 | 547 | 597 |  |  |  | 110
Loganlea | F836 | Loganlea | Browns Plains | NCC Rating (A) | 894 | 894 | 894 | 894 | 894 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 183 | 179 | 177 | 177 | 178 |  |  |  | 110
|  |  |  | Power Factor | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 |  |  |  | 110
|  |  |  | ECC Rating (A) | 894 | 894 | 894 | 894 | 894 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 412 | 402 | 402 | 399 | 400 |  |  |  | 110
Loganlea | F843 | Loganlea | Browns Plains | NCC Rating (A) | 949 | 949 | 949 | 949 | 949 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 233 | 228 | 226 | 225 | 227 |  |  |  | 110
|  |  |  | Power Factor | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 |  |  |  | 110
|  |  |  | ECC Rating (A) | 949 | 949 | 949 | 949 | 949 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 407 | 397 | 397 | 394 | 395 |  |  |  | 110
Loganlea | F904/1 | Beenleigh | Rocky Point Tee | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Rural | 52 | NA | 110
|  |  |  | 10 POE Load (A) | 22 | 23 | 22 | 23 | 23 |  |  |  | 110
|  |  |  | Power Factor | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 |  |  |  | 110
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 24 | 24 | 24 | 24 | 24 |  |  |  | 110
Loganlea | F904/2 | Rocky Point Tee | Rocky Point | NCC Rating (A) | 868 | 868 | 868 | 868 | 868 | Rural | 52 | NA | 110
|  |  |  | 10 POE Load (A) | 35 | 35 | 35 | 35 | 35 |  |  |  | 110
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1 |  |  |  | 110
|  |  |  | ECC Rating (A) | 868 | 868 | 868 | 868 | 868 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 35 | 35 | 35 | 35 | 35 |  |  |  | 110
Loganlea | F904/3 | Rocky Point Tee | Ibis | NCC Rating (A) | 325 | 325 | 325 | 325 | 325 | Rural | 52 | NA | 110
|  |  |  | 10 POE Load (A) | 14 | 14 | 14 | 14 | 14 |  |  |  | 110
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 1 | 1 |  |  |  | 110
|  |  |  | ECC Rating (A) | 325 | 325 | 325 | 325 | 325 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 58 | 58 | 58 | 58 | 58 |  |  |  | 110
Middle Ridge | F726 | Postmans Ridge | Gatton | NCC Rating (A) | 690 | 690 | 690 | 690 | 690 | Rural | 52 | NA | 110
|  |  |  | 10 POE Load (A) | 119 | 128 | 127 | 127 | 127 |  |  |  | 110
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 |  |  |  | 110
|  |  |  | ECC Rating (A) | 690 | 690 | 690 | 690 | 690 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 356 | 362 | 363 | 367 | 398 |  |  |  | 110
Middle Ridge | F727 | Middle Ridge | Postmans Ridge | NCC Rating (A) | 690 | 690 | 690 | 690 | 690 | Rural | 52 | NA | 110
|  |  |  | 10 POE Load (A) | 130 | 134 | 133 | 133 | 133 |  |  |  | 110
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1 |  |  |  | 110
|  |  |  | ECC Rating (A) | 690 | 690 | 690 | 690 | 690 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 267 | 275 | 274 | 273 | 273 |  |  |  | 110
Middle Ridge | F7348 | Middle Ridge | Postmans Ridge | NCC Rating (A) | 1280 | 1280 | 1280 | 1280 | 1280 | Rural | 52 | NA | 110
|  |  |  | 10 POE Load (A) | 150 | 154 | 154 | 153 | 153 |  |  |  | 110
|  |  |  | Power Factor | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1280 | 1280 | 1280 | 1280 | 1280 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 274 | 277 | 277 | 280 | 297 |  |  |  | 110
Molendinar | F7193 | Molendinar | Cades County | NCC Rating (A) | 1108 | 1108 | 1108 | 1108 | 1108 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 322 | 321 | 317 | 321 | 305 |  |  |  | 110
|  |  |  | Power Factor | 0.98 | 0.99 | 0.99 | 0.99 | 0.98 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1108 | 1108 | 1108 | 1108 | 1108 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 554 | 552 | 557 | 553 | 514 |  |  |  | 110
Molendinar | F7229 | Molendinar | Robina | NCC Rating (A) | 1412 | 1412 | 1412 | 1412 | 1412 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 57 | 58 | 61 | 56 | 87 |  |  |  | 110
|  |  |  | Power Factor | 0.26 | 0.27 | 0.25 | 0.29 | 0.75 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1412 | 1412 | 1412 | 1412 | 1412 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 198 | 195 | 196 | 194 | 221 |  |  |  | 110
Molendinar | F7283 | Cades County | Coomera | NCC Rating (A) | 1088 | 1088 | 1088 | 1088 | 1088 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 402 | 421 | 416 | 424 | 387 |  |  |  | 110
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 0.99 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1088 | 1088 | 1088 | 1088 | 1088 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 624 | 629 | 634 | 640 | 645 |  |  |  | 110
Molendinar | F7297 | Molendinar | Cades County | NCC Rating (A) | 1108 | 1108 | 1108 | 1108 | 1108 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 322 | 321 | 317 | 321 | 305 |  |  |  | 110
|  |  |  | Power Factor | 0.98 | 0.99 | 0.99 | 0.99 | 0.98 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1108 | 1108 | 1108 | 1108 | 1108 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 554 | 552 | 557 | 553 | 514 |  |  |  | 110
Molendinar | F798 | Molendinar | Nerang | NCC Rating (A) | 1250 | 1250 | 1250 | 1250 | 1250 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 152 | 153 | 155 | 153 | 201 |  |  |  | 110
|  |  |  | Power Factor | 0.88 | 0.88 | 0.87 | 0.89 | 0.93 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1250 | 1250 | 1250 | 1250 | 1250 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 240 | 243 | 243 | 243 | 333 |  |  |  | 110
Molendinar | F907 | Molendinar | Southport | NCC Rating (A) | 834 | 834 | 834 | 834 | 834 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 121 | 121 | 123 | 123 | 124 |  |  |  | 110
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1 |  |  |  | 110
|  |  |  | ECC Rating (A) | 834 | 834 | 834 | 834 | 834 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 254 | 253 | 257 | 257 | 260 |  |  |  | 110
Molendinar | F917 | Molendinar | Southport | NCC Rating (A) | 1035 | 1035 | 1035 | 1035 | 1035 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 141 | 141 | 142 | 142 | 144 |  |  |  | 110
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1035 | 1035 | 1035 | 1035 | 1035 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 254 | 253 | 256 | 256 | 260 |  |  |  | 110
Molendinar | F916 | Molendinar | Surfers Paradise | NCC Rating (A) | 1100 | 1100 | 1100 | 1100 | 1100 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 263 | 269 | 275 | 271 | 385 |  |  |  | 110
|  |  |  | Power Factor | 0.92 | 0.92 | 0.91 | 0.93 | 0.96 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1100 | 1100 | 1100 | 1100 | 1100 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 398 | 403 | 406 | 408 | 578 |  |  |  | 110
Mudgeeraba | F706 | Mudgeeraba | Nerang | NCC Rating (A) | 1250 | 1250 | 1250 | 1250 | 1250 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 89 | 88 | 90 | 87 | 51 |  |  |  | 110
|  |  |  | Power Factor | 0.91 | 0.9 | 0.89 | 0.92 | 0.62 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1250 | 1250 | 1250 | 1250 | 1250 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 209 | 208 | 209 | 209 | 212 |  |  |  | 110
Mudgeeraba | F754 | Mudgeeraba | Burleigh Heads | NCC Rating (A) | 1267 | 1267 | 1267 | 1267 | 1267 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 379 | 378 | 381 | 381 | 385 |  |  |  | 110
|  |  |  | Power Factor | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1267 | 1267 | 1267 | 1267 | 1267 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 751 | 749 | 756 | 755 | 766 |  |  |  | 110
Mudgeeraba | F755 | Mudgeeraba | Burleigh Heads | NCC Rating (A) | 1267 | 1267 | 1267 | 1267 | 1267 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 379 | 378 | 381 | 381 | 385 |  |  |  | 110
|  |  |  | Power Factor | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1267 | 1267 | 1267 | 1267 | 1267 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 751 | 749 | 756 | 755 | 766 |  |  |  | 110
Mudgeeraba | F779 | Mudgeeraba | Merrimac | NCC Rating (A) | 1412 | 1412 | 1412 | 1412 | 1412 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 144 | 143 | 146 | 143 | 96 |  |  |  | 110
|  |  |  | Power Factor | 0.93 | 0.92 | 0.92 | 0.93 | 0.81 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1412 | 1412 | 1412 | 1412 | 1412 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 254 | 253 | 257 | 254 | 256 |  |  |  | 110
Mudgeeraba | F780 | Mudgeeraba | Merrimac | NCC Rating (A) | 1412 | 1412 | 1412 | 1412 | 1412 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 144 | 143 | 146 | 143 | 96 |  |  |  | 110
|  |  |  | Power Factor | 0.93 | 0.92 | 0.92 | 0.93 | 0.81 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1412 | 1412 | 1412 | 1412 | 1412 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 254 | 253 | 257 | 254 | 256 |  |  |  | 110
Mudgeeraba | F794 | Mudgeeraba | Robina | NCC Rating (A) | 1412 | 1412 | 1412 | 1412 | 1412 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 186 | 182 | 184 | 182 | 134 |  |  |  | 110
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 0.99 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1412 | 1412 | 1412 | 1412 | 1412 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 281 | 277 | 280 | 278 | 228 |  |  |  | 110
Mudgeeraba | F826 | Broadbeach | Surfers Paradise | NCC Rating (A) | 574 | 574 | 574 | 574 | 574 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 64 | 66 | 69 | 63 | 97 |  |  |  | 110
|  |  |  | Power Factor | 0.21 | 0.23 | 0.22 | 0.25 | 0.74 |  |  |  | 110
|  |  |  | ECC Rating (A) | 574 | 574 | 574 | 574 | 574 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 130 | 133 | 131 | 126 | 185 |  |  |  | 110
Mudgeeraba | F827 | Broadbeach | Surfers Paradise | NCC Rating (A) | 574 | 574 | 574 | 574 | 574 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 64 | 66 | 69 | 63 | 97 |  |  |  | 110
|  |  |  | Power Factor | 0.21 | 0.23 | 0.22 | 0.25 | 0.74 |  |  |  | 110
|  |  |  | ECC Rating (A) | 574 | 574 | 574 | 574 | 574 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 130 | 133 | 131 | 126 | 184 |  |  |  | 110
Mudgeeraba | F838 | Mudgeeraba | Varsity Lakes | NCC Rating (A) | 1347 | 1347 | 1347 | 1347 | 1347 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 64 | 64 | 64 | 64 | 65 |  |  |  | 110
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1347 | 1347 | 1347 | 1347 | 1347 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 123 | 123 | 124 | 123 | 125 |  |  |  | 110
Mudgeeraba | F839 | Mudgeeraba | Varsity Lakes | NCC Rating (A) | 1347 | 1347 | 1347 | 1347 | 1347 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 64 | 64 | 64 | 64 | 65 |  |  |  | 110
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1347 | 1347 | 1347 | 1347 | 1347 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 123 | 123 | 124 | 123 | 125 |  |  |  | 110
Mudgeeraba | F918 | Merrimac | Broadbeach | NCC Rating (A) | 1286 | 1286 | 1286 | 1286 | 1286 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 98 | 98 | 101 | 97 | 64 |  |  |  | 110
|  |  |  | Power Factor | 0.81 | 0.8 | 0.79 | 0.82 | 0.37 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1286 | 1286 | 1286 | 1286 | 1286 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 206 | 205 | 209 | 206 | 204 |  |  |  | 110
Mudgeeraba | F919 | Merrimac | Broadbeach | NCC Rating (A) | 1286 | 1286 | 1286 | 1286 | 1286 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 98 | 98 | 101 | 97 | 64 |  |  |  | 110
|  |  |  | Power Factor | 0.81 | 0.8 | 0.79 | 0.82 | 0.37 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1286 | 1286 | 1286 | 1286 | 1286 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 206 | 205 | 209 | 206 | 204 |  |  |  | 110
Murarrie | F7270 | Murarrie | Lytton Bulk | NCC Rating (A) | 1364 | 1364 | 1364 | 1364 | 1364 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 233 | 242 | 243 | 241 | 248 |  |  |  | 110
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1364 | 1364 | 1364 | 1364 | 1364 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 455 | 473 | 475 | 469 | 482 |  |  |  | 110
Murarrie | F7271 | Murarrie | Lytton Bulk | NCC Rating (A) | 1364 | 1364 | 1364 | 1364 | 1364 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 233 | 242 | 243 | 241 | 248 |  |  |  | 110
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1364 | 1364 | 1364 | 1364 | 1364 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 455 | 473 | 475 | 469 | 482 |  |  |  | 110
Murarrie | F7272 | Murarrie | Doboy | NCC Rating (A) | 1220 | 1220 | 1220 | 1220 | 1220 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 177 | 178 | 179 | 177 | 178 |  |  |  | 110
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1220 | 1220 | 1220 | 1220 | 1220 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 268 | 270 | 272 | 268 | 269 |  |  |  | 110
Murarrie | F7273 | Murarrie | Doboy | NCC Rating (A) | 1220 | 1220 | 1220 | 1220 | 1220 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 177 | 178 | 179 | 177 | 178 |  |  |  | 110
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1220 | 1220 | 1220 | 1220 | 1220 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 268 | 270 | 272 | 268 | 269 |  |  |  | 110
Murarrie | F7274 | Murarrie | Doboy | NCC Rating (A) | 1220 | 1220 | 1220 | 1220 | 1220 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 177 | 178 | 179 | 177 | 178 |  |  |  | 110
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1220 | 1220 | 1220 | 1220 | 1220 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 268 | 270 | 272 | 268 | 269 |  |  |  | 110
Palmwoods | F745/2 | Moodlu | Beerwah Tee | NCC Rating (A) | 1064 | 1064 | 1064 | 1064 | 1064 | Rural | 52 | NA | 110
|  |  |  | 10 POE Load (A) | 111 | 109 | 104 | 101 | 99 |  |  |  | 110
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.98 | 0.98 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1064 | 1064 | 1064 | 1064 | 1064 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 213 | 213 | 208 | 204 | 194 |  |  |  | 110
Palmwoods | F745/3 | Moodlu | Caboolture | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Rural | 52 | NA | 110
|  |  |  | 10 POE Load (A) | 332 | 331 | 335 | 336 | 342 |  |  |  | 110
|  |  |  | Power Factor | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 |  |  |  | 110
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 646 | 642 | 651 | 654 | 662 |  |  |  | 110
Palmwoods | F745/4 | Palmwoods | Beerwah Tee | NCC Rating (A) | 1064 | 1064 | 1064 | 1064 | 1064 | Rural | 52 | NA | 110
|  |  |  | 10 POE Load (A) | 231 | 229 | 229 | 227 | 227 |  |  |  | 110
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1064 | 1064 | 1064 | 1064 | 1064 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 443 | 444 | 448 | 447 | 442 |  |  |  | 110
Palmwoods | F745/5 | Beerwah Tee | Beerwah | NCC Rating (A) | 975 | 975 | 975 | 975 | 975 | Rural | 52 | NA | 110
|  |  |  | 10 POE Load (A) | 121 | 121 | 126 | 127 | 130 |  |  |  | 110
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 |  |  |  | 110
|  |  |  | ECC Rating (A) | 975 | 975 | 975 | 975 | 975 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 233 | 234 | 244 | 246 | 250 |  |  |  | 110
Palmwoods | F746/2 | Moodlu | Beerwah Tee | NCC Rating (A) | 1064 | 1064 | 1064 | 1064 | 1064 | Rural | 52 | NA | 110
|  |  |  | 10 POE Load (A) | 111 | 109 | 104 | 101 | 99 |  |  |  | 110
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.98 | 0.98 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1064 | 1064 | 1064 | 1064 | 1064 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 213 | 213 | 208 | 204 | 194 |  |  |  | 110
Palmwoods | F746/3 | Moodlu | Caboolture | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Rural | 52 | NA | 110
|  |  |  | 10 POE Load (A) | 333 | 331 | 335 | 337 | 343 |  |  |  | 110
|  |  |  | Power Factor | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 |  |  |  | 110
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 646 | 642 | 651 | 654 | 662 |  |  |  | 110
Palmwoods | F746/4 | Palmwoods | Beerwah Tee | NCC Rating (A) | 1064 | 1064 | 1064 | 1064 | 1064 | Rural | 52 | NA | 110
|  |  |  | 10 POE Load (A) | 231 | 229 | 229 | 227 | 228 |  |  |  | 110
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1064 | 1064 | 1064 | 1064 | 1064 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 443 | 444 | 448 | 447 | 442 |  |  |  | 110
Palmwoods | F746/5 | Beerwah Tee | Beerwah | NCC Rating (A) | 1033 | 1033 | 1033 | 1033 | 1033 | Rural | 52 | NA | 110
|  |  |  | 10 POE Load (A) | 120 | 121 | 126 | 127 | 129 |  |  |  | 110
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1033 | 1033 | 1033 | 1033 | 1033 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 233 | 234 | 244 | 246 | 250 |  |  |  | 110
Palmwoods 132 kV | F7189/1 | Palmwoods | Image Flat | NCC Rating (A) | 1052 | 1052 | 1052 | 1052 | 1052 | Rural | 44 | NA | 132
|  |  |  | 10 POE Load (A) | 115 | 113 | 116 | 116 | 119 |  |  |  | 132
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 |  |  |  | 132
|  |  |  | ECC Rating (A) | 1052 | 1052 | 1052 | 1052 | 1052 |  |  |  | 132
|  |  |  | 50 POE Load (A) | 228 | 223 | 228 | 228 | 231 |  |  |  | 132
Palmwoods 132 kV | F7189/2 | Image Flat | Cooroy | NCC Rating (A) | 942 | 942 | 942 | 942 | 942 | Rural | 44 | NA | 132
|  |  |  | 10 POE Load (A) | 54 | 59 | 57 | 59 | 59 |  |  |  | 132
|  |  |  | Power Factor | 0.87 | 0.88 | 0.87 | 0.86 | 0.85 |  |  |  | 132
|  |  |  | ECC Rating (A) | 942 | 942 | 942 | 942 | 942 |  |  |  | 132
|  |  |  | 50 POE Load (A) | 279 | 290 | 289 | 287 | 285 |  |  |  | 132
Palmwoods 132 kV | F7189/3 | Image Flat | Nambour | NCC Rating (A) | 833 | 833 | 833 | 833 | 833 | Rural | 44 | NA | 132
|  |  |  | 10 POE Load (A) | 162 | 164 | 166 | 166 | 169 |  |  |  | 132
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 0.99 |  |  |  | 132
|  |  |  | ECC Rating (A) | 833 | 833 | 833 | 833 | 833 |  |  |  | 132
|  |  |  | 50 POE Load (A) | 308 | 311 | 315 | 316 | 320 |  |  |  | 132
Palmwoods 132 kV | F7298 | Sunrise Hills | Noosaville | NCC Rating (A) | 975 | 975 | 975 | 975 | 975 | Urban | 17 | NA | 132
|  |  |  | 10 POE Load (A) | 73 | 72 | 72 | 72 | 72 |  |  |  | 132
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 |  |  |  | 132
|  |  |  | ECC Rating (A) | 975 | 975 | 975 | 975 | 975 |  |  |  | 132
|  |  |  | 50 POE Load (A) | 137 | 135 | 135 | 134 | 136 |  |  |  | 132
Palmwoods 132 kV | F777 | Palmwoods | Mooloolaba | NCC Rating (A) | 1469 | 1469 | 1469 | 1469 | 1469 | Urban | 17 | NA | 132
|  |  |  | 10 POE Load (A) | 274 | 281 | 291 | 296 | 302 |  |  |  | 132
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1 |  |  |  | 132
|  |  |  | ECC Rating (A) | 1469 | 1469 | 1469 | 1469 | 1469 |  |  |  | 132
|  |  |  | 50 POE Load (A) | 380 | 391 | 404 | 412 | 419 |  |  |  | 132
Palmwoods 132 kV | F778 | Palmwoods | Mooloolaba | NCC Rating (A) | 1469 | 1469 | 1469 | 1469 | 1469 | Urban | 17 | NA | 132
|  |  |  | 10 POE Load (A) | 274 | 281 | 291 | 296 | 302 |  |  |  | 132
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1 |  |  |  | 132
|  |  |  | ECC Rating (A) | 1469 | 1469 | 1469 | 1469 | 1469 |  |  |  | 132
|  |  |  | 50 POE Load (A) | 434 | 447 | 463 | 471 | 480 |  |  |  | 132
Palmwoods 132 kV | F790 | Sunrise Hills | Noosaville | NCC Rating (A) | 975 | 975 | 975 | 975 | 975 | Urban | 17 | NA | 132
|  |  |  | 10 POE Load (A) | 74 | 72 | 72 | 72 | 73 |  |  |  | 132
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 |  |  |  | 132
|  |  |  | ECC Rating (A) | 975 | 975 | 975 | 975 | 975 |  |  |  | 132
|  |  |  | 50 POE Load (A) | 141 | 138 | 139 | 138 | 140 |  |  |  | 132
Palmwoods 132 kV | F795/1 | Palmwoods | Image Flat | NCC Rating (A) | 1052 | 1052 | 1052 | 1052 | 1052 | Rural | 44 | NA | 132
|  |  |  | 10 POE Load (A) | 115 | 112 | 116 | 116 | 119 |  |  |  | 132
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 |  |  |  | 132
|  |  |  | ECC Rating (A) | 1052 | 1052 | 1052 | 1052 | 1052 |  |  |  | 132
|  |  |  | 50 POE Load (A) | 228 | 223 | 228 | 228 | 231 |  |  |  | 132
Palmwoods 132 kV | F795/2 | Image Flat | Cooroy | NCC Rating (A) | 942 | 942 | 942 | 942 | 942 | Rural | 44 | NA | 132
|  |  |  | 10 POE Load (A) | 54 | 59 | 57 | 59 | 59 |  |  |  | 132
|  |  |  | Power Factor | 0.88 | 0.88 | 0.87 | 0.86 | 0.85 |  |  |  | 132
|  |  |  | ECC Rating (A) | 942 | 942 | 942 | 942 | 942 |  |  |  | 132
|  |  |  | 50 POE Load (A) | 280 | 291 | 289 | 288 | 286 |  |  |  | 132
Palmwoods 132 kV | F795/3 | Image Flat | Nambour | NCC Rating (A) | 833 | 833 | 833 | 833 | 833 | Rural | 44 | NA | 132
|  |  |  | 10 POE Load (A) | 162 | 164 | 166 | 166 | 169 |  |  |  | 132
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 0.99 |  |  |  | 132
|  |  |  | ECC Rating (A) | 833 | 833 | 833 | 833 | 833 |  |  |  | 132
|  |  |  | 50 POE Load (A) | 308 | 311 | 315 | 316 | 320 |  |  |  | 132
Palmwoods 132 kV | F796 | Cooroy | Sunrise Hills | NCC Rating (A) | 949 | 949 | 949 | 949 | 949 | Rural | 44 | NA | 132
|  |  |  | 10 POE Load (A) | 241 | 237 | 244 | 243 | 245 |  |  |  | 132
|  |  |  | Power Factor | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 |  |  |  | 132
|  |  |  | ECC Rating (A) | 949 | 949 | 949 | 949 | 949 |  |  |  | 132
|  |  |  | 50 POE Load (A) | 452 | 443 | 457 | 456 | 459 |  |  |  | 132
Palmwoods 132 kV | F797 | Cooroy | Sunrise Hills | NCC Rating (A) | 975 | 975 | 975 | 975 | 975 | Rural | 44 | NA | 132
|  |  |  | 10 POE Load (A) | 242 | 237 | 244 | 243 | 245 |  |  |  | 132
|  |  |  | Power Factor | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 |  |  |  | 132
|  |  |  | ECC Rating (A) | 975 | 975 | 975 | 975 | 975 |  |  |  | 132
|  |  |  | 50 POE Load (A) | 452 | 443 | 457 | 456 | 459 |  |  |  | 132
Palmwoods 132 kV | F803 | Mooloolaba | Caloundra | NCC Rating (A) | 975 | 975 | 975 | 975 | 975 | Urban | 17 | NA | 132
|  |  |  | 10 POE Load (A) | 186 | 193 | 203 | 207 | 214 |  |  |  | 132
|  |  |  | Power Factor | 0.98 | 0.98 | 0.98 | 0.98 | 0.97 |  |  |  | 132
|  |  |  | ECC Rating (A) | 975 | 975 | 975 | 975 | 975 |  |  |  | 132
|  |  |  | 50 POE Load (A) | 425 | 442 | 467 | 475 | 488 |  |  |  | 132
Palmwoods 132 kV | F804 | Caloundra | Currimundi | NCC Rating (A) | 975 | 975 | 975 | 975 | 975 | Urban | 17 | NA | 132
|  |  |  | 10 POE Load (A) | 30 | 29 | 27 | 29 | 32 |  |  |  | 132
|  |  |  | Power Factor | 0.98 | 0.98 | 0.98 | 0.97 | 0.97 |  |  |  | 132
|  |  |  | ECC Rating (A) | 975 | 975 | 975 | 975 | 975 |  |  |  | 132
|  |  |  | 50 POE Load (A) | 220 | 232 | 249 | 251 | 256 |  |  |  | 132
Palmwoods 132 kV | F815 | Mooloolaba | Alexandra Headlands | NCC Rating (A) | 975 | 975 | 975 | 975 | 975 | Urban | 17 | NA | 132
|  |  |  | 10 POE Load (A) | 63 | 59 | 58 | 62 | 61 |  |  |  | 132
|  |  |  | Power Factor | 0.69 | 0.66 | 0.65 | 0.66 | 0.66 |  |  |  | 132
|  |  |  | ECC Rating (A) | 975 | 975 | 975 | 975 | 975 |  |  |  | 132
|  |  |  | 50 POE Load (A) | 150 | 159 | 165 | 165 | 168 |  |  |  | 132
Palmwoods 132 kV | F816 | Mooloolaba | West Maroochydore | NCC Rating (A) | 975 | 975 | 975 | 975 | 975 | Urban | 17 | NA | 132
|  |  |  | 10 POE Load (A) | 91 | 95 | 99 | 100 | 103 |  |  |  | 132
|  |  |  | Power Factor | 0.9 | 0.92 | 0.93 | 0.93 | 0.94 |  |  |  | 132
|  |  |  | ECC Rating (A) | 975 | 975 | 975 | 975 | 975 |  |  |  | 132
|  |  |  | 50 POE Load (A) | 167 | 174 | 181 | 184 | 187 |  |  |  | 132
Palmwoods 132 kV | F819 | Mooloolaba | Kawana | NCC Rating (A) | 894 | 894 | 894 | 894 | 894 | Urban | 17 | NA | 132
|  |  |  | 10 POE Load (A) | 260 | 270 | 285 | 289 | 296 |  |  |  | 132
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 |  |  |  | 132
|  |  |  | ECC Rating (A) | 894 | 894 | 894 | 894 | 894 |  |  |  | 132
|  |  |  | 50 POE Load (A) | 422 | 439 | 464 | 472 | 485 |  |  |  | 132
Palmwoods 132 kV | F821 | West Maroochydore | Alexandra Headlands | NCC Rating (A) | 975 | 975 | 975 | 975 | 975 | Urban | 17 | NA | 132
|  |  |  | 10 POE Load (A) | 191 | 193 | 199 | 206 | 209 |  |  |  | 132
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1 |  |  |  | 132
|  |  |  | ECC Rating (A) | 975 | 975 | 975 | 975 | 975 |  |  |  | 132
|  |  |  | 50 POE Load (A) | 341 | 351 | 363 | 373 | 379 |  |  |  | 132
Palmwoods 132 kV | F844 | Kawana | Birtinya | NCC Rating (A) | 975 | 975 | 975 | 975 | 975 | Urban | 17 | NA | 132
|  |  |  | 10 POE Load (A) | 167 | 179 | 194 | 198 | 204 |  |  |  | 132
|  |  |  | Power Factor | 1 | 1 | 1 | 0.99 | 0.99 |  |  |  | 132
|  |  |  | ECC Rating (A) | 975 | 975 | 975 | 975 | 975 |  |  |  | 132
|  |  |  | 50 POE Load (A) | 335 | 354 | 378 | 387 | 399 |  |  |  | 132
Palmwoods 132 kV | F851 | Birtinya | Currimundi | NCC Rating (A) | 975 | 975 | 975 | 975 | 975 | Urban | 17 | NA | 132
|  |  |  | 10 POE Load (A) | 99 | 98 | 98 | 102 | 106 |  |  |  | 132
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1 |  |  |  | 132
|  |  |  | ECC Rating (A) | 975 | 975 | 975 | 975 | 975 |  |  |  | 132
|  |  |  | 50 POE Load (A) | 270 | 276 | 286 | 293 | 304 |  |  |  | 132
Palmwoods 132 kV | F845 | Palmwoods | West Maroochydore | NCC Rating (A) | 1376 | 1376 | 1376 | 1376 | 1376 | Urban | 17 | NA | 132
|  |  |  | 10 POE Load (A) | 199 | 203 | 209 | 214 | 218 |  |  |  | 132
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1 |  |  |  | 132
|  |  |  | ECC Rating (A) | 1376 | 1376 | 1376 | 1376 | 1376 |  |  |  | 132
|  |  |  | 50 POE Load (A) | 264 | 270 | 279 | 285 | 289 |  |  |  | 132
Palmwoods 132 kV | F846 | Palmwoods | West Maroochydore | NCC Rating (A) | 1376 | 1376 | 1376 | 1376 | 1376 | Urban | 17 | NA | 132
|  |  |  | 10 POE Load (A) | 199 | 203 | 209 | 214 | 218 |  |  |  | 132
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1 |  |  |  | 132
|  |  |  | ECC Rating (A) | 1376 | 1376 | 1376 | 1376 | 1376 |  |  |  | 132
|  |  |  | 50 POE Load (A) | 264 | 270 | 279 | 285 | 289 |  |  |  | 132
Rocklea | F817 | Rocklea | Archerfield | NCC Rating (A) | 1220 | 1220 | 1220 | 1220 | 1220 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 129 | 121 | 120 | 119 | 118 |  |  |  | 110
|  |  |  | Power Factor | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1220 | 1220 | 1220 | 1220 | 1220 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 252 | 236 | 235 | 231 | 231 |  |  |  | 110
Rocklea | F818 | Rocklea | Archerfield | NCC Rating (A) | 1220 | 1220 | 1220 | 1220 | 1220 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 129 | 121 | 120 | 119 | 118 |  |  |  | 110
|  |  |  | Power Factor | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1220 | 1220 | 1220 | 1220 | 1220 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 252 | 236 | 235 | 231 | 231 |  |  |  | 110
South Pine | F7337 | Nudgee | Myrtletown | NCC Rating (A) | 1171 | 1171 | 1171 | 1171 | 1171 | High Sec | NA | NA | 110
|  |  |  | 10 POE Load (A) | 96 | 95 | 95 | 95 | 95 |  |  |  | 110
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1171 | 1171 | 1171 | 1171 | 1171 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 191 | 191 | 191 | 190 | 189 |  |  |  | 110
South Pine | F7338 | Nudgee | Myrtletown | NCC Rating (A) | 1171 | 1171 | 1171 | 1171 | 1171 | High Sec | NA | NA | 110
|  |  |  | 10 POE Load (A) | 96 | 95 | 95 | 95 | 95 |  |  |  | 110
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1171 | 1171 | 1171 | 1171 | 1171 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 191 | 191 | 191 | 190 | 189 |  |  |  | 110
South Pine | F7341 | South Pine | Nudgee | NCC Rating (A) | 1663 | 1663 | 1663 | 1663 | 1663 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 492 | 518 | 529 | 527 | 530 |  |  |  | 110
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1663 | 1663 | 1663 | 1663 | 1663 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 970 | 1023 | 1047 | 1043 | 1040 |  |  |  | 110
South Pine | F7342 | South Pine | Nudgee | NCC Rating (A) | 1663 | 1663 | 1663 | 1663 | 1663 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 493 | 518 | 530 | 528 | 531 |  |  |  | 110
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1663 | 1663 | 1663 | 1663 | 1663 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 970 | 1023 | 1047 | 1043 | 1040 |  |  |  | 110
South Pine | F7344 | South Pine | Griffin | NCC Rating (A) | 1293 | 1293 | 1293 | 1293 | 1293 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 212 | 209 | 214 | 215 | 223 |  |  |  | 110
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1293 | 1293 | 1293 | 1293 | 1293 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 389 | 389 | 394 | 401 | 412 |  |  |  | 110
South Pine | F7345 | South Pine | Griffin | NCC Rating (A) | 1293 | 1293 | 1293 | 1293 | 1293 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 212 | 209 | 214 | 215 | 223 |  |  |  | 110
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1293 | 1293 | 1293 | 1293 | 1293 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 389 | 389 | 394 | 401 | 412 |  |  |  | 110
South Pine | F7358 | Griffin | Hays Inlet | NCC Rating (A) | 1600 | 1600 | 1600 | 1600 | 1600 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 203 | 197 | 206 | 201 | 204 |  |  |  | 110
|  |  |  | Power Factor | 0.98 | 0.99 | 0.98 | 0.99 | 0.99 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1600 | 1600 | 1600 | 1600 | 1600 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 300 | 300 | 305 | 306 | 309 |  |  |  | 110
South Pine | F737/1 | South Pine | Bunyaville | NCC Rating (A) | 1164 | 1164 | 1164 | 1164 | 1164 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 325 | 323 | 327 | 326 | 327 |  |  |  | 110
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1164 | 1164 | 1164 | 1164 | 1164 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 634 | 629 | 638 | 635 | 640 |  |  |  | 110
South Pine | F737/2 | Bunyaville | Stafford | NCC Rating (A) | 1370 | 1370 | 1370 | 1370 | 1370 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 329 | 327 | 331 | 330 | 332 |  |  |  | 110
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1370 | 1370 | 1370 | 1370 | 1370 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 640 | 635 | 643 | 641 | 646 |  |  |  | 110
South Pine | F738/1 | South Pine | Bunyaville | NCC Rating (A) | 1164 | 1164 | 1164 | 1164 | 1164 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 325 | 323 | 327 | 326 | 327 |  |  |  | 110
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1164 | 1164 | 1164 | 1164 | 1164 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 634 | 629 | 638 | 635 | 640 |  |  |  | 110
South Pine | F738/2 | Bunyaville B | Stafford | NCC Rating (A) | 1370 | 1370 | 1370 | 1370 | 1370 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 329 | 327 | 331 | 330 | 332 |  |  |  | 110
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1370 | 1370 | 1370 | 1370 | 1370 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 640 | 634 | 643 | 640 | 645 |  |  |  | 110
South Pine | F739 | South Pine | Bald Hills | NCC Rating (A) | 1600 | 1600 | 1600 | 1600 | 1600 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 210 | 208 | 208 | 207 | 208 |  |  |  | 110
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1600 | 1600 | 1600 | 1600 | 1600 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 387 | 383 | 384 | 382 | 381 |  |  |  | 110
South Pine | F740 | South Pine | Sandgate | NCC Rating (A) | 1600 | 1600 | 1600 | 1600 | 1600 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 193 | 192 | 192 | 191 | 192 |  |  |  | 110
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1600 | 1600 | 1600 | 1600 | 1600 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 387 | 383 | 384 | 382 | 381 |  |  |  | 110
South Pine | F741 | South Pine | Hays Inlet | NCC Rating (A) | 904 | 904 | 904 | 904 | 904 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 220 | 223 | 223 | 228 | 232 |  |  |  | 110
|  |  |  | Power Factor | 0.98 | 0.98 | 0.98 | 0.97 | 0.97 |  |  |  | 110
|  |  |  | ECC Rating (A) | 904 | 904 | 904 | 904 | 904 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 317 | 317 | 322 | 324 | 327 |  |  |  | 110
South Pine | F742 | South Pine | Hays Inlet | NCC Rating (A) | 904 | 904 | 904 | 904 | 904 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 219 | 222 | 222 | 227 | 231 |  |  |  | 110
|  |  |  | Power Factor | 0.98 | 0.98 | 0.98 | 0.97 | 0.97 |  |  |  | 110
|  |  |  | ECC Rating (A) | 904 | 904 | 904 | 904 | 904 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 317 | 317 | 321 | 323 | 327 |  |  |  | 110
South Pine | F7299 | South Pine | Brendale | NCC Rating (A) | 1336 | 1336 | 1336 | 1336 | 1336 | Rural | 52 | NA | 110
|  |  |  | 10 POE Load (A) | 233 | 230 | 234 | 233 | 234 |  |  |  | 110
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1336 | 1336 | 1336 | 1336 | 1336 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 331 | 327 | 333 | 331 | 331 |  |  |  | 110
South Pine | F743 | South Pine | Brendale | NCC Rating (A) | 785 | 785 | 785 | 785 | 785 | Rural | 52 | NA | 110
|  |  |  | 10 POE Load (A) | 233 | 230 | 234 | 233 | 234 |  |  |  | 110
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1 |  |  |  | 110
|  |  |  | ECC Rating (A) | 785 | 785 | 785 | 785 | 785 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 331 | 327 | 333 | 331 | 331 |  |  |  | 110
South Pine | F744 | South Pine | Brendale | NCC Rating (A) | 785 | 785 | 785 | 785 | 785 | Rural | 52 | NA | 110
|  |  |  | 10 POE Load (A) | 233 | 230 | 234 | 233 | 234 |  |  |  | 110
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1 |  |  |  | 110
|  |  |  | ECC Rating (A) | 785 | 785 | 785 | 785 | 785 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 331 | 327 | 333 | 331 | 331 |  |  |  | 110
South Pine | F745/1 | South Pine | Moodlu | NCC Rating (A) | 1064 | 1064 | 1064 | 1064 | 1064 | Rural | 52 | NA | 110
|  |  |  | 10 POE Load (A) | 221 | 222 | 231 | 236 | 244 |  |  |  | 110
|  |  |  | Power Factor | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1064 | 1064 | 1064 | 1064 | 1064 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 435 | 432 | 446 | 453 | 469 |  |  |  | 110
South Pine | F746/1 | South Pine | Moodlu | NCC Rating (A) | 1064 | 1064 | 1064 | 1064 | 1064 | Rural | 52 | NA | 110
|  |  |  | 10 POE Load (A) | 222 | 222 | 231 | 236 | 244 |  |  |  | 110
|  |  |  | Power Factor | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1064 | 1064 | 1064 | 1064 | 1064 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 435 | 432 | 446 | 453 | 469 |  |  |  | 110
South Pine | F831 | Bald Hills | Sandgate | NCC Rating (A) | 1600 | 1600 | 1600 | 1600 | 1600 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 167 | 165 | 166 | 165 | 166 |  |  |  | 110
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 |  |  |  | 110
|  |  |  | ECC Rating (A) | 1600 | 1600 | 1600 | 1600 | 1600 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 344 | 340 | 341 | 339 | 339 |  |  |  | 110
South Pine | F912 | Nudgee | Meeandah | NCC Rating (A) | 491 | 491 | 491 | 491 | 491 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 84 | 99 | 101 | 101 | 102 |  |  |  | 110
|  |  |  | Power Factor | 0.98 | 1 | 1 | 1 | 1 |  |  |  | 110
|  |  |  | ECC Rating (A) | 491 | 491 | 491 | 491 | 491 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 167 | 199 | 202 | 202 | 203 |  |  |  | 110
South Pine | F913 | Nudgee | Meeandah | NCC Rating (A) | 491 | 491 | 491 | 491 | 491 | Urban | 21 | NA | 110
|  |  |  | 10 POE Load (A) | 84 | 99 | 101 | 101 | 102 |  |  |  | 110
|  |  |  | Power Factor | 0.98 | 1 | 1 | 1 | 1 |  |  |  | 110
|  |  |  | ECC Rating (A) | 491 | 491 | 491 | 491 | 491 |  |  |  | 110
|  |  |  | 50 POE Load (A) | 167 | 199 | 202 | 202 | 203 |  |  |  | 110
Woolooga 132 kV | F7186 | Cooran | Cooroy | NCC Rating (A) | 963 | 963 | 963 | 963 | 963 | Rural | 44 | NA | 132
|  |  |  | 10 POE Load (A) | 282 | 282 | 284 | 283 | 283 |  |  |  | 132
|  |  |  | Power Factor | 0.8 | 0.8 | 0.81 | 0.81 | 0.82 |  |  |  | 132
|  |  |  | ECC Rating (A) | 963 | 963 | 963 | 963 | 963 |  |  |  | 132
|  |  |  | 50 POE Load (A) | 485 | 496 | 498 | 496 | 496 |  |  |  | 132
Woolooga 132 kV | F7343 | Traveston | Cooran | NCC Rating (A) | 963 | 963 | 963 | 963 | 963 | Rural | 44 | NA | 132
|  |  |  | 10 POE Load (A) | 305 | 305 | 307 | 306 | 307 |  |  |  | 132
|  |  |  | Power Factor | 0.85 | 0.85 | 0.86 | 0.86 | 0.86 |  |  |  | 132
|  |  |  | ECC Rating (A) | 963 | 963 | 963 | 963 | 963 |  |  |  | 132
|  |  |  | 50 POE Load (A) | 508 | 519 | 521 | 519 | 519 |  |  |  | 132
Woolooga 132 kV | F747/1 | Gympie | Traveston | NCC Rating (A) | 963 | 963 | 963 | 963 | 963 | Rural | 44 | NA | 132
|  |  |  | 10 POE Load (A) | 317 | 317 | 319 | 319 | 319 |  |  |  | 132
|  |  |  | Power Factor | 0.88 | 0.88 | 0.88 | 0.89 | 0.89 |  |  |  | 132
|  |  |  | ECC Rating (A) | 963 | 963 | 963 | 963 | 963 |  |  |  | 132
|  |  |  | 50 POE Load (A) | 521 | 531 | 534 | 532 | 531 |  |  |  | 132
Woolooga 132 kV | F747/2 | Woolooga | Gympie | NCC Rating (A) | 983 | 983 | 983 | 983 | 983 | Rural | 44 | NA | 132
|  |  |  | 10 POE Load (A) | 460 | 458 | 461 | 460 | 461 |  |  |  | 132
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1 |  |  |  | 132
|  |  |  | ECC Rating (A) | 983 | 983 | 983 | 983 | 983 |  |  |  | 132
|  |  |  | 50 POE Load (A) | 669 | 674 | 677 | 674 | 674 |  |  |  | 132
Woolooga 132 kV | F748/1 | Gympie | Cooroy | NCC Rating (A) | 963 | 963 | 963 | 963 | 963 | Rural | 44 | NA | 132
|  |  |  | 10 POE Load (A) | 368 | 368 | 372 | 371 | 372 |  |  |  | 132
|  |  |  | Power Factor | 0.95 | 0.95 | 0.95 | 0.95 | 0.96 |  |  |  | 132
|  |  |  | ECC Rating (A) | 963 | 963 | 963 | 963 | 963 |  |  |  | 132
|  |  |  | 50 POE Load (A) | 622 | 631 | 635 | 632 | 631 |  |  |  | 132
Woolooga 132 kV | F748/2 | Woolooga | Gympie | NCC Rating (A) | 983 | 983 | 983 | 983 | 983 | Rural | 44 | NA | 132
|  |  |  | 10 POE Load (A) | 487 | 485 | 488 | 487 | 488 |  |  |  | 132
|  |  |  | Power Factor | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 |  |  |  | 132
|  |  |  | ECC Rating (A) | 983 | 983 | 983 | 983 | 983 |  |  |  | 132
|  |  |  | 50 POE Load (A) | 729 | 738 | 741 | 738 | 737 |  |  |  | 132