## Notes
Sub-Transmission Feeders Forecasts (Energex Distribution Annual Planning Report 2021-22 to 2025-26)
This workbook provides 5 year forecast capacity and loading information for sub-transmission feeders in the Energex network.
This workbook forms part of the Energex Distribution Annual Planning Report 2021-22 to 2025-26 (DAPR) and should be read in conjunction with the report document.
Energex Distribution Annual Planning Report is prepared and made available solely for information purposes. While care was taken in the preparation of the information in this report, and it is provided in good faith, Energex accepts no responsibility or liability (including without limitation, liability to any person by reason of negligence or negligent mis-statement) for any loss or damage that may be incurred by any person acting in reliance on this information or assumptions drawn from it, except to the extent that liability under any applicable Queensland or Commonwealth of Australia statute cannot be excluded.
It contains assumptions regarding, among other things, economic growth and load forecasts which may or may not prove to be correct. The forecasts included in the document involve subjective judgements and analysis which are subject to significant uncertainties and contingencies, many of which are out of the control of Energex. Furthermore, forecasted data is subject to ongoing variation due to COVID 19 impacts. Energex makes no representation or warranty as to the accuracy, reliability, completeness or suitability for any particular purpose of the information in this document. All information should be independently investigated, reviewed, analysed and verified, and must not be relied upon in connection with any investment proposal or decision.
The following sections list the 33kV feeders, their forecast loads, power factor, customer category and available load transfers. The feeder loads are calculated from load flow results using forecast substation demands. For the transmission and sub-transmission feeders, load flow studies are conducted for system normal and single contingency situations.
The forecast and capacity cut-off date for the winter season is 1 June of each year, and for the summer season is 1 December of each year. For example, 2022 winter forecast includes all committed projects with a proposed commissioning date up to 1 June 2022, and the 2021/22 summer forecast includes all committed projects with a proposed commissioning date up to 1 December 2021.
Assessment of 33kV feeders is performed under four possible risk periods: winter day, winter night, summer day and summer night. For the summer table, the worst case (highest) load between summer day and summer night has been represented in the table.
Peak, reconciled, compensated load forecasts have been used in the 33kV feeder analyses, with 50 PoE forecast load used for single contingency studies, and 10 PoE forecast load used for system normal studies.
Feeder capacities are shown for ECC and NCC. These ratings have also been adjusted for known committed projects. All load transfers associated with contingent condition include acceptable feeder voltage profiles.
Although the conductor rating is generally the limiting factor for feeder capacity, there are other significant items of plant, such as the feeder circuit breaker, that can also restrict capacity. Furthermore, other factors such as voltage constraints and load sharing between parallel underground feeders can sometimes de‑rate the capacity of the feeders due to thermal characteristic constraints. Each of these factors has been taken into account in the production of the forecast tables.
Interconnected feeders that supply multiple customers are examined in the following tables. Feeders exclusively supplying a customer owned substation or dedicated to a customer are not included in these tables.
A definition of terms is shown in the table below.
Definition of Terms Feeder Capacity and Forecast Tables
Term | Definition
NCC Rating (A) | Normal Cyclic Capacity - the total capacity with all network components and equipment intact. This is the maximum permissible peak daily loading for a given load cycle that a feeder can supply each day of its life. For overhead feeders, the NCC is the conductor rating with an assumed 1m/s wind, orthogonal to the line. For underground cables, the NCC assumes that there are sufficient temperature and current operating margins from the thermal inertia of the cable and its surroundings.
10 PoE Load (A) | Peak load forecast with 10% probability of being exceeded (one in every 10 years will be exceeded). Based on normal expected growth rates and weather corrected starting loads.
Power Factor (System Normal) | Lowest power factor along the feeder at 10 PoE Peak Load. Where the Power Factor is either 0 the feeder is a normally open feeder that does not have load under System Normal conditions.
ECC Rating (A) | Emergency Cyclic Capacity – the long term firm delivery capacity under single contingency conditions. Some underground cables are installed in close proximity to other circuits and are normally de‑rated to allow for the heat generated by the adjacent cables. ECC is the higher capacity available when any adjacent circuits have been unloaded. For overhead conductors which do not benefit from this phenomenon, the ECC is synonymous with the NCC.
50 PoE Load (A) | Peak load forecast with 50% probability of being exceeded (one in every two years will be exceeded). Based on normal expected growth rates & weather corrected starting loads. This is the worst case (highest) load forecast beween summer day and summer night.
Security Standard | For security standard application, the general type of customer a sub-transmission, or transmission feeder is supplying.
Transfers | This is the total amount of load transfers that are available following the worst case network contingency. This includes automatic transfers that are controlled automatically through SCADA and are generally implemented within a minute, load transfers that can be implemented through screen switching by a network controller, manual transfers that are deployed via manually controlled switchgear locally by field staff, and mobile generation which can be deployed by field staff by moving generation to specific sites. It should be noted under the Safety Net in the Distribution Authority, it is generally assumed that 4MVA (70A) of generation is available for Urban feeders to meet this criteria and 10MVA (170A) is available for Rural feeders. These values have been used as a default in the forecast tables where these are sufficient to reduce the 50PoE load below the ECC rating. Where the load is still above the ECC rating, specific load transfers have been calculated for the feeder to determine whether the Safety Net criteria is met.
Hours PA > 95% Peak Load | The forecast number of hours per annum where the load exceeded 95% of the peak 50 PoE demand. This information is not readily available for every feeder without significant analysis being undertaken. As such, this has only been provided where a feeder does not meet the Safety Net criteria or is otherwise in the Limitations and Proposed Solutions table.

## 33kV Feeders - Summer
Bulk Supply Name | Feeder | From Substation | To Substation | Attributes | 2022 | 2023 | 2024 | 2025 | 2026 | Security Standard | Transfers | Hours above 95%
Abermain Bulk | 357-1 | Abermain BS | 357 Tee1 | NCC Rating (A) | 505 | 505 | 505 | 505 | 505 | Urban | 70
Abermain Bulk | 357-1 | Abermain BS | 357 Tee1 | 10 POE Load (A) | 198.7694 | 192.2326 | 188.6653 | 185.4494 | 185.2643
Abermain Bulk | 357-1 | Abermain BS | 357 Tee1 | Power Factor | 0.97355 | 0.97477 | 0.97486 | 0.97546 | 0.97549
Abermain Bulk | 357-1 | Abermain BS | 357 Tee1 | ECC Rating (A) | 505 | 505 | 505 | 505 | 505
Abermain Bulk | 357-1 | Abermain BS | 357 Tee1 | 50 POE Load (A) | 417.9267 | 410.0893 | 405.0372 | 399.9725 | 399.5997
Abermain Bulk | 357-2 | 357 Tee1 | Redbank | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Abermain Bulk | 357-2 | 357 Tee1 | Redbank | 10 POE Load (A) | 0.19555 | 0.1957 | 0.19578 | 0.19586 | 0.19586
Abermain Bulk | 357-2 | 357 Tee1 | Redbank | Power Factor | 1.4767e-05 | 1.4767e-05 | 1.4767e-05 | 1.4767e-05 | 1.4767e-05
Abermain Bulk | 357-2 | 357 Tee1 | Redbank | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Abermain Bulk | 357-2 | 357 Tee1 | Redbank | 50 POE Load (A) | 255.5005 | 252.8685 | 250.6956 | 248.2044 | 247.9885
Abermain Bulk | 357-3 | 357 Tee1 | Moggill | NCC Rating (A) | 710 | 710 | 710 | 710 | 710 | Urban | 70
Abermain Bulk | 357-3 | 357 Tee1 | Moggill | 10 POE Load (A) | 199.7117 | 193.1581 | 189.5926 | 186.3682 | 186.1826
Abermain Bulk | 357-3 | 357 Tee1 | Moggill | Power Factor | 0.97794 | 0.97888 | 0.97886 | 0.97933 | 0.97935
Abermain Bulk | 357-3 | 357 Tee1 | Moggill | ECC Rating (A) | 710 | 710 | 710 | 710 | 710
Abermain Bulk | 357-3 | 357 Tee1 | Moggill | 50 POE Load (A) | 163.4801 | 158.2605 | 155.3826 | 152.8019 | 152.6445
Abermain Bulk | 358-1 | Abermain BS | Ebbw Vale | NCC Rating (A) | 473 | 473 | 473 | 473 | 473 | Rural | 170
Abermain Bulk | 358-1 | Abermain BS | Ebbw Vale | 10 POE Load (A) | 0.82619 | 0.82619 | 0.82619 | 0.82619 | 0.82619
Abermain Bulk | 358-1 | Abermain BS | Ebbw Vale | Power Factor | -6.9808e-06 | -6.9808e-06 | -6.981e-06 | -6.9808e-06 | -6.981e-06
Abermain Bulk | 364-1 | Marburg | Rosewood | NCC Rating (A) | 155 | 155 | 155 | 155 | 155 | Rural | 170
Abermain Bulk | 364-1 | Marburg | Rosewood | 10 POE Load (A) | 88.549 | 93.8744 | 120.3139 | 136.7882 | 143.5358
Abermain Bulk | 364-1 | Marburg | Rosewood | Power Factor | 0.99943 | 0.99977 | 1 | 0.99979 | 0.99959
Abermain Bulk | 364-1 | Marburg | Rosewood | ECC Rating (A) | 155 | 155 | 155 | 155 | 155
Abermain Bulk | 364-1 | Marburg | Rosewood | 50 POE Load (A) | 85.2717 | 90.509 | 116.4124 | 132.5747 | 139.0904
Abermain Bulk | 365-1 | Abermain BS | 365 Tee1 | NCC Rating (A) | 746 | 746 | 746 | 746 | 746 | Rural | 170
Abermain Bulk | 365-1 | Abermain BS | 365 Tee1 | 10 POE Load (A) | 424.3214 | 446.1099 | 542.6024 | 603.2642 | 630.6327
Abermain Bulk | 365-1 | Abermain BS | 365 Tee1 | Power Factor | 0.95219 | 0.95059 | 0.9413 | 0.93844 | 0.93685
Abermain Bulk | 365-1 | Abermain BS | 365 Tee1 | ECC Rating (A) | 746 | 746 | 746 | 746 | 746
Abermain Bulk | 365-1 | Abermain BS | 365 Tee1 | 50 POE Load (A) | 385.3408 | 406.0411 | 499.212 | 557.9365 | 583.6015
Abermain Bulk | 365-2 | 365 Tee1 | 366 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Abermain Bulk | 365-2 | 365 Tee1 | 366 Tee1 | 10 POE Load (A) | 0.0092987 | 0.0092676 | 0.0091243 | 0.0090493 | 0.009012
Abermain Bulk | 365-2 | 365 Tee1 | 366 Tee1 | Power Factor | 2.0182e-05 | 2.0181e-05 | 2.0182e-05 | 2.0181e-05 | 2.0183e-05
Abermain Bulk | 365-3 | 365 Tee1 | Karrabin | NCC Rating (A) | 804 | 804 | 804 | 804 | 804 | Rural | 170
Abermain Bulk | 365-3 | 365 Tee1 | Karrabin | 10 POE Load (A) | 424.5315 | 446.3227 | 542.8277 | 603.4937 | 630.8632
Abermain Bulk | 365-3 | 365 Tee1 | Karrabin | Power Factor | 0.95306 | 0.95153 | 0.94253 | 0.93982 | 0.93831
Abermain Bulk | 365-3 | 365 Tee1 | Karrabin | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Abermain Bulk | 365-3 | 365 Tee1 | Karrabin | 50 POE Load (A) | 385.5471 | 406.2503 | 499.4347 | 558.1645 | 583.8309
Abermain Bulk | 366-1 | Abermain BS | 366 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Abermain Bulk | 366-1 | Abermain BS | 366 Tee1 | 10 POE Load (A) | 463.2274 | 487.0148 | 592.3597 | 658.5873 | 688.4669
Abermain Bulk | 366-1 | Abermain BS | 366 Tee1 | Power Factor | 0.93201 | 0.92901 | 0.91315 | 0.90689 | 0.9036
Abermain Bulk | 366-1 | Abermain BS | 366 Tee1 | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Abermain Bulk | 366-1 | Abermain BS | 366 Tee1 | 50 POE Load (A) | 420.6705 | 443.2698 | 544.9882 | 609.1004 | 637.1203
Abermain Bulk | 366-2 | 366 Tee1 | Karrabin | NCC Rating (A) | 758 | 758 | 758 | 758 | 758 | Rural | 170
Abermain Bulk | 366-2 | 366 Tee1 | Karrabin | 10 POE Load (A) | 463.3111 | 487.0996 | 592.4496 | 658.679 | 688.559
Abermain Bulk | 366-2 | 366 Tee1 | Karrabin | Power Factor | -0.94617 | -0.94428 | -0.93494 | -0.93077 | -0.92931
Abermain Bulk | 366-2 | 366 Tee1 | Karrabin | ECC Rating (A) | 758 | 758 | 758 | 758 | 758
Abermain Bulk | 366-2 | 366 Tee1 | Karrabin | 50 POE Load (A) | 420.7526 | 443.3532 | 545.077 | 609.1915 | 637.2119
Abermain Bulk | 366-3 | 366 Tee1 | 365 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Abermain Bulk | 366-3 | 366 Tee1 | 365 Tee1 | 10 POE Load (A) | 0.020888 | 0.020823 | 0.020522 | 0.020364 | 0.020285
Abermain Bulk | 366-3 | 366 Tee1 | 365 Tee1 | Power Factor | 9.0274e-06 | 9.0274e-06 | 9.0276e-06 | 9.0276e-06 | 9.0272e-06
Abermain Bulk | 367-1 | Abermain BS | Mt Crosby West | NCC Rating (A) | 530 | 530 | 530 | 530 | 530 | Rural | 170
Abermain Bulk | 367-1 | Abermain BS | Mt Crosby West | 10 POE Load (A) | 281.8425 | 280.2717 | 279.6296 | 278.7293 | 279.0656
Abermain Bulk | 367-1 | Abermain BS | Mt Crosby West | Power Factor | 0.94857 | 0.94862 | 0.94864 | 0.94867 | 0.94866
Abermain Bulk | 367-1 | Abermain BS | Mt Crosby West | ECC Rating (A) | 530 | 530 | 530 | 530 | 530
Abermain Bulk | 367-1 | Abermain BS | Mt Crosby West | 50 POE Load (A) | 263.1099 | 261.701 | 261.125 | 260.3173 | 260.6191
Abermain Bulk | 368-1 | Abermain BS | Mt Crosby | NCC Rating (A) | 529 | 529 | 529 | 529 | 529 | HighSec | 0
Abermain Bulk | 368-1 | Abermain BS | Mt Crosby | 10 POE Load (A) | 221.6759 | 220.6322 | 220.2057 | 219.6075 | 219.8309
Abermain Bulk | 368-1 | Abermain BS | Mt Crosby | Power Factor | 0.94007 | 0.94013 | 0.94015 | 0.94018 | 0.94017
Abermain Bulk | 368-1 | Abermain BS | Mt Crosby | ECC Rating (A) | 529 | 529 | 529 | 529 | 529
Abermain Bulk | 368-1 | Abermain BS | Mt Crosby | 50 POE Load (A) | 208.3932 | 207.4576 | 207.0751 | 206.5387 | 206.7391
Abermain Bulk | 369-1 | Abermain BS | Nth Ipswich | NCC Rating (A) | 499 | 499 | 499 | 499 | 499 | Urban | 70
Abermain Bulk | 369-1 | Abermain BS | Nth Ipswich | 10 POE Load (A) | 234.1362 | 235.6365 | 237.4322 | 237.4879 | 240.2995
Abermain Bulk | 369-1 | Abermain BS | Nth Ipswich | Power Factor | 0.99291 | 0.99269 | 0.99243 | 0.99242 | 0.99201
Abermain Bulk | 369-1 | Abermain BS | Nth Ipswich | ECC Rating (A) | 499 | 499 | 499 | 499 | 499
Abermain Bulk | 369-1 | Abermain BS | Nth Ipswich | 50 POE Load (A) | 222.4244 | 223.8361 | 225.5253 | 225.5777 | 228.2213
Abermain Bulk | 370-1 | Abermain BS | Nth Ipswich | NCC Rating (A) | 499 | 499 | 499 | 499 | 499 | Urban | 70
Abermain Bulk | 370-1 | Abermain BS | Nth Ipswich | 10 POE Load (A) | 238.1922 | 239.7185 | 241.5454 | 241.6021 | 244.4625
Abermain Bulk | 370-1 | Abermain BS | Nth Ipswich | Power Factor | 0.99354 | 0.99333 | 0.99308 | 0.99307 | 0.99268
Abermain Bulk | 370-1 | Abermain BS | Nth Ipswich | ECC Rating (A) | 499 | 499 | 499 | 499 | 499
Abermain Bulk | 370-1 | Abermain BS | Nth Ipswich | 50 POE Load (A) | 226.206 | 227.6416 | 229.3596 | 229.4129 | 232.1015
Abermain Bulk | 387-1 | Abermain BS | Marburg | NCC Rating (A) | 290 | 290 | 290 | 290 | 290 | Rural | 170
Abermain Bulk | 387-1 | Abermain BS | Marburg | 10 POE Load (A) | 198.7346 | 206.749 | 238.0213 | 257.9434 | 268.1155
Abermain Bulk | 387-1 | Abermain BS | Marburg | Power Factor | 0.99526 | 0.99485 | 0.99293 | 0.99218 | 0.99159
Abermain Bulk | 387-1 | Abermain BS | Marburg | ECC Rating (A) | 290 | 290 | 290 | 290 | 290
Abermain Bulk | 387-1 | Abermain BS | Marburg | 50 POE Load (A) | 174.2333 | 181.6096 | 211.2994 | 230.1754 | 239.4279
Abermain Bulk | 3901-1 | Karrabin | Amberley | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
Abermain Bulk | 3901-1 | Karrabin | Amberley | 10 POE Load (A) | 204.7134 | 223.5705 | 317.2663 | 374.7624 | 396.8626
Abermain Bulk | 3901-1 | Karrabin | Amberley | Power Factor | 0.94294 | 0.94046 | 0.92968 | 0.92846 | 0.92765
Abermain Bulk | 3901-1 | Karrabin | Amberley | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Abermain Bulk | 3901-1 | Karrabin | Amberley | 50 POE Load (A) | 184.1971 | 202.4218 | 293.9524 | 349.9396 | 371.0384
Abermain Bulk | 420-1 | Mt Crosby West | Mt Crosby | NCC Rating (A) | 349 | 349 | 349 | 349 | 349 | HighSec | 0
Abermain Bulk | 420-1 | Mt Crosby West | Mt Crosby | 10 POE Load (A) | 23.3111 | 24.1932 | 24.5567 | 25.069 | 24.8773
Abermain Bulk | 420-1 | Mt Crosby West | Mt Crosby | Power Factor | 0.92186 | 0.88882 | 0.87205 | 0.84476 | 0.8555
Abermain Bulk | 420-1 | Mt Crosby West | Mt Crosby | ECC Rating (A) | 349 | 349 | 349 | 349 | 349
Abermain Bulk | 420-1 | Mt Crosby West | Mt Crosby | 50 POE Load (A) | 29.6211 | 30.4613 | 30.806 | 31.2903 | 31.1092
Abermain Bulk | 436-1 | Amberley | 436 Tee1 | NCC Rating (A) | 351 | 351 | 351 | 351 | 351 | Rural | 170
Abermain Bulk | 436-1 | Amberley | 436 Tee1 | 10 POE Load (A) | 69.6887 | 67.344 | 49.6866 | 41.5673 | 40.3762
Abermain Bulk | 436-1 | Amberley | 436 Tee1 | Power Factor | -0.94224 | -0.936 | -0.89137 | -0.80092 | -0.74141
Abermain Bulk | 436-1 | Amberley | 436 Tee1 | ECC Rating (A) | 351 | 351 | 351 | 351 | 351
Abermain Bulk | 436-1 | Amberley | 436 Tee1 | 50 POE Load (A) | 58.7242 | 56.076 | 37.9816 | 29.5494 | 28.0293
Abermain Bulk | 436-2 | 436 Tee1 | Ebeneezer | NCC Rating (A) | 403 | 403 | 403 | 403 | 403 | Rural | 170
Abermain Bulk | 436-2 | 436 Tee1 | Ebeneezer | 10 POE Load (A) | 0.16972 | 0.1689 | 0.16521 | 0.16328 | 0.16232
Abermain Bulk | 436-2 | 436 Tee1 | Ebeneezer | Power Factor | 5.5134e-06 | 5.5137e-06 | 5.5134e-06 | 5.5136e-06 | 5.5134e-06
Abermain Bulk | 436-4 | 436 Tee1 | Rosewood | NCC Rating (A) | 208 | 208 | 208 | 208 | 208 | Rural | 170
Abermain Bulk | 436-4 | 436 Tee1 | Rosewood | 10 POE Load (A) | 69.8588 | 67.5208 | 49.8944 | 41.8053 | 40.6277
Abermain Bulk | 436-4 | 436 Tee1 | Rosewood | Power Factor | -0.94118 | -0.93463 | -0.88655 | -0.79114 | -0.73003
Abermain Bulk | 436-4 | 436 Tee1 | Rosewood | ECC Rating (A) | 208 | 208 | 208 | 208 | 208
Abermain Bulk | 436-4 | 436 Tee1 | Rosewood | 50 POE Load (A) | 228 | 236 | 245 | 250 | 228
Abermain Bulk | 445-1 | Abermain BS | Moggill | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70
Abermain Bulk | 445-1 | Abermain BS | Moggill | 10 POE Load (A) | 269.8877 | 261.0173 | 256.1808 | 251.8168 | 251.5657
Abermain Bulk | 445-1 | Abermain BS | Moggill | Power Factor | 0.97339 | 0.9744 | 0.97438 | 0.97488 | 0.97491
Abermain Bulk | 445-1 | Abermain BS | Moggill | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Abermain Bulk | 445-1 | Abermain BS | Moggill | 50 POE Load (A) | 333 | 331 | 330 | 326 | 326
Abermain Bulk | 475-1 | Karrabin | Amberley | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
Abermain Bulk | 475-1 | Karrabin | Amberley | 10 POE Load (A) | 201.6922 | 220.2709 | 312.5834 | 369.2304 | 391.0043
Abermain Bulk | 475-1 | Karrabin | Amberley | Power Factor | 0.94379 | 0.94132 | 0.93062 | 0.92941 | 0.9286
Abermain Bulk | 475-1 | Karrabin | Amberley | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Abermain Bulk | 475-1 | Karrabin | Amberley | 50 POE Load (A) | 362 | 400 | 438 | 441 | 441
Abermain Bulk | 673-1 | Moggill | Kenmore | NCC Rating (A) | 636 | 636 | 636 | 636 | 636 | Urban | 70
Abermain Bulk | 673-1 | Moggill | Kenmore | 10 POE Load (A) | 3.3869 | 3.3919 | 3.3947 | 3.3971 | 3.3973
Abermain Bulk | 673-1 | Moggill | Kenmore | Power Factor | 2.3519e-06 | 2.3519e-06 | 2.3519e-06 | 2.3519e-06 | 2.3519e-06
Abermain Bulk | 673-1 | Moggill | Kenmore | ECC Rating (A) | 636 | 636 | 636 | 636 | 636
Abermain Bulk | 673-1 | Moggill | Kenmore | 50 POE Load (A) | 3.4136 | 3.4174 | 3.4195 | 3.4214 | 3.4215
Algester Bulk | 3400-1 | Algester BS | Calamvale | NCC Rating (A) | 694 | 694 | 694 | 694 | 694 | Urban | 70
Algester Bulk | 3400-1 | Algester BS | Calamvale | 10 POE Load (A) | 358.2479 | 356.7454 | 356.4481 | 355.9024 | 358.0349
Algester Bulk | 3400-1 | Algester BS | Calamvale | Power Factor | 0.98506 | 0.98529 | 0.98534 | 0.98542 | 0.9851
Algester Bulk | 3400-1 | Algester BS | Calamvale | ECC Rating (A) | 765 | 765 | 765 | 765 | 765
Algester Bulk | 3400-1 | Algester BS | Calamvale | 50 POE Load (A) | 635 | 633 | 630 | 624 | 624
Algester Bulk | 3402-1 | Algester BS | Acacia Ridge | NCC Rating (A) | 687 | 687 | 687 | 687 | 687 | Urban | 70
Algester Bulk | 3402-1 | Algester BS | Acacia Ridge | 10 POE Load (A) | 160.3447 | 171.3957 | 170.2091 | 168.2696 | 167.8706
Algester Bulk | 3402-1 | Algester BS | Acacia Ridge | Power Factor | -0.9836 | -0.97999 | -0.98041 | -0.9811 | -0.98124
Algester Bulk | 3402-1 | Algester BS | Acacia Ridge | ECC Rating (A) | 739 | 739 | 739 | 739 | 739
Algester Bulk | 3402-1 | Algester BS | Acacia Ridge | 50 POE Load (A) | 283 | 282 | 282 | 280 | 283
Algester Bulk | 3403-1 | Algester BS | Acacia Ridge | NCC Rating (A) | 687 | 687 | 687 | 687 | 687 | Urban | 70
Algester Bulk | 3403-1 | Algester BS | Acacia Ridge | 10 POE Load (A) | 160.8038 | 171.8863 | 170.6963 | 168.7513 | 168.3512
Algester Bulk | 3403-1 | Algester BS | Acacia Ridge | Power Factor | -0.98362 | -0.98001 | -0.98043 | -0.98112 | -0.98126
Algester Bulk | 3403-1 | Algester BS | Acacia Ridge | ECC Rating (A) | 739 | 739 | 739 | 739 | 739
Algester Bulk | 3403-1 | Algester BS | Acacia Ridge | 50 POE Load (A) | 283 | 282 | 282 | 280 | 283
Algester Bulk | 3405-1 | Algester BS | Calamvale | NCC Rating (A) | 694 | 694 | 694 | 694 | 694 | Urban | 70
Algester Bulk | 3405-1 | Algester BS | Calamvale | 10 POE Load (A) | 358.6601 | 357.1559 | 356.8583 | 356.3119 | 358.4469
Algester Bulk | 3405-1 | Algester BS | Calamvale | Power Factor | 0.98506 | 0.98529 | 0.98533 | 0.98542 | 0.98509
Algester Bulk | 3405-1 | Algester BS | Calamvale | ECC Rating (A) | 765 | 765 | 765 | 765 | 765
Algester Bulk | 3405-1 | Algester BS | Calamvale | 50 POE Load (A) | 635 | 633 | 630 | 624 | 635
Archerfield Bulk | 597-1 | Rocklea | Salisbury | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70
Archerfield Bulk | 597-1 | Rocklea | Salisbury | 10 POE Load (A) | 218.8158 | 212.1121 | 210.5731 | 210.2489 | 211.3811
Archerfield Bulk | 597-1 | Rocklea | Salisbury | Power Factor | 0.97236 | 0.97309 | 0.97326 | 0.9733 | 0.97317
Archerfield Bulk | 597-1 | Rocklea | Salisbury | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
Archerfield Bulk | 597-1 | Rocklea | Salisbury | 50 POE Load (A) | 185.7186 | 180.0792 | 178.7843 | 178.5118 | 179.4647
Archerfield Bulk | 635-1 | Archerfield BS | Coopers Plains | NCC Rating (A) | 523 | 523 | 523 | 523 | 523 | Urban | 70
Archerfield Bulk | 635-1 | Archerfield BS | Coopers Plains | 10 POE Load (A) | 305.7489 | 299.3312 | 293.0833 | 286.14 | 281.625
Archerfield Bulk | 635-1 | Archerfield BS | Coopers Plains | Power Factor | 0.98704 | 0.98822 | 0.98936 | 0.9906 | 0.99139
Archerfield Bulk | 635-1 | Archerfield BS | Coopers Plains | ECC Rating (A) | 523 | 523 | 523 | 523 | 523
Archerfield Bulk | 635-1 | Archerfield BS | Coopers Plains | 50 POE Load (A) | 299.4859 | 293.2161 | 287.112 | 280.3288 | 275.9181
Archerfield Bulk | 650-1 | Archerfield BS | Rocklea | NCC Rating (A) | 650 | 650 | 650 | 650 | 650 | Urban | 70
Archerfield Bulk | 650-1 | Archerfield BS | Rocklea | 10 POE Load (A) | 267.078 | 261.6141 | 258.8671 | 256.3115 | 255.9795
Archerfield Bulk | 650-1 | Archerfield BS | Rocklea | Power Factor | 0.97026 | 0.97078 | 0.97104 | 0.97129 | 0.97132
Archerfield Bulk | 650-1 | Archerfield BS | Rocklea | ECC Rating (A) | 740 | 740 | 740 | 740 | 740
Archerfield Bulk | 650-1 | Archerfield BS | Rocklea | 50 POE Load (A) | 455 | 447 | 443 | 438 | 438
Archerfield Bulk | 651-1 | Archerfield BS | Rocklea | NCC Rating (A) | 650 | 650 | 650 | 650 | 650 | Urban | 70
Archerfield Bulk | 651-1 | Archerfield BS | Rocklea | 10 POE Load (A) | 264.0239 | 258.6229 | 255.9075 | 253.3812 | 253.0531
Archerfield Bulk | 651-1 | Archerfield BS | Rocklea | Power Factor | 0.97033 | 0.97085 | 0.97111 | 0.97135 | 0.97139
Archerfield Bulk | 651-1 | Archerfield BS | Rocklea | ECC Rating (A) | 740 | 740 | 740 | 740 | 740
Archerfield Bulk | 651-1 | Archerfield BS | Rocklea | 50 POE Load (A) | 455 | 447 | 443 | 438 | 438
Ashgrove West Bulk | 432-1 | Ashgrove West BS | Toowong | NCC Rating (A) | 476 | 476 | 476 | 476 | 476 | Urban | 70
Ashgrove West Bulk | 432-1 | Ashgrove West BS | Toowong | 10 POE Load (A) | 13.5922 | 13.5922 | 13.5922 | 13.5922 | 13.5922
Ashgrove West Bulk | 432-1 | Ashgrove West BS | Toowong | Power Factor | 4.2657e-05 | 4.2657e-05 | 4.2657e-05 | 4.2657e-05 | 4.2657e-05
Ashgrove West Bulk | 432-1 | Ashgrove West BS | Toowong | ECC Rating (A) | 476 | 476 | 476 | 476 | 476
Ashgrove West Bulk | 432-1 | Ashgrove West BS | Toowong | 50 POE Load (A) | 13.5922 | 13.5922 | 13.5922 | 13.5922 | 13.5922
Ashgrove West Bulk | 552-1 | Ashgrove West BS | Ashgrove | NCC Rating (A) | 598 | 598 | 598 | 598 | 598 | Urban | 70
Ashgrove West Bulk | 552-1 | Ashgrove West BS | Ashgrove | 10 POE Load (A) | 189.9566 | 189.0342 | 188.8699 | 188.5942 | 189.6023
Ashgrove West Bulk | 552-1 | Ashgrove West BS | Ashgrove | Power Factor | 0.99993 | 0.99995 | 0.99995 | 0.99995 | 0.99994
Ashgrove West Bulk | 552-1 | Ashgrove West BS | Ashgrove | ECC Rating (A) | 598 | 598 | 598 | 598 | 598
Ashgrove West Bulk | 552-1 | Ashgrove West BS | Ashgrove | 50 POE Load (A) | 239 | 239 | 238 | 236 | 236
Ashgrove West Bulk | 565-1 | Ashgrove West BS | Ashgrove | NCC Rating (A) | 851 | 851 | 851 | 851 | 851 | Urban | 70
Ashgrove West Bulk | 565-1 | Ashgrove West BS | Ashgrove | 10 POE Load (A) | 131.1057 | 130.4704 | 130.3572 | 130.1673 | 130.8617
Ashgrove West Bulk | 565-1 | Ashgrove West BS | Ashgrove | Power Factor | 0.99044 | 0.99061 | 0.99064 | 0.99069 | 0.9905
Ashgrove West Bulk | 565-1 | Ashgrove West BS | Ashgrove | ECC Rating (A) | 851 | 851 | 851 | 851 | 851
Ashgrove West Bulk | 565-1 | Ashgrove West BS | Ashgrove | 50 POE Load (A) | 111.0671 | 110.5332 | 110.4381 | 110.2785 | 110.862
Ashgrove West Bulk | 570-1 | Ashgrove West BS | Ashgrove | NCC Rating (A) | 598 | 598 | 598 | 598 | 598 | Urban | 70
Ashgrove West Bulk | 570-1 | Ashgrove West BS | Ashgrove | 10 POE Load (A) | 185.5431 | 184.642 | 184.4815 | 184.2122 | 185.1969
Ashgrove West Bulk | 570-1 | Ashgrove West BS | Ashgrove | Power Factor | 0.99994 | 0.99995 | 0.99996 | 0.99996 | 0.99995
Ashgrove West Bulk | 570-1 | Ashgrove West BS | Ashgrove | ECC Rating (A) | 672 | 672 | 672 | 672 | 672
Ashgrove West Bulk | 570-1 | Ashgrove West BS | Ashgrove | 50 POE Load (A) | 237 | 237 | 236 | 234 | 234
Ashgrove West Bulk | 585-1 | Ashgrove West BS | The Gap | NCC Rating (A) | 622 | 622 | 622 | 622 | 622 | Urban | 70
Ashgrove West Bulk | 585-1 | Ashgrove West BS | The Gap | 10 POE Load (A) | 184.5887 | 182.6289 | 181.3371 | 179.5831 | 179.314
Ashgrove West Bulk | 585-1 | Ashgrove West BS | The Gap | Power Factor | 0.99088 | 0.99107 | 0.9912 | 0.99138 | 0.9914
Ashgrove West Bulk | 585-1 | Ashgrove West BS | The Gap | ECC Rating (A) | 622 | 622 | 622 | 622 | 622
Ashgrove West Bulk | 585-1 | Ashgrove West BS | The Gap | 50 POE Load (A) | 297.1392 | 295.485 | 294.3504 | 292.8089 | 292.5768
Ashgrove West Bulk | 586-1 | Ashgrove West BS | The Gap | NCC Rating (A) | 622 | 622 | 622 | 622 | 622 | Urban | 70
Ashgrove West Bulk | 586-1 | Ashgrove West BS | The Gap | 10 POE Load (A) | 184.8431 | 182.8762 | 181.5799 | 179.8197 | 179.5497
Ashgrove West Bulk | 586-1 | Ashgrove West BS | The Gap | Power Factor | 0.99002 | 0.99023 | 0.99037 | 0.99057 | 0.9906
Ashgrove West Bulk | 586-1 | Ashgrove West BS | The Gap | ECC Rating (A) | 622 | 622 | 622 | 622 | 622
Ashgrove West Bulk | 586-1 | Ashgrove West BS | The Gap | 50 POE Load (A) | 297.3208 | 295.5935 | 294.4568 | 292.9126 | 292.6801
Ashgrove West Bulk | 590-1 | Ashgrove BS | Toowong | NCC Rating (A) | 705 | 705 | 705 | 705 | 705 | Urban | 70
Ashgrove West Bulk | 590-1 | Ashgrove BS | Toowong | 10 POE Load (A) | 368.2665 | 366.4484 | 365.2576 | 362.9305 | 364.6956
Ashgrove West Bulk | 590-1 | Ashgrove BS | Toowong | Power Factor | 0.98007 | 0.98036 | 0.98055 | 0.98086 | 0.98064
Ashgrove West Bulk | 590-1 | Ashgrove BS | Toowong | ECC Rating (A) | 705 | 705 | 705 | 705 | 705
Ashgrove West Bulk | 590-1 | Ashgrove BS | Toowong | 50 POE Load (A) | 613 | 615 | 615 | 614 | 614
Ashgrove West Bulk | 591-1 | Ashgrove BS | Toowong | NCC Rating (A) | 705 | 705 | 705 | 705 | 705 | Urban | 70
Ashgrove West Bulk | 591-1 | Ashgrove BS | Toowong | 10 POE Load (A) | 368.154 | 366.3364 | 365.146 | 362.8196 | 364.5842
Ashgrove West Bulk | 591-1 | Ashgrove BS | Toowong | Power Factor | 0.98002 | 0.98031 | 0.9805 | 0.98081 | 0.98058
Ashgrove West Bulk | 591-1 | Ashgrove BS | Toowong | ECC Rating (A) | 705 | 705 | 705 | 705 | 705
Ashgrove West Bulk | 591-1 | Ashgrove BS | Toowong | 50 POE Load (A) | 613 | 615 | 615 | 614 | 614
Ashgrove West Bulk | 675-1 | Ashgrove | Newmarket | NCC Rating (A) | 492 | 492 | 492 | 492 | 492 | Urban | 70
Ashgrove West Bulk | 675-1 | Ashgrove | Newmarket | 10 POE Load (A) | 17.161 | 17.1611 | 17.1612 | 17.1612 | 17.1611
Ashgrove West Bulk | 675-1 | Ashgrove | Newmarket | Power Factor | 3.5471e-05 | 3.5471e-05 | 3.5471e-05 | 3.5471e-05 | 3.5471e-05
Ashgrove West Bulk | 675-1 | Ashgrove | Newmarket | ECC Rating (A) | 492 | 492 | 492 | 492 | 492
Ashgrove West Bulk | 675-1 | Ashgrove | Newmarket | 50 POE Load (A) | 17.1653 | 17.1654 | 17.1654 | 17.1654 | 17.1653
Ashgrove West Bulk | 676-1 | Ashgrove | Newmarket | NCC Rating (A) | 492 | 492 | 492 | 492 | 492 | Urban | 70
Ashgrove West Bulk | 676-1 | Ashgrove | Newmarket | 10 POE Load (A) | 17.0349 | 17.035 | 17.0351 | 17.0351 | 17.0349
Ashgrove West Bulk | 676-1 | Ashgrove | Newmarket | Power Factor | 3.5079e-05 | 3.5079e-05 | 3.5079e-05 | 3.5079e-05 | 3.5079e-05
Ashgrove West Bulk | 676-1 | Ashgrove | Newmarket | ECC Rating (A) | 492 | 492 | 492 | 492 | 492
Ashgrove West Bulk | 676-1 | Ashgrove | Newmarket | 50 POE Load (A) | 17.0391 | 17.0392 | 17.0393 | 17.0393 | 17.0392
Beaudesert Bulk | 314-1 | Beaudesert BS | Jimboomba | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Rural | 170
Beaudesert Bulk | 314-1 | Beaudesert BS | Jimboomba | 10 POE Load (A) | 1.6333 | 1.6333 | 1.6333 | 1.6333 | 1.6333
Beaudesert Bulk | 314-1 | Beaudesert BS | Jimboomba | Power Factor | 0.00013446 | 0.00013446 | 0.00013446 | 0.00013446 | 0.00013446
Beaudesert Bulk | 314-1 | Beaudesert BS | Jimboomba | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
Beaudesert Bulk | 314-1 | Beaudesert BS | Jimboomba | 50 POE Load (A) | 1.6333 | 1.6333 | 1.6333 | 1.6333 | 1.6333
Beaudesert Bulk | 404-1 | Beaudesert | Innisplain | NCC Rating (A) | 155 | 155 | 155 | 155 | 155 | Rural | 170
Beaudesert Bulk | 404-1 | Beaudesert | Innisplain | 10 POE Load (A) | 137.7069 | 139.7611 | 141.9817 | 143.7613 | 146.6773
Beaudesert Bulk | 404-1 | Beaudesert | Innisplain | Power Factor | 0.9803 | 0.97992 | 0.97951 | 0.9796 | 0.97907
Beaudesert Bulk | 404-1 | Beaudesert | Innisplain | ECC Rating (A) | 155 | 155 | 155 | 155 | 155
Beaudesert Bulk | 404-1 | Beaudesert | Innisplain | 50 POE Load (A) | 115.5219 | 117.1826 | 118.8809 | 120.4183 | 122.7613
Beaudesert Bulk | 466-1 | Beaudesert BS | Bromelton | NCC Rating (A) | 403 | 403 | 403 | 403 | 403 | Rural | 170
Beaudesert Bulk | 466-1 | Beaudesert BS | Bromelton | 10 POE Load (A) | 99.6779 | 114.6785 | 130.2579 | 136.0478 | 136.8884
Beaudesert Bulk | 466-1 | Beaudesert BS | Bromelton | Power Factor | 0.99313 | 0.98932 | 0.98583 | 0.99365 | 0.99346
Beaudesert Bulk | 466-1 | Beaudesert BS | Bromelton | ECC Rating (A) | 403 | 403 | 403 | 403 | 403
Beaudesert Bulk | 466-1 | Beaudesert BS | Bromelton | 50 POE Load (A) | 179 | 205 | 227 | 240 | 240
Beaudesert Bulk | 467-1 | Beaudesert BS | Bromelton | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
Beaudesert Bulk | 467-1 | Beaudesert BS | Bromelton | 10 POE Load (A) | 67.1092 | 77.2129 | 87.7061 | 91.5998 | 92.1646
Beaudesert Bulk | 467-1 | Beaudesert BS | Bromelton | Power Factor | 0.99995 | 0.99982 | 0.99904 | 0.99998 | 0.99999
Beaudesert Bulk | 467-1 | Beaudesert BS | Bromelton | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Beaudesert Bulk | 467-1 | Beaudesert BS | Bromelton | 50 POE Load (A) | 64.3739 | 74.4351 | 84.8862 | 90.0745 | 89.3733
Beaudesert Bulk | 468-1 | Beaudesert BS | Beaudesert | NCC Rating (A) | 579 | 579 | 579 | 579 | 579 | Rural | 170
Beaudesert Bulk | 468-1 | Beaudesert BS | Beaudesert | 10 POE Load (A) | 327.328 | 331.5472 | 337.2219 | 341.8282 | 349.181
Beaudesert Bulk | 468-1 | Beaudesert BS | Beaudesert | Power Factor | 0.91648 | 0.91539 | 0.91393 | 0.91289 | 0.91107
Beaudesert Bulk | 468-1 | Beaudesert BS | Beaudesert | ECC Rating (A) | 579 | 579 | 579 | 579 | 579
Beaudesert Bulk | 468-1 | Beaudesert BS | Beaudesert | 50 POE Load (A) | 424.3234 | 427.4285 | 432.0813 | 435.9782 | 443.3382
Beaudesert Bulk | 469-1 | Beaudesert BS | 469 Tee1 | NCC Rating (A) | 537 | 537 | 537 | 537 | 537 | Rural | 170
Beaudesert Bulk | 469-1 | Beaudesert BS | 469 Tee1 | 10 POE Load (A) | 334.2752 | 338.5612 | 344.334 | 349.0173 | 356.5059
Beaudesert Bulk | 469-1 | Beaudesert BS | 469 Tee1 | Power Factor | 0.95086 | 0.94999 | 0.94882 | 0.94798 | 0.94651
Beaudesert Bulk | 469-1 | Beaudesert BS | 469 Tee1 | ECC Rating (A) | 537 | 537 | 537 | 537 | 537
Beaudesert Bulk | 469-1 | Beaudesert BS | 469 Tee1 | 50 POE Load (A) | 280.8906 | 284.3414 | 288.5704 | 292.3993 | 298.4346
Beaudesert Bulk | 469-2 | 469 Tee1 | Beaudesert | NCC Rating (A) | 579 | 579 | 579 | 579 | 579 | Rural | 170
Beaudesert Bulk | 469-2 | 469 Tee1 | Beaudesert | 10 POE Load (A) | 260.7559 | 265.4048 | 271.2431 | 276.1477 | 282.417
Beaudesert Bulk | 469-2 | 469 Tee1 | Beaudesert | Power Factor | 0.94358 | 0.94261 | 0.94129 | 0.94038 | 0.93871
Beaudesert Bulk | 469-2 | 469 Tee1 | Beaudesert | ECC Rating (A) | 579 | 579 | 579 | 579 | 579
Beaudesert Bulk | 469-2 | 469 Tee1 | Beaudesert | 50 POE Load (A) | 450 | 458 | 467 | 475 | 475
Beaudesert Bulk | 469-3 | 469 Tee1 | Mt Tamborine Bus 2 | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Rural | 170
Beaudesert Bulk | 469-3 | 469 Tee1 | Mt Tamborine Bus 2 | 10 POE Load (A) | 75.796 | 75.4746 | 75.5082 | 75.3805 | 75.9167
Beaudesert Bulk | 469-3 | 469 Tee1 | Mt Tamborine Bus 2 | Power Factor | 0.98239 | 0.98241 | 0.98241 | 0.98242 | 0.98237
Beaudesert Bulk | 469-3 | 469 Tee1 | Mt Tamborine Bus 2 | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
Beaudesert Bulk | 469-3 | 469 Tee1 | Mt Tamborine Bus 2 | 50 POE Load (A) | 218.5443 | 217.955 | 218.4713 | 218.4815 | 220.396
Beenleigh Bulk | 3590-1 | Beenleigh BS | Loganholme | NCC Rating (A) | 766 | 766 | 766 | 766 | 766 | Urban | 70
Beenleigh Bulk | 3590-1 | Beenleigh BS | Loganholme | 10 POE Load (A) | 440.7261 | 435.5744 | 432.6295 | 428.0863 | 427.6635
Beenleigh Bulk | 3590-1 | Beenleigh BS | Loganholme | Power Factor | 0.99418 | 0.99446 | 0.99479 | 0.99503 | 0.99506
Beenleigh Bulk | 3590-1 | Beenleigh BS | Loganholme | ECC Rating (A) | 766 | 766 | 766 | 766 | 766
Beenleigh Bulk | 3590-1 | Beenleigh BS | Loganholme | 50 POE Load (A) | 647 | 673 | 670 | 666 | 666
Beenleigh Bulk | 3591-1 | Cornubia | Loganholme | NCC Rating (A) | 807 | 807 | 807 | 807 | 807 | Urban | 70
Beenleigh Bulk | 3591-1 | Cornubia | Loganholme | 10 POE Load (A) | 77.6866 | 76.7386 | 75.9013 | 74.3823 | 73.3091
Beenleigh Bulk | 3591-1 | Cornubia | Loganholme | Power Factor | 0.99997 | 1 | 0.99996 | 0.99983 | 0.9997
Beenleigh Bulk | 3591-1 | Cornubia | Loganholme | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Beenleigh Bulk | 3591-1 | Cornubia | Loganholme | 50 POE Load (A) | 444 | 471 | 469 | 466 | 460
Beenleigh Bulk | 3600-1 | Yatala | Stapylton | NCC Rating (A) | 713 | 713 | 713 | 713 | 713 | Rural | 170
Beenleigh Bulk | 3600-1 | Yatala | Stapylton | 10 POE Load (A) | 97.0559 | 95.8962 | 95.0204 | 94.3733 | 94.3285
Beenleigh Bulk | 3600-1 | Yatala | Stapylton | Power Factor | 0.97112 | 0.9713 | 0.97143 | 0.97153 | 0.97154
Beenleigh Bulk | 3600-1 | Yatala | Stapylton | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
Beenleigh Bulk | 3600-1 | Yatala | Stapylton | 50 POE Load (A) | 192 | 191 | 191 | 190 | 190
Beenleigh Bulk | 3601-1 | Yatala | Stapylton | NCC Rating (A) | 713 | 713 | 713 | 713 | 713 | Rural | 170
Beenleigh Bulk | 3601-1 | Yatala | Stapylton | 10 POE Load (A) | 92.9722 | 91.8614 | 91.0225 | 90.4027 | 90.3598
Beenleigh Bulk | 3601-1 | Yatala | Stapylton | Power Factor | 0.96909 | 0.96928 | 0.96942 | 0.96953 | 0.96954
Beenleigh Bulk | 3601-1 | Yatala | Stapylton | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
Beenleigh Bulk | 3601-1 | Yatala | Stapylton | 50 POE Load (A) | 193 | 192 | 191 | 190 | 189
Beenleigh Bulk | 3620-1 | Beenleigh BS | Logan Village | NCC Rating (A) | 490 | 490 | 490 | 490 | 490 | Rural | 170
Beenleigh Bulk | 3620-1 | Beenleigh BS | Logan Village | 10 POE Load (A) | 1.8209 | 1.8209 | 1.8209 | 1.8209 | 1.8209
Beenleigh Bulk | 3620-1 | Beenleigh BS | Logan Village | Power Factor | 0.00010523 | 0.00010523 | 0.00010523 | 0.00010523 | 0.00010523
Beenleigh Bulk | 3620-1 | Beenleigh BS | Logan Village | ECC Rating (A) | 490 | 490 | 490 | 490 | 490
Beenleigh Bulk | 3620-1 | Beenleigh BS | Logan Village | 50 POE Load (A) | 338 | 348 | 355 | 362 | 370
Beenleigh Bulk | 402-1 | Beenleigh BS | 402 Tee1 | NCC Rating (A) | 579 | 579 | 579 | 579 | 579 | Urban | 70
Beenleigh Bulk | 402-1 | Beenleigh BS | 402 Tee1 | 10 POE Load (A) | 164.9559 | 164.6319 | 165.1891 | 165.3374 | 166.9411
Beenleigh Bulk | 402-1 | Beenleigh BS | 402 Tee1 | Power Factor | 0.98574 | 0.98577 | 0.98575 | 0.98575 | 0.98566
Beenleigh Bulk | 402-1 | Beenleigh BS | 402 Tee1 | ECC Rating (A) | 579 | 579 | 579 | 579 | 579
Beenleigh Bulk | 402-1 | Beenleigh BS | 402 Tee1 | 50 POE Load (A) | 382 | 386 | 386 | 386 | 386
Beenleigh Bulk | 402-2 | 402 Tee1 | Tamborine Village | NCC Rating (A) | 439 | 439 | 439 | 439 | 439 | Urban | 70
Beenleigh Bulk | 402-2 | 402 Tee1 | Tamborine Village | 10 POE Load (A) | 89.806 | 89.8262 | 90.3628 | 90.6542 | 91.7251
Beenleigh Bulk | 402-2 | 402 Tee1 | Tamborine Village | Power Factor | 0.98956 | 0.98956 | 0.98951 | 0.98948 | 0.98938
Beenleigh Bulk | 402-2 | 402 Tee1 | Tamborine Village | ECC Rating (A) | 439 | 439 | 439 | 439 | 439
Beenleigh Bulk | 402-2 | 402 Tee1 | Tamborine Village | 50 POE Load (A) | 80.8655 | 80.8849 | 81.3651 | 81.6264 | 82.5825
Beenleigh Bulk | 402-3 | 402 Tee1 | Mt Tamborine Bus 1 | NCC Rating (A) | 812 | 812 | 812 | 812 | 812 | Urban | 70
Beenleigh Bulk | 402-3 | 402 Tee1 | Mt Tamborine Bus 1 | 10 POE Load (A) | 76.9483 | 76.5966 | 76.6152 | 76.4679 | 77.007
Beenleigh Bulk | 402-3 | 402 Tee1 | Mt Tamborine Bus 1 | Power Factor | 0.98244 | 0.98246 | 0.98246 | 0.98247 | 0.98243
Beenleigh Bulk | 402-3 | 402 Tee1 | Mt Tamborine Bus 1 | ECC Rating (A) | 812 | 812 | 812 | 812 | 812
Beenleigh Bulk | 402-3 | 402 Tee1 | Mt Tamborine Bus 1 | 50 POE Load (A) | 299 | 301 | 301 | 301 | 301
Beenleigh Bulk | 405-1 | Beenleigh BS | 405 Tee1 | NCC Rating (A) | 807 | 807 | 807 | 807 | 807 | Urban | 70
Beenleigh Bulk | 405-1 | Beenleigh BS | 405 Tee1 | 10 POE Load (A) | 306.6221 | 303.0602 | 301.141 | 298.2712 | 298.3747
Beenleigh Bulk | 405-1 | Beenleigh BS | 405 Tee1 | Power Factor | 0.98654 | 0.98697 | 0.98739 | 0.98774 | 0.98775
Beenleigh Bulk | 405-1 | Beenleigh BS | 405 Tee1 | ECC Rating (A) | 807 | 807 | 807 | 807 | 807
Beenleigh Bulk | 405-1 | Beenleigh BS | 405 Tee1 | 50 POE Load (A) | 661 | 693 | 690 | 685 | 680
Beenleigh Bulk | 405-3 | 405 Tee1 | Cornubia | NCC Rating (A) | 774 | 774 | 774 | 774 | 774 | Urban | 70
Beenleigh Bulk | 405-3 | 405 Tee1 | Cornubia | 10 POE Load (A) | 306.7868 | 303.2225 | 301.302 | 298.4301 | 298.5335
Beenleigh Bulk | 405-3 | 405 Tee1 | Cornubia | Power Factor | 0.98912 | 0.98948 | 0.98985 | 0.99014 | 0.99015
Beenleigh Bulk | 405-3 | 405 Tee1 | Cornubia | ECC Rating (A) | 774 | 774 | 774 | 774 | 774
Beenleigh Bulk | 405-3 | 405 Tee1 | Cornubia | 50 POE Load (A) | 661 | 693 | 690 | 685 | 680
Beenleigh Bulk | 419-1 | Loganholme | Tanah Merah | NCC Rating (A) | 712 | 712 | 712 | 712 | 712 | Urban | 70
Beenleigh Bulk | 419-1 | Loganholme | Tanah Merah | 10 POE Load (A) | 0.90886 | 0.90926 | 0.90956 | 0.90991 | 0.90994
Beenleigh Bulk | 419-1 | Loganholme | Tanah Merah | Power Factor | -2.6742e-06 | -2.6744e-06 | -2.6738e-06 | -2.6749e-06 | -2.6743e-06
Beenleigh Bulk | 419-1 | Loganholme | Tanah Merah | ECC Rating (A) | 712 | 712 | 712 | 712 | 712
Beenleigh Bulk | 419-1 | Loganholme | Tanah Merah | 50 POE Load (A) | 308.0621 | 305.9789 | 305.4715 | 304.8839 | 306.5517
Beenleigh Bulk | 426-1 | Beenleigh BS | Yatala | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Rural | 170
Beenleigh Bulk | 426-1 | Beenleigh BS | Yatala | 10 POE Load (A) | 96.8054 | 95.6468 | 94.772 | 94.1255 | 94.0807
Beenleigh Bulk | 426-1 | Beenleigh BS | Yatala | Power Factor | 0.99898 | 0.99898 | 0.99898 | 0.99898 | 0.99898
Beenleigh Bulk | 426-1 | Beenleigh BS | Yatala | ECC Rating (A) | 740 | 740 | 740 | 740 | 740
Beenleigh Bulk | 426-1 | Beenleigh BS | Yatala | 50 POE Load (A) | 94.2901 | 93.1615 | 92.3091 | 91.6791 | 91.6355
Beenleigh Bulk | 427-1 | Beenleigh BS | Yatala | NCC Rating (A) | 740 | 740 | 740 | 740 | 740 | Rural | 170
Beenleigh Bulk | 427-1 | Beenleigh BS | Yatala | 10 POE Load (A) | 92.8245 | 91.7144 | 90.8762 | 90.2569 | 90.214
Beenleigh Bulk | 427-1 | Beenleigh BS | Yatala | Power Factor | 0.96927 | 0.9695 | 0.96968 | 0.96981 | 0.96982
Beenleigh Bulk | 427-1 | Beenleigh BS | Yatala | ECC Rating (A) | 740 | 740 | 740 | 740 | 740
Beenleigh Bulk | 427-1 | Beenleigh BS | Yatala | 50 POE Load (A) | 90.4127 | 89.3313 | 88.5146 | 87.9111 | 87.8693
Beenleigh Bulk | 453-1 | Beenleigh BS | Beenleigh Nth | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 90
Beenleigh Bulk | 453-1 | Beenleigh BS | Beenleigh Nth | 10 POE Load (A) | 794.7022 | 799.7009 | 807.3627 | 814.796 | 827.9021
Beenleigh Bulk | 453-1 | Beenleigh BS | Beenleigh Nth | Power Factor | 0.97436 | 0.97421 | 0.97398 | 0.97375 | 0.97333
Beenleigh Bulk | 453-1 | Beenleigh BS | Beenleigh Nth | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Beenleigh Bulk | 453-1 | Beenleigh BS | Beenleigh Nth | 50 POE Load (A) | 854.6251 | 858.887 | 866.1881 | 872.6276 | 885.5926
Beenleigh Bulk | 496-1 | Beenleigh Nth | Bethania | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70
Beenleigh Bulk | 496-1 | Beenleigh Nth | Bethania | 10 POE Load (A) | 434.3109 | 435.4905 | 438.9744 | 442.6812 | 449.5264
Beenleigh Bulk | 496-1 | Beenleigh Nth | Bethania | Power Factor | -0.9762 | -0.97612 | -0.97589 | -0.97565 | -0.97521
Beenleigh Bulk | 496-1 | Beenleigh Nth | Bethania | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Beenleigh Bulk | 496-1 | Beenleigh Nth | Bethania | 50 POE Load (A) | 515.9055 | 516.5925 | 519.9885 | 522.9805 | 530.1002
Beerwah Bulk | 324-1 | Woodford | Kilcoy | NCC Rating (A) | 348 | 348 | 348 | 348 | 348 | Rural | 170
Beerwah Bulk | 324-1 | Woodford | Kilcoy | 10 POE Load (A) | 269.94 | 271.9604 | 273.2617 | 273.5418 | 276.756
Beerwah Bulk | 324-1 | Woodford | Kilcoy | Power Factor | 0.98421 | 0.98381 | 0.98355 | 0.98349 | 0.98285
Beerwah Bulk | 324-1 | Woodford | Kilcoy | ECC Rating (A) | 348 | 348 | 348 | 348 | 348
Beerwah Bulk | 324-1 | Woodford | Kilcoy | 50 POE Load (A) | 244.8519 | 246.5375 | 247.6209 | 247.8541 | 250.5224
Beerwah Bulk | 428-1 | Beerwah BS | Woodford | NCC Rating (A) | 351 | 351 | 351 | 351 | 351 | Rural | 170
Beerwah Bulk | 428-1 | Beerwah BS | Woodford | 10 POE Load (A) | 311.0639 | 313.9454 | 315.8086 | 316.2104 | 320.8408
Beerwah Bulk | 428-1 | Beerwah BS | Woodford | Power Factor | 0.93197 | 0.93077 | 0.92999 | 0.92982 | 0.92789
Beerwah Bulk | 428-1 | Beerwah BS | Woodford | ECC Rating (A) | 351 | 351 | 351 | 351 | 351
Beerwah Bulk | 428-1 | Beerwah BS | Woodford | 50 POE Load (A) | 275.8533 | 278.1207 | 279.5823 | 279.8973 | 283.5128
Beerwah Bulk | 447-1 | Somerset Dam | Kilcoy | NCC Rating (A) | 155 | 155 | 155 | 155 | 155 | Rural | 170
Beerwah Bulk | 447-1 | Somerset Dam | Kilcoy | 10 POE Load (A) | 1.4242 | 1.4215 | 1.4197 | 1.4193 | 1.415
Beerwah Bulk | 447-1 | Somerset Dam | Kilcoy | Power Factor | 0.00025447 | 0.00025447 | 0.00025447 | 0.00025447 | 0.00025447
Beerwah Bulk | 447-1 | Somerset Dam | Kilcoy | ECC Rating (A) | 155 | 155 | 155 | 155 | 155
Beerwah Bulk | 447-1 | Somerset Dam | Kilcoy | 50 POE Load (A) | 244.8519 | 246.5375 | 247.6209 | 247.8541 | 250.5224
Beerwah Bulk | 477-1 | 477 Tee1 | Maleny | NCC Rating (A) | 155 | 155 | 155 | 155 | 155 | Rural | 170
Beerwah Bulk | 477-1 | 477 Tee1 | Maleny | 10 POE Load (A) | 1.5629 | 1.5635 | 1.5637 | 1.5639 | 1.5634
Beerwah Bulk | 477-1 | 477 Tee1 | Maleny | Power Factor | 0.00031257 | 0.00031257 | 0.00031257 | 0.00031257 | 0.00031257
Beerwah Bulk | 477-1 | 477 Tee1 | Maleny | ECC Rating (A) | 155 | 155 | 155 | 155 | 155
Beerwah Bulk | 477-1 | 477 Tee1 | Maleny | 50 POE Load (A) | 1.5688 | 1.5693 | 1.5695 | 1.5697 | 1.5692
Beerwah Bulk | 477-2 | 477 Tee1 | Woodford | NCC Rating (A) | 330 | 330 | 330 | 330 | 330 | Rural | 170
Beerwah Bulk | 477-2 | 477 Tee1 | Woodford | 10 POE Load (A) | 208.2156 | 206.6767 | 206.0614 | 205.4597 | 206.9301
Beerwah Bulk | 477-2 | 477 Tee1 | Woodford | Power Factor | 0.9852 | 0.98533 | 0.98538 | 0.98543 | 0.98531
Beerwah Bulk | 477-2 | 477 Tee1 | Woodford | ECC Rating (A) | 300 | 300 | 300 | 300 | 300
Beerwah Bulk | 477-2 | 477 Tee1 | Woodford | 50 POE Load (A) | 190.7405 | 189.3528 | 188.7975 | 188.2546 | 189.5812
Beerwah Bulk | 477-3 | Beerwah | 477 Tee1 | NCC Rating (A) | 711 | 711 | 711 | 711 | 711 | Rural | 170
Beerwah Bulk | 477-3 | Beerwah | 477 Tee1 | 10 POE Load (A) | 207.7713 | 206.2344 | 205.6199 | 205.019 | 206.4874
Beerwah Bulk | 477-3 | Beerwah | 477 Tee1 | Power Factor | 0.97108 | 0.97142 | 0.97156 | 0.97169 | 0.97136
Beerwah Bulk | 477-3 | Beerwah | 477 Tee1 | ECC Rating (A) | 711 | 711 | 711 | 711 | 711
Beerwah Bulk | 477-3 | Beerwah | 477 Tee1 | 50 POE Load (A) | 190.3135 | 188.9275 | 188.3729 | 187.8308 | 189.1556
Beerwah Bulk | 608-1 | Beerwah BS | Landsborough | NCC Rating (A) | 412 | 412 | 412 | 412 | 412 | Rural | 170
Beerwah Bulk | 608-1 | Beerwah BS | Landsborough | 10 POE Load (A) | 266.5015 | 295.2512 | 306.1369 | 316.9026 | 329.2164
Beerwah Bulk | 608-1 | Beerwah BS | Landsborough | Power Factor | 0.97974 | 0.97749 | 0.97634 | 0.97517 | 0.9747
Beerwah Bulk | 608-1 | Beerwah BS | Landsborough | ECC Rating (A) | 412 | 412 | 412 | 412 | 412
Beerwah Bulk | 608-1 | Beerwah BS | Landsborough | 50 POE Load (A) | 518.615 | 548.5169 | 559.8346 | 569.8801 | 585.0266
Belmont Bulk | 527-1 | Mt Gravatt | Upper Mt Gravatt | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70
Belmont Bulk | 527-1 | Mt Gravatt | Upper Mt Gravatt | 10 POE Load (A) | 118.111 | 116.593 | 115.4864 | 113.7425 | 112.9923
Belmont Bulk | 527-1 | Mt Gravatt | Upper Mt Gravatt | Power Factor | 0.98478 | 0.98341 | 0.98225 | 0.98032 | 0.9795
Belmont Bulk | 527-1 | Mt Gravatt | Upper Mt Gravatt | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Belmont Bulk | 527-1 | Mt Gravatt | Upper Mt Gravatt | 50 POE Load (A) | 99.3809 | 98.1441 | 97.2676 | 95.85 | 95.2366
Belmont Bulk | 631-1 | Belmont BS | Mt Gravatt | NCC Rating (A) | 420 | 420 | 420 | 420 | 420 | Urban | 70
Belmont Bulk | 631-1 | Belmont BS | Mt Gravatt | 10 POE Load (A) | 280 | 281 | 281 | 281 | 281
Belmont Bulk | 631-1 | Belmont BS | Mt Gravatt | Power Factor | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
Belmont Bulk | 631-1 | Belmont BS | Mt Gravatt | ECC Rating (A) | 465 | 465 | 465 | 465 | 465
Belmont Bulk | 631-1 | Belmont BS | Mt Gravatt | 50 POE Load (A) | 443 | 444 | 444 | 444 | 444
Belmont Bulk | 632-1 | Belmont BS | Mt Gravatt | NCC Rating (A) | 420 | 420 | 420 | 420 | 420 | Urban | 70
Belmont Bulk | 632-1 | Belmont BS | Mt Gravatt | 10 POE Load (A) | 279 | 279 | 279 | 279 | 279
Belmont Bulk | 632-1 | Belmont BS | Mt Gravatt | Power Factor | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
Belmont Bulk | 632-1 | Belmont BS | Mt Gravatt | ECC Rating (A) | 452 | 452 | 452 | 452 | 452
Belmont Bulk | 632-1 | Belmont BS | Mt Gravatt | 50 POE Load (A) | 442 | 443 | 443 | 443 | 443
Belmont Bulk | 647-1 | Belmont BS | Eight Mile Plains Bus 2 | NCC Rating (A) | 479 | 479 | 479 | 479 | 479 | Urban | 90
Belmont Bulk | 647-1 | Belmont BS | Eight Mile Plains Bus 2 | 10 POE Load (A) | 252.9757 | 359.6965 | 360.0065 | 360.2965 | 363.4251
Belmont Bulk | 647-1 | Belmont BS | Eight Mile Plains Bus 2 | Power Factor | 0.98198 | 0.97216 | 0.97213 | 0.97211 | 0.97179
Belmont Bulk | 647-1 | Belmont BS | Eight Mile Plains Bus 2 | ECC Rating (A) | 479 | 479 | 479 | 479 | 479
Belmont Bulk | 647-1 | Belmont BS | Eight Mile Plains Bus 2 | 50 POE Load (A) | 461.5677 | 564.3381 | 564.8134 | 565.2837 | 570.0359
Belmont Bulk | 660-1 | Belmont BS | Scrub Road | NCC Rating (A) | 676 | 676 | 676 | 676 | 676 | Urban | 70
Belmont Bulk | 660-1 | Belmont BS | Scrub Road | 10 POE Load (A) | 271.2337 | 265.1323 | 261.2422 | 256.092 | 254.0513
Belmont Bulk | 660-1 | Belmont BS | Scrub Road | Power Factor | 0.96712 | 0.96766 | 0.968 | 0.96845 | 0.96824
Belmont Bulk | 660-1 | Belmont BS | Scrub Road | ECC Rating (A) | 751 | 751 | 751 | 751 | 751
Belmont Bulk | 660-1 | Belmont BS | Scrub Road | 50 POE Load (A) | 493 | 493 | 490 | 486 | 480
Belmont Bulk | 661-1 | Belmont BS | Scrub Road | NCC Rating (A) | 676 | 676 | 676 | 676 | 676 | Urban | 70
Belmont Bulk | 661-1 | Belmont BS | Scrub Road | 10 POE Load (A) | 274.1325 | 267.9659 | 264.0343 | 258.829 | 256.7664
Belmont Bulk | 661-1 | Belmont BS | Scrub Road | Power Factor | 0.96712 | 0.96766 | 0.968 | 0.96845 | 0.96824
Belmont Bulk | 661-1 | Belmont BS | Scrub Road | ECC Rating (A) | 751 | 751 | 751 | 751 | 751
Belmont Bulk | 661-1 | Belmont BS | Scrub Road | 50 POE Load (A) | 493 | 493 | 490 | 486 | 480
Belmont Bulk | 662-1 | Belmont BS | Upper Mt Gravatt | NCC Rating (A) | 656 | 656 | 656 | 656 | 656 | Urban | 70
Belmont Bulk | 662-1 | Belmont BS | Upper Mt Gravatt | 10 POE Load (A) | 243.2475 | 241.1992 | 240.1426 | 238.1115 | 238.0846
Belmont Bulk | 662-1 | Belmont BS | Upper Mt Gravatt | Power Factor | 0.97679 | 0.97728 | 0.97753 | 0.978 | 0.97772
Belmont Bulk | 662-1 | Belmont BS | Upper Mt Gravatt | ECC Rating (A) | 737 | 737 | 737 | 737 | 737
Belmont Bulk | 662-1 | Belmont BS | Upper Mt Gravatt | 50 POE Load (A) | 303 | 303 | 492 | 489 | 470
Belmont Bulk | 663-1 | Belmont BS | Upper Mt Gravatt | NCC Rating (A) | 656 | 656 | 656 | 656 | 656 | Urban | 70
Belmont Bulk | 663-1 | Belmont BS | Upper Mt Gravatt | 10 POE Load (A) | 246.123 | 244.0504 | 242.9812 | 240.9259 | 240.8987
Belmont Bulk | 663-1 | Belmont BS | Upper Mt Gravatt | Power Factor | 0.97666 | 0.97715 | 0.9774 | 0.97787 | 0.97759
Belmont Bulk | 663-1 | Belmont BS | Upper Mt Gravatt | ECC Rating (A) | 737 | 737 | 737 | 737 | 737
Belmont Bulk | 663-1 | Belmont BS | Upper Mt Gravatt | 50 POE Load (A) | 305 | 305 | 492 | 489 | 480
Belmont Bulk | 692-1 | Belmont BS | Holland Pk East | NCC Rating (A) | 421 | 421 | 421 | 421 | 421 | Urban | 70
Belmont Bulk | 692-1 | Belmont BS | Holland Pk East | 10 POE Load (A) | 184.9956 | 183.8691 | 183.7454 | 183.6268 | 184.7129
Belmont Bulk | 692-1 | Belmont BS | Holland Pk East | Power Factor | -0.96369 | -0.96382 | -0.96383 | -0.96385 | -0.96372
Belmont Bulk | 692-1 | Belmont BS | Holland Pk East | ECC Rating (A) | 465 | 465 | 465 | 465 | 465
Belmont Bulk | 692-1 | Belmont BS | Holland Pk East | 50 POE Load (A) | 170.7925 | 169.7557 | 169.6419 | 169.5327 | 170.5323
Belmont Bulk | 693-1 | Belmont BS | Holland Pk East | NCC Rating (A) | 421 | 421 | 421 | 421 | 421 | Urban | 70
Belmont Bulk | 693-1 | Belmont BS | Holland Pk East | 10 POE Load (A) | 186.5141 | 185.3781 | 185.2534 | 185.1338 | 186.2291
Belmont Bulk | 693-1 | Belmont BS | Holland Pk East | Power Factor | -0.96401 | -0.96414 | -0.96415 | -0.96417 | -0.96404
Belmont Bulk | 693-1 | Belmont BS | Holland Pk East | ECC Rating (A) | 465 | 465 | 465 | 465 | 465
Belmont Bulk | 693-1 | Belmont BS | Holland Pk East | 50 POE Load (A) | 172.1914 | 171.1459 | 171.0312 | 170.921 | 171.9291
Brendale Bulk | 303-1 | Brendale BS | Albany Ck | NCC Rating (A) | 725 | 725 | 725 | 725 | 725 | Urban | 70
Brendale Bulk | 303-1 | Brendale BS | Albany Ck | 10 POE Load (A) | 264.4099 | 262.1553 | 261.4168 | 260.1043 | 260.779
Brendale Bulk | 303-1 | Brendale BS | Albany Ck | Power Factor | 0.97875 | 0.97901 | 0.9791 | 0.97925 | 0.97917
Brendale Bulk | 303-1 | Brendale BS | Albany Ck | ECC Rating (A) | 824 | 824 | 824 | 824 | 824
Brendale Bulk | 303-1 | Brendale BS | Albany Ck | 50 POE Load (A) | 235.9352 | 233.9353 | 233.2802 | 232.1157 | 232.7144
Brendale Bulk | 309-1 | Brendale BS | 309 Tee1 | NCC Rating (A) | 627 | 627 | 627 | 627 | 627 | Rural | 170
Brendale Bulk | 309-1 | Brendale BS | 309 Tee1 | 10 POE Load (A) | 335.5081 | 332.8279 | 331.5974 | 330.4696 | 331.9421
Brendale Bulk | 309-1 | Brendale BS | 309 Tee1 | Power Factor | 0.96437 | 0.96464 | 0.96477 | 0.96488 | 0.96468
Brendale Bulk | 309-1 | Brendale BS | 309 Tee1 | ECC Rating (A) | 627 | 627 | 627 | 627 | 627
Brendale Bulk | 309-1 | Brendale BS | 309 Tee1 | 50 POE Load (A) | 285.1005 | 283.0333 | 282 | 281.0485 | 282.2608
Brendale Bulk | 309-2 | 309 Tee1 | Samford | NCC Rating (A) | 711 | 711 | 711 | 711 | 711 | Rural | 170
Brendale Bulk | 309-2 | 309 Tee1 | Samford | 10 POE Load (A) | 92.2836 | 90.3054 | 89.5471 | 88.6769 | 88.6045
Brendale Bulk | 309-2 | 309 Tee1 | Samford | Power Factor | -0.98429 | -0.98471 | -0.98485 | -0.98504 | -0.98519
Brendale Bulk | 309-2 | 309 Tee1 | Samford | ECC Rating (A) | 711 | 711 | 711 | 711 | 711
Brendale Bulk | 309-2 | 309 Tee1 | Samford | 50 POE Load (A) | 264 | 263 | 262 | 259 | 259
Brendale Bulk | 309-3 | 309 Tee1 | Arana Hills | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Rural | 170
Brendale Bulk | 309-3 | 309 Tee1 | Arana Hills | 10 POE Load (A) | 244.565 | 243.8156 | 243.3409 | 243.0854 | 244.6576
Brendale Bulk | 309-3 | 309 Tee1 | Arana Hills | Power Factor | 0.96406 | 0.9643 | 0.96442 | 0.96452 | 0.96426
Brendale Bulk | 309-3 | 309 Tee1 | Arana Hills | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
Brendale Bulk | 309-3 | 309 Tee1 | Arana Hills | 50 POE Load (A) | 609 | 608 | 606 | 602 | 600
Brendale Bulk | 310-1 | Brendale BS | 310 Tee1 | NCC Rating (A) | 627 | 627 | 627 | 627 | 627 | Urban | 70
Brendale Bulk | 310-1 | Brendale BS | 310 Tee1 | 10 POE Load (A) | 497.5765 | 494.2888 | 492.703 | 491.3509 | 493.8151
Brendale Bulk | 310-1 | Brendale BS | 310 Tee1 | Power Factor | 0.96668 | 0.96693 | 0.96705 | 0.96715 | 0.96694
Brendale Bulk | 310-1 | Brendale BS | 310 Tee1 | ECC Rating (A) | 627 | 627 | 627 | 627 | 627
Brendale Bulk | 310-1 | Brendale BS | 310 Tee1 | 50 POE Load (A) | 585 | 585 | 582 | 579 | 575
Brendale Bulk | 310-2 | 310 Tee1 | Arana Hills | NCC Rating (A) | 792 | 792 | 792 | 792 | 792 | Urban | 70
Brendale Bulk | 310-2 | 310 Tee1 | Arana Hills | 10 POE Load (A) | 497.6462 | 494.3584 | 492.7724 | 491.4202 | 493.8846
Brendale Bulk | 310-2 | 310 Tee1 | Arana Hills | Power Factor | 0.97096 | 0.97116 | 0.97126 | 0.97134 | 0.97117
Brendale Bulk | 310-2 | 310 Tee1 | Arana Hills | ECC Rating (A) | 792 | 792 | 792 | 792 | 792
Brendale Bulk | 310-2 | 310 Tee1 | Arana Hills | 50 POE Load (A) | 419.2561 | 416.9651 | 415.6529 | 414.5303 | 416.5484
Brendale Bulk | 310-3 | 310 Tee1 | 569 Tee1 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70
Brendale Bulk | 310-3 | 310 Tee1 | 569 Tee1 | 10 POE Load (A) | 0.10949 | 0.10953 | 0.10955 | 0.10957 | 0.10954
Brendale Bulk | 310-3 | 310 Tee1 | 569 Tee1 | Power Factor | 2.0842e-06 | 2.0842e-06 | 2.0841e-06 | 2.0842e-06 | 2.0842e-06
Brendale Bulk | 333-1 | Brendale BS | Lawnton | NCC Rating (A) | 732 | 732 | 732 | 732 | 732 | Urban | 70
Brendale Bulk | 333-1 | Brendale BS | Lawnton | 10 POE Load (A) | 372.3288 | 390.8065 | 391.4441 | 390.9445 | 393.4426
Brendale Bulk | 333-1 | Brendale BS | Lawnton | Power Factor | 0.98326 | 0.98114 | 0.98109 | 0.98116 | 0.9809
Brendale Bulk | 333-1 | Brendale BS | Lawnton | ECC Rating (A) | 732 | 732 | 732 | 732 | 732
Brendale Bulk | 333-1 | Brendale BS | Lawnton | 50 POE Load (A) | 546 | 549 | 550 | 551 | 550
Brendale Bulk | 3340-1 | Brendale Bs | Strathpine | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Urban | 70
Brendale Bulk | 3340-1 | Brendale Bs | Strathpine | 10 POE Load (A) | 147.4817 | 145.6484 | 143.3509 | 140.7753 | 138.9491
Brendale Bulk | 3340-1 | Brendale Bs | Strathpine | Power Factor | 0.98471 | 0.98543 | 0.98633 | 0.98691 | 0.98762
Brendale Bulk | 3340-1 | Brendale Bs | Strathpine | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
Brendale Bulk | 3340-1 | Brendale Bs | Strathpine | 50 POE Load (A) | 140.0794 | 138.345 | 136.1735 | 133.6778 | 131.955
Brendale Bulk | 334-1 | Lawnton | 334 Tee1 | NCC Rating (A) | 578 | 578 | 578 | 578 | 578 | Rural | 170
Brendale Bulk | 334-1 | Lawnton | 334 Tee1 | 10 POE Load (A) | 58.8495 | 68.196 | 69.4398 | 70.7534 | 72.2873
Brendale Bulk | 334-1 | Lawnton | 334 Tee1 | Power Factor | 0.99346 | 0.99911 | 0.99946 | 0.99972 | 0.99991
Brendale Bulk | 334-1 | Lawnton | 334 Tee1 | ECC Rating (A) | 578 | 578 | 578 | 578 | 578
Brendale Bulk | 334-1 | Lawnton | 334 Tee1 | 50 POE Load (A) | 214 | 214 | 213 | 212 | 210
Brendale Bulk | 334-2 | 334 Tee1 | Whiteside | NCC Rating (A) | 750 | 750 | 750 | 750 | 750 | Rural | 170
Brendale Bulk | 334-2 | 334 Tee1 | Whiteside | 10 POE Load (A) | 73.0254 | 70.7304 | 69.8444 | 68.5385 | 68.0083
Brendale Bulk | 334-2 | 334 Tee1 | Whiteside | Power Factor | 0.93401 | 0.93437 | 0.9346 | 0.93494 | 0.93507
Brendale Bulk | 334-2 | 334 Tee1 | Whiteside | ECC Rating (A) | 750 | 750 | 750 | 750 | 750
Brendale Bulk | 334-2 | 334 Tee1 | Whiteside | 50 POE Load (A) | 138 | 138 | 137 | 136 | 134
Brendale Bulk | 334-3 | 334 Tee1 | Nth Pine Dam | NCC Rating (A) | 578 | 578 | 578 | 578 | 578 | Rural | 170
Brendale Bulk | 334-3 | 334 Tee1 | Nth Pine Dam | 10 POE Load (A) | 127.7054 | 135.6382 | 136.1285 | 136.2819 | 137.4131
Brendale Bulk | 334-3 | 334 Tee1 | Nth Pine Dam | Power Factor | 0.99213 | 0.98952 | 0.98935 | 0.98928 | 0.98893
Brendale Bulk | 334-3 | 334 Tee1 | Nth Pine Dam | ECC Rating (A) | 578 | 578 | 578 | 578 | 578
Brendale Bulk | 334-3 | 334 Tee1 | Nth Pine Dam | 50 POE Load (A) | 174 | 175 | 176 | 177 | 177
Brendale Bulk | 335-1 | Brendale BS | 335 Tee1 | NCC Rating (A) | 485 | 485 | 485 | 485 | 485 | Rural | 170
Brendale Bulk | 335-1 | Brendale BS | 335 Tee1 | 10 POE Load (A) | 220.4781 | 227.5841 | 227.3041 | 226.2199 | 227.0391
Brendale Bulk | 335-1 | Brendale BS | 335 Tee1 | Power Factor | -0.96586 | -0.96448 | -0.96457 | -0.96486 | -0.96463
Brendale Bulk | 335-1 | Brendale BS | 335 Tee1 | ECC Rating (A) | 485 | 485 | 485 | 485 | 485
Brendale Bulk | 335-1 | Brendale BS | 335 Tee1 | 50 POE Load (A) | 302 | 304 | 304 | 304 | 304
Brendale Bulk | 335-2 | 335 Tee | Whiteside | NCC Rating (A) | 750 | 750 | 750 | 750 | 750 | Rural | 170
Brendale Bulk | 335-2 | 335 Tee | Whiteside | 10 POE Load (A) | 91.7508 | 90.8131 | 90.0303 | 88.7822 | 88.4523
Brendale Bulk | 335-2 | 335 Tee | Whiteside | Power Factor | 0.95041 | 0.95083 | 0.95109 | 0.9515 | 0.95161
Brendale Bulk | 335-2 | 335 Tee | Whiteside | ECC Rating (A) | 750 | 750 | 750 | 750 | 750
Brendale Bulk | 335-2 | 335 Tee | Whiteside | 50 POE Load (A) | 81.6878 | 80.9006 | 80.1964 | 79.0794 | 78.7738
Brendale Bulk | 335-3 | 335 Tee | Nth Pine Dam | NCC Rating (A) | 485 | 485 | 485 | 485 | 485 | Rural | 170
Brendale Bulk | 335-3 | 335 Tee | Nth Pine Dam | 10 POE Load (A) | 129.7226 | 137.6711 | 138.1566 | 138.3011 | 139.4324
Brendale Bulk | 335-3 | 335 Tee | Nth Pine Dam | Power Factor | -0.98558 | -0.98351 | -0.98334 | -0.98327 | -0.98288
Brendale Bulk | 335-3 | 335 Tee | Nth Pine Dam | ECC Rating (A) | 485 | 485 | 485 | 485 | 485
Brendale Bulk | 335-3 | 335 Tee | Nth Pine Dam | 50 POE Load (A) | 107.381 | 115.1333 | 115.5249 | 115.6381 | 116.5542
Brendale Bulk | 336-1 | Brendale BS | Strathpine | NCC Rating (A) | 455 | 455 | 455 | 455 | 455 | Urban | 70
Brendale Bulk | 336-1 | Brendale BS | Strathpine | 10 POE Load (A) | 168.5156 | 166.4196 | 163.793 | 160.8475 | 158.7597
Brendale Bulk | 336-1 | Brendale BS | Strathpine | Power Factor | 0.9959 | 0.99626 | 0.9967 | 0.99698 | 0.99731
Brendale Bulk | 336-1 | Brendale BS | Strathpine | ECC Rating (A) | 455 | 455 | 455 | 455 | 455
Brendale Bulk | 336-1 | Brendale BS | Strathpine | 50 POE Load (A) | 160.0519 | 158.069 | 155.5867 | 152.7337 | 150.7644
Brendale Bulk | 3364-1 | Brendale BS | Albany Ck | NCC Rating (A) | 725 | 725 | 725 | 725 | 725 | Urban | 70
Brendale Bulk | 3364-1 | Brendale BS | Albany Ck | 10 POE Load (A) | 271.0051 | 268.6942 | 267.9373 | 266.592 | 267.2835
Brendale Bulk | 3364-1 | Brendale BS | Albany Ck | Power Factor | 0.97842 | 0.97868 | 0.97877 | 0.97891 | 0.97884
Brendale Bulk | 3364-1 | Brendale BS | Albany Ck | ECC Rating (A) | 824 | 824 | 824 | 824 | 824
Brendale Bulk | 3364-1 | Brendale BS | Albany Ck | 50 POE Load (A) | 241.8198 | 239.77 | 239.0985 | 237.905 | 238.5185
Brendale Bulk | 337-1 | Brendale BS | Strathpine | NCC Rating (A) | 490 | 490 | 490 | 490 | 490 | Urban | 70
Brendale Bulk | 337-1 | Brendale BS | Strathpine | 10 POE Load (A) | 138.2792 | 136.5597 | 134.4048 | 131.9883 | 130.2755
Brendale Bulk | 337-1 | Brendale BS | Strathpine | Power Factor | 0.99082 | 0.99133 | 0.99196 | 0.99234 | 0.99283
Brendale Bulk | 337-1 | Brendale BS | Strathpine | ECC Rating (A) | 490 | 490 | 490 | 490 | 490
Brendale Bulk | 337-1 | Brendale BS | Strathpine | 50 POE Load (A) | 131.3356 | 129.7089 | 127.6724 | 125.3318 | 123.7162
Brendale Bulk | 342-1 | Brendale BS | Bald Hills Bus 2 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70
Brendale Bulk | 342-1 | Brendale BS | Bald Hills Bus 2 | 10 POE Load (A) | 69.6615 | 69.1664 | 69.0452 | 68.859 | 69.1687
Brendale Bulk | 342-1 | Brendale BS | Bald Hills Bus 2 | Power Factor | 0.99971 | 0.99973 | 0.99973 | 0.99974 | 0.99973
Brendale Bulk | 342-1 | Brendale BS | Bald Hills Bus 2 | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Brendale Bulk | 342-1 | Brendale BS | Bald Hills Bus 2 | 50 POE Load (A) | 64.4145 | 63.957 | 63.845 | 63.6731 | 63.9591
Brendale Bulk | 349-1 | Brendale BS | Lawnton | NCC Rating (A) | 717 | 717 | 717 | 717 | 717 | Urban | 70
Brendale Bulk | 349-1 | Brendale BS | Lawnton | 10 POE Load (A) | 399.8932 | 419.7385 | 420.4233 | 419.8867 | 422.5697
Brendale Bulk | 349-1 | Brendale BS | Lawnton | Power Factor | 0.98225 | 0.98001 | 0.97995 | 0.98002 | 0.97975
Brendale Bulk | 349-1 | Brendale BS | Lawnton | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
Brendale Bulk | 349-1 | Brendale BS | Lawnton | 50 POE Load (A) | 334.7685 | 354.251 | 354.7549 | 354.2387 | 356.3882
Brendale Bulk | 464-1 | Brendale BS | Samford | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
Brendale Bulk | 464-1 | Brendale BS | Samford | 10 POE Load (A) | 241.3287 | 238.8085 | 237.7193 | 236.6349 | 237.4564
Brendale Bulk | 464-1 | Brendale BS | Samford | Power Factor | 0.97196 | 0.97215 | 0.97224 | 0.97232 | 0.97221
Brendale Bulk | 464-1 | Brendale BS | Samford | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Brendale Bulk | 464-1 | Brendale BS | Samford | 50 POE Load (A) | 208.1442 | 206.0078 | 205.0765 | 204.1459 | 204.8311
Browns Plains Bulk | 406A-1 | Bethania | Kingston | NCC Rating (A) | 529 | 529 | 529 | 529 | 529 | Urban | 70
Browns Plains Bulk | 406A-1 | Bethania | Kingston | 10 POE Load (A) | 1.0615 | 1.0616 | 1.0616 | 1.0616 | 1.0615
Browns Plains Bulk | 406A-1 | Bethania | Kingston | Power Factor | 5.1152e-05 | 5.1165e-05 | 5.1148e-05 | 5.1142e-05 | 5.1149e-05
Browns Plains Bulk | 406A-1 | Bethania | Kingston | ECC Rating (A) | 529 | 529 | 529 | 529 | 529
Browns Plains Bulk | 406A-1 | Bethania | Kingston | 50 POE Load (A) | 367.6085 | 368.588 | 371.4871 | 374.3484 | 380.033
Browns Plains Bulk | 406B-1 | Crestmead | Kingston | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
Browns Plains Bulk | 406B-1 | Crestmead | Kingston | 10 POE Load (A) | 1.6924 | 1.6925 | 1.6924 | 1.6924 | 1.6924
Browns Plains Bulk | 406B-1 | Crestmead | Kingston | Power Factor | 5.9382e-06 | 5.9385e-06 | 5.9381e-06 | 5.9382e-06 | 5.9384e-06
Browns Plains Bulk | 406B-1 | Crestmead | Kingston | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Browns Plains Bulk | 406B-1 | Crestmead | Kingston | 50 POE Load (A) | 368.2396 | 369.2192 | 372.1183 | 374.9796 | 380.6641
Browns Plains Bulk | 478-1 | Browns Plains BS | Nth Maclean | NCC Rating (A) | 813 | 813 | 813 | 813 | 813 | Rural | 170
Browns Plains Bulk | 478-1 | Browns Plains BS | Nth Maclean | 10 POE Load (A) | 2.172 | 2.172 | 2.172 | 2.172 | 2.172
Browns Plains Bulk | 478-1 | Browns Plains BS | Nth Maclean | Power Factor | 5.063e-05 | 5.063e-05 | 5.063e-05 | 5.063e-05 | 5.063e-05
Browns Plains Bulk | 478-1 | Browns Plains BS | Nth Maclean | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Browns Plains Bulk | 478-1 | Browns Plains BS | Nth Maclean | 50 POE Load (A) | 597.8536 | 596.8613 | 613.5533 | 631.3352 | 653.5853
Browns Plains Bulk | 481-1 | Browns Plains BS | Cresmead | NCC Rating (A) | 705 | 705 | 705 | 705 | 705 | Urban | 70
Browns Plains Bulk | 481-1 | Browns Plains BS | Cresmead | 10 POE Load (A) | 278.7333 | 276.9125 | 277.3933 | 277.6402 | 280
Browns Plains Bulk | 481-1 | Browns Plains BS | Cresmead | Power Factor | 0.97882 | 0.97905 | 0.97899 | 0.97896 | 0.97867
Browns Plains Bulk | 481-1 | Browns Plains BS | Cresmead | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Browns Plains Bulk | 481-1 | Browns Plains BS | Cresmead | 50 POE Load (A) | 535 | 535 | 534 | 531 | 531
Browns Plains Bulk | 482-1 | Browns Plains BS | Cresmead | NCC Rating (A) | 704 | 704 | 704 | 704 | 704 | Urban | 70
Browns Plains Bulk | 482-1 | Browns Plains BS | Cresmead | 10 POE Load (A) | 280.2856 | 278.4545 | 278.938 | 279.1864 | 281.5594
Browns Plains Bulk | 482-1 | Browns Plains BS | Cresmead | Power Factor | 0.97858 | 0.97881 | 0.97875 | 0.97872 | 0.97843
Browns Plains Bulk | 482-1 | Browns Plains BS | Cresmead | ECC Rating (A) | 704 | 704 | 704 | 704 | 704
Browns Plains Bulk | 482-1 | Browns Plains BS | Cresmead | 50 POE Load (A) | 254.474 | 252.8196 | 253.2565 | 253.4809 | 255.6247
Browns Plains Bulk | 542-1 | Browns Plains BS | Heathwood | NCC Rating (A) | 704 | 704 | 704 | 704 | 704 | Urban | 70
Browns Plains Bulk | 542-1 | Browns Plains BS | Heathwood | 10 POE Load (A) | 603.0419 | 602.7182 | 602.3447 | 600.9629 | 604.1656
Browns Plains Bulk | 542-1 | Browns Plains BS | Heathwood | Power Factor | 0.96983 | 0.96984 | 0.96987 | 0.96994 | 0.96976
Browns Plains Bulk | 542-1 | Browns Plains BS | Heathwood | ECC Rating (A) | 704 | 704 | 704 | 704 | 704
Browns Plains Bulk | 542-1 | Browns Plains BS | Heathwood | 50 POE Load (A) | 570.1694 | 569.8655 | 569.5146 | 568.2171 | 571.2248
Burleigh Heads Bulk | 3751-1 | Burleigh Hds BS | Currumbin | NCC Rating (A) | 606 | 606 | 606 | 606 | 606 | Urban | 321
Burleigh Heads Bulk | 3751-1 | Burleigh Hds BS | Currumbin | 10 POE Load (A) | 617.5974 | 619.2061 | 621.6206 | 623.8018 | 629.2162
Burleigh Heads Bulk | 3751-1 | Burleigh Hds BS | Currumbin | Power Factor | 0.95589 | 0.9558 | 0.95613 | 0.95606 | 0.95589
Burleigh Heads Bulk | 3751-1 | Burleigh Hds BS | Currumbin | ECC Rating (A) | 695 | 695 | 695 | 695 | 695
Burleigh Heads Bulk | 3751-1 | Burleigh Hds BS | Currumbin | 50 POE Load (A) | 937 | 942 | 946 | 946 | 946
Burleigh Heads Bulk | 3755-1 | Burleigh Hds BS | Currumbin | NCC Rating (A) | 606 | 606 | 606 | 606 | 606 | Urban | 321
Burleigh Heads Bulk | 3755-1 | Burleigh Hds BS | Currumbin | 10 POE Load (A) | 617.2678 | 618.8756 | 621.2888 | 623.4688 | 628.8803
Burleigh Heads Bulk | 3755-1 | Burleigh Hds BS | Currumbin | Power Factor | 0.95589 | 0.95579 | 0.95612 | 0.95606 | 0.95588
Burleigh Heads Bulk | 3755-1 | Burleigh Hds BS | Currumbin | ECC Rating (A) | 695 | 695 | 695 | 695 | 695
Burleigh Heads Bulk | 3755-1 | Burleigh Hds BS | Currumbin | 50 POE Load (A) | 937 | 942 | 946 | 946 | 946
Burleigh Heads Bulk | 3756-1 | Burleigh Hds BS | 3756 Tee1 | NCC Rating (A) | 715 | 715 | 715 | 715 | 715 | Urban | 70
Burleigh Heads Bulk | 3756-1 | Burleigh Hds BS | 3756 Tee1 | 10 POE Load (A) | 192.0051 | 192.4059 | 193.1489 | 193.8684 | 195.683
Burleigh Heads Bulk | 3756-1 | Burleigh Hds BS | 3756 Tee1 | Power Factor | 0.97208 | 0.97202 | 0.97253 | 0.97247 | 0.9723
Burleigh Heads Bulk | 3756-1 | Burleigh Hds BS | 3756 Tee1 | ECC Rating (A) | 715 | 715 | 715 | 715 | 715
Burleigh Heads Bulk | 3756-1 | Burleigh Hds BS | 3756 Tee1 | 50 POE Load (A) | 182.5162 | 182.8848 | 183.5771 | 184.2483 | 185.9396
Burleigh Heads Bulk | 3756-2 | 3756 Tee1 | Palm Beach | NCC Rating (A) | 532 | 532 | 532 | 532 | 532 | Urban | 70
Burleigh Heads Bulk | 3756-2 | 3756 Tee1 | Palm Beach | 10 POE Load (A) | 156.5364 | 155.9221 | 156.4399 | 157.3994 | 160.0737
Burleigh Heads Bulk | 3756-2 | 3756 Tee1 | Palm Beach | Power Factor | 0.97421 | 0.97431 | 0.97739 | 0.97729 | 0.97701
Burleigh Heads Bulk | 3756-2 | 3756 Tee1 | Palm Beach | ECC Rating (A) | 532 | 532 | 532 | 532 | 532
Burleigh Heads Bulk | 3756-2 | 3756 Tee1 | Palm Beach | 50 POE Load (A) | 348 | 350 | 350 | 350 | 350
Burleigh Heads Bulk | 3756-3 | 3756 Tee1 | 3756 Tee2 | NCC Rating (A) | 636 | 636 | 636 | 636 | 636 | Urban | 70
Burleigh Heads Bulk | 3756-3 | 3756 Tee1 | 3756 Tee2 | 10 POE Load (A) | 35.6314 | 36.6543 | 36.8839 | 36.6457 | 35.7905
Burleigh Heads Bulk | 3756-3 | 3756 Tee1 | 3756 Tee2 | Power Factor | -0.94562 | -0.94532 | -0.94374 | -0.94348 | -0.94265
Burleigh Heads Bulk | 3756-3 | 3756 Tee1 | 3756 Tee2 | ECC Rating (A) | 636 | 636 | 636 | 636 | 636
Burleigh Heads Bulk | 3756-3 | 3756 Tee1 | 3756 Tee2 | 50 POE Load (A) | 241 | 243 | 244 | 244 | 244
Burleigh Heads Bulk | 3756-4 | 3756 Tee2 | Currumbin | NCC Rating (A) | 717 | 717 | 717 | 717 | 717 | Urban | 70
Burleigh Heads Bulk | 3756-4 | 3756 Tee2 | Currumbin | 10 POE Load (A) | 35.7417 | 36.7648 | 36.9947 | 36.7569 | 35.9028
Burleigh Heads Bulk | 3756-4 | 3756 Tee2 | Currumbin | Power Factor | -0.94271 | -0.94249 | -0.94057 | -0.94027 | -0.93933
Burleigh Heads Bulk | 3756-4 | 3756 Tee2 | Currumbin | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
Burleigh Heads Bulk | 3756-4 | 3756 Tee2 | Currumbin | 50 POE Load (A) | 39.9262 | 40.8694 | 41.0848 | 40.8664 | 40.0749
Burleigh Heads Bulk | 393-1 | Currumbin | Kirra | NCC Rating (A) | 403 | 403 | 403 | 403 | 403 | Urban | 70
Burleigh Heads Bulk | 393-1 | Currumbin | Kirra | 10 POE Load (A) | 335.4753 | 338.4498 | 340.7423 | 342.4178 | 346.7427
Burleigh Heads Bulk | 393-1 | Currumbin | Kirra | Power Factor | 0.9575 | 0.95728 | 0.95711 | 0.95698 | 0.95666
Burleigh Heads Bulk | 393-1 | Currumbin | Kirra | ECC Rating (A) | 403 | 403 | 403 | 403 | 403
Burleigh Heads Bulk | 393-1 | Currumbin | Kirra | 50 POE Load (A) | 306.5174 | 309.2148 | 311.2925 | 312.8107 | 316.7283
Burleigh Heads Bulk | 395-1 | Burleigh Hds BS | Miami | NCC Rating (A) | 654 | 654 | 654 | 654 | 654 | Urban | 70
Burleigh Heads Bulk | 395-1 | Burleigh Hds BS | Miami | 10 POE Load (A) | 471.7133 | 474.2453 | 479.1458 | 484.0201 | 492.4996
Burleigh Heads Bulk | 395-1 | Burleigh Hds BS | Miami | Power Factor | 0.976 | 0.9759 | 0.97573 | 0.97555 | 0.97523
Burleigh Heads Bulk | 396-1 | Burleigh Hds BS | Palm Beach | NCC Rating (A) | 806 | 806 | 806 | 806 | 806 | Urban | 70
Burleigh Heads Bulk | 396-1 | Burleigh Hds BS | Palm Beach | 10 POE Load (A) | 220.7666 | 221.2027 | 222.0548 | 222.892 | 225.0104
Burleigh Heads Bulk | 396-1 | Burleigh Hds BS | Palm Beach | Power Factor | 0.97052 | 0.97046 | 0.97105 | 0.97098 | 0.9708
Burleigh Heads Bulk | 396-1 | Burleigh Hds BS | Palm Beach | ECC Rating (A) | 806 | 806 | 806 | 806 | 806
Burleigh Heads Bulk | 396-1 | Burleigh Hds BS | Palm Beach | 50 POE Load (A) | 350 | 352 | 352 | 352 | 352
Burleigh Heads Bulk | 397-1 | Burleigh Hds BS | 397 Tee1 | NCC Rating (A) | 602 | 602 | 602 | 602 | 602 | Urban | 70
Burleigh Heads Bulk | 397-1 | Burleigh Hds BS | 397 Tee1 | 10 POE Load (A) | 2.5543 | 2.5543 | 2.5543 | 2.5543 | 2.5543
Burleigh Heads Bulk | 397-1 | Burleigh Hds BS | 397 Tee1 | Power Factor | 1.828e-05 | 1.828e-05 | 1.828e-05 | 1.828e-05 | 1.828e-05
Burleigh Heads Bulk | 397-3 | 397 Tee1 | 397 Tee2 | NCC Rating (A) | 529 | 529 | 529 | 529 | 529 | Urban | 70
Burleigh Heads Bulk | 397-3 | 397 Tee1 | 397 Tee2 | 10 POE Load (A) | 1.5716 | 1.5716 | 1.5716 | 1.5716 | 1.5716
Burleigh Heads Bulk | 397-3 | 397 Tee1 | 397 Tee2 | Power Factor | 3.1331e-05 | 3.1331e-05 | 3.1331e-05 | 3.1331e-05 | 3.1331e-05
Burleigh Heads Bulk | 397-4 | 397 Tee2 | 3700 Tee1 | NCC Rating (A) | 362 | 362 | 362 | 362 | 362 | Urban | 70
Burleigh Heads Bulk | 397-4 | 397 Tee2 | 3700 Tee1 | 10 POE Load (A) | 0.47718 | 0.47718 | 0.47718 | 0.47718 | 0.47718
Burleigh Heads Bulk | 397-4 | 397 Tee2 | 3700 Tee1 | Power Factor | 2.8117e-05 | 2.8117e-05 | 2.8117e-05 | 2.8112e-05 | 2.8117e-05
Burleigh Heads Bulk | 397-5 | 397 Tee2 | Mudgeeraba BS | NCC Rating (A) | 703 | 703 | 703 | 703 | 703 | Urban | 70
Burleigh Heads Bulk | 397-5 | 397 Tee2 | Mudgeeraba BS | 10 POE Load (A) | 0.31956 | 0.31956 | 0.31956 | 0.31956 | 0.31956
Burleigh Heads Bulk | 397-5 | 397 Tee2 | Mudgeeraba BS | Power Factor | 4.0403e-06 | 4.0403e-06 | 4.0403e-06 | 4.0388e-06 | 4.0403e-06
Caboolture Bulk | 321-1 | Caboolture BS | Caboolture West | NCC Rating (A) | 509 | 509 | 509 | 509 | 509 | Rural | 170
Caboolture Bulk | 321-1 | Caboolture BS | Caboolture West | 10 POE Load (A) | 302.2803 | 304.5319 | 307.5194 | 310.1076 | 314.8877
Caboolture Bulk | 321-1 | Caboolture BS | Caboolture West | Power Factor | 0.97412 | 0.97384 | 0.9734 | 0.97302 | 0.97244
Caboolture Bulk | 321-1 | Caboolture BS | Caboolture West | ECC Rating (A) | 509 | 509 | 509 | 509 | 509
Caboolture Bulk | 321-1 | Caboolture BS | Caboolture West | 50 POE Load (A) | 395 | 397 | 399 | 399 | 399
Caboolture Bulk | 322-1 | Caboolture BS | Caboolture West | NCC Rating (A) | 509 | 509 | 509 | 509 | 509 | Rural | 170
Caboolture Bulk | 322-1 | Caboolture BS | Caboolture West | 10 POE Load (A) | 317.8301 | 320.1973 | 323.3382 | 326.0594 | 331.0849
Caboolture Bulk | 322-1 | Caboolture BS | Caboolture West | Power Factor | 0.96574 | 0.96542 | 0.96491 | 0.96448 | 0.96382
Caboolture Bulk | 322-1 | Caboolture BS | Caboolture West | ECC Rating (A) | 509 | 509 | 509 | 509 | 509
Caboolture Bulk | 322-1 | Caboolture BS | Caboolture West | 50 POE Load (A) | 401 | 404 | 406 | 406 | 408
Caboolture Bulk | 323-1 | Caboolture West | 323 Tee1 | NCC Rating (A) | 510 | 510 | 510 | 510 | 510 | Rural | 170
Caboolture Bulk | 323-1 | Caboolture West | 323 Tee1 | 10 POE Load (A) | 82.3633 | 81.7872 | 81.7639 | 81.7869 | 82.4088
Caboolture Bulk | 323-1 | Caboolture West | 323 Tee1 | Power Factor | 0.98843 | 0.9885 | 0.98851 | 0.9885 | 0.98842
Caboolture Bulk | 323-1 | Caboolture West | 323 Tee1 | ECC Rating (A) | 510 | 510 | 510 | 510 | 510
Caboolture Bulk | 323-1 | Caboolture West | 323 Tee1 | 50 POE Load (A) | 246 | 246 | 246 | 245 | 250
Caboolture Bulk | 323-2 | 323 Tee1 | Wamuran | NCC Rating (A) | 457 | 457 | 457 | 457 | 457 | Rural | 170
Caboolture Bulk | 323-2 | 323 Tee1 | Wamuran | 10 POE Load (A) | 82.5663 | 81.9896 | 81.9663 | 81.9893 | 82.6117
Caboolture Bulk | 323-2 | 323 Tee1 | Wamuran | Power Factor | 0.98627 | 0.98633 | 0.98633 | 0.98633 | 0.98626
Caboolture Bulk | 323-2 | 323 Tee1 | Wamuran | ECC Rating (A) | 457 | 457 | 457 | 457 | 457
Caboolture Bulk | 323-2 | 323 Tee1 | Wamuran | 50 POE Load (A) | 75.9012 | 75.3843 | 75.3615 | 75.3796 | 75.9354
Caboolture Bulk | 323-3 | 323 Tee1 | Woodford | NCC Rating (A) | 271 | 271 | 271 | 271 | 271 | Rural | 170
Caboolture Bulk | 323-3 | 323 Tee1 | Woodford | 10 POE Load (A) | 1.1458 | 1.1457 | 1.1455 | 1.1453 | 1.1449
Caboolture Bulk | 323-3 | 323 Tee1 | Woodford | Power Factor | 0.00012203 | 0.00012193 | 0.00012195 | 0.00012197 | 0.00012197
Caboolture Bulk | 323-3 | 323 Tee1 | Woodford | ECC Rating (A) | 271 | 271 | 271 | 271 | 271
Caboolture Bulk | 323-3 | 323 Tee1 | Woodford | 50 POE Load (A) | 177 | 177 | 177 | 176 | 176
Caboolture Bulk | 350-1 | Caboolture BS | Ningi | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Caboolture Bulk | 350-1 | Caboolture BS | Ningi | 10 POE Load (A) | 410.0577 | 409.2989 | 410.4024 | 411.7536 | 415.9328
Caboolture Bulk | 350-1 | Caboolture BS | Ningi | Power Factor | 0.98029 | 0.98035 | 0.98031 | 0.98024 | 0.9801
Caboolture Bulk | 350-1 | Caboolture BS | Ningi | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Caboolture Bulk | 350-1 | Caboolture BS | Ningi | 50 POE Load (A) | 758 | 762 | 762 | 763 | 780
Caboolture Bulk | 412-1 | Caboolture BS | Toorbul Pt | NCC Rating (A) | 823 | 823 | 823 | 823 | 823 | Rural | 170
Caboolture Bulk | 412-1 | Caboolture BS | Toorbul Pt | 10 POE Load (A) | 345.5448 | 344.8338 | 345.7444 | 346.929 | 350.5789
Caboolture Bulk | 412-1 | Caboolture BS | Toorbul Pt | Power Factor | 0.96429 | 0.96439 | 0.96432 | 0.9642 | 0.9638
Caboolture Bulk | 412-1 | Caboolture BS | Toorbul Pt | ECC Rating (A) | 823 | 823 | 823 | 823 | 823
Caboolture Bulk | 412-1 | Caboolture BS | Toorbul Pt | 50 POE Load (A) | 806 | 813 | 813 | 815 | 820
Caboolture Bulk | 417-1 | Ningi | Toorbul Pt | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Caboolture Bulk | 417-1 | Ningi | Toorbul Pt | 10 POE Load (A) | 241.7455 | 241.1222 | 241.7252 | 242.6352 | 245.4131
Caboolture Bulk | 417-1 | Ningi | Toorbul Pt | Power Factor | 0.98929 | 0.98936 | 0.98934 | 0.98929 | 0.98909
Caboolture Bulk | 417-1 | Ningi | Toorbul Pt | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Caboolture Bulk | 417-1 | Ningi | Toorbul Pt | 50 POE Load (A) | 595 | 598 | 598 | 599 | 610
Caboolture Bulk | 431-1 | Toorbul Point | Bribie Is | NCC Rating (A) | 396 | 396 | 396 | 396 | 396 | Urban | 70
Caboolture Bulk | 431-1 | Toorbul Point | Bribie Is | 10 POE Load (A) | 230.0906 | 229.4066 | 229.819 | 230.5187 | 232.9867
Caboolture Bulk | 431-1 | Toorbul Point | Bribie Is | Power Factor | 0.97911 | 0.97919 | 0.97914 | 0.97906 | 0.97879
Caboolture Bulk | 431-1 | Toorbul Point | Bribie Is | ECC Rating (A) | 443 | 443 | 443 | 443 | 443
Caboolture Bulk | 431-1 | Toorbul Point | Bribie Is | 50 POE Load (A) | 398 | 400 | 400 | 400 | 410
Caboolture Bulk | 448-1 | Morayfield Nth | 448 Tee1 | NCC Rating (A) | 776 | 776 | 776 | 776 | 776 | Rural | 170
Caboolture Bulk | 448-1 | Morayfield Nth | 448 Tee1 | 10 POE Load (A) | 661.0803 | 676.1535 | 687.6162 | 698.6186 | 713.2877
Caboolture Bulk | 448-1 | Morayfield Nth | 448 Tee1 | Power Factor | -0.94861 | -0.94813 | -0.94706 | -0.94545 | -0.94465
Caboolture Bulk | 448-1 | Morayfield Nth | 448 Tee1 | ECC Rating (A) | 776 | 776 | 776 | 776 | 776
Caboolture Bulk | 448-1 | Morayfield Nth | 448 Tee1 | 50 POE Load (A) | 597.1753 | 612.0552 | 622.2191 | 631.4468 | 644.957
Caboolture Bulk | 448-2 | 448 Tee1 | Morayfield | NCC Rating (A) | 698 | 698 | 698 | 698 | 698 | Rural | 170
Caboolture Bulk | 448-2 | 448 Tee1 | Morayfield | 10 POE Load (A) | 654.9394 | 672.6723 | 685.3944 | 697.5185 | 713.1026
Caboolture Bulk | 448-2 | 448 Tee1 | Morayfield | Power Factor | 0.9881 | 0.98744 | 0.98656 | 0.98577 | 0.98461
Caboolture Bulk | 448-2 | 448 Tee1 | Morayfield | ECC Rating (A) | 698 | 698 | 698 | 698 | 698
Caboolture Bulk | 448-2 | 448 Tee1 | Morayfield | 50 POE Load (A) | 591.7112 | 609.4717 | 617.7322 | 627.7982 | 642.1859
Caboolture Bulk | 448-3 | 448 Tee1 | Caboolture West | NCC Rating (A) | 485 | 485 | 485 | 485 | 485 | Rural | 170
Caboolture Bulk | 448-3 | 448 Tee1 | Caboolture West | 10 POE Load (A) | 10.7253 | 10.4439 | 10.2736 | 10.2189 | 10.3756
Caboolture Bulk | 448-3 | 448 Tee1 | Caboolture West | Power Factor | 0.93705 | 0.80949 | 0.67847 | 0.60562 | 0.68576
Caboolture Bulk | 448-3 | 448 Tee1 | Caboolture West | ECC Rating (A) | 485 | 485 | 485 | 485 | 485
Caboolture Bulk | 448-3 | 448 Tee1 | Caboolture West | 50 POE Load (A) | 137 | 137 | 137 | 136 | 140
Caboolture Bulk | 457-1 | Toorbul Pt | Bribie Island | NCC Rating (A) | 402 | 402 | 402 | 402 | 402 | Urban | 70
Caboolture Bulk | 457-1 | Toorbul Pt | Bribie Island | 10 POE Load (A) | 228.5746 | 227.8947 | 228.3046 | 229.0002 | 231.4537
Caboolture Bulk | 457-1 | Toorbul Pt | Bribie Island | Power Factor | 0.9818 | 0.98187 | 0.98182 | 0.98175 | 0.98149
Caboolture Bulk | 457-1 | Toorbul Pt | Bribie Island | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
Caboolture Bulk | 457-1 | Toorbul Pt | Bribie Island | 50 POE Load (A) | 207.1535 | 206.5464 | 206.91 | 207.5289 | 209.7215
Caboolture Bulk | 461-1 | Caboolture BS | Morayfield Nth | NCC Rating (A) | 676 | 676 | 676 | 676 | 676 | Urban | 238
Caboolture Bulk | 461-1 | Caboolture BS | Morayfield Nth | 10 POE Load (A) | 614.8544 | 622.8293 | 630.5227 | 636.8861 | 647.7395
Caboolture Bulk | 461-1 | Caboolture BS | Morayfield Nth | Power Factor | -0.95451 | -0.95417 | -0.95346 | -0.95253 | -0.95186
Caboolture Bulk | 461-1 | Caboolture BS | Morayfield Nth | ECC Rating (A) | 758 | 758 | 758 | 758 | 758
Caboolture Bulk | 461-1 | Caboolture BS | Morayfield Nth | 50 POE Load (A) | 884 | 894 | 901 | 905 | 920
Caboolture Bulk | 499-1 | Caboolture BS | Morayfield Nth | NCC Rating (A) | 676 | 676 | 676 | 676 | 676 | Urban | 239
Caboolture Bulk | 499-1 | Caboolture BS | Morayfield Nth | 10 POE Load (A) | 619.2702 | 627.3026 | 635.0513 | 641.4605 | 652.392
Caboolture Bulk | 499-1 | Caboolture BS | Morayfield Nth | Power Factor | -0.95454 | -0.9542 | -0.95349 | -0.95256 | -0.95189
Caboolture Bulk | 499-1 | Caboolture BS | Morayfield Nth | ECC Rating (A) | 758 | 758 | 758 | 758 | 758
Caboolture Bulk | 499-1 | Caboolture BS | Morayfield Nth | 50 POE Load (A) | 886 | 895 | 902 | 906 | 915
Cleveland Bulk | 3550-1 | Cleveland BS | Victoria Pt | NCC Rating (A) | 746 | 746 | 746 | 746 | 746 | Urban | 70
Cleveland Bulk | 3550-1 | Cleveland BS | Victoria Pt | 10 POE Load (A) | 523.4985 | 522.3442 | 524.1647 | 524.6605 | 529.3592
Cleveland Bulk | 3550-1 | Cleveland BS | Victoria Pt | Power Factor | 0.97766 | 0.97768 | 0.97771 | 0.97766 | 0.97739
Cleveland Bulk | 3550-1 | Cleveland BS | Victoria Pt | ECC Rating (A) | 746 | 746 | 746 | 746 | 746
Cleveland Bulk | 3550-1 | Cleveland BS | Victoria Pt | 50 POE Load (A) | 660 | 665 | 666 | 668 | 690
Cleveland Bulk | 3570-1 | Capalaba South | Capalaba | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70
Cleveland Bulk | 3570-1 | Capalaba South | Capalaba | 10 POE Load (A) | 108.6518 | 108.8101 | 107.9624 | 106.2756 | 105.9364
Cleveland Bulk | 3570-1 | Capalaba South | Capalaba | Power Factor | 1 | 1 | 1 | 0.99995 | 0.92775
Cleveland Bulk | 3570-1 | Capalaba South | Capalaba | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Cleveland Bulk | 3570-1 | Capalaba South | Capalaba | 50 POE Load (A) | 323 | 323 | 322 | 320 | 315
Cleveland Bulk | 3580-1 | Redland Bay | 3580 Tee1 | NCC Rating (A) | 717 | 717 | 717 | 717 | 717 | Urban | 70
Cleveland Bulk | 3580-1 | Redland Bay | 3580 Tee1 | 10 POE Load (A) | 62.7062 | 64.4795 | 66.1158 | 67.3438 | 69.2625
Cleveland Bulk | 3580-1 | Redland Bay | 3580 Tee1 | Power Factor | 0.99363 | 0.99315 | 0.99231 | 0.99201 | 0.99153
Cleveland Bulk | 3580-1 | Redland Bay | 3580 Tee1 | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
Cleveland Bulk | 3580-1 | Redland Bay | 3580 Tee1 | 50 POE Load (A) | 55.6057 | 57.2773 | 58.8365 | 59.9797 | 61.7431
Cleveland Bulk | 3580-2 | 3580 Tee1 | Mt Cotton | NCC Rating (A) | 527 | 527 | 527 | 527 | 527 | Urban | 70
Cleveland Bulk | 3580-2 | 3580 Tee1 | Mt Cotton | 10 POE Load (A) | 62.5219 | 64.2944 | 65.9325 | 67.1595 | 69.0758
Cleveland Bulk | 3580-2 | 3580 Tee1 | Mt Cotton | Power Factor | 0.99539 | 0.9949 | 0.99411 | 0.9938 | 0.99332
Cleveland Bulk | 3580-2 | 3580 Tee1 | Mt Cotton | ECC Rating (A) | 527 | 527 | 527 | 527 | 527
Cleveland Bulk | 3580-2 | 3580 Tee1 | Mt Cotton | 50 POE Load (A) | 336 | 340 | 342 | 345 | 350
Cleveland Bulk | 3580-3 | 3580 Tee1 | Cornubia | NCC Rating (A) | 717 | 717 | 717 | 717 | 717 | Urban | 70
Cleveland Bulk | 3580-3 | 3580 Tee1 | Cornubia | 10 POE Load (A) | 0.64625 | 0.64635 | 0.64635 | 0.64635 | 0.64626
Cleveland Bulk | 3580-3 | 3580 Tee1 | Cornubia | Power Factor | 1.4334e-05 | 1.4334e-05 | 1.4334e-05 | 1.4334e-05 | 1.4334e-05
Cleveland Bulk | 371-1 | Cleveland BS | Birkdale | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Cleveland Bulk | 371-1 | Cleveland BS | Birkdale | 10 POE Load (A) | 488.5058 | 483.6687 | 481.936 | 479.1234 | 481.1202
Cleveland Bulk | 371-1 | Cleveland BS | Birkdale | Power Factor | 0.9772 | 0.97754 | 0.97762 | 0.97789 | 0.96534
Cleveland Bulk | 371-1 | Cleveland BS | Birkdale | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Cleveland Bulk | 371-1 | Cleveland BS | Birkdale | 50 POE Load (A) | 448.8379 | 444.4276 | 442.8606 | 440.3569 | 442.1479
Cleveland Bulk | 372-1 | Cleveland BS | Raby Bay | NCC Rating (A) | 611 | 611 | 611 | 611 | 611 | Urban | 308
Cleveland Bulk | 372-1 | Cleveland BS | Raby Bay | 10 POE Load (A) | 439.0346 | 438.1789 | 439.5935 | 440.1788 | 444.8951
Cleveland Bulk | 372-1 | Cleveland BS | Raby Bay | Power Factor | 0.97123 | 0.97133 | 0.97118 | 0.97149 | 0.96837
Cleveland Bulk | 372-1 | Cleveland BS | Raby Bay | ECC Rating (A) | 686 | 686 | 686 | 686 | 686
Cleveland Bulk | 372-1 | Cleveland BS | Raby Bay | 50 POE Load (A) | 759 | 764 | 765 | 767 | 770
Cleveland Bulk | 373-1 | Raby Bay | Capalaba | NCC Rating (A) | 715 | 715 | 715 | 715 | 715 | Urban | 70
Cleveland Bulk | 373-1 | Raby Bay | Capalaba | 10 POE Load (A) | 367.7001 | 363.6478 | 361.9509 | 359.4434 | 360.2929
Cleveland Bulk | 373-1 | Raby Bay | Capalaba | Power Factor | -0.9555 | -0.95592 | -0.95611 | -0.9564 | -0.95582
Cleveland Bulk | 373-1 | Raby Bay | Capalaba | ECC Rating (A) | 715 | 715 | 715 | 715 | 715
Cleveland Bulk | 373-1 | Raby Bay | Capalaba | 50 POE Load (A) | 568 | 568 | 565 | 562 | 560
Cleveland Bulk | 374-1 | Cleveland BS | Capalaba South | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Cleveland Bulk | 374-1 | Cleveland BS | Capalaba South | 10 POE Load (A) | 425.7986 | 421.4434 | 420.0012 | 417.7312 | 419.3105
Cleveland Bulk | 374-1 | Cleveland BS | Capalaba South | Power Factor | 0.97683 | 0.97721 | 0.97728 | 0.97763 | 0.95838
Cleveland Bulk | 374-1 | Cleveland BS | Capalaba South | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Cleveland Bulk | 374-1 | Cleveland BS | Capalaba South | 50 POE Load (A) | 609 | 609 | 606 | 603 | 600
Cleveland Bulk | 375-1 | Cleveland BS | 375 Tee1 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
Cleveland Bulk | 375-1 | Cleveland BS | 375 Tee1 | 10 POE Load (A) | 194.9484 | 193.1135 | 193.0166 | 192.7051 | 193.7576
Cleveland Bulk | 375-1 | Cleveland BS | 375 Tee1 | Power Factor | 0.98901 | 0.98903 | 0.9891 | 0.98905 | 0.98888
Cleveland Bulk | 375-1 | Cleveland BS | 375 Tee1 | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Cleveland Bulk | 375-1 | Cleveland BS | 375 Tee1 | 50 POE Load (A) | 476 | 480 | 482 | 484 | 490
Cleveland Bulk | 375-2 | 375 Tee1 | Mt Cotton | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
Cleveland Bulk | 375-2 | 375 Tee1 | Mt Cotton | 10 POE Load (A) | 195.0211 | 193.186 | 193.0896 | 192.7782 | 193.8311
Cleveland Bulk | 375-2 | 375 Tee1 | Mt Cotton | Power Factor | 0.99222 | 0.99222 | 0.99228 | 0.99223 | 0.99211
Cleveland Bulk | 375-2 | 375 Tee1 | Mt Cotton | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Cleveland Bulk | 375-2 | 375 Tee1 | Mt Cotton | 50 POE Load (A) | 476 | 480 | 482 | 484 | 490
Cleveland Bulk | 375-3 | 375 Tee1 | 425 Tee1 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
Cleveland Bulk | 375-3 | 375 Tee1 | 425 Tee1 | 10 POE Load (A) | 0.00064745 | 0.00064748 | 0.00064748 | 0.00064748 | 0.00064745
Cleveland Bulk | 375-3 | 375 Tee1 | 425 Tee1 | Power Factor | 0.00030462 | 0.00030508 | 0.00030513 | 0.00030455 | 0.0003048
Cleveland Bulk | 413-1 | Cleveland BS | Raby Bay | NCC Rating (A) | 611 | 611 | 611 | 611 | 611 | Urban | 320
Cleveland Bulk | 413-1 | Cleveland BS | Raby Bay | 10 POE Load (A) | 444.3566 | 443.4905 | 444.9223 | 445.5147 | 450.2884
Cleveland Bulk | 413-1 | Cleveland BS | Raby Bay | Power Factor | 0.97119 | 0.97129 | 0.97114 | 0.97145 | 0.96833
Cleveland Bulk | 413-1 | Cleveland BS | Raby Bay | ECC Rating (A) | 611 | 611 | 611 | 611 | 611
Cleveland Bulk | 413-1 | Cleveland BS | Raby Bay | 50 POE Load (A) | 760 | 764 | 766 | 767 | 780
Cleveland Bulk | 425-1 | Cleveland BS | Victoria Pt | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70
Cleveland Bulk | 425-1 | Cleveland BS | Victoria Pt | 10 POE Load (A) | 231.5563 | 231.0452 | 231.8496 | 232.0682 | 234.1532
Cleveland Bulk | 425-1 | Cleveland BS | Victoria Pt | Power Factor | 0.99044 | 0.99045 | 0.99047 | 0.99043 | 0.99022
Cleveland Bulk | 425-1 | Cleveland BS | Victoria Pt | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Cleveland Bulk | 425-1 | Cleveland BS | Victoria Pt | 50 POE Load (A) | 592 | 597 | 598 | 599 | 610
Cleveland Bulk | 465-1 | Victoria Pt | Redland Bay | NCC Rating (A) | 508 | 508 | 508 | 508 | 508 | Urban | 70
Cleveland Bulk | 465-1 | Victoria Pt | Redland Bay | 10 POE Load (A) | 297.1146 | 296.613 | 298.3928 | 299.7377 | 303.356
Cleveland Bulk | 465-1 | Victoria Pt | Redland Bay | Power Factor | 0.98447 | 0.98448 | 0.98404 | 0.98395 | 0.98374
Cleveland Bulk | 465-1 | Victoria Pt | Redland Bay | ECC Rating (A) | 508 | 508 | 508 | 508 | 508
Cleveland Bulk | 465-1 | Victoria Pt | Redland Bay | 50 POE Load (A) | 458 | 462 | 464 | 465 | 470
Cleveland Bulk | 484-1 | Capalaba | Birkdale | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70
Cleveland Bulk | 484-1 | Capalaba | Birkdale | 10 POE Load (A) | 140.3779 | 138.9137 | 138.4198 | 137.5806 | 138.6053
Cleveland Bulk | 484-1 | Capalaba | Birkdale | Power Factor | 0.96756 | 0.9682 | 0.96837 | 0.96867 | 0.99954
Cleveland Bulk | 484-1 | Capalaba | Birkdale | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Cleveland Bulk | 484-1 | Capalaba | Birkdale | 50 POE Load (A) | 589 | 589 | 586 | 583 | 590
Coomera Bulk | 3640-1 | Coomera BS | Hope Is | NCC Rating (A) | 713 | 713 | 713 | 713 | 713 | Urban | 70
Coomera Bulk | 3640-1 | Coomera BS | Hope Is | 10 POE Load (A) | 384.0838 | 383.6702 | 384.2756 | 385.3287 | 389.0161
Coomera Bulk | 3640-1 | Coomera BS | Hope Is | Power Factor | 0.97702 | 0.97711 | 0.97692 | 0.9767 | 0.97651
Coomera Bulk | 3640-1 | Coomera BS | Hope Is | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
Coomera Bulk | 3640-1 | Coomera BS | Hope Is | 50 POE Load (A) | 626 | 635 | 647 | 643 | 650
Coomera Bulk | 3641-1 | Coomera BS | Pimpama East | NCC Rating (A) | 713 | 713 | 713 | 713 | 713 | Urban | 70
Coomera Bulk | 3641-1 | Coomera BS | Pimpama East | 10 POE Load (A) | 339.1479 | 353.6477 | 364.6181 | 375.5141 | 388.9159
Coomera Bulk | 3641-1 | Coomera BS | Pimpama East | Power Factor | 0.98004 | 0.97863 | 0.97754 | 0.97641 | 0.97604
Coomera Bulk | 3641-1 | Coomera BS | Pimpama East | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
Coomera Bulk | 3641-1 | Coomera BS | Pimpama East | 50 POE Load (A) | 595 | 622 | 652 | 666 | 670
Coomera Bulk | 3642-1 | Coomera BS | Pimpama East | NCC Rating (A) | 713 | 713 | 713 | 713 | 713 | Urban | 70
Coomera Bulk | 3642-1 | Coomera BS | Pimpama East | 10 POE Load (A) | 341.8218 | 356.4358 | 367.4926 | 378.4744 | 391.9817
Coomera Bulk | 3642-1 | Coomera BS | Pimpama East | Power Factor | 0.97997 | 0.97856 | 0.97746 | 0.97634 | 0.97596
Coomera Bulk | 3642-1 | Coomera BS | Pimpama East | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
Coomera Bulk | 3642-1 | Coomera BS | Pimpama East | 50 POE Load (A) | 595 | 622 | 653 | 665 | 674
Coomera Bulk | 394-1 | Coomera BS | Hope Is | NCC Rating (A) | 716 | 716 | 716 | 716 | 716 | Urban | 70
Coomera Bulk | 394-1 | Coomera BS | Hope Is | 10 POE Load (A) | 393.4658 | 393.042 | 393.6633 | 394.7424 | 398.5209
Coomera Bulk | 394-1 | Coomera BS | Hope Is | Power Factor | 0.98131 | 0.98139 | 0.98122 | 0.98102 | 0.98085
Coomera Bulk | 394-1 | Coomera BS | Hope Is | ECC Rating (A) | 716 | 716 | 716 | 716 | 716
Coomera Bulk | 394-1 | Coomera BS | Hope Is | 50 POE Load (A) | 636 | 649 | 645 | 650 | 655
Coorparoo Bulk | 3429-1 | Coorparoo BS | Holland Park | NCC Rating (A) | 735 | 735 | 735 | 735 | 735 | Urban | 70
Coorparoo Bulk | 3429-1 | Coorparoo BS | Holland Park | 10 POE Load (A) | 232.9247 | 233.0426 | 233.5597 | 233.7941 | 235.6162
Coorparoo Bulk | 3429-1 | Coorparoo BS | Holland Park | Power Factor | 0.97397 | 0.97396 | 0.9739 | 0.97388 | 0.97368
Coorparoo Bulk | 3429-1 | Coorparoo BS | Holland Park | ECC Rating (A) | 790 | 790 | 790 | 790 | 790
Coorparoo Bulk | 3429-1 | Coorparoo BS | Holland Park | 50 POE Load (A) | 392 | 394 | 395 | 394 | 400
Coorparoo Bulk | 3430-1 | Coorparoo BS | Holland Park | NCC Rating (A) | 735 | 735 | 735 | 735 | 735 | Urban | 70
Coorparoo Bulk | 3430-1 | Coorparoo BS | Holland Park | 10 POE Load (A) | 228.4619 | 228.5775 | 229.0848 | 229.3147 | 231.1018
Coorparoo Bulk | 3430-1 | Coorparoo BS | Holland Park | Power Factor | 0.97393 | 0.97392 | 0.97386 | 0.97384 | 0.97364
Coorparoo Bulk | 3430-1 | Coorparoo BS | Holland Park | ECC Rating (A) | 790 | 790 | 790 | 790 | 790
Coorparoo Bulk | 3430-1 | Coorparoo BS | Holland Park | 50 POE Load (A) | 393 | 395 | 395 | 395 | 420
Coorparoo Bulk | 584-4 | 584 Tee2 | Coorparoo BS | NCC Rating (A) | 721 | 721 | 721 | 721 | 721 | Urban | 70
Coorparoo Bulk | 584-4 | 584 Tee2 | Coorparoo BS | 10 POE Load (A) | 2.2136 | 2.2136 | 2.2136 | 2.2136 | 2.2136
Coorparoo Bulk | 584-4 | 584 Tee2 | Coorparoo BS | Power Factor | -6.6107e-07 | -6.6105e-07 | -6.6107e-07 | -6.6105e-07 | -6.6103e-07
Coorparoo Bulk | 612-1 | Coorparoo BS | Camp Hill | NCC Rating (A) | 766 | 766 | 766 | 766 | 766 | Urban | 70
Coorparoo Bulk | 612-1 | Coorparoo BS | Camp Hill | 10 POE Load (A) | 336.7204 | 334.2467 | 334.0422 | 333.6254 | 335.6524
Coorparoo Bulk | 612-1 | Coorparoo BS | Camp Hill | Power Factor | -0.97148 | -0.97174 | -0.97177 | -0.97181 | -0.97159
Coorparoo Bulk | 612-1 | Coorparoo BS | Camp Hill | ECC Rating (A) | 766 | 766 | 766 | 766 | 766
Coorparoo Bulk | 612-1 | Coorparoo BS | Camp Hill | 50 POE Load (A) | 563 | 564 | 563 | 561 | 575
Coorparoo Bulk | 613-1 | Coorparoo BS | Camp Hill | NCC Rating (A) | 766 | 766 | 766 | 766 | 766 | Urban | 70
Coorparoo Bulk | 613-1 | Coorparoo BS | Camp Hill | 10 POE Load (A) | 336.7204 | 334.2467 | 334.0422 | 333.6254 | 335.6523
Coorparoo Bulk | 613-1 | Coorparoo BS | Camp Hill | Power Factor | -0.97148 | -0.97174 | -0.97177 | -0.97181 | -0.97159
Coorparoo Bulk | 613-1 | Coorparoo BS | Camp Hill | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Coorparoo Bulk | 613-1 | Coorparoo BS | Camp Hill | 50 POE Load (A) | 563 | 564 | 563 | 561 | 570
Coorparoo Bulk | 648-1 | Scrub Rd | 648 Tee1 | NCC Rating (A) | 597 | 597 | 597 | 597 | 597 | Urban | 70
Coorparoo Bulk | 648-1 | Scrub Rd | 648 Tee1 | 10 POE Load (A) | 0.59953 | 0.59956 | 0.59956 | 0.59956 | 0.59954
Coorparoo Bulk | 648-1 | Scrub Rd | 648 Tee1 | Power Factor | 1.126e-05 | 1.126e-05 | 1.126e-05 | 1.126e-05 | 1.126e-05
Coorparoo Bulk | 648-2 | 648 Tee1 | 584 Tee1 | NCC Rating (A) | 348 | 348 | 348 | 348 | 348 | Urban | 70
Coorparoo Bulk | 648-2 | 648 Tee1 | 584 Tee1 | 10 POE Load (A) | 0.059542 | 0.059544 | 0.059544 | 0.059545 | 0.059542
Coorparoo Bulk | 648-2 | 648 Tee1 | 584 Tee1 | Power Factor | 1.5497e-05 | 1.55e-05 | 1.5497e-05 | 1.5498e-05 | 1.5495e-05
Coorparoo Bulk | 648-3 | 648 Tee1 | Camp Hill | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Coorparoo Bulk | 648-3 | 648 Tee1 | Camp Hill | 10 POE Load (A) | 0.88476 | 0.88479 | 0.8848 | 0.8848 | 0.88477
Coorparoo Bulk | 648-3 | 648 Tee1 | Camp Hill | Power Factor | 2.2116e-05 | 2.2116e-05 | 2.2116e-05 | 2.2116e-05 | 2.2116e-05
Doboy Bulk | 3426-1 | Queensport | Bulimba | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Doboy Bulk | 3426-1 | Queensport | Bulimba | 10 POE Load (A) | 326.0767 | 324.4902 | 323.9685 | 323.0493 | 324.2277
Doboy Bulk | 3426-1 | Queensport | Bulimba | Power Factor | 0.96016 | 0.96035 | 0.96042 | 0.96053 | 0.96039
Doboy Bulk | 3426-1 | Queensport | Bulimba | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Doboy Bulk | 3426-1 | Queensport | Bulimba | 50 POE Load (A) | 455 | 456 | 491 | 532 | 550
Doboy Bulk | 414-1 | Doboy BS | Tingalpa | NCC Rating (A) | 351 | 351 | 351 | 351 | 351 | Urban | 70
Doboy Bulk | 414-1 | Doboy BS | Tingalpa | 10 POE Load (A) | 200.805 | 199.3434 | 198.7798 | 197.9945 | 198.5705
Doboy Bulk | 414-1 | Doboy BS | Tingalpa | Power Factor | 0.96696 | 0.96716 | 0.96724 | 0.96736 | 0.96727
Doboy Bulk | 414-1 | Doboy BS | Tingalpa | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
Doboy Bulk | 414-1 | Doboy BS | Tingalpa | 50 POE Load (A) | 413 | 413 | 412 | 405 | 420
Doboy Bulk | 416-1 | Doboy BS | Murarrie | NCC Rating (A) | 355 | 355 | 355 | 355 | 355 | Urban | 70
Doboy Bulk | 416-1 | Doboy BS | Murarrie | 10 POE Load (A) | 220.6374 | 220.5063 | 220.1541 | 219.3064 | 220.0723
Doboy Bulk | 416-1 | Doboy BS | Murarrie | Power Factor | 0.99777 | 0.99778 | 0.99782 | 0.9979 | 0.99783
Doboy Bulk | 416-1 | Doboy BS | Murarrie | ECC Rating (A) | 470 | 470 | 470 | 470 | 470
Doboy Bulk | 416-1 | Doboy BS | Murarrie | 50 POE Load (A) | 421 | 419 | 419 | 417 | 415
Doboy Bulk | 443-1 | Queensport | Bulimba | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70
Doboy Bulk | 443-1 | Queensport | Bulimba | 10 POE Load (A) | 230.2266 | 229.1053 | 228.7366 | 228.0869 | 228.9197
Doboy Bulk | 443-1 | Queensport | Bulimba | Power Factor | 0.96867 | 0.96883 | 0.96888 | 0.96897 | 0.96885
Doboy Bulk | 443-1 | Queensport | Bulimba | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Doboy Bulk | 443-1 | Queensport | Bulimba | 50 POE Load (A) | 457 | 458 | 495 | 536 | 540
Doboy Bulk | 558-1 | Hemmant | Tingalpa | NCC Rating (A) | 680 | 680 | 680 | 680 | 680 | Urban | 70
Doboy Bulk | 558-1 | Hemmant | Tingalpa | 10 POE Load (A) | 266.3756 | 264.3469 | 263.6612 | 262.7126 | 263.5395
Doboy Bulk | 558-1 | Hemmant | Tingalpa | Power Factor | 0.96191 | 0.96215 | 0.96224 | 0.96235 | 0.96225
Doboy Bulk | 558-1 | Hemmant | Tingalpa | ECC Rating (A) | 680 | 680 | 680 | 680 | 680
Doboy Bulk | 558-1 | Hemmant | Tingalpa | 50 POE Load (A) | 410 | 410 | 409 | 402 | 396
Doboy Bulk | 563-1 | Doboy BS | Hemmant | NCC Rating (A) | 371 | 371 | 371 | 371 | 371 | Urban | 70
Doboy Bulk | 563-1 | Doboy BS | Hemmant | 10 POE Load (A) | 227.6297 | 226.461 | 225.4794 | 224.0729 | 224.3739
Doboy Bulk | 563-1 | Doboy BS | Hemmant | Power Factor | 0.97955 | 0.97975 | 0.97984 | 0.97997 | 0.9799
Doboy Bulk | 563-1 | Doboy BS | Hemmant | ECC Rating (A) | 429 | 429 | 429 | 429 | 429
Doboy Bulk | 563-1 | Doboy BS | Hemmant | 50 POE Load (A) | 385 | 384 | 383 | 381 | 374
Doboy Bulk | 564-1 | Doboy BS | Hemmant | NCC Rating (A) | 371 | 371 | 371 | 371 | 371 | Urban | 70
Doboy Bulk | 564-1 | Doboy BS | Hemmant | 10 POE Load (A) | 218.6736 | 217.551 | 216.6082 | 215.2574 | 215.5465
Doboy Bulk | 564-1 | Doboy BS | Hemmant | Power Factor | 0.97659 | 0.9768 | 0.9769 | 0.97704 | 0.97696
Doboy Bulk | 564-1 | Doboy BS | Hemmant | ECC Rating (A) | 429 | 429 | 429 | 429 | 429
Doboy Bulk | 564-1 | Doboy BS | Hemmant | 50 POE Load (A) | 201.5622 | 200.5519 | 199.6695 | 198.4042 | 198.6494
Doboy Bulk | 575C-1 | Doboy BS | Murarrie | NCC Rating (A) | 355 | 355 | 355 | 355 | 355 | Urban | 70
Doboy Bulk | 575C-1 | Doboy BS | Murarrie | 10 POE Load (A) | 208.5427 | 208.4188 | 208.086 | 207.2849 | 208.0087
Doboy Bulk | 575C-1 | Doboy BS | Murarrie | Power Factor | 0.99726 | 0.99728 | 0.99732 | 0.99741 | 0.99733
Doboy Bulk | 575C-1 | Doboy BS | Murarrie | ECC Rating (A) | 475 | 475 | 475 | 475 | 475
Doboy Bulk | 575C-1 | Doboy BS | Murarrie | 50 POE Load (A) | 207.0318 | 206.908 | 206.5774 | 205.782 | 206.4995
Doboy Bulk | 581-1 | Doboy BS | Queensport | NCC Rating (A) | 661 | 661 | 661 | 661 | 661 | Urban | 166 | 8
Doboy Bulk | 581-1 | Doboy BS | Queensport | 10 POE Load (A) | 560.7489 | 559.1422 | 557.9488 | 555.6496 | 557.4314
Doboy Bulk | 581-1 | Doboy BS | Queensport | Power Factor | 0.97414 | 0.97428 | 0.97439 | 0.97461 | 0.97445
Doboy Bulk | 581-1 | Doboy BS | Queensport | ECC Rating (A) | 785 | 785 | 785 | 785 | 785
Doboy Bulk | 581-1 | Doboy BS | Queensport | 50 POE Load (A) | 923 | 924 | 955 | 994 | 994
Doboy Bulk | 645-1 | Doboy BS | Gibson Island | NCC Rating (A) | 433 | 433 | 433 | 433 | 433 | HighSec | 0
Doboy Bulk | 645-1 | Doboy BS | Gibson Island | 10 POE Load (A) | 6.747 | 6.747 | 6.747 | 6.747 | 6.747
Doboy Bulk | 645-1 | Doboy BS | Gibson Island | Power Factor | 2.1138e-05 | 2.1138e-05 | 2.1138e-05 | 2.1138e-05 | 2.1138e-05
Doboy Bulk | 645-1 | Doboy BS | Gibson Island | ECC Rating (A) | 433 | 433 | 433 | 433 | 433
Doboy Bulk | 645-1 | Doboy BS | Gibson Island | 50 POE Load (A) | 156 | 156 | 156 | 156 | 155
Doboy Bulk | 677-1 | Doboy BS | Queensport | NCC Rating (A) | 661 | 661 | 661 | 661 | 661 | Urban | 166 | 8
Doboy Bulk | 677-1 | Doboy BS | Queensport | 10 POE Load (A) | 559.1876 | 557.5854 | 556.3953 | 554.1026 | 555.8794
Doboy Bulk | 677-1 | Doboy BS | Queensport | Power Factor | 0.97415 | 0.97429 | 0.9744 | 0.97462 | 0.97446
Doboy Bulk | 677-1 | Doboy BS | Queensport | ECC Rating (A) | 785 | 785 | 785 | 785 | 785
Doboy Bulk | 677-1 | Doboy BS | Queensport | 50 POE Load (A) | 923 | 924 | 955 | 994 | 994
Gatton Bulk | 377-1 | Gatton BS | 377 Tee1 | NCC Rating (A) | 821 | 821 | 821 | 821 | 821 | Rural | 170
Gatton Bulk | 377-1 | Gatton BS | 377 Tee1 | 10 POE Load (A) | 305.4523 | 302.6898 | 301.2904 | 298.6449 | 297.9695
Gatton Bulk | 377-1 | Gatton BS | 377 Tee1 | Power Factor | 0.98448 | 0.98499 | 0.98524 | 0.98571 | 0.98585
Gatton Bulk | 377-1 | Gatton BS | 377 Tee1 | ECC Rating (A) | 959 | 959 | 959 | 959 | 959
Gatton Bulk | 377-1 | Gatton BS | 377 Tee1 | 50 POE Load (A) | 461 | 461 | 460 | 459 | 458
Gatton Bulk | 377-2 | 377 Tee1 | 487 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Gatton Bulk | 377-2 | 377 Tee1 | 487 Tee1 | 10 POE Load (A) | 0.0043949 | 0.0043949 | 0.0043949 | 0.0043949 | 0.0043949
Gatton Bulk | 377-2 | 377 Tee1 | 487 Tee1 | Power Factor | 4.5101e-05 | 4.5101e-05 | 4.5115e-05 | 4.512e-05 | 4.5111e-05
Gatton Bulk | 377-3 | 377 Tee1 | 377 Tee2 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Gatton Bulk | 377-3 | 377 Tee1 | 377 Tee2 | 10 POE Load (A) | 305.5381 | 302.7758 | 301.3762 | 298.7304 | 298.0549
Gatton Bulk | 377-3 | 377 Tee1 | 377 Tee2 | Power Factor | 0.9843 | 0.98481 | 0.98506 | 0.98553 | 0.98567
Gatton Bulk | 377-3 | 377 Tee1 | 377 Tee2 | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Gatton Bulk | 377-3 | 377 Tee1 | 377 Tee2 | 50 POE Load (A) | 461 | 461 | 460 | 459 | 459
Gatton Bulk | 377-4 | 377 Tee2 | Gatton | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
Gatton Bulk | 377-4 | 377 Tee2 | Gatton | 10 POE Load (A) | 305.8478 | 303.0863 | 301.6862 | 299.0395 | 298.3637
Gatton Bulk | 377-4 | 377 Tee2 | Gatton | Power Factor | 0.99027 | 0.99062 | 0.99079 | 0.99111 | 0.99121
Gatton Bulk | 377-4 | 377 Tee2 | Gatton | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Gatton Bulk | 377-4 | 377 Tee2 | Gatton | 50 POE Load (A) | 461 | 461 | 461 | 459 | 458
Gatton Bulk | 377-5 | 377 Tee2 | Glenmore Grove | NCC Rating (A) | 355 | 355 | 355 | 355 | 355 | Rural | 170
Gatton Bulk | 377-5 | 377 Tee2 | Glenmore Grove | 10 POE Load (A) | 0.61639 | 0.6165 | 0.61655 | 0.61666 | 0.61668
Gatton Bulk | 377-5 | 377 Tee2 | Glenmore Grove | Power Factor | 3.0304e-05 | 3.0304e-05 | 3.0304e-05 | 3.0304e-05 | 3.0304e-05
Gatton Bulk | 3859-1 | Gatton BS | Springfield Central | NCC Rating (A) | 764 | 764 | 764 | 764 | 764 | Rural | 170
Gatton Bulk | 3859-1 | Gatton BS | Springfield Central | 10 POE Load (A) | 39.8463 | 39.3657 | 39.0223 | 38.4269 | 38.1165
Gatton Bulk | 3859-1 | Gatton BS | Springfield Central | Power Factor | 0.96836 | 0.96871 | 0.96896 | 0.9694 | 0.96963
Gatton Bulk | 3859-1 | Gatton BS | Springfield Central | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Gatton Bulk | 3859-1 | Gatton BS | Springfield Central | 50 POE Load (A) | 36.2272 | 35.7915 | 35.4801 | 34.9402 | 34.6588
Gatton Bulk | 3860-1 | Gatton BS | Springfield Central | NCC Rating (A) | 764 | 764 | 764 | 764 | 764 | Rural | 170
Gatton Bulk | 3860-1 | Gatton BS | Springfield Central | 10 POE Load (A) | 39.8329 | 39.3526 | 39.0094 | 38.4143 | 38.1042
Gatton Bulk | 3860-1 | Gatton BS | Springfield Central | Power Factor | 0.96822 | 0.96857 | 0.96882 | 0.96925 | 0.96949
Gatton Bulk | 3860-1 | Gatton BS | Springfield Central | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Gatton Bulk | 3860-1 | Gatton BS | Springfield Central | 50 POE Load (A) | 36.216 | 35.7805 | 35.4694 | 34.9298 | 34.6486
Gatton Bulk | 487-1 | Gatton BS | 487 Tee1 | NCC Rating (A) | 821 | 821 | 821 | 821 | 821 | Rural | 170
Gatton Bulk | 487-1 | Gatton BS | 487 Tee1 | 10 POE Load (A) | 307.4363 | 304.2549 | 302.5215 | 299.3956 | 298.2471
Gatton Bulk | 487-1 | Gatton BS | 487 Tee1 | Power Factor | 0.98047 | 0.98107 | 0.98139 | 0.98196 | 0.98218
Gatton Bulk | 487-1 | Gatton BS | 487 Tee1 | ECC Rating (A) | 821 | 821 | 821 | 821 | 821
Gatton Bulk | 487-1 | Gatton BS | 487 Tee1 | 50 POE Load (A) | 551 | 551 | 550 | 548 | 546
Gatton Bulk | 487-2 | 487 Tee1 | 377 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Gatton Bulk | 487-2 | 487 Tee1 | 377 Tee1 | 10 POE Load (A) | 0.0045534 | 0.0045534 | 0.0045534 | 0.0045535 | 0.0045535
Gatton Bulk | 487-2 | 487 Tee1 | 377 Tee1 | Power Factor | 4.3524e-05 | 4.3536e-05 | 4.3524e-05 | 4.3525e-05 | 4.353e-05
Gatton Bulk | 487-3 | 487 Tee1 | 487 Tee2 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Gatton Bulk | 487-3 | 487 Tee1 | 487 Tee2 | 10 POE Load (A) | 308.5641 | 305.384 | 303.6484 | 300.5183 | 299.3682
Gatton Bulk | 487-3 | 487 Tee1 | 487 Tee2 | Power Factor | 0.98323 | 0.98375 | 0.98403 | 0.98453 | 0.98473
Gatton Bulk | 487-3 | 487 Tee1 | 487 Tee2 | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Gatton Bulk | 487-3 | 487 Tee1 | 487 Tee2 | 50 POE Load (A) | 552 | 551 | 551 | 548 | 545
Gatton Bulk | 487-6 | 487 Tee3 | 3844 Tee1 | NCC Rating (A) | 251 | 251 | 251 | 251 | 251 | Rural | 170
Gatton Bulk | 487-6 | 487 Tee3 | 3844 Tee1 | 10 POE Load (A) | 0.015341 | 0.015352 | 0.015359 | 0.01537 | 0.015377
Gatton Bulk | 487-6 | 487 Tee3 | 3844 Tee1 | Power Factor | -6.7679e-05 | -6.769e-05 | -6.7698e-05 | -6.7697e-05 | -6.7685e-05
Gatton Bulk | 487-8 | 487 Tee4 | 3844 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Gatton Bulk | 487-8 | 487 Tee4 | 3844 Tee1 | 10 POE Load (A) | 0.00040734 | 0.00040765 | 0.00040785 | 0.00040816 | 0.00040834
Gatton Bulk | 487-8 | 487 Tee4 | 3844 Tee1 | Power Factor | -0.99997 | -0.99999 | -0.99996 | -1 | -0.99997
Gatton Bulk | 487-9 | 487 Tee2 | Gatton | NCC Rating (A) | 713 | 713 | 713 | 713 | 713 | Rural | 170
Gatton Bulk | 487-9 | 487 Tee2 | Gatton | 10 POE Load (A) | 198.0053 | 196.717 | 196.2155 | 195.0789 | 195.2266
Gatton Bulk | 487-9 | 487 Tee2 | Gatton | Power Factor | 0.99749 | 0.99765 | 0.99769 | 0.99781 | 0.99779
Gatton Bulk | 487-9 | 487 Tee2 | Gatton | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
Gatton Bulk | 487-9 | 487 Tee2 | Gatton | 50 POE Load (A) | 469 | 469 | 469 | 467 | 469
Gatton Bulk | 531-1 | Gatton | Tenthill | NCC Rating (A) | 200 | 200 | 200 | 200 | 200 | Rural | 170
Gatton Bulk | 531-1 | Gatton | Tenthill | 10 POE Load (A) | 91.788 | 90.7978 | 90.2806 | 89.6791 | 89.6941
Gatton Bulk | 531-1 | Gatton | Tenthill | Power Factor | -0.97473 | -0.97497 | -0.97513 | -0.97533 | -0.97542
Gatton Bulk | 531-1 | Gatton | Tenthill | ECC Rating (A) | 155 | 200 | 200 | 200 | 200
Gatton Bulk | 531-1 | Gatton | Tenthill | 50 POE Load (A) | 82.577 | 81.6801 | 81.2149 | 80.6739 | 80.6835
Gatton Bulk | 532-1 | Tenthill | 532 Tee1 | NCC Rating (A) | 208 | 208 | 208 | 208 | 208 | Rural | 170
Gatton Bulk | 532-1 | Tenthill | 532 Tee1 | 10 POE Load (A) | 0.0023146 | 0.0023157 | 0.0023163 | 0.0023173 | 0.0023175
Gatton Bulk | 532-1 | Tenthill | 532 Tee1 | Power Factor | 8.2581e-05 | 8.2584e-05 | 8.2592e-05 | 8.2616e-05 | 8.2577e-05
Gatton Bulk | 533-1 | Tenthill | Mt Sylvia | NCC Rating (A) | 78 | 78 | 78 | 78 | 78 | Rural | 170
Gatton Bulk | 533-1 | Tenthill | Mt Sylvia | 10 POE Load (A) | 22.5714 | 22.2076 | 21.9939 | 21.7102 | 21.5775
Gatton Bulk | 533-1 | Tenthill | Mt Sylvia | Power Factor | 0.91824 | 0.91846 | 0.9186 | 0.91878 | 0.91887
Gatton Bulk | 533-1 | Tenthill | Mt Sylvia | ECC Rating (A) | 78 | 78 | 78 | 78 | 78
Gatton Bulk | 533-1 | Tenthill | Mt Sylvia | 50 POE Load (A) | 20.8781 | 20.5414 | 20.3447 | 20.0839 | 19.9615
Goodna Bulk | 3800-1 | Goodna BS | Cooneana | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
Goodna Bulk | 3800-1 | Goodna BS | Cooneana | 10 POE Load (A) | 109.3765 | 97.3896 | 112.2531 | 126.8733 | 142.4239
Goodna Bulk | 3800-1 | Goodna BS | Cooneana | Power Factor | 0.98643 | 0.98835 | 0.98595 | 0.98408 | 0.98037
Goodna Bulk | 3800-1 | Goodna BS | Cooneana | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Goodna Bulk | 3800-1 | Goodna BS | Cooneana | 50 POE Load (A) | 183 | 204 | 222 | 242 | 260
Goodna Bulk | 3801-1 | Goodna BS | Carol Pk Central | NCC Rating (A) | 720 | 720 | 720 | 720 | 720 | Urban | 70
Goodna Bulk | 3801-1 | Goodna BS | Carol Pk Central | 10 POE Load (A) | 280.0989 | 281.9269 | 283.2206 | 283.1133 | 286.0414
Goodna Bulk | 3801-1 | Goodna BS | Carol Pk Central | Power Factor | 0.98985 | 0.98973 | 0.9897 | 0.98994 | 0.98955
Goodna Bulk | 3801-1 | Goodna BS | Carol Pk Central | ECC Rating (A) | 765 | 765 | 765 | 765 | 765
Goodna Bulk | 3801-1 | Goodna BS | Carol Pk Central | 50 POE Load (A) | 454 | 457 | 453 | 455 | 460
Goodna Bulk | 3802-1 | Goodna BS | Springfield | NCC Rating (A) | 592 | 592 | 592 | 592 | 592 | Urban | 70
Goodna Bulk | 3802-1 | Goodna BS | Springfield | 10 POE Load (A) | 407.5034 | 415.5939 | 426.7515 | 437.1334 | 451.2694
Goodna Bulk | 3802-1 | Goodna BS | Springfield | Power Factor | -0.98915 | -0.98873 | -0.988 | -0.98747 | -0.98621
Goodna Bulk | 3802-1 | Goodna BS | Springfield | ECC Rating (A) | 675 | 675 | 675 | 675 | 675
Goodna Bulk | 3802-1 | Goodna BS | Springfield | 50 POE Load (A) | 698 | 714 | 718 | 729 | 740
Goodna Bulk | 3803-1 | Goodna BS | Carol Park | NCC Rating (A) | 502 | 502 | 502 | 502 | 502 | Urban | 70
Goodna Bulk | 3803-1 | Goodna BS | Carol Park | 10 POE Load (A) | 267.769 | 272.5384 | 278.0873 | 282.4659 | 289.7223
Goodna Bulk | 3803-1 | Goodna BS | Carol Park | Power Factor | 0.99342 | 0.99319 | 0.99284 | 0.99275 | 0.99199
Goodna Bulk | 3803-1 | Goodna BS | Carol Park | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Goodna Bulk | 3803-1 | Goodna BS | Carol Park | 50 POE Load (A) | 347 | 353 | 354 | 358 | 370
Goodna Bulk | 3805-1 | Goodna BS | Carol Park | NCC Rating (A) | 502 | 502 | 502 | 502 | 502 | Urban | 70
Goodna Bulk | 3805-1 | Goodna BS | Carol Park | 10 POE Load (A) | 244.8529 | 249.2142 | 254.2882 | 258.2919 | 264.9275
Goodna Bulk | 3805-1 | Goodna BS | Carol Park | Power Factor | 0.99178 | 0.99152 | 0.99114 | 0.99103 | 0.9902
Goodna Bulk | 3805-1 | Goodna BS | Carol Park | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Goodna Bulk | 3805-1 | Goodna BS | Carol Park | 50 POE Load (A) | 333 | 339 | 340 | 344 | 360
Goodna Bulk | 3806-1 | Goodna BS | Springfield | NCC Rating (A) | 592 | 592 | 592 | 592 | 592 | Urban | 70
Goodna Bulk | 3806-1 | Goodna BS | Springfield | 10 POE Load (A) | 405.9647 | 414.0246 | 425.1401 | 435.4828 | 449.5656
Goodna Bulk | 3806-1 | Goodna BS | Springfield | Power Factor | 0.99348 | 0.99304 | 0.99231 | 0.99163 | 0.99066
Goodna Bulk | 3806-1 | Goodna BS | Springfield | ECC Rating (A) | 675 | 675 | 675 | 675 | 675
Goodna Bulk | 3806-1 | Goodna BS | Springfield | 50 POE Load (A) | 698 | 714 | 718 | 729 | 740
Goodna Bulk | 3807-1 | Goodna BS | Redbank | NCC Rating (A) | 748 | 748 | 748 | 748 | 748 | Urban | 70
Goodna Bulk | 3807-1 | Goodna BS | Redbank | 10 POE Load (A) | 286.2185 | 283.2569 | 280.8125 | 278.0096 | 277.7669
Goodna Bulk | 3807-1 | Goodna BS | Redbank | Power Factor | 0.9745 | 0.9746 | 0.97468 | 0.97478 | 0.97479
Goodna Bulk | 3807-1 | Goodna BS | Redbank | ECC Rating (A) | 748 | 748 | 748 | 748 | 748
Goodna Bulk | 3807-1 | Goodna BS | Redbank | 50 POE Load (A) | 345 | 346 | 346 | 349 | 360
Goodna Bulk | 3808-1 | Goodna BS | Carol Pk Central | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70
Goodna Bulk | 3808-1 | Goodna BS | Carol Pk Central | 10 POE Load (A) | 280.5998 | 282.4311 | 283.7272 | 283.6197 | 286.5531
Goodna Bulk | 3808-1 | Goodna BS | Carol Pk Central | Power Factor | 0.98996 | 0.98983 | 0.9898 | 0.99004 | 0.98966
Goodna Bulk | 3808-1 | Goodna BS | Carol Pk Central | ECC Rating (A) | 748 | 748 | 748 | 748 | 748
Goodna Bulk | 3808-1 | Goodna BS | Carol Pk Central | 50 POE Load (A) | 454 | 457 | 454 | 455 | 455
Goodna Bulk | 3809-1 | Goodna BS | Cooneana | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
Goodna Bulk | 3809-1 | Goodna BS | Cooneana | 10 POE Load (A) | 123.6152 | 110.0667 | 126.8666 | 143.3921 | 160.9681
Goodna Bulk | 3809-1 | Goodna BS | Cooneana | Power Factor | 0.98729 | 0.98915 | 0.98682 | 0.98499 | 0.98138
Goodna Bulk | 3809-1 | Goodna BS | Cooneana | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Goodna Bulk | 3809-1 | Goodna BS | Cooneana | 50 POE Load (A) | 182 | 204 | 222 | 242 | 250
Goodna Bulk | 3880-1 | Carol Park | Springfield Central | NCC Rating (A) | 742 | 742 | 742 | 742 | 742 | Urban | 70
Goodna Bulk | 3880-1 | Carol Park | Springfield Central | 10 POE Load (A) | 208.3669 | 222.1358 | 237.3465 | 251.7487 | 268.9252
Goodna Bulk | 3880-1 | Carol Park | Springfield Central | Power Factor | 1 | 0.99986 | 0.99947 | 0.9989 | 0.99831
Goodna Bulk | 3880-1 | Carol Park | Springfield Central | ECC Rating (A) | 742 | 742 | 742 | 742 | 742
Goodna Bulk | 3880-1 | Carol Park | Springfield Central | 50 POE Load (A) | 387 | 406 | 419 | 437 | 450
Goodna Bulk | 3881-1 | Springfield | Springfield Central | NCC Rating (A) | 742 | 742 | 742 | 742 | 742 | Urban | 70
Goodna Bulk | 3881-1 | Springfield | Springfield Central | 10 POE Load (A) | 238.6404 | 253.7611 | 270.3295 | 286.7438 | 304.6292
Goodna Bulk | 3881-1 | Springfield | Springfield Central | Power Factor | 0.9925 | 0.99143 | 0.99021 | 0.98897 | 0.98799
Goodna Bulk | 3881-1 | Springfield | Springfield Central | ECC Rating (A) | 742 | 742 | 742 | 742 | 742
Goodna Bulk | 3881-1 | Springfield | Springfield Central | 50 POE Load (A) | 382 | 401 | 414 | 431 | 440
Goodna Bulk | 456-1 | Wacol Sth | 456 Tee1 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70
Goodna Bulk | 456-1 | Wacol Sth | 456 Tee1 | 10 POE Load (A) | 116.3938 | 119.6096 | 123.6589 | 127.2605 | 132.1185
Goodna Bulk | 456-1 | Wacol Sth | 456 Tee1 | Power Factor | 0.99829 | 0.99804 | 0.99763 | 0.99724 | 0.99676
Goodna Bulk | 456-2 | 456 Tee1 | Carol Pk Central | NCC Rating (A) | 441 | 441 | 441 | 441 | 441 | Urban | 70
Goodna Bulk | 456-2 | 456 Tee1 | Carol Pk Central | 10 POE Load (A) | 116.3938 | 119.6096 | 123.6589 | 127.2605 | 132.1185
Goodna Bulk | 456-2 | 456 Tee1 | Carol Pk Central | Power Factor | -0.9918 | -0.99142 | -0.99076 | -0.99042 | -0.98918
Goodna Bulk | 456-2 | 456 Tee1 | Carol Pk Central | ECC Rating (A) | 441 | 441 | 441 | 441 | 441
Goodna Bulk | 456-2 | 456 Tee1 | Carol Pk Central | 50 POE Load (A) | 105.9741 | 108.5291 | 111.8272 | 114.8406 | 118.7123
Goodna Bulk | 456-3 | 456 Tee1 | Carol Pk | NCC Rating (A) | 441 | 441 | 441 | 441 | 441 | Urban | 70
Goodna Bulk | 456-3 | 456 Tee1 | Carol Pk | 10 POE Load (A) | 116.6145 | 119.8346 | 123.8915 | 127.4967 | 132.3683
Goodna Bulk | 456-3 | 456 Tee1 | Carol Pk | Power Factor | 0.99818 | 0.99793 | 0.99751 | 0.99713 | 0.99665
Goodna Bulk | 456-3 | 456 Tee1 | Carol Pk | ECC Rating (A) | 441 | 441 | 441 | 441 | 441
Goodna Bulk | 456-3 | 456 Tee1 | Carol Pk | 50 POE Load (A) | 106.1752 | 108.7322 | 112.0356 | 115.0532 | 118.9329
Griffin Bulk | 312-1 | Kallangur | Narangba | NCC Rating (A) | 422 | 422 | 422 | 422 | 422 | Rural | 170
Griffin Bulk | 312-1 | Kallangur | Narangba | 10 POE Load (A) | 0.64319 | 0.64313 | 0.64278 | 0.64245 | 0.64208
Griffin Bulk | 312-1 | Kallangur | Narangba | Power Factor | -1.3713e-06 | -1.371e-06 | -1.3714e-06 | -1.3711e-06 | -1.3713e-06
Griffin Bulk | 320-1 | Griffin BS | 320 Tee1 | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70
Griffin Bulk | 320-1 | Griffin BS | 320 Tee1 | 10 POE Load (A) | 414.2684 | 414.2441 | 421.1082 | 426.8946 | 434.9232
Griffin Bulk | 320-1 | Griffin BS | 320 Tee1 | Power Factor | 0.99111 | 0.99116 | 0.99079 | 0.99073 | 0.98995
Griffin Bulk | 320-1 | Griffin BS | 320 Tee1 | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
Griffin Bulk | 320-1 | Griffin BS | 320 Tee1 | 50 POE Load (A) | 521 | 526 | 536 | 545 | 560
Griffin Bulk | 320-2 | 320 Tee1 | Mango Hill Bus 2 | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 70 | 15
Griffin Bulk | 320-2 | 320 Tee1 | Mango Hill Bus 2 | 10 POE Load (A) | 347.1727 | 344.1538 | 340.7841 | 336.4479 | 334.9747
Griffin Bulk | 320-2 | 320 Tee1 | Mango Hill Bus 2 | Power Factor | 0.9996 | 0.99967 | 0.99973 | 0.99989 | 0.99984
Griffin Bulk | 320-2 | 320 Tee1 | Mango Hill Bus 2 | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
Griffin Bulk | 320-2 | 320 Tee1 | Mango Hill Bus 2 | 50 POE Load (A) | 555 | 560 | 563 | 564 | 580
Griffin Bulk | 320-3 | 320 Tee1 | Kalangur | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 70
Griffin Bulk | 320-3 | 320 Tee1 | Kalangur | 10 POE Load (A) | 113.3747 | 116.383 | 127.2234 | 138.17 | 148.191
Griffin Bulk | 320-3 | 320 Tee1 | Kalangur | Power Factor | 0.935 | 0.93593 | 0.93868 | 0.93966 | 0.94191
Griffin Bulk | 320-3 | 320 Tee1 | Kalangur | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
Griffin Bulk | 320-3 | 320 Tee1 | Kalangur | 50 POE Load (A) | 308 | 312 | 327 | 344 | 350
Griffin Bulk | 3329-1 | Griffin BS | 3329 Tee1 | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70
Griffin Bulk | 3329-1 | Griffin BS | 3329 Tee1 | 10 POE Load (A) | 435.7877 | 438.2681 | 452.9933 | 466.4895 | 481.89
Griffin Bulk | 3329-1 | Griffin BS | 3329 Tee1 | Power Factor | 0.97517 | 0.97483 | 0.97313 | 0.97164 | 0.96968
Griffin Bulk | 3329-1 | Griffin BS | 3329 Tee1 | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
Griffin Bulk | 3329-1 | Griffin BS | 3329 Tee1 | 50 POE Load (A) | 488 | 493 | 510 | 527 | 530
Griffin Bulk | 3329-2 | 3329 Tee1 | 3330 Tee1 | NCC Rating (A) | 748 | 748 | 748 | 748 | 748 | Urban | 70
Griffin Bulk | 3329-2 | 3329 Tee1 | 3330 Tee1 | 10 POE Load (A) | 0.029142 | 0.029141 | 0.029136 | 0.029131 | 0.029125
Griffin Bulk | 3329-2 | 3329 Tee1 | 3330 Tee1 | Power Factor | 6.7994e-06 | 6.7996e-06 | 6.7993e-06 | 6.7992e-06 | 6.7996e-06
Griffin Bulk | 3329-3 | 3329 Tee1 | Kallangur | NCC Rating (A) | 711 | 711 | 711 | 711 | 711 | Urban | 70
Griffin Bulk | 3329-3 | 3329 Tee1 | Kallangur | 10 POE Load (A) | 435.8775 | 438.3584 | 453.0863 | 466.5846 | 481.988
Griffin Bulk | 3329-3 | 3329 Tee1 | Kallangur | Power Factor | 0.97595 | 0.97565 | 0.97416 | 0.97287 | 0.97115
Griffin Bulk | 3329-3 | 3329 Tee1 | Kallangur | ECC Rating (A) | 711 | 711 | 711 | 711 | 711
Griffin Bulk | 3329-3 | 3329 Tee1 | Kallangur | 50 POE Load (A) | 403.8868 | 406.1371 | 420.4644 | 433.7996 | 448.4058
Griffin Bulk | 3330-1 | Griffin BS | 3330 Tee1 | NCC Rating (A) | 717 | 717 | 717 | 717 | 717 | Urban | 70
Griffin Bulk | 3330-1 | Griffin BS | 3330 Tee1 | 10 POE Load (A) | 224.1206 | 225.2831 | 232.5645 | 239.2147 | 246.8472
Griffin Bulk | 3330-1 | Griffin BS | 3330 Tee1 | Power Factor | 0.98414 | 0.98389 | 0.98259 | 0.98144 | 0.9799
Griffin Bulk | 3330-1 | Griffin BS | 3330 Tee1 | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
Griffin Bulk | 3330-1 | Griffin BS | 3330 Tee1 | 50 POE Load (A) | 353 | 357 | 369 | 381 | 400
Griffin Bulk | 3330-2 | 3330 Tee1 | 3329 Tee1 | NCC Rating (A) | 523 | 523 | 523 | 523 | 523 | Urban | 70
Griffin Bulk | 3330-2 | 3330 Tee1 | 3329 Tee1 | 10 POE Load (A) | 0.014138 | 0.014137 | 0.014135 | 0.014134 | 0.014132
Griffin Bulk | 3330-2 | 3330 Tee1 | 3329 Tee1 | Power Factor | 1.9246e-05 | 1.9244e-05 | 1.9245e-05 | 1.9244e-05 | 1.9245e-05
Griffin Bulk | 3330-3 | 3330 Tee1 | APM | NCC Rating (A) | 717 | 717 | 717 | 717 | 717 | Urban | 70
Griffin Bulk | 3330-3 | 3330 Tee1 | APM | 10 POE Load (A) | 224.2535 | 225.417 | 232.7032 | 239.3575 | 246.9954
Griffin Bulk | 3330-3 | 3330 Tee1 | APM | Power Factor | 0.9849 | 0.98467 | 0.98354 | 0.98256 | 0.98121
Griffin Bulk | 3330-3 | 3330 Tee1 | APM | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
Griffin Bulk | 3330-3 | 3330 Tee1 | APM | 50 POE Load (A) | 353 | 357 | 369 | 381 | 390
Griffin Bulk | 3331-1 | 3331 Tee1 | Kallangur | NCC Rating (A) | 717 | 717 | 717 | 717 | 717 | Urban | 70
Griffin Bulk | 3331-1 | 3331 Tee1 | Kallangur | 10 POE Load (A) | 176.933 | 178.3475 | 185.4 | 192.0275 | 199.3043
Griffin Bulk | 3331-1 | 3331 Tee1 | Kallangur | Power Factor | 0.98809 | 0.98783 | 0.98663 | 0.98544 | 0.98415
Griffin Bulk | 3331-1 | 3331 Tee1 | Kallangur | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
Griffin Bulk | 3331-1 | 3331 Tee1 | Kallangur | 50 POE Load (A) | 315 | 319 | 331 | 343 | 350
Griffin Bulk | 3331-3 | Aust Paper Mills | 3331 Tee1 | NCC Rating (A) | 717 | 717 | 717 | 717 | 717 | Urban | 70
Griffin Bulk | 3331-3 | Aust Paper Mills | 3331 Tee1 | 10 POE Load (A) | 223.7075 | 224.8695 | 232.1641 | 238.8276 | 246.4583
Griffin Bulk | 3331-3 | Aust Paper Mills | 3331 Tee1 | Power Factor | 0.98665 | 0.98643 | 0.98532 | 0.98434 | 0.98305
Griffin Bulk | 3331-3 | Aust Paper Mills | 3331 Tee1 | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
Griffin Bulk | 3331-3 | Aust Paper Mills | 3331 Tee1 | 50 POE Load (A) | 353 | 357 | 369 | 381 | 390
Griffin Bulk | 3359-1 | 3359 Tee1 | Hays Inlet | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70
Griffin Bulk | 3359-1 | 3359 Tee1 | Hays Inlet | 10 POE Load (A) | 0.38789 | 0.38792 | 0.3879 | 0.38792 | 0.38785
Griffin Bulk | 3359-1 | 3359 Tee1 | Hays Inlet | Power Factor | -1.0508e-06 | -1.0503e-06 | -1.0517e-06 | -1.0512e-06 | -1.051e-06
Griffin Bulk | 3359-2 | 3359 Tee1 | 3359 Tee2 | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70
Griffin Bulk | 3359-2 | 3359 Tee1 | 3359 Tee2 | 10 POE Load (A) | 346.9702 | 345.655 | 347.4293 | 348.2851 | 351.435
Griffin Bulk | 3359-2 | 3359 Tee1 | 3359 Tee2 | Power Factor | 0.96494 | 0.9654 | 0.96562 | 0.96677 | 0.96584
Griffin Bulk | 3359-2 | 3359 Tee1 | 3359 Tee2 | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
Griffin Bulk | 3359-2 | 3359 Tee1 | 3359 Tee2 | 50 POE Load (A) | 551 | 556 | 559 | 560 | 565
Griffin Bulk | 3359-3 | 3359 Tee2 | 3359 Tee3 | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70
Griffin Bulk | 3359-3 | 3359 Tee2 | 3359 Tee3 | 10 POE Load (A) | 347.1179 | 345.8018 | 347.5755 | 348.4303 | 351.5803
Griffin Bulk | 3359-3 | 3359 Tee2 | 3359 Tee3 | Power Factor | 0.96488 | 0.96534 | 0.96557 | 0.96672 | 0.9658
Griffin Bulk | 3359-3 | 3359 Tee2 | 3359 Tee3 | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
Griffin Bulk | 3359-3 | 3359 Tee2 | 3359 Tee3 | 50 POE Load (A) | 551 | 556 | 559 | 561 | 570
Griffin Bulk | 3359-4 | 3359 Tee3 | Mango Hill Bus 2 | NCC Rating (A) | 762 | 762 | 762 | 762 | 762 | Urban | 70
Griffin Bulk | 3359-4 | 3359 Tee3 | Mango Hill Bus 2 | 10 POE Load (A) | 347.729 | 346.4094 | 348.1804 | 349.0314 | 352.1815
Griffin Bulk | 3359-4 | 3359 Tee3 | Mango Hill Bus 2 | Power Factor | 0.96628 | 0.96673 | 0.96697 | 0.96811 | 0.96723
Griffin Bulk | 3359-4 | 3359 Tee3 | Mango Hill Bus 2 | ECC Rating (A) | 762 | 762 | 762 | 762 | 762
Griffin Bulk | 3359-4 | 3359 Tee3 | Mango Hill Bus 2 | 50 POE Load (A) | 735.5521 | 743.1881 | 755.0889 | 766.0588 | 783.2315
Griffin Bulk | 3359-5 | 3359 Tee2 | P51001-D | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70
Griffin Bulk | 3359-5 | 3359 Tee2 | P51001-D | 10 POE Load (A) | 0.46359 | 0.46362 | 0.46359 | 0.46362 | 0.46353
Griffin Bulk | 3359-5 | 3359 Tee2 | P51001-D | Power Factor | 8.5354e-06 | 8.5353e-06 | 8.5353e-06 | 8.5353e-06 | 8.5354e-06
Griffin Bulk | 3359-6 | 3359 Tee3 | X18574-E | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Urban | 70
Griffin Bulk | 3359-6 | 3359 Tee3 | X18574-E | 10 POE Load (A) | 0.19176 | 0.19177 | 0.19176 | 0.19177 | 0.19174
Griffin Bulk | 3359-6 | 3359 Tee3 | X18574-E | Power Factor | 3.3927e-06 | 3.3927e-06 | 3.3928e-06 | 3.3927e-06 | 3.3928e-06
Griffin Bulk | 3359-7 | Griffin BS | 3359 Tee1 | NCC Rating (A) | 703 | 703 | 703 | 703 | 703 | Urban | 70
Griffin Bulk | 3359-7 | Griffin BS | 3359 Tee1 | 10 POE Load (A) | 346.842 | 345.5276 | 347.3024 | 348.1589 | 351.3087
Griffin Bulk | 3359-7 | Griffin BS | 3359 Tee1 | Power Factor | 0.95995 | 0.96046 | 0.96066 | 0.96185 | 0.9608
Griffin Bulk | 3359-7 | Griffin BS | 3359 Tee1 | ECC Rating (A) | 703 | 703 | 703 | 703 | 703
Griffin Bulk | 3359-7 | Griffin BS | 3359 Tee1 | 50 POE Load (A) | 551 | 556 | 559 | 560 | 570
Griffin Bulk | 338-1 | Griffin BS | Strathpine | NCC Rating (A) | 348 | 348 | 348 | 348 | 348 | Urban | 70
Griffin Bulk | 338-1 | Griffin BS | Strathpine | 10 POE Load (A) | 4.0492 | 4.0492 | 4.0492 | 4.0492 | 4.0492
Griffin Bulk | 338-1 | Griffin BS | Strathpine | Power Factor | 0.00011973 | 0.00011973 | 0.00011973 | 0.00011973 | 0.00011973
Griffin Bulk | 338-1 | Griffin BS | Strathpine | ECC Rating (A) | 348 | 348 | 348 | 348 | 348
Griffin Bulk | 338-1 | Griffin BS | Strathpine | 50 POE Load (A) | 4.0492 | 4.0492 | 4.0492 | 4.0492 | 4.0492
Gympie Bulk | 3004-1 | Coondoo Ck Reg | Tin Can Bay | NCC Rating (A) | 127 | 127 | 127 | 127 | 127 | Rural | 170
Gympie Bulk | 3004-1 | Coondoo Ck Reg | Tin Can Bay | 10 POE Load (A) | 1.2219 | 1.222 | 1.2219 | 1.2219 | 1.2217
Gympie Bulk | 3004-1 | Coondoo Ck Reg | Tin Can Bay | Power Factor | 0.00028204 | 0.00028204 | 0.00028204 | 0.00028204 | 0.00028204
Gympie Bulk | 3004-1 | Coondoo Ck Reg | Tin Can Bay | ECC Rating (A) | 127 | 127 | 127 | 127 | 127
Gympie Bulk | 3004-1 | Coondoo Ck Reg | Tin Can Bay | 50 POE Load (A) | 1.2213 | 1.2214 | 1.2213 | 1.2213 | 1.2211
Gympie Bulk | 3005-1 | Coondoo Ck Reg | Tin Can Bay | NCC Rating (A) | 403 | 403 | 403 | 403 | 403 | Rural | 170
Gympie Bulk | 3005-1 | Coondoo Ck Reg | Tin Can Bay | 10 POE Load (A) | 77.388 | 77.2716 | 77.4672 | 77.643 | 78.3075
Gympie Bulk | 3005-1 | Coondoo Ck Reg | Tin Can Bay | Power Factor | 0.99708 | 0.9971 | 0.99706 | 0.99703 | 0.9969
Gympie Bulk | 3005-1 | Coondoo Ck Reg | Tin Can Bay | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
Gympie Bulk | 3005-1 | Coondoo Ck Reg | Tin Can Bay | 50 POE Load (A) | 72.6262 | 72.5178 | 72.7007 | 72.8652 | 73.4855
Gympie Bulk | 3009-1 | Gympie BS | Gympie Nth | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Rural | 170
Gympie Bulk | 3009-1 | Gympie BS | Gympie Nth | 10 POE Load (A) | 138.1537 | 136.9008 | 136.069 | 134.7207 | 134.8875
Gympie Bulk | 3009-1 | Gympie BS | Gympie Nth | Power Factor | 0.99053 | 0.99073 | 0.99086 | 0.99107 | 0.99105
Gympie Bulk | 3009-1 | Gympie BS | Gympie Nth | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
Gympie Bulk | 3009-1 | Gympie BS | Gympie Nth | 50 POE Load (A) | 246 | 246 | 246 | 245 | 245
Gympie Bulk | 3011-1 | Gympie BS | Gympie Nth | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Rural | 170
Gympie Bulk | 3011-1 | Gympie BS | Gympie Nth | 10 POE Load (A) | 138.1917 | 136.9385 | 136.1065 | 134.7578 | 134.9246
Gympie Bulk | 3011-1 | Gympie BS | Gympie Nth | Power Factor | 0.99052 | 0.99072 | 0.99085 | 0.99107 | 0.99104
Gympie Bulk | 3011-1 | Gympie BS | Gympie Nth | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
Gympie Bulk | 3011-1 | Gympie BS | Gympie Nth | 50 POE Load (A) | 246 | 246 | 246 | 245 | 245
Gympie Bulk | 339/2-1 | Amamoor | 339 Tee1 | NCC Rating (A) | 155 | 155 | 155 | 155 | 155 | Rural | 170
Gympie Bulk | 339/2-1 | Amamoor | 339 Tee1 | 10 POE Load (A) | 58.372 | 56.2634 | 55.6716 | 55.6389 | 55.6696
Gympie Bulk | 339/2-1 | Amamoor | 339 Tee1 | Power Factor | 0.9799 | 0.98314 | 0.98407 | 0.9841 | 0.98406
Gympie Bulk | 339/2-1 | Amamoor | 339 Tee1 | ECC Rating (A) | 155 | 155 | 155 | 155 | 155
Gympie Bulk | 339/2-1 | Amamoor | 339 Tee1 | 50 POE Load (A) | 53.6901 | 51.8241 | 51.2978 | 51.2695 | 51.2964
Gympie Bulk | 339/2-2 | 339 Tee1 | Imbil | NCC Rating (A) | 200 | 200 | 200 | 200 | 200 | Rural | 170
Gympie Bulk | 339/2-2 | 339 Tee1 | Imbil | 10 POE Load (A) | 46.1162 | 44.0652 | 43.4917 | 43.4628 | 43.491
Gympie Bulk | 339/2-2 | 339 Tee1 | Imbil | Power Factor | 0.99151 | 0.99444 | 0.99521 | 0.99523 | 0.9952
Gympie Bulk | 339/2-2 | 339 Tee1 | Imbil | ECC Rating (A) | 200 | 200 | 200 | 200 | 200
Gympie Bulk | 339/2-2 | 339 Tee1 | Imbil | 50 POE Load (A) | 41.7284 | 39.9271 | 39.4218 | 39.3971 | 39.4216
Gympie Bulk | 339/2-5 | 339 Tee2 | 340 Tee2 | NCC Rating (A) | 155 | 155 | 155 | 155 | 155 | Rural | 170
Gympie Bulk | 339/2-5 | 339 Tee2 | 340 Tee2 | 10 POE Load (A) | 0.13487 | 0.13511 | 0.13519 | 0.13523 | 0.1352
Gympie Bulk | 339/2-5 | 339 Tee2 | 340 Tee2 | Power Factor | 3.5781e-06 | 3.5781e-06 | 3.5781e-06 | 3.5781e-06 | 3.5781e-06
Gympie Bulk | 339-1 | Gympie BS | 339 Tee1 | NCC Rating (A) | 742 | 742 | 742 | 742 | 742 | Rural | 170
Gympie Bulk | 339-1 | Gympie BS | 339 Tee1 | 10 POE Load (A) | 166.0416 | 163.2217 | 162.3205 | 161.7673 | 162.086
Gympie Bulk | 339-1 | Gympie BS | 339 Tee1 | Power Factor | 0.94975 | 0.95184 | 0.95245 | 0.95258 | 0.9525
Gympie Bulk | 339-1 | Gympie BS | 339 Tee1 | ECC Rating (A) | 742 | 742 | 742 | 742 | 742
Gympie Bulk | 339-1 | Gympie BS | 339 Tee1 | 50 POE Load (A) | 153.5478 | 151.0808 | 150.2744 | 149.7674 | 150.0592
Gympie Bulk | 339-2 | 339 Tee1 | Amamoor | NCC Rating (A) | 210 | 210 | 210 | 210 | 210 | Rural | 170
Gympie Bulk | 339-2 | 339 Tee1 | Amamoor | 10 POE Load (A) | 166.3753 | 163.5506 | 162.6479 | 162.0942 | 162.4132
Gympie Bulk | 339-2 | 339 Tee1 | Amamoor | Power Factor | 0.95864 | 0.96043 | 0.96095 | 0.96104 | 0.96098
Gympie Bulk | 339-2 | 339 Tee1 | Amamoor | ECC Rating (A) | 210 | 210 | 210 | 210 | 210
Gympie Bulk | 339-2 | 339 Tee1 | Amamoor | 50 POE Load (A) | 153.8655 | 151.3947 | 150.5868 | 150.0793 | 150.3715
Gympie Bulk | 339-3 | 339 Tee1 | 340 Tee1 | NCC Rating (A) | 210 | 210 | 210 | 210 | 210 | Rural | 170
Gympie Bulk | 339-3 | 339 Tee1 | 340 Tee1 | 10 POE Load (A) | 0.00034436 | 0.00034436 | 0.00034436 | 0.00034436 | 0.00034436
Gympie Bulk | 339-3 | 339 Tee1 | 340 Tee1 | Power Factor | 0.00059245 | 0.00059346 | 0.00059366 | 0.00059309 | 0.0005932
Gympie Bulk | 340-1 | Gympie BS | 340 Tee1 | NCC Rating (A) | 349 | 349 | 349 | 349 | 349 | Rural | 170
Gympie Bulk | 340-1 | Gympie BS | 340 Tee1 | 10 POE Load (A) | 68.6581 | 72.5029 | 72.1471 | 71.5381 | 71.4887
Gympie Bulk | 340-1 | Gympie BS | 340 Tee1 | Power Factor | 0.96578 | 0.96428 | 0.96442 | 0.96465 | 0.96467
Gympie Bulk | 340-1 | Gympie BS | 340 Tee1 | ECC Rating (A) | 349 | 349 | 349 | 349 | 349
Gympie Bulk | 340-1 | Gympie BS | 340 Tee1 | 50 POE Load (A) | 132 | 132 | 132 | 132 | 132
Gympie Bulk | 340-2 | 340 Tee1 | 339 Tee1 | NCC Rating (A) | 349 | 349 | 349 | 349 | 349 | Rural | 170
Gympie Bulk | 340-2 | 340 Tee1 | 339 Tee1 | 10 POE Load (A) | 0.001928 | 0.001928 | 0.001928 | 0.001928 | 0.001928
Gympie Bulk | 340-2 | 340 Tee1 | 339 Tee1 | Power Factor | 0.00010576 | 0.00010575 | 0.00010583 | 0.00010583 | 0.00010586
Gympie Bulk | 340-4 | 340 Tee1 | 340 Tee2 | NCC Rating (A) | 349 | 349 | 349 | 349 | 349 | Rural | 170
Gympie Bulk | 340-4 | 340 Tee1 | 340 Tee2 | 10 POE Load (A) | 68.7537 | 72.6002 | 72.2442 | 71.6349 | 71.5856
Gympie Bulk | 340-4 | 340 Tee1 | 340 Tee2 | Power Factor | 0.96528 | 0.96385 | 0.96398 | 0.9642 | 0.96422
Gympie Bulk | 340-4 | 340 Tee1 | 340 Tee2 | ECC Rating (A) | 349 | 349 | 349 | 349 | 349
Gympie Bulk | 340-4 | 340 Tee1 | 340 Tee2 | 50 POE Load (A) | 132 | 132 | 132 | 132 | 132
Gympie Bulk | 340-5 | 340 Tee2 | 340 Tee3 | NCC Rating (A) | 328 | 328 | 328 | 328 | 328 | Rural | 170
Gympie Bulk | 340-5 | 340 Tee2 | 340 Tee3 | 10 POE Load (A) | 3.4865 | 3.4857 | 3.4858 | 3.4859 | 3.4859
Gympie Bulk | 340-5 | 340 Tee2 | 340 Tee3 | Power Factor | 0.00076215 | 0.00076215 | 0.00076215 | 0.00076215 | 0.00076215
Gympie Bulk | 340-5 | 340 Tee2 | 340 Tee3 | ECC Rating (A) | 328 | 328 | 328 | 328 | 328
Gympie Bulk | 340-5 | 340 Tee2 | 340 Tee3 | 50 POE Load (A) | 3.4876 | 3.4868 | 3.4868 | 3.487 | 3.487
Gympie Bulk | 340-6 | 340 Tee3 | 339 Tee2 | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Rural | 170
Gympie Bulk | 340-6 | 340 Tee3 | 339 Tee2 | 10 POE Load (A) | 1.5743 | 1.5739 | 1.5739 | 1.574 | 1.574
Gympie Bulk | 340-6 | 340 Tee3 | 339 Tee2 | Power Factor | 0.00014067 | 0.00014067 | 0.00014067 | 0.00014067 | 0.00014067
Gympie Bulk | 340-6 | 340 Tee3 | 339 Tee2 | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
Gympie Bulk | 340-6 | 340 Tee3 | 339 Tee2 | 50 POE Load (A) | 1.5748 | 1.5744 | 1.5744 | 1.5745 | 1.5745
Gympie Bulk | 340-7 | 339 Tee2 | Kenilworth | NCC Rating (A) | 208 | 208 | 208 | 208 | 208 | Rural | 170
Gympie Bulk | 340-7 | 339 Tee2 | Kenilworth | 10 POE Load (A) | 1.5705 | 1.5701 | 1.5702 | 1.5702 | 1.5702
Gympie Bulk | 340-7 | 339 Tee2 | Kenilworth | Power Factor | 0.0001403 | 0.0001403 | 0.0001403 | 0.0001403 | 0.0001403
Gympie Bulk | 340-7 | 339 Tee2 | Kenilworth | ECC Rating (A) | 208 | 208 | 208 | 208 | 208
Gympie Bulk | 340-7 | 339 Tee2 | Kenilworth | 50 POE Load (A) | 1.571 | 1.5706 | 1.5706 | 1.5707 | 1.5707
Gympie Bulk | 340-8 | 340 Tee3 | Black Mountain | NCC Rating (A) | 328 | 328 | 328 | 328 | 328 | Rural | 170
Gympie Bulk | 340-8 | 340 Tee3 | Black Mountain | 10 POE Load (A) | 0.6133 | 0.61316 | 0.61317 | 0.61319 | 0.6132
Gympie Bulk | 340-8 | 340 Tee3 | Black Mountain | Power Factor | 4.3695e-05 | 4.3695e-05 | 4.3695e-05 | 4.3695e-05 | 4.3695e-05
Gympie Bulk | 340-9 | 340 Tee2 | Gympie South | NCC Rating (A) | 403 | 403 | 403 | 403 | 403 | Rural | 170
Gympie Bulk | 340-9 | 340 Tee2 | Gympie South | 10 POE Load (A) | 69.8954 | 73.7545 | 73.3973 | 72.786 | 72.7365
Gympie Bulk | 340-9 | 340 Tee2 | Gympie South | Power Factor | 0.9508 | 0.95003 | 0.9501 | 0.95023 | 0.95024
Gympie Bulk | 340-9 | 340 Tee2 | Gympie South | ECC Rating (A) | 403 | 403 | 403 | 403 | 403
Gympie Bulk | 340-9 | 340 Tee2 | Gympie South | 50 POE Load (A) | 133 | 133 | 133 | 133 | 133
Gympie Bulk | 341-1 | Gympie BS | 341 Tee1 | NCC Rating (A) | 211 | 211 | 211 | 211 | 211 | Rural | 170
Gympie Bulk | 341-1 | Gympie BS | 341 Tee1 | 10 POE Load (A) | 147.5854 | 147.432 | 147.4827 | 147.4961 | 147.8526
Gympie Bulk | 341-1 | Gympie BS | 341 Tee1 | Power Factor | 0.99951 | 0.99951 | 0.9995 | 0.9995 | 0.99949
Gympie Bulk | 341-1 | Gympie BS | 341 Tee1 | ECC Rating (A) | 211 | 211 | 211 | 211 | 211
Gympie Bulk | 341-1 | Gympie BS | 341 Tee1 | 50 POE Load (A) | 142.6232 | 142.4853 | 142.5352 | 142.5519 | 142.8833
Gympie Bulk | 341-2 | 341 Tee1 | Customer | NCC Rating (A) | 410 | 410 | 410 | 410 | 410 | Rural | 170
Gympie Bulk | 341-2 | 341 Tee1 | Customer | 10 POE Load (A) | 75.0503 | 75.0089 | 74.8806 | 74.7347 | 74.4755
Gympie Bulk | 341-2 | 341 Tee1 | Customer | Power Factor | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 1
Gympie Bulk | 341-2 | 341 Tee1 | Customer | ECC Rating (A) | 463 | 463 | 463 | 463 | 463
Gympie Bulk | 341-2 | 341 Tee1 | Customer | 50 POE Load (A) | 236.9671 | 237.5518 | 237.4063 | 236.2456 | 236
Gympie Bulk | 341-3 | 341 Tee1 | Coondoo Ck Reg | NCC Rating (A) | 210 | 210 | 210 | 210 | 210 | Rural | 170
Gympie Bulk | 341-3 | 341 Tee1 | Coondoo Ck Reg | 10 POE Load (A) | 81.0002 | 80.8787 | 81.0828 | 81.2663 | 81.9599
Gympie Bulk | 341-3 | 341 Tee1 | Coondoo Ck Reg | Power Factor | 0.99836 | 0.99838 | 0.99835 | 0.99832 | 0.99821
Gympie Bulk | 341-3 | 341 Tee1 | Coondoo Ck Reg | ECC Rating (A) | 210 | 210 | 210 | 210 | 210
Gympie Bulk | 341-3 | 341 Tee1 | Coondoo Ck Reg | 50 POE Load (A) | 162 | 163 | 162 | 162 | 162
Gympie Bulk | 341-4 | Coondoo Ck Reg | 341 Tee2 | NCC Rating (A) | 717 | 717 | 717 | 717 | 717 | Rural | 170
Gympie Bulk | 341-4 | Coondoo Ck Reg | 341 Tee2 | 10 POE Load (A) | 77.144 | 77.0282 | 77.2226 | 77.3974 | 78.058
Gympie Bulk | 341-4 | Coondoo Ck Reg | 341 Tee2 | Power Factor | 0.99838 | 0.9984 | 0.99836 | 0.99834 | 0.99823
Gympie Bulk | 341-4 | Coondoo Ck Reg | 341 Tee2 | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
Gympie Bulk | 341-4 | Coondoo Ck Reg | 341 Tee2 | 50 POE Load (A) | 138 | 138 | 138 | 138 | 138
Gympie Bulk | 351-1 | Gympie BS | Gympie Sth | NCC Rating (A) | 355 | 355 | 355 | 355 | 355 | Rural | 170
Gympie Bulk | 351-1 | Gympie BS | Gympie Sth | 10 POE Load (A) | 79.1493 | 83.5727 | 83.1633 | 82.4626 | 82.4059
Gympie Bulk | 351-1 | Gympie BS | Gympie Sth | Power Factor | 0.96146 | 0.9599 | 0.96004 | 0.96028 | 0.9603
Gympie Bulk | 351-1 | Gympie BS | Gympie Sth | ECC Rating (A) | 355 | 355 | 355 | 355 | 355
Gympie Bulk | 351-1 | Gympie BS | Gympie Sth | 50 POE Load (A) | 133 | 133 | 133 | 133 | 133
Gympie Bulk | 429-1 | Gympie BS | 429 Tee1 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
Gympie Bulk | 429-1 | Gympie BS | 429 Tee1 | 10 POE Load (A) | 213.4677 | 213.084 | 213.0447 | 212.9035 | 213.3791
Gympie Bulk | 429-1 | Gympie BS | 429 Tee1 | Power Factor | 0.95731 | 0.95731 | 0.95726 | 0.95721 | 0.95708
Gympie Bulk | 429-1 | Gympie BS | 429 Tee1 | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Gympie Bulk | 429-1 | Gympie BS | 429 Tee1 | 50 POE Load (A) | 204.3204 | 203.9791 | 203.9509 | 203.8324 | 204.2725
Gympie Bulk | 429-2 | 429 Tee1 | Goomboorian | NCC Rating (A) | 461 | 461 | 461 | 461 | 461 | Rural | 170
Gympie Bulk | 429-2 | 429 Tee1 | Goomboorian | 10 POE Load (A) | 52.3879 | 51.991 | 51.7884 | 51.4719 | 51.5586
Gympie Bulk | 429-2 | 429 Tee1 | Goomboorian | Power Factor | 0.99431 | 0.99434 | 0.99436 | 0.99438 | 0.99437
Gympie Bulk | 429-2 | 429 Tee1 | Goomboorian | ECC Rating (A) | 461 | 461 | 461 | 461 | 461
Gympie Bulk | 429-2 | 429 Tee1 | Goomboorian | 50 POE Load (A) | 46.2676 | 45.9178 | 45.7392 | 45.4601 | 45.5362
Gympie Bulk | 429-3 | 429 Tee1 | Toolara Forest | NCC Rating (A) | 410 | 410 | 410 | 410 | 410 | Rural | 170
Gympie Bulk | 429-3 | 429 Tee1 | Toolara Forest | 10 POE Load (A) | 162.2731 | 162.2818 | 162.4442 | 162.6175 | 163.0112
Gympie Bulk | 429-3 | 429 Tee1 | Toolara Forest | Power Factor | 0.96019 | 0.96025 | 0.96025 | 0.96027 | 0.96018
Gympie Bulk | 429-3 | 429 Tee1 | Toolara Forest | ECC Rating (A) | 463 | 463 | 463 | 463 | 463
Gympie Bulk | 429-3 | 429 Tee1 | Toolara Forest | 50 POE Load (A) | 244 | 245 | 245 | 243 | 240
Hays Inlet Bulk | 305-1 | Hays Inlet BS | Deception Bay | NCC Rating (A) | 759 | 759 | 759 | 759 | 759 | Urban | 266 | 0.5
Hays Inlet Bulk | 305-1 | Hays Inlet BS | Deception Bay | 10 POE Load (A) | 722.7033 | 724.7579 | 729.7297 | 733.7683 | 743.0297
Hays Inlet Bulk | 305-1 | Hays Inlet BS | Deception Bay | Power Factor | 0.96666 | 0.96656 | 0.96643 | 0.96622 | 0.96573
Hays Inlet Bulk | 305-1 | Hays Inlet BS | Deception Bay | ECC Rating (A) | 759 | 759 | 759 | 759 | 759
Hays Inlet Bulk | 305-1 | Hays Inlet BS | Deception Bay | 50 POE Load (A) | 980 | 988 | 992 | 996 | 1000
Hays Inlet Bulk | 311-1 | Hays Inlet BS | Deception Bay | NCC Rating (A) | 623 | 623 | 623 | 623 | 623 | Urban | 154 | 0.5
Hays Inlet Bulk | 311-1 | Hays Inlet BS | Deception Bay | 10 POE Load (A) | 238.5056 | 239.1842 | 240.8272 | 242.1611 | 245.2201
Hays Inlet Bulk | 311-1 | Hays Inlet BS | Deception Bay | Power Factor | -0.97471 | -0.97461 | -0.97447 | -0.97428 | -0.97384
Hays Inlet Bulk | 311-1 | Hays Inlet BS | Deception Bay | ECC Rating (A) | 623 | 623 | 623 | 623 | 623
Hays Inlet Bulk | 311-1 | Hays Inlet BS | Deception Bay | 50 POE Load (A) | 717 | 722 | 724 | 726 | 713.1241
Hays Inlet Bulk | 3250-1 | Deception Bay | Burpengary | NCC Rating (A) | 713 | 713 | 713 | 713 | 713 | Urban | 256 | 0.5
Hays Inlet Bulk | 3250-1 | Deception Bay | Burpengary | 10 POE Load (A) | 446.73 | 448.1268 | 452.0429 | 455.5418 | 462.3216
Hays Inlet Bulk | 3250-1 | Deception Bay | Burpengary | Power Factor | 0.98158 | 0.98151 | 0.98154 | 0.98136 | 0.98101
Hays Inlet Bulk | 3250-1 | Deception Bay | Burpengary | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
Hays Inlet Bulk | 3250-1 | Deception Bay | Burpengary | 50 POE Load (A) | 875.2995 | 878.6034 | 886.9491 | 894.2574 | 907.9211
Hays Inlet Bulk | 325-1 | Hays Inlet BS | Scarborough | NCC Rating (A) | 529 | 529 | 529 | 529 | 529 | Urban | 70
Hays Inlet Bulk | 325-1 | Hays Inlet BS | Scarborough | 10 POE Load (A) | 331.7692 | 333.4986 | 336.5843 | 338.0614 | 343.2884
Hays Inlet Bulk | 325-1 | Hays Inlet BS | Scarborough | Power Factor | 0.98796 | 0.98803 | 0.98797 | 0.98799 | 0.98794
Hays Inlet Bulk | 325-1 | Hays Inlet BS | Scarborough | ECC Rating (A) | 529 | 529 | 529 | 529 | 529
Hays Inlet Bulk | 325-1 | Hays Inlet BS | Scarborough | 50 POE Load (A) | 405 | 410 | 412 | 414 | 416
Hays Inlet Bulk | 3251-1 | Burpengary | Morayfield | NCC Rating (A) | 464 | 464 | 464 | 464 | 464 | Rural | 170
Hays Inlet Bulk | 3251-1 | Burpengary | Morayfield | 10 POE Load (A) | 1.1894 | 1.1893 | 1.1889 | 1.1885 | 1.1876
Hays Inlet Bulk | 3251-1 | Burpengary | Morayfield | Power Factor | 4.3774e-07 | 4.3775e-07 | 4.3774e-07 | 4.3774e-07 | 4.3786e-07
Hays Inlet Bulk | 3251-1 | Burpengary | Morayfield | ECC Rating (A) | 464 | 464 | 464 | 464 | 464
Hays Inlet Bulk | 3251-1 | Burpengary | Morayfield | 50 POE Load (A) | 598.3691 | 613.2489 | 623.4124 | 632.6397 | 646.1492
Hays Inlet Bulk | 326-1 | Redcliffe | Scarborough | NCC Rating (A) | 322 | 322 | 322 | 322 | 322 | Urban | 70
Hays Inlet Bulk | 326-1 | Redcliffe | Scarborough | 10 POE Load (A) | 58.7799 | 61.1654 | 64.2677 | 67.1591 | 70.855
Hays Inlet Bulk | 326-1 | Redcliffe | Scarborough | Power Factor | 0.99911 | 0.99866 | 0.99825 | 0.99774 | 0.99711
Hays Inlet Bulk | 326-1 | Redcliffe | Scarborough | ECC Rating (A) | 322 | 322 | 322 | 322 | 322
Hays Inlet Bulk | 326-1 | Redcliffe | Scarborough | 50 POE Load (A) | 49.5563 | 51.6801 | 54.4626 | 57.0503 | 60.195
Hays Inlet Bulk | 327-1 | Hays Inlet BS | Mango Hill Bus 1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Hays Inlet Bulk | 327-1 | Hays Inlet BS | Mango Hill Bus 1 | 10 POE Load (A) | 469.8784 | 479.9059 | 491.5477 | 501.9176 | 518.0554
Hays Inlet Bulk | 327-1 | Hays Inlet BS | Mango Hill Bus 1 | Power Factor | -0.96287 | -0.96154 | -0.95996 | -0.96016 | -0.95798
Hays Inlet Bulk | 327-1 | Hays Inlet BS | Mango Hill Bus 1 | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Hays Inlet Bulk | 327-1 | Hays Inlet BS | Mango Hill Bus 1 | 50 POE Load (A) | 420.0182 | 428.829 | 439.0447 | 449.0854 | 463.2988
Hays Inlet Bulk | 329-1 | Redcliffe | Duffield Rd | NCC Rating (A) | 578 | 578 | 578 | 578 | 578 | Urban | 70
Hays Inlet Bulk | 329-1 | Redcliffe | Duffield Rd | 10 POE Load (A) | 124.9057 | 126.2538 | 127.684 | 128.4112 | 130.2141
Hays Inlet Bulk | 329-1 | Redcliffe | Duffield Rd | Power Factor | 0.97543 | 0.97533 | 0.97223 | 0.97542 | 0.97222
Hays Inlet Bulk | 329-1 | Redcliffe | Duffield Rd | ECC Rating (A) | 578 | 578 | 578 | 578 | 578
Hays Inlet Bulk | 329-1 | Redcliffe | Duffield Rd | 50 POE Load (A) | 258 | 260 | 262 | 264 | 266
Hays Inlet Bulk | 330-1 | Hays Inlet BS | Duffield Rd | NCC Rating (A) | 543 | 543 | 543 | 543 | 543 | Urban | 70
Hays Inlet Bulk | 330-1 | Hays Inlet BS | Duffield Rd | 10 POE Load (A) | 285.6951 | 285.9406 | 287.1937 | 287.5792 | 290.9291
Hays Inlet Bulk | 330-1 | Hays Inlet BS | Duffield Rd | Power Factor | -0.96326 | -0.96328 | -0.96245 | -0.96323 | -0.96211
Hays Inlet Bulk | 330-1 | Hays Inlet BS | Duffield Rd | ECC Rating (A) | 578 | 578 | 578 | 578 | 578
Hays Inlet Bulk | 330-1 | Hays Inlet BS | Duffield Rd | 50 POE Load (A) | 396 | 398 | 399 | 399 | 403
Hays Inlet Bulk | 331-1 | Hays Inlet BS | Duffield Rd | NCC Rating (A) | 430 | 430 | 430 | 430 | 430 | Urban | 70
Hays Inlet Bulk | 331-1 | Hays Inlet BS | Duffield Rd | 10 POE Load (A) | 287.1934 | 287.4401 | 288.6998 | 289.0874 | 292.4549
Hays Inlet Bulk | 331-1 | Hays Inlet BS | Duffield Rd | Power Factor | -0.9586 | -0.95863 | -0.95775 | -0.95857 | -0.95739
Hays Inlet Bulk | 331-1 | Hays Inlet BS | Duffield Rd | ECC Rating (A) | 573 | 573 | 573 | 573 | 573
Hays Inlet Bulk | 331-1 | Hays Inlet BS | Duffield Rd | 50 POE Load (A) | 396 | 397 | 398 | 398 | 404
Hays Inlet Bulk | 332-1 | Hays Inlet BS | Redcliffe | NCC Rating (A) | 524 | 524 | 524 | 524 | 524 | Urban | 70
Hays Inlet Bulk | 332-1 | Hays Inlet BS | Redcliffe | 10 POE Load (A) | 311.8965 | 312.8324 | 315.0422 | 315.3908 | 319.5223
Hays Inlet Bulk | 332-1 | Hays Inlet BS | Redcliffe | Power Factor | 0.96384 | 0.96396 | 0.96377 | 0.96376 | 0.96356
Hays Inlet Bulk | 332-1 | Hays Inlet BS | Redcliffe | ECC Rating (A) | 524 | 524 | 524 | 524 | 524
Hays Inlet Bulk | 332-1 | Hays Inlet BS | Redcliffe | 50 POE Load (A) | 282.2814 | 283.1064 | 284.5551 | 285.367 | 288.4954
Hays Inlet Bulk | 451-1 | Narangba | Burpengary | NCC Rating (A) | 422 | 422 | 422 | 422 | 422 | Urban | 70
Hays Inlet Bulk | 451-1 | Narangba | Burpengary | 10 POE Load (A) | 52.0023 | 51.0418 | 50.4291 | 49.3362 | 48.6298
Hays Inlet Bulk | 451-1 | Narangba | Burpengary | Power Factor | 0.96679 | 0.96712 | 0.96509 | 0.96535 | 0.96534
Hays Inlet Bulk | 451-1 | Narangba | Burpengary | ECC Rating (A) | 422 | 422 | 422 | 422 | 422
Hays Inlet Bulk | 451-1 | Narangba | Burpengary | 50 POE Load (A) | 42.4932 | 41.5884 | 40.8316 | 39.7728 | 39.0251
Hays Inlet Bulk | 497-1 | Hays Inlet BS | Narangba | NCC Rating (A) | 713 | 713 | 713 | 713 | 713 | Rural | 300
Hays Inlet Bulk | 497-1 | Hays Inlet BS | Narangba | 10 POE Load (A) | 502.0726 | 504.2244 | 508.9297 | 513.3304 | 521.3963
Hays Inlet Bulk | 497-1 | Hays Inlet BS | Narangba | Power Factor | -0.96166 | -0.9615 | -0.9615 | -0.96117 | -0.96054
Hays Inlet Bulk | 497-1 | Hays Inlet BS | Narangba | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
Hays Inlet Bulk | 497-1 | Hays Inlet BS | Narangba | 50 POE Load (A) | 931.851 | 935.8673 | 945.043 | 953.2193 | 968.146
Jimboomba Bulk | 470-1 | Jimboomba BS | Logan Village | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Rural | 170
Jimboomba Bulk | 470-1 | Jimboomba BS | Logan Village | 10 POE Load (A) | 388.7819 | 397.8383 | 408.5457 | 417.9745 | 430.5239
Jimboomba Bulk | 470-1 | Jimboomba BS | Logan Village | Power Factor | 0.97944 | 0.9786 | 0.97758 | 0.97658 | 0.9765
Jimboomba Bulk | 479-1 | Jimboomba BS | Nth Maclean | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Jimboomba Bulk | 479-1 | Jimboomba BS | Nth Maclean | 10 POE Load (A) | 648.6218 | 648.6926 | 667.1772 | 687.0899 | 712.0852
Jimboomba Bulk | 479-1 | Jimboomba BS | Nth Maclean | Power Factor | 0.96567 | 0.96566 | 0.96556 | 0.96431 | 0.96269
Jimboomba Bulk | 479-1 | Jimboomba BS | Nth Maclean | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Jimboomba Bulk | 479-1 | Jimboomba BS | Nth Maclean | 50 POE Load (A) | 595.6815 | 594.6893 | 611.3812 | 629.1631 | 651.4133
Lockrose Bulk | 378-1 | Lockrose BS | 378 Tee1 | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
Lockrose Bulk | 378-1 | Lockrose BS | 378 Tee1 | 10 POE Load (A) | 221.4855 | 221.242 | 235.0647 | 248.5645 | 281.9444
Lockrose Bulk | 378-1 | Lockrose BS | 378 Tee1 | Power Factor | -0.95717 | -0.9572 | -0.95278 | -0.94875 | -0.93944
Lockrose Bulk | 378-1 | Lockrose BS | 378 Tee1 | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
Lockrose Bulk | 378-1 | Lockrose BS | 378 Tee1 | 50 POE Load (A) | 341 | 345 | 347 | 349 | 354
Lockrose Bulk | 378-2 | 378 Tee1 | Glenmore Grove | NCC Rating (A) | 442 | 442 | 442 | 442 | 442 | Rural | 170
Lockrose Bulk | 378-2 | 378 Tee1 | Glenmore Grove | 10 POE Load (A) | 85.7897 | 85.5027 | 85.5294 | 85.5149 | 91.6015
Lockrose Bulk | 378-2 | 378 Tee1 | Glenmore Grove | Power Factor | -0.99112 | -0.99123 | -0.99125 | -0.99147 | -0.9893
Lockrose Bulk | 378-2 | 378 Tee1 | Glenmore Grove | ECC Rating (A) | 442 | 442 | 442 | 442 | 442
Lockrose Bulk | 378-2 | 378 Tee1 | Glenmore Grove | 50 POE Load (A) | 80.9822 | 80.7122 | 80.7509 | 80.7285 | 86.6683
Lockrose Bulk | 378-3 | 378 Tee1 | 378 Tee2 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Lockrose Bulk | 378-3 | 378 Tee1 | 378 Tee2 | 10 POE Load (A) | 137.613 | 137.6639 | 151.7385 | 165.4756 | 193.1302
Lockrose Bulk | 378-3 | 378 Tee1 | 378 Tee2 | Power Factor | 0.93452 | 0.93451 | 0.93065 | 0.92639 | 0.91854
Lockrose Bulk | 378-3 | 378 Tee1 | 378 Tee2 | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Lockrose Bulk | 378-3 | 378 Tee1 | 378 Tee2 | 50 POE Load (A) | 229 | 232 | 234 | 236 | 245
Lockrose Bulk | 378-4 | 378 Tee2 | 532 Tee1 | NCC Rating (A) | 200 | 200 | 200 | 200 | 200 | Rural | 170
Lockrose Bulk | 378-4 | 378 Tee2 | 532 Tee1 | 10 POE Load (A) | 0.87574 | 0.87575 | 0.87127 | 0.86674 | 0.85693
Lockrose Bulk | 378-4 | 378 Tee2 | 532 Tee1 | Power Factor | -5.6276e-06 | -5.6276e-06 | -5.6276e-06 | -5.6276e-06 | -5.6276e-06
Lockrose Bulk | 378-5 | 378 Tee2 | Laidley | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Lockrose Bulk | 378-5 | 378 Tee2 | Laidley | 10 POE Load (A) | 137.9358 | 137.9868 | 152.0683 | 165.8094 | 193.4737
Lockrose Bulk | 378-5 | 378 Tee2 | Laidley | Power Factor | 0.94023 | 0.94022 | 0.93793 | 0.93535 | 0.93076
Lockrose Bulk | 378-5 | 378 Tee2 | Laidley | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Lockrose Bulk | 378-5 | 378 Tee2 | Laidley | 50 POE Load (A) | 229 | 232 | 234 | 236 | 245
Lockrose Bulk | 380-1 | Murrumba | 380 Tee1 | NCC Rating (A) | 200 | 200 | 200 | 200 | 200 | Rural | 170
Lockrose Bulk | 380-1 | Murrumba | 380 Tee1 | 10 POE Load (A) | 68.2419 | 68.0325 | 68.1698 | 68.3896 | 69.1147
Lockrose Bulk | 380-1 | Murrumba | 380 Tee1 | Power Factor | 0.98679 | 0.98693 | 0.98682 | 0.98674 | 0.98633
Lockrose Bulk | 380-1 | Murrumba | 380 Tee1 | ECC Rating (A) | 200 | 200 | 200 | 200 | 200
Lockrose Bulk | 380-1 | Murrumba | 380 Tee1 | 50 POE Load (A) | 163 | 164 | 164 | 165 | 165
Lockrose Bulk | 380-2 | 380 Tee1 | Somerset Dam | NCC Rating (A) | 160 | 160 | 160 | 160 | 160 | Rural | 170
Lockrose Bulk | 380-2 | 380 Tee1 | Somerset Dam | 10 POE Load (A) | 7.468 | 7.5488 | 7.6283 | 7.7249 | 7.844
Lockrose Bulk | 380-2 | 380 Tee1 | Somerset Dam | Power Factor | 0.99394 | 0.99388 | 0.99383 | 0.99375 | 0.99365
Lockrose Bulk | 380-2 | 380 Tee1 | Somerset Dam | ECC Rating (A) | 160 | 160 | 160 | 160 | 160
Lockrose Bulk | 380-2 | 380 Tee1 | Somerset Dam | 50 POE Load (A) | 7.0173 | 7.0937 | 7.1682 | 7.2203 | 7.3274
Lockrose Bulk | 380-3 | 380 Tee1 | Toogoolahwah | NCC Rating (A) | 200 | 200 | 200 | 200 | 200 | Rural | 170
Lockrose Bulk | 380-3 | 380 Tee1 | Toogoolahwah | 10 POE Load (A) | 61.0411 | 60.7498 | 60.8087 | 60.9321 | 61.5409
Lockrose Bulk | 380-3 | 380 Tee1 | Toogoolahwah | Power Factor | 0.98516 | 0.98531 | 0.98518 | 0.98512 | 0.98469
Lockrose Bulk | 380-3 | 380 Tee1 | Toogoolahwah | ECC Rating (A) | 200 | 200 | 200 | 200 | 200
Lockrose Bulk | 380-3 | 380 Tee1 | Toogoolahwah | 50 POE Load (A) | 156 | 157 | 157 | 158 | 158
Lockrose Bulk | 381-1 | Lockrose BS | 381 Tee1 | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
Lockrose Bulk | 381-1 | Lockrose BS | 381 Tee1 | 10 POE Load (A) | 209.44 | 209.5074 | 209.7121 | 219.642 | 231.6522
Lockrose Bulk | 381-1 | Lockrose BS | 381 Tee1 | Power Factor | 0.97437 | 0.97441 | 0.97438 | 0.97242 | 0.96978
Lockrose Bulk | 381-1 | Lockrose BS | 381 Tee1 | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
Lockrose Bulk | 381-1 | Lockrose BS | 381 Tee1 | 50 POE Load (A) | 389 | 389 | 390 | 390 | 395
Lockrose Bulk | 381-2 | 381 Tee1 | 382 Tee1 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
Lockrose Bulk | 381-2 | 381 Tee1 | 382 Tee1 | 10 POE Load (A) | 0.005965 | 0.005965 | 0.005965 | 0.005964 | 0.0059628
Lockrose Bulk | 381-2 | 381 Tee1 | 382 Tee1 | Power Factor | -1 | -1 | -1 | -1 | -1
Lockrose Bulk | 381-3 | 381 Tee1 | 381 Tee2 | NCC Rating (A) | 200 | 200 | 200 | 200 | 200 | Rural | 170
Lockrose Bulk | 381-3 | 381 Tee1 | 381 Tee2 | 10 POE Load (A) | 209.5386 | 209.6059 | 209.8107 | 219.7437 | 231.7576
Lockrose Bulk | 381-3 | 381 Tee1 | 381 Tee2 | Power Factor | 0.97887 | 0.97891 | 0.97889 | 0.97735 | 0.97525
Lockrose Bulk | 381-3 | 381 Tee1 | 381 Tee2 | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
Lockrose Bulk | 381-3 | 381 Tee1 | 381 Tee2 | 50 POE Load (A) | 389 | 389 | 390 | 390 | 390
Lockrose Bulk | 381-4 | 381 Tee2 | 383 Tee1 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
Lockrose Bulk | 381-4 | 381 Tee2 | 383 Tee1 | 10 POE Load (A) | 0.0057581 | 0.005758 | 0.0057578 | 0.0057484 | 0.0057368
Lockrose Bulk | 381-4 | 381 Tee2 | 383 Tee1 | Power Factor | 3.3851e-05 | 3.3859e-05 | 3.3857e-05 | 3.3854e-05 | 3.3854e-05
Lockrose Bulk | 381-5 | 381 Tee2 | 381 Tee3 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
Lockrose Bulk | 381-5 | 381 Tee2 | 381 Tee3 | 10 POE Load (A) | 209.6704 | 209.7374 | 209.9422 | 219.8788 | 231.8971
Lockrose Bulk | 381-5 | 381 Tee2 | 381 Tee3 | Power Factor | 0.97899 | 0.97903 | 0.97901 | 0.97749 | 0.97541
Lockrose Bulk | 381-5 | 381 Tee2 | 381 Tee3 | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Lockrose Bulk | 381-5 | 381 Tee2 | 381 Tee3 | 50 POE Load (A) | 389 | 389 | 390 | 390 | 390
Lockrose Bulk | 381-6 | 381 Tee3 | Coominya TR2 | NCC Rating (A) | 403 | 403 | 403 | 403 | 403 | Rural | 170
Lockrose Bulk | 381-6 | 381 Tee3 | Coominya TR2 | 10 POE Load (A) | 65.9113 | 66.2922 | 66.4887 | 73.8111 | 82.0421
Lockrose Bulk | 381-6 | 381 Tee3 | Coominya TR2 | Power Factor | 0.99899 | 0.99893 | 0.9989 | 0.99754 | 0.99586
Lockrose Bulk | 381-6 | 381 Tee3 | Coominya TR2 | ECC Rating (A) | 403 | 403 | 403 | 403 | 403
Lockrose Bulk | 381-6 | 381 Tee3 | Coominya TR2 | 50 POE Load (A) | 65.1132 | 65.4899 | 65.6835 | 70.509 | 78.5919
Lockrose Bulk | 381-7 | 381 Tee3 | 381 Tee4 | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170
Lockrose Bulk | 381-7 | 381 Tee3 | 381 Tee4 | 10 POE Load (A) | 144.9401 | 144.616 | 144.6204 | 147.4674 | 151.5658
Lockrose Bulk | 381-7 | 381 Tee3 | 381 Tee4 | Power Factor | 0.9724 | 0.97254 | 0.97256 | 0.97237 | 0.97181
Lockrose Bulk | 381-7 | 381 Tee3 | 381 Tee4 | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
Lockrose Bulk | 381-7 | 381 Tee3 | 381 Tee4 | 50 POE Load (A) | 304 | 304 | 305 | 305 | 305
Lockrose Bulk | 381-8 | 381 Tee4 | Coominya TR1 | NCC Rating (A) | 403 | 403 | 403 | 403 | 403 | Rural | 170
Lockrose Bulk | 381-8 | 381 Tee4 | Coominya TR1 | 10 POE Load (A) | 65.9065 | 66.287 | 66.4832 | 73.7972 | 82.012
Lockrose Bulk | 381-8 | 381 Tee4 | Coominya TR1 | Power Factor | 0.999 | 0.99894 | 0.9989 | 0.9976 | 0.99588
Lockrose Bulk | 381-8 | 381 Tee4 | Coominya TR1 | ECC Rating (A) | 403 | 403 | 403 | 403 | 403
Lockrose Bulk | 381-8 | 381 Tee4 | Coominya TR1 | 50 POE Load (A) | 65.1098 | 65.4856 | 65.6786 | 70.4981 | 78.5692
Lockrose Bulk | 381-9 | 381 Tee4 | Paddys Gully | NCC Rating (A) | 200 | 200 | 200 | 200 | 200 | Rural | 170
Lockrose Bulk | 381-9 | 381 Tee4 | Paddys Gully | 10 POE Load (A) | 81.9393 | 81.2206 | 81.0248 | 76.7868 | 72.9467
Lockrose Bulk | 381-9 | 381 Tee4 | Paddys Gully | Power Factor | 0.92686 | 0.92678 | 0.92668 | 0.92376 | 0.92025
Lockrose Bulk | 381-9 | 381 Tee4 | Paddys Gully | ECC Rating (A) | 200 | 200 | 200 | 200 | 200
Lockrose Bulk | 381-9 | 381 Tee4 | Paddys Gully | 50 POE Load (A) | 246 | 246 | 246 | 246 | 246
Lockrose Bulk | 382-1 | Lockrose BS | 382 Tee1 | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
Lockrose Bulk | 382-1 | Lockrose BS | 382 Tee1 | 10 POE Load (A) | 183.9302 | 183.6003 | 183.636 | 188.1397 | 194.2552
Lockrose Bulk | 382-1 | Lockrose BS | 382 Tee1 | Power Factor | 0.97147 | 0.97159 | 0.97159 | 0.97058 | 0.96898
Lockrose Bulk | 382-1 | Lockrose BS | 382 Tee1 | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
Lockrose Bulk | 382-1 | Lockrose BS | 382 Tee1 | 50 POE Load (A) | 224 | 224 | 224 | 225 | 245
Lockrose Bulk | 382-2 | 382 Tee1 | 381 Tee1 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
Lockrose Bulk | 382-2 | 382 Tee1 | 381 Tee1 | 10 POE Load (A) | 0.010295 | 0.010295 | 0.010295 | 0.010295 | 0.010294
Lockrose Bulk | 382-2 | 382 Tee1 | 381 Tee1 | Power Factor | 1.9416e-05 | 1.9415e-05 | 1.9415e-05 | 1.9415e-05 | 1.9413e-05
Lockrose Bulk | 382-3 | 382 Tee1 | Paddys Gully | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
Lockrose Bulk | 382-3 | 382 Tee1 | Paddys Gully | 10 POE Load (A) | 184.2851 | 183.9543 | 183.99 | 188.4983 | 194.6208
Lockrose Bulk | 382-3 | 382 Tee1 | Paddys Gully | Power Factor | 0.98468 | 0.98477 | 0.98477 | 0.98442 | 0.98384
Lockrose Bulk | 382-3 | 382 Tee1 | Paddys Gully | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
Lockrose Bulk | 382-3 | 382 Tee1 | Paddys Gully | 50 POE Load (A) | 168.0546 | 167.7995 | 167.83 | 169.4595 | 175.2876
Lockrose Bulk | 3828-1 | Paddy's Gully | Esk | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Rural | 170
Lockrose Bulk | 3828-1 | Paddy's Gully | Esk | 10 POE Load (A) | 129.4026 | 128.5645 | 128.3782 | 128.4828 | 129.6133
Lockrose Bulk | 3828-1 | Paddy's Gully | Esk | Power Factor | 0.98137 | 0.98155 | 0.98159 | 0.98156 | 0.98141
Lockrose Bulk | 3828-1 | Paddy's Gully | Esk | ECC Rating (A) | 155 | 400 | 400 | 400 | 400
Lockrose Bulk | 3828-1 | Paddy's Gully | Esk | 50 POE Load (A) | 219 | 212 | 213 | 213 | 213
Lockrose Bulk | 3829-1 | Paddy's Gully | Murrumba | NCC Rating (A) | 155 | 155 | 155 | 155 | 155 | Rural | 170
Lockrose Bulk | 3829-1 | Paddy's Gully | Murrumba | 10 POE Load (A) | 122.821 | 122.6638 | 122.6983 | 122.8224 | 123.8284
Lockrose Bulk | 3829-1 | Paddy's Gully | Murrumba | Power Factor | 0.96252 | 0.96259 | 0.96256 | 0.96251 | 0.96213
Lockrose Bulk | 3829-1 | Paddy's Gully | Murrumba | ECC Rating (A) | 155 | 155 | 155 | 155 | 155
Lockrose Bulk | 3829-1 | Paddy's Gully | Murrumba | 50 POE Load (A) | 211 | 213 | 213 | 213 | 213
Lockrose Bulk | 3831-1 | Lockrose BS | Tarampa | NCC Rating (A) | 355 | 355 | 355 | 355 | 355 | Rural | 170
Lockrose Bulk | 3831-1 | Lockrose BS | Tarampa | 10 POE Load (A) | 183.9657 | 183.8124 | 184.6748 | 185.0377 | 186.6753
Lockrose Bulk | 3831-1 | Lockrose BS | Tarampa | Power Factor | 0.95491 | 0.95493 | 0.95485 | 0.95482 | 0.95468
Lockrose Bulk | 3831-1 | Lockrose BS | Tarampa | ECC Rating (A) | 355 | 355 | 355 | 355 | 355
Lockrose Bulk | 3831-1 | Lockrose BS | Tarampa | 50 POE Load (A) | 162.3641 | 162.23 | 162.9843 | 163.3016 | 164.7334
Lockrose Bulk | 3832-1 | Tarampa | 383 Tee1 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
Lockrose Bulk | 3832-1 | Tarampa | 383 Tee1 | 10 POE Load (A) | 0.0051241 | 0.0051256 | 0.0051254 | 0.0051262 | 0.0051249
Lockrose Bulk | 3832-1 | Tarampa | 383 Tee1 | Power Factor | -1 | -1 | -1 | -1 | -1
Lockrose Bulk | 3832-2 | 3832 Tee1 | 381 Tee1 | NCC Rating (A) | 155 | 700 | 700 | 700 | 700 | Rural | 170
Lockrose Bulk | 3832-2 | 3832 Tee1 | 381 Tee1 | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lockrose Bulk | 3832-2 | 3832 Tee1 | 381 Tee1 | Power Factor | 0 | 0 | 0 | 0 | 0
Lockrose Bulk | 3832-3 | 3832 Tee1 | Lowood | NCC Rating (A) | 434 | 434 | 434 | 434 | 434 | Rural | 170
Lockrose Bulk | 3832-3 | 3832 Tee1 | Lowood | 10 POE Load (A) | 0.72429 | 0.72451 | 0.72448 | 0.72459 | 0.72442
Lockrose Bulk | 3832-3 | 3832 Tee1 | Lowood | Power Factor | -8.0548e-06 | -8.0547e-06 | -8.0546e-06 | -8.0547e-06 | -8.0548e-06
Lockrose Bulk | 3832-3 | 3832 Tee1 | Lowood | ECC Rating (A) | 434 | 434 | 434 | 434 | 434
Lockrose Bulk | 3832-3 | 3832 Tee1 | Lowood | 50 POE Load (A) | 0.731 | 0.73117 | 0.73115 | 0.73124 | 0.7311
Lockrose Bulk | 3840-1 | Esk | Toogoolawah | NCC Rating (A) | 155 | 155 | 155 | 155 | 155 | Rural | 170
Lockrose Bulk | 3840-1 | Esk | Toogoolawah | 10 POE Load (A) | 59.7279 | 59.6023 | 59.7507 | 59.9227 | 60.5563
Lockrose Bulk | 3840-1 | Esk | Toogoolawah | Power Factor | 0.98948 | 0.9896 | 0.98957 | 0.98953 | 0.98918
Lockrose Bulk | 3840-1 | Esk | Toogoolawah | ECC Rating (A) | 155 | 155 | 155 | 155 | 155
Lockrose Bulk | 3840-1 | Esk | Toogoolawah | 50 POE Load (A) | 161 | 155 | 156 | 156 | 156
Lockrose Bulk | 384-1 | Lockrose BS | 384 Tee1 | NCC Rating (A) | 451 | 451 | 451 | 451 | 451 | Rural | 170
Lockrose Bulk | 384-1 | Lockrose BS | 384 Tee1 | 10 POE Load (A) | 231.4944 | 231.243 | 245.7189 | 259.7973 | 294.5936
Lockrose Bulk | 384-1 | Lockrose BS | 384 Tee1 | Power Factor | -0.98307 | -0.98311 | -0.98125 | -0.9795 | -0.97464
Lockrose Bulk | 384-1 | Lockrose BS | 384 Tee1 | ECC Rating (A) | 451 | 451 | 451 | 451 | 451
Lockrose Bulk | 384-1 | Lockrose BS | 384 Tee1 | 50 POE Load (A) | 207.4857 | 207.251 | 220.9932 | 234.4205 | 267.5397
Lockrose Bulk | 384-2 | 384 Tee1 | Glenmore Grove | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
Lockrose Bulk | 384-2 | 384 Tee1 | Glenmore Grove | 10 POE Load (A) | 85.5076 | 85.2212 | 85.2391 | 85.1915 | 91.1949
Lockrose Bulk | 384-2 | 384 Tee1 | Glenmore Grove | Power Factor | 0.99192 | 0.99203 | 0.99204 | 0.99208 | 0.99001
Lockrose Bulk | 384-2 | 384 Tee1 | Glenmore Grove | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
Lockrose Bulk | 384-2 | 384 Tee1 | Glenmore Grove | 50 POE Load (A) | 80.7498 | 80.4802 | 80.4882 | 80.4357 | 86.3212
Lockrose Bulk | 384-3 | 384 Tee1 | Laidley1 | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Rural | 170
Lockrose Bulk | 384-3 | 384 Tee1 | Laidley1 | 10 POE Load (A) | 146.3946 | 146.433 | 160.9802 | 175.1879 | 204.0913
Lockrose Bulk | 384-3 | 384 Tee1 | Laidley1 | Power Factor | 0.98273 | 0.98273 | 0.98139 | 0.97993 | 0.97715
Lockrose Bulk | 384-3 | 384 Tee1 | Laidley1 | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
Lockrose Bulk | 384-3 | 384 Tee1 | Laidley1 | 50 POE Load (A) | 229 | 232 | 235 | 236 | 236
Lockrose Bulk | 3870-1 | Lockrose BS | Lowood | NCC Rating (A) | 703 | 703 | 703 | 703 | 703 | Rural | 170
Lockrose Bulk | 3870-1 | Lockrose BS | Lowood | 10 POE Load (A) | 235.8495 | 234.5879 | 234.7911 | 234.1376 | 235.1523
Lockrose Bulk | 3870-1 | Lockrose BS | Lowood | Power Factor | 0.96801 | 0.96811 | 0.96809 | 0.96814 | 0.96806
Lockrose Bulk | 3870-1 | Lockrose BS | Lowood | ECC Rating (A) | 703 | 703 | 703 | 703 | 703
Lockrose Bulk | 3870-1 | Lockrose BS | Lowood | 50 POE Load (A) | 196.7317 | 195.7332 | 195.8965 | 195.3634 | 196.1678
Lockrose Bulk | 3871-1 | Lowood | Wivenhoe | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170
Lockrose Bulk | 3871-1 | Lowood | Wivenhoe | 10 POE Load (A) | 166.8448 | 165.7763 | 165.9682 | 165.5097 | 166.2632
Lockrose Bulk | 3871-1 | Lowood | Wivenhoe | Power Factor | 0.9719 | 0.97202 | 0.972 | 0.97205 | 0.97197
Lockrose Bulk | 3871-1 | Lowood | Wivenhoe | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
Lockrose Bulk | 3871-1 | Lowood | Wivenhoe | 50 POE Load (A) | 137.1478 | 136.293 | 136.4473 | 136.0798 | 136.6809
Loganlea Bulk | 407-1 | Loganlea BS | Woodridge | NCC Rating (A) | 777 | 777 | 777 | 777 | 777 | Urban | 70
Loganlea Bulk | 407-1 | Loganlea BS | Woodridge | 10 POE Load (A) | 378.6117 | 371.9879 | 366.8813 | 360.724 | 358.2734
Loganlea Bulk | 407-1 | Loganlea BS | Woodridge | Power Factor | 0.98696 | 0.98767 | 0.98821 | 0.98886 | 0.98912
Loganlea Bulk | 407-1 | Loganlea BS | Woodridge | ECC Rating (A) | 777 | 777 | 777 | 777 | 777
Loganlea Bulk | 407-1 | Loganlea BS | Woodridge | 50 POE Load (A) | 582 | 600 | 598 | 593 | 590
Loganlea Bulk | 408-1 | Loganlea BS | Kingston | NCC Rating (A) | 529 | 529 | 529 | 529 | 529 | Urban | 280
Loganlea Bulk | 408-1 | Loganlea BS | Kingston | 10 POE Load (A) | 370.1467 | 371.854 | 374.8914 | 377.6459 | 383.5407
Loganlea Bulk | 408-1 | Loganlea BS | Kingston | Power Factor | 0.9578 | 0.9586 | 0.95793 | 0.95732 | 0.95611
Loganlea Bulk | 408-1 | Loganlea BS | Kingston | ECC Rating (A) | 529 | 529 | 529 | 529 | 529
Loganlea Bulk | 408-1 | Loganlea BS | Kingston | 50 POE Load (A) | 571 | 573 | 574 | 574 | 574
Loganlea Bulk | 409-1 | Loganlea BS | Woodridge | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
Loganlea Bulk | 409-1 | Loganlea BS | Woodridge | 10 POE Load (A) | 338.1822 | 332.2656 | 327.7042 | 322.2042 | 320.0153
Loganlea Bulk | 409-1 | Loganlea BS | Woodridge | Power Factor | 0.98865 | 0.98931 | 0.98982 | 0.99042 | 0.99065
Loganlea Bulk | 409-1 | Loganlea BS | Woodridge | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Loganlea Bulk | 409-1 | Loganlea BS | Woodridge | 50 POE Load (A) | 584 | 603 | 600 | 595 | 590
Loganlea Bulk | 418-1 | Loganlea BS | Tanah Merah | NCC Rating (A) | 631 | 631 | 631 | 631 | 631 | Urban | 70
Loganlea Bulk | 418-1 | Loganlea BS | Tanah Merah | 10 POE Load (A) | 363.0882 | 360.6058 | 360.0003 | 359.2995 | 361.288
Loganlea Bulk | 418-1 | Loganlea BS | Tanah Merah | Power Factor | 0.00013354 | 0.00013355 | 0.00013341 | 0.00013344 | 0.00013351
Loganlea Bulk | 418-1 | Loganlea BS | Tanah Merah | ECC Rating (A) | 631 | 631 | 631 | 631 | 631
Loganlea Bulk | 418-1 | Loganlea BS | Tanah Merah | 50 POE Load (A) | 307.1509 | 305.0689 | 304.5612 | 303.9732 | 305.6411
Loganlea Bulk | 452-1 | Loganlea BS | Kingston | NCC Rating (A) | 510 | 510 | 510 | 510 | 510 | Urban | 280
Loganlea Bulk | 452-1 | Loganlea BS | Kingston | 10 POE Load (A) | 300.513 | 301.8989 | 304.3647 | 306.6008 | 311.3851
Loganlea Bulk | 452-1 | Loganlea BS | Kingston | Power Factor | 0.98687 | 0.98732 | 0.98694 | 0.9866 | 0.98591
Loganlea Bulk | 452-1 | Loganlea BS | Kingston | ECC Rating (A) | 510 | 510 | 510 | 510 | 510
Loganlea Bulk | 452-1 | Loganlea BS | Kingston | 50 POE Load (A) | 276.298 | 277.5622 | 279.8111 | 281.8503 | 285.9167
Lytton Bulk | 3302-1 | Lytton BS | Fisherman Is B | NCC Rating (A) | 650 | 650 | 650 | 650 | 650 | Urban | 70
Lytton Bulk | 3302-1 | Lytton BS | Fisherman Is B | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lytton Bulk | 3302-1 | Lytton BS | Fisherman Is B | Power Factor | 1 | 1 | 1 | 1 | 1
Lytton Bulk | 3302-1 | Lytton BS | Fisherman Is B | ECC Rating (A) | 650 | 650 | 650 | 650 | 650
Lytton Bulk | 3302-1 | Lytton BS | Fisherman Is B | 50 POE Load (A) | 508 | 511 | 511 | 539 | 550
Lytton Bulk | 3303-1 | Lytton BS | Fisherman Is B | NCC Rating (A) | 600 | 600 | 600 | 600 | 600 | Urban | 70
Lytton Bulk | 3303-1 | Lytton BS | Fisherman Is B | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lytton Bulk | 3303-1 | Lytton BS | Fisherman Is B | Power Factor | 1 | 1 | 1 | 1 | 1
Lytton Bulk | 3303-1 | Lytton BS | Fisherman Is B | ECC Rating (A) | 600 | 600 | 600 | 600 | 600
Lytton Bulk | 3303-1 | Lytton BS | Fisherman Is B | 50 POE Load (A) | 508 | 511 | 511 | 539 | 545
Lytton Bulk | 490-1 | Lytton BS | Gibson Island | NCC Rating (A) | 628 | 628 | 628 | 628 | 628 | HighSec | 0
Lytton Bulk | 490-1 | Lytton BS | Gibson Island | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lytton Bulk | 490-1 | Lytton BS | Gibson Island | Power Factor | 1 | 1 | 1 | 1 | 1
Lytton Bulk | 490-1 | Lytton BS | Gibson Island | ECC Rating (A) | 628 | 628 | 628 | 628 | 628
Lytton Bulk | 490-1 | Lytton BS | Gibson Island | 50 POE Load (A) | 304 | 304 | 304 | 303 | 303
Lytton Bulk | 491-1 | Lytton BS | Lytton | NCC Rating (A) | 450 | 450 | 450 | 450 | 450 | HighSec | 314
Lytton Bulk | 491-1 | Lytton BS | Lytton | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lytton Bulk | 491-1 | Lytton BS | Lytton | Power Factor | 1 | 1 | 1 | 1 | 1
Lytton Bulk | 491-1 | Lytton BS | Lytton | ECC Rating (A) | 450 | 450 | 450 | 450 | 450
Lytton Bulk | 491-1 | Lytton BS | Lytton | 50 POE Load (A) | 498 | 499 | 499 | 531 | 540
Lytton Bulk | 492-1 | Lytton BS | Gibson Island | NCC Rating (A) | 463 | 463 | 463 | 463 | 463 | HighSec | 0
Lytton Bulk | 492-1 | Lytton BS | Gibson Island | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lytton Bulk | 492-1 | Lytton BS | Gibson Island | Power Factor | 1 | 1 | 1 | 1 | 1
Lytton Bulk | 492-1 | Lytton BS | Gibson Island | ECC Rating (A) | 463 | 463 | 463 | 463 | 463
Lytton Bulk | 492-1 | Lytton BS | Gibson Island | 50 POE Load (A) | 304 | 304 | 304 | 303 | 303
Lytton Bulk | 493-1 | Lytton BS | Lytton | NCC Rating (A) | 536 | 536 | 536 | 536 | 536 | HighSec | 0
Lytton Bulk | 493-1 | Lytton BS | Lytton | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lytton Bulk | 493-1 | Lytton BS | Lytton | Power Factor | 1 | 1 | 1 | 1 | 1
Lytton Bulk | 493-1 | Lytton BS | Lytton | ECC Rating (A) | 536 | 536 | 536 | 536 | 536
Lytton Bulk | 493-1 | Lytton BS | Lytton | 50 POE Load (A) | 497 | 499 | 499 | 530 | 540
Lytton Bulk | 494-1 | Fisherman Is B | Fishermans Is | NCC Rating (A) | 488 | 488 | 488 | 488 | 488 | Urban | 70
Lytton Bulk | 494-1 | Fisherman Is B | Fishermans Is | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lytton Bulk | 494-1 | Fisherman Is B | Fishermans Is | Power Factor | 1 | 1 | 1 | 1 | 1
Lytton Bulk | 494-1 | Fisherman Is B | Fishermans Is | ECC Rating (A) | 488 | 488 | 488 | 488 | 488
Lytton Bulk | 494-1 | Fisherman Is B | Fishermans Is | 50 POE Load (A) | 270 | 268 | 268 | 295 | 310
Lytton Bulk | 495-1 | Fisherman Is B | Fisherman Is | NCC Rating (A) | 600 | 600 | 600 | 600 | 600 | Urban | 70
Lytton Bulk | 495-1 | Fisherman Is B | Fisherman Is | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lytton Bulk | 495-1 | Fisherman Is B | Fisherman Is | Power Factor | 1 | 1 | 1 | 1 | 1
Lytton Bulk | 495-1 | Fisherman Is B | Fisherman Is | ECC Rating (A) | 600 | 600 | 600 | 600 | 600
Lytton Bulk | 495-1 | Fisherman Is B | Fisherman Is | 50 POE Load (A) | 269 | 267 | 267 | 294 | 310
Lytton Bulk | 560-1 | Lytton BS | 560 Tee1 | NCC Rating (A) | 527 | 527 | 527 | 527 | 527 | Urban | 70
Lytton Bulk | 560-1 | Lytton BS | 560 Tee1 | 10 POE Load (A) | 169.3267 | 168.1693 | 167.872 | 167.4272 | 168.2026
Lytton Bulk | 560-1 | Lytton BS | 560 Tee1 | Power Factor | 0.98888 | 0.98903 | 0.98906 | 0.98912 | 0.98902
Lytton Bulk | 560-1 | Lytton BS | 560 Tee1 | ECC Rating (A) | 527 | 527 | 527 | 527 | 527
Lytton Bulk | 560-1 | Lytton BS | 560 Tee1 | 50 POE Load (A) | 486 | 486 | 484 | 481 | 490
Lytton Bulk | 560-14 | 560 Tee1 | 560 Tee2 | NCC Rating (A) | 367 | 367 | 367 | 367 | 367 | Urban | 70
Lytton Bulk | 560-14 | 560 Tee1 | 560 Tee2 | 10 POE Load (A) | 69.8323 | 69.3549 | 69.2323 | 69.0488 | 69.3686
Lytton Bulk | 560-14 | 560 Tee1 | 560 Tee2 | Power Factor | -0.98631 | -0.98646 | -0.9865 | -0.98656 | -0.98646
Lytton Bulk | 560-14 | 560 Tee1 | 560 Tee2 | ECC Rating (A) | 367 | 367 | 367 | 367 | 367
Lytton Bulk | 560-14 | 560 Tee1 | 560 Tee2 | 50 POE Load (A) | 200 | 200 | 200 | 198 | 198
Lytton Bulk | 560-15 | 560 Tee1 | 560 Tee2 | NCC Rating (A) | 351 | 351 | 351 | 351 | 351 | Urban | 70
Lytton Bulk | 560-15 | 560 Tee1 | 560 Tee2 | 10 POE Load (A) | 101.5412 | 100.8541 | 100.6776 | 100.4135 | 100.8738
Lytton Bulk | 560-15 | 560 Tee1 | 560 Tee2 | Power Factor | 0.9889 | 0.98903 | 0.98907 | 0.98912 | 0.98903
Lytton Bulk | 560-15 | 560 Tee1 | 560 Tee2 | ECC Rating (A) | 351 | 351 | 351 | 351 | 351
Lytton Bulk | 560-15 | 560 Tee1 | 560 Tee2 | 50 POE Load (A) | 286 | 286 | 284 | 283 | 283
Lytton Bulk | 560-16 | Lota | 560 Tee1 | NCC Rating (A) | 983 | 983 | 983 | 983 | 983 | Urban | 70
Lytton Bulk | 560-16 | Lota | 560 Tee1 | 10 POE Load (A) | 171.2821 | 170.1167 | 169.8173 | 169.3694 | 170.1501
Lytton Bulk | 560-16 | Lota | 560 Tee1 | Power Factor | -0.97713 | -0.97722 | -0.97724 | -0.97727 | -0.97721
Lytton Bulk | 560-16 | Lota | 560 Tee1 | ECC Rating (A) | 983 | 983 | 983 | 983 | 983
Lytton Bulk | 560-16 | Lota | 560 Tee1 | 50 POE Load (A) | 488 | 488 | 486 | 484 | 490
Lytton Bulk | 560-2 | 560 Tee1 | Tingalpa | NCC Rating (A) | 600 | 600 | 600 | 600 | 600 | Urban | 70
Lytton Bulk | 560-2 | 560 Tee1 | Tingalpa | 10 POE Load (A) | 0.10066 | 0.10067 | 0.10067 | 0.10068 | 0.10067
Lytton Bulk | 560-2 | 560 Tee1 | Tingalpa | Power Factor | 1.9415e-06 | 1.9404e-06 | 1.9415e-06 | 1.9412e-06 | 1.9414e-06
Lytton Bulk | 560-3 | 560 Tee1 | 560 Tee2 | NCC Rating (A) | 600 | 600 | 600 | 600 | 600 | Urban | 70
Lytton Bulk | 560-3 | 560 Tee1 | 560 Tee2 | 10 POE Load (A) | 169.4088 | 168.2508 | 167.9534 | 167.5084 | 168.2841
Lytton Bulk | 560-3 | 560 Tee1 | 560 Tee2 | Power Factor | -0.98765 | -0.98781 | -0.98785 | -0.98791 | -0.98781
Lytton Bulk | 560-3 | 560 Tee1 | 560 Tee2 | ECC Rating (A) | 600 | 600 | 600 | 600 | 600
Lytton Bulk | 560-3 | 560 Tee1 | 560 Tee2 | 50 POE Load (A) | 486 | 486 | 484 | 481 | 490
Lytton Bulk | 560-5 | Lota | 560 Tee2 | NCC Rating (A) | 704 | 704 | 704 | 704 | 704 | Urban | 70
Lytton Bulk | 560-5 | Lota | 560 Tee2 | 10 POE Load (A) | 99.7079 | 99.0266 | 98.8516 | 98.5897 | 99.0462
Lytton Bulk | 560-5 | Lota | 560 Tee2 | Power Factor | -0.98793 | -0.98809 | -0.98813 | -0.98819 | -0.98809
Lytton Bulk | 560-5 | Lota | 560 Tee2 | ECC Rating (A) | 704 | 704 | 704 | 704 | 704
Lytton Bulk | 560-5 | Lota | 560 Tee2 | 50 POE Load (A) | 286 | 286 | 284 | 283 | 283
Lytton Bulk | 569-1 | Lytton BS | Lota | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Urban | 70
Lytton Bulk | 569-1 | Lytton BS | Lota | 10 POE Load (A) | 349.5376 | 347.149 | 346.5355 | 345.6174 | 347.2176
Lytton Bulk | 569-1 | Lytton BS | Lota | Power Factor | 0.96659 | 0.96682 | 0.96688 | 0.96697 | 0.96681
Lytton Bulk | 569-1 | Lytton BS | Lota | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
Lytton Bulk | 569-1 | Lytton BS | Lota | 50 POE Load (A) | 467 | 467 | 465 | 462 | 460
Lytton Bulk | 599-1 | Hemmant | Lindum | NCC Rating (A) | 443 | 443 | 443 | 443 | 443 | Urban | 70
Lytton Bulk | 599-1 | Hemmant | Lindum | 10 POE Load (A) | 1.7438 | 1.7438 | 1.7438 | 1.7438 | 1.7437
Lytton Bulk | 599-1 | Hemmant | Lindum | Power Factor | -1.1634e-06 | -1.1627e-06 | -1.1625e-06 | -1.1632e-06 | -1.163e-06
Lytton Bulk | 599-1 | Hemmant | Lindum | ECC Rating (A) | 443 | 443 | 443 | 443 | 443
Lytton Bulk | 599-1 | Hemmant | Lindum | 50 POE Load (A) | 1.744 | 1.744 | 1.7439 | 1.7439 | 1.7439
Lytton Bulk | 681-1 | Lindum | Wynnum | NCC Rating (A) | 661 | 661 | 661 | 661 | 661 | Urban | 70
Lytton Bulk | 681-1 | Lindum | Wynnum | 10 POE Load (A) | 212.2563 | 212.8723 | 214.4248 | 216.0119 | 219.1505
Lytton Bulk | 681-1 | Lindum | Wynnum | Power Factor | 0.97042 | 0.97033 | 0.97012 | 0.9699 | 0.96946
Lytton Bulk | 681-1 | Lindum | Wynnum | ECC Rating (A) | 790 | 790 | 790 | 790 | 790
Lytton Bulk | 681-1 | Lindum | Wynnum | 50 POE Load (A) | 382 | 384 | 385 | 385 | 385
Lytton Bulk | 682-1 | Lindum | Wynnum | NCC Rating (A) | 661 | 661 | 661 | 661 | 661 | Urban | 70
Lytton Bulk | 682-1 | Lindum | Wynnum | 10 POE Load (A) | 203.4209 | 204.0113 | 205.4991 | 207.02 | 210.0278
Lytton Bulk | 682-1 | Lindum | Wynnum | Power Factor | -0.9634 | -0.96333 | -0.96316 | -0.96298 | -0.96264
Lytton Bulk | 682-1 | Lindum | Wynnum | ECC Rating (A) | 790 | 790 | 790 | 790 | 790
Lytton Bulk | 682-1 | Lindum | Wynnum | 50 POE Load (A) | 383 | 385 | 386 | 386 | 386
Lytton Bulk | 687-1 | Lytton BS | 687 Tee1 | NCC Rating (A) | 758 | 758 | 758 | 758 | 758 | Urban | 70
Lytton Bulk | 687-1 | Lytton BS | 687 Tee1 | 10 POE Load (A) | 150.4169 | 150.8553 | 151.9604 | 153.09 | 155.324
Lytton Bulk | 687-1 | Lytton BS | 687 Tee1 | Power Factor | 0.98934 | 0.98927 | 0.98911 | 0.98895 | 0.98862
Lytton Bulk | 687-1 | Lytton BS | 687 Tee1 | ECC Rating (A) | 758 | 758 | 758 | 758 | 758
Lytton Bulk | 687-1 | Lytton BS | 687 Tee1 | 50 POE Load (A) | 367 | 370 | 370 | 370 | 370
Lytton Bulk | 687-2 | 687 Tee1 | Lytton | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 70
Lytton Bulk | 687-2 | 687 Tee1 | Lytton | 10 POE Load (A) | 2.2893 | 2.2893 | 2.2893 | 2.2893 | 2.2893
Lytton Bulk | 687-2 | 687 Tee1 | Lytton | Power Factor | 1.8338e-05 | 1.8338e-05 | 1.8338e-05 | 1.8338e-05 | 1.8338e-05
Lytton Bulk | 687-2 | 687 Tee1 | Lytton | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
Lytton Bulk | 687-2 | 687 Tee1 | Lytton | 50 POE Load (A) | 2.2893 | 2.2893 | 2.2893 | 2.2893 | 2.2893
Lytton Bulk | 687-3 | 687 Tee1 | Lindum | NCC Rating (A) | 636 | 636 | 636 | 636 | 636 | Urban | 70
Lytton Bulk | 687-3 | 687 Tee1 | Lindum | 10 POE Load (A) | 150.7876 | 151.2269 | 152.3342 | 153.4662 | 155.7047
Lytton Bulk | 687-3 | 687 Tee1 | Lindum | Power Factor | 0.9863 | 0.98624 | 0.98609 | 0.98593 | 0.98562
Lytton Bulk | 687-3 | 687 Tee1 | Lindum | ECC Rating (A) | 636 | 636 | 636 | 636 | 636
Lytton Bulk | 687-3 | 687 Tee1 | Lindum | 50 POE Load (A) | 368 | 370 | 371 | 371 | 371
Lytton Bulk | 688-1 | Lytton BS | Lindum | NCC Rating (A) | 636 | 636 | 636 | 636 | 636 | Urban | 70
Lytton Bulk | 688-1 | Lytton BS | Lindum | 10 POE Load (A) | 262.4982 | 263.2634 | 265.192 | 267.1635 | 271.0623
Lytton Bulk | 688-1 | Lytton BS | Lindum | Power Factor | 0.96154 | 0.96143 | 0.96116 | 0.96088 | 0.96032
Lytton Bulk | 688-1 | Lytton BS | Lindum | ECC Rating (A) | 636 | 636 | 636 | 636 | 636
Lytton Bulk | 688-1 | Lytton BS | Lindum | 50 POE Load (A) | 367 | 369 | 370 | 370 | 370
Meeandah Bulk | 3374-1 | Whinstanes | Hamilton Lands | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70
Meeandah Bulk | 3374-1 | Whinstanes | Hamilton Lands | 10 POE Load (A) | 94.6729 | 93.0475 | 91.4087 | 89.4785 | 88.0016
Meeandah Bulk | 3374-1 | Whinstanes | Hamilton Lands | Power Factor | 0.92563 | 0.92599 | 0.92638 | 0.92686 | 0.92726
Meeandah Bulk | 3374-1 | Whinstanes | Hamilton Lands | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
Meeandah Bulk | 3374-1 | Whinstanes | Hamilton Lands | 50 POE Load (A) | 247 | 247 | 246 | 245 | 243
Meeandah Bulk | 506-1 | Meeandah BS | Hamilton Lands | NCC Rating (A) | 720 | 720 | 720 | 720 | 720 | Urban | 70
Meeandah Bulk | 506-1 | Meeandah BS | Hamilton Lands | 10 POE Load (A) | 205.4203 | 208.6839 | 211.5932 | 214.1059 | 217.6772
Meeandah Bulk | 506-1 | Meeandah BS | Hamilton Lands | Power Factor | 0.97975 | 0.97879 | 0.9781 | 0.97736 | 0.97632
Meeandah Bulk | 506-1 | Meeandah BS | Hamilton Lands | ECC Rating (A) | 787 | 787 | 787 | 787 | 787
Meeandah Bulk | 506-1 | Meeandah BS | Hamilton Lands | 50 POE Load (A) | 334 | 333 | 333 | 333 | 333
Meeandah Bulk | 513-1 | Meeandah BS | Hamilton Lands | NCC Rating (A) | 720 | 720 | 720 | 720 | 720 | Urban | 70
Meeandah Bulk | 513-1 | Meeandah BS | Hamilton Lands | 10 POE Load (A) | 203.7855 | 207.0232 | 209.9094 | 212.402 | 215.9449
Meeandah Bulk | 513-1 | Meeandah BS | Hamilton Lands | Power Factor | 0.9798 | 0.97884 | 0.97815 | 0.97741 | 0.97637
Meeandah Bulk | 513-1 | Meeandah BS | Hamilton Lands | ECC Rating (A) | 787 | 787 | 787 | 787 | 787
Meeandah Bulk | 513-1 | Meeandah BS | Hamilton Lands | 50 POE Load (A) | 333 | 332 | 333 | 332 | 331
Meeandah Bulk | 556-1 | Meeandah BS | Whinstanes | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70
Meeandah Bulk | 556-1 | Meeandah BS | Whinstanes | 10 POE Load (A) | 171.199 | 172.1441 | 172.8552 | 173.1798 | 174.3897
Meeandah Bulk | 556-1 | Meeandah BS | Whinstanes | Power Factor | 0.94936 | 0.94906 | 0.94894 | 0.94881 | 0.94843
Meeandah Bulk | 556-1 | Meeandah BS | Whinstanes | ECC Rating (A) | 704 | 704 | 704 | 704 | 704
Meeandah Bulk | 556-1 | Meeandah BS | Whinstanes | 50 POE Load (A) | 247 | 247 | 246 | 245 | 245
Meeandah Bulk | 609-1 | Meeandah BS | Myrtletown | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Meeandah Bulk | 609-1 | Meeandah BS | Myrtletown | 10 POE Load (A) | 0.84162 | 0.84162 | 0.84162 | 0.84162 | 0.84162
Meeandah Bulk | 609-1 | Meeandah BS | Myrtletown | Power Factor | 5.6184e-06 | 5.6184e-06 | 5.6182e-06 | 5.6187e-06 | 5.6184e-06
Meeandah Bulk | 610-1 | Meeandah BS | Myrtletown | NCC Rating (A) | 748 | 748 | 748 | 748 | 748 | Urban | 70
Meeandah Bulk | 610-1 | Meeandah BS | Myrtletown | 10 POE Load (A) | 0.56892 | 0.56892 | 0.56892 | 0.56892 | 0.56892
Meeandah Bulk | 610-1 | Meeandah BS | Myrtletown | Power Factor | 9.0967e-06 | 9.097e-06 | 9.0967e-06 | 9.097e-06 | 9.0967e-06
Molendinar Bulk | 3670-1 | Molendinar BS | Parkwood | NCC Rating (A) | 710 | 710 | 710 | 710 | 710 | Urban | 70
Molendinar Bulk | 3670-1 | Molendinar BS | Parkwood | 10 POE Load (A) | 383.507 | 397.04 | 396.8486 | 412.0857 | 414.0098
Molendinar Bulk | 3670-1 | Molendinar BS | Parkwood | Power Factor | 0.97232 | 0.97167 | 0.97158 | 0.97095 | 0.97061
Molendinar Bulk | 3670-1 | Molendinar BS | Parkwood | ECC Rating (A) | 710 | 710 | 710 | 710 | 710
Molendinar Bulk | 3670-1 | Molendinar BS | Parkwood | 50 POE Load (A) | 536.6795 | 552.4882 | 552.9188 | 570.7505 | 569.278
Molendinar Bulk | 3671-1 | Molendinar BS | Parkwood | NCC Rating (A) | 708 | 708 | 708 | 708 | 708 | Urban | 70
Molendinar Bulk | 3671-1 | Molendinar BS | Parkwood | 10 POE Load (A) | 304.942 | 315.7045 | 315.5524 | 327.6705 | 329.2009
Molendinar Bulk | 3671-1 | Molendinar BS | Parkwood | Power Factor | 0.98055 | 0.98 | 0.97993 | 0.97939 | 0.9791
Molendinar Bulk | 3671-1 | Molendinar BS | Parkwood | ECC Rating (A) | 708 | 708 | 708 | 708 | 708
Molendinar Bulk | 3671-1 | Molendinar BS | Parkwood | 50 POE Load (A) | 457 | 478 | 480 | 500 | 500
Molendinar Bulk | 389-1 | Parkwood | 389 Tee1 | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
Molendinar Bulk | 389-1 | Parkwood | 389 Tee1 | 10 POE Load (A) | 373.6031 | 367.0049 | 369.1404 | 362.4091 | 367.8708
Molendinar Bulk | 389-1 | Parkwood | 389 Tee1 | Power Factor | 0.97827 | 0.97865 | 0.97842 | 0.97882 | 0.9781
Molendinar Bulk | 389-1 | Parkwood | 389 Tee1 | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Molendinar Bulk | 389-1 | Parkwood | 389 Tee1 | 50 POE Load (A) | 740 | 743 | 747 | 746 | 748
Molendinar Bulk | 389-2 | F389 Tee1 | Labrador | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
Molendinar Bulk | 389-2 | F389 Tee1 | Labrador | 10 POE Load (A) | 273.6455 | 274.6593 | 277.7274 | 277.7868 | 282.7707
Molendinar Bulk | 389-2 | F389 Tee1 | Labrador | Power Factor | 0.93552 | 0.93504 | 0.9349 | 0.93439 | 0.93409
Molendinar Bulk | 389-2 | F389 Tee1 | Labrador | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Molendinar Bulk | 389-2 | F389 Tee1 | Labrador | 50 POE Load (A) | 414 | 420 | 424 | 427 | 429
Molendinar Bulk | 389-3 | F389 Tee1 | Hollywell | NCC Rating (A) | 631 | 631 | 631 | 631 | 631 | Urban | 70
Molendinar Bulk | 389-3 | F389 Tee1 | Hollywell | 10 POE Load (A) | 111.7256 | 105.142 | 104.4281 | 98.6112 | 99.0956
Molendinar Bulk | 389-3 | F389 Tee1 | Hollywell | Power Factor | 0.98395 | 0.97714 | 0.97602 | 0.96811 | 0.96894
Molendinar Bulk | 389-3 | F389 Tee1 | Hollywell | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
Molendinar Bulk | 389-3 | F389 Tee1 | Hollywell | 50 POE Load (A) | 642 | 645 | 646 | 647 | 647
Molendinar Bulk | 390-1 | Molendinar BS | F390 Tee1 | NCC Rating (A) | 637 | 637 | 637 | 637 | 637 | Urban | 70
Molendinar Bulk | 390-1 | Molendinar BS | F390 Tee1 | 10 POE Load (A) | 125.2081 | 149.9378 | 148.9783 | 147.5152 | 147.2693
Molendinar Bulk | 390-1 | Molendinar BS | F390 Tee1 | Power Factor | 0.9997 | 0.9949 | 0.99516 | 0.99555 | 0.99561
Molendinar Bulk | 390-1 | Molendinar BS | F390 Tee1 | ECC Rating (A) | 637 | 637 | 637 | 637 | 637
Molendinar Bulk | 390-1 | Molendinar BS | F390 Tee1 | 50 POE Load (A) | 581.4046 | 599.3682 | 603.1732 | 606.4791 | 614.3888
Molendinar Bulk | 390-2 | F390 Tee | Bundall | NCC Rating (A) | 578 | 578 | 578 | 578 | 578 | Urban | 70
Molendinar Bulk | 390-2 | F390 Tee | Bundall | 10 POE Load (A) | 125.3364 | 150.2567 | 149.2908 | 147.8177 | 147.5701
Molendinar Bulk | 390-2 | F390 Tee | Bundall | Power Factor | 0.99944 | 0.9951 | 0.99532 | 0.99565 | 0.99571
Molendinar Bulk | 390-2 | F390 Tee | Bundall | ECC Rating (A) | 653 | 653 | 653 | 653 | 653
Molendinar Bulk | 390-2 | F390 Tee | Bundall | 50 POE Load (A) | 305 | 304 | 304 | 303 | 303
Molendinar Bulk | 390-3 | F390 Tee | Miami | NCC Rating (A) | 529 | 529 | 529 | 529 | 529 | Urban | 70
Molendinar Bulk | 390-3 | F390 Tee | Miami | 10 POE Load (A) | 0.18269 | 0.18193 | 0.18196 | 0.18201 | 0.18202
Molendinar Bulk | 390-3 | F390 Tee | Miami | Power Factor | 1 | 1 | 1 | 1 | 1
Molendinar Bulk | 390-3 | F390 Tee | Miami | ECC Rating (A) | 529 | 529 | 529 | 529 | 529
Molendinar Bulk | 390-3 | F390 Tee | Miami | 50 POE Load (A) | 454.9182 | 457.3514 | 462.0603 | 466.7436 | 474.8898
Molendinar Bulk | 391-1 | Molendinar BS | Bundall | NCC Rating (A) | 623 | 623 | 623 | 623 | 623 | Urban | 70
Molendinar Bulk | 391-1 | Molendinar BS | Bundall | 10 POE Load (A) | 156.3577 | 188.2072 | 187.0011 | 185.1619 | 184.8528
Molendinar Bulk | 391-1 | Molendinar BS | Bundall | Power Factor | 0.99463 | 0.98528 | 0.98567 | 0.98627 | 0.98637
Molendinar Bulk | 391-1 | Molendinar BS | Bundall | ECC Rating (A) | 623 | 623 | 623 | 623 | 623
Molendinar Bulk | 391-1 | Molendinar BS | Bundall | 50 POE Load (A) | 297 | 296 | 296 | 294 | 300
Molendinar Bulk | 392-1 | Molendinar BS | Gaven | NCC Rating (A) | 708 | 708 | 708 | 708 | 708 | Urban | 70
Molendinar Bulk | 392-1 | Molendinar BS | Gaven | 10 POE Load (A) | 263.687 | 257.1395 | 256.0009 | 255.5028 | 256.921
Molendinar Bulk | 392-1 | Molendinar BS | Gaven | Power Factor | 0.96802 | 0.96879 | 0.96893 | 0.96898 | 0.96882
Molendinar Bulk | 392-1 | Molendinar BS | Gaven | ECC Rating (A) | 708 | 708 | 708 | 708 | 708
Molendinar Bulk | 392-1 | Molendinar BS | Gaven | 50 POE Load (A) | 496 | 496 | 494 | 492 | 492
Molendinar Bulk | 421-1 | Molendinar BS | Arundel | NCC Rating (A) | 673 | 673 | 673 | 673 | 673 | Urban | 553
Molendinar Bulk | 421-1 | Molendinar BS | Arundel | 10 POE Load (A) | 513.1677 | 513.3357 | 511.9934 | 514.6107 | 518.5682
Molendinar Bulk | 421-1 | Molendinar BS | Arundel | Power Factor | 0.98031 | 0.98041 | 0.98053 | 0.98034 | 0.97982
Molendinar Bulk | 421-1 | Molendinar BS | Arundel | ECC Rating (A) | 721 | 721 | 721 | 721 | 721
Molendinar Bulk | 421-1 | Molendinar BS | Arundel | 50 POE Load (A) | 796 | 807 | 808 | 815 | 815
Molendinar Bulk | 458-1 | Molendinar BS | Labrador | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
Molendinar Bulk | 458-1 | Molendinar BS | Labrador | 10 POE Load (A) | 212.0017 | 214.3308 | 215.0845 | 217.7203 | 219.9692
Molendinar Bulk | 458-1 | Molendinar BS | Labrador | Power Factor | 0.97893 | 0.97883 | 0.97866 | 0.97856 | 0.97813
Molendinar Bulk | 458-1 | Molendinar BS | Labrador | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Molendinar Bulk | 458-1 | Molendinar BS | Labrador | 50 POE Load (A) | 516.1486 | 518.0767 | 519.4741 | 522.9242 | 527.4045
Molendinar Bulk | 473-1 | Molendinar BS | Gaven | NCC Rating (A) | 717 | 717 | 717 | 717 | 717 | Urban | 70
Molendinar Bulk | 473-1 | Molendinar BS | Gaven | 10 POE Load (A) | 264.2899 | 257.7275 | 256.5863 | 256.087 | 257.5085
Molendinar Bulk | 473-1 | Molendinar BS | Gaven | Power Factor | 0.96797 | 0.96874 | 0.96887 | 0.96893 | 0.96877
Molendinar Bulk | 473-1 | Molendinar BS | Gaven | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
Molendinar Bulk | 473-1 | Molendinar BS | Gaven | 50 POE Load (A) | 497 | 496 | 495 | 492 | 495
Molendinar Bulk | 474A-1 | Arundel | Hollywell | NCC Rating (A) | 631 | 631 | 631 | 631 | 631 | Urban | 517
Molendinar Bulk | 474A-1 | Arundel | Hollywell | 10 POE Load (A) | 621.886 | 628.474 | 631.1893 | 638.4178 | 644.5769
Molendinar Bulk | 474A-1 | Arundel | Hollywell | Power Factor | -0.97185 | -0.97158 | -0.97134 | -0.97101 | -0.97046
Molendinar Bulk | 474A-1 | Arundel | Hollywell | ECC Rating (A) | 631 | 631 | 631 | 631 | 631
Molendinar Bulk | 474A-1 | Arundel | Hollywell | 50 POE Load (A) | 905.825 | 926.3926 | 928.5663 | 951.5595 | 952.8725
Molendinar Bulk | 474B-1 | Hope Is | Hollywell | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Urban | 70
Molendinar Bulk | 474B-1 | Hope Is | Hollywell | 10 POE Load (A) | 3.7674 | 3.7669 | 3.7667 | 3.7659 | 3.7648
Molendinar Bulk | 474B-1 | Hope Is | Hollywell | Power Factor | 5.1781e-05 | 5.1781e-05 | 5.1781e-05 | 5.1781e-05 | 5.1781e-05
Molendinar Bulk | 474B-1 | Hope Is | Hollywell | ECC Rating (A) | 786 | 786 | 786 | 786 | 786
Molendinar Bulk | 474B-1 | Hope Is | Hollywell | 50 POE Load (A) | 329.8632 | 329.5199 | 330.2637 | 331.1374 | 334.2085
Molendinar Bulk | 486-1 | Molendinar BS | Arundel | NCC Rating (A) | 673 | 673 | 673 | 673 | 673 | Urban | 70
Molendinar Bulk | 486-1 | Molendinar BS | Arundel | 10 POE Load (A) | 513.5388 | 513.7069 | 512.3635 | 514.9828 | 518.9432
Molendinar Bulk | 486-1 | Molendinar BS | Arundel | Power Factor | 0.98029 | 0.98038 | 0.9805 | 0.98031 | 0.9798
Molendinar Bulk | 486-1 | Molendinar BS | Arundel | ECC Rating (A) | 721 | 721 | 721 | 721 | 721
Molendinar Bulk | 486-1 | Molendinar BS | Arundel | 50 POE Load (A) | 796 | 807 | 809 | 815 | 815
Mudgeeraba Bulk | 3700-1 | Mudgeeraba BS | 3700 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Mudgeeraba Bulk | 3700-1 | Mudgeeraba BS | 3700 Tee1 | 10 POE Load (A) | 239.3505 | 239.3833 | 240.8386 | 241.7432 | 244.5983
Mudgeeraba Bulk | 3700-1 | Mudgeeraba BS | 3700 Tee1 | Power Factor | 0.97233 | 0.97232 | 0.97214 | 0.97202 | 0.97165
Mudgeeraba Bulk | 3700-1 | Mudgeeraba BS | 3700 Tee1 | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Mudgeeraba Bulk | 3700-1 | Mudgeeraba BS | 3700 Tee1 | 50 POE Load (A) | 442 | 446 | 447 | 448 | 448
Mudgeeraba Bulk | 3700-2 | 3700 Tee1 | 3701 Tee1 | NCC Rating (A) | 723 | 723 | 723 | 723 | 723 | Rural | 170
Mudgeeraba Bulk | 3700-2 | 3700 Tee1 | 3701 Tee1 | 10 POE Load (A) | 0.0029965 | 0.0029965 | 0.0029965 | 0.0029965 | 0.0029965
Mudgeeraba Bulk | 3700-2 | 3700 Tee1 | 3701 Tee1 | Power Factor | 6.6143e-05 | 6.6145e-05 | 6.6104e-05 | 6.6116e-05 | 6.6126e-05
Mudgeeraba Bulk | 3700-3 | 3700 Tee1 | 3700 Tee2 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Mudgeeraba Bulk | 3700-3 | 3700 Tee1 | 3700 Tee2 | 10 POE Load (A) | 239.3992 | 239.432 | 240.8874 | 241.7921 | 244.6475
Mudgeeraba Bulk | 3700-3 | 3700 Tee1 | 3700 Tee2 | Power Factor | 0.97344 | 0.97344 | 0.97327 | 0.97317 | 0.97283
Mudgeeraba Bulk | 3700-3 | 3700 Tee1 | 3700 Tee2 | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Mudgeeraba Bulk | 3700-3 | 3700 Tee1 | 3700 Tee2 | 50 POE Load (A) | 443 | 446 | 447 | 448 | 448
Mudgeeraba Bulk | 3700-4 | 3700 Tee2 | 3702 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Mudgeeraba Bulk | 3700-4 | 3700 Tee2 | 3702 Tee1 | 10 POE Load (A) | 0.12291 | 0.12291 | 0.1229 | 0.1229 | 0.12288
Mudgeeraba Bulk | 3700-4 | 3700 Tee2 | 3702 Tee1 | Power Factor | 8.6872e-06 | 8.6885e-06 | 8.6866e-06 | 8.6862e-06 | 8.6875e-06
Mudgeeraba Bulk | 3700-5 | 3700 Tee2 | Mudgeeraba Pkg | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Mudgeeraba Bulk | 3700-5 | 3700 Tee2 | Mudgeeraba Pkg | 10 POE Load (A) | 239.4634 | 239.4962 | 240.9519 | 241.8566 | 244.7124
Mudgeeraba Bulk | 3700-5 | 3700 Tee2 | Mudgeeraba Pkg | Power Factor | 0.97562 | 0.97561 | 0.97547 | 0.97538 | 0.97509
Mudgeeraba Bulk | 3700-5 | 3700 Tee2 | Mudgeeraba Pkg | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Mudgeeraba Bulk | 3700-5 | 3700 Tee2 | Mudgeeraba Pkg | 50 POE Load (A) | 443 | 446 | 447 | 448 | 448
Mudgeeraba Bulk | 3701-1 | Mudgeeraba | Mudgeeraba Pkg | NCC Rating (A) | 529 | 529 | 529 | 529 | 529 | Rural | 170
Mudgeeraba Bulk | 3701-1 | Mudgeeraba | Mudgeeraba Pkg | 10 POE Load (A) | 259.3904 | 259.4259 | 261.0018 | 261.9812 | 265.0729
Mudgeeraba Bulk | 3701-1 | Mudgeeraba | Mudgeeraba Pkg | Power Factor | 0.9697 | 0.9697 | 0.96953 | 0.96943 | 0.9691
Mudgeeraba Bulk | 3701-1 | Mudgeeraba | Mudgeeraba Pkg | ECC Rating (A) | 529 | 529 | 529 | 529 | 529
Mudgeeraba Bulk | 3701-1 | Mudgeeraba | Mudgeeraba Pkg | 50 POE Load (A) | 441 | 444 | 446 | 447 | 447
Nambour Bulk | 307-1 | Nambour BS | 307 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170
Nambour Bulk | 307-1 | Nambour BS | 307 Tee1 | 10 POE Load (A) | 91.18 | 91.4431 | 92.0001 | 92.3438 | 93.2359
Nambour Bulk | 307-1 | Nambour BS | 307 Tee1 | Power Factor | 0.94107 | 0.94096 | 0.94073 | 0.94059 | 0.94096
Nambour Bulk | 307-1 | Nambour BS | 307 Tee1 | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Nambour Bulk | 307-1 | Nambour BS | 307 Tee1 | 50 POE Load (A) | 551.6229 | 624.5828 | 626.5289 | 628.4123 | 636.556
Nambour Bulk | 307-2 | 307 Tee1 | Yandina | NCC Rating (A) | 755 | 755 | 755 | 755 | 755 | Rural | 170
Nambour Bulk | 307-2 | 307 Tee1 | Yandina | 10 POE Load (A) | 92.0262 | 92.2899 | 92.8482 | 93.1927 | 94.0818
Nambour Bulk | 307-2 | 307 Tee1 | Yandina | Power Factor | 0.93805 | 0.93796 | 0.93776 | 0.93764 | 0.93808
Nambour Bulk | 307-2 | 307 Tee1 | Yandina | ECC Rating (A) | 755 | 755 | 755 | 755 | 755
Nambour Bulk | 307-2 | 307 Tee1 | Yandina | 50 POE Load (A) | 149 | 151 | 151 | 152 | 152
Nambour Bulk | 344-1 | Nambour BS | Maleny | NCC Rating (A) | 155 | 155 | 155 | 155 | 155 | Rural | 170
Nambour Bulk | 344-1 | Nambour BS | Maleny | 10 POE Load (A) | 174.2583 | 173.2559 | 173.0327 | 172.1957 | 173.784
Nambour Bulk | 344-1 | Nambour BS | Maleny | Power Factor | 0.94586 | 0.94559 | 0.94553 | 0.9453 | 0.94573
Nambour Bulk | 344-1 | Nambour BS | Maleny | ECC Rating (A) | 155 | 155 | 155 | 200 | 200
Nambour Bulk | 344-1 | Nambour BS | Maleny | 50 POE Load (A) | 122 | 122 | 121 | 116 | 116
Nambour Bulk | 345-1 | Nambour BS | Kenilworth | NCC Rating (A) | 208 | 208 | 208 | 208 | 208 | Rural | 170
Nambour Bulk | 345-1 | Nambour BS | Kenilworth | 10 POE Load (A) | 83.8653 | 83.4372 | 83.2728 | 82.8714 | 83.3986
Nambour Bulk | 345-1 | Nambour BS | Kenilworth | Power Factor | 0.98999 | 0.99003 | 0.99004 | 0.99008 | 0.99003
Nambour Bulk | 345-1 | Nambour BS | Kenilworth | ECC Rating (A) | 208 | 208 | 208 | 208 | 208
Nambour Bulk | 345-1 | Nambour BS | Kenilworth | 50 POE Load (A) | 78 | 78 | 77 | 77 | 77
Nambour Bulk | 347-1 | Nambour BS | 347 Tee1 | NCC Rating (A) | 412 | 412 | 412 | 412 | 412 | Rural | 170
Nambour Bulk | 347-1 | Nambour BS | 347 Tee1 | 10 POE Load (A) | 199.9821 | 200.7128 | 202.4932 | 204.2049 | 207.9162
Nambour Bulk | 347-1 | Nambour BS | 347 Tee1 | Power Factor | 0.95896 | 0.95882 | 0.95849 | 0.95816 | 0.95745
Nambour Bulk | 347-1 | Nambour BS | 347 Tee1 | ECC Rating (A) | 412 | 412 | 412 | 412 | 412
Nambour Bulk | 347-1 | Nambour BS | 347 Tee1 | 50 POE Load (A) | 371.0688 | 371.9879 | 375.2324 | 378.3471 | 385.1164
Nambour Bulk | 347-2 | 347 Tee1 | Palmwoods Central | NCC Rating (A) | 357 | 357 | 357 | 357 | 357 | Rural | 170
Nambour Bulk | 347-2 | 347 Tee1 | Palmwoods Central | 10 POE Load (A) | 200.4899 | 201.2213 | 203.0033 | 204.7166 | 208.4314
Nambour Bulk | 347-2 | 347 Tee1 | Palmwoods Central | Power Factor | 0.96153 | 0.96142 | 0.96116 | 0.96091 | 0.96035
Nambour Bulk | 347-2 | 347 Tee1 | Palmwoods Central | ECC Rating (A) | 357 | 357 | 357 | 357 | 357
Nambour Bulk | 347-2 | 347 Tee1 | Palmwoods Central | 50 POE Load (A) | 430.0053 | 458.095 | 469.5727 | 480.8608 | 495.7745
Nambour Bulk | 347-3 | 347 Tee1 | Landsborough | NCC Rating (A) | 403 | 403 | 403 | 403 | 403 | Rural | 170
Nambour Bulk | 347-3 | 347 Tee1 | Landsborough | 10 POE Load (A) | 1.6474 | 1.6471 | 1.6465 | 1.6459 | 1.6447
Nambour Bulk | 347-3 | 347 Tee1 | Landsborough | Power Factor | 0.00019082 | 0.00019082 | 0.00019082 | 0.00019082 | 0.00019082
Nambour Bulk | 347-3 | 347 Tee1 | Landsborough | ECC Rating (A) | 403 | 403 | 403 | 403 | 403
Nambour Bulk | 347-3 | 347 Tee1 | Landsborough | 50 POE Load (A) | 245.8737 | 273.5057 | 283.36 | 293.0896 | 304.6159
Nambour Bulk | 348-1 | Nambour BS | Palmwoods Central | NCC Rating (A) | 403 | 403 | 403 | 403 | 403 | Rural | 170
Nambour Bulk | 348-1 | Nambour BS | Palmwoods Central | 10 POE Load (A) | 255.9011 | 256.8358 | 259.1133 | 261.3029 | 266.0505
Nambour Bulk | 348-1 | Nambour BS | Palmwoods Central | Power Factor | 0.95467 | 0.95455 | 0.95424 | 0.95395 | 0.95331
Nambour Bulk | 348-1 | Nambour BS | Palmwoods Central | ECC Rating (A) | 403 | 403 | 403 | 403 | 403
Nambour Bulk | 348-1 | Nambour BS | Palmwoods Central | 50 POE Load (A) | 422.3868 | 423.4378 | 427.1334 | 430.6813 | 438.392
Nambour Bulk | 489-1 | Nambour BS | Yandina | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
Nambour Bulk | 489-1 | Nambour BS | Yandina | 10 POE Load (A) | 82.889 | 83.1277 | 83.6329 | 83.9447 | 84.7539
Nambour Bulk | 489-1 | Nambour BS | Yandina | Power Factor | 0.99979 | 0.99979 | 0.99981 | 0.99981 | 0.99983
Nambour Bulk | 489-1 | Nambour BS | Yandina | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
Nambour Bulk | 489-1 | Nambour BS | Yandina | 50 POE Load (A) | 196 | 197 | 198 | 198 | 198
Nudgee Bulk | 3280-1 | Hendra | Clayfield | NCC Rating (A) | 725 | 725 | 725 | 725 | 725 | Urban | 70
Nudgee Bulk | 3280-1 | Hendra | Clayfield | 10 POE Load (A) | 169.302 | 169.9415 | 170.8055 | 171.7045 | 173.7939
Nudgee Bulk | 3280-1 | Hendra | Clayfield | Power Factor | 0.98018 | 0.98009 | 0.97996 | 0.97984 | 0.97956
Nudgee Bulk | 3280-1 | Hendra | Clayfield | ECC Rating (A) | 725 | 725 | 725 | 725 | 725
Nudgee Bulk | 3280-1 | Hendra | Clayfield | 50 POE Load (A) | 155.6372 | 156.2197 | 157.1021 | 157.9269 | 159.8431
Nudgee Bulk | 540-1 | Hendra | Nundah | NCC Rating (A) | 704 | 704 | 704 | 704 | 704 | Urban | 70
Nudgee Bulk | 540-1 | Hendra | Nundah | 10 POE Load (A) | 234.5785 | 240.3312 | 240.9458 | 242.2334 | 245.5059
Nudgee Bulk | 540-1 | Hendra | Nundah | Power Factor | -0.98191 | -0.98096 | -0.98104 | -0.98086 | -0.98051
Nudgee Bulk | 540-1 | Hendra | Nundah | ECC Rating (A) | 704 | 704 | 704 | 704 | 704
Nudgee Bulk | 540-1 | Hendra | Nundah | 50 POE Load (A) | 406 | 408 | 408 | 408 | 408
Nudgee Bulk | 593-1 | Nudgee BS | Nundah | NCC Rating (A) | 696 | 696 | 696 | 696 | 696 | Urban | 192
Nudgee Bulk | 593-1 | Nudgee BS | Nundah | 10 POE Load (A) | 652.0032 | 656.4784 | 656.8133 | 657.6467 | 663.2462
Nudgee Bulk | 593-1 | Nudgee BS | Nundah | Power Factor | -0.97201 | -0.9717 | -0.97176 | -0.97172 | -0.97148
Nudgee Bulk | 593-1 | Nudgee BS | Nundah | ECC Rating (A) | 696 | 696 | 696 | 696 | 696
Nudgee Bulk | 593-1 | Nudgee BS | Nundah | 50 POE Load (A) | 771 | 772 | 772 | 770 | 770
Nudgee Bulk | 604-1 | Nudgee BS | Geebung | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Urban | 70
Nudgee Bulk | 604-1 | Nudgee BS | Geebung | 10 POE Load (A) | 208.5502 | 206.413 | 203.9097 | 206.3732 | 204.9874
Nudgee Bulk | 604-1 | Nudgee BS | Geebung | Power Factor | -0.99159 | -0.99193 | -0.99233 | -0.9704 | -0.97079
Nudgee Bulk | 604-1 | Nudgee BS | Geebung | ECC Rating (A) | 491 | 491 | 491 | 491 | 491
Nudgee Bulk | 604-1 | Nudgee BS | Geebung | 50 POE Load (A) | 289 | 286 | 284 | 282 | 191.9834
Nudgee Bulk | 605-1 | Nudgee BS | Geebung | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Urban | 70
Nudgee Bulk | 605-1 | Nudgee BS | Geebung | 10 POE Load (A) | 208.7903 | 206.6507 | 204.1447 | 206.6077 | 205.2203
Nudgee Bulk | 605-1 | Nudgee BS | Geebung | Power Factor | 0.99989 | 0.99995 | 0.99999 | 1 | 1
Nudgee Bulk | 605-1 | Nudgee BS | Geebung | ECC Rating (A) | 491 | 491 | 491 | 491 | 491
Nudgee Bulk | 605-1 | Nudgee BS | Geebung | 50 POE Load (A) | 289 | 286 | 284 | 282 | 192.2016
Nudgee Bulk | 622-1 | Nudgee BS | Hendra | NCC Rating (A) | 738 | 738 | 738 | 738 | 738 | Urban | 70
Nudgee Bulk | 622-1 | Nudgee BS | Hendra | 10 POE Load (A) | 448.485 | 454.9272 | 455.5288 | 456.872 | 461.7519
Nudgee Bulk | 622-1 | Nudgee BS | Hendra | Power Factor | 0.971 | 0.97068 | 0.97064 | 0.97034 | 0.96997
Nudgee Bulk | 622-1 | Nudgee BS | Hendra | ECC Rating (A) | 738 | 738 | 738 | 738 | 738
Nudgee Bulk | 622-1 | Nudgee BS | Hendra | 50 POE Load (A) | 699 | 701 | 701 | 699 | 427.6815
Nudgee Bulk | 623-1 | Nudgee BS | Hendra | NCC Rating (A) | 738 | 738 | 738 | 738 | 738 | Urban | 70
Nudgee Bulk | 623-1 | Nudgee BS | Hendra | 10 POE Load (A) | 448.485 | 454.9272 | 455.5288 | 456.872 | 461.7519
Nudgee Bulk | 623-1 | Nudgee BS | Hendra | Power Factor | 0.971 | 0.97068 | 0.97064 | 0.97034 | 0.96997
Nudgee Bulk | 623-1 | Nudgee BS | Hendra | ECC Rating (A) | 738 | 738 | 738 | 738 | 738
Nudgee Bulk | 623-1 | Nudgee BS | Hendra | 50 POE Load (A) | 699 | 701 | 701 | 699 | 427.6815
Nudgee Bulk | 636-1 | Hendra | Clayfield | NCC Rating (A) | 725 | 725 | 725 | 725 | 725 | Urban | 70
Nudgee Bulk | 636-1 | Hendra | Clayfield | 10 POE Load (A) | 170.2023 | 170.8451 | 171.7109 | 172.6147 | 174.715
Nudgee Bulk | 636-1 | Hendra | Clayfield | Power Factor | -0.9678 | -0.96773 | -0.96813 | -0.96803 | -0.96779
Nudgee Bulk | 636-1 | Hendra | Clayfield | ECC Rating (A) | 725 | 725 | 725 | 725 | 725
Nudgee Bulk | 636-1 | Hendra | Clayfield | 50 POE Load (A) | 336 | 337 | 337 | 336 | 336
Nudgee Bulk | 643-1 | Hendra | Hamilton | NCC Rating (A) | 711 | 711 | 711 | 711 | 711 | Urban | 70
Nudgee Bulk | 643-1 | Hendra | Hamilton | 10 POE Load (A) | 214.6259 | 215.9602 | 217.7613 | 219.3703 | 222.5142
Nudgee Bulk | 643-1 | Hendra | Hamilton | Power Factor | 0.97185 | 0.97168 | 0.97145 | 0.97064 | 0.97023
Nudgee Bulk | 643-1 | Hendra | Hamilton | ECC Rating (A) | 760 | 760 | 760 | 760 | 760
Nudgee Bulk | 643-1 | Hendra | Hamilton | 50 POE Load (A) | 401.9059 | 404.3896 | 407.4259 | 410.4262 | 416.2848
Nudgee Bulk | 674-1 | Hendra | Hamilton | NCC Rating (A) | 711 | 711 | 711 | 711 | 711 | Urban | 70
Nudgee Bulk | 674-1 | Hendra | Hamilton | 10 POE Load (A) | 214.1575 | 215.4888 | 217.286 | 218.8915 | 222.0285
Nudgee Bulk | 674-1 | Hendra | Hamilton | Power Factor | 0.97183 | 0.97166 | 0.97144 | 0.97062 | 0.97021
Nudgee Bulk | 674-1 | Hendra | Hamilton | ECC Rating (A) | 760 | 760 | 760 | 760 | 760
Nudgee Bulk | 674-1 | Hendra | Hamilton | 50 POE Load (A) | 385 | 388 | 390 | 390 | 390
Nudgee Bulk | 683-1 | Nudgee BS | Geebung | NCC Rating (A) | 478 | 478 | 478 | 478 | 478 | Urban | 70
Nudgee Bulk | 683-1 | Nudgee BS | Geebung | 10 POE Load (A) | 204.8895 | 202.7995 | 200.3519 | 202.3048 | 200.9462
Nudgee Bulk | 683-1 | Nudgee BS | Geebung | Power Factor | -0.98689 | -0.98734 | -0.98788 | -0.96104 | -0.96152
Nudgee Bulk | 683-1 | Nudgee BS | Geebung | ECC Rating (A) | 478 | 478 | 478 | 478 | 478
Nudgee Bulk | 683-1 | Nudgee BS | Geebung | 50 POE Load (A) | 283 | 280 | 278 | 276 | 276
Postmans Ridge Bulk | 376-1 | Postmans Ridge BS | Helidon | NCC Rating (A) | 290 | 290 | 290 | 290 | 290 | Rural | 170
Postmans Ridge Bulk | 376-1 | Postmans Ridge BS | Helidon | 10 POE Load (A) | 62.3043 | 61.7139 | 61.2649 | 60.7608 | 60.9591
Postmans Ridge Bulk | 376-1 | Postmans Ridge BS | Helidon | Power Factor | 0.96291 | 0.96308 | 0.96321 | 0.96335 | 0.9633
Postmans Ridge Bulk | 376-1 | Postmans Ridge BS | Helidon | ECC Rating (A) | 290 | 290 | 290 | 290 | 290
Postmans Ridge Bulk | 376-1 | Postmans Ridge BS | Helidon | 50 POE Load (A) | 57.772 | 57.2259 | 56.8105 | 56.3441 | 56.5275
Postmans Ridge Bulk | 379-1 | Postmans Ridge BS | Carpendale | NCC Rating (A) | 200 | 200 | 200 | 200 | 200 | Rural | 170
Postmans Ridge Bulk | 379-1 | Postmans Ridge BS | Carpendale | 10 POE Load (A) | 32.9388 | 32.9584 | 32.8962 | 32.7598 | 32.9403
Postmans Ridge Bulk | 379-1 | Postmans Ridge BS | Carpendale | Power Factor | 0.99474 | 0.99473 | 0.99475 | 0.99478 | 0.99474
Postmans Ridge Bulk | 379-1 | Postmans Ridge BS | Carpendale | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Postmans Ridge Bulk | 379-1 | Postmans Ridge BS | Carpendale | 50 POE Load (A) | 29.6583 | 29.6759 | 29.62 | 29.4974 | 29.6596
Postmans Ridge Bulk | 379-2 | Carpendale | Tenthill | NCC Rating (A) | 155 | 155 | 155 | 155 | 155 | Rural | 170
Postmans Ridge Bulk | 379-2 | Carpendale | Tenthill | 10 POE Load (A) | 0.6661 | 0.6661 | 0.66611 | 0.66612 | 0.6661
Postmans Ridge Bulk | 379-2 | Carpendale | Tenthill | Power Factor | 0.0001188 | 0.00011877 | 0.00011878 | 0.00011876 | 0.00011886
Raceview Bulk | 354-1 | Raceview BS | Roderick St | NCC Rating (A) | 497 | 497 | 497 | 497 | 497 | Urban | 70
Raceview Bulk | 354-1 | Raceview BS | Roderick St | 10 POE Load (A) | 344.9385 | 343.4682 | 343.1216 | 342.1126 | 343.5073
Raceview Bulk | 354-1 | Raceview BS | Roderick St | Power Factor | 0.99532 | 0.99544 | 0.99547 | 0.99556 | 0.99545
Raceview Bulk | 354-1 | Raceview BS | Roderick St | ECC Rating (A) | 517 | 517 | 517 | 517 | 517
Raceview Bulk | 354-1 | Raceview BS | Roderick St | 50 POE Load (A) | 447 | 448 | 449 | 449 | 449
Raceview Bulk | 355-1 | Roderick St | Booval | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 70
Raceview Bulk | 355-1 | Roderick St | Booval | 10 POE Load (A) | 175.7175 | 174.9238 | 174.4244 | 173.7579 | 174.0246
Raceview Bulk | 355-1 | Roderick St | Booval | Power Factor | -0.97793 | -0.9782 | -0.97832 | -0.97853 | -0.97837
Raceview Bulk | 355-1 | Roderick St | Booval | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
Raceview Bulk | 355-1 | Roderick St | Booval | 50 POE Load (A) | 451 | 452 | 453 | 453 | 453
Raceview Bulk | 361-1 | Raceview BS | Booval | NCC Rating (A) | 631 | 631 | 631 | 631 | 631 | Urban | 70
Raceview Bulk | 361-1 | Raceview BS | Booval | 10 POE Load (A) | 404.3828 | 402.7618 | 403.1358 | 402.3183 | 405.0329
Raceview Bulk | 361-1 | Raceview BS | Booval | Power Factor | 0.98994 | 0.99009 | 0.99005 | 0.99013 | 0.98987
Raceview Bulk | 361-1 | Raceview BS | Booval | ECC Rating (A) | 631 | 631 | 631 | 631 | 631
Raceview Bulk | 361-1 | Raceview BS | Booval | 50 POE Load (A) | 545 | 547 | 548 | 548 | 548
Raceview Bulk | 362-1 | Raceview BS | 362 Tee1 | NCC Rating (A) | 357 | 357 | 357 | 357 | 357 | Rural | 170
Raceview Bulk | 362-1 | Raceview BS | 362 Tee1 | 10 POE Load (A) | 162.7542 | 162.7636 | 163.234 | 163.3376 | 169.3417
Raceview Bulk | 362-1 | Raceview BS | 362 Tee1 | Power Factor | 0.98839 | 0.98848 | 0.98848 | 0.98855 | 0.98765
Raceview Bulk | 362-1 | Raceview BS | 362 Tee1 | ECC Rating (A) | 357 | 357 | 357 | 357 | 357
Raceview Bulk | 362-1 | Raceview BS | 362 Tee1 | 50 POE Load (A) | 366 | 376 | 384 | 391 | 391
Raceview Bulk | 362-2 | 362 Tee1 | Flinders | NCC Rating (A) | 708 | 708 | 708 | 708 | 708 | Rural | 170
Raceview Bulk | 362-2 | 362 Tee1 | Flinders | 10 POE Load (A) | 52.3479 | 51.6778 | 51.1256 | 50.4237 | 46.8156
Raceview Bulk | 362-2 | 362 Tee1 | Flinders | Power Factor | 0.677 | 0.67297 | 0.6675 | 0.66278 | 0.61403
Raceview Bulk | 362-2 | 362 Tee1 | Flinders | ECC Rating (A) | 708 | 708 | 708 | 708 | 708
Raceview Bulk | 362-2 | 362 Tee1 | Flinders | 50 POE Load (A) | 195 | 203 | 211 | 218 | 218
Raceview Bulk | 362-3 | 362 Tee1 | Kalbar | NCC Rating (A) | 708 | 708 | 708 | 708 | 708 | Rural | 170
Raceview Bulk | 362-3 | 362 Tee1 | Kalbar | 10 POE Load (A) | 204.5844 | 203.8201 | 203.5792 | 202.8637 | 203.9697
Raceview Bulk | 362-3 | 362 Tee1 | Kalbar | Power Factor | 0.96951 | 0.96972 | 0.96978 | 0.96998 | 0.96961
Raceview Bulk | 362-3 | 362 Tee1 | Kalbar | ECC Rating (A) | 708 | 708 | 708 | 708 | 708
Raceview Bulk | 362-3 | 362 Tee1 | Kalbar | 50 POE Load (A) | 305 | 306 | 306 | 305 | 305
Raceview Bulk | 363-1 | Raceview BS | 363 Tee1 | NCC Rating (A) | 351 | 351 | 351 | 351 | 351 | Rural | 170
Raceview Bulk | 363-1 | Raceview BS | 363 Tee1 | 10 POE Load (A) | 160.2722 | 160.2458 | 160.6709 | 160.7341 | 166.35
Raceview Bulk | 363-1 | Raceview BS | 363 Tee1 | Power Factor | 0.99242 | 0.99249 | 0.99249 | 0.99254 | 0.9918
Raceview Bulk | 363-1 | Raceview BS | 363 Tee1 | ECC Rating (A) | 351 | 351 | 351 | 351 | 351
Raceview Bulk | 363-1 | Raceview BS | 363 Tee1 | 50 POE Load (A) | 347 | 356 | 364 | 370 | 370
Raceview Bulk | 363-2 | 363 Tee1 | Flinders | NCC Rating (A) | 403 | 403 | 403 | 403 | 403 | Rural | 170
Raceview Bulk | 363-2 | 363 Tee1 | Flinders | 10 POE Load (A) | 12.5115 | 12.1802 | 11.8551 | 11.5504 | 10.4931
Raceview Bulk | 363-2 | 363 Tee1 | Flinders | Power Factor | -0.73853 | -0.71205 | -0.68261 | -0.6479 | -0.3081
Raceview Bulk | 363-2 | 363 Tee1 | Flinders | ECC Rating (A) | 403 | 403 | 403 | 403 | 403
Raceview Bulk | 363-2 | 363 Tee1 | Flinders | 50 POE Load (A) | 196 | 203 | 210 | 217 | 217
Raceview Bulk | 363-3 | 363 Tee1 | Kalbar | NCC Rating (A) | 374 | 374 | 374 | 374 | 374 | Rural | 170
Raceview Bulk | 363-3 | 363 Tee1 | Kalbar | 10 POE Load (A) | 167.9436 | 167.3519 | 167.1928 | 166.6444 | 167.8535
Raceview Bulk | 363-3 | 363 Tee1 | Kalbar | Power Factor | 0.99998 | 0.99999 | 0.99999 | 0.99999 | 0.99998
Raceview Bulk | 363-3 | 363 Tee1 | Kalbar | ECC Rating (A) | 374 | 374 | 374 | 374 | 374
Raceview Bulk | 363-3 | 363 Tee1 | Kalbar | 50 POE Load (A) | 325 | 326 | 325 | 324 | 324
Raceview Bulk | 3960-1 | Ipswich Sth | Yamanto | NCC Rating (A) | 711 | 711 | 711 | 711 | 711 | Urban | 70
Raceview Bulk | 3960-1 | Ipswich Sth | Yamanto | 10 POE Load (A) | 438.612 | 446.593 | 456.2205 | 464.2906 | 480.15
Raceview Bulk | 3960-1 | Ipswich Sth | Yamanto | Power Factor | 0.94493 | 0.94439 | 0.94357 | 0.94293 | 0.94134
Raceview Bulk | 3960-1 | Ipswich Sth | Yamanto | ECC Rating (A) | 711 | 711 | 711 | 711 | 711
Raceview Bulk | 3960-1 | Ipswich Sth | Yamanto | 50 POE Load (A) | 375.984 | 382.4678 | 390.3165 | 396.8644 | 411.146
Raceview Bulk | 3972-1 | Yamanto | Flinders | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Raceview Bulk | 3972-1 | Yamanto | Flinders | 10 POE Load (A) | 165.5848 | 164.5428 | 163.9045 | 162.933 | 169.1219
Raceview Bulk | 3972-1 | Yamanto | Flinders | Power Factor | 0.90555 | 0.90527 | 0.90466 | 0.90435 | 0.90145
Raceview Bulk | 3972-1 | Yamanto | Flinders | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Raceview Bulk | 3972-1 | Yamanto | Flinders | 50 POE Load (A) | 286 | 300 | 314 | 326 | 326
Raceview Bulk | 3980-1 | Kalbar | Boonah | NCC Rating (A) | 713 | 713 | 713 | 713 | 713 | Rural | 170
Raceview Bulk | 3980-1 | Kalbar | Boonah | 10 POE Load (A) | 100.556 | 100.1132 | 99.9825 | 99.6052 | 100.2476
Raceview Bulk | 3980-1 | Kalbar | Boonah | Power Factor | 0.98184 | 0.98193 | 0.98195 | 0.98203 | 0.98185
Raceview Bulk | 3980-1 | Kalbar | Boonah | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
Raceview Bulk | 3980-1 | Kalbar | Boonah | 50 POE Load (A) | 145 | 144 | 144 | 144 | 144
Raceview Bulk | 401-1 | Kalbar | Boonah | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170
Raceview Bulk | 401-1 | Kalbar | Boonah | 10 POE Load (A) | 96.2418 | 95.8167 | 95.6913 | 95.3288 | 95.9465
Raceview Bulk | 401-1 | Kalbar | Boonah | Power Factor | 0.98195 | 0.98204 | 0.98206 | 0.98214 | 0.98196
Raceview Bulk | 401-1 | Kalbar | Boonah | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Raceview Bulk | 401-1 | Kalbar | Boonah | 50 POE Load (A) | 145 | 145 | 145 | 145 | 145
Raceview Bulk | 411-1 | Raceview BS | Booval | NCC Rating (A) | 558 | 558 | 558 | 558 | 558 | Urban | 70
Raceview Bulk | 411-1 | Raceview BS | Booval | 10 POE Load (A) | 342.194 | 340.8225 | 341.139 | 340.4472 | 342.7441
Raceview Bulk | 411-1 | Raceview BS | Booval | Power Factor | 0.99533 | 0.99544 | 0.99541 | 0.99546 | 0.99528
Raceview Bulk | 411-1 | Raceview BS | Booval | ECC Rating (A) | 631 | 631 | 631 | 631 | 631
Raceview Bulk | 411-1 | Raceview BS | Booval | 50 POE Load (A) | 530 | 531 | 533 | 532 | 532
Raceview Bulk | 509A-1 | Raceview BS | Ipswich Sth | NCC Rating (A) | 721 | 721 | 721 | 721 | 721 | Urban | 70
Raceview Bulk | 509A-1 | Raceview BS | Ipswich Sth | 10 POE Load (A) | 461.7569 | 471.9866 | 484.1355 | 495.1199 | 511.4675
Raceview Bulk | 509A-1 | Raceview BS | Ipswich Sth | Power Factor | 0.96453 | 0.96385 | 0.96319 | 0.96243 | 0.96129
Raceview Bulk | 509A-1 | Raceview BS | Ipswich Sth | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Raceview Bulk | 509A-1 | Raceview BS | Ipswich Sth | 50 POE Load (A) | 711 | 731 | 748 | 763 | 763
Raceview Bulk | 509B-1 | Raceview BS | Cooneana | NCC Rating (A) | 455 | 455 | 455 | 455 | 455 | Rural | 170
Raceview Bulk | 509B-1 | Raceview BS | Cooneana | 10 POE Load (A) | 0.61752 | 0.61752 | 0.61752 | 0.61752 | 0.61752
Raceview Bulk | 509B-1 | Raceview BS | Cooneana | Power Factor | 8.7908e-06 | 8.7907e-06 | 8.7913e-06 | 8.791e-06 | 8.7909e-06
Raceview Bulk | 510A-1 | Raceview BS | Ipswich Sth | NCC Rating (A) | 721 | 721 | 721 | 721 | 721 | Urban | 70
Raceview Bulk | 510A-1 | Raceview BS | Ipswich Sth | 10 POE Load (A) | 457.1179 | 467.2447 | 479.2712 | 490.1451 | 506.3281
Raceview Bulk | 510A-1 | Raceview BS | Ipswich Sth | Power Factor | 0.96456 | 0.96388 | 0.96322 | 0.96246 | 0.96132
Raceview Bulk | 510A-1 | Raceview BS | Ipswich Sth | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Raceview Bulk | 510A-1 | Raceview BS | Ipswich Sth | 50 POE Load (A) | 711 | 731 | 748 | 763 | 763
Raceview Bulk | 510B-1 | Raceview BS | Cooneana | NCC Rating (A) | 426 | 426 | 426 | 426 | 426 | Rural | 170
Raceview Bulk | 510B-1 | Raceview BS | Cooneana | 10 POE Load (A) | 0.72281 | 0.72281 | 0.72281 | 0.72281 | 0.72281
Raceview Bulk | 510B-1 | Raceview BS | Cooneana | Power Factor | 1.6632e-05 | 1.6632e-05 | 1.6632e-05 | 1.6632e-05 | 1.6632e-05
Richlands Bulk | 3818-1 | Richlands BS | Wacol | NCC Rating (A) | 750 | 750 | 750 | 750 | 750 | Urban | 70
Richlands Bulk | 3818-1 | Richlands BS | Wacol | 10 POE Load (A) | 110.0573 | 112.676 | 111.8734 | 110.7774 | 110.4406
Richlands Bulk | 3818-1 | Richlands BS | Wacol | Power Factor | 0.99807 | 0.99861 | 0.99845 | 0.99823 | 0.99816
Richlands Bulk | 3818-1 | Richlands BS | Wacol | ECC Rating (A) | 750 | 750 | 750 | 750 | 750
Richlands Bulk | 3818-1 | Richlands BS | Wacol | 50 POE Load (A) | 211.8754 | 217.2963 | 215.7508 | 213.6407 | 212.9916
Richlands Bulk | 454-1 | Richlands BS | Wacol Sth | NCC Rating (A) | 430 | 430 | 430 | 430 | 430 | Urban | 70
Richlands Bulk | 454-1 | Richlands BS | Wacol Sth | 10 POE Load (A) | 205.4729 | 204.8058 | 204.1512 | 202.9286 | 203.9937
Richlands Bulk | 454-1 | Richlands BS | Wacol Sth | Power Factor | 0.97309 | 0.97315 | 0.97322 | 0.97335 | 0.97323
Richlands Bulk | 454-1 | Richlands BS | Wacol Sth | ECC Rating (A) | 460 | 460 | 460 | 460 | 460
Richlands Bulk | 454-1 | Richlands BS | Wacol Sth | 50 POE Load (A) | 369 | 367 | 367 | 365 | 365
Richlands Bulk | 455-1 | Richlands BS | Wacol Sth | NCC Rating (A) | 430 | 430 | 430 | 430 | 430 | Urban | 70
Richlands Bulk | 455-1 | Richlands BS | Wacol Sth | 10 POE Load (A) | 206.7881 | 206.1168 | 205.4579 | 204.2275 | 205.2995
Richlands Bulk | 455-1 | Richlands BS | Wacol Sth | Power Factor | 0.97313 | 0.9732 | 0.97326 | 0.9734 | 0.97328
Richlands Bulk | 455-1 | Richlands BS | Wacol Sth | ECC Rating (A) | 460 | 460 | 460 | 460 | 460
Richlands Bulk | 455-1 | Richlands BS | Wacol Sth | 50 POE Load (A) | 369 | 367 | 367 | 364 | 364
Richlands Bulk | 543-1 | Inala | 543 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Richlands Bulk | 543-1 | Inala | 543 Tee1 | 10 POE Load (A) | 2.9547 | 2.9545 | 2.9542 | 2.9539 | 2.9536
Richlands Bulk | 543-1 | Inala | 543 Tee1 | Power Factor | -8.3786e-05 | -8.3786e-05 | -8.3786e-05 | -8.3786e-05 | -8.3786e-05
Richlands Bulk | 543-1 | Inala | 543 Tee1 | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Richlands Bulk | 543-1 | Inala | 543 Tee1 | 50 POE Load (A) | 573.1264 | 572.8223 | 572.4711 | 571.1734 | 574.1806
Richlands Bulk | 543-2 | 543 Tee1 | Coopers Plains | NCC Rating (A) | 348 | 348 | 348 | 348 | 348 | Urban | 70
Richlands Bulk | 543-2 | 543 Tee1 | Coopers Plains | 10 POE Load (A) | 0.21157 | 0.21155 | 0.21153 | 0.21151 | 0.21149
Richlands Bulk | 543-2 | 543 Tee1 | Coopers Plains | Power Factor | -7.5154e-06 | -7.5156e-06 | -7.5151e-06 | -7.5144e-06 | -7.5148e-06
Richlands Bulk | 543-2 | 543 Tee1 | Coopers Plains | ECC Rating (A) | 348 | 348 | 348 | 348 | 348
Richlands Bulk | 543-2 | 543 Tee1 | Coopers Plains | 50 POE Load (A) | 299.6976 | 293.4279 | 287.3237 | 280.5405 | 276.1298
Richlands Bulk | 543-3 | 543 Tee1 | Heathwood | NCC Rating (A) | 807 | 807 | 807 | 807 | 807 | Urban | 70
Richlands Bulk | 543-3 | 543 Tee1 | Heathwood | 10 POE Load (A) | 2.2085 | 2.2084 | 2.2081 | 2.2079 | 2.2077
Richlands Bulk | 543-3 | 543 Tee1 | Heathwood | Power Factor | 9.1011e-05 | 9.1011e-05 | 9.1011e-05 | 9.1011e-05 | 9.1011e-05
Richlands Bulk | 543-3 | 543 Tee1 | Heathwood | ECC Rating (A) | 807 | 807 | 807 | 807 | 807
Richlands Bulk | 543-3 | 543 Tee1 | Heathwood | 50 POE Load (A) | 572.3796 | 572.0755 | 571.7245 | 570.4268 | 573.4341
Richlands Bulk | 616-1 | Richlands BS | Darra | NCC Rating (A) | 407 | 407 | 407 | 407 | 407 | Urban | 70
Richlands Bulk | 616-1 | Richlands BS | Darra | 10 POE Load (A) | 253.3807 | 251.2438 | 249.491 | 247.1466 | 246.1179
Richlands Bulk | 616-1 | Richlands BS | Darra | Power Factor | 0.93306 | 0.93026 | 0.92784 | 0.92446 | 0.92294
Richlands Bulk | 616-1 | Richlands BS | Darra | ECC Rating (A) | 440 | 440 | 440 | 440 | 440
Richlands Bulk | 616-1 | Richlands BS | Darra | 50 POE Load (A) | 356 | 353 | 351 | 349 | 356
Richlands Bulk | 617-1 | Richlands BS | Darra | NCC Rating (A) | 407 | 407 | 407 | 407 | 407 | Urban | 70
Richlands Bulk | 617-1 | Richlands BS | Darra | 10 POE Load (A) | 261.8059 | 259.5958 | 257.7828 | 255.3579 | 254.2939
Richlands Bulk | 617-1 | Richlands BS | Darra | Power Factor | 0.93334 | 0.93055 | 0.92813 | 0.92476 | 0.92324
Richlands Bulk | 617-1 | Richlands BS | Darra | ECC Rating (A) | 440 | 440 | 440 | 440 | 440
Richlands Bulk | 617-1 | Richlands BS | Darra | 50 POE Load (A) | 361 | 358 | 356 | 354 | 361
Richlands Bulk | 618-1 | Richlands BS | Inala | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70
Richlands Bulk | 618-1 | Richlands BS | Inala | 10 POE Load (A) | 375.0393 | 377.5939 | 380.46 | 382.9141 | 388.1022
Richlands Bulk | 618-1 | Richlands BS | Inala | Power Factor | 0.96028 | 0.96 | 0.95969 | 0.95942 | 0.95995
Richlands Bulk | 618-1 | Richlands BS | Inala | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
Richlands Bulk | 618-1 | Richlands BS | Inala | 50 POE Load (A) | 669 | 671 | 672 | 670 | 670
Richlands Bulk | 619-1 | Richlands BS | Inala | NCC Rating (A) | 550 | 550 | 550 | 550 | 550 | Urban | 70
Richlands Bulk | 619-1 | Richlands BS | Inala | 10 POE Load (A) | 242.2514 | 243.9009 | 245.7515 | 247.3362 | 250.6861
Richlands Bulk | 619-1 | Richlands BS | Inala | Power Factor | 0.96084 | 0.96056 | 0.96026 | 0.95999 | 0.96052
Richlands Bulk | 619-1 | Richlands BS | Inala | ECC Rating (A) | 550 | 550 | 550 | 550 | 550
Richlands Bulk | 619-1 | Richlands BS | Inala | 50 POE Load (A) | 539 | 542 | 544 | 543 | 543
Richlands Bulk | 620-1 | Richlands BS | Oxley | NCC Rating (A) | 324 | 324 | 324 | 324 | 324 | Urban | 70
Richlands Bulk | 620-1 | Richlands BS | Oxley | 10 POE Load (A) | 182.6596 | 180.3731 | 178.4235 | 175.6453 | 174.7807
Richlands Bulk | 620-1 | Richlands BS | Oxley | Power Factor | -0.95456 | -0.95485 | -0.9551 | -0.95545 | -0.95556
Richlands Bulk | 620-1 | Richlands BS | Oxley | ECC Rating (A) | 359 | 359 | 359 | 359 | 359
Richlands Bulk | 620-1 | Richlands BS | Oxley | 50 POE Load (A) | 336 | 334 | 333 | 331 | 331
Richlands Bulk | 621-1 | Richlands BS | Oxley | NCC Rating (A) | 324 | 324 | 324 | 324 | 324 | Urban | 70
Richlands Bulk | 621-1 | Richlands BS | Oxley | 10 POE Load (A) | 173.84 | 171.664 | 169.8085 | 167.1646 | 166.3417
Richlands Bulk | 621-1 | Richlands BS | Oxley | Power Factor | -0.94887 | -0.94918 | -0.94944 | -0.94982 | -0.94993
Richlands Bulk | 621-1 | Richlands BS | Oxley | ECC Rating (A) | 359 | 359 | 359 | 359 | 359
Richlands Bulk | 621-1 | Richlands BS | Oxley | 50 POE Load (A) | 336 | 334 | 333 | 331 | 331
Richlands Bulk | 641-1 | Darra | Jindalee | NCC Rating (A) | 703 | 703 | 703 | 703 | 703 | Urban | 70
Richlands Bulk | 641-1 | Darra | Jindalee | 10 POE Load (A) | 160.7842 | 157.871 | 155.897 | 153.2138 | 151.9403
Richlands Bulk | 641-1 | Darra | Jindalee | Power Factor | -0.97162 | -0.97195 | -0.97217 | -0.97248 | -0.97262
Richlands Bulk | 641-1 | Darra | Jindalee | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Richlands Bulk | 641-1 | Darra | Jindalee | 50 POE Load (A) | 259 | 258 | 257 | 255 | 255
Richlands Bulk | 642-1 | Darra | Jindalee | NCC Rating (A) | 703 | 703 | 703 | 703 | 703 | Urban | 70
Richlands Bulk | 642-1 | Darra | Jindalee | 10 POE Load (A) | 157.5758 | 154.7214 | 152.7873 | 150.1583 | 148.9105
Richlands Bulk | 642-1 | Darra | Jindalee | Power Factor | -0.97042 | -0.97076 | -0.97098 | -0.97129 | -0.97143
Richlands Bulk | 642-1 | Darra | Jindalee | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Richlands Bulk | 642-1 | Darra | Jindalee | 50 POE Load (A) | 259 | 258 | 257 | 255 | 255
Richlands Bulk | 679-1 | Richlands BS | Wacol | NCC Rating (A) | 605 | 605 | 605 | 605 | 605 | Urban | 70
Richlands Bulk | 679-1 | Richlands BS | Wacol | 10 POE Load (A) | 111.503 | 114.1918 | 113.3785 | 112.268 | 111.9267
Richlands Bulk | 679-1 | Richlands BS | Wacol | Power Factor | -0.98829 | -0.98758 | -0.98786 | -0.98823 | -0.98835
Richlands Bulk | 679-1 | Richlands BS | Wacol | ECC Rating (A) | 605 | 605 | 605 | 605 | 605
Richlands Bulk | 679-1 | Richlands BS | Wacol | 50 POE Load (A) | 211.8754 | 217.2963 | 215.7508 | 213.6407 | 212.9916
Richlands Bulk | 680-1 | Richlands BS | Wacol | NCC Rating (A) | 750 | 750 | 750 | 750 | 750 | Urban | 70
Richlands Bulk | 680-1 | Richlands BS | Wacol | 10 POE Load (A) | 224.1441 | 229.7329 | 228.0459 | 225.744 | 225.0369
Richlands Bulk | 680-1 | Richlands BS | Wacol | Power Factor | 0.99919 | 0.99877 | 0.99891 | 0.99908 | 0.99913
Richlands Bulk | 680-1 | Richlands BS | Wacol | ECC Rating (A) | 750 | 750 | 750 | 750 | 750
Richlands Bulk | 680-1 | Richlands BS | Wacol | 50 POE Load (A) | 113 | 113 | 112 | 111 | 111
Richlands Bulk | 700-1 | Richlands BS | Darra | NCC Rating (A) | 517 | 517 | 517 | 517 | 517 | Urban | 70
Richlands Bulk | 700-1 | Richlands BS | Darra | 10 POE Load (A) | 200.4126 | 198.724 | 197.3389 | 195.4866 | 194.6738
Richlands Bulk | 700-1 | Richlands BS | Darra | Power Factor | 0.95873 | 0.95651 | 0.95457 | 0.95186 | 0.95063
Richlands Bulk | 700-1 | Richlands BS | Darra | ECC Rating (A) | 517 | 517 | 517 | 517 | 517
Richlands Bulk | 700-1 | Richlands BS | Darra | 50 POE Load (A) | 282 | 279 | 278 | 276 | 276
Runcorn Bulk | 3440-1 | Runcorn BS | Sunnybank | NCC Rating (A) | 544 | 544 | 544 | 544 | 544 | Urban | 70
Runcorn Bulk | 3440-1 | Runcorn BS | Sunnybank | 10 POE Load (A) | 497.2027 | 493.7052 | 490.4104 | 485.0155 | 484.8502
Runcorn Bulk | 3440-1 | Runcorn BS | Sunnybank | Power Factor | 0.98802 | 0.98832 | 0.98859 | 0.98903 | 0.98905
Runcorn Bulk | 3440-1 | Runcorn BS | Sunnybank | ECC Rating (A) | 544 | 544 | 544 | 544 | 544
Runcorn Bulk | 3440-1 | Runcorn BS | Sunnybank | 50 POE Load (A) | 540 | 541 | 541 | 541 | 541
Runcorn Bulk | 433-1 | Runcorn BS | Calamvale | NCC Rating (A) | 406 | 406 | 406 | 406 | 406 | Urban | 70
Runcorn Bulk | 433-1 | Runcorn BS | Calamvale | 10 POE Load (A) | 2.3615 | 2.3615 | 2.3615 | 2.3615 | 2.3615
Runcorn Bulk | 433-1 | Runcorn BS | Calamvale | Power Factor | 4.0608e-05 | 4.0608e-05 | 4.0608e-05 | 4.0608e-05 | 4.0608e-05
Runcorn Bulk | 433-1 | Runcorn BS | Calamvale | ECC Rating (A) | 406 | 406 | 406 | 406 | 406
Runcorn Bulk | 433-1 | Runcorn BS | Calamvale | 50 POE Load (A) | 2.3615 | 2.3615 | 2.3615 | 2.3615 | 2.3615
Runcorn Bulk | 434-1 | Runcorn | Calamvale | NCC Rating (A) | 406 | 406 | 406 | 406 | 406 | Urban | 70
Runcorn Bulk | 434-1 | Runcorn | Calamvale | 10 POE Load (A) | 1.6813 | 1.6813 | 1.6813 | 1.6812 | 1.6811
Runcorn Bulk | 434-1 | Runcorn | Calamvale | Power Factor | 6.272e-05 | 6.272e-05 | 6.272e-05 | 6.272e-05 | 6.272e-05
Runcorn Bulk | 434-1 | Runcorn | Calamvale | ECC Rating (A) | 406 | 406 | 406 | 406 | 406
Runcorn Bulk | 434-1 | Runcorn | Calamvale | 50 POE Load (A) | 1.6825 | 1.6825 | 1.6825 | 1.6825 | 1.6824
Runcorn Bulk | 459A-1 | Upper Mt Gravatt | Sunnybank | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70
Runcorn Bulk | 459A-1 | Upper Mt Gravatt | Sunnybank | 10 POE Load (A) | 96 | 102 | 102 | 0 | 0
Runcorn Bulk | 459A-1 | Upper Mt Gravatt | Sunnybank | Power Factor | 0.93 | 0.926 | 0.926 | 0.926 | 0.926
Runcorn Bulk | 459A-1 | Upper Mt Gravatt | Sunnybank | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Runcorn Bulk | 459A-1 | Upper Mt Gravatt | Sunnybank | 50 POE Load (A) | 554 | 555 | 555 | 555 | 555
Runcorn Bulk | 459B-1 | Runcorn BS | Upper Mt Gravatt | NCC Rating (A) | 801 | 801 | 801 | 801 | 801 | Urban | 70
Runcorn Bulk | 459B-1 | Runcorn BS | Upper Mt Gravatt | 10 POE Load (A) | 94 | 101 | 101 | 101 | 101
Runcorn Bulk | 459B-1 | Runcorn BS | Upper Mt Gravatt | Power Factor | 0.942 | 0.937 | 0.937 | 0.937 | 0.937
Runcorn Bulk | 459B-1 | Runcorn BS | Upper Mt Gravatt | ECC Rating (A) | 801 | 801 | 801 | 801 | 801
Runcorn Bulk | 459B-1 | Runcorn BS | Upper Mt Gravatt | 50 POE Load (A) | 553 | 554 | 554 | 554 | 554
Runcorn Bulk | 667-1 | Runcorn BS | Acacia Ridge | NCC Rating (A) | 426 | 426 | 426 | 426 | 426 | Urban | 70
Runcorn Bulk | 667-1 | Runcorn BS | Acacia Ridge | 10 POE Load (A) | 27.7987 | 27.7987 | 27.7987 | 27.7987 | 27.7987
Runcorn Bulk | 667-1 | Runcorn BS | Acacia Ridge | Power Factor | 9.2863e-05 | 9.2863e-05 | 9.2863e-05 | 9.2863e-05 | 9.2863e-05
Runcorn Bulk | 667-1 | Runcorn BS | Acacia Ridge | ECC Rating (A) | 426 | 426 | 426 | 426 | 426
Runcorn Bulk | 667-1 | Runcorn BS | Acacia Ridge | 50 POE Load (A) | 27.7987 | 27.7987 | 27.7987 | 27.7987 | 27.7987
Runcorn Bulk | 668-1 | Runcorn BS | Acacia Ridge | NCC Rating (A) | 426 | 426 | 426 | 426 | 426 | Urban | 70
Runcorn Bulk | 668-1 | Runcorn BS | Acacia Ridge | 10 POE Load (A) | 27.9347 | 27.9347 | 27.9347 | 27.9347 | 27.9347
Runcorn Bulk | 668-1 | Runcorn BS | Acacia Ridge | Power Factor | -1 | -1 | -1 | -1 | -1
Runcorn Bulk | 668-1 | Runcorn BS | Acacia Ridge | ECC Rating (A) | 426 | 426 | 426 | 426 | 426
Runcorn Bulk | 668-1 | Runcorn BS | Acacia Ridge | 50 POE Load (A) | 27.9347 | 27.9347 | 27.9347 | 27.9347 | 27.9347
Runcorn Bulk | 690-1 | Runcorn BS | Runcorn | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70
Runcorn Bulk | 690-1 | Runcorn BS | Runcorn | 10 POE Load (A) | 246.0265 | 245.6016 | 246.2175 | 247.1655 | 250.1435
Runcorn Bulk | 690-1 | Runcorn BS | Runcorn | Power Factor | 0.9763 | 0.97634 | 0.97628 | 0.97619 | 0.9759
Runcorn Bulk | 690-1 | Runcorn BS | Runcorn | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Runcorn Bulk | 690-1 | Runcorn BS | Runcorn | 50 POE Load (A) | 355 | 355 | 353 | 353 | 353
Runcorn Bulk | 691-1 | Runcorn BS | Runcorn | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70
Runcorn Bulk | 691-1 | Runcorn BS | Runcorn | 10 POE Load (A) | 194.7237 | 194.3874 | 194.8748 | 195.625 | 197.9817
Runcorn Bulk | 691-1 | Runcorn BS | Runcorn | Power Factor | 0.97683 | 0.97687 | 0.97682 | 0.97673 | 0.97644
Runcorn Bulk | 691-1 | Runcorn BS | Runcorn | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
Runcorn Bulk | 691-1 | Runcorn BS | Runcorn | 50 POE Load (A) | 355 | 356 | 354 | 353 | 353
Runcorn Bulk | 694-1 | Runcorn BS | Eight Mile Plains Bus 1 | NCC Rating (A) | 531 | 531 | 531 | 531 | 531 | Urban | 70
Runcorn Bulk | 694-1 | Runcorn BS | Eight Mile Plains Bus 1 | 10 POE Load (A) | 272.4614 | 269.517 | 269.8183 | 270.1633 | 272.5259
Runcorn Bulk | 694-1 | Runcorn BS | Eight Mile Plains Bus 1 | Power Factor | 0.97956 | 0.98 | 0.97996 | 0.97991 | 0.97955
Runcorn Bulk | 694-1 | Runcorn BS | Eight Mile Plains Bus 1 | ECC Rating (A) | 531 | 531 | 531 | 531 | 531
Runcorn Bulk | 694-1 | Runcorn BS | Eight Mile Plains Bus 1 | 50 POE Load (A) | 461.5677 | 564.3381 | 564.8134 | 565.2837 | 570.0359
Sandgate Bulk | 3290-1 | Sandgate BS | Bald Hills Bus 1 | NCC Rating (A) | 853 | 853 | 853 | 853 | 853 | Urban | 70
Sandgate Bulk | 3290-1 | Sandgate BS | Bald Hills Bus 1 | 10 POE Load (A) | 69.6815 | 69.1863 | 69.065 | 68.8789 | 69.1886
Sandgate Bulk | 3290-1 | Sandgate BS | Bald Hills Bus 1 | Power Factor | 1 | 0.99999 | 0.99999 | 0.99999 | 0.99999
Sandgate Bulk | 3290-1 | Sandgate BS | Bald Hills Bus 1 | ECC Rating (A) | 853 | 853 | 853 | 853 | 853
Sandgate Bulk | 3290-1 | Sandgate BS | Bald Hills Bus 1 | 50 POE Load (A) | 295 | 295 | 293 | 291 | 291
Sandgate Bulk | 505-1 | Sandgate BS | Zilmere | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70
Sandgate Bulk | 505-1 | Sandgate BS | Zilmere | 10 POE Load (A) | 285.4352 | 283.8745 | 283.2681 | 282.6277 | 284.3771
Sandgate Bulk | 505-1 | Sandgate BS | Zilmere | Power Factor | -0.97533 | -0.97579 | -0.97596 | -0.97615 | -0.97564
Sandgate Bulk | 505-1 | Sandgate BS | Zilmere | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
Sandgate Bulk | 505-1 | Sandgate BS | Zilmere | 50 POE Load (A) | 378 | 377 | 376 | 373 | 373
Sandgate Bulk | 524-1 | Sandgate BS | Geebung | NCC Rating (A) | 453 | 453 | 453 | 453 | 453 | Urban | 70
Sandgate Bulk | 524-1 | Sandgate BS | Geebung | 10 POE Load (A) | 192.0856 | 191.04 | 190.6337 | 190.2046 | 191.3767
Sandgate Bulk | 524-1 | Sandgate BS | Geebung | Power Factor | -0.98744 | -0.98777 | -0.9879 | -0.98803 | -0.98766
Sandgate Bulk | 524-1 | Sandgate BS | Geebung | ECC Rating (A) | 453 | 453 | 453 | 453 | 453
Sandgate Bulk | 524-1 | Sandgate BS | Geebung | 50 POE Load (A) | 319 | 318 | 317 | 315 | 315
Sandgate Bulk | 524-2 | Geebung | Zillmere | NCC Rating (A) | 410 | 410 | 410 | 410 | 410 | Urban | 70
Sandgate Bulk | 524-2 | Geebung | Zillmere | 10 POE Load (A) | 197.0731 | 195.9883 | 195.5666 | 195.1214 | 196.3376
Sandgate Bulk | 524-2 | Geebung | Zillmere | Power Factor | 0.99391 | 0.99413 | 0.99422 | 0.99431 | 0.99406
Sandgate Bulk | 524-2 | Geebung | Zillmere | ECC Rating (A) | 410 | 410 | 410 | 410 | 410
Sandgate Bulk | 524-2 | Geebung | Zillmere | 50 POE Load (A) | 324 | 323 | 322 | 319 | 319
Sandgate Bulk | 561-1 | Sandgate BS | Brighton TR1 | NCC Rating (A) | 786 | 786 | 786 | 786 | 786 | Urban | 70
Sandgate Bulk | 561-1 | Sandgate BS | Brighton TR1 | 10 POE Load (A) | 98.1102 | 97.3493 | 97.0905 | 96.6913 | 97.2794
Sandgate Bulk | 561-1 | Sandgate BS | Brighton TR1 | Power Factor | 0.98929 | 0.98936 | 0.98939 | 0.98943 | 0.98937
Sandgate Bulk | 561-1 | Sandgate BS | Brighton TR1 | ECC Rating (A) | 786 | 786 | 786 | 786 | 786
Sandgate Bulk | 561-1 | Sandgate BS | Brighton TR1 | 50 POE Load (A) | 171 | 171 | 170 | 169 | 169
Sandgate Bulk | 656-1 | Sandgate BS | Brighton TR2 | NCC Rating (A) | 270 | 270 | 270 | 270 | 270 | Urban | 70
Sandgate Bulk | 656-1 | Sandgate BS | Brighton TR2 | 10 POE Load (A) | 94.0122 | 93.2831 | 93.035 | 92.6525 | 93.216
Sandgate Bulk | 656-1 | Sandgate BS | Brighton TR2 | Power Factor | 0.99799 | 0.99803 | 0.99804 | 0.99806 | 0.99803
Sandgate Bulk | 656-1 | Sandgate BS | Brighton TR2 | ECC Rating (A) | 270 | 270 | 270 | 270 | 270
Sandgate Bulk | 656-1 | Sandgate BS | Brighton TR2 | 50 POE Load (A) | 172 | 172 | 172 | 171 | 171
Sandgate Bulk | 664-1 | Geebung | Zillmere | NCC Rating (A) | 410 | 410 | 410 | 410 | 410 | Urban | 70
Sandgate Bulk | 664-1 | Geebung | Zillmere | 10 POE Load (A) | 24.6499 | 24.6526 | 24.6537 | 24.6548 | 24.6517
Sandgate Bulk | 664-1 | Geebung | Zillmere | Power Factor | -1 | -1 | -1 | -1 | -1
Sandgate Bulk | 664-1 | Geebung | Zillmere | ECC Rating (A) | 410 | 410 | 410 | 410 | 410
Sandgate Bulk | 664-1 | Geebung | Zillmere | 50 POE Load (A) | 24.6823 | 24.6848 | 24.6857 | 24.6868 | 24.684
Sandgate Bulk | 671-1 | Sandagate BS | Zillmere | NCC Rating (A) | 507 | 507 | 507 | 507 | 507 | Urban | 70
Sandgate Bulk | 671-1 | Sandagate BS | Zillmere | 10 POE Load (A) | 168.2809 | 167.361 | 167.0036 | 166.6261 | 167.6573
Sandgate Bulk | 671-1 | Sandagate BS | Zillmere | Power Factor | 0.99908 | 0.99918 | 0.99922 | 0.99925 | 0.99915
Sandgate Bulk | 671-1 | Sandagate BS | Zillmere | ECC Rating (A) | 507 | 507 | 507 | 507 | 507
Sandgate Bulk | 671-1 | Sandagate BS | Zillmere | 50 POE Load (A) | 280 | 279 | 278 | 276 | 276
Stafford Bulk | 548-1 | Stafford BS | Enoggera | NCC Rating (A) | 836 | 836 | 836 | 836 | 836 | Urban | 70
Stafford Bulk | 548-1 | Stafford BS | Enoggera | 10 POE Load (A) | 555.6569 | 553.7462 | 553.5565 | 552.8377 | 555.1841
Stafford Bulk | 548-1 | Stafford BS | Enoggera | Power Factor | 0.97513 | 0.97526 | 0.97531 | 0.97538 | 0.97529
Stafford Bulk | 548-1 | Stafford BS | Enoggera | ECC Rating (A) | 963 | 963 | 963 | 963 | 963
Stafford Bulk | 548-1 | Stafford BS | Enoggera | 50 POE Load (A) | 1006 | 1008 | 1007 | 1003 | 1003
Stafford Bulk | 550-1 | Stafford BS | Chermside | NCC Rating (A) | 668 | 668 | 668 | 668 | 668 | Urban | 70
Stafford Bulk | 550-1 | Stafford BS | Chermside | 10 POE Load (A) | 213.2554 | 212.1464 | 210.9991 | 209.3297 | 209.5254
Stafford Bulk | 550-1 | Stafford BS | Chermside | Power Factor | 0.99731 | 0.99744 | 0.99758 | 0.99777 | 0.99775
Stafford Bulk | 550-1 | Stafford BS | Chermside | ECC Rating (A) | 789 | 789 | 789 | 789 | 789
Stafford Bulk | 550-1 | Stafford BS | Chermside | 50 POE Load (A) | 704 | 706 | 706 | 704 | 704
Stafford Bulk | 551-1 | Stafford BS | Chermside | NCC Rating (A) | 668 | 668 | 668 | 668 | 668 | Urban | 70
Stafford Bulk | 551-1 | Stafford BS | Chermside | 10 POE Load (A) | 212.8488 | 211.7418 | 210.5967 | 208.9305 | 209.1258
Stafford Bulk | 551-1 | Stafford BS | Chermside | Power Factor | 0.99731 | 0.99745 | 0.99758 | 0.99778 | 0.99775
Stafford Bulk | 551-1 | Stafford BS | Chermside | ECC Rating (A) | 789 | 789 | 789 | 789 | 789
Stafford Bulk | 551-1 | Stafford BS | Chermside | 50 POE Load (A) | 704 | 706 | 706 | 704 | 704
Stafford Bulk | 567-1 | Stafford BS | Kedron | NCC Rating (A) | 576 | 576 | 576 | 576 | 576 | Urban | 70
Stafford Bulk | 567-1 | Stafford BS | Kedron | 10 POE Load (A) | 281.6721 | 281.288 | 295.4556 | 295.7455 | 296.7397
Stafford Bulk | 567-1 | Stafford BS | Kedron | Power Factor | 0.9837 | 0.98375 | 0.98146 | 0.98142 | 0.99693
Stafford Bulk | 567-1 | Stafford BS | Kedron | ECC Rating (A) | 643 | 643 | 643 | 643 | 643
Stafford Bulk | 567-1 | Stafford BS | Kedron | 50 POE Load (A) | 493 | 496 | 496 | 496 | 496
Stafford Bulk | 568-1 | Stafford BS | Kedron | NCC Rating (A) | 576 | 576 | 576 | 576 | 576 | Urban | 70
Stafford Bulk | 568-1 | Stafford BS | Kedron | 10 POE Load (A) | 283.8071 | 283.42 | 297.6956 | 297.9877 | 298.9944
Stafford Bulk | 568-1 | Stafford BS | Kedron | Power Factor | -0.96405 | -0.96409 | -0.96246 | -0.96242 | -0.97045
Stafford Bulk | 568-1 | Stafford BS | Kedron | ECC Rating (A) | 643 | 643 | 643 | 643 | 643
Stafford Bulk | 568-1 | Stafford BS | Kedron | 50 POE Load (A) | 493 | 496 | 496 | 496 | 496
Stafford Bulk | 594-1 | Stafford BS | Enoggera | NCC Rating (A) | 836 | 836 | 836 | 836 | 836 | Urban | 70
Stafford Bulk | 594-1 | Stafford BS | Enoggera | 10 POE Load (A) | 552.1521 | 550.2534 | 550.0649 | 549.3506 | 551.6823
Stafford Bulk | 594-1 | Stafford BS | Enoggera | Power Factor | 0.97515 | 0.97528 | 0.97533 | 0.9754 | 0.97531
Stafford Bulk | 594-1 | Stafford BS | Enoggera | ECC Rating (A) | 963 | 963 | 963 | 963 | 963
Stafford Bulk | 594-1 | Stafford BS | Enoggera | 50 POE Load (A) | 1006 | 1008 | 1007 | 1003 | 1003
Stafford Bulk | 595-1 | Enoggera | Grovely | NCC Rating (A) | 720 | 720 | 720 | 720 | 720 | Urban | 70
Stafford Bulk | 595-1 | Enoggera | Grovely | 10 POE Load (A) | 244.4365 | 242.306 | 241.2558 | 239.8721 | 240.3297
Stafford Bulk | 595-1 | Enoggera | Grovely | Power Factor | 0.97619 | 0.97648 | 0.97662 | 0.97681 | 0.97674
Stafford Bulk | 595-1 | Enoggera | Grovely | ECC Rating (A) | 720 | 720 | 720 | 720 | 720
Stafford Bulk | 595-1 | Enoggera | Grovely | 50 POE Load (A) | 428 | 427 | 425 | 422 | 422
Stafford Bulk | 596-1 | Enoggera | Grovely | NCC Rating (A) | 720 | 720 | 720 | 720 | 720 | Urban | 70
Stafford Bulk | 596-1 | Enoggera | Grovely | 10 POE Load (A) | 246.073 | 243.9283 | 242.871 | 241.4781 | 241.9387
Stafford Bulk | 596-1 | Enoggera | Grovely | Power Factor | 0.97616 | 0.97645 | 0.97659 | 0.97678 | 0.97671
Stafford Bulk | 596-1 | Enoggera | Grovely | ECC Rating (A) | 720 | 720 | 720 | 720 | 720
Stafford Bulk | 596-1 | Enoggera | Grovely | 50 POE Load (A) | 428 | 427 | 425 | 422 | 422
Stafford Bulk | 607-1 | Chermside | Zillmere | NCC Rating (A) | 311 | 311 | 311 | 311 | 311 | Urban | 70
Stafford Bulk | 607-1 | Chermside | Zillmere | 10 POE Load (A) | 0.83295 | 0.83297 | 0.83298 | 0.83301 | 0.83301
Stafford Bulk | 607-1 | Chermside | Zillmere | Power Factor | 1.3215e-05 | 1.3215e-05 | 1.3215e-05 | 1.3215e-05 | 1.3215e-05
Sunrise Hills Bulk | 308-1 | Perigian | 308 Tee1 | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
Sunrise Hills Bulk | 308-1 | Perigian | 308 Tee1 | 10 POE Load (A) | 476.7726 | 550.429 | 551.9194 | 553.5549 | 561.1035
Sunrise Hills Bulk | 308-1 | Perigian | 308 Tee1 | Power Factor | 0.9539 | 0.94204 | 0.94178 | 0.94149 | 0.94013
Sunrise Hills Bulk | 308-1 | Perigian | 308 Tee1 | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Sunrise Hills Bulk | 308-1 | Perigian | 308 Tee1 | 50 POE Load (A) | 464.1937 | 536.9018 | 538.3148 | 539.8693 | 547.1158
Sunrise Hills Bulk | 308-2 | 308 Tee1 | Coolum | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
Sunrise Hills Bulk | 308-2 | 308 Tee1 | Coolum | 10 POE Load (A) | 476.8034 | 550.4627 | 551.9531 | 553.5887 | 561.1376
Sunrise Hills Bulk | 308-2 | 308 Tee1 | Coolum | Power Factor | 0.96104 | 0.95123 | 0.95101 | 0.95077 | 0.94964
Sunrise Hills Bulk | 308-2 | 308 Tee1 | Coolum | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Sunrise Hills Bulk | 308-2 | 308 Tee1 | Coolum | 50 POE Load (A) | 464.2242 | 536.9353 | 538.3484 | 539.9029 | 547.1497
Sunrise Hills Bulk | 308-3 | 308 Tee1 | 307 Tee2 | NCC Rating (A) | 529 | 529 | 529 | 529 | 529 | Urban | 70
Sunrise Hills Bulk | 308-3 | 308 Tee1 | 307 Tee2 | 10 POE Load (A) | 0.0067745 | 0.0066449 | 0.0066405 | 0.0066365 | 0.0066196
Sunrise Hills Bulk | 308-3 | 308 Tee1 | 307 Tee2 | Power Factor | -1 | -1 | -1 | -1 | -1
Sunrise Hills Bulk | 3100-1 | Sunrise Hills BS | 3100 Tee1 | NCC Rating (A) | 529 | 529 | 529 | 529 | 529 | Urban | 70
Sunrise Hills Bulk | 3100-1 | Sunrise Hills BS | 3100 Tee1 | 10 POE Load (A) | 699.3276 | 774.5798 | 777.8377 | 780.5721 | 791.327
Sunrise Hills Bulk | 3100-1 | Sunrise Hills BS | 3100 Tee1 | Power Factor | -0.00040931 | -0.00040954 | -0.00040842 | -0.00040902 | -0.00040831
Sunrise Hills Bulk | 3100-1 | Sunrise Hills BS | 3100 Tee1 | ECC Rating (A) | 793 | 793 | 793 | 793 | 793
Sunrise Hills Bulk | 3100-1 | Sunrise Hills BS | 3100 Tee1 | 50 POE Load (A) | 669.098 | 743.1399 | 746.1672 | 748.7231 | 758.885
Sunrise Hills Bulk | 3100-2 | 3100 Tee1 | Peregian | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
Sunrise Hills Bulk | 3100-2 | 3100 Tee1 | Peregian | 10 POE Load (A) | 699.5198 | 774.7946 | 778.0529 | 780.7878 | 791.545
Sunrise Hills Bulk | 3100-2 | 3100 Tee1 | Peregian | Power Factor | -0.96417 | -0.9547 | -0.95451 | -0.95428 | -0.95322
Sunrise Hills Bulk | 3100-2 | 3100 Tee1 | Peregian | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Sunrise Hills Bulk | 3100-2 | 3100 Tee1 | Peregian | 50 POE Load (A) | 669.2872 | 743.3526 | 746.3802 | 748.9367 | 759.1008
Sunrise Hills Bulk | 343-1 | Sunrise Hills BS | 343 Tee1 | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Rural | 170
Sunrise Hills Bulk | 343-1 | Sunrise Hills BS | 343 Tee1 | 10 POE Load (A) | 377.7761 | 371.4106 | 369.0832 | 364.4821 | 366.337
Sunrise Hills Bulk | 343-1 | Sunrise Hills BS | 343 Tee1 | Power Factor | 0.97189 | 0.97255 | 0.97282 | 0.97318 | 0.97307
Sunrise Hills Bulk | 343-1 | Sunrise Hills BS | 343 Tee1 | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Sunrise Hills Bulk | 343-1 | Sunrise Hills BS | 343 Tee1 | 50 POE Load (A) | 652 | 650 | 648 | 644 | 644
Sunrise Hills Bulk | 343-2 | 343 Tee1 | Tewantin | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Rural | 170
Sunrise Hills Bulk | 343-2 | 343 Tee1 | Tewantin | 10 POE Load (A) | 192.8674 | 187.0004 | 184.2228 | 179.0138 | 179.3007
Sunrise Hills Bulk | 343-2 | 343 Tee1 | Tewantin | Power Factor | -0.93792 | -0.9391 | -0.93959 | -0.94791 | -0.94777
Sunrise Hills Bulk | 343-2 | 343 Tee1 | Tewantin | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Sunrise Hills Bulk | 343-2 | 343 Tee1 | Tewantin | 50 POE Load (A) | 420 | 417 | 414 | 411 | 411
Sunrise Hills Bulk | 343-3 | 343 Tee1 | Cooroy | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Rural | 170
Sunrise Hills Bulk | 343-3 | 343 Tee1 | Cooroy | 10 POE Load (A) | 191.3869 | 190.7829 | 191.1969 | 191.3955 | 192.995
Sunrise Hills Bulk | 343-3 | 343 Tee1 | Cooroy | Power Factor | 0.99299 | 0.99303 | 0.99301 | 0.99301 | 0.99294
Sunrise Hills Bulk | 343-3 | 343 Tee1 | Cooroy | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
Sunrise Hills Bulk | 343-3 | 343 Tee1 | Cooroy | 50 POE Load (A) | 238 | 239 | 239 | 239 | 239
Sunrise Hills Bulk | 346-1 | Sunrise Hills BS | 346 Tee1 | NCC Rating (A) | 976 | 976 | 976 | 976 | 976 | Urban | 70
Sunrise Hills Bulk | 346-1 | Sunrise Hills BS | 346 Tee1 | 10 POE Load (A) | 288.9418 | 282.7725 | 280.2022 | 275.327 | 276.4178
Sunrise Hills Bulk | 346-1 | Sunrise Hills BS | 346 Tee1 | Power Factor | -0.9548 | -0.95591 | -0.9564 | -0.96144 | -0.96133
Sunrise Hills Bulk | 346-1 | Sunrise Hills BS | 346 Tee1 | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Sunrise Hills Bulk | 346-1 | Sunrise Hills BS | 346 Tee1 | 50 POE Load (A) | 342 | 340 | 337 | 334 | 334
Sunrise Hills Bulk | 346-2 | 346 Tee1 | Tewantin | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70
Sunrise Hills Bulk | 346-2 | 346 Tee1 | Tewantin | 10 POE Load (A) | 288.9979 | 282.828 | 280.2574 | 275.3789 | 276.4697
Sunrise Hills Bulk | 346-2 | 346 Tee1 | Tewantin | Power Factor | 0.9664 | 0.96716 | 0.96749 | 0.96793 | 0.96783
Sunrise Hills Bulk | 346-2 | 346 Tee1 | Tewantin | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
Sunrise Hills Bulk | 346-2 | 346 Tee1 | Tewantin | 50 POE Load (A) | 418 | 414 | 412 | 408 | 408
Sunrise Hills Bulk | 346-3 | 346 Tee1 | 3100 Tee1 | NCC Rating (A) | 529 | 529 | 529 | 529 | 529 | Urban | 70
Sunrise Hills Bulk | 346-3 | 346 Tee1 | 3100 Tee1 | 10 POE Load (A) | 0.00064601 | 0.00064601 | 0.00064601 | 0.00064601 | 0.00064601
Sunrise Hills Bulk | 346-3 | 346 Tee1 | 3100 Tee1 | Power Factor | 0.00030686 | 0.00030706 | 0.0003069 | 0.00030679 | 0.00030684
Sunrise Hills Bulk | 488-1 | Cooroy | 488 Tee1 | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
Sunrise Hills Bulk | 488-1 | Cooroy | 488 Tee1 | 10 POE Load (A) | 66.141 | 66.3516 | 66.8519 | 67.2508 | 68.1227
Sunrise Hills Bulk | 488-1 | Cooroy | 488 Tee1 | Power Factor | 0.99618 | 0.99616 | 0.9961 | 0.99605 | 0.99595
Sunrise Hills Bulk | 488-1 | Cooroy | 488 Tee1 | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
Sunrise Hills Bulk | 488-1 | Cooroy | 488 Tee1 | 50 POE Load (A) | 131 | 132 | 132 | 132 | 132
Sunrise Hills Bulk | 488-3 | 488 Tee1 | 488 Tee2 | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
Sunrise Hills Bulk | 488-3 | 488 Tee1 | 488 Tee2 | 10 POE Load (A) | 66.1515 | 66.3621 | 66.8625 | 67.2614 | 68.1334
Sunrise Hills Bulk | 488-3 | 488 Tee1 | 488 Tee2 | Power Factor | 0.9957 | 0.99568 | 0.99562 | 0.99558 | 0.99547
Sunrise Hills Bulk | 488-3 | 488 Tee1 | 488 Tee2 | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
Sunrise Hills Bulk | 488-3 | 488 Tee1 | 488 Tee2 | 50 POE Load (A) | 131 | 132 | 132 | 132 | 132
Sunrise Hills Bulk | 488-4 | 488 Tee2 | Black Mtn | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170
Sunrise Hills Bulk | 488-4 | 488 Tee2 | Black Mtn | 10 POE Load (A) | 0.3199 | 0.31999 | 0.31997 | 0.32002 | 0.31989
Sunrise Hills Bulk | 488-4 | 488 Tee2 | Black Mtn | Power Factor | 1.5722e-05 | 1.5722e-05 | 1.5722e-05 | 1.5722e-05 | 1.5722e-05
Sunrise Hills Bulk | 488-4 | 488 Tee2 | Black Mtn | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
Sunrise Hills Bulk | 488-4 | 488 Tee2 | Black Mtn | 50 POE Load (A) | 0.32097 | 0.32105 | 0.32103 | 0.32104 | 0.32092
Sunrise Hills Bulk | 488-5 | 488 Tee2 | 488 Tee3 | NCC Rating (A) | 403 | 403 | 403 | 403 | 403 | Rural | 170
Sunrise Hills Bulk | 488-5 | 488 Tee2 | 488 Tee3 | 10 POE Load (A) | 66.2179 | 66.4287 | 66.9294 | 67.3287 | 68.2013
Sunrise Hills Bulk | 488-5 | 488 Tee2 | 488 Tee3 | Power Factor | 0.99527 | 0.99525 | 0.99519 | 0.99515 | 0.99505
Sunrise Hills Bulk | 488-5 | 488 Tee2 | 488 Tee3 | ECC Rating (A) | 403 | 403 | 403 | 403 | 403
Sunrise Hills Bulk | 488-5 | 488 Tee2 | 488 Tee3 | 50 POE Load (A) | 63.4222 | 63.6285 | 64.1076 | 64.4901 | 65.3202
Sunrise Hills Bulk | 488-6 | 488 Tee3 | Eumundi | NCC Rating (A) | 438 | 438 | 438 | 438 | 438 | Rural | 170
Sunrise Hills Bulk | 488-6 | 488 Tee3 | Eumundi | 10 POE Load (A) | 66.3333 | 66.5443 | 67.0454 | 67.4451 | 68.3184
Sunrise Hills Bulk | 488-6 | 488 Tee3 | Eumundi | Power Factor | 0.99382 | 0.99381 | 0.99377 | 0.99374 | 0.99367
Sunrise Hills Bulk | 488-6 | 488 Tee3 | Eumundi | ECC Rating (A) | 438 | 438 | 438 | 438 | 438
Sunrise Hills Bulk | 488-6 | 488 Tee3 | Eumundi | 50 POE Load (A) | 63.5354 | 63.7419 | 64.2214 | 64.6042 | 65.435
Sunrise Hills Bulk | 488-7 | 488 Tee3 | Yandina | NCC Rating (A) | 403 | 403 | 403 | 403 | 403 | Rural | 170
Sunrise Hills Bulk | 488-7 | 488 Tee3 | Yandina | 10 POE Load (A) | 1.0448 | 1.045 | 1.0449 | 1.0451 | 1.0446
Sunrise Hills Bulk | 488-7 | 488 Tee3 | Yandina | Power Factor | 1.4326e-06 | 1.4325e-06 | 1.4325e-06 | 1.4326e-06 | 1.4325e-06
Sunrise Hills Bulk | 488-7 | 488 Tee3 | Yandina | ECC Rating (A) | 403 | 403 | 403 | 403 | 403
Sunrise Hills Bulk | 488-7 | 488 Tee3 | Yandina | 50 POE Load (A) | 1.0485 | 1.0487 | 1.0486 | 1.0486 | 1.0481
Tennyson Bulk | 3390-1 | Taringa | Indooroopilly | NCC Rating (A) | 728 | 728 | 728 | 728 | 728 | Urban | 70
Tennyson Bulk | 3390-1 | Taringa | Indooroopilly | 10 POE Load (A) | 155.6373 | 150.8849 | 149.0444 | 147.6938 | 147.3843
Tennyson Bulk | 3390-1 | Taringa | Indooroopilly | Power Factor | 0.95522 | 0.95526 | 0.95602 | 0.95652 | 0.95656
Tennyson Bulk | 3390-1 | Taringa | Indooroopilly | ECC Rating (A) | 728 | 728 | 728 | 728 | 728
Tennyson Bulk | 3390-1 | Taringa | Indooroopilly | 50 POE Load (A) | 131.6308 | 127.3764 | 125.839 | 124.6911 | 124.4159
Tennyson Bulk | 3393-1 | Tennyson BS | St Lucia TR1 | NCC Rating (A) | 610 | 610 | 610 | 610 | 610 | Urban | 70
Tennyson Bulk | 3393-1 | Tennyson BS | St Lucia TR1 | 10 POE Load (A) | 120.4205 | 118.8996 | 117.949 | 116.7289 | 116.1133
Tennyson Bulk | 3393-1 | Tennyson BS | St Lucia TR1 | Power Factor | 0.99728 | 0.99755 | 0.99774 | 0.99796 | 0.99806
Tennyson Bulk | 3393-1 | Tennyson BS | St Lucia TR1 | ECC Rating (A) | 610 | 610 | 610 | 610 | 610
Tennyson Bulk | 3393-1 | Tennyson BS | St Lucia TR1 | 50 POE Load (A) | 305 | 305 | 304 | 302 | 302
Tennyson Bulk | 3394-1 | Tennyson BS | St Lucia TR2 | NCC Rating (A) | 610 | 610 | 610 | 610 | 610 | Urban | 70
Tennyson Bulk | 3394-1 | Tennyson BS | St Lucia TR2 | 10 POE Load (A) | 240.8997 | 237.3894 | 235.3721 | 232.7374 | 231.3165
Tennyson Bulk | 3394-1 | Tennyson BS | St Lucia TR2 | Power Factor | 0.98884 | 0.9896 | 0.99002 | 0.99058 | 0.99088
Tennyson Bulk | 3394-1 | Tennyson BS | St Lucia TR2 | ECC Rating (A) | 610 | 610 | 610 | 610 | 610
Tennyson Bulk | 3394-1 | Tennyson BS | St Lucia TR2 | 50 POE Load (A) | 140 | 140 | 140 | 139 | 139
Tennyson Bulk | 3460-1 | Annerley | Buranda | NCC Rating (A) | 802 | 802 | 802 | 802 | 802 | Urban | 70
Tennyson Bulk | 3460-1 | Annerley | Buranda | 10 POE Load (A) | 183.4202 | 210.2307 | 219.5752 | 219.0121 | 220.482
Tennyson Bulk | 3460-1 | Annerley | Buranda | Power Factor | 0.97516 | 0.97187 | 0.97074 | 0.97081 | 0.97121
Tennyson Bulk | 3460-1 | Annerley | Buranda | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Tennyson Bulk | 3460-1 | Annerley | Buranda | 50 POE Load (A) | 410 | 486 | 488 | 488 | 488
Tennyson Bulk | 3461-1 | Annerley | Buranda | NCC Rating (A) | 802 | 802 | 802 | 802 | 802 | Urban | 70
Tennyson Bulk | 3461-1 | Annerley | Buranda | 10 POE Load (A) | 183.7019 | 210.5536 | 219.9126 | 219.3486 | 220.8208
Tennyson Bulk | 3461-1 | Annerley | Buranda | Power Factor | 0.97517 | 0.97188 | 0.97075 | 0.97082 | 0.97123
Tennyson Bulk | 3461-1 | Annerley | Buranda | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Tennyson Bulk | 3461-1 | Annerley | Buranda | 50 POE Load (A) | 410 | 486 | 488 | 488 | 488
Tennyson Bulk | 410-1 | Sherwood | Indooroopilly | NCC Rating (A) | 400 | 400 | 400 | 400 | 400 | Urban | 70
Tennyson Bulk | 410-1 | Sherwood | Indooroopilly | 10 POE Load (A) | 271.3564 | 269.3894 | 266.8177 | 264.7208 | 264.4963
Tennyson Bulk | 410-1 | Sherwood | Indooroopilly | Power Factor | 0.98108 | 0.98145 | 0.982 | 0.98237 | 0.98247
Tennyson Bulk | 410-1 | Sherwood | Indooroopilly | ECC Rating (A) | 451 | 451 | 451 | 451 | 451
Tennyson Bulk | 410-1 | Sherwood | Indooroopilly | 50 POE Load (A) | 379 | 380 | 380 | 378 | 378
Tennyson Bulk | 460-1 | Tennyson BS | Sherwood | NCC Rating (A) | 762 | 762 | 762 | 762 | 762 | Urban | 70
Tennyson Bulk | 460-1 | Tennyson BS | Sherwood | 10 POE Load (A) | 451.2251 | 447.0629 | 443.798 | 441.3134 | 441.7866
Tennyson Bulk | 460-1 | Tennyson BS | Sherwood | Power Factor | 0.96798 | 0.96831 | 0.96875 | 0.96906 | 0.96903
Tennyson Bulk | 460-1 | Tennyson BS | Sherwood | ECC Rating (A) | 763 | 763 | 763 | 763 | 763
Tennyson Bulk | 460-1 | Tennyson BS | Sherwood | 50 POE Load (A) | 524 | 524 | 523 | 520 | 520
Tennyson Bulk | 480-1 | Taringa | St Lucia | NCC Rating (A) | 610 | 610 | 610 | 610 | 610 | Urban | 70
Tennyson Bulk | 480-1 | Taringa | St Lucia | 10 POE Load (A) | 117.0031 | 115.2001 | 114.2312 | 112.9455 | 112.2133
Tennyson Bulk | 480-1 | Taringa | St Lucia | Power Factor | -0.9914 | -0.99193 | -0.99219 | -0.99256 | -0.99278
Tennyson Bulk | 480-1 | Taringa | St Lucia | ECC Rating (A) | 610 | 610 | 610 | 610 | 610
Tennyson Bulk | 480-1 | Taringa | St Lucia | 50 POE Load (A) | 303 | 303 | 303 | 301 | 301
Tennyson Bulk | 504-1 | Tennyson BS | Taringa | NCC Rating (A) | 601 | 601 | 601 | 601 | 601 | Urban | 70
Tennyson Bulk | 504-1 | Tennyson BS | Taringa | 10 POE Load (A) | 343.0002 | 344.2229 | 342.3049 | 340.6549 | 341.2852
Tennyson Bulk | 504-1 | Tennyson BS | Taringa | Power Factor | -0.97462 | -0.9751 | -0.97545 | -0.97574 | -0.97577
Tennyson Bulk | 504-1 | Tennyson BS | Taringa | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
Tennyson Bulk | 504-1 | Tennyson BS | Taringa | 50 POE Load (A) | 464 | 465 | 465 | 462 | 462
Tennyson Bulk | 507A-1 | Toowong | Indooroopilly | NCC Rating (A) | 735 | 735 | 735 | 735 | 735 | Urban | 70
Tennyson Bulk | 507A-1 | Toowong | Indooroopilly | 10 POE Load (A) | 159.0325 | 154.1679 | 152.2842 | 150.9019 | 150.585
Tennyson Bulk | 507A-1 | Toowong | Indooroopilly | Power Factor | 0.94929 | 0.94893 | 0.94957 | 0.94998 | 0.94999
Tennyson Bulk | 507A-1 | Toowong | Indooroopilly | ECC Rating (A) | 858 | 858 | 858 | 858 | 858
Tennyson Bulk | 507A-1 | Toowong | Indooroopilly | 50 POE Load (A) | 170 | 170 | 170 | 168 | 168
Tennyson Bulk | 507B-1 | Toowong | Taringa | NCC Rating (A) | 727 | 727 | 727 | 727 | 727 | Urban | 70
Tennyson Bulk | 507B-1 | Toowong | Taringa | 10 POE Load (A) | 156.7915 | 151.9325 | 150.0583 | 148.6824 | 148.3654
Tennyson Bulk | 507B-1 | Toowong | Taringa | Power Factor | 0.95976 | 0.9598 | 0.96053 | 0.961 | 0.96104
Tennyson Bulk | 507B-1 | Toowong | Taringa | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Tennyson Bulk | 507B-1 | Toowong | Taringa | 50 POE Load (A) | 168 | 168 | 168 | 166 | 166
Tennyson Bulk | 511-1 | Tennyson BS | Moorooka | NCC Rating (A) | 739 | 739 | 739 | 739 | 739 | Urban | 70
Tennyson Bulk | 511-1 | Tennyson BS | Moorooka | 10 POE Load (A) | 151.1708 | 152.4182 | 154.0419 | 155.5256 | 157.9954
Tennyson Bulk | 511-1 | Tennyson BS | Moorooka | Power Factor | -0.9603 | -0.96014 | -0.95994 | -0.95975 | -0.95943
Tennyson Bulk | 511-1 | Tennyson BS | Moorooka | ECC Rating (A) | 753 | 753 | 753 | 753 | 753
Tennyson Bulk | 511-1 | Tennyson BS | Moorooka | 50 POE Load (A) | 287 | 290 | 292 | 294 | 294
Tennyson Bulk | 514-1 | Tennyson BS | Moorooka | NCC Rating (A) | 739 | 739 | 739 | 739 | 739 | Urban | 70
Tennyson Bulk | 514-1 | Tennyson BS | Moorooka | 10 POE Load (A) | 158.3018 | 159.6079 | 161.308 | 162.8615 | 165.4477
Tennyson Bulk | 514-1 | Tennyson BS | Moorooka | Power Factor | 0.96502 | 0.96487 | 0.96467 | 0.96449 | 0.96418
Tennyson Bulk | 514-1 | Tennyson BS | Moorooka | ECC Rating (A) | 753 | 753 | 753 | 753 | 753
Tennyson Bulk | 514-1 | Tennyson BS | Moorooka | 50 POE Load (A) | 287 | 289 | 292 | 294 | 294
Tennyson Bulk | 515-1 | Tennyson BS | Sherwood | NCC Rating (A) | 740 | 740 | 740 | 740 | 740 | Urban | 70
Tennyson Bulk | 515-1 | Tennyson BS | Sherwood | 10 POE Load (A) | 478.34 | 473.9261 | 470.464 | 467.8294 | 468.3311
Tennyson Bulk | 515-1 | Tennyson BS | Sherwood | Power Factor | 0.97251 | 0.97281 | 0.97322 | 0.97351 | 0.97348
Tennyson Bulk | 515-1 | Tennyson BS | Sherwood | ECC Rating (A) | 740 | 740 | 740 | 740 | 740
Tennyson Bulk | 515-1 | Tennyson BS | Sherwood | 50 POE Load (A) | 554 | 555 | 554 | 550 | 550
Tennyson Bulk | 523A-1 | Tennyson BS | Rocklea | NCC Rating (A) | 650 | 650 | 650 | 650 | 650 | Urban | 70
Tennyson Bulk | 523A-1 | Tennyson BS | Rocklea | 10 POE Load (A) | 7.7342 | 7.7342 | 7.7342 | 7.7342 | 7.7342
Tennyson Bulk | 523A-1 | Tennyson BS | Rocklea | Power Factor | 1.0729e-05 | 1.0729e-05 | 1.0729e-05 | 1.0729e-05 | 1.0729e-05
Tennyson Bulk | 523A-1 | Tennyson BS | Rocklea | ECC Rating (A) | 650 | 650 | 650 | 650 | 650
Tennyson Bulk | 523A-1 | Tennyson BS | Rocklea | 50 POE Load (A) | 7.7342 | 7.7342 | 7.7342 | 7.7342 | 7.7342
Tennyson Bulk | 539-1 | Sherwood | Kenmore | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 340
Tennyson Bulk | 539-1 | Sherwood | Kenmore | 10 POE Load (A) | 323.4113 | 316.4164 | 311.7011 | 308.9799 | 308.2143
Tennyson Bulk | 539-1 | Sherwood | Kenmore | Power Factor | 0.97318 | 0.97334 | 0.97393 | 0.97426 | 0.97436
Tennyson Bulk | 539-1 | Sherwood | Kenmore | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
Tennyson Bulk | 539-1 | Sherwood | Kenmore | 50 POE Load (A) | 577 | 576 | 573 | 567 | 567
Tennyson Bulk | 554-1 | Tennyson BS | Sherwood | NCC Rating (A) | 716 | 716 | 716 | 716 | 716 | Urban | 70
Tennyson Bulk | 554-1 | Tennyson BS | Sherwood | 10 POE Load (A) | 506.9692 | 502.2912 | 498.6224 | 495.8304 | 496.3622
Tennyson Bulk | 554-1 | Tennyson BS | Sherwood | Power Factor | 0.96957 | 0.96988 | 0.97032 | 0.97062 | 0.97059
Tennyson Bulk | 554-1 | Tennyson BS | Sherwood | ECC Rating (A) | 716 | 716 | 716 | 716 | 716
Tennyson Bulk | 554-1 | Tennyson BS | Sherwood | 50 POE Load (A) | 575 | 576 | 575 | 571 | 571
Tennyson Bulk | 571-1 | Indooroopilly | Kenmore | NCC Rating (A) | 527 | 527 | 527 | 527 | 527 | Urban | 70
Tennyson Bulk | 571-1 | Indooroopilly | Kenmore | 10 POE Load (A) | 423.6944 | 413.6406 | 407.1897 | 403.5849 | 402.4983
Tennyson Bulk | 571-1 | Indooroopilly | Kenmore | Power Factor | 0.95692 | 0.95768 | 0.95843 | 0.95884 | 0.95896
Tennyson Bulk | 571-1 | Indooroopilly | Kenmore | ECC Rating (A) | 527 | 527 | 527 | 527 | 527
Tennyson Bulk | 571-1 | Indooroopilly | Kenmore | 50 POE Load (A) | 569 | 567 | 564 | 558 | 558
Tennyson Bulk | 606-1 | Tennyson BS | Taringa | NCC Rating (A) | 601 | 601 | 601 | 601 | 601 | Urban | 70
Tennyson Bulk | 606-1 | Tennyson BS | Taringa | 10 POE Load (A) | 344.6149 | 345.8435 | 343.9164 | 342.2588 | 342.892
Tennyson Bulk | 606-1 | Tennyson BS | Taringa | Power Factor | 0.98219 | 0.98234 | 0.9827 | 0.98298 | 0.98299
Tennyson Bulk | 606-1 | Tennyson BS | Taringa | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
Tennyson Bulk | 606-1 | Tennyson BS | Taringa | 50 POE Load (A) | 465 | 466 | 466 | 463 | 463
Tennyson Bulk | 637-1 | Tennyson BS | Annerley | NCC Rating (A) | 716 | 716 | 716 | 716 | 716 | Urban | 70
Tennyson Bulk | 637-1 | Tennyson BS | Annerley | 10 POE Load (A) | 338.9684 | 366.4325 | 376.8583 | 377.3183 | 380.8218
Tennyson Bulk | 637-1 | Tennyson BS | Annerley | Power Factor | 0.97776 | 0.97567 | 0.97486 | 0.97484 | 0.97489
Tennyson Bulk | 637-1 | Tennyson BS | Annerley | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Tennyson Bulk | 637-1 | Tennyson BS | Annerley | 50 POE Load (A) | 671 | 742 | 746 | 746 | 746
Tennyson Bulk | 638-1 | Tennyson BS | Annerley | NCC Rating (A) | 716 | 716 | 716 | 716 | 716 | Urban | 70
Tennyson Bulk | 638-1 | Tennyson BS | Annerley | 10 POE Load (A) | 340.1182 | 367.6756 | 378.1369 | 378.5984 | 382.1139
Tennyson Bulk | 638-1 | Tennyson BS | Annerley | Power Factor | 0.97775 | 0.97565 | 0.97485 | 0.97483 | 0.97488
Tennyson Bulk | 638-1 | Tennyson BS | Annerley | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
Tennyson Bulk | 638-1 | Tennyson BS | Annerley | 50 POE Load (A) | 671 | 742 | 746 | 746 | 746
Tennyson Bulk | F703-1 | Sherwood | Indooroopilly | NCC Rating (A) | 400 | 400 | 400 | 400 | 400 | Urban | 70
Tennyson Bulk | F703-1 | Sherwood | Indooroopilly | 10 POE Load (A) | 274.1782 | 272.191 | 269.5924 | 267.4737 | 267.2469
Tennyson Bulk | F703-1 | Sherwood | Indooroopilly | Power Factor | 0.98116 | 0.98153 | 0.98208 | 0.98245 | 0.98255
Tennyson Bulk | F703-1 | Sherwood | Indooroopilly | ECC Rating (A) | 451 | 451 | 451 | 451 | 451
Tennyson Bulk | F703-1 | Sherwood | Indooroopilly | 50 POE Load (A) | 381 | 382 | 381 | 380 | 380
Victoria Park Bulk | 627-1 | Victoria Pk BS | Astor Tce | NCC Rating (A) | 415 | 415 | 415 | 415 | 415 | Urban | 70
Victoria Park Bulk | 627-1 | Victoria Pk BS | Astor Tce | 10 POE Load (A) | 0.15298 | 0.15298 | 0.15298 | 0.15298 | 0.15298
Victoria Park Bulk | 627-1 | Victoria Pk BS | Astor Tce | Power Factor | 0.96802 | 0.96802 | 0.96802 | 0.96802 | 0.96802
Victoria Park Bulk | 627-1 | Victoria Pk BS | Astor Tce | ECC Rating (A) | 415 | 415 | 415 | 415 | 415
Victoria Park Bulk | 627-1 | Victoria Pk BS | Astor Tce | 50 POE Load (A) | 220.5021 | 221 | 221.0068 | 220.5693 | 221.3564
Victoria Park Bulk | 628-1 | Victoria Pk BS | Astor Tce | NCC Rating (A) | 415 | 415 | 415 | 415 | 415 | Urban | 70
Victoria Park Bulk | 628-1 | Victoria Pk BS | Astor Tce | 10 POE Load (A) | 229.8056 | 230.3259 | 230.3331 | 229.8759 | 230.8147
Victoria Park Bulk | 628-1 | Victoria Pk BS | Astor Tce | Power Factor | 0.99213 | 0.99204 | 0.99204 | 0.99212 | 0.99196
Victoria Park Bulk | 628-1 | Victoria Pk BS | Astor Tce | ECC Rating (A) | 415 | 415 | 415 | 415 | 415
Victoria Park Bulk | 628-1 | Victoria Pk BS | Astor Tce | 50 POE Load (A) | 446 | 447 | 447 | 447 | 447
Victoria Park Bulk | 639-1 | Victoria Pk BS | Newmarket | NCC Rating (A) | 503 | 503 | 503 | 503 | 503 | Urban | 70
Victoria Park Bulk | 639-1 | Victoria Pk BS | Newmarket | 10 POE Load (A) | 227.5139 | 226.9332 | 227.0613 | 227.0822 | 228.805
Victoria Park Bulk | 639-1 | Victoria Pk BS | Newmarket | Power Factor | 0.98515 | 0.98524 | 0.98522 | 0.98521 | 0.98498
Victoria Park Bulk | 639-1 | Victoria Pk BS | Newmarket | ECC Rating (A) | 585 | 585 | 585 | 585 | 585
Victoria Park Bulk | 639-1 | Victoria Pk BS | Newmarket | 50 POE Load (A) | 394 | 394 | 393 | 391 | 391
Victoria Park Bulk | 649-1 | Victoria Pk BS | Astor Tce | NCC Rating (A) | 415 | 415 | 415 | 415 | 415 | Urban | 70
Victoria Park Bulk | 649-1 | Victoria Pk BS | Astor Tce | 10 POE Load (A) | 232.5534 | 233.0798 | 233.087 | 232.6244 | 233.5743
Victoria Park Bulk | 649-1 | Victoria Pk BS | Astor Tce | Power Factor | 0.99227 | 0.99219 | 0.99218 | 0.99226 | 0.9921
Victoria Park Bulk | 649-1 | Victoria Pk BS | Astor Tce | ECC Rating (A) | 415 | 415 | 415 | 415 | 415
Victoria Park Bulk | 649-1 | Victoria Pk BS | Astor Tce | 50 POE Load (A) | 446 | 447 | 447 | 446 | 446
Victoria Park Bulk | 653-1 | Victoria Pk BS | Newmarket | NCC Rating (A) | 503 | 503 | 503 | 503 | 503 | Urban | 70
Victoria Park Bulk | 653-1 | Victoria Pk BS | Newmarket | 10 POE Load (A) | 227.5139 | 226.9333 | 227.0613 | 227.0822 | 228.805
Victoria Park Bulk | 653-1 | Victoria Pk BS | Newmarket | Power Factor | -0.96336 | -0.96343 | -0.96342 | -0.96341 | -0.96321
Victoria Park Bulk | 653-1 | Victoria Pk BS | Newmarket | ECC Rating (A) | 585 | 585 | 585 | 585 | 585
Victoria Park Bulk | 653-1 | Victoria Pk BS | Newmarket | 50 POE Load (A) | 394 | 394 | 393 | 391 | 391
Victoria Park Bulk | 689-1 | Victoria Pk BS | Astor Tce | NCC Rating (A) | 538 | 538 | 538 | 538 | 538 | Urban | 70
Victoria Park Bulk | 689-1 | Victoria Pk BS | Astor Tce | 10 POE Load (A) | 9.2482 | 9.2482 | 9.2482 | 9.2482 | 9.2482
Victoria Park Bulk | 689-1 | Victoria Pk BS | Astor Tce | Power Factor | -1 | -1 | -1 | -1 | -1
Victoria Park Bulk | 689-1 | Victoria Pk BS | Astor Tce | ECC Rating (A) | 538 | 538 | 538 | 538 | 538
Victoria Park Bulk | 689-1 | Victoria Pk BS | Astor Tce | 50 POE Load (A) | 9.2482 | 9.2482 | 9.2482 | 9.2482 | 9.2482
Note on L1631: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: F421-1: Open CB4742 @ ARL and Open CB3892 @ LDR
Note on L1646: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: F474A-1: Open CB4742 @ HWL and Open CB3892 @ LDR