## Coversheet
Customer R1 Checklist and GPS Issues Register (5MW and above)
This document is intended for use by the Proponent, the relevant NSP, and AEMO to confirm that the applicant has provided all required information to support Registration, and to facilitate the tracking of comments and issues.
After the R1 package has been accepted, this document will also be used to monitor and record matters related to the Generator Performance Standards (GPS), the GPS Compliance Report, and the RUG throughout the Registration process.
Proponents are to make note of:
The Power System Model Guidelines
AEMO Access Standard Assessment Guide
AEMO Dynamic Model Acceptance Guideline
AEMO Connection Application Submission Review Checklist
R1 Capability Assessment Guideline
AEMO R1 Capability Form
AEMO Connection Process Guide - Completion
Commissioning Program Template
Hold Point Template
AEMO Communication System Failure Guidelines
AEMO PSSE 36 Transition
5.3.9 Guideline
Please note: This is a general reference list and may not capture every requirement for all projects. Proponents should consult their project sponsor for clarification before commencing the R1 and R2 phases. This document does not cover construction activities. Proponents are responsible for ensuring they are using the most current version of the checklist at the time of submission. It is strongly recommended that R1 and R2 submissions follow a clear and well‑structured file hierarchy. Files should be appropriately referenced within the checklist, and a transmittal should be included to help quickly identify any missing or blocked files, reducing the likelihood of rework.
Release:
2026-02-24
Ver 2.6
Updated AEMO Commissioning documentation linked
Status
Submitted. Detail review in R1 due diligence phase.
Not submitted.
Submitted. Submission not acceptable.
No change from application, no additional documentation needed
Quality
Preliminary review indicates consistency.
Preliminary review indicates lack of consistency.
Model Checks
Preliminary review indicates model suitable to commence R1 due diligence.
Preliminary review indicates model is not suitable to commence R1 due diligence.
Submitted. Model to be reviewed in R1 Due Diligence.

## R1 Application review checklist
Item | Description | Customer Check and File/s Reference Select N/A if applicable | NSP Status | NSP Comment | AEMO Comment | Reference
Documentation completeness checklist
Note | This checklist is for Registration technical assessment, not construction activities or detailed design. Registration technical studies and construction can occur in parallel, or separately, and are not linked.
1 | Payment - does the customer wish to have an invoice issued during the completeness review?
2 | Completed AEMO R1 checklist - https://aemo.com.au/-/media/files/electricity/nem/network_connections/stage-6/generator-connection-r1-submission-checklist.pdf
3 | Site Location and Layout drawings
4 | Single line diagrams of the proposed: • Connection arrangement and generating system clearly showing the connection point including primary electrical SLD for all collector circuits showing switching arrangements for each generating unit.
• Revenue meters and power quality meters
• Protection systems
• Auxiliary supply arrangement, detailing agreed auxiliary arrangement
• SCADA and communications SLD
5 | Updated Generator Performance Standards (GPS) (as agreed at 5.3.4A) in Microsoft Word format. Ensure all clauses which make reference to 'to be completed with detailed design' have been updated to reflect the appropriate wording. NB: If any previously agreed Negotiated Access Standard requires a change or an Automatic Access Standard require modification to Negotiated, please discuss with AEMO and NSP representatives for the most appropriate mechanism. This may require a 5.3.9 process, which can occur parallel to the R1 capability phase.
6 | 5.3.9 documentation, if relevant. Refer to AEMO templates - https://www.aemo.com.au/-/media/files/electricity/nem/network_connections/transmission-and-distribution/ner-5-3-9-altering-a-generating-system/gs-or-irs-change-form.docx
7 | If relevant, and there are changes since 5.3.4A agreement, updated connection studies report(s) detailing and demonstrating how the applicant intends to meet each of the performance standards.
8 | Updated PSS®E software simulation models (in .DLL or .obj/.lib in V34.5 format and V36 format) representing the generating system that meet the Generating System Model Guidelines and Modelling Requirements, to reflect any changes the occur due to detailed design. RMS PSS®E model files include (.sav, .raw, .dyr files) and sequence component data and connection numbers for Transformer vector group orientation. Generator impedance data must be consistent with the equipment data sheets and S5.2.8, and facilitate calculation of short-circuit currents (e.g. using ‘IEC’ method)
9 | If relevant, updated releasable user guide (RUG) incorporating details on how to use all PSS®E simulation models including load flow setup of the generating system, generating system voltage control scheme details, model control modes , dynamic setup with details of the model’s ICONs, CONs, STATEs and VARs. RUG is consistent with and meets the requirements of information in the AEMO Template RUG Template is available at: https://www.aemo.com.au/-/media/Files/Electricity/NEM/Network_Connections/Transmission-and-Distribution/Template-for-preparation-of-a-Releasable-User-Guide.docx
10 | If relevant, an updated complete set of PSCAD software simulation models including user guides (item 11) representing the generating system that meet the Power System Model Guidelines. The model shall also comply with Modelling Requirements (https://aemo.com.au/en/energy-systems/electricity/national-electricity-market-nem/participate-in-the-market/network-connections/modelling-requirements). Please note the NEM has transitioned to PSCAD v5. As such, models will now need to be submitted in v5. V5 Models must be compiled with Intel OneAPI Fortran Compiler: Classic 2021.x (32-bit & 64-bit). Models shall be delivered in a format that allows for maintenance for life of asset. (e.g. .dll, support files). NB. As per PSMG it is important that elements such as OLTC tap changers are represented accurately.
11 | If relevant, updated releasable user guide (RUG) incorporating details on how to use all PSCAD simulation models. RUG is consistent with and meets the requirements of information in the AEMO Template RUG Template is available at: https://www.aemo.com.au/-/media/Files/Electricity/NEM/Network_Connections/Transmission-and-Distribution/Template-for-preparation-of-a-Releasable-User-Guide.docx
12 | If the PSCAD MAT was not supplied at Application stage, the PSCAD Model Acceptance Test (MAT). This guideline can be found at: https://aemo.com.au/-/media/files/electricity/nem/network_connections/model-acceptance-test-guideline-nov-2021.pdf
13 | Updated Voltage Control Strategy document, finalising any matters which require input from detailed design.
14 | Generating System Design Datasheets including all referenced documents within the datasheets (Schedule 5.5 of the NER) S- Standard D- Design R1 – Registered pre- connection R2 – Registered post- connection Note: Not applicable data sheets shall be “greyed” out and not removed from the datasheets submission prior to AEMO reviewing and accepting it as “not applicable”.
15 | If updates are required from Application stage, generating system reactive capability curve during steady state conditions and transients. Capability curve points in MS Excel format.
16 | Final protection and control scheme details including those required to be modelled to assess the impact of the proposed generating system connection. N.B. This detail must include information on protection functionality and settings relating to S5.2.5.8, S5.2.5.9 and S5.2.5.10 protection schemes.
17 | If not previously suppiled at Application, confirmation of validity of models at low SCR levels. PSCAD - Supported by factory or laboratory testing (OEM). PSSe - Supported by model benchmarking against PSCAD.
18 | Where model updates have occurred, benchmarking report for the PSS®E and PSCAD responses, to confirm validity of PSS®E models and demonstrate minimum SCR for which the PSS®E model is valid
19 | Model source code associated with all PSS®E user written simulation models. The source must be for the model as applied and used in the assessment of the GPS and its Releasable User Guide. It must meet FORTAN/FLX source requirements as in Modelling Requirements (can be supplied to AEMO only).
20 | A set of functional block diagrams for RMS PSS®E models and PSCAD/EMTDC models including all functions between feedback signals and generating system output. The parameters of each functional block including all settings, gains, time constants, delays, deadbands and limits, as expected to be represented in standard Laplace block diagram. The characteristics of non-linear elements. The model functional block diagram illustrates all derivative states including derivative state variable names consistent with the block diagrams and the model settings/parameters.
21 | A map of parameters for PSS®E and PSCAD™ Models , including conversion process where applicable
22 | If required, and there are changes from the Application stage, Audio Frequency Load Control (AFLC) Compliance Studies.
23 | If there are updates or changes from the Application stage, Harmonic Compliance Studies.
24 | If relevant, updated Powerfactory model suitable for harmonic studies
25 | Energy Conversion Model. See https://aemo.com.au/energy-systems/electricity/national-electricity-market-nem/participate-in-the-market/registration/register-as-a-generator-in-the-nem for more information
26 | GPS Compliance Test Plan ('Commissioning Plan'). Refer to AEMO template https://www.aemo.com.au/-/media/files/electricity/nem/network_connections/transmission-and-distribution/completion/commissioning-program-template.docx
27 | SCADA signal list
28 | Copy of Full Impact Assessment, if relevant
29 | Communication failure control documentation, with an updates due to detailed design, as per AEMO guideline, https://aemo.com.au/-/media/files/electricity/nem/network_connections/stage-6/communication-system-failure-guidelines.pdf?la=en
Information consistency and quality check
1 | PSS®E and PSCAD Models are consistent with the final 'as constructed' or 'as designed' physical representation of the Generating System
2 | PSS®E and PSCAD Models are consistent with the final 'as constructed' or 'as designed' data sheets and the representation in the Generator Performance Standard – connection study report.
3 | PSS®E and PSCAD Models – parameters and performances are consistent with the following items: - Protection systems – over-voltage, over- frequency, under-voltage and under-frequency settings - Any other limitations or protection systems that would otherwise limit accuracy of one of the models, e.g. Multiple LVRT capability and protection settings for overspeed or oscillatory protection - Disturbance ride through logic and performance is consistent for the application of balanced disturbances, where models are consistent during and after the applied disturbance - Plant control system parameters and (step/induced disturbance) responses including and where applicable: o Active Power Controller o Frequency Controller o Voltage, PF and/or Reactive Power Controller To support these requirements the Applicant has provided PSSE/ PSCAD benchmarking assessment of the generating system based on a SMIB case setup taking into consideration lowest SCR conditions at POC. Application of balanced 3 phase voltage disturbance for a range of retained voltage profiles is overlayed against the accuracy requirements. Signals taken into consideration are Power, Voltage and Reactive Power.
4 | Final 'as constructed' or 'as designed' Single Line diagrams align with the model representation
5 | Protection settings report does not over-rule any other requirement in the GPS (i.e. quality check to ensure that protection settings design (which may be undertaken at detailed design stage) does not impede any otherwise agreed GPS item or stated capability)
Initial Model Check
1 | PSS®E model is provided as per Power System Model Guidelines. PSS®E model version is also consistent with Modelling Requirements. When the PSS®E model is opened and executed with PSSE software version used by AEMO: - The model does not result in unstable initialisation or initialisation that requires settling -The model does not result in initialisation or run time errors including non-convergence or suspect state errors - The model is dynamically stable for all possible ranges of system strength (short circuit ratio and X/R ratio) where the generating system would be in operation. - The model allows active power, voltage, power factor, and reactive power reference change to be performed
2 | PSCAD model is provided as per Power System Model Guidelines. PSCAD model version is also consistent with Modelling Requirements. When the PSCAD model is opened and executed: - The model is dynamically stable for all possible ranges of system strength (short circuit ratio and X/R ratio) where the generating system would be in operation, and the model presented in the SMIB case is representative of the lowest SCR for the generating system. - The model initialises and is able to remain stable at rated output and prior to application of any disturbance. - The model is able to run through a balanced fault application in the SMIB case and achieve stable operating condition upon removal of the fault/disturbance. - The model is able to run through an unbalanced single phase and phase-to- phase-to-ground disturbance application in the SMIB case and achieve stable operating condition upon removal of the disturbance. - The generating system (model) meets the requirements of the NER under the definition of “continuous uninterrupted operation” including “responding so as to not exacerbate or prolong the disturbance”. - The model allows active power, voltage, power factor, and reactive power reference change to be performed
Requirements for Commissioning
Informative, to clarify requirements that must be met prior to commissioning commencement
1 | Registration with AEMO. Please note the NEM Generation Registration Guidelines, found on the AEMO Website https://www.aemo.com.au/energy-systems/electricity/national-electricity-market-nem/participate-in-the-market/registration/registration-fact-sheets-and-guides
2 | SCADA signal check through to AEMO (Part of Registration)
3 | Energy Conversion Model Available
4 | If required, site-specific DLF (Part of Registration)
5 | Agreed GPS Compliance Test Plan ('Commissioning Plan')
6 | Agreed Operating Protocol
7 | Commissioning Schedule for the GPS Commissioning Process
8 | Detailed commissioning schedule for first and second hold points
9 | Calibration certificates for compliance/R2 measurement equipment provided to AEMO and NSP
10 | Pre-test simulation studies, including wide area studies of impacts of voltage steps and reactive capability tests
11 | 7 days background PQ data recorded
12 | AFWs submitted (10 business days lead time); 28 days required for Powerlink switching
13 | Physical settings uploaded into each power plant controller and inverter provided to the NSP and AEMO
14 | Comparison of physical settings, PSCAD settings, and PSS®E settings
15 | Details of the hot commissioning tests to be applied, detailing real power output steps, test duration, reactive power tests
16 | Pre-commissioning internal plant checks as relevant, e.g. internal communications fail tests, communications delay timing tests, handover between Master and Slave PPC, protection systems commissioned and injection tests, etc. NB. There may be specific requirements for your site. The above is general in nature and may not capture all required tests.
17 | HV audit completed and signed-off
18 | Risk assessments completed and signed-off
19 | If relevant, curtailment scheme(s) commissioned and operational

## DataCategories
Data is coded in categories, according to the stage at which it is available in the build-up of data during the process of forming a connection or obtaining access to a network, with data acquired at each stage being carried forward, or enhanced in subsequent stages, e.g. by testing. The Power System Model Guidelines, Power System Design Data Sheet and Power System Setting Data Sheet identify for each type of data, its category in terms of clause S5.5.2. Codes: S = Standard Planning Data; D = Detailed Planning Data; R = Registered Data (R1 pre-connection, R2 post-connection)
Preliminary system planning data - Preliminary system planning data is required for submission with the application to connect, to allow the Network Service Provider to prepare an offer of terms and conditions for a connection agreement and to assess the requirement for, and effect of, network augmentation or extension options. Such data is normally limited to the items denoted as Standard Planning Data (S) in the Power System Model Guidelines, Power System Design Data Sheet, Power System Setting Data Sheet and in schedules 5.5.3 to 5.5.5. The Network Service Provider may, in cases where there is reasonable doubt as to the viability of a proposal, require the submission of other data before making an offer to connect or to amend a connection agreement.
Registered system planning data - Registered system planning data is the class of data which will be included in the connection agreement signed by both parties. It consists of the preliminary system planning data plus those items denoted in the attached schedules as Detailed Planning Data (D). The latter must be submitted by the Registered Participant in time for inclusion in the connection agreement.
Registered data - Registered Data consists of data validated and agreed between the Network Service Provider and the Registered Participant, such data being: (a) prior to actual connection and provision of access, data derived from manufacturers' data, detailed design calculations, works or site tests etc. (R1); and (b) after connection, data derived from on-system testing (R2). All of the data will, from this stage, be categorised and referred to as Registered Data; but for convenience the schedules omit placing a higher ranked code next to items which are expected to already be valid at an earlier stage.

## GPS
NSP Comments and Issues List
Item | Section | Reference | Issue/Comment | Proponent Response | AEMO comments | NSP Comments | Issue Status | Reference Information
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21

## GPS Compliance Report
NSP Comments and Issues List
Item | Section | Reference | Issue/Comment | Proponent Response | AEMO comments | NSP Comments | Issue Status | Reference Information
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21

## RUG
NSP Comments and Issues List
Item | Section | Reference | Issue/Comment | Proponent Response | AEMO comments | NSP Comments | Issue Status | Reference Information
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21