## Coversheet
Application Checklist For Loads
This document is to be used by the Applicant and Energex to determine whether a load connection has included all of the required information to progress an application.
Refer to S5.3.1 of the National Electricity Rules, "Conditions for Connection of Customers"
Other resources:
Large Customer Connection Manual
MIR
QECM
STNW3522 Standard for Large Customer Connections
AEMO System Strength Impact Assessment Guidelines
STNW1179
Please note this list is a general list and may not reflect all requirements in some cases. Please discuss specific questions with your project sponsor prior to application.
Release:
2026-02-12
Ver 3.4
Doc ID: MCT034

## Application review checklist
Item | Description | Customer Check | Energex Comment | Reference | Status
Documentation completeness checklist
1 | Energex Technical Assessment
2 | Completed Application Form
3 | Payment - does the customer wish to have an invoice issued during the completeness review?
4 | Customer's preference for Contestable Works, DCT Works
5 | Site Location and Layout drawings - Customer switchroom location - DNSP room location and size - Cable / Conductor path from property boundary to switchroom - Access easements and roadways, plant delivery route
6a | Single line diagrams of the proposed: - Connection arrangement clearly showing the connection point including primary electrical SLD for all circuits showing switching arrangements, noting compliance with STNW3522 - DNSP required relays, CTs,VTs and isolation points as relevant - if break-before-make generation is included, this must be shown and demonstrated to be break-before-make
6b | Revenue meters and Power quality meters as applicable (can be provided once detailed design is complete)
6c | If interlocking is present, evidence that the interlocking is fail-safe, compliant with QECM v4 section 5.6
7 | Where required, LV CT Metering Advice submitted
8 | List of all significant disturbing loads (e.g. pumps, welders, bore mills): - motor sizes and starting methods (DOL, star-delta, VSD, etc) - frequency of starts and duty cycles - operational power factors - motor datasheets, including synchronous, transient and sub-transient reactances - inverter-based load information, if applicable -harmonic performance
8a | If disturbing loads are present, a voltage fluctuation (i.e., flicker) study to demonstrate compliance with the allocation provided in the planning report
9 | Intended operating times
10 | Transformer or plant energisation study where need indicated in the Technical Assessment
11 | Evidence of compliance with the requirements of Schedule 5.3 as indicated in the Technical Assessment
12 | If indicated in the planning report, design report to demonstrate compliance with power factor requirements
13 | If relevant, a complete set of PSCAD software simulation models including user guides (see Item 14) representing the inverter based load that meet the Power System Model Guidelines. The model shall also comply with Modelling Requirements (https://aemo.com.au/en/energy-systems/electricity/national-electricity-market-nem/participate-in-the-market/network-connections/modelling-requirements). If you are unsure whether this applies to your project, refer to the Technical Assessment.
14 | If relevant, Releasable User Guide (RUG) incorporating details on how to use all PSCAD simulation models; RUG is consistent with and meets the requirements of information in the AEMO Template RUG Template is available at: https://www.aemo.com.au/-/media/Files/Electricity/NEM/Network_Connections/Transmission-and-Distribution/Template-for-preparation-of-a-Releasable-User-Guide.docx
15 | Consideration of future generation needs, to ensure design allows for compliance with generation standards