## Notes
Sub-Transmission Feeders Forecasts (Energex Distribution Annual Planning Report 2020-21 to 2024-25)
This workbook provides 5 year forecast capacity and loading information for sub-transmission feeders in the Energex network.
This workbook forms part of the Energex Distribution Annual Planning Report 2020-21 to 2024-25 (DAPR) and should be read in conjunction with the report document.
Energex Distribution Annual Planning Report is prepared and made available solely for information purposes. While care was taken in the preparation of the information in this report, and it is provided in good faith, Energex accepts no responsibility or liability (including without limitation, liability to any person by reason of negligence or negligent mis-statement) for any loss or damage that may be incurred by any person acting in reliance on this information or assumptions drawn from it, except to the extent that liability under any applicable Queensland or Commonwealth of Australia statute cannot be excluded.
It contains assumptions regarding, among other things, economic growth and load forecasts which may or may not prove to be correct. The forecasts included in the document involve subjective judgements and analysis which are subject to significant uncertainties and contingencies, many of which are out of the control of Energex. Furthermore, forecasted data is subject to ongoing variation due to COVID 19 impacts. Energex makes no representation or warranty as to the accuracy, reliability, completeness or suitability for any particular purpose of the information in this document. All information should be independently investigated, reviewed, analysed and verified, and must not be relied upon in connection with any investment proposal or decision.
The following sections list the 33kV feeders, their forecast loads, power factor, customer category and available load transfers. The feeder loads are calculated from load flow results using forecast substation demands. For the transmission and sub-transmission feeders, load flow studies are conducted for system normal and single contingency situations.
The forecast and capacity cut-off date for the winter season is 1 June of each year, and for the summer season is 1 December of each year. For example, 2021 winter forecast includes all committed projects with a proposed commissioning date up to 1 June 2021, and the 2020/21 summer forecast includes all committed projects with a proposed commissioning date up to 1 December 2020.
Assessment of 33 kV feeders is performed under four possible risk periods: winter day, winter night, summer day and summer night. For the winter table, the worst case (highest) load between winter day and winter night has been represented in the table.
Peak, reconciled, compensated load forecasts have been used in the 33kV feeder analyses, with 50 PoE forecast load used for single contingency studies, and 10 PoE forecast load used for system normal studies.
Feeder capacities are shown for ECC and NCC. These ratings have also been adjusted for known committed projects. All load transfers associated with contingent condition include acceptable feeder voltage profiles.
Although the conductor rating is generally the limiting factor for feeder capacity, there are other significant items of plant, such as the feeder circuit breaker, that can also restrict capacity. Furthermore, other factors such as voltage constraints and load sharing between parallel underground feeders can sometimes de‑rate the capacity of the feeders due to thermal characteristic constraints. Each of these factors has been taken into account in the production of the forecast tables.
Interconnected feeders that supply multiple customers are examined in the following tables. Feeders exclusively supplying a customer owned substation or dedicated to a customer are not included in these tables.
A definition of terms is shown in the table below.
Definition of Terms Feeder Capacity and Forecast Tables
Term | Definition
NCC Rating (A) | Normal Cyclic Capacity - the total capacity with all network components and equipment intact. This is the maximum permissible peak daily loading for a given load cycle that a feeder can supply each day of its life. For overhead feeders, the NCC is the conductor rating with an assumed 1m/s wind, orthogonal to the line. For underground cables, the NCC assumes that there are sufficient temperature and current operating margins from the thermal inertia of the cable and its surroundings.
10 PoE Load (A) | Peak load forecast with 10% probability of being exceeded (one in every 10 years will be exceeded). Based on normal expected growth rates and weather corrected starting loads.
Power Factor (System Normal) | Lowest power factor along the feeder at 10 PoE Peak Load. Where the Power Factor is either 0 the feeder is a normally open feeder that does not have load under System Normal conditions.
ECC Rating (A) | Emergency Cyclic Capacity – the long term firm delivery capacity under single contingency conditions. Some underground cables are installed in close proximity to other circuits and are normally de‑rated to allow for the heat generated by the adjacent cables. ECC is the higher capacity available when any adjacent circuits have been unloaded. For overhead conductors which do not benefit from this phenomenon, the ECC is synonymous with the NCC.
50 PoE Load (A) | Peak load forecast with 50% probability of being exceeded (one in every two years will be exceeded). Based on normal expected growth rates & weather corrected starting loads. This is the worst case (highest) load forecast beween winter day and winter night.
Customer Category | For security standard application, the general type of customer a sub-transmission, or transmission feeder is supplying.
Transfers | This is the total amount of load transfers that are available following the worst case network contingency. This includes automatic transfers that are controlled automatically through SCADA and are generally implemented within a minute, load transfers that can be implemented through screen switching by a network controller, manual transfers that are deployed via manually controlled switchgear locally by field staff, and mobile generation which can be deployed by field staff by moving generation to specific sites. It should be noted under the Safety Net in the Distribution Authority, it is generally assumed that 4MVA (70A) of generation is available for Urban feeders to meet this criteria and 10MVA (170A) is available for Rural feeders. These values have been used as a default in the forecast tables where these are sufficient to reduce the 50PoE load below the ECC rating. Where the load is still above the ECC rating, specific load transfers have been calculated for the feeder to determine whether the Safety Net criteria is met.
Hours PA > 95% Peak Load | The forecast number of hours per annum where the load exceeded 95% of the peak 50 PoE demand. This information is not readily available for every feeder without significant analysis being undertaken. As such, this has only been provided where a feeder does not meet the Safety Net criteria or is otherwise in the Limitations and Proposed Solutions table.

## 33kV Feeders-Winter
Bulk Supply Name | Feeder | From Substation | To Substation | Attributes | 2021 | 2022 | 2023 | 2024 | 2025 | Customer Category | Transfers | Hours PA > 95% Peak Load
Abermain Bulk | 357-1 | Abermain BS | 357 Tee1 | NCC Rating (A) | 554 | 554 | 554 | 554 | 554 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 92 | 91 | 90 | 89 | 88
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1
|  |  |  | ECC Rating (A) | 554 | 554 | 554 | 554 | 554
|  |  |  | 50 POE Load (A) | 233 | 277 | 275 | 273 | 273
Abermain Bulk | 357-2 | 357 Tee1 | Redbank | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 180 | 238 | 237 | 236 | 236
Abermain Bulk | 357-3 | 357 Tee1 | Moggill | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 92 | 91 | 90 | 89 | 89
|  |  |  | Power Factor | 0.998 | 0.998 | 0.998 | 0.998 | 0.998
|  |  |  | ECC Rating (A) | 917 | 917 | 917 | 917 | 917
|  |  |  | 50 POE Load (A) | 270 | 266 | 264 | 261 | 259
Abermain Bulk | 358-1 | Abermain BS | Ebbw Vale | NCC Rating (A) | 525 | 525 | 525 | 525 | 525 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 525 | 525 | 525 | 525 | 525
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Abermain Bulk | 364-1 | Marburg | Rosewood | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 63 | 63 | 69 | 74 | 79
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 0.999
|  |  |  | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | 50 POE Load (A) | 202 | 202 | 226 | 242 | 260
Abermain Bulk | 365-1 | Abermain BS | 365 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 271 | 272 | 305 | 322 | 340
|  |  |  | Power Factor | 0.955 | 0.955 | 0.952 | 0.948 | 0.943
|  |  |  | ECC Rating (A) | 944 | 944 | 944 | 944 | 944
|  |  |  | 50 POE Load (A) | 644 | 646 | 732 | 779 | 827
Abermain Bulk | 365-2 | 365 Tee1 | 366 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Abermain Bulk | 365-3 | 365 Tee1 | Karrabin | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 271 | 272 | 305 | 322 | 340
|  |  |  | Power Factor | 0.965 | 0.965 | 0.964 | 0.961 | 0.958
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 510 | 511 | 579 | 616 | 654
Abermain Bulk | 366-1 | Abermain BS | 366 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 296 | 297 | 333 | 352 | 371
|  |  |  | Power Factor | 0.955 | 0.955 | 0.952 | 0.948 | 0.944
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 513 | 515 | 582 | 619 | 657
Abermain Bulk | 366-2 | 366 Tee1 | Karrabin | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 296 | 297 | 333 | 352 | 371
|  |  |  | Power Factor | 0.965 | 0.965 | 0.964 | 0.96 | 0.957
|  |  |  | ECC Rating (A) | 845 | 845 | 845 | 845 | 845
|  |  |  | 50 POE Load (A) | 572 | 574 | 649 | 690 | 732
Abermain Bulk | 366-3 | 366 Tee1 | 365 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Abermain Bulk | 367-1 | Abermain BS | Mt Crosby West | NCC Rating (A) | 581 | 581 | 581 | 581 | 581 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 215 | 214 | 216 | 215 | 215
|  |  |  | Power Factor | 0.928 | 0.922 | 0.958 | 0.958 | 0.959
|  |  |  | ECC Rating (A) | 581 | 581 | 581 | 581 | 581
|  |  |  | 50 POE Load (A) | 388 | 385 | 388 | 387 | 387
Abermain Bulk | 368-1 | Abermain BS | Mt Crosby | NCC Rating (A) | 552 | 552 | 552 | 552 | 552 | HighSec | 0 | NA
|  |  |  | 10 POE Load (A) | 172 | 171 | 172 | 171 | 171
|  |  |  | Power Factor | 0.914 | 0.906 | 0.95 | 0.95 | 0.95
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 390 | 388 | 388 | 389 | 389
Abermain Bulk | 369-1 | Abermain BS | Nth Ipswich | NCC Rating (A) | 548 | 548 | 548 | 548 | 548 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 128 | 128 | 128 | 129 | 129
|  |  |  | Power Factor | 0.986 | 0.986 | 0.986 | 0.986 | 0.986
|  |  |  | ECC Rating (A) | 548 | 548 | 548 | 548 | 548
|  |  |  | 50 POE Load (A) | 274 | 274 | 275 | 276 | 277
Abermain Bulk | 370-1 | Abermain BS | Nth Ipswich | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 130 | 130 | 130 | 131 | 132
|  |  |  | Power Factor | 0.987 | 0.987 | 0.987 | 0.987 | 0.986
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 276 | 276 | 277 | 278 | 280
Abermain Bulk | 387-1 | Abermain BS | Marburg | NCC Rating (A) | 290 | 290 | 290 | 290 | 290 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 122 | 122 | 130 | 136 | 142
|  |  |  | Power Factor | 0.994 | 0.994 | 0.994 | 0.993 | 0.991
|  |  |  | ECC Rating (A) | 290 | 290 | 290 | 290 | 290
|  |  |  | 50 POE Load (A) | 163 | 163 | 177 | 187 | 198
Abermain Bulk | 3901-1 | Karrabin | Amberley | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 136 | 136 | 136 | 152 | 168
|  |  |  | Power Factor | 0.946 | 0.946 | 0.943 | 0.937 | 0.931
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 377 | 377 | 376 | 421 | 468
Abermain Bulk | 420-1 | Mt Crosby West | Mt Crosby | NCC Rating (A) | 490 | 490 | 490 | 490 | 490 | HighSec | 0 | NA
|  |  |  | 10 POE Load (A) | 33 | 34 | 37 | 37 | 38
|  |  |  | Power Factor | 0.728 | 0.799 | 0.963 | 0.964 | 0.964
|  |  |  | ECC Rating (A) | 490 | 490 | 490 | 490 | 490
|  |  |  | 50 POE Load (A) | 208 | 208 | 211 | 211 | 212
Abermain Bulk | 436-1 | Amberley | 436 Tee1 | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 39 | 38 | 36 | 34 | 33
|  |  |  | Power Factor | 0.726 | 0.724 | 0.665 | 0.623 | 0.582
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | 50 POE Load (A) | 214 | 214 | 220 | 225 | 232
Abermain Bulk | 436-2 | 436 Tee1 | Ebeneezer | NCC Rating (A) | 521 | 521 | 521 | 521 | 521 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 521 | 521 | 521 | 521 | 521
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Abermain Bulk | 436-4 | 436 Tee1 | Rosewood | NCC Rating (A) | 416 | 416 | 416 | 416 | 416 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 39 | 39 | 37 | 35 | 33
|  |  |  | Power Factor | 0.719 | 0.718 | 0.658 | 0.616 | 0.574
|  |  |  | ECC Rating (A) | 416 | 416 | 416 | 416 | 416
|  |  |  | 50 POE Load (A) | 304 | 304 | 312 | 320 | 329
Abermain Bulk | 445-1 | Abermain BS | Moggill | NCC Rating (A) | 776 | 776 | 776 | 776 | 776 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 126 | 124 | 123 | 122 | 121
|  |  |  | Power Factor | 0.998 | 0.998 | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 300 | 296 | 293 | 290 | 288
Abermain Bulk | 475-1 | Karrabin | Amberley | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 135 | 135 | 135 | 150 | 167
|  |  |  | Power Factor | 0.947 | 0.947 | 0.945 | 0.939 | 0.933
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 377 | 376 | 376 | 421 | 468
Abermain Bulk | 673-1 | Moggill | Kenmore | NCC Rating (A) | 636 | 636 | 636 | 636 | 636 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 5 | 5 | 5 | 5 | 5
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 636 | 636 | 636 | 636 | 636
|  |  |  | 50 POE Load (A) | 5 | 5 | 5 | 5 | 5
Algester Bulk | 3400-1 | Algester BS | Calamvale | NCC Rating (A) | 735 | 735 | 735 | 735 | 735 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 230 | 227 | 225 | 224 | 223
|  |  |  | Power Factor | 0.993 | 0.993 | 0.993 | 0.993 | 0.993
|  |  |  | ECC Rating (A) | 810 | 810 | 810 | 810 | 810
|  |  |  | 50 POE Load (A) | 471 | 465 | 461 | 458 | 454
Algester Bulk | 3402-1 | Algester BS | Acacia Ridge | NCC Rating (A) | 728 | 728 | 728 | 728 | 728 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 134 | 132 | 130 | 137 | 136
|  |  |  | Power Factor | 0.997 | 0.998 | 0.998 | 0.93 | 0.93
|  |  |  | ECC Rating (A) | 782 | 782 | 782 | 782 | 782
|  |  |  | 50 POE Load (A) | 291 | 287 | 283 | 281 | 279
Algester Bulk | 3403-1 | Algester BS | Acacia Ridge | NCC Rating (A) | 728 | 728 | 728 | 728 | 728 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 134 | 132 | 131 | 137 | 136
|  |  |  | Power Factor | 0.997 | 0.998 | 0.998 | 0.93 | 0.93
|  |  |  | ECC Rating (A) | 782 | 782 | 782 | 782 | 782
|  |  |  | 50 POE Load (A) | 291 | 287 | 283 | 281 | 279
Algester Bulk | 3405-1 | Algester BS | Calamvale | NCC Rating (A) | 735 | 735 | 735 | 735 | 735 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 230 | 227 | 226 | 225 | 223
|  |  |  | Power Factor | 0.993 | 0.993 | 0.993 | 0.993 | 0.993
|  |  |  | ECC Rating (A) | 810 | 810 | 810 | 810 | 810
|  |  |  | 50 POE Load (A) | 471 | 465 | 461 | 458 | 454
Archerfield Bulk | 597-1 | Rocklea | Salisbury | NCC Rating (A) | 710 | 710 | 710 | 710 | 710 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 149 | 143 | 137 | 132 | 131
|  |  |  | Power Factor | 0.977 | 0.978 | 0.978 | 0.979 | 0.979
|  |  |  | ECC Rating (A) | 710 | 710 | 710 | 710 | 710
|  |  |  | 50 POE Load (A) | 144 | 138 | 132 | 128 | 126
Archerfield Bulk | 635-1 | Archerfield BS | Coopers Plains | NCC Rating (A) | 573 | 573 | 573 | 573 | 573 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 294 | 280 | 260 | 246 | 241
|  |  |  | Power Factor | 0.994 | 0.996 | 0.933 | 0.934 | 0.935
|  |  |  | ECC Rating (A) | 573 | 573 | 573 | 573 | 573
|  |  |  | 50 POE Load (A) | 311 | 323 | 274 | 260 | 254
Archerfield Bulk | 650-1 | Archerfield BS | Rocklea | NCC Rating (A) | 688 | 688 | 688 | 688 | 688 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 202 | 197 | 191 | 186 | 184
|  |  |  | Power Factor | 0.974 | 0.974 | 0.974 | 0.975 | 0.975
|  |  |  | ECC Rating (A) | 784 | 784 | 784 | 784 | 784
|  |  |  | 50 POE Load (A) | 409 | 397 | 386 | 376 | 373
Archerfield Bulk | 651-1 | Archerfield BS | Rocklea | NCC Rating (A) | 688 | 688 | 688 | 688 | 688 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 200 | 194 | 189 | 184 | 182
|  |  |  | Power Factor | 0.973 | 0.974 | 0.974 | 0.975 | 0.975
|  |  |  | ECC Rating (A) | 784 | 784 | 784 | 784 | 784
|  |  |  | 50 POE Load (A) | 409 | 397 | 386 | 377 | 373
Ashgrove West Bulk | 432-1 | Ashgrove West BS | Toowong | NCC Rating (A) | 516 | 516 | 516 | 516 | 516 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 14 | 14 | 14 | 14 | 14
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 516 | 516 | 516 | 516 | 516
|  |  |  | 50 POE Load (A) | 15 | 15 | 15 | 15 | 15
Ashgrove West Bulk | 552-1 | Ashgrove West BS | Ashgrove | NCC Rating (A) | 634 | 634 | 634 | 634 | 634 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 119 | 117 | 116 | 115 | 115
|  |  |  | Power Factor | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
|  |  |  | ECC Rating (A) | 634 | 634 | 634 | 634 | 634
|  |  |  | 50 POE Load (A) | 185 | 182 | 181 | 179 | 178
Ashgrove West Bulk | 565-1 | Ashgrove West BS | Ashgrove | NCC Rating (A) | 882 | 882 | 882 | 882 | 882 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 82 | 81 | 80 | 79 | 79
|  |  |  | Power Factor | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
|  |  |  | ECC Rating (A) | 882 | 882 | 882 | 882 | 882
|  |  |  | 50 POE Load (A) | 126 | 124 | 123 | 122 | 122
Ashgrove West Bulk | 570-1 | Ashgrove West BS | Ashgrove | NCC Rating (A) | 634 | 634 | 634 | 634 | 634 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 116 | 114 | 114 | 113 | 112
|  |  |  | Power Factor | 0.997 | 0.997 | 0.997 | 0.997 | 0.996
|  |  |  | ECC Rating (A) | 712 | 712 | 712 | 712 | 712
|  |  |  | 50 POE Load (A) | 183 | 181 | 179 | 178 | 177
Ashgrove West Bulk | 585-1 | Ashgrove West BS | The Gap | NCC Rating (A) | 659 | 659 | 659 | 659 | 659 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 116 | 114 | 113 | 112 | 111
|  |  |  | Power Factor | 0.997 | 0.997 | 0.997 | 0.998 | 0.998
|  |  |  | ECC Rating (A) | 659 | 659 | 659 | 659 | 659
|  |  |  | 50 POE Load (A) | 116 | 114 | 113 | 112 | 111
Ashgrove West Bulk | 586-1 | Ashgrove West BS | The Gap | NCC Rating (A) | 659 | 659 | 659 | 659 | 659 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 131 | 129 | 128 | 127 | 126
|  |  |  | Power Factor | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
|  |  |  | ECC Rating (A) | 659 | 659 | 659 | 659 | 659
|  |  |  | 50 POE Load (A) | 131 | 129 | 128 | 127 | 126
Ashgrove West Bulk | 590-1 | Ashgrove BS | Toowong | NCC Rating (A) | 705 | 705 | 705 | 705 | 705 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 259 | 257 | 256 | 255 | 254
|  |  |  | Power Factor | 0.98 | 0.981 | 0.981 | 0.981 | 0.981
|  |  |  | ECC Rating (A) | 705 | 705 | 705 | 705 | 705
|  |  |  | 50 POE Load (A) | 494 | 489 | 487 | 485 | 484
Ashgrove West Bulk | 591-1 | Ashgrove BS | Toowong | NCC Rating (A) | 705 | 705 | 705 | 705 | 705 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 259 | 256 | 255 | 255 | 254
|  |  |  | Power Factor | 0.98 | 0.98 | 0.981 | 0.981 | 0.981
|  |  |  | ECC Rating (A) | 705 | 705 | 705 | 705 | 705
|  |  |  | 50 POE Load (A) | 494 | 489 | 487 | 485 | 484
Ashgrove West Bulk | 675-1 | Ashgrove | Newmarket | NCC Rating (A) | 527 | 527 | 527 | 527 | 527 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 17 | 17 | 17 | 17 | 17
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 527 | 527 | 527 | 527 | 527
|  |  |  | 50 POE Load (A) | 19 | 19 | 19 | 19 | 19
Ashgrove West Bulk | 676-1 | Ashgrove | Newmarket | NCC Rating (A) | 527 | 527 | 527 | 527 | 527 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 17 | 17 | 17 | 17 | 17
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 527 | 527 | 527 | 527 | 527
|  |  |  | 50 POE Load (A) | 19 | 19 | 19 | 19 | 19
Beaudesert Bulk | 314-1 | Beaudesert BS | Jimboomba | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Beaudesert Bulk | 404-1 | Beaudesert | Innisplain | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 107 | 107 | 109 | 110 | 112
|  |  |  | Power Factor | 0.985 | 0.985 | 0.984 | 0.984 | 0.984
|  |  |  | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | 50 POE Load (A) | 191 | 191 | 194 | 196 | 199
Beaudesert Bulk | 466-1 | Beaudesert BS | Bromelton | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 87 | 91 | 105 | 118 | 131
|  |  |  | Power Factor | 0.967 | 0.995 | 0.992 | 0.989 | 0.985
|  |  |  | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
|  |  |  | 50 POE Load (A) | 205 | 215 | 247 | 279 | 312
Beaudesert Bulk | 467-1 | Beaudesert BS | Bromelton | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 58 | 61 | 70 | 78 | 88
|  |  |  | Power Factor | 0.992 | 0.999 | 1 | 1 | 0.999
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 212 | 222 | 256 | 289 | 324
Beaudesert Bulk | 468-1 | Beaudesert BS | Beaudesert | NCC Rating (A) | 579 | 579 | 579 | 579 | 579 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 251 | 251 | 253 | 255 | 257
|  |  |  | Power Factor | 0.952 | 0.952 | 0.952 | 0.952 | 0.951
|  |  |  | ECC Rating (A) | 579 | 579 | 579 | 579 | 579
|  |  |  | 50 POE Load (A) | 315 | 313 | 314 | 316 | 318
Beaudesert Bulk | 469-1 | Beaudesert BS | 469 Tee1 | NCC Rating (A) | 537 | 537 | 537 | 537 | 537 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 260 | 260 | 262 | 264 | 266
|  |  |  | Power Factor | 0.98 | 0.98 | 0.98 | 0.98 | 0.979
|  |  |  | ECC Rating (A) | 537 | 537 | 537 | 537 | 537
|  |  |  | 50 POE Load (A) | 488 | 488 | 491 | 495 | 499
Beaudesert Bulk | 469-2 | 469 Tee1 | Beaudesert | NCC Rating (A) | 579 | 579 | 579 | 579 | 579 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 94 | 96 | 98 | 101 | 103
|  |  |  | Power Factor | 0.993 | 0.993 | 0.992 | 0.992 | 0.991
|  |  |  | ECC Rating (A) | 579 | 579 | 579 | 579 | 579
|  |  |  | 50 POE Load (A) | 330 | 331 | 335 | 339 | 345
Beaudesert Bulk | 469-3 | 469 Tee1 | Mt Tamborine Bus 2 | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 167 | 164 | 164 | 164 | 163
|  |  |  | Power Factor | 0.978 | 0.979 | 0.979 | 0.979 | 0.979
|  |  |  | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
|  |  |  | 50 POE Load (A) | 319 | 314 | 312 | 311 | 310
Beenleigh Bulk | 3590-1 | Beenleigh BS | Loganholme | NCC Rating (A) | 810 | 810 | 810 | 810 | 810 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 268 | 264 | 262 | 260 | 258
|  |  |  | Power Factor | 0.986 | 0.987 | 0.987 | 0.987 | 0.987
|  |  |  | ECC Rating (A) | 810 | 810 | 810 | 810 | 810
|  |  |  | 50 POE Load (A) | 472 | 465 | 461 | 457 | 454
Beenleigh Bulk | 3591-1 | Cornubia | Loganholme | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 32 | 32 | 32 | 31 | 31
|  |  |  | Power Factor | 0.879 | 0.879 | 0.878 | 0.877 | 0.878
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 290 | 286 | 283 | 280 | 279
Beenleigh Bulk | 3600-1 | Yatala | Stapylton | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 73 | 80 | 79 | 78 | 78
|  |  |  | Power Factor | 0.974 | 0.973 | 0.974 | 0.974 | 0.974
|  |  |  | ECC Rating (A) | 921 | 921 | 921 | 921 | 921
|  |  |  | 50 POE Load (A) | 180 | 199 | 197 | 195 | 194
Beenleigh Bulk | 3601-1 | Yatala | Stapylton | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 70 | 77 | 76 | 75 | 75
|  |  |  | Power Factor | 0.972 | 0.971 | 0.971 | 0.971 | 0.971
|  |  |  | ECC Rating (A) | 921 | 921 | 921 | 921 | 921
|  |  |  | 50 POE Load (A) | 180 | 200 | 197 | 195 | 194
Beenleigh Bulk | 3620-1 | Beenleigh BS | Logan Village | NCC Rating (A) | 490 | 490 | 490 | 490 | 490 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 490 | 490 | 490 | 490 | 490
|  |  |  | 50 POE Load (A) | 182 | 179 | 182 | 185 | 189
Beenleigh Bulk | 402-1 | Beenleigh BS | 402 Tee1 | NCC Rating (A) | 579 | 579 | 579 | 579 | 579 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 220 | 217 | 216 | 216 | 215
|  |  |  | Power Factor | 0.975 | 0.976 | 0.976 | 0.976 | 0.976
|  |  |  | ECC Rating (A) | 579 | 579 | 579 | 579 | 579
|  |  |  | 50 POE Load (A) | 404 | 398 | 396 | 395 | 394
Beenleigh Bulk | 402-2 | 402 Tee1 | Tamborine Village | NCC Rating (A) | 469 | 469 | 469 | 469 | 469 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 63 | 62 | 63 | 63 | 63
|  |  |  | Power Factor | 0.988 | 0.988 | 0.988 | 0.988 | 0.988
|  |  |  | ECC Rating (A) | 469 | 469 | 469 | 469 | 469
|  |  |  | 50 POE Load (A) | 68 | 68 | 68 | 68 | 68
Beenleigh Bulk | 402-3 | 402 Tee1 | Mt Tamborine Bus 1 | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 157 | 155 | 154 | 153 | 152
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | ECC Rating (A) | 812 | 812 | 812 | 812 | 812
|  |  |  | 50 POE Load (A) | 340 | 335 | 333 | 332 | 330
Beenleigh Bulk | 405-1 | Beenleigh BS | 405 Tee1 | NCC Rating (A) | 868 | 868 | 868 | 868 | 868 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 194 | 191 | 190 | 188 | 187
|  |  |  | Power Factor | 0.986 | 0.986 | 0.986 | 0.986 | 0.986
|  |  |  | ECC Rating (A) | 988 | 988 | 988 | 988 | 988
|  |  |  | 50 POE Load (A) | 553 | 545 | 540 | 535 | 532
Beenleigh Bulk | 405-3 | 405 Tee1 | Cornubia | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 194 | 192 | 190 | 188 | 187
|  |  |  | Power Factor | 0.988 | 0.988 | 0.988 | 0.988 | 0.988
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 467 | 460 | 456 | 452 | 449
Beenleigh Bulk | 419-1 | Loganholme | Tanah Merah | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 896 | 896 | 896 | 896 | 896
|  |  |  | 50 POE Load (A) | 276 | 271 | 269 | 266 | 264
Beenleigh Bulk | 426-1 | Beenleigh BS | Yatala | NCC Rating (A) | 785 | 785 | 785 | 785 | 785 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 72 | 80 | 79 | 78 | 78
|  |  |  | Power Factor | 0.545 | 0.545 | 0.545 | 0.545 | 0.545
|  |  |  | ECC Rating (A) | 785 | 785 | 785 | 785 | 785
|  |  |  | 50 POE Load (A) | 148 | 163 | 161 | 160 | 159
Beenleigh Bulk | 427-1 | Beenleigh BS | Yatala | NCC Rating (A) | 785 | 785 | 785 | 785 | 785 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 69 | 77 | 76 | 75 | 74
|  |  |  | Power Factor | 0.976 | 0.974 | 0.974 | 0.975 | 0.975
|  |  |  | ECC Rating (A) | 785 | 785 | 785 | 785 | 785
|  |  |  | 50 POE Load (A) | 148 | 164 | 161 | 160 | 159
Beenleigh Bulk | 453-1 | Beenleigh BS | Beenleigh Nth | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 499 | 496 | 498 | 499 | 501
|  |  |  | Power Factor | 0.992 | 0.992 | 0.992 | 0.992 | 0.992
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 478 | 476 | 477 | 479 | 480
Beenleigh Bulk | 496-1 | Beenleigh Nth | Bethania | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 253 | 251 | 251 | 251 | 251
|  |  |  | Power Factor | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 355 | 353 | 353 | 353 | 353
Beerwah Bulk | 324-1 | Woodford | Kilcoy | NCC Rating (A) | 348 | 348 | 348 | 348 | 348 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 187 | 188 | 181 | 182 | 182
|  |  |  | Power Factor | 0.98 | 0.98 | 0.978 | 0.978 | 0.978
|  |  |  | ECC Rating (A) | 348 | 348 | 348 | 348 | 348
|  |  |  | 50 POE Load (A) | 181 | 180 | 176 | 175 | 175
Beerwah Bulk | 428-1 | Beerwah BS | Woodford | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 202 | 204 | 196 | 196 | 196
|  |  |  | Power Factor | 0.963 | 0.966 | 0.966 | 0.966 | 0.965
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | 50 POE Load (A) | 276 | 274 | 266 | 267 | 267
Beerwah Bulk | 447-1 | Somerset Dam | Kilcoy | NCC Rating (A) | 290 | 290 | 290 | 290 | 290 | Rural | 170 | 2
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 290 | 290 | 290 | 290 | 290
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Beerwah Bulk | 477-1 | 477 Tee1 | Maleny | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170 | 6
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Beerwah Bulk | 477-2 | 477 Tee1 | Woodford | NCC Rating (A) | 381 | 381 | 381 | 381 | 381 | Rural | 170 | 6
|  |  |  | 10 POE Load (A) | 149 | 147 | 146 | 145 | 145
|  |  |  | Power Factor | 0.991 | 0.991 | 0.991 | 0.991 | 0.991
|  |  |  | ECC Rating (A) | 381 | 381 | 381 | 381 | 381
|  |  |  | 50 POE Load (A) | 176 | 174 | 173 | 172 | 172
Beerwah Bulk | 477-3 | Beerwah | 477 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170 | 6
|  |  |  | 10 POE Load (A) | 149 | 147 | 146 | 145 | 145
|  |  |  | Power Factor | 0.988 | 0.988 | 0.988 | 0.988 | 0.988
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 159 | 158 | 157 | 156 | 155
Beerwah Bulk | 608-1 | Beerwah BS | Landsborough | NCC Rating (A) | 412 | 412 | 412 | 412 | 412 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 196 | 212 | 230 | 237 | 244
|  |  |  | Power Factor | 0.991 | 0.989 | 0.988 | 0.987 | 0.986
|  |  |  | ECC Rating (A) | 412 | 412 | 412 | 412 | 412
|  |  |  | 50 POE Load (A) | 186 | 202 | 219 | 226 | 232
Belmont Bulk | 527-1 | Mt Gravatt | Upper Mt Gravatt | NCC Rating (A) | 631 | 631 | 631 | 631 | 631 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 47 | 46 | 46 | 3 | 3
|  |  |  | Power Factor | 0.942 | 0.942 | 0.941 | 0.865 | 0.865
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 631 | 631
|  |  |  | 50 POE Load (A) | 159 | 158 | 157 | 3 | 3
Belmont Bulk | 631-1 | Belmont BS | Mt Gravatt | NCC Rating (A) | 446 | 446 | 446 | 446 | 446 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 215 | 212 | 212 | 212 | 212
|  |  |  | Power Factor | 0.99 | 0.991 | 0.991 | 0.991 | 0.991
|  |  |  | ECC Rating (A) | 494 | 494 | 494 | 494 | 494
|  |  |  | 50 POE Load (A) | 371 | 366 | 365 | 365 | 365
Belmont Bulk | 632-1 | Belmont BS | Mt Gravatt | NCC Rating (A) | 446 | 446 | 446 | 446 | 446 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 214 | 211 | 210 | 210 | 210
|  |  |  | Power Factor | 0.99 | 0.99 | 0.991 | 0.99 | 0.99
|  |  |  | ECC Rating (A) | 481 | 481 | 481 | 481 | 481
|  |  |  | 50 POE Load (A) | 370 | 366 | 364 | 364 | 364
Belmont Bulk | 647-1 | Belmont BS | Eight Mile Plains Bus 2 | NCC Rating (A) | 566 | 566 | 566 | 566 | 566 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 189 | 187 | 185 | 183 | 182
|  |  |  | Power Factor | 0.973 | 0.974 | 0.974 | 0.974 | 0.974
|  |  |  | ECC Rating (A) | 602 | 602 | 602 | 602 | 602
|  |  |  | 50 POE Load (A) | 470 | 464 | 459 | 454 | 451
Belmont Bulk | 660-1 | Belmont BS | Scrub Road | NCC Rating (A) | 716 | 716 | 716 | 716 | 716 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 184 | 181 | 180 | 178 | 177
|  |  |  | Power Factor | 0.987 | 0.987 | 0.987 | 0.987 | 0.987
|  |  |  | ECC Rating (A) | 795 | 795 | 795 | 795 | 795
|  |  |  | 50 POE Load (A) | 366 | 361 | 358 | 355 | 354
Belmont Bulk | 661-1 | Belmont BS | Scrub Road | NCC Rating (A) | 716 | 716 | 716 | 716 | 716 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 186 | 183 | 182 | 180 | 179
|  |  |  | Power Factor | 0.987 | 0.987 | 0.987 | 0.987 | 0.987
|  |  |  | ECC Rating (A) | 795 | 795 | 795 | 795 | 795
|  |  |  | 50 POE Load (A) | 366 | 361 | 358 | 355 | 354
Belmont Bulk | 662-1 | Belmont BS | Upper Mt Gravatt | NCC Rating (A) | 695 | 695 | 695 | 695 | 695 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 142 | 141 | 140 | 156 | 155
|  |  |  | Power Factor | 0.967 | 0.967 | 0.967 | 0.987 | 0.987
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 222 | 219 | 218 | 324 | 323
Belmont Bulk | 663-1 | Belmont BS | Upper Mt Gravatt | NCC Rating (A) | 695 | 695 | 695 | 695 | 695 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 144 | 142 | 142 | 158 | 157
|  |  |  | Power Factor | 0.967 | 0.967 | 0.967 | 0.988 | 0.988
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 223 | 220 | 219 | 324 | 323
Belmont Bulk | 692-1 | Belmont BS | Holland Pk East | NCC Rating (A) | 447 | 447 | 447 | 447 | 447 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 136 | 135 | 134 | 133 | 133
|  |  |  | Power Factor | 0.987 | 0.987 | 0.987 | 0.987 | 0.987
|  |  |  | ECC Rating (A) | 494 | 494 | 494 | 494 | 494
|  |  |  | 50 POE Load (A) | 274 | 271 | 270 | 268 | 267
Belmont Bulk | 693-1 | Belmont BS | Holland Pk East | NCC Rating (A) | 447 | 447 | 447 | 447 | 447 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 137 | 136 | 135 | 134 | 134
|  |  |  | Power Factor | 0.987 | 0.987 | 0.987 | 0.987 | 0.987
|  |  |  | ECC Rating (A) | 494 | 494 | 494 | 494 | 494
|  |  |  | 50 POE Load (A) | 274 | 271 | 270 | 268 | 267
Brendale Bulk | 303-1 | Brendale BS | Albany Ck | NCC Rating (A) | 788 | 788 | 788 | 788 | 788 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 161 | 159 | 158 | 157 | 155
|  |  |  | Power Factor | 0.995 | 0.995 | 0.996 | 0.996 | 0.996
|  |  |  | ECC Rating (A) | 902 | 902 | 902 | 902 | 902
|  |  |  | 50 POE Load (A) | 333 | 328 | 326 | 323 | 320
Brendale Bulk | 309-1 | Brendale BS | 309 Tee1 | NCC Rating (A) | 810 | 810 | 810 | 810 | 810 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 199 | 196 | 195 | 193 | 192
|  |  |  | Power Factor | 0.994 | 0.994 | 0.994 | 0.994 | 0.994
|  |  |  | ECC Rating (A) | 894 | 894 | 894 | 894 | 894
|  |  |  | 50 POE Load (A) | 563 | 555 | 551 | 547 | 543
Brendale Bulk | 309-2 | 309 Tee1 | Samford | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 59 | 58 | 58 | 57 | 56
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 224 | 221 | 219 | 217 | 215
Brendale Bulk | 309-3 | 309 Tee1 | Arana Hills | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 141 | 139 | 138 | 137 | 136
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | ECC Rating (A) | 912 | 912 | 912 | 912 | 912
|  |  |  | 50 POE Load (A) | 547 | 538 | 534 | 531 | 527
Brendale Bulk | 310-1 | Brendale BS | 310 Tee1 | NCC Rating (A) | 715 | 715 | 715 | 715 | 715 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 292 | 288 | 286 | 284 | 282
|  |  |  | Power Factor | 0.993 | 0.993 | 0.993 | 0.993 | 0.993
|  |  |  | ECC Rating (A) | 894 | 894 | 894 | 894 | 894
|  |  |  | 50 POE Load (A) | 585 | 576 | 573 | 569 | 565
Brendale Bulk | 310-2 | 310 Tee1 | Arana Hills | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 292 | 288 | 286 | 284 | 282
|  |  |  | Power Factor | 0.995 | 0.995 | 0.995 | 0.995 | 0.996
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 415 | 408 | 406 | 403 | 400
Brendale Bulk | 310-3 | 310 Tee1 | 569 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Brendale Bulk | 333-1 | Brendale BS | Lawnton | NCC Rating (A) | 826 | 826 | 826 | 826 | 826 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 204 | 202 | 215 | 215 | 214
|  |  |  | Power Factor | 0.974 | 0.975 | 0.975 | 0.975 | 0.975
|  |  |  | ECC Rating (A) | 846 | 846 | 846 | 846 | 846
|  |  |  | 50 POE Load (A) | 389 | 385 | 411 | 410 | 410
Brendale Bulk | 3340-1 | Brendale Bs | Strathpine | NCC Rating (A) | 561 | 561 | 561 | 561 | 561 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 100 | 101 | 97 | 93 | 92
|  |  |  | Power Factor | 0.983 | 0.982 | 0.984 | 0.987 | 0.988
|  |  |  | ECC Rating (A) | 561 | 561 | 561 | 561 | 561
|  |  |  | 50 POE Load (A) | 166 | 168 | 161 | 156 | 153
Brendale Bulk | 334-1 | Lawnton | 334 Tee1 | NCC Rating (A) | 645 | 645 | 645 | 645 | 645 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 55 | 53 | 49 | 48 | 48
|  |  |  | Power Factor | 0.781 | 0.779 | 0.748 | 0.745 | 0.742
|  |  |  | ECC Rating (A) | 865 | 865 | 865 | 865 | 865
|  |  |  | 50 POE Load (A) | 275 | 272 | 270 | 268 | 267
Brendale Bulk | 334-2 | 334 Tee1 | Whiteside | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 64 | 63 | 62 | 62 | 61
|  |  |  | Power Factor | 0.947 | 0.947 | 0.947 | 0.947 | 0.947
|  |  |  | ECC Rating (A) | 949 | 949 | 949 | 949 | 949
|  |  |  | 50 POE Load (A) | 157 | 155 | 154 | 153 | 152
Brendale Bulk | 334-3 | 334 Tee1 | Nth Pine Dam | NCC Rating (A) | 645 | 645 | 645 | 645 | 645 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 36 | 36 | 41 | 41 | 41
|  |  |  | Power Factor | 0.976 | 0.977 | 0.987 | 0.987 | 0.988
|  |  |  | ECC Rating (A) | 865 | 865 | 865 | 865 | 865
|  |  |  | 50 POE Load (A) | 134 | 133 | 147 | 147 | 147
Brendale Bulk | 335-1 | Brendale BS | 335 Tee1 | NCC Rating (A) | 531 | 531 | 531 | 531 | 531 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 151 | 150 | 155 | 154 | 154
|  |  |  | Power Factor | 0.956 | 0.957 | 0.957 | 0.957 | 0.958
|  |  |  | ECC Rating (A) | 531 | 531 | 531 | 531 | 531
|  |  |  | 50 POE Load (A) | 225 | 223 | 233 | 233 | 232
Brendale Bulk | 335-2 | 335 Tee | Whiteside | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 70 | 69 | 69 | 68 | 67
|  |  |  | Power Factor | 0.955 | 0.955 | 0.956 | 0.956 | 0.956
|  |  |  | ECC Rating (A) | 949 | 949 | 949 | 949 | 949
|  |  |  | 50 POE Load (A) | 157 | 154 | 153 | 152 | 151
Brendale Bulk | 335-3 | 335 Tee | Nth Pine Dam | NCC Rating (A) | 531 | 531 | 531 | 531 | 531 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 83 | 82 | 87 | 87 | 87
|  |  |  | Power Factor | 0.963 | 0.964 | 0.965 | 0.965 | 0.965
|  |  |  | ECC Rating (A) | 531 | 531 | 531 | 531 | 531
|  |  |  | 50 POE Load (A) | 151 | 150 | 160 | 160 | 160
Brendale Bulk | 336-1 | Brendale BS | Strathpine | NCC Rating (A) | 515 | 515 | 515 | 515 | 515 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 114 | 115 | 111 | 107 | 105
|  |  |  | Power Factor | 0.995 | 0.995 | 0.996 | 0.997 | 0.998
|  |  |  | ECC Rating (A) | 515 | 515 | 515 | 515 | 515
|  |  |  | 50 POE Load (A) | 182 | 185 | 177 | 171 | 168
Brendale Bulk | 3364-1 | Brendale BS | Albany Ck | NCC Rating (A) | 788 | 788 | 788 | 788 | 788 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 165 | 163 | 162 | 160 | 159
|  |  |  | Power Factor | 0.995 | 0.995 | 0.995 | 0.996 | 0.996
|  |  |  | ECC Rating (A) | 902 | 902 | 902 | 902 | 902
|  |  |  | 50 POE Load (A) | 332 | 327 | 325 | 323 | 320
Brendale Bulk | 337-1 | Brendale BS | Strathpine | NCC Rating (A) | 537 | 537 | 537 | 537 | 537 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 94 | 95 | 91 | 88 | 87
|  |  |  | Power Factor | 0.992 | 0.992 | 0.993 | 0.995 | 0.996
|  |  |  | ECC Rating (A) | 537 | 537 | 537 | 537 | 537
|  |  |  | 50 POE Load (A) | 157 | 159 | 153 | 147 | 145
Brendale Bulk | 342-1 | Brendale BS | Bald Hills Bus 2 | NCC Rating (A) | 654 | 654 | 654 | 654 | 654 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 108 | 106 | 105 | 105 | 104
|  |  |  | Power Factor | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 280 | 276 | 274 | 272 | 270
Brendale Bulk | 349-1 | Brendale BS | Lawnton | NCC Rating (A) | 805 | 805 | 805 | 805 | 805 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 212 | 210 | 223 | 223 | 223
|  |  |  | Power Factor | 0.972 | 0.972 | 0.973 | 0.973 | 0.973
|  |  |  | ECC Rating (A) | 822 | 822 | 822 | 822 | 822
|  |  |  | 50 POE Load (A) | 390 | 386 | 412 | 411 | 411
Brendale Bulk | 464-1 | Brendale BS | Samford | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 144 | 142 | 141 | 140 | 139
|  |  |  | Power Factor | 0.995 | 0.995 | 0.995 | 0.996 | 0.996
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 322 | 317 | 315 | 313 | 310
Browns Plains Bulk | 406A-1 | Bethania | Kingston | NCC Rating (A) | 647 | 647 | 647 | 647 | 647 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 775 | 775 | 775 | 775 | 775
|  |  |  | 50 POE Load (A) | 353 | 351 | 352 | 351 | 352
Browns Plains Bulk | 406B-1 | Crestmead | Kingston | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 830 | 830 | 830 | 830 | 830
|  |  |  | 50 POE Load (A) | 256 | 255 | 255 | 255 | 255
Browns Plains Bulk | 478-1 | Browns Plains BS | Nth Maclean | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 356 | 362 | 361 | 368 | 374
Browns Plains Bulk | 481-1 | Browns Plains BS | Cresmead | NCC Rating (A) | 741 | 741 | 741 | 741 | 741 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 191 | 223 | 222 | 220 | 219
|  |  |  | Power Factor | 0.98 | 0.977 | 0.977 | 0.977 | 0.977
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 384 | 453 | 450 | 447 | 445
Browns Plains Bulk | 482-1 | Browns Plains BS | Cresmead | NCC Rating (A) | 741 | 741 | 741 | 741 | 741 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 192 | 224 | 223 | 221 | 221
|  |  |  | Power Factor | 0.98 | 0.977 | 0.977 | 0.977 | 0.977
|  |  |  | ECC Rating (A) | 775 | 775 | 775 | 775 | 775
|  |  |  | 50 POE Load (A) | 402 | 475 | 471 | 468 | 466
Browns Plains Bulk | 542-1 | Browns Plains BS | Heathwood | NCC Rating (A) | 745 | 745 | 745 | 745 | 745 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 354 | 351 | 349 | 347 | 346
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | ECC Rating (A) | 745 | 745 | 745 | 745 | 745
|  |  |  | 50 POE Load (A) | 366 | 363 | 361 | 359 | 358
Burleigh Heads Bulk | 3751-1 | Burleigh Hds BS | Currumbin | NCC Rating (A) | 606 | 606 | 606 | 606 | 606 | Urban | 321 | NA
|  |  |  | 10 POE Load (A) | 529 | 531 | 531 | 531 | 531
|  |  |  | Power Factor | 0.963 | 0.964 | 0.964 | 0.964 | 0.963
|  |  |  | ECC Rating (A) | 695 | 695 | 695 | 695 | 695
|  |  |  | 50 POE Load (A) | 866 | 858 | 857 | 857 | 857
Burleigh Heads Bulk | 3755-1 | Burleigh Hds BS | Currumbin | NCC Rating (A) | 606 | 606 | 606 | 606 | 606 | Urban | 321 | NA
|  |  |  | 10 POE Load (A) | 529 | 531 | 531 | 530 | 531
|  |  |  | Power Factor | 0.963 | 0.964 | 0.964 | 0.964 | 0.963
|  |  |  | ECC Rating (A) | 695 | 695 | 695 | 695 | 695
|  |  |  | 50 POE Load (A) | 866 | 858 | 857 | 856 | 857
Burleigh Heads Bulk | 3756-1 | Burleigh Hds BS | 3756 Tee1 | NCC Rating (A) | 715 | 715 | 715 | 715 | 715 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 167 | 167 | 167 | 167 | 167
|  |  |  | Power Factor | 0.976 | 0.976 | 0.976 | 0.976 | 0.975
|  |  |  | ECC Rating (A) | 715 | 715 | 715 | 715 | 715
|  |  |  | 50 POE Load (A) | 254 | 251 | 251 | 251 | 251
Burleigh Heads Bulk | 3756-2 | 3756 Tee1 | Palm Beach | NCC Rating (A) | 614 | 614 | 614 | 614 | 614 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 140 | 141 | 140 | 140 | 139
|  |  |  | Power Factor | 0.981 | 0.982 | 0.982 | 0.983 | 0.978
|  |  |  | ECC Rating (A) | 614 | 614 | 614 | 614 | 614
|  |  |  | 50 POE Load (A) | 370 | 366 | 366 | 365 | 365
Burleigh Heads Bulk | 3756-3 | 3756 Tee1 | 3756 Tee2 | NCC Rating (A) | 636 | 636 | 636 | 636 | 636 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 46 | 46 | 46 | 46 | 46
|  |  |  | Power Factor | 0.98 | 0.978 | 0.977 | 0.977 | 0.986
|  |  |  | ECC Rating (A) | 636 | 636 | 636 | 636 | 636
|  |  |  | 50 POE Load (A) | 218 | 226 | 226 | 226 | 227
Burleigh Heads Bulk | 3756-4 | 3756 Tee2 | Currumbin | NCC Rating (A) | 790 | 790 | 790 | 790 | 790 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 46 | 46 | 46 | 46 | 47
|  |  |  | Power Factor | 0.979 | 0.976 | 0.976 | 0.976 | 0.985
|  |  |  | ECC Rating (A) | 790 | 790 | 790 | 790 | 790
|  |  |  | 50 POE Load (A) | 241 | 249 | 249 | 249 | 250
Burleigh Heads Bulk | 393-1 | Currumbin | Kirra | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 234 | 236 | 236 | 237 | 239
|  |  |  | Power Factor | 0.975 | 0.975 | 0.975 | 0.975 | 0.974
|  |  |  | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
|  |  |  | 50 POE Load (A) | 336 | 334 | 334 | 336 | 338
Burleigh Heads Bulk | 395-1 | Burleigh Hds BS | Miami | NCC Rating (A) | 747 | 747 | 747 | 747 | 747 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 387 | 390 | 391 | 393 | 394
|  |  |  | Power Factor | 0.989 | 0.989 | 0.989 | 0.989 | 0.989
|  |  |  | ECC Rating (A) | 747 | 747 | 747 | 747 | 747
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Burleigh Heads Bulk | 396-1 | Burleigh Hds BS | Palm Beach | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 190 | 191 | 191 | 191 | 191
|  |  |  | Power Factor | 0.974 | 0.974 | 0.974 | 0.974 | 0.973
|  |  |  | ECC Rating (A) | 806 | 806 | 806 | 806 | 806
|  |  |  | 50 POE Load (A) | 322 | 319 | 318 | 318 | 318
Burleigh Heads Bulk | 397-1 | Burleigh Hds BS | 397 Tee1 | NCC Rating (A) | 659 | 659 | 659 | 659 | 659 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 659 | 659 | 659 | 659 | 659
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Burleigh Heads Bulk | 397-3 | 397 Tee1 | 397 Tee2 | NCC Rating (A) | 706 | 706 | 706 | 706 | 706 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 706 | 706 | 706 | 706 | 706
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Burleigh Heads Bulk | 397-4 | 397 Tee2 | 3700 Tee1 | NCC Rating (A) | 362 | 362 | 362 | 362 | 362 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 362 | 362 | 362 | 362 | 362
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Burleigh Heads Bulk | 397-5 | 397 Tee2 | Mudgeeraba BS | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Caboolture Bulk | 321-1 | Caboolture BS | Caboolture West | NCC Rating (A) | 688 | 688 | 688 | 688 | 688 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 192 | 191 | 192 | 192 | 192
|  |  |  | Power Factor | 0.991 | 0.991 | 0.991 | 0.991 | 0.991
|  |  |  | ECC Rating (A) | 688 | 688 | 688 | 688 | 688
|  |  |  | 50 POE Load (A) | 383 | 382 | 383 | 383 | 384
Caboolture Bulk | 322-1 | Caboolture BS | Caboolture West | NCC Rating (A) | 688 | 688 | 688 | 688 | 688 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 199 | 198 | 199 | 199 | 200
|  |  |  | Power Factor | 0.985 | 0.985 | 0.985 | 0.985 | 0.985
|  |  |  | ECC Rating (A) | 688 | 688 | 688 | 688 | 688
|  |  |  | 50 POE Load (A) | 389 | 388 | 390 | 390 | 390
Caboolture Bulk | 323-1 | Caboolture West | 323 Tee1 | NCC Rating (A) | 348 | 582 | 582 | 582 | 582 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 62 | 61 | 61 | 61 | 60
|  |  |  | Power Factor | 0.996 | 0.997 | 0.997 | 0.997 | 0.997
|  |  |  | ECC Rating (A) | 348 | 584 | 584 | 584 | 584
|  |  |  | 50 POE Load (A) | 292 | 228 | 227 | 225 | 224
Caboolture Bulk | 323-2 | 323 Tee1 | Wamuran | NCC Rating (A) | 489 | 489 | 489 | 489 | 489 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 63 | 61 | 61 | 61 | 61
|  |  |  | Power Factor | 0.994 | 0.994 | 0.994 | 0.994 | 0.994
|  |  |  | ECC Rating (A) | 489 | 489 | 489 | 489 | 489
|  |  |  | 50 POE Load (A) | 66 | 64 | 64 | 63 | 63
Caboolture Bulk | 323-3 | 323 Tee1 | Woodford | NCC Rating (A) | 348 | 382 | 382 | 382 | 382 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 348 | 382 | 382 | 382 | 382
|  |  |  | 50 POE Load (A) | 206 | 196 | 196 | 194 | 194
Caboolture Bulk | 350-1 | Caboolture BS | Ningi | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 316 | 322 | 321 | 321 | 320
|  |  |  | Power Factor | 0.991 | 0.99 | 0.99 | 0.991 | 0.991
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 569 | 584 | 582 | 582 | 580
Caboolture Bulk | 412-1 | Caboolture BS | Toorbul Pt | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 252 | 259 | 258 | 258 | 257
|  |  |  | Power Factor | 0.983 | 0.982 | 0.982 | 0.982 | 0.982
|  |  |  | ECC Rating (A) | 1018 | 1018 | 1018 | 1018 | 1018
|  |  |  | 50 POE Load (A) | 724 | 730 | 727 | 726 | 724
Caboolture Bulk | 417-1 | Ningi | Toorbul Pt | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 188 | 196 | 196 | 196 | 195
|  |  |  | Power Factor | 0.998 | 0.998 | 0.998 | 0.998 | 0.998
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 443 | 460 | 459 | 459 | 457
Caboolture Bulk | 431-1 | Toorbul Point | Bribie Is | NCC Rating (A) | 419 | 419 | 419 | 419 | 419 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 164 | 162 | 162 | 162 | 161
|  |  |  | Power Factor | 0.994 | 0.994 | 0.994 | 0.994 | 0.994
|  |  |  | ECC Rating (A) | 470 | 470 | 470 | 470 | 470
|  |  |  | 50 POE Load (A) | 327 | 325 | 324 | 324 | 323
Caboolture Bulk | 448-1 | Morayfield Nth | 448 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 370 | 375 | 384 | 387 | 389
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | ECC Rating (A) | 822 | 822 | 822 | 822 | 822
|  |  |  | 50 POE Load (A) | 464 | 470 | 479 | 482 | 485
Caboolture Bulk | 448-2 | 448 Tee1 | Morayfield | NCC Rating (A) | 737 | 737 | 737 | 737 | 737 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 348 | 356 | 366 | 369 | 373
|  |  |  | Power Factor | 0.994 | 0.994 | 0.993 | 0.993 | 0.993
|  |  |  | ECC Rating (A) | 737 | 737 | 737 | 737 | 737
|  |  |  | 50 POE Load (A) | 352 | 360 | 371 | 374 | 378
Caboolture Bulk | 448-3 | 448 Tee1 | Caboolture West | NCC Rating (A) | 504 | 504 | 504 | 504 | 504 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 25 | 23 | 21 | 21 | 20
|  |  |  | Power Factor | 0.922 | 0.917 | 0.912 | 0.909 | 0.905
|  |  |  | ECC Rating (A) | 504 | 504 | 504 | 504 | 504
|  |  |  | 50 POE Load (A) | 111 | 109 | 107 | 106 | 106
Caboolture Bulk | 457-1 | Toorbul Pt | Bribie Island | NCC Rating (A) | 425 | 425 | 425 | 425 | 425 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 163 | 161 | 161 | 161 | 161
|  |  |  | Power Factor | 0.996 | 0.996 | 0.996 | 0.996 | 0.996
|  |  |  | ECC Rating (A) | 618 | 618 | 618 | 618 | 618
|  |  |  | 50 POE Load (A) | 327 | 325 | 324 | 323 | 323
Caboolture Bulk | 461-1 | Caboolture BS | Morayfield Nth | NCC Rating (A) | 762 | 762 | 762 | 762 | 762 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 355 | 357 | 361 | 362 | 364
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | ECC Rating (A) | 797 | 797 | 797 | 797 | 797
|  |  |  | 50 POE Load (A) | 691 | 695 | 703 | 705 | 709
Caboolture Bulk | 499-1 | Caboolture BS | Morayfield Nth | NCC Rating (A) | 762 | 762 | 762 | 762 | 762 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 358 | 359 | 363 | 364 | 366
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | ECC Rating (A) | 797 | 797 | 797 | 797 | 797
|  |  |  | 50 POE Load (A) | 692 | 696 | 704 | 706 | 710
Cleveland Bulk | 3550-1 | Cleveland BS | Victoria Pt | NCC Rating (A) | 775 | 775 | 775 | 775 | 775 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 382 | 379 | 379 | 379 | 379
|  |  |  | Power Factor | 0.989 | 0.989 | 0.989 | 0.989 | 0.989
|  |  |  | ECC Rating (A) | 775 | 775 | 775 | 775 | 775
|  |  |  | 50 POE Load (A) | 526 | 522 | 521 | 521 | 521
Cleveland Bulk | 3570-1 | Capalaba South | Capalaba | NCC Rating (A) | 649 | 649 | 649 | 649 | 649 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 57 | 57 | 57 | 57 | 57
|  |  |  | Power Factor | 0.971 | 0.971 | 0.972 | 0.973 | 0.973
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 325 | 319 | 315 | 313 | 310
Cleveland Bulk | 3580-1 | Redland Bay | 3580 Tee1 | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 27 | 28 | 28 | 29 | 29
|  |  |  | Power Factor | 0.998 | 0.998 | 0.998 | 0.999 | 0.999
|  |  |  | ECC Rating (A) | 926 | 926 | 926 | 926 | 926
|  |  |  | 50 POE Load (A) | 313 | 313 | 314 | 315 | 317
Cleveland Bulk | 3580-2 | 3580 Tee1 | Mt Cotton | NCC Rating (A) | 715 | 715 | 715 | 715 | 715 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 27 | 28 | 28 | 29 | 29
|  |  |  | Power Factor | 0.996 | 0.996 | 0.996 | 0.997 | 0.997
|  |  |  | ECC Rating (A) | 715 | 715 | 715 | 715 | 715
|  |  |  | 50 POE Load (A) | 329 | 328 | 330 | 331 | 333
Cleveland Bulk | 3580-3 | 3580 Tee1 | Cornubia | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Cleveland Bulk | 371-1 | Cleveland BS | Birkdale | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 325 | 320 | 317 | 315 | 313
|  |  |  | Power Factor | 0.987 | 0.987 | 0.987 | 0.987 | 0.987
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 420 | 413 | 410 | 407 | 404
Cleveland Bulk | 372-1 | Cleveland BS | Raby Bay | NCC Rating (A) | 648 | 648 | 648 | 648 | 648 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 296 | 293 | 293 | 293 | 293
|  |  |  | Power Factor | 0.993 | 0.993 | 0.993 | 0.993 | 0.993
|  |  |  | ECC Rating (A) | 726 | 726 | 726 | 726 | 726
|  |  |  | 50 POE Load (A) | 581 | 576 | 575 | 575 | 575
Cleveland Bulk | 373-1 | Raby Bay | Capalaba | NCC Rating (A) | 715 | 715 | 715 | 715 | 715 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 242 | 238 | 236 | 234 | 232
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | ECC Rating (A) | 715 | 715 | 715 | 715 | 715
|  |  |  | 50 POE Load (A) | 399 | 393 | 389 | 386 | 383
Cleveland Bulk | 374-1 | Cleveland BS | Capalaba South | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 283 | 278 | 275 | 274 | 272
|  |  |  | Power Factor | 0.984 | 0.984 | 0.984 | 0.984 | 0.984
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 429 | 422 | 418 | 415 | 413
Cleveland Bulk | 375-1 | Cleveland BS | 375 Tee1 | NCC Rating (A) | 649 | 649 | 649 | 649 | 649 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 151 | 150 | 150 | 150 | 150
|  |  |  | Power Factor | 0.992 | 0.992 | 0.992 | 0.992 | 0.992
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 543 | 539 | 539 | 540 | 541
Cleveland Bulk | 375-2 | 375 Tee1 | Mt Cotton | NCC Rating (A) | 678 | 678 | 678 | 678 | 678 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 152 | 150 | 150 | 150 | 150
|  |  |  | Power Factor | 0.993 | 0.993 | 0.993 | 0.993 | 0.993
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 543 | 539 | 539 | 540 | 541
Cleveland Bulk | 375-3 | 375 Tee1 | 425 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Cleveland Bulk | 413-1 | Cleveland BS | Raby Bay | NCC Rating (A) | 648 | 648 | 648 | 648 | 648 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 300 | 297 | 296 | 296 | 296
|  |  |  | Power Factor | 0.993 | 0.993 | 0.993 | 0.993 | 0.993
|  |  |  | ECC Rating (A) | 726 | 726 | 726 | 726 | 726
|  |  |  | 50 POE Load (A) | 582 | 576 | 576 | 576 | 576
Cleveland Bulk | 425-1 | Cleveland BS | Victoria Pt | NCC Rating (A) | 705 | 705 | 705 | 705 | 705 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 169 | 168 | 168 | 168 | 168
|  |  |  | Power Factor | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 667 | 662 | 662 | 662 | 662
Cleveland Bulk | 465-1 | Victoria Pt | Redland Bay | NCC Rating (A) | 562 | 562 | 562 | 562 | 562 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 224 | 223 | 223 | 224 | 225
|  |  |  | Power Factor | 0.379 | 0.379 | 0.966 | 0.966 | 0.966
|  |  |  | ECC Rating (A) | 562 | 562 | 562 | 562 | 562
|  |  |  | 50 POE Load (A) | 397 | 394 | 394 | 395 | 395
Cleveland Bulk | 484-1 | Capalaba | Birkdale | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 98 | 97 | 97 | 96 | 95
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 609 | 600 | 596 | 592 | 588
Coomera Bulk | 3640-1 | Coomera BS | Hope Is | NCC Rating (A) | 759 | 759 | 759 | 759 | 759 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 203 | 203 | 205 | 206 | 207
|  |  |  | Power Factor | 0.995 | 0.995 | 0.995 | 0.995 | 0.994
|  |  |  | ECC Rating (A) | 921 | 921 | 921 | 921 | 921
|  |  |  | 50 POE Load (A) | 501 | 501 | 505 | 508 | 511
Coomera Bulk | 3641-1 | Coomera BS | Pimpama East | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 208 | 215 | 223 | 231 | 239
|  |  |  | Power Factor | 0.987 | 0.987 | 0.986 | 0.986 | 0.985
|  |  |  | ECC Rating (A) | 921 | 921 | 921 | 921 | 921
|  |  |  | 50 POE Load (A) | 520 | 537 | 557 | 578 | 598
Coomera Bulk | 3642-1 | Coomera BS | Pimpama East | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 210 | 216 | 225 | 233 | 241
|  |  |  | Power Factor | 0.987 | 0.987 | 0.986 | 0.986 | 0.985
|  |  |  | ECC Rating (A) | 921 | 921 | 921 | 921 | 921
|  |  |  | 50 POE Load (A) | 520 | 536 | 557 | 577 | 598
Coomera Bulk | 394-1 | Coomera BS | Hope Is | NCC Rating (A) | 759 | 759 | 759 | 759 | 759 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 208 | 208 | 210 | 211 | 212
|  |  |  | Power Factor | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
|  |  |  | ECC Rating (A) | 759 | 759 | 759 | 759 | 759
|  |  |  | 50 POE Load (A) | 412 | 413 | 416 | 418 | 421
Coorparoo Bulk | 3429-1 | Coorparoo BS | Holland Park | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 152 | 154 | 153 | 153 | 153
|  |  |  | Power Factor | 0.996 | 0.996 | 0.996 | 0.996 | 0.996
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 309 | 310 | 309 | 309 | 308
Coorparoo Bulk | 3430-1 | Coorparoo BS | Holland Park | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 155 | 151 | 150 | 150 | 150
|  |  |  | Power Factor | 0.996 | 0.996 | 0.996 | 0.996 | 0.996
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 309 | 310 | 309 | 309 | 309
Coorparoo Bulk | 584-4 | 584 Tee2 | Coorparoo BS | NCC Rating (A) | 764 | 764 | 764 | 764 | 764 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 764 | 764 | 764 | 764 | 764
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Coorparoo Bulk | 612-1 | Coorparoo BS | Camp Hill | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 224 | 221 | 220 | 219 | 218
|  |  |  | Power Factor | 0.993 | 0.994 | 0.994 | 0.994 | 0.994
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 434 | 429 | 427 | 425 | 423
Coorparoo Bulk | 613-1 | Coorparoo BS | Camp Hill | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 224 | 221 | 220 | 219 | 218
|  |  |  | Power Factor | 0.993 | 0.994 | 0.994 | 0.994 | 0.994
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 434 | 429 | 427 | 425 | 423
Coorparoo Bulk | 648-1 | Scrub Rd | 648 Tee1 | NCC Rating (A) | 654 | 654 | 654 | 654 | 654 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 654 | 654 | 654 | 654 | 654
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Coorparoo Bulk | 648-2 | 648 Tee1 | 584 Tee1 | NCC Rating (A) | 348 | 348 | 348 | 348 | 348 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 348 | 348 | 348 | 348 | 348
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Coorparoo Bulk | 648-3 | 648 Tee1 | Camp Hill | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Doboy Bulk | 3426-1 | Queensport | Bulimba | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 187 | 184 | 184 | 216 | 250
|  |  |  | Power Factor | 0.993 | 0.993 | 0.993 | 0.992 | 0.99
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 289 | 285 | 284 | 310 | 340
Doboy Bulk | 414-1 | Doboy BS | Tingalpa | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 122 | 121 | 121 | 120 | 119
|  |  |  | Power Factor | 0.991 | 0.991 | 0.991 | 0.991 | 0.991
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | 50 POE Load (A) | 274 | 270 | 269 | 267 | 266
Doboy Bulk | 416-1 | Doboy BS | Murarrie | NCC Rating (A) | 397 | 397 | 397 | 397 | 397 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 157 | 164 | 162 | 160 | 160
|  |  |  | Power Factor | 0.961 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | ECC Rating (A) | 528 | 528 | 528 | 528 | 528
|  |  |  | 50 POE Load (A) | 343 | 359 | 354 | 351 | 350
Doboy Bulk | 443-1 | Queensport | Bulimba | NCC Rating (A) | 652 | 652 | 652 | 652 | 652 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 132 | 130 | 130 | 153 | 177
|  |  |  | Power Factor | 0.997 | 0.997 | 0.997 | 0.996 | 0.994
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 428 | 423 | 421 | 460 | 505
Doboy Bulk | 558-1 | Hemmant | Tingalpa | NCC Rating (A) | 680 | 680 | 680 | 680 | 680 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 162 | 159 | 157 | 157 | 156
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.991
|  |  |  | ECC Rating (A) | 680 | 680 | 680 | 680 | 680
|  |  |  | 50 POE Load (A) | 273 | 269 | 267 | 266 | 265
Doboy Bulk | 563-1 | Doboy BS | Hemmant | NCC Rating (A) | 389 | 389 | 389 | 389 | 389 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 140 | 142 | 152 | 151 | 150
|  |  |  | Power Factor | 0.987 | 0.987 | 0.986 | 0.986 | 0.987
|  |  |  | ECC Rating (A) | 452 | 452 | 452 | 452 | 452
|  |  |  | 50 POE Load (A) | 267 | 272 | 293 | 290 | 289
Doboy Bulk | 564-1 | Doboy BS | Hemmant | NCC Rating (A) | 389 | 389 | 389 | 389 | 389 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 134 | 136 | 146 | 145 | 144
|  |  |  | Power Factor | 0.984 | 0.984 | 0.983 | 0.983 | 0.984
|  |  |  | ECC Rating (A) | 452 | 452 | 452 | 452 | 452
|  |  |  | 50 POE Load (A) | 266 | 271 | 292 | 289 | 288
Doboy Bulk | 575C-1 | Doboy BS | Murarrie | NCC Rating (A) | 397 | 397 | 397 | 397 | 397 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 149 | 156 | 154 | 152 | 152
|  |  |  | Power Factor | 0.958 | 0.958 | 0.958 | 0.958 | 0.958
|  |  |  | ECC Rating (A) | 532 | 532 | 532 | 532 | 532
|  |  |  | 50 POE Load (A) | 344 | 360 | 355 | 351 | 350
Doboy Bulk | 581-1 | Doboy BS | Queensport | NCC Rating (A) | 699 | 699 | 699 | 699 | 699 | Urban | 166 | 3.5
|  |  |  | 10 POE Load (A) | 371 | 366 | 364 | 390 | 416
|  |  |  | Power Factor | 0.976 | 0.976 | 0.976 | 0.976 | 0.976
|  |  |  | ECC Rating (A) | 828 | 828 | 828 | 828 | 828
|  |  |  | 50 POE Load (A) | 712 | 703 | 698 | 751 | 805
Doboy Bulk | 645-1 | Doboy BS | Gibson Island | NCC Rating (A) | 468 | 468 | 468 | 468 | 468 | HighSec | 0 | NA
|  |  |  | 10 POE Load (A) | 5 | 5 | 5 | 5 | 5
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 468 | 468 | 468 | 468 | 468
|  |  |  | 50 POE Load (A) | 161 | 159 | 158 | 169 | 169
Doboy Bulk | 677-1 | Doboy BS | Queensport | NCC Rating (A) | 699 | 699 | 699 | 699 | 699 | Urban | 166 | 1.5
|  |  |  | 10 POE Load (A) | 370 | 365 | 363 | 389 | 415
|  |  |  | Power Factor | 0.976 | 0.976 | 0.976 | 0.976 | 0.976
|  |  |  | ECC Rating (A) | 828 | 828 | 828 | 828 | 828
|  |  |  | 50 POE Load (A) | 712 | 703 | 698 | 751 | 805
Gatton Bulk | 377-1 | Gatton BS | 377 Tee1 | NCC Rating (A) | 891 | 891 | 891 | 891 | 891 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 209 | 214 | 219 | 218 | 217
|  |  |  | Power Factor | 0.969 | 0.969 | 0.968 | 0.968 | 0.968
|  |  |  | ECC Rating (A) | 1041 | 1041 | 1041 | 1041 | 1041
|  |  |  | 50 POE Load (A) | 371 | 381 | 393 | 390 | 389
Gatton Bulk | 377-2 | 377 Tee1 | 487 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Gatton Bulk | 377-3 | 377 Tee1 | 377 Tee2 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 209 | 214 | 219 | 218 | 217
|  |  |  | Power Factor | 0.969 | 0.969 | 0.968 | 0.968 | 0.968
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 342 | 351 | 362 | 360 | 359
Gatton Bulk | 377-4 | 377 Tee2 | Gatton | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 210 | 214 | 220 | 218 | 217
|  |  |  | Power Factor | 0.972 | 0.971 | 0.971 | 0.971 | 0.971
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 506 | 519 | 536 | 532 | 531
Gatton Bulk | 377-5 | 377 Tee2 | Glenmore Grove | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Gatton Bulk | 3859-1 | Gatton BS | Springfield Central | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 27 | 26 | 26 | 26 | 26
|  |  |  | Power Factor | 0.909 | 0.909 | 0.909 | 0.909 | 0.909
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 55 | 54 | 54 | 53 | 53
Gatton Bulk | 3860-1 | Gatton BS | Springfield Central | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 27 | 26 | 26 | 26 | 26
|  |  |  | Power Factor | 0.909 | 0.909 | 0.909 | 0.909 | 0.909
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 55 | 54 | 54 | 53 | 53
Gatton Bulk | 487-1 | Gatton BS | 487 Tee1 | NCC Rating (A) | 891 | 891 | 891 | 891 | 891 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 207 | 210 | 215 | 213 | 212
|  |  |  | Power Factor | 0.972 | 0.971 | 0.971 | 0.971 | 0.971
|  |  |  | ECC Rating (A) | 891 | 891 | 891 | 891 | 891
|  |  |  | 50 POE Load (A) | 448 | 457 | 468 | 465 | 463
Gatton Bulk | 487-2 | 487 Tee1 | 377 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Gatton Bulk | 487-3 | 487 Tee1 | 487 Tee2 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 208 | 211 | 215 | 214 | 213
|  |  |  | Power Factor | 0.971 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 413 | 422 | 432 | 429 | 428
Gatton Bulk | 487-6 | 487 Tee3 | 3844 Tee1 | NCC Rating (A) | 348 | 348 | 348 | 348 | 348 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 348 | 348 | 348 | 348 | 348
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Gatton Bulk | 487-8 | 487 Tee4 | 3844 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Gatton Bulk | 487-9 | 487 Tee2 | Gatton | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 140 | 145 | 150 | 149 | 149
|  |  |  | Power Factor | 0.975 | 0.974 | 0.973 | 0.974 | 0.974
|  |  |  | ECC Rating (A) | 921 | 921 | 921 | 921 | 921
|  |  |  | 50 POE Load (A) | 447 | 460 | 474 | 471 | 470
Gatton Bulk | 531-1 | Gatton | Tenthill | NCC Rating (A) | 293 | 293 | 293 | 432 | 432 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 78 | 78 | 78 | 77 | 77
|  |  |  | Power Factor | 0.978 | 0.978 | 0.978 | 0.978 | 0.978
|  |  |  | ECC Rating (A) | 293 | 293 | 293 | 432 | 432
|  |  |  | 50 POE Load (A) | 141 | 141 | 141 | 160 | 160
Gatton Bulk | 532-1 | Tenthill | 532 Tee1 | NCC Rating (A) | 416 | 416 | 416 | 416 | 416 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 416 | 416 | 416 | 416 | 416
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Gatton Bulk | 533-1 | Tenthill | Mt Sylvia | NCC Rating (A) | 144 | 144 | 144 | 144 | 144 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 20 | 20 | 20 | 19 | 19
|  |  |  | Power Factor | 0.901 | 0.901 | 0.901 | 0.9 | 0.9
|  |  |  | ECC Rating (A) | 144 | 144 | 144 | 144 | 144
|  |  |  | 50 POE Load (A) | 36 | 35 | 35 | 34 | 34
Goodna Bulk | 3800-1 | Goodna BS | Cooneana | NCC Rating (A) | 695 | 695 | 695 | 695 | 695 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 49 | 57 | 64 | 71 | 77
|  |  |  | Power Factor | 0.994 | 0.993 | 0.996 | 0.995 | 0.995
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 147 | 167 | 188 | 209 | 229
Goodna Bulk | 3801-1 | Goodna BS | Carol Pk Central | NCC Rating (A) | 793 | 793 | 793 | 793 | 793 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 225 | 234 | 232 | 231 | 231
|  |  |  | Power Factor | 0.99 | 0.989 | 0.989 | 0.989 | 0.989
|  |  |  | ECC Rating (A) | 827 | 827 | 827 | 827 | 827
|  |  |  | 50 POE Load (A) | 449 | 446 | 442 | 442 | 442
Goodna Bulk | 3802-1 | Goodna BS | Springfield | NCC Rating (A) | 627 | 627 | 627 | 627 | 627 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 230 | 237 | 240 | 244 | 248
|  |  |  | Power Factor | 0.989 | 0.989 | 0.988 | 0.988 | 0.988
|  |  |  | ECC Rating (A) | 714 | 714 | 714 | 714 | 714
|  |  |  | 50 POE Load (A) | 455 | 466 | 473 | 480 | 488
Goodna Bulk | 3803-1 | Goodna BS | Carol Park | NCC Rating (A) | 550 | 550 | 550 | 550 | 550 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 185 | 190 | 191 | 192 | 194
|  |  |  | Power Factor | 0.974 | 0.971 | 0.971 | 0.971 | 0.971
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 404 | 409 | 411 | 414 | 418
Goodna Bulk | 3805-1 | Goodna BS | Carol Park | NCC Rating (A) | 550 | 550 | 550 | 550 | 550 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 169 | 173 | 174 | 176 | 177
|  |  |  | Power Factor | 0.971 | 0.968 | 0.968 | 0.968 | 0.968
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 388 | 393 | 395 | 398 | 402
Goodna Bulk | 3806-1 | Goodna BS | Springfield | NCC Rating (A) | 627 | 627 | 627 | 627 | 627 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 229 | 236 | 239 | 243 | 247
|  |  |  | Power Factor | 0.989 | 0.989 | 0.988 | 0.988 | 0.988
|  |  |  | ECC Rating (A) | 714 | 714 | 714 | 714 | 714
|  |  |  | 50 POE Load (A) | 455 | 466 | 473 | 480 | 487
Goodna Bulk | 3807-1 | Goodna BS | Redbank | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 181 | 238 | 237 | 236 | 236
|  |  |  | Power Factor | 0.983 | 0.981 | 0.98 | 0.98 | 0.98
|  |  |  | ECC Rating (A) | 1250 | 1250 | 1250 | 1250 | 1250
|  |  |  | 50 POE Load (A) | 295 | 388 | 386 | 384 | 384
Goodna Bulk | 3808-1 | Goodna BS | Carol Pk Central | NCC Rating (A) | 751 | 751 | 751 | 751 | 751 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 225 | 234 | 232 | 232 | 232
|  |  |  | Power Factor | 0.99 | 0.989 | 0.989 | 0.989 | 0.989
|  |  |  | ECC Rating (A) | 803 | 803 | 803 | 803 | 803
|  |  |  | 50 POE Load (A) | 438 | 435 | 431 | 430 | 431
Goodna Bulk | 3809-1 | Goodna BS | Cooneana | NCC Rating (A) | 695 | 695 | 695 | 695 | 695 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 56 | 64 | 72 | 80 | 88
|  |  |  | Power Factor | 0.995 | 0.994 | 0.996 | 0.996 | 0.995
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 147 | 167 | 188 | 209 | 229
Goodna Bulk | 3880-1 | Carol Park | Springfield Central | NCC Rating (A) | 794 | 794 | 794 | 794 | 794 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 99 | 109 | 115 | 120 | 125
|  |  |  | Power Factor | 0.986 | 0.986 | 0.985 | 0.985 | 0.984
|  |  |  | ECC Rating (A) | 794 | 794 | 794 | 794 | 794
|  |  |  | 50 POE Load (A) | 220 | 242 | 254 | 264 | 275
Goodna Bulk | 3881-1 | Springfield | Springfield Central | NCC Rating (A) | 794 | 794 | 794 | 794 | 794 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 119 | 130 | 136 | 141 | 147
|  |  |  | Power Factor | 0.972 | 0.97 | 0.97 | 0.97 | 0.969
|  |  |  | ECC Rating (A) | 794 | 794 | 794 | 794 | 794
|  |  |  | 50 POE Load (A) | 218 | 240 | 251 | 261 | 272
Goodna Bulk | 456-1 | Wacol Sth | 456 Tee1 | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0.928 | 0.973 | 0.972 | 0.972 | 0.972
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Goodna Bulk | 456-2 | 456 Tee1 | Carol Pk Central | NCC Rating (A) | 493 | 493 | 493 | 493 | 493 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 70 | 69 | 70 | 72 | 73
|  |  |  | Power Factor | 0.928 | 0.973 | 0.972 | 0.972 | 0.972
|  |  |  | ECC Rating (A) | 493 | 493 | 493 | 493 | 493
|  |  |  | 50 POE Load (A) | 152 | 156 | 158 | 160 | 162
Goodna Bulk | 456-3 | 456 Tee1 | Carol Pk | NCC Rating (A) | 493 | 493 | 493 | 493 | 493 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 70 | 69 | 70 | 72 | 73
|  |  |  | Power Factor | 0.921 | 0.968 | 0.968 | 0.968 | 0.967
|  |  |  | ECC Rating (A) | 493 | 493 | 493 | 493 | 493
|  |  |  | 50 POE Load (A) | 152 | 156 | 158 | 160 | 162
Griffin Bulk | 312-1 | Kallangur | Narangba | NCC Rating (A) | 489 | 489 | 489 | 489 | 489 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 489 | 489 | 489 | 489 | 489
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Griffin Bulk | 320-1 | Griffin BS | 320 Tee1 | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70 | 0.5
|  |  |  | 10 POE Load (A) | 237 | 236 | 237 | 238 | 243
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1
|  |  |  | ECC Rating (A) | 912 | 912 | 912 | 912 | 912
|  |  |  | 50 POE Load (A) | 452 | 450 | 452 | 454 | 466
Griffin Bulk | 320-2 | 320 Tee1 | Mango Hill Bus 2 | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 70 | 0.5
|  |  |  | 10 POE Load (A) | 150 | 149 | 149 | 149 | 148
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | 50 POE Load (A) | 316 | 315 | 315 | 316 | 317
Griffin Bulk | 320-3 | 320 Tee1 | Kalangur | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 70 | 0.5
|  |  |  | 10 POE Load (A) | 88 | 88 | 89 | 90 | 95
|  |  |  | Power Factor | 0.993 | 0.993 | 0.993 | 0.993 | 0.993
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | 50 POE Load (A) | 241 | 241 | 243 | 244 | 255
Griffin Bulk | 3329-1 | Griffin BS | 3329 Tee1 | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 279 | 279 | 280 | 281 | 290
|  |  |  | Power Factor | 0.996 | 0.996 | 0.996 | 0.996 | 0.996
|  |  |  | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | 50 POE Load (A) | 351 | 350 | 351 | 353 | 364
Griffin Bulk | 3329-2 | 3329 Tee1 | 3330 Tee1 | NCC Rating (A) | 865 | 865 | 865 | 865 | 865 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 865 | 865 | 865 | 865 | 865
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Griffin Bulk | 3329-3 | 3329 Tee1 | Kallangur | NCC Rating (A) | 762 | 762 | 762 | 762 | 762 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 280 | 279 | 281 | 282 | 291
|  |  |  | Power Factor | 0.996 | 0.996 | 0.996 | 0.996 | 0.996
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 404 | 403 | 405 | 406 | 420
Griffin Bulk | 3330-1 | Griffin BS | 3330 Tee1 | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 144 | 144 | 145 | 145 | 150
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1
|  |  |  | ECC Rating (A) | 926 | 926 | 926 | 926 | 926
|  |  |  | 50 POE Load (A) | 326 | 325 | 327 | 328 | 339
Griffin Bulk | 3330-2 | 3330 Tee1 | 3329 Tee1 | NCC Rating (A) | 793 | 793 | 793 | 793 | 793 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 793 | 793 | 793 | 793 | 793
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Griffin Bulk | 3330-3 | 3330 Tee1 | APM | NCC Rating (A) | 865 | 865 | 865 | 865 | 865 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 144 | 144 | 145 | 145 | 150
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1
|  |  |  | ECC Rating (A) | 926 | 926 | 926 | 926 | 926
|  |  |  | 50 POE Load (A) | 326 | 325 | 327 | 328 | 339
Griffin Bulk | 3331-1 | 3331 Tee1 | Kallangur | NCC Rating (A) | 926 | 926 | 926 | 926 | 926 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 117 | 117 | 118 | 119 | 123
|  |  |  | Power Factor | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
|  |  |  | ECC Rating (A) | 926 | 926 | 926 | 926 | 926
|  |  |  | 50 POE Load (A) | 292 | 291 | 293 | 295 | 306
Griffin Bulk | 3331-3 | Aust Paper Mills | 3331 Tee1 | NCC Rating (A) | 840 | 840 | 840 | 840 | 840 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 144 | 144 | 145 | 145 | 150
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1
|  |  |  | ECC Rating (A) | 926 | 926 | 926 | 926 | 926
|  |  |  | 50 POE Load (A) | 326 | 325 | 327 | 328 | 339
Griffin Bulk | 3359-1 | 3359 Tee1 | Hays Inlet | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Griffin Bulk | 3359-2 | 3359 Tee1 | 3359 Tee2 | NCC Rating (A) | 912 | 912 | 912 | 912 | 912 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 177 | 176 | 176 | 177 | 179
|  |  |  | Power Factor | 0.985 | 0.985 | 0.985 | 0.985 | 0.985
|  |  |  | ECC Rating (A) | 912 | 912 | 912 | 912 | 912
|  |  |  | 50 POE Load (A) | 410 | 408 | 408 | 409 | 410
Griffin Bulk | 3359-3 | 3359 Tee2 | 3359 Tee3 | NCC Rating (A) | 912 | 912 | 912 | 912 | 912 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 177 | 176 | 176 | 177 | 179
|  |  |  | Power Factor | 0.985 | 0.985 | 0.985 | 0.985 | 0.985
|  |  |  | ECC Rating (A) | 912 | 912 | 912 | 912 | 912
|  |  |  | 50 POE Load (A) | 410 | 408 | 408 | 409 | 410
Griffin Bulk | 3359-4 | 3359 Tee3 | Mango Hill Bus 2 | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 177 | 176 | 177 | 177 | 179
|  |  |  | Power Factor | 0.983 | 0.983 | 0.983 | 0.983 | 0.984
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 330 | 329 | 329 | 330 | 331
Griffin Bulk | 3359-5 | 3359 Tee2 | P51001-D | NCC Rating (A) | 495 | 818 | 818 | 818 | 818 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 495 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Griffin Bulk | 3359-6 | 3359 Tee3 | X18574-E | NCC Rating (A) | 495 | 582 | 582 | 582 | 582 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 495 | 582 | 582 | 582 | 582
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Griffin Bulk | 3359-7 | Griffin BS | 3359 Tee1 | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 176 | 176 | 176 | 176 | 178
|  |  |  | Power Factor | 0.984 | 0.984 | 0.984 | 0.984 | 0.984
|  |  |  | ECC Rating (A) | 917 | 917 | 917 | 917 | 917
|  |  |  | 50 POE Load (A) | 410 | 408 | 409 | 409 | 411
Griffin Bulk | 338-1 | Griffin BS | Strathpine | NCC Rating (A) | 348 | 348 | 348 | 348 | 348 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 348 | 348 | 348 | 348 | 348
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Gympie Bulk | 3004-1 | Coondoo Ck Reg | Tin Can Bay | NCC Rating (A) | 246 | 246 | 246 | 246 | 246 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 37 | 37 | 36 | 36 | 36
|  |  |  | Power Factor | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (A) | 246 | 246 | 246 | 246 | 246
|  |  |  | 50 POE Load (A) | 81 | 78 | 78 | 77 | 77
Gympie Bulk | 3005-1 | Coondoo Ck Reg | Tin Can Bay | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 86 | 85 | 84 | 84 | 83
|  |  |  | Power Factor | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
|  |  |  | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
|  |  |  | 50 POE Load (A) | 96 | 94 | 93 | 92 | 92
Gympie Bulk | 3009-1 | Gympie BS | Gympie Nth | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 104 | 103 | 103 | 103 | 102
|  |  |  | Power Factor | 0.993 | 0.993 | 0.993 | 0.993 | 0.993
|  |  |  | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | 50 POE Load (A) | 198 | 195 | 194 | 193 | 192
Gympie Bulk | 3011-1 | Gympie BS | Gympie Nth | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 104 | 103 | 103 | 103 | 102
|  |  |  | Power Factor | 0.993 | 0.993 | 0.993 | 0.993 | 0.993
|  |  |  | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | 50 POE Load (A) | 198 | 195 | 194 | 193 | 192
Gympie Bulk | 339/2-1 | Amamoor | 339 Tee1 | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170 | 3
|  |  |  | 10 POE Load (A) | 70 | 69 | 68 | 66 | 66
|  |  |  | Power Factor | 0.884 | 0.885 | 0.885 | 0.886 | 0.886
|  |  |  | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | 50 POE Load (A) | 127 | 124 | 122 | 119 | 118
Gympie Bulk | 339/2-2 | 339 Tee1 | Imbil | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170 | 3
|  |  |  | 10 POE Load (A) | 57 | 56 | 55 | 54 | 53
|  |  |  | Power Factor | 0.878 | 0.879 | 0.879 | 0.88 | 0.88
|  |  |  | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | 50 POE Load (A) | 118 | 115 | 113 | 110 | 109
Gympie Bulk | 339/2-5 | 339 Tee2 | 340 Tee2 | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170 | 3
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Gympie Bulk | 339-1 | Gympie BS | 339 Tee1 | NCC Rating (A) | 786 | 786 | 786 | 786 | 786 | Rural | 170 | 3
|  |  |  | 10 POE Load (A) | 179 | 186 | 185 | 183 | 182
|  |  |  | Power Factor | 0.899 | 0.898 | 0.899 | 0.9 | 0.9
|  |  |  | ECC Rating (A) | 786 | 786 | 786 | 786 | 786
|  |  |  | 50 POE Load (A) | 179 | 186 | 184 | 183 | 181
Gympie Bulk | 339-2 | 339 Tee1 | Amamoor | NCC Rating (A) | 322 | 322 | 322 | 322 | 322 | Rural | 170 | 3
|  |  |  | 10 POE Load (A) | 179 | 186 | 186 | 184 | 183
|  |  |  | Power Factor | 0.899 | 0.898 | 0.899 | 0.9 | 0.9
|  |  |  | ECC Rating (A) | 322 | 322 | 322 | 322 | 322
|  |  |  | 50 POE Load (A) | 260 | 271 | 268 | 265 | 263
Gympie Bulk | 339-3 | 339 Tee1 | 340 Tee1 | NCC Rating (A) | 322 | 322 | 322 | 322 | 322 | Rural | 170 | 3
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 322 | 322 | 322 | 322 | 322
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Gympie Bulk | 340-1 | Gympie BS | 340 Tee1 | NCC Rating (A) | 490 | 490 | 490 | 490 | 490 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 56 | 55 | 55 | 55 | 55
|  |  |  | Power Factor | 0.967 | 0.967 | 0.967 | 0.967 | 0.967
|  |  |  | ECC Rating (A) | 490 | 490 | 490 | 490 | 490
|  |  |  | 50 POE Load (A) | 167 | 165 | 164 | 164 | 163
Gympie Bulk | 340-2 | 340 Tee1 | 339 Tee1 | NCC Rating (A) | 490 | 490 | 490 | 490 | 490 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 490 | 490 | 490 | 490 | 490
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Gympie Bulk | 340-4 | 340 Tee1 | 340 Tee2 | NCC Rating (A) | 490 | 490 | 490 | 490 | 490 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 56 | 56 | 56 | 55 | 55
|  |  |  | Power Factor | 0.966 | 0.966 | 0.966 | 0.966 | 0.966
|  |  |  | ECC Rating (A) | 490 | 490 | 490 | 490 | 490
|  |  |  | 50 POE Load (A) | 167 | 165 | 164 | 164 | 163
Gympie Bulk | 340-5 | 340 Tee2 | 340 Tee3 | NCC Rating (A) | 401 | 401 | 401 | 401 | 401 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 401 | 401 | 401 | 401 | 401
|  |  |  | 50 POE Load (A) | 4 | 4 | 4 | 4 | 4
Gympie Bulk | 340-6 | 340 Tee3 | 339 Tee2 | NCC Rating (A) | 912 | 912 | 912 | 912 | 912 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 912 | 912 | 912 | 912 | 912
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Gympie Bulk | 340-7 | 339 Tee2 | Kenilworth | NCC Rating (A) | 416 | 416 | 416 | 416 | 416 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 416 | 416 | 416 | 416 | 416
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Gympie Bulk | 340-8 | 340 Tee3 | Black Mountain | NCC Rating (A) | 401 | 401 | 401 | 401 | 401 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 401 | 401 | 401 | 401 | 401
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Gympie Bulk | 340-9 | 340 Tee2 | Gympie South | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 57 | 57 | 57 | 56 | 56
|  |  |  | Power Factor | 0.949 | 0.949 | 0.949 | 0.949 | 0.949
|  |  |  | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
|  |  |  | 50 POE Load (A) | 173 | 171 | 170 | 170 | 169
Gympie Bulk | 341-1 | Gympie BS | 341 Tee1 | NCC Rating (A) | 455 | 455 | 455 | 455 | 455 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 209 | 207 | 208 | 207 | 206
|  |  |  | Power Factor | 0.998 | 0.998 | 0.998 | 0.998 | 0.998
|  |  |  | ECC Rating (A) | 194 | 194 | 194 | 194 | 194
|  |  |  | 50 POE Load (A) | 421 | 416 | 415 | 414 | 412
Gympie Bulk | 341-2 | 341 Tee1 | Customer | NCC Rating (A) | 454 | 454 | 454 | 454 | 454 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 85 | 84 | 83 | 83 | 83
|  |  |  | Power Factor | 0.988 | 0.989 | 0.988 | 0.988 | 0.988
|  |  |  | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
|  |  |  | 50 POE Load (A) | 304.036 | 300.2814 | 299.4495 | 298.4187 | 297.63
Gympie Bulk | 341-3 | 341 Tee1 | Coondoo Ck Reg | NCC Rating (A) | 292 | 292 | 292 | 292 | 292 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 131 | 129 | 130 | 129 | 129
|  |  |  | Power Factor | 0.998 | 0.998 | 0.998 | 0.998 | 0.999
|  |  |  | ECC Rating (A) | 292 | 292 | 292 | 292 | 292
|  |  |  | 50 POE Load (A) | 225 | 219 | 218 | 216 | 215
Gympie Bulk | 341-4 | Coondoo Ck Reg | 341 Tee2 | NCC Rating (A) | 926 | 926 | 926 | 926 | 926 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 123 | 121 | 120 | 120 | 119
|  |  |  | Power Factor | 0.998 | 0.998 | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (A) | 926 | 926 | 926 | 926 | 926
|  |  |  | 50 POE Load (A) | 178 | 173 | 172 | 171 | 169
Gympie Bulk | 351-1 | Gympie BS | Gympie Sth | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 65 | 64 | 64 | 64 | 64
|  |  |  | Power Factor | 0.961 | 0.962 | 0.961 | 0.962 | 0.962
|  |  |  | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
|  |  |  | 50 POE Load (A) | 173 | 171 | 170 | 169 | 169
Gympie Bulk | 429-1 | Gympie BS | 429 Tee1 | NCC Rating (A) | 786 | 786 | 786 | 786 | 786 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 283 | 279 | 281 | 280 | 279
|  |  |  | Power Factor | 0.957 | 0.957 | 0.958 | 0.958 | 0.958
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 524 | 516 | 514 | 512 | 510
Gympie Bulk | 429-2 | 429 Tee1 | Goomboorian | NCC Rating (A) | 492 | 492 | 492 | 492 | 492 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 41 | 41 | 41 | 41 | 40
|  |  |  | Power Factor | 0.998 | 0.998 | 0.998 | 0.998 | 0.998
|  |  |  | ECC Rating (A) | 492 | 492 | 492 | 492 | 492
|  |  |  | 50 POE Load (A) | 43 | 42 | 42 | 42 | 41
Gympie Bulk | 429-3 | 429 Tee1 | Toolara Forest | NCC Rating (A) | 454 | 454 | 454 | 454 | 454 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 243 | 240 | 241 | 241 | 240
|  |  |  | Power Factor | 0.964 | 0.964 | 0.965 | 0.965 | 0.965
|  |  |  | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
|  |  |  | 50 POE Load (A) | 357 | 352 | 351 | 349 | 348
Hays Inlet Bulk | 305-1 | Hays Inlet BS | Deception Bay | NCC Rating (A) | 759 | 759 | 759 | 759 | 759 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 458 | 455 | 455 | 455 | 456
|  |  |  | Power Factor | 0.988 | 0.988 | 0.988 | 0.988 | 0.988
|  |  |  | ECC Rating (A) | 759 | 759 | 759 | 759 | 759
|  |  |  | 50 POE Load (A) | 678 | 674 | 675 | 676 | 678
Hays Inlet Bulk | 311-1 | Hays Inlet BS | Deception Bay | NCC Rating (A) | 681 | 681 | 681 | 681 | 681 | Urban | 70 | 4.5
|  |  |  | 10 POE Load (A) | 152 | 151 | 151 | 151 | 152
|  |  |  | Power Factor | 0.996 | 0.996 | 0.996 | 0.996 | 0.996
|  |  |  | ECC Rating (A) | 681 | 681 | 681 | 681 | 681
|  |  |  | 50 POE Load (A) | 533 | 529 | 530 | 530 | 530
Hays Inlet Bulk | 3250-1 | Deception Bay | Burpengary | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 269 | 268 | 269 | 270 | 271
|  |  |  | Power Factor | 0.988 | 0.988 | 0.988 | 0.988 | 0.988
|  |  |  | ECC Rating (A) | 921 | 921 | 921 | 921 | 921
|  |  |  | 50 POE Load (A) | 749 | 746 | 748 | 750 | 754
Hays Inlet Bulk | 325-1 | Hays Inlet BS | Scarborough | NCC Rating (A) | 734 | 734 | 734 | 734 | 734 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 227 | 226 | 227 | 228 | 229
|  |  |  | Power Factor | 0.995 | 0.995 | 0.995 | 0.996 | 0.996
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 450 | 448 | 449 | 451 | 453
Hays Inlet Bulk | 3251-1 | Burpengary | Morayfield | NCC Rating (A) | 508 | 508 | 508 | 508 | 508 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 508 | 508 | 508 | 508 | 508
|  |  |  | 50 POE Load (A) | 373 | 382 | 394 | 398 | 402
Hays Inlet Bulk | 326-1 | Redcliffe | Scarborough | NCC Rating (A) | 688 | 688 | 688 | 688 | 688 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 20 | 21 | 23 | 24 | 26
|  |  |  | Power Factor | 0.998 | 0.999 | 1 | 1 | 0.999
|  |  |  | ECC Rating (A) | 785 | 785 | 785 | 785 | 785
|  |  |  | 50 POE Load (A) | 576 | 577 | 583 | 588 | 593
Hays Inlet Bulk | 327-1 | Hays Inlet BS | Mango Hill Bus 1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 243 | 243 | 246 | 248 | 250
|  |  |  | Power Factor | 0.98 | 0.98 | 0.979 | 0.979 | 0.979
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 231 | 231 | 233 | 235 | 238
Hays Inlet Bulk | 329-1 | Redcliffe | Duffield Rd | NCC Rating (A) | 688 | 688 | 688 | 688 | 688 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 70 | 71 | 71 | 71 | 72
|  |  |  | Power Factor | 0.995 | 0.995 | 0.995 | 0.995 | 0.995
|  |  |  | ECC Rating (A) | 864 | 864 | 864 | 864 | 864
|  |  |  | 50 POE Load (A) | 275 | 274 | 275 | 275 | 276
Hays Inlet Bulk | 330-1 | Hays Inlet BS | Duffield Rd | NCC Rating (A) | 595 | 595 | 595 | 595 | 595 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 209 | 207 | 207 | 208 | 208
|  |  |  | Power Factor | 0.992 | 0.992 | 0.992 | 0.992 | 0.992
|  |  |  | ECC Rating (A) | 864 | 864 | 864 | 864 | 864
|  |  |  | 50 POE Load (A) | 468 | 464 | 464 | 463 | 463
Hays Inlet Bulk | 331-1 | Hays Inlet BS | Duffield Rd | NCC Rating (A) | 595 | 595 | 595 | 595 | 595 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 210 | 208 | 208 | 206 | 206
|  |  |  | Power Factor | 0.989 | 0.989 | 0.989 | 0.989 | 0.989
|  |  |  | ECC Rating (A) | 864 | 864 | 864 | 864 | 864
|  |  |  | 50 POE Load (A) | 468 | 465 | 464 | 461 | 461
Hays Inlet Bulk | 332-1 | Hays Inlet BS | Redcliffe | NCC Rating (A) | 677 | 677 | 677 | 677 | 677 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 215 | 213 | 213 | 214 | 214
|  |  |  | Power Factor | 0.985 | 0.985 | 0.985 | 0.985 | 0.985
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 478 | 474 | 475 | 477 | 478
Hays Inlet Bulk | 451-1 | Narangba | Burpengary | NCC Rating (A) | 489 | 489 | 489 | 489 | 489 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 26 | 27 | 27 | 28 | 29
|  |  |  | Power Factor | 0.752 | 0.757 | 0.761 | 0.769 | 0.778
|  |  |  | ECC Rating (A) | 489 | 489 | 489 | 489 | 489
|  |  |  | 50 POE Load (A) | 371 | 369 | 371 | 373 | 376
Hays Inlet Bulk | 497-1 | Hays Inlet BS | Narangba | NCC Rating (A) | 720 | 720 | 720 | 720 | 720 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 322 | 321 | 322 | 323 | 324
|  |  |  | Power Factor | 0.981 | 0.981 | 0.981 | 0.981 | 0.98
|  |  |  | ECC Rating (A) | 921 | 921 | 921 | 921 | 921
|  |  |  | 50 POE Load (A) | 744 | 741 | 742 | 745 | 748
Jimboomba Bulk | 470-1 | Jimboomba BS | Logan Village | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 189 | 186 | 190 | 193 | 196
|  |  |  | Power Factor | 0.991 | 0.991 | 0.991 | 0.991 | 0.99
|  |  |  | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
|  |  |  | 50 POE Load (A) | 158.76 | 156.24 | 159.6 | 162.12 | 164.64
Jimboomba Bulk | 479-1 | Jimboomba BS | Nth Maclean | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 377 | 383 | 382 | 390 | 397
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.989 | 0.989
|  |  |  | ECC Rating (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lockrose Bulk | 378-1 | Lockrose BS | 378 Tee1 | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 136 | 135 | 151 | 152 | 152
|  |  |  | Power Factor | 0.964 | 0.964 | 0.955 | 0.955 | 0.955
|  |  |  | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | 50 POE Load (A) | 272 | 271 | 232 | 233 | 234
Lockrose Bulk | 378-2 | 378 Tee1 | Glenmore Grove | NCC Rating (A) | 800 | 800 | 473 | 473 | 473 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 62 | 62 | 83 | 83 | 83
|  |  |  | Power Factor | 0.987 | 0.987 | 0.962 | 0.962 | 0.962
|  |  |  | ECC Rating (A) | 800 | 800 | 473 | 473 | 473
|  |  |  | 50 POE Load (A) | 120 | 119 | 85 | 85 | 85
Lockrose Bulk | 378-3 | 378 Tee1 | 378 Tee2 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 75 | 74 | 69 | 69 | 70
|  |  |  | Power Factor | 0.943 | 0.943 | 0.954 | 0.954 | 0.953
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 153 | 152 | 152 | 154 | 154
Lockrose Bulk | 378-4 | 378 Tee2 | 532 Tee1 | NCC Rating (A) | 416 | 416 | 416 | 416 | 416 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 416 | 416 | 416 | 416 | 416
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lockrose Bulk | 378-5 | 378 Tee2 | Laidley | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 75 | 75 | 69 | 69 | 70
|  |  |  | Power Factor | 0.94 | 0.94 | 0.95 | 0.95 | 0.95
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 153 | 153 | 153 | 154 | 155
Lockrose Bulk | 380-1 | Murrumba | 380 Tee1 | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 45 | 44 | 40 | 40 | 40
|  |  |  | Power Factor | 0.955 | 0.955 | 0.975 | 0.975 | 0.975
|  |  |  | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | 50 POE Load (A) | 246 | 244 | 244 | 244 | 244
Lockrose Bulk | 380-2 | 380 Tee1 | Somerset Dam | NCC Rating (A) | 324 | 324 | 324 | 324 | 324 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 7 | 7 | 7 | 7 | 7
|  |  |  | Power Factor | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
|  |  |  | ECC Rating (A) | 324 | 324 | 324 | 324 | 324
|  |  |  | 50 POE Load (A) | 15 | 15 | 15 | 15 | 15
Lockrose Bulk | 380-3 | 380 Tee1 | Toogoolahwah | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 39 | 39 | 33 | 33 | 33
|  |  |  | Power Factor | 0.928 | 0.928 | 0.955 | 0.954 | 0.954
|  |  |  | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | 50 POE Load (A) | 233 | 230 | 231 | 230 | 230
Lockrose Bulk | 381-1 | Lockrose BS | 381 Tee1 | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 133 | 138 | 146 | 146 | 145
|  |  |  | Power Factor | 0.969 | 0.969 | 0.949 | 0.949 | 0.949
|  |  |  | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | 50 POE Load (A) | 292 | 301 | 278 | 277 | 277
Lockrose Bulk | 381-2 | 381 Tee1 | 382 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lockrose Bulk | 381-3 | 381 Tee1 | 381 Tee2 | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 133 | 138 | 146 | 146 | 146
|  |  |  | Power Factor | 0.969 | 0.969 | 0.949 | 0.949 | 0.949
|  |  |  | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | 50 POE Load (A) | 292 | 301 | 278 | 278 | 277
Lockrose Bulk | 381-4 | 381 Tee2 | 383 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lockrose Bulk | 381-5 | 381 Tee2 | 381 Tee3 | NCC Rating (A) | 293 | 293 | 582 | 582 | 582 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 133 | 138 | 146 | 146 | 146
|  |  |  | Power Factor | 0.971 | 0.971 | 0.952 | 0.952 | 0.952
|  |  |  | ECC Rating (A) | 293 | 293 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 292 | 301 | 411 | 411 | 410
Lockrose Bulk | 381-6 | 381 Tee3 | Coominya TR2 | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 54 | 59 | 58 | 58 | 58
|  |  |  | Power Factor | 0.972 | 0.971 | 0.971 | 0.971 | 0.971
|  |  |  | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
|  |  |  | 50 POE Load (A) | 80 | 89 | 84 | 83 | 83
Lockrose Bulk | 381-7 | 381 Tee3 | 381 Tee4 | NCC Rating (A) | 293 | 293 | 582 | 582 | 582 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 79 | 79 | 88 | 88 | 88
|  |  |  | Power Factor | 0.978 | 0.978 | 0.947 | 0.947 | 0.947
|  |  |  | ECC Rating (A) | 293 | 293 | 582 | 582 | 582
|  |  |  | 50 POE Load (A) | 237 | 240 | 220 | 220 | 220
Lockrose Bulk | 381-8 | 381 Tee4 | Coominya TR1 | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 37 | 41 | 40 | 40 | 40
|  |  |  | Power Factor | 0.973 | 0.972 | 0.972 | 0.972 | 0.972
|  |  |  | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
|  |  |  | 50 POE Load (A) | 56 | 62 | 58 | 58 | 58
Lockrose Bulk | 381-9 | 381 Tee4 | Paddys Gully | NCC Rating (A) | 293 | 293 | 432 | 432 | 432 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 42 | 38 | 49 | 49 | 49
|  |  |  | Power Factor | 0.979 | 0.981 | 0.917 | 0.917 | 0.917
|  |  |  | ECC Rating (A) | 293 | 293 | 432 | 432 | 432
|  |  |  | 50 POE Load (A) | 376 | 374 | 390 | 390 | 390
Lockrose Bulk | 382-1 | Lockrose BS | 382 Tee1 | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 136 | 138 | 124 | 124 | 124
|  |  |  | Power Factor | 0.93 | 0.93 | 0.955 | 0.955 | 0.955
|  |  |  | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | 50 POE Load (A) | 172 | 170 | 168 | 168 | 168
Lockrose Bulk | 382-2 | 382 Tee1 | 381 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lockrose Bulk | 382-3 | 382 Tee1 | Paddys Gully | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 137 | 139 | 125 | 125 | 125
|  |  |  | Power Factor | 0.93 | 0.93 | 0.955 | 0.955 | 0.955
|  |  |  | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | 50 POE Load (A) | 173 | 170 | 169 | 169 | 169
Lockrose Bulk | 3828-1 | Paddy's Gully | Esk | NCC Rating (A) | 293 | 293 | 800 | 800 | 800 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 70 | 69 | 73 | 73 | 73
|  |  |  | Power Factor | 0.987 | 0.987 | 0.978 | 0.978 | 0.978
|  |  |  | ECC Rating (A) | 293 | 293 | 912 | 912 | 912
|  |  |  | 50 POE Load (A) | 325 | 321 | 215 | 215 | 215
Lockrose Bulk | 3829-1 | Paddy's Gully | Murrumba | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 94 | 93 | 88 | 88 | 88
|  |  |  | Power Factor | 0.909 | 0.91 | 0.921 | 0.921 | 0.921
|  |  |  | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | 50 POE Load (A) | 306 | 303 | 303 | 303 | 302
Lockrose Bulk | 3831-1 | Lockrose BS | Tarampa | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 106 | 104 | 104 | 104 | 103
|  |  |  | Power Factor | 0.964 | 0.964 | 0.964 | 0.965 | 0.965
|  |  |  | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
|  |  |  | 50 POE Load (A) | 145 | 143 | 142 | 142 | 142
Lockrose Bulk | 3832-1 | Tarampa | 383 Tee1 | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lockrose Bulk | 3832-2 | 3832 Tee1 | 381 Tee1 | NCC Rating (A) | 293 | 293 | 912 | 912 | 912 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 293 | 293 | 912 | 912 | 912
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lockrose Bulk | 3832-3 | 3832 Tee1 | Lowood | NCC Rating (A) | 434 | 434 | 434 | 434 | 434 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 434 | 434 | 434 | 434 | 434
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lockrose Bulk | 3840-1 | Esk | Toogoolawah | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 32 | 32 | 37 | 37 | 37
|  |  |  | Power Factor | 0.975 | 0.975 | 0.951 | 0.951 | 0.951
|  |  |  | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | 50 POE Load (A) | 257 | 255 | 248 | 248 | 248
Lockrose Bulk | 384-1 | Lockrose BS | 384 Tee1 | NCC Rating (A) | 451 | 451 | 451 | 451 | 451 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 141 | 141 | 126 | 126 | 127
|  |  |  | Power Factor | 0.962 | 0.963 | 0.973 | 0.973 | 0.973
|  |  |  | ECC Rating (A) | 451 | 451 | 451 | 451 | 451
|  |  |  | 50 POE Load (A) | 273 | 272 | 190 | 191 | 192
Lockrose Bulk | 384-2 | 384 Tee1 | Glenmore Grove | NCC Rating (A) | 689 | 689 | 473 | 473 | 473 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 63 | 62 | 40 | 40 | 40
|  |  |  | Power Factor | 0.906 | 0.906 | 0.944 | 0.944 | 0.944
|  |  |  | ECC Rating (A) | 689 | 689 | 689 | 689 | 689
|  |  |  | 50 POE Load (A) | 281 | 279 | 89 | 89 | 89
Lockrose Bulk | 384-3 | 384 Tee1 | Laidley1 | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 81 | 81 | 87 | 87 | 88
|  |  |  | Power Factor | 0.991 | 0.991 | 0.984 | 0.984 | 0.984
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | 50 POE Load (A) | 153 | 153 | 153 | 154 | 155
Lockrose Bulk | 3870-1 | Lockrose BS | Lowood | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 114 | 113 | 113 | 113 | 113
|  |  |  | Power Factor | 0.971 | 0.971 | 0.972 | 0.972 | 0.971
|  |  |  | ECC Rating (A) | 917 | 917 | 917 | 917 | 917
|  |  |  | 50 POE Load (A) | 140 | 139 | 139 | 139 | 139
Lockrose Bulk | 3871-1 | Lowood | Wivenhoe | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 80 | 79 | 79 | 79 | 79
|  |  |  | Power Factor | 0.978 | 0.978 | 0.978 | 0.978 | 0.978
|  |  |  | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | 50 POE Load (A) | 75 | 75 | 75 | 75 | 75
Loganlea Bulk | 407-1 | Loganlea BS | Woodridge | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 245 | 240 | 237 | 234 | 233
|  |  |  | Power Factor | 0.977 | 0.977 | 0.977 | 0.978 | 0.978
|  |  |  | ECC Rating (A) | 832 | 832 | 832 | 832 | 832
|  |  |  | 50 POE Load (A) | 474 | 466 | 460 | 454 | 451
Loganlea Bulk | 408-1 | Loganlea BS | Kingston | NCC Rating (A) | 724 | 724 | 724 | 724 | 724 | Urban | 280 | NA
|  |  |  | 10 POE Load (A) | 303 | 278 | 278 | 277 | 276
|  |  |  | Power Factor | 0.94 | 0.943 | 0.943 | 0.943 | 0.943
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 772 | 707 | 706 | 703 | 702
Loganlea Bulk | 409-1 | Loganlea BS | Woodridge | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 219 | 215 | 212 | 210 | 208
|  |  |  | Power Factor | 0.979 | 0.979 | 0.98 | 0.98 | 0.98
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 444 | 436 | 430 | 425 | 422
Loganlea Bulk | 418-1 | Loganlea BS | Tanah Merah | NCC Rating (A) | 692 | 692 | 692 | 692 | 692 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 226 | 223 | 221 | 219 | 217
|  |  |  | Power Factor | 0.996 | 0.996 | 0.996 | 0.996 | 0.996
|  |  |  | ECC Rating (A) | 692 | 692 | 692 | 692 | 692
|  |  |  | 50 POE Load (A) | 235 | 231 | 229 | 226 | 225
Loganlea Bulk | 452-1 | Loganlea BS | Kingston | NCC Rating (A) | 567 | 567 | 567 | 567 | 567 | Urban | 280 | NA
|  |  |  | 10 POE Load (A) | 246 | 226 | 226 | 225 | 225
|  |  |  | Power Factor | 0.977 | 0.979 | 0.979 | 0.979 | 0.979
|  |  |  | ECC Rating (A) | 567 | 567 | 567 | 567 | 567
|  |  |  | 50 POE Load (A) | 585 | 536 | 534 | 533 | 532
Lytton Bulk | 3302-1 | Lytton BS | Fisherman Is B | NCC Rating (A) | 690 | 690 | 690 | 690 | 690 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 192 | 229 | 235 | 235 | 234
|  |  |  | Power Factor | 0.904 | 0.905 | 0.905 | 0.905 | 0.905
|  |  |  | ECC Rating (A) | 690 | 690 | 690 | 690 | 690
|  |  |  | 50 POE Load (A) | 405 | 487 | 500 | 499 | 498
Lytton Bulk | 3303-1 | Lytton BS | Fisherman Is B | NCC Rating (A) | 650 | 650 | 650 | 650 | 650 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 192 | 229 | 235 | 234 | 233
|  |  |  | Power Factor | 0.904 | 0.905 | 0.905 | 0.905 | 0.905
|  |  |  | ECC Rating (A) | 650 | 650 | 650 | 650 | 650
|  |  |  | 50 POE Load (A) | 414 | 497 | 511 | 509 | 508
Lytton Bulk | 490-1 | Lytton BS | Gibson Island | NCC Rating (A) | 664 | 664 | 664 | 664 | 664 | HighSec | 0 | NA
|  |  |  | 10 POE Load (A) | 151 | 150 | 150 | 149 | 149
|  |  |  | Power Factor | 0.99 | 0.991 | 0.991 | 0.991 | 0.991
|  |  |  | ECC Rating (A) | 664 | 664 | 664 | 664 | 664
|  |  |  | 50 POE Load (A) | 310 | 307 | 307 | 324 | 323
Lytton Bulk | 491-1 | Lytton BS | Lytton | NCC Rating (A) | 511 | 511 | 511 | 511 | 511 | HighSec | 0 | NA
|  |  |  | 10 POE Load (A) | 209 | 206 | 221 | 220 | 220
|  |  |  | Power Factor | 0.991 | 0.991 | 0.987 | 0.988 | 0.988
|  |  |  | ECC Rating (A) | 511 | 511 | 511 | 511 | 511
|  |  |  | 50 POE Load (A) | 469 | 464 | 497 | 492 | 491
Lytton Bulk | 492-1 | Lytton BS | Gibson Island | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | HighSec | 0 | NA
|  |  |  | 10 POE Load (A) | 145 | 144 | 144 | 143 | 143
|  |  |  | Power Factor | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
|  |  |  | 50 POE Load (A) | 324 | 321 | 321 | 339 | 338
Lytton Bulk | 493-1 | Lytton BS | Lytton | NCC Rating (A) | 573 | 573 | 573 | 573 | 573 | HighSec | 0 | NA
|  |  |  | 10 POE Load (A) | 209 | 207 | 222 | 221 | 221
|  |  |  | Power Factor | 0.957 | 0.958 | 0.95 | 0.95 | 0.951
|  |  |  | ECC Rating (A) | 573 | 573 | 573 | 573 | 573
|  |  |  | 50 POE Load (A) | 441 | 436 | 468 | 463 | 462
Lytton Bulk | 494-1 | Fisherman Is B | Fishermans Is | NCC Rating (A) | 546 | 546 | 546 | 546 | 546 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 75 | 113 | 119 | 119 | 118
|  |  |  | Power Factor | 0.972 | 0.967 | 0.966 | 0.966 | 0.966
|  |  |  | ECC Rating (A) | 546 | 546 | 546 | 546 | 546
|  |  |  | 50 POE Load (A) | 165 | 250 | 264 | 263 | 263
Lytton Bulk | 495-1 | Fisherman Is B | Fisherman Is | NCC Rating (A) | 600 | 600 | 600 | 600 | 600 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 76 | 114 | 121 | 120 | 120
|  |  |  | Power Factor | 0.891 | 0.886 | 0.885 | 0.885 | 0.885
|  |  |  | ECC Rating (A) | 600 | 600 | 600 | 600 | 600
|  |  |  | 50 POE Load (A) | 146 | 222 | 235 | 234 | 234
Lytton Bulk | 560-1 | Lytton BS | 560 Tee1 | NCC Rating (A) | 527 | 527 | 527 | 527 | 527 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 133 | 119 | 118 | 117 | 117
|  |  |  | Power Factor | 0.996 | 0.999 | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (A) | 527 | 527 | 527 | 527 | 527
|  |  |  | 50 POE Load (A) | 357 | 352 | 350 | 348 | 345
Lytton Bulk | 560-14 | 560 Tee1 | 560 Tee2 | NCC Rating (A) | 527 | 527 | 527 | 527 | 527 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 55 | 49 | 49 | 48 | 48
|  |  |  | Power Factor | 0.994 | 1 | 1 | 1 | 1
|  |  |  | ECC Rating (A) | 527 | 527 | 527 | 527 | 527
|  |  |  | 50 POE Load (A) | 212 | 208 | 207 | 206 | 205
Lytton Bulk | 560-15 | 560 Tee1 | 560 Tee2 | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 79 | 70 | 70 | 69 | 69
|  |  |  | Power Factor | 0.97 | 0.988 | 0.988 | 0.988 | 0.988
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | 50 POE Load (A) | 296 | 292 | 290 | 288 | 287
Lytton Bulk | 560-16 | Lota | 560 Tee1 | NCC Rating (A) | 1053 | 1053 | 1053 | 1053 | 1053 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 135 | 120 | 119 | 118 | 118
|  |  |  | Power Factor | 0.982 | 0.996 | 0.996 | 0.996 | 0.996
|  |  |  | ECC Rating (A) | 1053 | 1053 | 1053 | 1053 | 1053
|  |  |  | 50 POE Load (A) | 384 | 378 | 376 | 374 | 371
Lytton Bulk | 560-2 | 560 Tee1 | Tingalpa | NCC Rating (A) | 600 | 600 | 600 | 600 | 600 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
Lytton Bulk | 560-3 | 560 Tee1 | 560 Tee2 | NCC Rating (A) | 600 | 600 | 600 | 600 | 600 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 133 | 119 | 118 | 118 | 117
|  |  |  | Power Factor | 0.996 | 0.999 | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (A) | 600 | 600 | 600 | 600 | 600
|  |  |  | 50 POE Load (A) | 357 | 352 | 350 | 348 | 346
Lytton Bulk | 560-5 | Lota | 560 Tee2 | NCC Rating (A) | 775 | 775 | 775 | 775 | 775 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 78 | 70 | 70 | 69 | 69
|  |  |  | Power Factor | 0.996 | 0.999 | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (A) | 775 | 775 | 775 | 775 | 775
|  |  |  | 50 POE Load (A) | 231 | 228 | 227 | 225 | 224
Lytton Bulk | 569-1 | Lytton BS | Lota | NCC Rating (A) | 490 | 582 | 582 | 582 | 582 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 237 | 245 | 244 | 242 | 241
|  |  |  | Power Factor | 0.999 | 0.995 | 0.996 | 0.996 | 0.996
|  |  |  | ECC Rating (A) | 490 | 582 | 582 | 582 | 582
|  |  |  | 50 POE Load (A) | 352 | 344 | 342 | 340 | 338
Lytton Bulk | 599-1 | Hemmant | Lindum | NCC Rating (A) | 630 | 630 | 630 | 630 | 630 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 630 | 630 | 630 | 630 | 630
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lytton Bulk | 681-1 | Lindum | Wynnum | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 159 | 158 | 158 | 158 | 158
|  |  |  | Power Factor | 0.984 | 0.984 | 0.984 | 0.984 | 0.984
|  |  |  | ECC Rating (A) | 837 | 837 | 837 | 837 | 837
|  |  |  | 50 POE Load (A) | 316 | 314 | 313 | 313 | 313
Lytton Bulk | 682-1 | Lindum | Wynnum | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 153 | 151 | 151 | 151 | 151
|  |  |  | Power Factor | 0.983 | 0.983 | 0.983 | 0.983 | 0.983
|  |  |  | ECC Rating (A) | 837 | 837 | 837 | 837 | 837
|  |  |  | 50 POE Load (A) | 317 | 314 | 314 | 314 | 314
Lytton Bulk | 687-1 | Lytton BS | 687 Tee1 | NCC Rating (A) | 759 | 759 | 759 | 759 | 759 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 113 | 112 | 112 | 112 | 112
|  |  |  | Power Factor | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (A) | 759 | 759 | 759 | 759 | 759
|  |  |  | 50 POE Load (A) | 291 | 288 | 288 | 288 | 288
Lytton Bulk | 687-2 | 687 Tee1 | Lytton | NCC Rating (A) | 517 | 517 | 517 | 517 | 517 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 517 | 517 | 517 | 517 | 517
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lytton Bulk | 687-3 | 687 Tee1 | Lindum | NCC Rating (A) | 636 | 636 | 636 | 636 | 636 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 113 | 112 | 112 | 112 | 112
|  |  |  | Power Factor | 0.998 | 0.998 | 0.998 | 0.998 | 0.998
|  |  |  | ECC Rating (A) | 636 | 636 | 636 | 636 | 636
|  |  |  | 50 POE Load (A) | 291 | 288 | 288 | 288 | 288
Lytton Bulk | 688-1 | Lytton BS | Lindum | NCC Rating (A) | 636 | 636 | 636 | 636 | 636 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 197 | 195 | 195 | 195 | 195
|  |  |  | Power Factor | 0.984 | 0.984 | 0.984 | 0.984 | 0.984
|  |  |  | ECC Rating (A) | 636 | 636 | 636 | 636 | 636
|  |  |  | 50 POE Load (A) | 290 | 288 | 288 | 288 | 287
Meeandah Bulk | 3374-1 | Whinstanes | Hamilton Lands | NCC Rating (A) | 546 | 775 | 775 | 775 | 775 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 39 | 81 | 81 | 81 | 81
|  |  |  | Power Factor | 0.813 | 0.935 | 0.935 | 0.936 | 0.936
|  |  |  | ECC Rating (A) | 546 | 0 | 0 | 0 | 0
|  |  |  | 50 POE Load (A) | 159 | 0 | 0 | 0 | 0
Meeandah Bulk | 506-1 | Meeandah BS | Hamilton Lands | NCC Rating (A) | 771 | 771 | 771 | 771 | 771 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 99 | 148 | 147 | 147 | 146
|  |  |  | Power Factor | 0.852 | 0.935 | 0.935 | 0.935 | 0.935
|  |  |  | ECC Rating (A) | 771 | 843 | 843 | 843 | 843
|  |  |  | 50 POE Load (A) | 187 | 269 | 268 | 266 | 266
Meeandah Bulk | 513-1 | Meeandah BS | Hamilton Lands | NCC Rating (A) | 771 | 771 | 771 | 771 | 771 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 98 | 147 | 146 | 145 | 145
|  |  |  | Power Factor | 0.852 | 0.934 | 0.935 | 0.935 | 0.935
|  |  |  | ECC Rating (A) | 771 | 843 | 843 | 843 | 843
|  |  |  | 50 POE Load (A) | 186 | 268 | 267 | 266 | 266
Meeandah Bulk | 556-1 | Meeandah BS | Whinstanes | NCC Rating (A) | 546 | 775 | 775 | 775 | 775 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 167 | 133 | 133 | 132 | 132
|  |  |  | Power Factor | 0.991 | 0.938 | 0.938 | 0.938 | 0.938
|  |  |  | ECC Rating (A) | 546 | 912 | 912 | 912 | 912
|  |  |  | 50 POE Load (A) | 249 | 274 | 274 | 273 | 272
Meeandah Bulk | 609-1 | Meeandah BS | Myrtletown | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Meeandah Bulk | 610-1 | Meeandah BS | Myrtletown | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Molendinar Bulk | 3670-1 | Molendinar BS | Parkwood | NCC Rating (A) | 790 | 790 | 790 | 790 | 790 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 244 | 242 | 242 | 251 | 251
|  |  |  | Power Factor | 0.991 | 0.992 | 0.992 | 0.991 | 0.991
|  |  |  | ECC Rating (A) | 790 | 790 | 790 | 790 | 790
|  |  |  | 50 POE Load (A) | 446 | 443 | 443 | 456 | 456
Molendinar Bulk | 3671-1 | Molendinar BS | Parkwood | NCC Rating (A) | 758 | 758 | 758 | 758 | 758 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 194 | 192 | 192 | 200 | 200
|  |  |  | Power Factor | 0.996 | 0.996 | 0.996 | 0.995 | 0.995
|  |  |  | ECC Rating (A) | 758 | 758 | 758 | 758 | 758
|  |  |  | 50 POE Load (A) | 348 | 345 | 345 | 359 | 359
Molendinar Bulk | 389-1 | Parkwood | 389 Tee1 | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 250 | 248 | 249 | 244 | 245
|  |  |  | Power Factor | 0.993 | 0.993 | 0.993 | 0.994 | 0.994
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 535 | 532 | 533 | 532 | 533
Molendinar Bulk | 389-2 | F389 Tee1 | Labrador | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 185 | 185 | 187 | 187 | 189
|  |  |  | Power Factor | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 312 | 312 | 314 | 316 | 318
Molendinar Bulk | 389-3 | F389 Tee1 | Hollywell | NCC Rating (A) | 659 | 659 | 659 | 659 | 659 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 67 | 66 | 65 | 60 | 59
|  |  |  | Power Factor | 0.995 | 0.994 | 0.994 | 0.991 | 0.99
|  |  |  | ECC Rating (A) | 749 | 749 | 749 | 749 | 749
|  |  |  | 50 POE Load (A) | 471 | 467 | 467 | 467 | 467
Molendinar Bulk | 390-1 | Molendinar BS | F390 Tee1 | NCC Rating (A) | 637 | 637 | 637 | 637 | 637 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 69 | 83 | 82 | 82 | 81
|  |  |  | Power Factor | 0.988 | 0.986 | 0.986 | 0.986 | 0.986
|  |  |  | ECC Rating (A) | 637 | 637 | 637 | 637 | 637
|  |  |  | 50 POE Load (A) | 398 | 410 | 411 | 411 | 412
Molendinar Bulk | 390-2 | F390 Tee | Bundall | NCC Rating (A) | 701 | 701 | 701 | 701 | 701 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 70 | 84 | 83 | 82 | 82
|  |  |  | Power Factor | 0.981 | 0.981 | 0.981 | 0.981 | 0.981
|  |  |  | ECC Rating (A) | 721 | 721 | 721 | 721 | 721
|  |  |  | 50 POE Load (A) | 171 | 209 | 207 | 205 | 205
Molendinar Bulk | 390-3 | F390 Tee | Miami | NCC Rating (A) | 688 | 688 | 688 | 688 | 688 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 571 | 570 | 572 | 574 | 576
Molendinar Bulk | 391-1 | Molendinar BS | Bundall | NCC Rating (A) | 688 | 688 | 688 | 688 | 688 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 86 | 103 | 102 | 102 | 101
|  |  |  | Power Factor | 0.972 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | ECC Rating (A) | 688 | 688 | 688 | 688 | 688
|  |  |  | 50 POE Load (A) | 169 | 205 | 203 | 202 | 201
Molendinar Bulk | 392-1 | Molendinar BS | Gaven | NCC Rating (A) | 758 | 758 | 758 | 758 | 758 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 162 | 169 | 168 | 167 | 166
|  |  |  | Power Factor | 0.994 | 0.994 | 0.994 | 0.994 | 0.994
|  |  |  | ECC Rating (A) | 758 | 758 | 758 | 758 | 758
|  |  |  | 50 POE Load (A) | 333 | 348 | 346 | 343 | 342
Molendinar Bulk | 421-1 | Molendinar BS | Arundel | NCC Rating (A) | 713 | 713 | 713 | 713 | 713 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 348 | 343 | 342 | 344 | 344
|  |  |  | Power Factor | 0.988 | 0.988 | 0.988 | 0.988 | 0.988
|  |  |  | ECC Rating (A) | 764 | 764 | 764 | 764 | 764
|  |  |  | 50 POE Load (A) | 631 | 623 | 621 | 625 | 625
Molendinar Bulk | 458-1 | Molendinar BS | Labrador | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 140 | 140 | 140 | 142 | 142
|  |  |  | Power Factor | 0.994 | 0.994 | 0.994 | 0.994 | 0.994
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 318 | 318 | 320 | 322 | 325
Molendinar Bulk | 473-1 | Molendinar BS | Gaven | NCC Rating (A) | 794 | 794 | 794 | 794 | 794 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 163 | 170 | 168 | 167 | 166
|  |  |  | Power Factor | 0.994 | 0.994 | 0.994 | 0.994 | 0.994
|  |  |  | ECC Rating (A) | 926 | 926 | 926 | 926 | 926
|  |  |  | 50 POE Load (A) | 402 | 420 | 417 | 414 | 412
Molendinar Bulk | 474A-1 | Arundel | Hollywell | NCC Rating (A) | 659 | 659 | 659 | 659 | 659 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 399 | 397 | 398 | 402 | 403
|  |  |  | Power Factor | 0.992 | 0.992 | 0.992 | 0.992 | 0.992
|  |  |  | ECC Rating (A) | 2000 | 2000 | 2000 | 2000 | 2000
|  |  |  | 50 POE Load (A) | 525 | 523 | 524 | 530 | 531
Molendinar Bulk | 474B-1 | Hope Is | Hollywell | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 4 | 4 | 4 | 4 | 4
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 935 | 935 | 935 | 935 | 935
|  |  |  | 50 POE Load (A) | 237 | 237 | 239 | 240 | 242
Molendinar Bulk | 486-1 | Molendinar BS | Arundel | NCC Rating (A) | 713 | 713 | 713 | 713 | 713 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 348 | 344 | 342 | 344 | 345
|  |  |  | Power Factor | 0.987 | 0.988 | 0.988 | 0.988 | 0.988
|  |  |  | ECC Rating (A) | 764 | 764 | 764 | 764 | 764
|  |  |  | 50 POE Load (A) | 631 | 624 | 621 | 625 | 625
Mudgeeraba Bulk | 3700-1 | Mudgeeraba BS | 3700 Tee1 | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 164 | 163 | 164 | 164 | 164
|  |  |  | Power Factor | 0.994 | 0.994 | 0.994 | 0.994 | 0.994
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 327 | 325 | 326 | 326 | 327
Mudgeeraba Bulk | 3700-2 | 3700 Tee1 | 3701 Tee1 | NCC Rating (A) | 1094 | 1094 | 1094 | 1094 | 1094 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 1094 | 1094 | 1094 | 1094 | 1094
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Mudgeeraba Bulk | 3700-3 | 3700 Tee1 | 3700 Tee2 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 164 | 163 | 164 | 164 | 164
|  |  |  | Power Factor | 0.994 | 0.994 | 0.994 | 0.994 | 0.994
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 327 | 325 | 326 | 326 | 327
Mudgeeraba Bulk | 3700-4 | 3700 Tee2 | 3702 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Mudgeeraba Bulk | 3700-5 | 3700 Tee2 | Mudgeeraba Pkg | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 164 | 163 | 164 | 164 | 164
|  |  |  | Power Factor | 0.995 | 0.995 | 0.995 | 0.995 | 0.995
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 327 | 325 | 326 | 326 | 327
Mudgeeraba Bulk | 3701-1 | Mudgeeraba | Mudgeeraba Pkg | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 179 | 178 | 178 | 179 | 179
|  |  |  | Power Factor | 0.978 | 0.978 | 0.978 | 0.978 | 0.978
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 481 | 478 | 479 | 480 | 480
Nambour Bulk | 307-1 | Nambour BS | 307 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 74 | 74 | 74 | 75 | 75
|  |  |  | Power Factor | 0.961 | 0.961 | 0.961 | 0.961 | 0.961
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 381 | 377 | 377 | 377 | 376
Nambour Bulk | 307-2 | 307 Tee1 | Yandina | NCC Rating (A) | 799 | 799 | 799 | 799 | 799 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 75 | 75 | 75 | 75 | 76
|  |  |  | Power Factor | 0.954 | 0.954 | 0.954 | 0.954 | 0.954
|  |  |  | ECC Rating (A) | 799 | 799 | 799 | 799 | 799
|  |  |  | 50 POE Load (A) | 141 | 141 | 141 | 142 | 142
Nambour Bulk | 344-1 | Nambour BS | Maleny | NCC Rating (A) | 293 | 293 | 293 | 293 | 432 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 182 | 179 | 178 | 177 | 167
|  |  |  | Power Factor | 0.993 | 0.993 | 0.993 | 0.993 | 0.994
|  |  |  | ECC Rating (A) | 293 | 293 | 293 | 293 | 432
|  |  |  | 50 POE Load (A) | 315 | 310 | 309 | 307 | 332
Nambour Bulk | 345-1 | Nambour BS | Kenilworth | NCC Rating (A) | 416 | 416 | 416 | 416 | 416 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 88 | 87 | 86 | 85 | 84
|  |  |  | Power Factor | 0.988 | 0.988 | 0.989 | 0.989 | 0.989
|  |  |  | ECC Rating (A) | 416 | 416 | 416 | 416 | 416
|  |  |  | 50 POE Load (A) | 167 | 165 | 163 | 161 | 160
Nambour Bulk | 347-1 | Nambour BS | 347 Tee1 | NCC Rating (A) | 412 | 412 | 412 | 412 | 412 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 155 | 154 | 155 | 156 | 156
|  |  |  | Power Factor | 0.982 | 0.982 | 0.982 | 0.982 | 0.982
|  |  |  | ECC Rating (A) | 412 | 412 | 412 | 412 | 412
|  |  |  | 50 POE Load (A) | 349 | 348 | 349 | 351 | 352
Nambour Bulk | 347-2 | 347 Tee1 | Palmwoods Central | NCC Rating (A) | 515 | 515 | 515 | 515 | 515 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 155 | 155 | 156 | 156 | 157
|  |  |  | Power Factor | 0.982 | 0.982 | 0.982 | 0.982 | 0.982
|  |  |  | ECC Rating (A) | 515 | 515 | 515 | 515 | 515
|  |  |  | 50 POE Load (A) | 504 | 502 | 504 | 506 | 508
Nambour Bulk | 347-3 | 347 Tee1 | Landsborough | NCC Rating (A) | 412 | 412 | 412 | 412 | 412 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
|  |  |  | 50 POE Load (A) | 290 | 316 | 346 | 357 | 367
Nambour Bulk | 348-1 | Nambour BS | Palmwoods Central | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 199 | 198 | 199 | 200 | 200
|  |  |  | Power Factor | 0.974 | 0.975 | 0.974 | 0.974 | 0.974
|  |  |  | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
|  |  |  | 50 POE Load (A) | 493 | 491 | 493 | 495 | 497
Nambour Bulk | 489-1 | Nambour BS | Yandina | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 68 | 68 | 68 | 68 | 68
|  |  |  | Power Factor | 0.998 | 0.998 | 0.998 | 0.998 | 0.998
|  |  |  | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | 50 POE Load (A) | 179 | 177 | 177 | 177 | 177
Nudgee Bulk | 3280-1 | Hendra | Clayfield | NCC Rating (A) | 0 | 725 | 725 | 725 | 725 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 6 | 6 | 6 | 6
|  |  |  | Power Factor | 0 | 1 | 1 | 1 | 1
|  |  |  | ECC Rating (A) | 0 | 725 | 725 | 725 | 725
|  |  |  | 50 POE Load (A) | 0 | 6 | 6 | 6 | 6
Nudgee Bulk | 535-1 | Hendra | Nundah | NCC Rating (A) | 314 | 0 | 0 | 0 | 0 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 42 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0.935 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 314 | 0 | 0 | 0 | 0
|  |  |  | 50 POE Load (A) | 158 | 0 | 0 | 0 | 0
Nudgee Bulk | 540-1 | Hendra | Nundah | NCC Rating (A) | 314 | 775 | 775 | 775 | 775 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 42 | 125 | 125 | 124 | 124
|  |  |  | Power Factor | 0.932 | 0.996 | 0.996 | 0.996 | 0.996
|  |  |  | ECC Rating (A) | 314 | 775 | 775 | 775 | 775
|  |  |  | 50 POE Load (A) | 158 | 312 | 311 | 309 | 307
Nudgee Bulk | 593-1 | Nudgee BS | Nundah | NCC Rating (A) | 778 | 778 | 778 | 778 | 778 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 370 | 416 | 414 | 412 | 411
|  |  |  | Power Factor | 0.999 | 0.997 | 0.997 | 0.997 | 0.997
|  |  |  | ECC Rating (A) | 778 | 778 | 778 | 778 | 778
|  |  |  | 50 POE Load (A) | 512 | 575 | 572 | 570 | 568
Nudgee Bulk | 604-1 | Nudgee BS | Geebung | NCC Rating (A) | 459 | 459 | 459 | 459 | 459 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 156 | 158 | 154 | 151 | 150
|  |  |  | Power Factor | 0.998 | 0.996 | 0.996 | 0.997 | 0.997
|  |  |  | ECC Rating (A) | 522 | 522 | 522 | 522 | 522
|  |  |  | 50 POE Load (A) | 251 | 246 | 241 | 236 | 234
Nudgee Bulk | 605-1 | Nudgee BS | Geebung | NCC Rating (A) | 459 | 459 | 459 | 459 | 459 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 156 | 158 | 154 | 152 | 150
|  |  |  | Power Factor | 0.998 | 0.996 | 0.996 | 0.997 | 0.997
|  |  |  | ECC Rating (A) | 522 | 522 | 522 | 522 | 522
|  |  |  | 50 POE Load (A) | 251 | 246 | 241 | 236 | 235
Nudgee Bulk | 622-1 | Nudgee BS | Hendra | NCC Rating (A) | 758 | 758 | 758 | 758 | 758 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 188 | 269 | 268 | 267 | 266
|  |  |  | Power Factor | 0.982 | 0.994 | 0.994 | 0.994 | 0.994
|  |  |  | ECC Rating (A) | 758 | 758 | 758 | 758 | 758
|  |  |  | 50 POE Load (A) | 368 | 469 | 466 | 464 | 463
Nudgee Bulk | 623-1 | Nudgee BS | Hendra | NCC Rating (A) | 758 | 758 | 758 | 758 | 758 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 188 | 269 | 268 | 267 | 266
|  |  |  | Power Factor | 0.982 | 0.994 | 0.994 | 0.994 | 0.994
|  |  |  | ECC Rating (A) | 758 | 758 | 758 | 758 | 758
|  |  |  | 50 POE Load (A) | 368 | 469 | 466 | 464 | 463
Nudgee Bulk | 636-1 | Hendra | Clayfield | NCC Rating (A) | 335 | 725 | 725 | 725 | 725 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 216 | 215 | 214 | 214
|  |  |  | Power Factor | 0 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | ECC Rating (A) | 335 | 725 | 725 | 725 | 725
|  |  |  | 50 POE Load (A) | 114 | 205 | 204 | 204 | 203
Nudgee Bulk | 643-1 | Hendra | Hamilton | NCC Rating (A) | 753 | 753 | 753 | 753 | 753 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 121 | 121 | 120 | 120 | 121
|  |  |  | Power Factor | 0.994 | 0.994 | 0.994 | 0.994 | 0.994
|  |  |  | ECC Rating (A) | 805 | 805 | 805 | 805 | 805
|  |  |  | 50 POE Load (A) | 247 | 247 | 246 | 246 | 247
Nudgee Bulk | 674-1 | Hendra | Hamilton | NCC Rating (A) | 753 | 753 | 753 | 753 | 753 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 120 | 120 | 120 | 120 | 121
|  |  |  | Power Factor | 0.994 | 0.994 | 0.994 | 0.994 | 0.994
|  |  |  | ECC Rating (A) | 805 | 805 | 805 | 805 | 805
|  |  |  | 50 POE Load (A) | 247 | 247 | 246 | 246 | 247
Nudgee Bulk | 683-1 | Nudgee BS | Geebung | NCC Rating (A) | 488 | 488 | 488 | 488 | 488 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 153 | 154 | 150 | 148 | 147
|  |  |  | Power Factor | 0.995 | 0.993 | 0.994 | 0.994 | 0.994
|  |  |  | ECC Rating (A) | 488 | 488 | 488 | 488 | 488
|  |  |  | 50 POE Load (A) | 236 | 231 | 226 | 222 | 220
Nudgee Bulk | 684-1 | Nudgee BS | Geebung | NCC Rating (A) | 578 | 578 | 578 | 578 | 578 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 578 | 578 | 578 | 578 | 578
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Postmans Ridge Bulk | 376-1 | Postmans Ridge BS | Helidon | NCC Rating (A) | 290 | 290 | 290 | 290 | 290 | Rural | 170 | 6
|  |  |  | 10 POE Load (A) | 38 | 38 | 38 | 38 | 38
|  |  |  | Power Factor | 0.976 | 0.976 | 0.976 | 0.976 | 0.976
|  |  |  | ECC Rating (A) | 290 | 290 | 290 | 290 | 290
|  |  |  | 50 POE Load (A) | 37 | 36 | 36 | 36 | 36
Postmans Ridge Bulk | 379-1 | Postmans Ridge BS | Carpendale | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 24 | 25 | 25 | 25 | 25
|  |  |  | Power Factor | 0.992 | 0.992 | 0.992 | 0.992 | 0.992
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 50 | 50 | 51 | 51 | 51
Postmans Ridge Bulk | 379-2 | Carpendale | Tenthill | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Raceview Bulk | 354-1 | Raceview BS | Roderick St | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 193 | 190 | 189 | 188 | 188
|  |  |  | Power Factor | 0.986 | 0.986 | 0.986 | 0.986 | 0.986
|  |  |  | ECC Rating (A) | 532 | 532 | 532 | 532 | 532
|  |  |  | 50 POE Load (A) | 295 | 292 | 289 | 288 | 288
Raceview Bulk | 355-1 | Roderick St | Booval | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 106 | 104 | 103 | 103 | 103
|  |  |  | Power Factor | 0.984 | 0.985 | 0.985 | 0.985 | 0.985
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | 50 POE Load (A) | 288 | 285 | 282 | 281 | 281
Raceview Bulk | 361-1 | Raceview BS | Booval | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 220 | 218 | 217 | 216 | 216
|  |  |  | Power Factor | 0.985 | 0.985 | 0.985 | 0.985 | 0.985
|  |  |  | ECC Rating (A) | 943 | 943 | 943 | 943 | 943
|  |  |  | 50 POE Load (A) | 531 | 526 | 524 | 522 | 522
Raceview Bulk | 362-1 | Raceview BS | 362 Tee1 | NCC Rating (A) | 515 | 515 | 515 | 515 | 515 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 96 | 96 | 96 | 95 | 95
|  |  |  | Power Factor | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (A) | 515 | 515 | 515 | 515 | 515
|  |  |  | 50 POE Load (A) | 297 | 309 | 312 | 315 | 318
Raceview Bulk | 362-2 | 362 Tee1 | Flinders | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 31 | 30 | 29 | 29 | 28
|  |  |  | Power Factor | 0.759 | 0.752 | 0.748 | 0.744 | 0.741
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 131 | 129 | 129 | 128 | 127
Raceview Bulk | 362-3 | 362 Tee1 | Kalbar | NCC Rating (A) | 400 | 400 | 400 | 400 | 400 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 121 | 120 | 119 | 119 | 118
|  |  |  | Power Factor | 0.981 | 0.981 | 0.982 | 0.982 | 0.982
|  |  |  | ECC Rating (A) | 400 | 400 | 400 | 400 | 400
|  |  |  | 50 POE Load (A) | 120 | 118 | 118 | 117 | 117
Raceview Bulk | 363-1 | Raceview BS | 363 Tee1 | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 95 | 94 | 94 | 94 | 94
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | 50 POE Load (A) | 277 | 287 | 290 | 293 | 296
Raceview Bulk | 363-2 | 363 Tee1 | Flinders | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 8 | 8 | 7 | 7 | 7
|  |  |  | Power Factor | 0.721 | 0.681 | 0.656 | 0.631 | 0.609
|  |  |  | ECC Rating (A) | 579 | 579 | 579 | 579 | 579
|  |  |  | 50 POE Load (A) | 138 | 150 | 153 | 157 | 160
Raceview Bulk | 363-3 | 363 Tee1 | Kalbar | NCC Rating (A) | 537 | 537 | 537 | 537 | 537 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 101 | 99 | 99 | 98 | 98
|  |  |  | Power Factor | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (A) | 537 | 537 | 537 | 537 | 537
|  |  |  | 50 POE Load (A) | 316 | 312 | 309 | 308 | 307
Raceview Bulk | 3960-1 | Ipswich Sth | Yamanto | NCC Rating (A) | 760 | 760 | 760 | 760 | 760 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 213 | 227 | 230 | 234 | 238
|  |  |  | Power Factor | 0.984 | 0.984 | 0.984 | 0.985 | 0.985
|  |  |  | ECC Rating (A) | 760 | 760 | 760 | 760 | 760
|  |  |  | 50 POE Load (A) | 274 | 288 | 292 | 295 | 299
Raceview Bulk | 3972-1 | Yamanto | Flinders | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 100 | 98 | 97 | 97 | 96
|  |  |  | Power Factor | 0.947 | 0.946 | 0.946 | 0.946 | 0.946
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 151 | 149 | 148 | 147 | 150
Raceview Bulk | 3980-1 | Kalbar | Boonah | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 53 | 52 | 52 | 52 | 51
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | ECC Rating (A) | 921 | 921 | 921 | 921 | 921
|  |  |  | 50 POE Load (A) | 127 | 125 | 124 | 123 | 122
Raceview Bulk | 401-1 | Kalbar | Boonah | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 51 | 50 | 50 | 50 | 49
|  |  |  | Power Factor | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 146 | 144 | 142 | 141 | 141
Raceview Bulk | 411-1 | Raceview BS | Booval | NCC Rating (A) | 618 | 618 | 618 | 618 | 618 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 186 | 184 | 183 | 183 | 183
|  |  |  | Power Factor | 0.991 | 0.992 | 0.992 | 0.992 | 0.992
|  |  |  | ECC Rating (A) | 943 | 943 | 943 | 943 | 943
|  |  |  | 50 POE Load (A) | 515 | 510 | 508 | 507 | 507
Raceview Bulk | 509A-1 | Raceview BS | Ipswich Sth | NCC Rating (A) | 763 | 763 | 763 | 763 | 763 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 227 | 235 | 239 | 244 | 249
|  |  |  | Power Factor | 0.993 | 0.993 | 0.993 | 0.993 | 0.993
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 445 | 462 | 470 | 479 | 489
Raceview Bulk | 509B-1 | Raceview BS | Cooneana | NCC Rating (A) | 509 | 509 | 509 | 509 | 509 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 509 | 509 | 509 | 509 | 509
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Raceview Bulk | 510A-1 | Raceview BS | Ipswich Sth | NCC Rating (A) | 763 | 763 | 763 | 763 | 763 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 225 | 233 | 237 | 242 | 246
|  |  |  | Power Factor | 0.993 | 0.993 | 0.993 | 0.993 | 0.993
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 445 | 462 | 470 | 479 | 489
Raceview Bulk | 510B-1 | Raceview BS | Cooneana | NCC Rating (A) | 476 | 476 | 476 | 476 | 476 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 476 | 476 | 476 | 476 | 476
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Richlands Bulk | 3818-1 | Richlands BS | Wacol | NCC Rating (A) | 760 | 760 | 760 | 760 | 760 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 106 | 104 | 102 | 101 | 100
|  |  |  | Power Factor | 0.961 | 0.961 | 0.961 | 0.961 | 0.962
|  |  |  | ECC Rating (A) | 760 | 760 | 760 | 760 | 760
|  |  |  | 50 POE Load (A) | 212 | 208 | 204 | 201 | 200
Richlands Bulk | 454-1 | Richlands BS | Wacol Sth | NCC Rating (A) | 475 | 475 | 475 | 475 | 475 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 169 | 167 | 164 | 163 | 162
|  |  |  | Power Factor | 0.971 | 0.971 | 0.971 | 0.971 | 0.971
|  |  |  | ECC Rating (A) | 520 | 520 | 520 | 520 | 520
|  |  |  | 50 POE Load (A) | 364 | 358 | 353 | 350 | 349
Richlands Bulk | 455-1 | Richlands BS | Wacol Sth | NCC Rating (A) | 475 | 475 | 475 | 475 | 475 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 170 | 168 | 165 | 164 | 163
|  |  |  | Power Factor | 0.971 | 0.971 | 0.971 | 0.971 | 0.971
|  |  |  | ECC Rating (A) | 520 | 520 | 520 | 520 | 520
|  |  |  | 50 POE Load (A) | 364 | 358 | 353 | 350 | 349
Richlands Bulk | 543-1 | Inala | 543 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 357 | 353 | 351 | 349 | 348
Richlands Bulk | 543-2 | 543 Tee1 | Coopers Plains | NCC Rating (A) | 348 | 348 | 348 | 348 | 348 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 348 | 348 | 348 | 348 | 348
|  |  |  | 50 POE Load (A) | 294 | 305 | 257 | 244 | 238
Richlands Bulk | 543-3 | 543 Tee1 | Heathwood | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 855 | 855 | 855 | 855 | 855
|  |  |  | 50 POE Load (A) | 378 | 374 | 372 | 370 | 369
Richlands Bulk | 616-1 | Richlands BS | Darra | NCC Rating (A) | 434 | 434 | 434 | 434 | 434 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 185 | 188 | 185 | 183 | 182
|  |  |  | Power Factor | 0.787 | 0.803 | 0.792 | 0.781 | 0.776
|  |  |  | ECC Rating (A) | 468 | 468 | 468 | 468 | 468
|  |  |  | 50 POE Load (A) | 303 | 308 | 304 | 300 | 299
Richlands Bulk | 617-1 | Richlands BS | Darra | NCC Rating (A) | 434 | 434 | 434 | 434 | 434 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 191 | 194 | 191 | 189 | 188
|  |  |  | Power Factor | 0.787 | 0.804 | 0.792 | 0.782 | 0.776
|  |  |  | ECC Rating (A) | 468 | 468 | 468 | 468 | 468
|  |  |  | 50 POE Load (A) | 307 | 312 | 308 | 305 | 303
Richlands Bulk | 618-1 | Richlands BS | Inala | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 295 | 293 | 293 | 293 | 293
|  |  |  | Power Factor | 0.984 | 0.985 | 0.985 | 0.985 | 0.985
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 502 | 498 | 497 | 495 | 495
Richlands Bulk | 619-1 | Richlands BS | Inala | NCC Rating (A) | 603 | 603 | 603 | 603 | 603 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 191 | 190 | 189 | 189 | 189
|  |  |  | Power Factor | 0.985 | 0.985 | 0.985 | 0.985 | 0.985
|  |  |  | ECC Rating (A) | 603 | 603 | 603 | 603 | 603
|  |  |  | 50 POE Load (A) | 516 | 513 | 512 | 511 | 512
Richlands Bulk | 620-1 | Richlands BS | Oxley | NCC Rating (A) | 342 | 342 | 342 | 342 | 342 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 127 | 125 | 123 | 122 | 121
|  |  |  | Power Factor | 0.984 | 0.984 | 0.984 | 0.984 | 0.984
|  |  |  | ECC Rating (A) | 378 | 378 | 378 | 378 | 378
|  |  |  | 50 POE Load (A) | 254 | 250 | 247 | 244 | 243
Richlands Bulk | 621-1 | Richlands BS | Oxley | NCC Rating (A) | 342 | 342 | 342 | 342 | 342 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 120 | 119 | 117 | 116 | 115
|  |  |  | Power Factor | 0.98 | 0.98 | 0.981 | 0.981 | 0.981
|  |  |  | ECC Rating (A) | 378 | 378 | 378 | 378 | 378
|  |  |  | 50 POE Load (A) | 254 | 250 | 247 | 244 | 243
Richlands Bulk | 641-1 | Darra | Jindalee | NCC Rating (A) | 744 | 744 | 744 | 744 | 744 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 75 | 74 | 73 | 72 | 72
|  |  |  | Power Factor | 0.996 | 0.996 | 0.996 | 0.996 | 0.996
|  |  |  | ECC Rating (A) | 826 | 826 | 826 | 826 | 826
|  |  |  | 50 POE Load (A) | 149 | 147 | 145 | 144 | 143
Richlands Bulk | 642-1 | Darra | Jindalee | NCC Rating (A) | 744 | 744 | 744 | 744 | 744 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 73 | 72 | 72 | 71 | 70
|  |  |  | Power Factor | 0.997 | 0.996 | 0.996 | 0.996 | 0.996
|  |  |  | ECC Rating (A) | 826 | 826 | 826 | 826 | 826
|  |  |  | 50 POE Load (A) | 149 | 147 | 145 | 144 | 143
Richlands Bulk | 679-1 | Richlands BS | Wacol | NCC Rating (A) | 663 | 663 | 663 | 663 | 663 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 107 | 105 | 103 | 102 | 101
|  |  |  | Power Factor | 0.962 | 0.962 | 0.962 | 0.963 | 0.963
|  |  |  | ECC Rating (A) | 663 | 663 | 663 | 663 | 663
|  |  |  | 50 POE Load (A) | 229 | 225 | 221 | 218 | 217
Richlands Bulk | 680-1 | Richlands BS | Wacol | NCC Rating (A) | 760 | 760 | 760 | 760 | 760 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 100 | 98 | 97 | 95 | 95
|  |  |  | Power Factor | 0.959 | 0.959 | 0.96 | 0.96 | 0.96
|  |  |  | ECC Rating (A) | 760 | 760 | 760 | 760 | 760
|  |  |  | 50 POE Load (A) | 98 | 97 | 95 | 94 | 93
Richlands Bulk | 700-1 | Richlands BS | Darra | NCC Rating (A) | 551 | 551 | 551 | 551 | 551 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 146 | 149 | 147 | 145 | 144
|  |  |  | Power Factor | 0.833 | 0.848 | 0.837 | 0.828 | 0.823
|  |  |  | ECC Rating (A) | 551 | 551 | 551 | 551 | 551
|  |  |  | 50 POE Load (A) | 239 | 243 | 240 | 238 | 236
Runcorn Bulk | 3440-1 | Runcorn BS | Sunnybank | NCC Rating (A) | 601 | 601 | 601 | 601 | 601 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 307 | 304 | 324 | 425 | 423
|  |  |  | Power Factor | 0.977 | 0.977 | 0.976 | 0.976 | 0.976
|  |  |  | ECC Rating (A) | 601 | 601 | 601 | 601 | 601
|  |  |  | 50 POE Load (A) | 398 | 394 | 394 | 394 | 394
Runcorn Bulk | 433-1 | Runcorn BS | Calamvale | NCC Rating (A) | 450 | 450 | 450 | 450 | 450 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 450 | 450 | 450 | 450 | 450
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Runcorn Bulk | 434-1 | Runcorn | Calamvale | NCC Rating (A) | 450 | 450 | 450 | 450 | 450 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 450 | 450 | 450 | 450 | 450
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Runcorn Bulk | 459A-1 | Upper Mt Gravatt | Sunnybank | NCC Rating (A) | 818 | 818 | 818 | 0 | 0 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 65 | 64 | 69 | 0 | 0
|  |  |  | Power Factor | 0.905 | 0.905 | 0.904 | 0 | 0
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 0 | 0
|  |  |  | 50 POE Load (A) | 543 | 537 | 575 | 0 | 0
Runcorn Bulk | 459B-1 | Runcorn BS | Upper Mt Gravatt | NCC Rating (A) | 848 | 848 | 848 | 0 | 0 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 64 | 63 | 67 | 0 | 0
|  |  |  | Power Factor | 0.925 | 0.925 | 0.923 | 0 | 0
|  |  |  | ECC Rating (A) | 848 | 848 | 848 | 0 | 0
|  |  |  | 50 POE Load (A) | 387 | 383 | 411 | 0 | 0
Runcorn Bulk | 667-1 | Runcorn BS | Acacia Ridge | NCC Rating (A) | 453 | 453 | 453 | 453 | 453 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 28 | 28 | 28 | 28 | 28
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 453 | 453 | 453 | 453 | 453
|  |  |  | 50 POE Load (A) | 30 | 30 | 30 | 30 | 30
Runcorn Bulk | 668-1 | Runcorn BS | Acacia Ridge | NCC Rating (A) | 453 | 453 | 453 | 453 | 453 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 28 | 28 | 28 | 28 | 28
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 453 | 453 | 453 | 453 | 453
|  |  |  | 50 POE Load (A) | 30 | 30 | 30 | 30 | 30
Runcorn Bulk | 690-1 | Runcorn BS | Runcorn | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 185 | 182 | 181 | 179 | 179
|  |  |  | Power Factor | 0.993 | 0.993 | 0.993 | 0.994 | 0.994
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 468 | 462 | 459 | 455 | 452
Runcorn Bulk | 691-1 | Runcorn BS | Runcorn | NCC Rating (A) | 685 | 685 | 685 | 685 | 685 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 146 | 144 | 143 | 142 | 141
|  |  |  | Power Factor | 0.993 | 0.994 | 0.994 | 0.994 | 0.994
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 469 | 462 | 460 | 455 | 453
Runcorn Bulk | 694-1 | Runcorn BS | Eight Mile Plains Bus 1 | NCC Rating (A) | 581 | 581 | 581 | 581 | 581 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 189 | 186 | 184 | 182 | 181
|  |  |  | Power Factor | 0.991 | 0.991 | 0.991 | 0.992 | 0.992
|  |  |  | ECC Rating (A) | 581 | 581 | 581 | 581 | 581
|  |  |  | 50 POE Load (A) | 397 | 391 | 387 | 382 | 380
Sandgate Bulk | 3290-1 | Sandgate BS | Bald Hills Bus 1 | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 92 | 91 | 90 | 90 | 89
|  |  |  | Power Factor | 0.994 | 0.994 | 0.994 | 0.994 | 0.994
|  |  |  | ECC Rating (A) | 912 | 912 | 912 | 912 | 912
|  |  |  | 50 POE Load (A) | 204 | 201 | 200 | 198 | 197
Sandgate Bulk | 505-1 | Sandgate BS | Zilmere | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 199 | 196 | 191 | 189 | 188
|  |  |  | Power Factor | 0.983 | 0.984 | 0.987 | 0.987 | 0.987
|  |  |  | ECC Rating (A) | 912 | 912 | 912 | 912 | 912
|  |  |  | 50 POE Load (A) | 358 | 352 | 341 | 338 | 336
Sandgate Bulk | 524-1 | Sandgate BS | Geebung | NCC Rating (A) | 521 | 521 | 521 | 521 | 521 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 134 | 132 | 128 | 127 | 127
|  |  |  | Power Factor | 0.994 | 0.994 | 0.996 | 0.996 | 0.996
|  |  |  | ECC Rating (A) | 521 | 521 | 521 | 521 | 521
|  |  |  | 50 POE Load (A) | 267 | 263 | 253 | 251 | 249
Sandgate Bulk | 524-2 | Geebung | Zillmere | NCC Rating (A) | 441 | 441 | 441 | 441 | 441 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 139 | 137 | 133 | 132 | 132
|  |  |  | Power Factor | 0.955 | 0.955 | 0.959 | 0.959 | 0.959
|  |  |  | ECC Rating (A) | 441 | 441 | 441 | 441 | 441
|  |  |  | 50 POE Load (A) | 255 | 252 | 242 | 240 | 238
Sandgate Bulk | 561-1 | Sandgate BS | Brighton TR1 | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 77 | 76 | 76 | 75 | 75
|  |  |  | Power Factor | 0.996 | 0.996 | 0.996 | 0.996 | 0.996
|  |  |  | ECC Rating (A) | 841 | 841 | 841 | 841 | 841
|  |  |  | 50 POE Load (A) | 150 | 147 | 147 | 146 | 145
Sandgate Bulk | 656-1 | Sandgate BS | Brighton TR2 | NCC Rating (A) | 379 | 379 | 379 | 379 | 379 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 75 | 73 | 73 | 73 | 72
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1
|  |  |  | ECC Rating (A) | 379 | 379 | 379 | 379 | 379
|  |  |  | 50 POE Load (A) | 198 | 195 | 194 | 192 | 191
Sandgate Bulk | 664-1 | Geebung | Zillmere | NCC Rating (A) | 441 | 441 | 441 | 441 | 441 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 25 | 25 | 25 | 25 | 25
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 441 | 441 | 441 | 441 | 441
|  |  |  | 50 POE Load (A) | 27 | 27 | 27 | 27 | 27
Sandgate Bulk | 671-1 | Sandagate BS | Zillmere | NCC Rating (A) | 495 | 495 | 527 | 527 | 527 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 110 | 109 | 113 | 112 | 111
|  |  |  | Power Factor | 0.999 | 0.999 | 0.997 | 0.998 | 0.998
|  |  |  | ECC Rating (A) | 495 | 495 | 599 | 599 | 599
|  |  |  | 50 POE Load (A) | 192 | 189 | 228 | 226 | 225
Stafford Bulk | 502-1 | Kedron | Clayfield | NCC Rating (A) | 334 | 0 | 0 | 0 | 0 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 109 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0.988 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 334 | 0 | 0 | 0 | 0
|  |  |  | 50 POE Load (A) | 228 | 0 | 0 | 0 | 0
Stafford Bulk | 522-1 | Kedron | Chermside | NCC Rating (A) | 308 | 0 | 0 | 0 | 0 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 308 | 0 | 0 | 0 | 0
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Stafford Bulk | 525-1 | Chermside | Zillmere | NCC Rating (A) | 332 | 0 | 0 | 0 | 0 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 308 | 0 | 0 | 0 | 0
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Stafford Bulk | 534-1 | Kedron | Clayfield | NCC Rating (A) | 334 | 0 | 0 | 0 | 0 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 109 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0.988 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 334 | 0 | 0 | 0 | 0
|  |  |  | 50 POE Load (A) | 228 | 0 | 0 | 0 | 0
Stafford Bulk | 548-1 | Stafford BS | Enoggera | NCC Rating (A) | 886 | 886 | 886 | 886 | 886 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 400 | 395 | 393 | 392 | 391
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | ECC Rating (A) | 1020 | 1020 | 1020 | 1020 | 1020
|  |  |  | 50 POE Load (A) | 812 | 801 | 798 | 795 | 793
Stafford Bulk | 550-1 | Stafford BS | Chermside | NCC Rating (A) | 748 | 748 | 748 | 748 | 748 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 253 | 250 | 249 | 248 | 247
|  |  |  | Power Factor | 0.996 | 0.996 | 0.996 | 0.996 | 0.996
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 546 | 541 | 538 | 536 | 535
Stafford Bulk | 551-1 | Stafford BS | Chermside | NCC Rating (A) | 748 | 748 | 748 | 748 | 748 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 253 | 250 | 248 | 247 | 247
|  |  |  | Power Factor | 0.996 | 0.996 | 0.996 | 0.996 | 0.996
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 546 | 541 | 538 | 536 | 535
Stafford Bulk | 567-1 | Stafford BS | Kedron | NCC Rating (A) | 613 | 613 | 613 | 613 | 613 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 302 | 192 | 191 | 191 | 191
|  |  |  | Power Factor | 0.992 | 0.994 | 0.994 | 0.994 | 0.994
|  |  |  | ECC Rating (A) | 685 | 685 | 685 | 685 | 685
|  |  |  | 50 POE Load (A) | 607 | 382 | 381 | 380 | 380
Stafford Bulk | 568-1 | Stafford BS | Kedron | NCC Rating (A) | 613 | 613 | 613 | 613 | 613 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 305 | 193 | 193 | 192 | 192
|  |  |  | Power Factor | 0.992 | 0.993 | 0.993 | 0.993 | 0.993
|  |  |  | ECC Rating (A) | 685 | 685 | 685 | 685 | 685
|  |  |  | 50 POE Load (A) | 607 | 382 | 381 | 380 | 380
Stafford Bulk | 594-1 | Stafford BS | Enoggera | NCC Rating (A) | 886 | 886 | 886 | 886 | 886 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 398 | 392 | 391 | 389 | 388
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | ECC Rating (A) | 1020 | 1020 | 1020 | 1020 | 1020
|  |  |  | 50 POE Load (A) | 812 | 801 | 798 | 795 | 793
Stafford Bulk | 595-1 | Enoggera | Grovely | NCC Rating (A) | 720 | 720 | 720 | 720 | 720 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 143 | 140 | 139 | 138 | 137
|  |  |  | Power Factor | 0.994 | 0.994 | 0.994 | 0.994 | 0.994
|  |  |  | ECC Rating (A) | 720 | 720 | 720 | 720 | 720
|  |  |  | 50 POE Load (A) | 274 | 270 | 268 | 266 | 264
Stafford Bulk | 596-1 | Enoggera | Grovely | NCC Rating (A) | 720 | 720 | 720 | 720 | 720 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 144 | 141 | 140 | 139 | 138
|  |  |  | Power Factor | 0.994 | 0.994 | 0.994 | 0.994 | 0.994
|  |  |  | ECC Rating (A) | 720 | 720 | 720 | 720 | 720
|  |  |  | 50 POE Load (A) | 274 | 270 | 268 | 266 | 264
Stafford Bulk | 607-1 | Chermside | Zillmere | NCC Rating (A) | 332 | 332 | 332 | 332 | 332 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 332 | 332 | 332 | 332 | 332
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Sunrise Hills Bulk | 308-1 | Perigian | 308 Tee1 | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 444 | 439 | 439 | 438 | 437
|  |  |  | Power Factor | 0.989 | 0.989 | 0.989 | 0.989 | 0.989
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 414 | 410 | 409 | 409 | 408
Sunrise Hills Bulk | 308-2 | 308 Tee1 | Coolum | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 444 | 439 | 439 | 438 | 437
|  |  |  | Power Factor | 0.992 | 0.992 | 0.992 | 0.993 | 0.993
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 415 | 410 | 409 | 409 | 408
Sunrise Hills Bulk | 308-3 | 308 Tee1 | 307 Tee2 | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Sunrise Hills Bulk | 3100-1 | Sunrise Hills BS | 3100 Tee1 | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 645 | 639 | 639 | 638 | 638
|  |  |  | Power Factor | 0.976 | 0.976 | 0.976 | 0.976 | 0.976
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 605 | 599 | 599 | 599 | 598
Sunrise Hills Bulk | 3100-2 | 3100 Tee1 | Perigian | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 645 | 639 | 639 | 638 | 638
|  |  |  | Power Factor | 0.976 | 0.976 | 0.976 | 0.976 | 0.976
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 599 | 594 | 594 | 594 | 593
Sunrise Hills Bulk | 343-1 | Sunrise Hills BS | 343 Tee1 | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 378 | 372 | 368 | 366 | 364
|  |  |  | Power Factor | 0.983 | 0.983 | 0.983 | 0.983 | 0.983
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 597 | 587 | 581 | 576 | 573
Sunrise Hills Bulk | 343-2 | 343 Tee1 | Tewantin | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 129 | 125 | 123 | 120 | 119
|  |  |  | Power Factor | 0.988 | 0.989 | 0.989 | 0.99 | 0.99
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 366 | 358 | 353 | 348 | 345
Sunrise Hills Bulk | 343-3 | 343 Tee1 | Cooroy | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 249 | 247 | 246 | 246 | 245
|  |  |  | Power Factor | 0.983 | 0.983 | 0.983 | 0.983 | 0.983
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | 50 POE Load (A) | 232 | 230 | 229 | 229 | 228
Sunrise Hills Bulk | 346-1 | Sunrise Hills BS | 346 Tee1 | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 257 | 253 | 250 | 247 | 245
|  |  |  | Power Factor | 0.984 | 0.984 | 0.984 | 0.984 | 0.984
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 298 | 292 | 287 | 283 | 281
Sunrise Hills Bulk | 346-2 | 346 Tee1 | Tewantin | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 257 | 253 | 250 | 247 | 245
|  |  |  | Power Factor | 0.984 | 0.984 | 0.984 | 0.984 | 0.984
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 363 | 356 | 350 | 346 | 343
Sunrise Hills Bulk | 346-3 | 346 Tee1 | 3100 Tee1 | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Sunrise Hills Bulk | 488-1 | Cooroy | 488 Tee1 | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 139 | 138 | 137 | 137 | 137
|  |  |  | Power Factor | 0.985 | 0.985 | 0.985 | 0.984 | 0.984
|  |  |  | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
|  |  |  | 50 POE Load (A) | 130 | 129 | 128 | 128 | 128
Sunrise Hills Bulk | 488-3 | 488 Tee1 | 488 Tee2 | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 139 | 138 | 137 | 137 | 137
|  |  |  | Power Factor | 0.985 | 0.985 | 0.985 | 0.984 | 0.984
|  |  |  | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | 50 POE Load (A) | 130 | 129 | 128 | 128 | 128
Sunrise Hills Bulk | 488-4 | 488 Tee2 | Black Mtn | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 75 | 74 | 74 | 74 | 74
|  |  |  | Power Factor | 0.963 | 0.963 | 0.963 | 0.961 | 0.961
|  |  |  | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | 50 POE Load (A) | 70 | 69 | 69 | 69 | 69
Sunrise Hills Bulk | 488-5 | 488 Tee2 | 488 Tee3 | NCC Rating (A) | 293 | 293 | 490 | 490 | 490 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 65 | 65 | 64 | 64 | 64
|  |  |  | Power Factor | 0.998 | 0.998 | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (A) | 293 | 293 | 490 | 490 | 490
|  |  |  | 50 POE Load (A) | 61 | 60 | 73 | 73 | 73
Sunrise Hills Bulk | 488-6 | 488 Tee3 | Eumundi | NCC Rating (A) | 468 | 468 | 468 | 468 | 468 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 65 | 65 | 64 | 64 | 64
|  |  |  | Power Factor | 0.998 | 0.998 | 0.998 | 0.998 | 0.998
|  |  |  | ECC Rating (A) | 468 | 468 | 468 | 468 | 468
|  |  |  | 50 POE Load (A) | 65 | 65 | 64 | 65 | 65
Sunrise Hills Bulk | 488-7 | 488 Tee3 | Yandina | NCC Rating (A) | 293 | 293 | 582 | 582 | 582 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 293 | 293 | 582 | 582 | 582
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Tennyson Bulk | 3390-1 | Taringa | Indooroopilly | NCC Rating (A) | 779 | 779 | 779 | 779 | 779 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 81 | 80 | 79 | 78 | 78
|  |  |  | Power Factor | 0.978 | 0.979 | 0.978 | 0.979 | 0.979
|  |  |  | ECC Rating (A) | 779 | 779 | 779 | 779 | 779
|  |  |  | 50 POE Load (A) | 119 | 118 | 116 | 116 | 115
Tennyson Bulk | 3393-1 | Tennyson BS | St Lucia TR1 | NCC Rating (A) | 640 | 640 | 640 | 640 | 640 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 130 | 128 | 127 | 126 | 126
|  |  |  | Power Factor | 0.966 | 0.967 | 0.967 | 0.967 | 0.967
|  |  |  | ECC Rating (A) | 640 | 640 | 640 | 640 | 640
|  |  |  | 50 POE Load (A) | 272 | 267 | 265 | 263 | 262
Tennyson Bulk | 3394-1 | Tennyson BS | St Lucia TR2 | NCC Rating (A) | 640 | 640 | 640 | 640 | 640 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 124 | 123 | 122 | 121 | 120
|  |  |  | Power Factor | 0.966 | 0.966 | 0.966 | 0.966 | 0.966
|  |  |  | ECC Rating (A) | 640 | 640 | 640 | 640 | 640
|  |  |  | 50 POE Load (A) | 124 | 122 | 121 | 121 | 120
Tennyson Bulk | 3460-1 | Annerley | Buranda | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 118 | 148 | 123 | 173 | 173
|  |  |  | Power Factor | 0.99 | 0.988 | 0.99 | 0.986 | 0.986
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 228 | 288 | 238 | 337 | 338
Tennyson Bulk | 3461-1 | Annerley | Buranda | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 118 | 149 | 123 | 173 | 173
|  |  |  | Power Factor | 0.99 | 0.988 | 0.99 | 0.986 | 0.986
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 228 | 288 | 238 | 337 | 338
Tennyson Bulk | 410-1 | Sherwood | Indooroopilly | NCC Rating (A) | 425 | 425 | 425 | 425 | 425 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 171 | 169 | 168 | 167 | 166
|  |  |  | Power Factor | 0.992 | 0.992 | 0.992 | 0.992 | 0.993
|  |  |  | ECC Rating (A) | 480 | 480 | 480 | 480 | 480
|  |  |  | 50 POE Load (A) | 285 | 282 | 280 | 279 | 278
Tennyson Bulk | 460-1 | Tennyson BS | Sherwood | NCC Rating (A) | 774 | 774 | 774 | 774 | 774 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 277 | 274 | 272 | 270 | 269
|  |  |  | Power Factor | 0.995 | 0.995 | 0.995 | 0.995 | 0.996
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 378 | 373 | 370 | 368 | 367
Tennyson Bulk | 480-1 | Taringa | St Lucia | NCC Rating (A) | 640 | 640 | 640 | 640 | 640 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 135 | 133 | 132 | 131 | 131
|  |  |  | Power Factor | 0.965 | 0.965 | 0.966 | 0.966 | 0.966
|  |  |  | ECC Rating (A) | 640 | 640 | 640 | 640 | 640
|  |  |  | 50 POE Load (A) | 270 | 266 | 263 | 262 | 261
Tennyson Bulk | 504-1 | Tennyson BS | Taringa | NCC Rating (A) | 637 | 637 | 637 | 637 | 637 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 236 | 233 | 231 | 230 | 229
|  |  |  | Power Factor | 0.995 | 0.995 | 0.995 | 0.995 | 0.995
|  |  |  | ECC Rating (A) | 742 | 742 | 742 | 742 | 742
|  |  |  | 50 POE Load (A) | 362 | 358 | 356 | 354 | 353
Tennyson Bulk | 507A-1 | Toowong | Indooroopilly | NCC Rating (A) | 786 | 786 | 786 | 786 | 786 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 82 | 81 | 80 | 80 | 79
|  |  |  | Power Factor | 0.982 | 0.982 | 0.982 | 0.982 | 0.982
|  |  |  | ECC Rating (A) | 917 | 917 | 917 | 917 | 917
|  |  |  | 50 POE Load (A) | 120 | 119 | 118 | 117 | 116
Tennyson Bulk | 507B-1 | Toowong | Taringa | NCC Rating (A) | 783 | 783 | 783 | 783 | 783 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 81 | 80 | 79 | 79 | 78
|  |  |  | Power Factor | 0.995 | 0.996 | 0.996 | 0.996 | 0.996
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 120 | 119 | 117 | 116 | 116
Tennyson Bulk | 511-1 | Tennyson BS | Moorooka | NCC Rating (A) | 801 | 801 | 801 | 801 | 801 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 121 | 119 | 119 | 119 | 119
|  |  |  | Power Factor | 0.981 | 0.981 | 0.981 | 0.981 | 0.981
|  |  |  | ECC Rating (A) | 816 | 816 | 816 | 816 | 816
|  |  |  | 50 POE Load (A) | 249 | 251 | 251 | 251 | 253
Tennyson Bulk | 514-1 | Tennyson BS | Moorooka | NCC Rating (A) | 801 | 801 | 801 | 801 | 801 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 121 | 122 | 122 | 122 | 123
|  |  |  | Power Factor | 0.981 | 0.982 | 0.982 | 0.982 | 0.982
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 249 | 251 | 251 | 251 | 252
Tennyson Bulk | 515-1 | Tennyson BS | Sherwood | NCC Rating (A) | 768 | 768 | 768 | 768 | 768 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 294 | 291 | 288 | 287 | 285
|  |  |  | Power Factor | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
|  |  |  | ECC Rating (A) | 797 | 797 | 797 | 797 | 797
|  |  |  | 50 POE Load (A) | 425 | 420 | 417 | 414 | 412
Tennyson Bulk | 523A&B-1 | Tennyson BS | Rocklea | NCC Rating (A) | 638 | 638 | 0 | 0 | 0 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 638 | 638 | 0 | 0 | 0
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Tennyson Bulk | 523A-1 | Tennyson BS | Rocklea | NCC Rating (A) | 0 | 0 | 688 | 688 | 688 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 8 | 8 | 8
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 0 | 0 | 688 | 688 | 688
|  |  |  | 50 POE Load (A) | 0 | 0 | 8 | 8 | 8
Tennyson Bulk | 539-1 | Sherwood | Kenmore | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 280 | NA
|  |  |  | 10 POE Load (A) | 201 | 198 | 196 | 194 | 193
|  |  |  | Power Factor | 0.995 | 0.996 | 0.996 | 0.996 | 0.996
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | 50 POE Load (A) | 440 | 433 | 429 | 425 | 422
Tennyson Bulk | 554-1 | Tennyson BS | Sherwood | NCC Rating (A) | 768 | 768 | 768 | 768 | 768 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 312 | 308 | 306 | 304 | 303
|  |  |  | Power Factor | 0.996 | 0.996 | 0.996 | 0.996 | 0.996
|  |  |  | ECC Rating (A) | 768 | 768 | 768 | 768 | 768
|  |  |  | 50 POE Load (A) | 439 | 433 | 430 | 428 | 426
Tennyson Bulk | 571-1 | Indooroopilly | Kenmore | NCC Rating (A) | 527 | 527 | 527 | 527 | 527 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 261 | 257 | 255 | 253 | 251
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.991
|  |  |  | ECC Rating (A) | 527 | 527 | 527 | 527 | 527
|  |  |  | 50 POE Load (A) | 435 | 428 | 424 | 420 | 417
Tennyson Bulk | 606-1 | Tennyson BS | Taringa | NCC Rating (A) | 637 | 637 | 637 | 637 | 637 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 237 | 234 | 232 | 231 | 230
|  |  |  | Power Factor | 0.995 | 0.995 | 0.995 | 0.995 | 0.995
|  |  |  | ECC Rating (A) | 742 | 742 | 742 | 742 | 742
|  |  |  | 50 POE Load (A) | 363 | 359 | 356 | 355 | 354
Tennyson Bulk | 637-1 | Tennyson BS | Annerley | NCC Rating (A) | 765 | 765 | 765 | 765 | 765 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 231 | 259 | 235 | 283 | 284
|  |  |  | Power Factor | 0.994 | 0.993 | 0.994 | 0.991 | 0.991
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 474 | 535 | 483 | 586 | 587
Tennyson Bulk | 638-1 | Tennyson BS | Annerley | NCC Rating (A) | 765 | 765 | 765 | 765 | 765 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 232 | 260 | 236 | 284 | 285
|  |  |  | Power Factor | 0.994 | 0.993 | 0.994 | 0.991 | 0.991
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 474 | 535 | 483 | 586 | 587
Tennyson Bulk | F703-1 | Sherwood | Indooroopilly | NCC Rating (A) | 425 | 425 | 425 | 425 | 425 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 173 | 171 | 169 | 169 | 168
|  |  |  | Power Factor | 0.992 | 0.993 | 0.993 | 0.993 | 0.993
|  |  |  | ECC Rating (A) | 480 | 480 | 480 | 480 | 480
|  |  |  | 50 POE Load (A) | 286 | 283 | 281 | 280 | 279
Victoria Park Bulk | 627-1 | Victoria Pk BS | Astor Tce | NCC Rating (A) | 525 | 525 | 525 | 525 | 525 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0.968 | 0.968 | 0.968 | 0.968 | 0.968
|  |  |  | ECC Rating (A) | 542 | 542 | 542 | 542 | 542
|  |  |  | 50 POE Load (A) | 186 | 184 | 183 | 182 | 181
Victoria Park Bulk | 628-1 | Victoria Pk BS | Astor Tce | NCC Rating (A) | 502 | 502 | 502 | 502 | 502 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 143 | 141 | 140 | 139 | 139
|  |  |  | Power Factor | 0.964 | 0.964 | 0.964 | 0.964 | 0.964
|  |  |  | ECC Rating (A) | 542 | 542 | 542 | 542 | 542
|  |  |  | 50 POE Load (A) | 379 | 374 | 372 | 370 | 369
Victoria Park Bulk | 639-1 | Victoria Pk BS | Newmarket | NCC Rating (A) | 536 | 536 | 536 | 536 | 536 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 142 | 140 | 139 | 138 | 137
|  |  |  | Power Factor | 0.996 | 0.996 | 0.996 | 0.996 | 0.996
|  |  |  | ECC Rating (A) | 623 | 623 | 623 | 623 | 623
|  |  |  | 50 POE Load (A) | 286 | 280 | 278 | 276 | 275
Victoria Park Bulk | 649-1 | Victoria Pk BS | Astor Tce | NCC Rating (A) | 525 | 525 | 525 | 525 | 525 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 144 | 143 | 142 | 141 | 141
|  |  |  | Power Factor | 0.964 | 0.964 | 0.964 | 0.964 | 0.964
|  |  |  | ECC Rating (A) | 542 | 542 | 542 | 542 | 542
|  |  |  | 50 POE Load (A) | 379 | 374 | 372 | 370 | 369
Victoria Park Bulk | 653-1 | Victoria Pk BS | Newmarket | NCC Rating (A) | 536 | 536 | 536 | 536 | 536 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 142 | 140 | 139 | 138 | 137
|  |  |  | Power Factor | 0.996 | 0.996 | 0.996 | 0.996 | 0.996
|  |  |  | ECC Rating (A) | 623 | 623 | 623 | 623 | 623
|  |  |  | 50 POE Load (A) | 286 | 280 | 278 | 276 | 275
Victoria Park Bulk | 659B-1 | Victoria Pk BS | Clayfield | NCC Rating (A) | 359 | 0 | 0 | 0 | 0 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 6 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 359 | 0 | 0 | 0 | 0
|  |  |  | 50 POE Load (A) | 111 | 0 | 0 | 0 | 0
Victoria Park Bulk | 689-1 | Victoria Pk BS | Astor Tce | NCC Rating (A) | 588 | 588 | 588 | 588 | 588 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 9 | 9 | 9 | 9 | 9
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 588 | 588 | 588 | 588 | 588
|  |  |  | 50 POE Load (A) | 10 | 10 | 10 | 10 | 10
Note on F1226: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Adjusted to reflect theoretical load on feeder ignoring voltage constraints